## Public Non-CIP CE Posting
Filing | Region | Registered Entity Name | NCR | NERC Violation ID | Standard | Req. | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity
2018-10-31 | Midwest Reliability Organization (MRO) | Menasha Utilities (WPPI-MU) | NCR10108 | MRO2016016186 | PRC-006-1 | R9 | On June 28, 2016, WPPI-MU submitted a Self-Certification stating that, as a Distribution Provider, it was in noncompliance with PRC-006-1 R9. WPPI-MU stated that it did not provide automatic tripping of Load in accordance with the underfrequency load shedding (UFLS) program as designed by its Planning Coordinator (PC). After submitting the Self-Certification, WPPI-MU discovered an additional instance of noncompliance. The first instance of noncompliance involved a UFLS relay at its Melissa substation that was responsible for potentially shedding a 0.35 MW feeder. The UFLS relay was set to operate at 59.3 Hz. Under the terms of the UFLS program, the UFLS relay should have been set to operate at 59 Hz. The noncompliance was caused because personnel applied incorrect relay settings during the reconfiguration of the circuit; the responsible personnel knew the setting was incorrect and intended to correct the settings, but failed to do so. Additionally, there was a lack of controls in place to ensure that relay settings were in accordance with the UFLS program. The second instance of noncompliance involved a UFLS relay at its Tayco substation that was responsible for potentially shedding 14.3 MW of Load. The UFLS relay was set to operate at 58.7 Hz. Under the terms of the UFLS program, the UFLS relay should have been set to 59 Hz. The noncompliance was caused by reporting the incorrect settings to its PC, which were then incorporated into the UFLS program. Additionally, there was a lack of controls in place to ensure that relay settings were in accordance with the UFLS program. This noncompliance started on October 1, 2013, when the Standard and Requirement became enforceable, and ended on December 24, 2016, when the settings at the Tayco substation were corrected. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The total amount of Load in the island that WPPI-MU is located in is approximately 13,600 MW, the potential loss of 15 MW would only impact about .1% of the total Load in the potential island. No harm is known to have occurred. WPPI-MU has no relevant history of noncompliance. | To mitigate this noncompliance, WPPI-MU: 1) changed the 0.35 feeder's circuit's relay setting at its Melissa substation to operate at 59.0 Hz; 2) changed the circuit's relay setting at its Tayco substation to operate at 59.0 Hz; and 3) modified its documented UFLS testing process to include confirmation steps and required notification and reporting steps in the case of inconsistencies.
2018-10-31 | Midwest Reliability Organization (MRO) | Noble Great Plains Windpark, LLC | NCR11070 | MRO2018020129 | MOD-026-1 | R2 | On July 24, 2018, NOBLEGP submitted a Self-Report stating that as a Generator Owner, it was in noncompliance with MOD-026-1 R2. Specifically, NOBLEGP was unable to provide a verified volt/var control function model for 30% of its applicable unit gross MVA to its Transmission Planner by July 1, 2018 as required by the phased implementation plan for the Standard. NOBLEGP owns a single wind generation unit, meaning that under the phased implementation plan, it was required to provide a verified model for that unit by July 1, 2018. The noncompliance was caused by inadequate internal controls to track the activities required by the Standard. The noncompliance began on July 1, 2018, the date the Standard and Requirement became enforceable, and ended on September 17, 2018, when NOBLEGP submitted its verified model to its Transmission Planner. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance impacted a single wind generation Facility with a capacity of 114 MW, which represents a minimal potential impact to the volt/var support for the overall system. Additionally, the noncompliance was self-identified, which limited the duration of the noncompliance to under three months. Finally, because NOBLEGP only has one Facility, mitigation of the noncompliance resulted in 100% completion almost six years in advance of the phased implementation plan’s 100% completion deadline. No harm is known to have occurred. NOBLEGP has had no prior instances of noncompliance with MOD-026-2. | To mitigate this noncompliance, NOBELGP: 1) had a third-party consultant complete the model verification; 2) submitted its model report to its Transmission Planner; 3) implemented monthly NERC compliance update calls to ensure applicable personnel are aware of NERC compliance due dates; and 4) implemented a process that tracks the implementation of new or revised NERC Reliability Standards.
2018-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Millennium Power Partners, LP | NCR07144 | NPCC2017017209 | PRC-005-1 | R2. | On March 2, 2017, Millennium Power Partners, LP ("the Entity") submitted a Self-Report stating that, as a Generator Owner ("GO"), it was in noncompliance with PRC-005-1.1b R2. Specifically, the Entity failed to demonstrate compliance with the standard and requirement as it did not retain documentary evidence of tests conducted before April 2012 for two Current Transformers (CTs) and six Potential Transformers (PTs). The Entity was also unable to locate any historic testing records for one additional PT, six additional CTs and one microprocessor relay. This noncompliance started on June 18, 2007, when the standard and requirement became enforceable, and ended in July 2017, when the Entity completed required tests for the aforementioned devices, all of which are associated with its single generating facility (a combined-cycle generating plant). The root cause of this instance of non-compliance has the following traits: a) Record keeping gaps (relating to maintenance activities) caused by a multitude of different types of test forms for relays, CTs, PTs and DC circuitry. b) Hired contractor's poor understanding of NERC testing requirements. c) Inadequate transitioning of compliance programs. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This instance of noncompliance affected the Entity's single generating facility, which is a combined-cycle ("CC") unit that was operated with capacity factors of 69% (in 2015), 55% (in 2016) and 41% (in 2017). The CC generating unit consists of one gas turbine and one steam turbine with a combined Summer Claimed Capability of 335 MW, which is approximately 13% of the Entity's RC's (ISO-NE) required operating reserves (2600 MWs). In conclusion, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily as a result of a malfunction of any of the untested devices, the RC would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) Completed required tests for the aforementioned noncompliant CTs, PTs and single microprocessor relay; and 2) To prevent a recurrence of similar instances of noncompliance, implemented, for its own facility, compliance test forms that are included in its parent company's (Talen Energy Corporation) protection system maintenance procedure (TE-NERC-203) and other compliance documents developed by its parent company (Talen's NERC compliance program TE-NERC-100, Internal controls document TE-NERC-404 and TE-NERC-203 (PRC-005) document).
2018-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Millennium Power Partners, LP | NCR07144 | NPCC2017017252 | PRC-005-2(i) | R3. | On March 22, 2017, Millennium Power Partners, LP ("the Entity") submitted a Self-Report stating that, as a Generator Owner ("GO"), it was in noncompliance with PRC-005-2(i) R3. Specifically, the Entity failed to demonstrate compliance with the standard and requirement as it did not retain documentary evidence of any 4-month periodic checks for DC grounds and electrolyte levels for its VLA batteries (Table 1-4(a) of the standard) and of any 4-month periodic checks for DC grounds for its VRLA batteries (Table 1-4(b) of the standard). Additionally, the Entity did not retain documentary evidence of any 18-month periodic readings of battery terminal connection resistance for its entire fleet of VLA and VRLA batteries (Tables 1-4(a) and 1-4(b), respectively). This noncompliance started on May 29, 2015, when the standard and requirement became enforceable, and ended on March 21, 2017, when the Entity completed required tests for the aforementioned DC supply devices, all of which are associated with its single generating facility (a combined-cycle generating plant). The root cause of this instance of non-compliance has the following traits: a) Record keeping gaps (relating to maintenance activities) caused by a multitude of different types of test forms for relays, CTs, PTs and DC circuitry. b) Hired contractor's poor understanding of NERC testing requirements. c) Inadequate transitioning of compliance programs. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This instance of noncompliance affected the Entity's single generating facility, which is a combined-cycle ("CC") unit that was operated with capacity factors of 69% (in 2015), 55% (in 2016) and 41% (in 2017). The CC generating unit consists of one gas turbine and one steam turbine with a combined Summer Claimed Capability of 335 MW, which is approximately 13% of the Entity's RC's (ISO-NE) required operating reserves (2600 MWs). In conclusion, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily as a result of a malfunction of any of the untested DC supply devices, the RC would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) Completed required tests for the aforementioned DC supply devices; and 2) To prevent a recurrence of similar instances of noncompliance, implemented, for its own facility, compliance test forms that are included in its parent company's (Talen Energy Corporation) protection system maintenance procedure (TE-NERC-203) and other compliance documents developed by its parent company (Talen's NERC compliance program TE-NERC-100, Internal controls document TE-NERC-404 and TE-NERC-203 (PRC-005) document).
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC2017018621 | MOD-025-2 | R1 | On November 1, 2017, Morgantown submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. The MOD-025 implementation plan required 40% of the entity’s applicable units to have generator real power and reactive power verification testing complete by July 1, 2016. The entity has a single generating unit. NRG Maintenance Services, LLC, a subsidiary of NRG, operates and maintains the entity plant under an Operation & Maintenance (O&M) Agreement. In preparing for the July 1, 2016 compliance date for MOD-025-2, NRG, on behalf of its wholly owned and O&M managed Registered Entities, determined that it would demonstrate compliance with MOD-025-2 by NERC Region rather than by individual Registered Entity. That decision resulted in NRG attempting to achieve compliance with MOD-025-2 by achieving compliance for 40% of its Registered Entities registered in the ReliabilityFirst footprint by the July 1, 2016 implementation date. This is not permissible under the implementation plan. Although the entity completed the required MOD-025-2 testing as of July 29, 2016, the entity self-reported that it did not verify 40% of its generating Facilities by July 1, 2016 as per Requirements R1 and R2 in the MOD-025 Implementation Plan. In addition, the entity did not submit or record all required data pursuant to MOD-025 Attachment 1. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the entity was unaware of the exact MOD-025-2 testing and coordination requirements. Verification is involved because the entity did not verify that it was able to achieve MOD-025-2 compliance on a Region basis, which is not permissible under the Standard. That failure to verify that the entity’s testing strategy was valid is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with MOD-025-2 R1 and ended on October 30, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized by a number of factors. First, the entity completed the testing less than one month late on July 29, 2016. It should also be noted that when the entity completed the overdue testing, no changes were required to show compliance with MOD-025. Second, entity personnel have historically been performing real and reactive power capability testing that match the requirements in MOD-025. (Entity personnel adhere to PJM Manual 14 D Rev 40 1/1/17 Attachment E. 2 -E3 Requirements and PJM Manual 21 Rev 12 1/1/17 Section 2.1-2.3 and Appendix A, where reactive testing for these units is performed every 66 months and where the net real power capability is performed annually. In this market, real and reactive power testing have been regularly verified, reported, communicated, and approved by PJM's Transmission Planner to validate generator capability.) The entity has also been sharing that information with PJM. Although the testing form that the entity provided to PJM following 2016 testing was incomplete, the entity still timely performed and submitted some of the testing required by MOD-025 before the July 1, 2016 implementation date. The entity also provided PJM with all of the information that PJM required to validate the entity’s net capability, which further reduces the risk. Lastly, the entity only contributes approximately 50 MW to the grid and operated at approximately a 93% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed the required real and reactive capability testing on the entity Generating unit. The entity forwarded the test results to FirstEnergy for submission to PJM; 2) completed the resubmittal of the MOD-025 Attachment 2 data on the appropriate form for the entity and submitted it to PJM; and 3) developed and implemented a process for internal review of test data by NRG Energy, Inc.’s Regulatory Compliance team prior to submittal to PJM to ensure all required data has been collected. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC2017018622 | MOD-025-2 | R2 | On November 1, 2017, Morgantown submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. The MOD-025 implementation plan required 40% of the entity’s applicable units to have performed generator real power and reactive power verification testing by July 1, 2016. The entity has a single generating unit. NRG Maintenance Services, LLC, a subsidiary of NRG, operates and maintains the entity plant under an Operation & Maintenance (O&M) Agreement. In preparing for the July 1, 2016 compliance date for MOD-025-2, NRG, on behalf of its wholly owned and O&M managed Registered Entities, determined that it would demonstrate compliance with MOD-025-2 by NERC Region rather than by individual Registered Entity. That decision resulted in NRG attempting to achieve compliance with MOD-025-2 by achieving compliance for 40% of its Registered Entities registered in the ReliabilityFirst footprint by the July 1, 2016 implementation date. This is not permissible under the implementation plan. Although the entity completed the required MOD-025-2 testing as of July 29, 2016, the entity self-reported that it did not verify 40% of its generating Facilities by July 1, 2016 as per Requirements R1 and R2 in the MOD-025 Implementation plan. In addition, the entity did not submit or record all required data pursuant to MOD-025 Attachment 1. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the entity was unaware of the exact MOD-025-2 testing and coordination requirements. Verification is involved because the entity did not verify that it was able to achieve MOD-025-2 compliance on a NERC Regional basis, which is not permissible under the Standard. That failure to verify that the entity’s testing strategy was valid is a the root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with MOD-025-2 R2 and ended on October 30, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized by a number of factors. First, the entity completed the testing less than one month late on July 29, 2016. It should also be noted that when the entity completed the overdue testing, no changes were required to show compliance with MOD-025. Second, entity personnel have historically been performing real and reactive power capability testing that match the requirements in MOD-025. (Entity personnel adhere to PJM Manual 14 D Rev 40 1/1/17 Attachment E. 2 -E3 Requirements and PJM Manual 21 Rev 12 1/1/17 Section 2.1-2.3 and Appendix A where reactive testing for these units is performed every 66 months and where the net real power capability is performed annually. In this market, real and reactive power testing have been regularly verified, reported, communicated and approved by PJM's Transmission Planner to validate generator capability.) The entity has also been sharing that information with PJM. Although the testing form that the entity provided to PJM following 2016 testing was incomplete, the entity still timely performed and submitted some of the testing required by MOD-025 before the July 1, 2016 implementation date. The entity also provided PJM with all of the information that PJM required to validate the entity’s net capability which further reduces the risk. Lastly, the entity only contributes approximately 50 MW to the grid and operated at approximately a 93% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed the required real and reactive capability testing on the entity Generating unit. The entity forwarded the test results to FirstEnergy for submission to PJM; 2) completed the resubmittal of the MOD-025 Attachment 2 data on the appropriate form for the entity and submitted it to PJM; and 3) developed and implemented a process for internal review of test data by NRG Energy, Inc.’s Regulatory Compliance team prior to submittal to PJM to ensure all required data has been collected. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC2017018623 | PRC-019-2 | R1 | On November 1, 2017, Morgantown submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. The PRC-019 implementation plan required 40% of the entity’s applicable units to have performed analyses to verify voltage regulating controls and system protection coordination by July 1, 2016. The entity did not complete the required analysis of 40% of the entity’s applicable units until November 30, 2016. The entity has one unit. NRG Maintenance Services, LLC, a subsidiary of NRG, operates and maintains the entity plant under an Operation & Maintenance (O&M) Agreement. In preparing for the July 1, 2016 compliance date for PRC-019, NRG, on behalf of its wholly owned and O&M managed Registered Entities determined that it would demonstrate compliance with MOD-025 by NERC Region rather than by individual Registered Entity. That decision resulted in NRG attempting to achieve compliance with PRC-019-2 by achieving compliance for 40% of its Registered Entities registered in the ReliabilityFirst footprint by the July 1, 2016 implementation date. This is not permissible under the implementation plan. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the entity was unaware of the exact PRC-019-2 testing and coordination requirements. Verification is involved because the entity did not verify that it was able to achieve PRC-019-2 compliance on a Regional basis, which is not permissible under the Standard. That failure to verify that the entity’s testing strategy was valid is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-019-2 R1 and ended on November 30, 2016, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control, which can result in a generator falsely tripping. The risk is minimized because the entity identified no deficiencies in the coordination of relay settings and the entity did not need to make any adjustments in the relays to achieve proper coordination. The entity also only performed the required coordination less than five months late. Lastly, the entity only contributes approximately 50 MW to the grid and operated at approximately a 93% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) adjusted NRG Energy, Inc.’s fleet-wide implementation plan to perform targeted analyses of applicable NRG Energy, Inc. units by NERC registration, including the O&M managed facilities, to meet the 2007-09 Generator Verification Implementation Plan for PRC-019 R1; and 2) completed the required analysis of the entity facility using the revised NRG Energy, Inc. implementation plan to meet the phased in implementation requirements per PRC-019-2 R1. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC2017018624 | PRC-024-2 | R1 | On November 1, 2017, Morgantown submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. The PRC-024 implementation plan required 40% of the entity’s applicable units to have verified that the generator frequency and generator voltage protective relaying settings do not trip the applicable unit within the "no trip zone" of PRC-024 Attachments 1 and 2 by July 1, 2016. The entity did not complete the required analysis of 40% of the entity’s applicable units until June 30, 2017 following PRC-024 related relay replacement and setting changes during the plant's 2017 Spring Outage. The entity has one unit. NRG Maintenance Services, LLC, a subsidiary of NRG, operates and maintains the entity plant under an Operation & Maintenance (O&M) Agreement. In preparing for the July 1, 2016 compliance date for PRC-024, NRG, on behalf of its wholly owned and O&M managed Registered Entities, attempted to demonstrate compliance with PRC-024 by NERC Region rather than by individual Registered Entity. That decision resulted in NRG attempting to achieve compliance with PRC-024 by achieving compliance for 40% of its Registered Entities registered in the ReliabilityFirst footprint by the July 1, 2016 implementation date. This is not permissible under the implementation plan. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the entity was unaware of the exact PRC-024-2 verification and coordination requirements. Verification is involved because the entity did not verify that it was able to achieve PRC-024-2 compliance on a Regional basis, which is not permissible under the Standard. That failure to verify that the entity’s testing strategy was valid is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R1 and ended on June 30, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because when the entity performed its PRC-024-2 evaluation in June 2017, no changes were required to bring the unit into compliance. Lastly, the entity only contributes approximately 50 MW to the grid and operated at approximately a 93% capacity factor during the noncompliance. (Although incorrect, NRG used its Region-wide methodology for PRC-024 compliance and achieved an Eastern Interconnection compliance level of 44% as of July 1, 2016, which reduces overall risk.) No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) adjusted NRG Energy, Inc.’s fleet-wide implementation plan to perform targeted analyses of applicable NRG Energy, Inc. units by NERC registration, including the O&M managed facilities, to meet the 2007-09 Generator Verification Implementation Plan for PRC-024 R1 & R2; and 2) completed the required analysis and related relay replacement and setting changes for the Morgantown facility using the revised NRG Energy, Inc. implementation plan to meet the phased in implementation requirements per PRC-024-2 R1&2. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC2017018625 | PRC-024-2 | R2 | On November 1, 2017, Morgantown submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. The PRC-024 implementation plan required 40% of the entity’s applicable units to have verified that the generator frequency and generator voltage protective relaying settings do not trip the applicable unit within the "no trip zone" of PRC-024 Attachments 1 and 2 by July 1, 2016. The entity did not complete the required analysis of 40% of the entity’s applicable units until June 30, 2017 following PRC-024 related relay replacement and setting changes during the plant's 2017 Spring Outage. The entity has one unit. NRG Maintenance Services, LLC, a subsidiary of NRG, operates and maintains the entity plant under an Operation & Maintenance (O&M) Agreement. In preparing for the July 1, 2016 compliance date for PRC-024, NRG, on behalf of its wholly owned and O&M managed Registered Entities incorrectly made the decision to demonstrate compliance with PRC-024 by NERC Region rather than by individual Registered Entity. That decision resulted in NRG attempting to achieve compliance with PRC-024 by achieving compliance for 40% of its Registered Entities registered in the ReliabilityFirst footprint by the July 1, 2016 implementation date. This is not permissible under the implementation plan. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the entity was unaware of the exact PRC-024-2 verification and coordination requirements. Verification is involved because the entity did not verify that it was able to achieve PRC-024-2 compliance on a Regional basis, which is not permissible under the Standard. That failure to verify that the entity’s testing strategy was valid is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R2 and ended on June 30, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. Here, when the entity performed its PRC-024-2 evaluation in June 2017, no changes were required to bring the unit into compliance. Lastly, the entity only contributes approximately 50 MW to the grid and operated at approximately a 93% capacity factor during the noncompliance. (Although incorrect, NRG used its Region-wide methodology for PRC-024 compliance and achieved an Eastern Interconnection compliance level of 44% as of July 1, 2016, which reduces overall risk.) No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) adjusted NRG Energy, Inc.’s fleet-wide implementation plan to perform targeted analyses of applicable NRG Energy, Inc. units by NERC registration, including the O&M managed facilities, to meet the 2007-09 Generator Verification Implementation Plan for PRC-024 R1 & R2; and 2) completed the required analysis and related relay replacement and setting changes for the entity facility using the revised NRG Energy, Inc. implementation plan to meet the phased in implementation requirements per PRC-024-2 R1&2. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | PSEG Fossil LLC (PSEG-Fossil) | NCR00893 | RFC2018020406 | VAR-002-4.1 | R1 | On August 1, 2018, the entity submitted a self-log stating that, as a Generator Operator, it was in noncompliance with VAR-002-4.1 R1. On the morning of July 9, 2018, a portion of the entity’s Bergen Station Unit 1 combined-cycle (CC) unit was inadvertently operated for less than one hour with two of four of its generators’ Automatic Voltage Regulators (AVRs) in manual control mode after release of the unit for dispatch to the Balancing Authority (PJM). The entity's Bergen Station Unit 1 has four Combustion Turbine Generators (CTGs). During the course of initial 1X1 startup of the unit’s Steam Turbine Generator (STG) and CTG module 1301 on July 9, 2018, at approximately 06:35hrs, the Bergen Unit 1 Operator issued a command from the STG unit’s T3000 turbine control system to its (separate) E3000 exciter control system to cause switching of the STG’s two generators’ AVRs from manual to automatic control mode. The command failed and the AVRs consequently remained in manual. The command failure was not noticed by Operators at this time as the AVR control output display on the T3000 operator screen indicated the AVRs were in automatic. The control room log indicates that at 06:46hrs the Operator notified the Station’s energy trader and PJM interface – PSEG Energy Resources and Trade LLC’s Generation Desk Operators (ER&T Gen Desk) - that the AVRs had been switched to Auto. Shift turnover occurred at 07:00hrs. The new shift immediately began (PJM-scheduled) startup of a second CT module – 1401. Bergen 1 was released, in 2X1 configuration, to PJM - through ER&T Gen Desk - for dispatch at 08:00hrs. While investigating an unrelated item at approximately 08:40hrs the Operators discovered that although the operator display on the T3000 showed that the STG AVRs were in automatic, the feedback behind the scenes (on the T3000 from the E3000) was indicating that the AVRs were in manual. Operators verified locally on the E3000 excitation system that the AVRs were in fact in manual despite the T3000 display indicating automatic. Operators immediately notified ER&T Gen Desk of the discovery of the AVRs being in manual and attempted correction of the control mode to automatic. Operators successfully corrected and verified AVR control mode to automatic, and notified ER&T Desk thereof, by 08:59hrs. The AVRs remained in automatic thereafter for the duration of the unit run (i.e. no Operator commands issued to change AVR control mode). Station investigated the relevant T3000 to E3000 command signaling (Profibus) configured by Siemens and observed that the specific T3000 to E3000 command signal duration for the AVR control mode change was different (shorter) than that of other similar-type commands. Station indicated that, due to delays from T3000 to E3000 signaling followed by E3000 execution of the T3000 command, then return feedback signaling from the E3000 to the T3000, there is a lag time in the reporting on AVR control mode status on the Bergen Unit 1 Operator’s T3000 display between issuing an AVR operating mode change command on the T3000 (to the E3000) and feedback from the E3000 to the T3000 display to indicate that the command has been successfully executed. It was noted that the startup procedure did not include explicit direction to the Operator to wait out the above-noted lag and verify that the AVR control mode change command had successfully executed (i.e. wait and confirm that the AVRs were displayed as being in Auto on the T3000 system before moving on to other startup activities). Station noted that there is an alarm annunciated to the Bergen Unit 1 Operator if one or more of its STG AVRs, once placed in automatic control mode by the Operator, switches back into manual for some reason other than an Operator command to do so. However, at the time of the July 9, 2018 incident, there was no alarm if an AVR operating mode change command was generated from the T3000 to the E3000, but was not executed by the E3000 (i.e. failed) and the AVR remained in manual – the incident central to the this incident. This noncompliance involves the management practices of reliability quality management, grid operations, and verification as the startup procedure did not include explicit direction to the Operator to wait out the above-noted lag and verify that the AVR control mode change command had successfully executed. That ineffective procedure is a root cause of this noncompliance. This noncompliance began on July 9, 2018 when the entity had two of its CTGs begin operating in Manual control mode with the AVR off and failed to notify PJM, and ended on July 9, 2019, when the entity began operating the two CTGs with AVR enabled again. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk to the BPS from this incident would have been inaction of Bergen Unit 1 STG AVRs while in manual control mode during the incident to automatically modify VAR output of the STG generators in support of maintaining BES 138 kV voltage at Bergen’s interconnection point in the event of a voltage disturbance/event on the Bulk Electric System (BES) at Bergen’s interconnection point. The risk is minimized because AVRs of the unit’s two CTGs in service at the time – the unit was in a 2X1 configuration - were in automatic mode and would have responded in case of a voltage disturbance/event. There was no actual impact to the BES as there was no voltage disturbance/event on the BES at Bergen’s interconnection point during the event. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) modified inter-systems signaling between Bergen Unit 1 STG T3000 and E3000 control systems; 2) modified Bergen Unit 1 startup procedure to include explicit lag wait out and AVR control mode status change verification; 3) modified alarm - Additional control system alarming for detection of re-occurrence of relevant ICS inter-systems signaling failure; and 4) reviewed and, if/as necessary, corrected extent of condition across the entity’s generation fleet – Bergen Unit 1 CTG modules (4) and Keys Energy Center (KEC) unit CC modules (STG and 2 CTGs).
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Seward Generation, LLC (Seward) | NCR11615 | RFC2017018499 | MOD-025-2 | R1 | On October 17, 2017, Seward submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. The entity, which has only one unit, was not compliant with MOD-025-2 R1 by the July 1, 2016 implementation date because (a) the entity’s real power testing was not valid; and (b) all required testing data was not submitted to its Transmission Planner per MOD-025 Attachment 2. (In preparing for the July 1, 2016 compliance date for MOD-025-2, NRG, on behalf of its wholly owned and managed Registered Entities, attempted to demonstrate compliance with MOD-025 by NERC Region rather than by individual Registered Entity. That decision resulted in NRG achieving compliance for 40% of all its Registered Entities registered in the ReliabilityFirst footprint by the July 1, 2016 implementation date. The entity was meant to be part of the 40% for which NRG completed testing by July 1, 2016.) NRG Maintenance Services, LLC, a subsidiary of NRG, operates and maintains the entity plant under an Operation & Maintenance (O&M) Agreement dated February 2, 2016. In anticipation of the initial compliance enforcement date of July 1, 2016, NRG, on behalf of the entity, completed real and reactive power testing on July 15, 2015 and August 25, 2015 respectively, in accordance with PJM market rules. However, following lessons learned from a ReliabilityFirst audit at another NRG subsidiary, NRG began a comprehensive fleet-wide review of all of its subsidiaries’ testing data. That review revealed the following deficiencies of the MOD-025 testing conducted at the entity: a. The entity conducted testing for net Real Power Capability on July 15, 2015 at “Emergency Max” conditions instead of “Eco Max” which allowed the entity to conduct testing without utilizing auxiliary load. This was not consistent with testing criteria under MOD-025 Attachment 1. b. The entity conducted Net Real Power Capability Testing using operational data, instead of being “staged” or prescheduled as required for the initial verification under MOD-025. Additionally, NRG determined that the data required by the Transmission Planner using the PJM market protocols and the test forms that were submitted to PJM did not match, or were not equivalent to MOD-025 Attachment 2. The forms that the entity submitted were very similar to, but not as inclusive as, MOD-025 Attachment 2, which required more data. On March 10, 2017, the entity resubmitted the MOD-025 required data using MOD-025 Attachment 2 in accordance with PJM Compliance Bulletin 23, the purpose of which was to document the process for Transmission Owners and Generator Owners to submit data to PJM as the Transmission Planner in accordance with MOD-025-2. Therefore, the entity’s real power testing was not valid and all required testing data was not submitted to PJM per MOD-025 Attachment 2. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the entity was unaware of the exact MOD-025-2 testing and coordination requirements. Verification is involved because the entity did not verify that it correctly completed MOD-025 testing. That lack of awareness of the MOD-025-2 testing and coordination requirements and that failure to verify are both root causes of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with MOD-025-2 R1 and ended on October 6, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because entity personnel have historically been performing real and reactive power capability testing that meet many of the requirements in MOD-025. (Entity personnel adhere to PJM Manual 14 D Rev 40 1/1/17 Attachment E. 2 -E3 Requirements and PJM Manual 21 Rev 12 1/1/17 Section 2.1-2.3 and Appendix A where reactive testing for these units is performed every 66 months and where the net real power capability is performed annually. In this market, real and reactive power testing have been regularly verified, reported, communicated and approved by PJM's Transmission Planner to validate generator capability.) The entity has also been sharing that information with PJM. Although the testing form that the entity provided to PJM following 2015 testing was incomplete, the entity still timely performed and submitted some of the testing required by MOD-025 before the July 1, 2016 implementation date. The entity also provided PJM with all of the information that PJM required to validate the entity’s net capability, which further reduces the risk. When the entity performed the overdue testing, the results affirmed that the entity can operate at the D-curve limits and no changes were required. Lastly, the entity contributes approximately 591 MW to the grid and operated at approximately a 57% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) retested the net real power capability testing on the entity unit. The results affirmed that the entity can operate at the D-curve limits and no changes were required. The entity forwarded the test results to Boston Energy Trading and Marketing LLC (BETM ) (the scheduling coordinator) for submission to PJM; 2) completed the resubmittal of the reactive testing data on the MOD-025 Attachment 2 data on the appropriate form for the entity and submitted to PJM (via BETM) in accordance with PJM Compliance Bulletin CB023 NERC Standard MOD-025-2 - Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability; and 3) developed and implemented a process for internal review of test data by NRG’s Regulatory Compliance team prior to submittal to PJM to ensure all required data has been collected. Completion of these Mitigating Activities will help ensure the entity takes a consistent approach to testing and submitting correct real and reactive power capability data to PJM in accordance with MOD-025 Requirements 1 and 2. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Seward Generation, LLC (Seward) | NCR11615 | RFC2017018541 | MOD-025-2 | R2 | On October 18, 2017, the entity submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. The entity, which has only one unit, was not compliant with MOD-025-2 R2 by the July 1, 2016 implementation date because (a) the entity’s real power testing was not valid; and (b) all required testing data was not submitted to its Transmission Planner per MOD-025 Attachment 2. (In preparing for the July 1, 2016 compliance date for MOD-025-2, NRG, on behalf of its wholly owned and managed Registered Entities, attempted to demonstrate compliance with MOD-025 by NERC Region rather than by individual Registered Entity. That decision resulted in NRG achieving compliance for 40% of all its Registered Entities registered in the ReliabilityFirst footprint by the July 1, 2016 implementation date. The entity was meant to be part of the 40% for which NRG completed testing by July 1, 2016.) NRG Maintenance Services, LLC, a subsidiary of NRG, operates and maintains the entity plant under an Operation & Maintenance (O&M) Agreement dated February 2, 2016. In anticipation of the initial compliance enforcement date of July 1, 2016, NRG, on behalf of the entity, completed real and reactive power testing on July 15, 2015 and August 25, 2015 respectively, in accordance with PJM market rules. However, following lessons learned from a ReliabilityFirst audit at another NRG subsidiary, NRG began a comprehensive fleet-wide review of all of its subsidiaries’ testing data. That review revealed the following deficiencies of the MOD-025 testing conducted at the entity: a. The entity conducted testing for net Real Power Capability on July 15, 2015 at “Emergency Max” conditions instead of “Eco Max” which allowed the entity to conduct testing without utilizing auxiliary load. This was not consistent with testing criteria under MOD-025 Attachment 1. b. The entity conducted Net Real Power Capability Testing using operational data, instead of being “staged” or prescheduled as required for the initial verification under MOD-025. Additionally, NRG determined that the data required by the Transmission Planner using the PJM market protocols and the test forms that were submitted to PJM did not match, or were not equivalent to MOD-025 Attachment 2. The forms that the entity submitted were very similar to, but not as inclusive as, MOD-025 Attachment 2, which required more data. On March 10, 2017, the entity resubmitted the MOD-025 required data using MOD-025 Attachment 2 in accordance with PJM Compliance Bulletin 23, the purpose of which was to document the process for Transmission Owners and Generator Owners to submit data to PJM as the Transmission Planner in accordance with MOD-025-2. Therefore, the entity’s real power testing was not valid and all required testing data was not submitted to PJM per MOD-025 Attachment 2. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the entity was unaware of the exact MOD-025-2 testing and coordination requirements. Verification is involved because the entity did not verify that it correctly completed MOD-025 testing. That lack of awareness of the MOD-025-2 testing and coordination requirements and that failure to verify are both root causes of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with MOD-025-2 R2 and ended on October 6, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because entity personnel have historically been performing real and reactive power capability testing that meet many of the requirements in MOD-025. (Entity personnel adhere to PJM Manual 14 D Rev 40 1/1/17 Attachment E. 2 -E3 Requirements and PJM Manual 21 Rev 12 1/1/17 Section 2.1-2.3 and Appendix A where reactive testing for these units is performed every 66 months and where the net real power capability is performed annually. In this market, real and reactive power testing have been regularly verified, reported, communicated and approved by PJM's Transmission Planner to validate generator capability.) The entity has also been sharing that information with PJM. Although the testing form that the entity provided to PJM following 2015 testing was incomplete, the entity still timely performed and submitted some of the testing required by MOD-025 before the July 1, 2016 implementation date. The entity also provided PJM with all of the information that PJM required to validate the entity’s net capability, which further reduces the risk. When the entity performed the overdue testing, the results affirmed that the entity can operate at the D-curve limits and no changes were required. Lastly, the entity contributes approximately 591 MW to the grid and operated at approximately a 57% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) retested the net real power capability testing on the entity unit. The results affirmed that the entity can operate at the D-curve limits and no changes were required. The entity forwarded the test results to Boston Energy Trading and Marketing LLC (BETM ) (the scheduling coordinator) for submission to PJM; 2) completed the resubmittal of the reactive testing data on the MOD-025 Attachment 2 data on the appropriate form for the entity and submitted to PJM (via BETM) in accordance with PJM Compliance Bulletin CB023 NERC Standard MOD-025-2 - Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability; and 3) developed and implemented a process for internal review of test data by NRG’s Regulatory Compliance team prior to submittal to PJM to ensure all required data has been collected. Completion of these Mitigating Activities will help ensure the entity takes a consistent approach to testing and submitting correct real and reactive power capability data to PJM in accordance with MOD-025 Requirements 1 and 2. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | UGI Utilities, Inc. (UGI) | NCR00935 | RFC2018019911 | PRC-006-2 | R9 | On June 13, 2018, UGI submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it was in noncompliance with PRC-006-2 R9. The entity did not meet the specified amount of automatic tripping of load in accordance with its Planning Coordinator’s underfrequency load shedding (UFLS) implementation schedule. During a substation expansion, the entity replaced several distribution circuit breakers. When specifying settings for the new relays, the entity did not include the under-frequency relay setting in the standard protection scheme. As a result, on September 11, 2017, the entity did not include the 59.3 Hz automatic under-frequency setting when the entity commissioned the circuit breaker. The entity identified the incorrect relay setting on April 30, 2018 and communicated this incorrect setting to the relay department. On May 2, 2018, the entity added the under-frequency setting (81) to the relay. The entity also verified and tested the setting. This noncompliance involves the management practices of asset and configuration management and verification. Asset and configuration management is involved because the entity did not include the 59.3 Hz automatic under-frequency setting when the entity commissioned the circuit breaker. Verification is involved because the entity did not have an effective verification control in place to ensure that it included the 59.3 Hz automatic under-frequency setting when the entity commissioned the circuit breaker. That lack of an effective verification control is a root cause of this noncompliance. This noncompliance started on September 11, 2017, when the entity did not include the under-frequency relay setting in the standard protection scheme when it commissioned a new circuit breaker and ended on May 2, 2018, when the entity added the under-frequency setting to the relay and verified and tested the setting. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that having an incorrect setting in place could make it more difficult for the entity to assist in helping to arrest declining frequency, assist recovery of frequency following underfrequency events, and provide last resort system preservation measures. The risk is minimized because, in the event where the system frequency decays to 59.3 Hz, the entity would still shed 18 MW out of the required 19 MW (10% of 190 MW) according to the Planning Coordinator’s automatic tripping of Load UFLS schedule during this noncompliance. The Planning Coordinator’s automatic tripping of Load UFLS schedule has a total aggregate load shed of 13,991 MW. At 18 MW, the entity's contribution to the total aggregate load would only be 0.1287%. The risk is further minimized because this noncompliance only reduced the entity’s load shed contribution by 0.0073% of the aggregate load shed required. Lastly, once the entity discovered this noncompliance, the entity quickly corrected it in less than three days, which indicates strong corrective controls. (ReliabilityFirst notes that during the noncompliance, there were no automatic load shed events.) No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity added the under-frequency setting (81U) to the relay and verified and tested the setting. To ensure that future relay replacements meet all compliance requirements, the entity took the following actions: 1) physically labeled all PRC relays; 2) highlighted all relays with 81U enabled settings in the Relay Data Book; 3) created a new procedure to ensure a review of historical relay settings is completed prior to an applicable relay being replaced; and 4) now holds bi-weekly Construction and Compliance meetings where representatives from each Operational Department provide an update to Compliance relative to existing and planned projects. ReliabilityFirst has verified the completion of all mitigation activity.
2018-10-31 | Texas Reliability Entity (Texas RE) | Anacacho Wind Farm, LLC (ANA) | NCR11265 | TRE2018019272 | MOD-025-2 | R2 | On February 26, 2018, E.ON Climate & Renewables, N.A., LLC (E.ON) submitted a Self-Report through an existing multi-region registered entity agreement under ANA stating that 16 of its individually-registered Generator Owner (GO) wind farms were in potential noncompliance with MOD-025-2 R2.2. Subsequently, E.ON provided a revised Self-Report document to clarify that the potential noncompliance pertained to 14 of its wind farms. According to E.ON, the identified GOs did not provide completed MOD-025-2, Attachment 2 forms or equivalent information to their Transmission Planners (TPs) within 90 calendar days of recording a Reactive Power capability verification. Following the submission of the Self-Report documents, Texas RE reviewed additional evidence regarding the timing of E.ON's submissions. Texas RE determined that there was no instance of noncompliance with MOD-025-2 R2.2, but one GO, ANA, was in noncompliance with MOD-025-2 R2.1. ANA previously completed a Reactive Power capability verification, consistent with MOD-025-2 R1, Attachment 1, on December 25, 2012. Therefore, ANA was compliant with MOD-025-2 R2 when the Standard became enforceable on July 1, 2016. Consistent with the five-year periodicity requirement specified in MOD-025-2, Attachment 1, ANA was required to complete its next Reactive Power verification within five years, or by December 25, 2017. ANA timely completed its leading Reactive Power at maximum Real Power capability; but, due to grid conditions at the time of the test ANA was unable to complete the lagging Reactive Power at maximum Real Power capability. For the remaining 13 GOs, E.ON provided documentation to demonstrate that the GOs all completed the required Reactive Power verification in accordance with MOD-025-2 R2 before July 1, 2016, and provided the verification to the relevant TPs prior to the July 1, 2016, enforcement date. Subsequently, two of the GOs then timely met the five-year periodicity requirement specified in MOD-025, Attachment 1 for Reactive Power verification, and the verification was provided to the TPs within 90 calendar days as required by MOD-025-2 R2.2. The root cause of the noncompliance was that ANA lacked a sufficient process to ensure timely compliance with all applicable requirements MOD-025-2. Specifically, ANA’s process did not adequately account for timely completing verifications following an unsuccessful verification attempt. In this instance, when ANA attempted to complete its Reactive Power verification, high voltage conditions on the grid prevented ANA from completing the lagging Reactive Power capability verification. ANA lacked a process to ensure that re-testing was expeditiously re-scheduled. This noncompliance started on December 26, 2017, five years and one day following ANA’s previous Reactive Power verification. The noncompliance ended on June 11, 2018, when ANA provided its completed Reactive Power verification to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following. First, ANA previously provided Reactive Power verifications under substantially similar region-specific output conditions in 2012, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, ANA’s single generation Facility has a nameplate capacity of 99.8 MW and operated at approximately a 42% capacity factor during the period from approximately December 25, 2017 to June 11, 2018. As a result, any errors in the Facility’s Reactive Power output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered ANA’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, ANA: 1) performed the required Reactive Power verification; 2) provided the Reactive Power verification to its TP; 3) adopted a documented process for compliance with MOD-025-2; and 4) implemented a MOD-025 dashboard within a new compliance management tool to: a) create and schedule tasks to timely address instances when an attempted verification must be rescheduled; and b) send automatic reminders to personnel six months, three months, and two weeks prior to upcoming MOD-025-2 compliance deadlines. Texas RE has verified the completion of all mitigation activity.
2018-10-31 | Texas Reliability Entity (Texas RE) | Bastrop Energy Partners, LP (BEP) | NCR04012 | TRE2018019919 | MOD-025-2 | R1 | On June 22, 2018, BEP submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, BEP did not verify the Real Power capability of its applicable generating units in accordance with MOD-025-2, Attachment 1 by July 1, 2016. On January 1, 2018, BEP engaged a contractor to conduct a NERC Standard gap analysis for its facility. On June 5, 2018, the contractor provided its final report to BEP, identifying a possible noncompliance with MOD-025-2. Specifically, although BEP conducted its Real Power verification for its single facility on June 27, 2017, it failed to complete the verification prior to the July 1, 2016 deadline. Additionally, the gap analysis report identified that BEP failed to provide the verification to its Transmission Planner (TP) as required by MOD-025-2 R1. Subsequently, on June 18, 2018, BEP provided the verification data to its TP. The root cause of this noncompliance was that BEP misinterpreted the compliance date specified in the MOD-025-2 implementation plan. In particular, BEP mistakenly believed that compliance with MOD-025-2 was not required until July 1, 2017. This noncompliance started on July 1, 2016, when MOD-025-2 became enforceable, and ended on June 18, 2018, when BEP provided the required Real Power verifications to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS) for the following reasons. First, BEP previously provided Real Power and Reactive Power verifications under substantially similar region-specific output conditions within five years of performing its MOD-025-2 Real Power capability verification, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, BEP provided similar Real Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. No harm is known to have occurred. Texas RE considered BEP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, BEP: 1) completed the required Real Power verification in accordance with MOD-025-2; 2) provided the verification data to its TP; 3) created automatic reminders to notify BEP personnel one year prior to the next MOD-025-2 deadline; and 4) engaged a third-party compliance contractor to conduct quarterly reviews, monitor new or revised NERC Reliability Standards; and conduct quarterly trainings regarding compliance with NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2018-10-31 | Texas Reliability Entity (Texas RE) | Bastrop Energy Partners, LP (BEP) | NCR04012 | TRE2018019920 | MOD-025-2 | R2 | On June 22, 2018, BEP submitted a Self-Report stating that, as a Generator Owner (GO), it had a possible noncompliance with MOD-025-2 R2. In particular, BEP did not verify the Reactive Power capability of its applicable generating units in accordance with MOD-025-2, Attachment 1 by July 1, 2016. On January 1, 2018, BEP engaged a contractor to conduct a NERC Standard gap analysis for its facility. On June 5, 2018, the contractor provided its final report to BEP, identifying a possible noncompliance with MOD-025-2. Specifically, although BEP conducted its Reactive Power verification for its single facility on June 27, 2017, it failed to complete the verification prior to the Juy 1, 2016 deadline. Additionally, the gap analysis report identified that BEP failed to provide the verification to its Transmission Planner (TP) as required by MOD-025-2 R2. Subsequently, on June 18, 2018, BEP provided the verification data to its TP. The root cause of this noncompliance was that BEP misinterpreted the compliance date specified in the MOD-025-2 implementation plan. In particular, BEP mistakenly believed that compliance with MOD-025-2 was not required until July 1, 2017. This noncompliance started on July 1, 2016, when MOD-025-2 became enforceable, and ended on June 18, 2018, when BEP provided the required Reactive Power verifications to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS) for the following reasons. First, BEP previously provided Real Power and Reactive Power verifications under substantially similar region-specific output conditions within five years of performing its MOD-025-2 Reactive Power capability verification, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, BEP provided similar Reactive Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. No harm is known to have occurred. Texas RE considered BEP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, BEP: 1) completed the required Reactive Power verification in accordance with MOD-025-2; 2) provided the verification data to its TP; 3) created automatic reminders to notify BEP personnel one year prior to the next MOD-025-2 deadline; and 4) engaged a a third-party compliance contractor to conduct quarterly reviews, monitor for new or revised NERC Reliability Standards; and conduct quarterly trainings regarding compliance with NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2018-10-31 | Texas Reliability Entity (Texas RE) | Calpine Corporation (CPN) | NCR00006 | TRE2017018204 | VAR-002-4 | R3 | During a Compliance Audit conducted per an existing multi-region registered entity agreement from July 19, 2017 through August 17, 2017, Texas RE determined that CPN, as a Generator Operator (GOP), was in noncompliance with VAR-002-4 Requirement 3 for a facility in the WECC region. Specifically, CPN failed to notify its Transmission Operator (TOP) within 30 minutes of the PSS status change. On May 9, 2017, facility personnel determined that, for three of the four combustion turbine-generators, each unit’s PSS status point in the data historian routinely toggled from “on” to “off” whenever each unit’s generator breaker “closed” or “opened.” However, for Unit 2, the “on/off” status point did not change state when the Unit 2 breaker opened, and instead indicated “on” status at all times. Further investigation discovered that a fuse holder for the 24 volt power supply circuit to the Unit 2 PSS located in a normally-closed cabinet was positioned to break the circuit (open position), and that the Unit 2 PSS was without power. Because of this issue, CPN failed to notify its TOP within 30 minutes of the PSS status change. The root cause of this non-compliance was due to the entity being unaware that their PSS was not in service. A software/logic flaw showed that the PSS state for one generating unit at the plant to be in service when it wasn’t. There is an alarm in place intended to notify operators when the PSS is not in service when the generator breaker is closed. However, in this instance, the PSS state was shown to be in service when it was off-line. This resulted in the operators being unaware that the PSS was off-line. The noncompliance began on September 28, 2016 when CPN failed to notify its TOP of a status change within 30 minutes of the change. The noncompliance ended on May 15, 2017, when CPN notified its TOP of the status of the PSS when it was back in service and fully operational. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance of non-compliance, CPN failed to notify its Transmission Operator within 30 minutes of a PSS status change of the Unit 2 combustion turbine generator. CPN owns and operates a 71.2 MVA generating unit that is part of a 433 MVA generating facility that was subject to this instance. There was no expected loss of generation for a failure to report the status of the PSS for one generating unit. In addition, this particular plant is located in a highly networked area, is a medium sized generating facility, and was only online for 9% of operating hours in Q2 2017. The audit team also noted that the facility maintained the voltage schedule provided to them by their TOP during the time period that the PSS was not in service. CPN implemented good detective controls to detect the above non-compliance issue. Specifically, CPN had implemented an alarm that would go off if the PSS for a generator was out of service when the generator breaker was closed. However, in this instance, the control failed due to a software flaw which forced the PSS of one generating unit to incorrectly indicate that it was in service at all times. Based on the controls analyzed, the probability that this instance of non-compliance would cause an impact to the reliability of the BES has been identified to be low. No harm is known to have occurred. | To mitigate this noncompliance, CPN: 1) engaged an outside controls firm to provide technical assistance in the formal investigation to troubleshoot the issue; 2) corrected the ladder logic in Unit 2 to match the logic in the other 3 combustion turbine units. This was done by removing a set of unused contacts on the Unit 2 ladder logic; 3) added the healthy/unhealthy PSS status indication to operator displays. It has also added alarms that will annunciate when the power supply to the PSS is unavailable and the generator breaker is closed; and 4) notified its TOP of the status of the PSS when it was back in service and fully operational.
2018-10-31 | Texas Reliability Entity (Texas RE) | Calpine Corporation (CPN) | NCR00006 | TRE2017018217 | VAR-501-WECC-2 | R1 | During a Compliance Audit conducted per an existing multi-region registered entity agreement from July 19, 2017 through August 17, 2017, Texas RE determined that CPN, as a Generator Operator (GOP), was in noncompliance with VAR-501-WECC-2 Requirement 1 for a facility in the WECC region. Specifically, CPN failed to have the PSS in service 98% of all operating hours during quarter 2 of 2017 for one of its generating units. On May 9, 2017, facility personnel determined that, for three of the four combustion turbine-generators, each unit’s PSS status point in the data historian routinely toggled from “on” to “off” whenever each unit’s generator breaker “closed” or “opened.” However, for Unit 2, the “on/off” status point did not change state when the Unit 2 breaker opened, and instead indicated “on” status at all times. Further investigation discovered that a fuse holder for the 24 volt power supply circuit to the Unit 2 PSS located in a normally-closed cabinet was positioned to break the circuit (open position), and that the Unit 2 PSS was without power. Because of this issue, CPN failed to notify its Transmission Operator (TOP) within 30 minutes of the PSS status change. The root cause of this non-compliance was due to the entity being unaware that their PSS was not in service. A software/logic flaw showed that the PSS state for one generating unit at the plant to be in service when it wasn’t. There is an alarm in place intended to notify operators when the PSS is not in service when the generator breaker is closed. However, in this instance, the PSS state was shown to be in service when it was off-line. This resulted in the operators being unaware that the PSS was off-line. The noncompliance began on May 1, 2017, when CPN failed to operate one of its generating units with the PSS in service for at least 98% of all operating hours during the second quarter of 2017. The noncompliance ended on May 15, 2017, when the PSS was put back into service. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance of non-compliance, CPN failed to have the PSS of one of its generating units in service for 98% of all operating hours during the second quarter of 2017. CPN owns and operates a 71.2 MVA generating unit that is part of a 433 MVA combined cycle facility that was subject to this instance. The operation of this generator without its PSS in service could potentially result in undamped oscillations and the unexpected loss of generation from this unit. However, this plant is located in a highly networked area, is a medium sized facility, and was only operated for approximately 9% of operating hours in Q2 2017. CPN implemented good detective controls to detect the above non-compliance issue. Specifically, CPN had implemented an alarm that would go off if the PSS for a generator was out of service when the generator breaker was closed. However, in this instance, the control failed due to a software flaw which forced the PSS of one generating unit to incorrectly indicate that it was in service at all times. Based on the controls analyzed, the probability that this instance of non-compliance would cause an impact to the reliability of the BES has been identified to be low. | To mitigate this noncompliance, CPN: 1) engaged an outside controls firm to provide technical assistance in the formal investigation to troubleshoot the issue; 2) corrected the ladder logic in Unit 2 to match the logic in the other 3 combustion turbine units. This was done by removing a set of unused contacts on the Unit 2 ladder logic; 3) added the healthy/unhealthy PSS status indication to operator displays. It has also added alarms that will annunciate when the power supply to the PSS is unavailable and the generator breaker is closed; and 4) brought the PSS back into service.
2018-10-31 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | WECC2017018061 | PRC-002-2 | R1 | On July 19, 2017, BHP submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-002-2 R1. Specifically, BHP reported that during an internal compliance review in May 2017, it discovered it had not identified the complete list of Bulk Electric System (BES) buses due to a misinterpretation of steps 6 and 7 from Attachment 1 of PRC-002-2 R1, Part 1.1. BHP incorrectly assessed that it only needed sequence of events recording (SER) and fault recording (FR) data for BES buses at one of its substations. BHP’s incorrect assumption led to an underreporting of BES buses. Since BHP did not correctly complete R1, Part 1.1 of the Standard for all required BES buses, it was not able to notify other owners of BES Elements connected to those BES buses, of which BES Elements require SER data and/or FR data, per the requirements of Part 1.2. After reviewing all relevant information, WECC determined that BHP failed to identify all the BES buses for which SER and FR data is required by using the methodology in PRC-002-2, R1, Part 1.1, Attachment 1. BHP also failed to notify other owners of BES Elements connected to those BES buses within 90-calendar days of completion of Part 1.1, of which BES Elements require SER data and/or FR data, as required by Part 1.2 of the Standard. The root cause of the issue was that BHP incorrectly completed infrequently performed steps. BHP misinterpreted the requirements for the list of BES buses required for PRC-002-2 R1, Attachment 1, steps 6 and 7. This resulted in fewer BES buses that BHP incorrectly determined would need SER and/or FR data. WECC determined that this issue began on July 1, 2016, when BHP did not follow methodology in Attachment 1 of PRC-002-2, R1 Part 1.1 to identify which BES buses require SER and FR data. WECC determined that the end date of this issue is June 20, 2017, when BHP completed the methodology outlined in Attachment 1 of the Standard to determine applicable BES buses requiring SER and FR data and notified entities who own BES elements connected to those BES buses for a total of 355 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, BHP failed to identify all the BES buses for which SER and FR data is required by using the methodology in PRC-002-2, R1, Part 1.1, Attachment 1. BHP also failed to notify other owners of BES Elements connected to those BES buses, within 90-calendar days of completion of Part 1.1, which BES Elements require SER data and/or FR data, as required by Part 1.2 of the Standard. Such failure could result in having inadequate data available to facilitate the analysis of BES Disturbances and impede the ability to implement changes that could reduce the likelihood of a similar event from occurring. This failure could lead to loss of BES elements in the future. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as negligible. However, BHP had strong detective controls. Specifically, BHP conducts an internal compliance review quarterly to ensure compliance with the Standards and detect potential issues. Based on this, WECC determined that there was a low likelihood of causing negligible harm to the BPS. No harm is known to have occurred. WECC notes that BHP does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, BHP: a. completed the analysis to identify BES buses that require SER and/or FR data, as described in PRC-002-2 Part 1.1, Attachment 1; b. notified owners of BES Elements connected to the BES buses identified in Part 1.1 of the Standard; c. conducted annual internal compliance review to ensure compliance and understanding of the requirements of the Standard; and d. created a recurring meeting event to guarantee compliance with Part 1.3 in the future.
2018-10-31 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2018020035 | COM-001-2.1 | R9 | On July 17, 2018, EWEB submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in noncompliance with COM-001-2.1 R9. Specifically, EWEB reported that during a readiness review of compliance documentation, it discovered that it did not test its Alternative Interpersonal Communication capability during the month of March 2017 as required by COM-001-2.1 R9. The technician responsible for performing the calendar month phone checks was on bereavement leave during March 2017. EWEB did not assign an internal backup personnel for its monthly phone checks, and controls were not in place to ensure all applicable Alternative Interpersonal Communications capabilities were checked each calendar month. On April 18, 2017, EWEB tested its Alternative Interpersonal Communication capability as required by the Standard. After reviewing all relevant information, WECC determined that EWEB failed to test its Alternative Interpersonal Communication capability at least once each calendar month as required by COM-001-2.1 R9. The root cause of the issue was that EWEB did not have internal controls to track that the phone testing was completed and no backup personnel was assigned for the monthly phone checks. WECC determined that this issue began on April 1, 2017, when EWEB failed to test its Alternative Interpersonal Communication capability during the calendar month of March 2017 and ended on April 18, 2017, when the entity tested its Alternative Interpersonal Communication capability for a total of 18 days. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, EWEB failed to test its Alternative Interpersonal Communication capability at least once each calendar month as required by COM-001-2.1 R9. Such failure could potentially affect the entity’s ability to communicate operating decisions needed to maintain reliability. EWEB owns and operates 100.3 miles of 115 kV transmission that is primarily used to serve the entity’s 557 MW of load that was applicable to this issue. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, as compensating controls, EWEB has other phones at the Primary Control Center (PCC), two of which were tested appropriately. EWEB also had an additional two phones at a Backup Control Center (BCC) that it could have activated. Based on this, WECC determined that there was a low likelihood of causing minor harm to the BPS. No harm is known to have occurred. WECC has determined that EWEB have no relevant compliance history related to this issue. | To remediate and mitigate this issue, EWEB: a. tested their Alternative Interpersonal Communication capability; b. wrote a procedure to use when training personnel to perform phone checks and reference as needed when performing; c. designated and trained personnel to perform monthly phone checks; and d. added a review step on the “Monthly Phone Check List” to ensure monthly phone checks are completed before each month-end.
2018-10-31 | Western Electricity Coordinating Council (WECC) | Topaz Solar Farms LLC (TSFL) | NCR11342 | WECC2017017462 | PRC-024-2 | R2 | On April 25, 2017, TSFL submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Specifically, TSFL reported that on July 15, 2016 it received a study from a third-party consultant which identified that 243 of its 689 inverters and protection relays were reviewed and set such that the generator voltage protective relaying did not trip the applicable generating unit(s), which did not meet the 40 percent of applicable Facilities to be set, per the implementation plan of PRC-024-2 R2. TSFL considered each inverter as a generating unit and the associated protective relays as the applicable Facilities. The study also recommended certain setting changes for the protective relays, per the requirements of the Standard. TSFL then conducted its own analysis of the results of the study with the TSFL equipment manager and updated the settings of the remaining 446 devices by October 19, 2016. After reviewing all relevant information, WECC determined that TSFL failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units as a result of a voltage excursion at the point of interconnection caused by an event on the transmission system external to the generating plant that remains within the "no trip zone" of PRC-024, R2 Attachment 2. Further, WECC determined that TSFL owns and operates a dispersed power resource comprised of 689 inverters, each operating as a single generating unit. Thereby the 1,550 MW solar plant should have been considered a single Facility and all protective relays should have been set by July 1, 2016. The root cause of the issue was due to insufficient time allotted for the tasks associated with performing the requirements of the Standard. Specifically, TSFL underestimated the time required to complete the study, coordinate with the third-party contractor and compile the results which led to delays in identifying the devices subject to the requirements of PRC-024-2 R2, Attachment 2. WECC determined that this issue began on July 1, 2016, and the end date of this issue was October 19, 2016, when TSFL updated the settings of the remaining 446 inverters and protective relays to meet PRC-024-2 R2, Attachment 2, for a total of 111 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, TSFL failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units as a result of a voltage excursion at the point of interconnection caused by an event on the transmission system external to the generating plant that remains within the "no trip zone" of PRC-024, R2 Attachment 2 for a single Facility. Such failure could result in a premature trip of the generating units due to voltage excursions within the “no trip zone.” The affected generation plant is a dispersed power resource, 1,550 MW, solar Facility. Only 4.8% of the inverters and protective relays were not set properly and thus only 28 MW of solar generating capacity was at risk of improperly tripping within the no-trip zone. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as negligible. However, the inverters and protective relays that were noncompliant with the voltage no-trip zone, were only noncompliant with the High-Voltage portion of the voltage no-trip zone. Based on this, WECC determined that there was a low likelihood of causing negligible harm to the BPS. No harm is known to have occurred. TSFL does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, TSFL: a. configured 446 inverter and protective relay settings with compliant settings; b. revised its interpretation and understanding of the definition of applicable Facilities in the Standard such that TSFL should be considered a single Facility, comprised of 689 inverter and protective relays; c. set internal deadlines for upcoming compliance activities such that these activities are accomplished well in advance of the regulatory compliance deadlines.
2018-09-27 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2018019521 | EOP-004-3 | R2 | On April 10, 2018, NSP, a Coordinated Oversight Program participant, submitted a self-log to MRO stating that, as a Transmission Operator, it was in noncompliance with EOP-004-3 R2. NSP, Public Service Company of Colorado (PSCO) (NCR05521), and Southwestern Public Service Company (SPS) (NCR01145) (hereafter referred to collectively as Xcel Energy) are Xcel Energy companies monitored together under the Coordinated Oversight Program. Xcel Energy stated that the noncompliance involved PSCO. Specifically, Xcel Energy failed to report a loss of Real-Time Contingency Analysis (RTCA) that lasted longer than 30 minutes within 24 hours. Xcel Energy stated that the loss occurred on October 28, 2017 and was recognized by the operator, who coordinated with its Reliability Coordinator to ensure on-going Real-Time Assessments were completed until Xcel Energy’s RTCA capabilities were restored. Per Xcel Energy, the event was properly logged in the daily operations log, but the operator did not initiate the reporting procedure. The noncompliance was discovered during a review of logs following a subsequent event that was properly reported. The cause of the noncompliance was that the operator failed to initiate the reporting procedure after a reportable event occurred and was logged. The noncompliance started on October 29, 2017, 24 hours after the reportable event occurred, and ended on January 17, 2018, when Xcel Energy reported the event. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was limited to a failure to promptly document the event with NERC; the inherent risk of the noncompliance is limited as reporting the event to NERC improves analytics, enhances trend spotting, and facilitates NERC Alerts, but does not directly support the system’s ability to recover from the event. Finally, Xcel Energy stated that the operator recognized the RTCA loss and worked with its Reliability Coordinator to maintain reliability by ensuring on-going Real-Time Assessments were completed. No harm is known to have occurred. MRO reviewed Xcel Energy's compliance history and determined there was no aggravating prior noncompliance. | To mitigate this noncompliance, Xcel Energy: 1) submitted the required EOP-004 form as well as a NERC Event Analysis report; 2) added a step to the daily log to verify if any reporting requirements were triggered; 3) created a laminated placement at the operator desks to help identify reportable events; 4) updated its Loss of Transmission Security Management procedure to include specific direction on EOP-004 reporting if RTCA is lost for more than 30 minutes; and 5) reviewed the event with operators during its annual training. The mitigating activities were limited to the PSCO system.
2018-09-27 | Northeast Power Coordinating Council, Inc. (NPCC) | Middleton Municipal Electric Department | NCR00333 | NPCC2018020127 | PRC-006-NPCC-1 | R4. | During a Compliance Spot Check conducted from May 22, 2018 to July 30, 2018, NPCC determined that Middleton Municipal Electric Department (the Entity), as a Distribution Provider Under-Frequency (DPUF), was in noncompliance with PRC-006-NPCC-1 R4. In reviewing the Entity’s Q2-2018 compliance Guided Self-Certification submittal, which was effected on May 21, 2018 for the reporting period April 1, 2017 to March 31, 2018, NPCC discovered that the Entity's 2017 UFLS Program utilized a total nominal operating time of 389 milliseconds (ms) for its single-stage load shedding, which is outside of the permissible time delay range (250ms-350ms). The total nominal operating time is the sum of the individual operating times of all components of an Entity's load shedding circuitry that operate in series in order to disconnect customer load. This noncompliance started on January 1, 2016, when the standard and requirement became enforceable, and ended on August 3, 2018, when the Entity implemented a smaller time delay setting for the main "Type 81" relay that reduced the total nominal operating time of its single-stage load shedding scheme to 258ms, a value which now falls within the permissible time delay range. The root cause of this instance of non-compliance was that the Entity's initial misunderstanding of the purpose of the main "Type 81" relay time delay setting and the inclusion of all interposing devices' operation times to achieve a total operating time for its load shedding scheme that falls within the permissible time delay range. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity is a small municipal electric utility with a registered function of Distribution Provider that serves a customer load of approximately 25MW. The Entity-owned distribution feeders interconnect to 115kV transmission facilities owned by its host Transmission Owner, National Grid USA. The Entity also owns and operates a UFLS Program that is designed to shed 12MW of load in system conditions with declining frequency. This noncompliance does not hinder the Entity's ability to actually implement load shedding. Rather, the noncompliant aspect of the Entity's UFLS Program consists of a total activation time that is 39ms slower than the maximum time delay permitted by Table 3 of the standard and requirement. Moreover, the Entity's Reliability Coordinator's (ISO-NE) required Operating Reserves (approximately 2600 MW) would adequately compensate for this instance of noncompliance during a declining frequency event. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) corrected the noncompliance by implementing a smaller time delay setting for the main "Type 81" relay that reduced the total nominal operating time of its single-stage load shedding scheme to 258ms, a value which now falls within the aforementioned permissible range. To prevent a recurrence of similar instances of noncompliance, the Entity: 1) provided compliance-related clarification to the contractor responsible for establishing and implementing time delay settings for all components of its load shedding circuitry in order to maintain compliance with the standard and requirement. NPCC has verified the completion of all mitigation activity.
2018-09-27 | Northeast Power Coordinating Council, Inc. (NPCC) | National Grid USA | NCR11171 | NPCC2018020335 | PRC-006-NPCC-1 | R11. | On September 5, 2018, National Grid USA (the Entity) submitted a self-log stating that, as a Distribution Provider (DP), it was in noncompliance with PRC-006-NPCC-1 R11. Specifically, the Entity failed to develop and submit for approval to its Planning Coordinator (PC), the ISO-NE, an implementation plan within 90 days of the request by its PC for implementation of applicable inhibit voltage thresholds settings within the Entity's UFLS Program. The PC made this request to all applicable UFLS entities, including the Entity, by posting a compliance bulletin on its website just prior to the enforcement date of the standard and requirement. On December 28, 2017, when responding to a UFLS data request from ISO-NE, the Entity discovered that fifteen underfrequency relays, located at fifteen substations in New England, used voltage inhibit settings that did not conform to the PC's required setting of 0.7 or below per unit. These relays were set to operate at voltage inhibit thresholds ranging from 0.75 per unit to 0.83 per unit. This noncompliance started on July 1, 2015, when the standard and requirement became enforceable, and ended on July 9, 2018, when the Entity, by completing the implementation of required voltage inhibit settings developed by its PC, effectively obviated the need for developing and submitting an implementation plan. The root cause of this instance of non-compliance was the Entity's initial belief that developing and submitting an implementation plan to its PC for approval was not necessary, based on an initial incorrect assessment that its UFLS program was conformant with the PC's inhibit thresholds specifications. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). An implementation plan developed by the Entity and approved by its PC, as required by the standard and requirement, is necessary to ensure that implementation of inhibit threshold requirements for UFLS Programs are correctly and timely implemented. In this particular case, however, approximately 89 MW of load shedding (less than 5% of the Entity's load shedding program) was incorrectly set to be activated at inhibit thresholds higher than the PC-recommended voltage inhibit settings of 0.7 or below per unit. In conclusion, this noncompliance does not hinder the Entity's ability to actually implement load shedding. In fact, the Entity's UFLS program is 100% compliant in terms of amount of load shedding and frequency threshold requirements. Additionally, the Entity's Reliability Coordinator's (ISO-NE) required Operating Reserves (approximately 2600 MW) would adequately compensate for this instance of noncompliance during a declining frequency event. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) by completing the implementation of required voltage inhibit settings developed by its PC, effectively obviated the need for developing and submitting an implementation plan. To prevent a recurrence of similar instances of noncompliance, the Entity's: 1) Protection Engineering management and Reliability Compliance Group held several discussions to emphasize the need for ensuring that the UFLS program continue to adhere to the PC's current inhibit thresholds specifications (0.7 or below per unit) as specified in the Entity's own Under-frequency Protection Application Guide. The Compliance Group is fully aware that future changes to inhibit thresholds will be effected via an implementation plan developed by the Entity that is subject to approval by its PC. NPCC has verified the completion of all mitigation activity.
2018-09-27 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2018019465 | PRC-019-2 | R1 | On March 23, 2018, AEP submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-019-2 R1. The entity’s Transmission Business Unit (Transmission) did not coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions per the Phased-In Implementation Plan for PRC-019. The entity system has only two synchronous condenser units, both in the ReliabilityFirst footprint. To comply with PRC-019-2 R1, the entity had to have one synchronous condenser unit addressed by 7/1/2016 and the other by 7/1/2017. During the initial internal standard review to establish Transmission's obligation and to develop implementation plans for the PRC-019 Standard, the entity team responsible for developing implementation plans did not effectively communicate with Transmission to determine if the entity had synchronous condensers in service. As a result, the entity team developing the plans mistakenly believed the entity did not have a PRC-019-2 obligation because it was unaware of the entity’s synchronous condensers. Transmission has only two synchronous condensers in-service and the two units were installed about 50 years ago. During the third quarter of 2017, entity compliance staff overseeing PRC-019 were informed of the existence of the two synchronous condensers. Once entity compliance staff became aware of the synchronous condensers by the team responsible for MOD-025-2 R3 implementation, the entity determined it had not met the Transmission Owner obligation for the PRC-019 R1 implementation plan. This noncompliance involves the management practices of asset and configuration management and verification. Asset and configuration management are involved because entity compliance staff were not aware of the existence of these two synchronous condensers. The entity also did not have a verification control in place to ensure that entity compliance staff were aware of all PRC-019 implicated equipment and that lack of a verification control is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-019-2 R1 and ended on April 19, 2018, when the entity finished evaluating and coordinating the voltage regulating system controls and the protection systems of both synchronous condensers. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is not coordinating voltage control, which can result in a generator falsely tripping. The risk is minimized because per TPL-001-4 R2.1.5, the entity has submitted its sparing strategy to PJM, the entity's Transmission Planner. As part of that sparing strategy, PJM has studied the impact of the possible unavailability of the synchronous condensers on system performance and has not identified any issues. Lastly, ReliabilityFirst notes that the synchronous condensers have performed as designed for 50 years and the synchronous condensers have been maintained via annual planned maintenance outages. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity will complete the following mitigation activities by October 24, 2018: 1) Evaluate the voltage regulating system controls and protection systems of each synchronous condenser and make the necessary changes (At the Opossum Creek synchronous condenser, testing revealed that the automatic voltage regulator (AVR) underexcitation limiter settings were -130 MVAR. These underexcitation limiter settings were subsequently adjusted to -90 MVAR. In addition, the steady state stability limit (SSSL) was calculated to be -149 MVAR. Therefore, the protection settings had to be adjusted to fall in between the limiter settings and the SSSL. New protection settings were issued on April 2. The field P&C personnel then applied these settings, and verification of the settings was completed on April 5, 2018. At the Fieldale synchronous condenser, testing revealed that automatic voltage regulator (AVR) underexcitation limiter settings were -160 MVAR. These underexcitation limiter settings were subsequently adjusted to -90 MVAR. In addition, the SSSL was calculated to be -158 MVAR. Therefore, the protection settings had to be adjusted to fall in between the limiter settings and the SSSL. New protection settings were issued on April 10. The field P&C personnel then applied these settings, and verification of the settings was completed on April 11, 2018.); 2) Establish a control in the entity’s risk and compliance system to ensure that the coordination of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions is completed within the required maximum of every five calendar years. This includes establishing a point person for PRC-019-2 compliance within Transmission Protection and Control Engineering which will help address a contributing cause of this noncompliance that was poor asset and configuration management. This person would be accountable for the standard and would become the knowledgeable subject matter expert of synchronous condensers; and 3) Update the existing MOD-025-2 control to include notifying Transmission Protection and Control Engineering when a capability verification will be conducted and that a PRC-019-2 review will be necessary within 90 days after the capability verification. Thereafter, the responsibility of oversight of MOD-025-2 R3 and PRC-019-2 would be assigned to the same Compliance Coordinator within Transmission Reliability Compliance (TRC). AEP needs until October 24, 2018 to complete this Mitigation Plan because of the large amount of time it takes AEP to establish the new control (Milestone 2) and to update the existing PRC-019-2 control (Milestone 3). The risk has already been mitigated because the necessary changes were applied to each synchronous condenser back in April of 2018.
2018-09-27 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2018019466 | PRC-019-2 | R2 | On March 23, 2018, AEP submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-019-2 R2. The entity’s Transmission Business Unit (Transmission) did not perform the coordination review and make any required changes as described in PRC-019-2 within 90 calendar days of the synchronous condenser equipment capability change. There are two synchronous condenser units within the ReliabilityFirst footprint and the entity performed the field verification of their capability, as required by MOD-025-2 R3, on May 16 and 17, 2016. The entity published the capability changes in July 2016 after PJM reviewed and confirmed the test results. The entity did not review the settings of the in-service limiters and Protection System devices after they verified capability changes to determine if PRC-019-2 was met. Therefore, the entity did not make the required setting changes. During the initial internal standard review to establish Transmission's obligation and to develop implementation plans for the PRC-019 Standard, the entity team responsible for developing implementation plans did not effectively communicate with Transmission to determine if the entity had synchronous condensers in service. As a result, the entity team developing the plans mistakenly believed the entity did not have a PRC-019-2 obligation because it was unaware of the entity’s synchronous condensers. Transmission has only two synchronous condensers in-service and the two units were installed about 50 years ago. During the third quarter of 2017, entity compliance staff overseeing PRC-019 were informed of the existence of the two synchronous condensers by the team responsible for MOD-025-2 R3 implementation. While determining all the obligations related to synchronous condensers, the entity initially discovered the PRC-019-2 R1 noncompliance and then found the coordination of the settings were not completed within 90 days of the field verification of the units' capabilities (MOD-025-2 R3) which were completed in May 2016. This noncompliance involves the management practices of asset and configuration management and verification. Asset and configuration management are involved because entity compliance staff were not aware of the existence of these two synchronous condensers. The entity also did not have a verification control in place to ensure that entity compliance staff were aware of all PRC-019 implicated equipment and that lack of a verification control is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-019-2 R2 and ended on April 19, 2018, when the entity finished evaluating and coordinating the voltage regulating system controls and the protection systems of both synchronous condensers. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is not coordinating voltage control, which can result in a generator falsely tripping. The risk is minimized because per TPL-001-4 R2.1.5, the entity has submitted its sparing strategy to PJM, the entity's Transmission Planner. As part of that sparing strategy, PJM has studied the impact of the possible unavailability of the synchronous condensers on system performance and has not identified any issues. Lastly, ReliabilityFirst notes that the synchronous condensers have performed as designed for 50 years and the synchronous condensers have been maintained via annual planned maintenance outages. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity will complete the following mitigation activities by October 24, 2018: 1) Evaluate the voltage regulating system controls and protection systems of each synchronous condenser and make the necessary changes (At the Opossum Creek synchronous condenser, testing revealed that the automatic voltage regulator (AVR) underexcitation limiter settings were -130 MVAR. These underexcitation limiter settings were subsequently adjusted to -90 MVAR. In addition, the steady state stability limit (SSSL) was calculated to be -149 MVAR. Therefore, the protection settings had to be adjusted to fall in between the limiter settings and the SSSL. New protection settings were issued on April 2. The field P&C personnel then applied these settings, and verification of the settings was completed on April 5, 2018. At the Fieldale synchronous condenser, testing revealed that automatic voltage regulator (AVR) underexcitation limiter settings were -160 MVAR. These underexcitation limiter settings were subsequently adjusted to -90 MVAR. In addition, the SSSL was calculated to be -158 MVAR. Therefore, the protection settings had to be adjusted to fall in between the limiter settings and the SSSL. New protection settings were issued on April 10. The field P&C personnel then applied these settings, and verification of the settings was completed on April 11, 2018.); 2) Establish a control in the entity’s risk and compliance system to ensure that the coordination of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions is completed within the required maximum of every five calendar years. This includes establishing a point person for PRC-019-2 compliance within Transmission Protection and Control Engineering which will help address a contributing cause of this noncompliance that was poor asset and configuration management; and 3) will update the existing MOD-025-2 control to include notifying Transmission Protection and Control Engineering when a capability verification will be conducted and that a PRC-019-2 review will be necessary within 90 days after the capability verification. Thereafter, the responsibility of oversight of MOD-025-2 R3 and PRC-019-2 would be assigned to the same Compliance Coordinator within Transmission Reliability Compliance (TRC). AEP needs until October 24, 2018 to complete this Mitigation Plan because of the large amount of time it takes AEP to establish the new control (Milestone 2) and to update the existing PRC-019-2 control (Milestone 3). The risk has already been mitigated because the necessary changes were applied to each synchronous condenser back in April of 2018.
2018-09-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Aurora Generation, LLC (Aurora) | NCR11659 | RFC2018019694 | PRC-024-2 | R2 | On May 4, 2018, Aurora submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. On July 12, 2016, LS Power completed the purchase of the entity plant from NRG. The previous owner of the entity had a large and diverse fleet with a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration. This compliance schedule did not include completing 40% of the applicable units for the entity plant by the July 1, 2016, deadline. The previous owner’s implementation plan only included completing 40% of the applicable units at other plants (not the entity) that were part of their bundled NERC registration. During the purchase process, LS Power did not effectively plan to ensure that the entity would be compliant with the July 1, 2016 newly enforceable Standards and Requirements once LS Power acquired the entity. This noncompliance involves the management practices of external interdependencies management and verification. External interdependencies management is involved because the entity’s noncompliance partially arose from its transfer in ownership close in time to the effective date for PRC-024-2 R2 and LS Power’s failure to effectively plan to ensure the entity had performed the required PRC-024 coordination after LS Power purchased the entity. Verification is involved because LS Power staff failed to verify that the entity performed the required coordination once LS Power separately registered the entity after the purchase. That failure to verify is a root cause of this noncompliance. This noncompliance started on September 13, 2016, when the entity was required to comply with PRC-024-2 R2 and ended on July 1, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone,” a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because when the entity performed the verification, under-voltage trip protection settings needed to be slightly modified to meet the PRC-024-2 voltage-ride through requirements for four of the entity’s six generating units. Two of the six generating units required no changes. The entity has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since the entity started operating. A contributing cause of this noncompliance is the sale of the entity to LS Power around the time that PRC-024 became enforceable and that is a one-time event, which makes recurrence of this noncompliance unlikely. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activities. The entity received four competitive cost proposals and performed a through technical and cost evaluation. LS Power selected Kestrel Power Engineering on September 26, 2016 to perform the required work. Even though PRC-019, PRC-024, and MOD-025 allow a staged implementation plan until July 1, 2019 for 100% completion, LS Power approved completing 100% of the activities for the four units at the entity in 2017. These mitigating activities remediate the noncompliance and complete the required PRC-019, PRC-024, and MOD-025 activities for all plant units significantly earlier than the NERC staged implementation schedule dates allow. The entity has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance: 1) The entity’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, the entity’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended; 2) The entity conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator Reliability Standards apply and what are their responsibilities; 3) The entity conducts internal audits of their NERC program on a three-year basis; and 4) The entity uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval.
2018-09-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Rockford Generation, LLC (Rockford) | NCR11660 | RFC2018019692 | PRC-024-2 | R2 | On May 4, 2018, Rockford submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. LS Power purchased the entity after the July 1, 2016 implementation date. (LS Power purchased the entity from NRG on July 12, 2016. ) The previous owner of the entity plant had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at the entity plant by July 1, 2016. The previous owner’s implementation plan only included completing 40% of the applicable units at other plants (not the entity plant) that were part of their bundled NERC registration. During the purchase process, LS Power did not effectively plan to ensure that the entity would be compliant with the July 1, 2016 newly enforceable Standards and Requirements once LS Power separately registered the entity. After purchasing the entity and separately registering the entity, LS Power discovered that the entity was not compliant with PRC-024-2 and took steps to return to compliance. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because the entity’s noncompliance partially arose from its transfer in ownership close in time to the effective date for PRC-024-2 R2 and LS Power’s failure to effectively plan to ensure the entity would be compliant after LS Power separately registered the entity after the purchase. Verification is involved because LS Power staff failed to verify that the entity would be in compliance with PRC-024-2 once LS Power separately registered the entity after the purchase. That failure to verify is a root cause of this noncompliance. This noncompliance started on September 13, 2016, when the entity was required to comply with PRC-024-2 R2 and ended on March 3, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because when the entity performed the required verification, only minimal changes needed to be made. The entity also has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since the entity started operating. A contributing cause of this noncompliance is the sale of the entity to LS Power around the time that PRC-024 became enforceable and LS Power separately registered the entity. Both of those are one time events that resulted from the sale of the plant and the implementation of a new Standard and are unlikely to occur again. Lastly, the entity contributes approximately 462 MW to the grid and operated at approximately a 7% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-024-2 R2 compliance history and determined there were no relevant instances of noncompliance. The entity originally self-reported noncompliances with MOD-025-2 R1, MOD-025-2 R2, PRC-019-2 R1, and PRC-024-2 R1 on October 3, 2016, and on October 4, 2016. ReliabilityFirst processed all four of those noncompliances in a Compliance Exception that was posted on October 31, 2017. After the Compliance Exception was posted, the entity discovered that it should have also self-reported a noncompliance with PRC-024-2 R2 on October 3, 2016, but made a mistake and inadvertently forgot to submit it. Once the entity discovered this mistake, they self-reported this noncompliance with PRC-024-2 R2. | To mitigate this noncompliance, the entity: 1) Requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activity. The entity selected Kestrel Power Engineering on September 26, 2016, to perform the required work; and 2) Even though the three standards mentioned above allow a staged implementation plan until July 1, 2019 for 100% completion, LS Power approved completing 100% of all units in 2017. The entity has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance: 1) the entity’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, the entity’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended; 2) conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator reliability Standards apply and what are their responsibilities; 3) conducts internal audits of their NERC program on a three-year basis; and 4) uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. ReliabilityFirst has verified the completion of all mitigation activity.
2018-09-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Seneca Generation, LLC (Seneca) | NCR11446 | RFC2018019693 | PRC-024-2 | R2 | On May 4, 2018, Seneca submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. LS Power purchased the entity in May 2016. The previous owner of the entity plant had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at the entity plant by July 1, 2016. The previous owner’s implementation plan only included completing 40% of the applicable units at other plants (not the entity) that were part of their bundled NERC registration. During the purchase process, LS Power did not effectively plan to ensure that the entity would be compliant with the July 1, 2016 newly enforceable Standards and Requirements once LS Power acquired the entity. This noncompliance involves the management practices of external interdependencies management and verification. External interdependencies management is involved because the entity’s noncompliance partially arose from its transfer in ownership close in time to the effective date for PRC-024-2 R2 and LS Power’s failure to effectively plan to ensure the entity would be compliant after LS Power purchased the entity. Verification is involved because LS Power staff failed to verify that the entity would be in compliance with PRC-024-2 once LS Power separately registered the entity after the purchase. That failure to verify is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R2 and ended on December 29, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone,” a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because when the entity performed the review and verification, no changes were required. The entity has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since the entity started operating. A contributing cause of this noncompliance is the sale of the entity to LS Power around the time that PRC-024 became enforceable and that is a onetime event that resulted from the sale of the plant and the implementation of a new Standard and is unlikely to occur again. Lastly, the entity contributes approximately 451 MW to the grid and operated at approximately a 14% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) Obtained cost proposals to complete the required PRC-024 activity and developed mitigating activities to ensure full compliance with PRC-024; and 2) Revised and updated its internal controls program to ensure future regulatory staged implementation plans are reviewed and completed by the due dates. The entity has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance: 1) The entity’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, the entity’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended; 2) The entity conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator Reliability Standards apply and what are their responsibilities; 3) The entity conducts internal audits of their NERC program on a three-year basis; and 4) The entity uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval.
2018-09-27 | SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2017017942 | PRC-005-1 | R2 | On July 12, 2017, BREC submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-005-6 R3. BREC did not conduct maintenance and testing activities as required by PRC-005-6 R3 for two pilot relays. SERC later determined that the noncompliance extended back to PRC-005-1 R2. In April 2017, a BREC plant engineer spot-checked plant relays while performing other duties in that area of the Wilson plant. During that review, the engineer noticed a relay test sticker containing a date outside of the BREC normal testing window. After reviewing the Protection System Maintenance and Testing Program (PSMP), the plant engineer contacted compliance staff to report a possible compliance issue. BREC determined that it failed to perform the required maintenance and testing activities required by the PSMP for two pilot relays out of 1,639 relays covered by PRC-005 (0.12%). One of the protection schemes in place to protect the 0.6 mile circuit connecting the Wilson generating station generator step-up transformer to the Wilson substation relies, in part, on two pilot relays. After an inadvertent trip of the generating unit during relay testing prior to June 18, 2007, BREC changed the maintenance and testing process for these two relays. Rather than performing traditional relay testing and calibration, BREC began utilizing successful trips to ensure proper operation of the relay and the overall protection scheme. BREC deemed these successful functional tests comparable to actual relay testing. However, BREC did not include this alternate testing in its PSMP document. Following the identification of the pilot relay issue, relay technicians, engineers, and management reviewed and discussed the relay test program, the relay test records, and schedules contained in the database to ensure BREC did not omit other relays. BREC cross-referenced the relay database against system drawings with an emphasis on plant relays and pilot relays. BREC did not identify any other issues. The primary cause of this noncompliance is BREC’s failure to classify the two relays as PRC-005 relays during the implementation of PRC-005-1. The change to the maintenance and testing practice resulted from reliability concerns associated with the relay test plan, specifically the possible trip of generator equipment during testing. BREC made the change prior to mandatory compliance with NERC Standards. Since BREC was not routinely testing the relays with a traditional schedule by relay technicians, the relays were not included in the relay testing database utilized by technicians. This noncompliance started on June 18, 2007, when PRC-005-1 became mandatory and enforceable, and ended on May 2, 2017, when BREC completed maintenance and testing required by PRC-005-6 R3. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BREC’s failure to perform the required maintenance and testing activities could have resulted in a misoperation of the pilot relays which would cause an unnecessary trip of the generating unit. However, the properly tested back-up protection would operate during a fault condition if the pilot relays failed to function as designed. In this situation, a Wilson generating unit trip would occur with or without proper pilot relay operation. Other relays provide protection for the 0.6 mile circuit. No misoperations of the two pilot relays occurred during the noncompliance. In addition, on May 2, 2017, BREC completed the testing on the relays and identified no issues with the relays. The Wilson facility is 448 MWs out of 1,904 MWs of BREC’s installed generation. The Wilson facility is not blackstart capable, and not designated as a critical facility by the Planning Authority. No harm is known to have occurred. SERC determined that BREC‘s PRC-005-1 R2 compliance history should not serve as a basis for applying a penalty. BREC’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID SERC2015014636. The mitigation activities for the prior noncompliance would not have prevented or identified the instant issue because those activities were focused on a review of Protection System devices in BREC’s database. In the instant noncompliance, BREC did not identify two pilot relays as Protection System devices and they were not included in the relevant database. | To mitigate this noncompliance, BREC: 1) tested the two pilot relays; 2) developed and implemented a new test procedure for the two relays; 2) added the two relays to the relay database; and 3) set up tracking of future test dates using the database tool.
2018-09-27 | SERC Reliability Corporation (SERC) | Cherokee County Cogeneration Partners, LLC (Cherokee) | NCR11191 | SERC2018018992 | PRC-024-2 | R1 | On January 15, 2018, Cherokee submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Cherokee did not set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1. On April 15, 2016, Cherokee completed generator frequency protective relay setting changes in advance of the July 1, 2016 enforceable date for PRC-024-2. During the week of October 9, 2017, an electrical contractor was on site performing protection scheme calibrations and functional testing. While performing the work, the contractor’s field engineer utilized records maintained by the contractor of previous calibrations and settings to verify the generator frequency protective relay settings. The contractor had not updated its records to reflect the April 15, 2016 setting changes which resulted in the field engineer using incorrect relay setting records. The field engineer changed the relay settings back to the pre-April 15, 2016 relay settings, which caused Cherokee to be noncompliant with PRC-024-2 R1. The contractor’s field engineer did not disclose to Cherokee that the field engineer changed the relay settings. During the week of December 4, 2017, Cherokee’s plant manager was collecting relay setting data for PRC-006-SERC-02, and contracted with the same electrical contractor to validate the relay settings. During this validation, the contractor discovered its field engineer had changed the settings to be noncompliant. On December 14, 2017, the contractor notified Cherokee of the error and dispatched a field engineer to the site to change the settings so the relay settings were again compliant with PRC-024-2 R1. The primary causes of this noncompliance were ineffective contractor oversight and ineffective document management practices. This noncompliance started on October 9, 2017, when the contractor changed the relay settings to be noncompliant, and ended on December 14, 2017, when the contractor corrected the relay settings to be compliant. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Premature tripping of generation assets could exacerbate a frequency disturbance. However, the Cherokee facility is a combined cycle plant comprised of one gas turbine with one steam turbine generator with a maximum capacity of 98 MW. In 2017, the facility operated at a capacity factor of 77%. The full output of the facility is under contract and dispatched by an entity with over 21,000 MWs of generation capacity, therefore an inadvertent trip of the Cherokee facility would have minimal impact to the BPS. In addition, during the noncompliance, the Cherokee facility did not trip despite the fact that the generator protective relay settings were not compliant with PRC-024-2 Attachment 1. Cherokee changed the underfrequency relay on both the gas and steam turbine generators setting from 59 Hz and time delay of 20 seconds to 59 Hz and time delay of 250 seconds to become compliant. No harm is known to have occurred. SERC considered Cherokee‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Cherokee: 1) changed the relay settings; 2) updated its procurement policy and work scope documents for protective relay maintenance, calibration, and testing to include the following language on all binding, service oriented purchase orders: “During the execution of services, you and your agents are not authorized to make any modifications or alterations to any equipment, component, controller, software, etc., without the expressed written permission of the facility’s management team. All changes to any system or component that will alter or affect fit, form, or function, must be fully vetted and approved by the facility’s management team prior to modification." Each contractor must sign the purchase order acknowledging they agreed to the terms; and 3) modified Section 8.2 of the Relay Cleaning, Calibration, and Testing scope of services document to specify that Cherokee will provide the relay maintenance, test, and calibration records that include all current settings to be utilized by the contractor to validate relay settings and calibrations during the maintenance activity.
2018-09-27 | SERC Reliability Corporation (SERC) | City of Springfield, IL - CWLP (CWLP) | NCR01328 | SERC2018019107 | PRC-019-2 | R1 | On February 2, 2018, CWLP submitted a Self-Report stating that, as a Generator Owner and Transmission Owner, it was in noncompliance with PRC-019-2 R1. CWLP did not coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions in accordance with the NERC implementation plan. SERC later determined that this noncompliance only applied to CWLP’s Generator Owner function. During the fall of 2012, CWLP completed an extensive dynamics data collection project as part of the MOD-026 Standards. In the fall of 2015, CWLP initiated the PRC-019 study with a third party vendor to ensure it completed the analysis and implemented any setting changes prior to the 40% implementation plan requirement. CWLP believed the MOD-026 data collection project included all of the data required for the PRC-019-2 analysis. In February 2016, the vendor provided draft reports and noted there was additional unit data necessary to complete the analysis that was not part of the MOD-026 data collection project, therefore the vendor could not complete the PRC-019 analysis. CWLP collected the required data it had internally but also had to work with various generator manufactures to collect the remaining data. During this time, CWLP also initiated a scheduled controls system upgrade which required coordination with the PRC-019-2 analysis data. In April 2017, CWLP provided the additional required data to the vendor to enable the vendor to complete the required PRC-019-2 analysis. In late 2017, CWLP attended an industry meeting that included a discussion of the PRC-019-2 implementation plan. During the discussion, a PRC subject matter expert discussed the July 1, 2016 40% compliance requirement. CWLP interpreted the implementation plan to require 40% compliance within two years of the July 1, 2016 effective date of PRC-019-2, or July 1, 2018. CWLP contacted SERC to confirm the PRC-019-2 Implementation Plan date for 40% complete by July 1, 2018 and SERC replied, stating that the PRC-019-2 implementation plan was the same as PRC-019-1, which required 40% completion by July 1, 2016. Because of CWLP’s misinterpretation of the PRC-019-2 implementation plan, none of the five CWLP units were compliant on July 1, 2016. The primary cause of this issue was CWLP’s misunderstanding that the implementation plan allowed two years from the effective date of PRC-019-2. CWLP did not understand that the PRC-019-1 implementation plan dates remained in effect for PRC-019-2. In addition, CWLP’s misunderstanding that the data collected for MOD-026 included all of the data required for the PRC-019-2 analysis contributed to the noncompliance. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on January 10, 2018, when 60% of the CWLP units were compliant with the implementation plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CWLP’s failure to verify that the voltage regulating system controls were properly coordinated with its Protection Systems could lead to a generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, by January 23, 2018, CWLP completed the coordination of four of its five units and only one unit required a coordination change. One unit required modifications to change the pick-up setting from 105% to 107% for two over-fluxing V/Hz relays to ensure coordination with the units’ control system protection. The one unit that required relay setting changes is a 112 MW unit that operates at less than a 5% capacity factor and it is unlikely that the generator would have operated in the no-trip zone. No harm is known to have occurred. SERC considered CWLP’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, CWLP: 1) completed the coordination study for 60% of the applicable units; 2) changed the two relay settings for the Interstate unit; 3) conducted training for engineers and I&C Technicians on the Ovation excitation system for the applicable units. This training will allow CWLP to provide the necessary excitation system settings file and other data to the vendor for the next PRC-019 analysis; 4) implemented two MAXIMO work orders for each of the applicable units to ensure the 5 year requirement for coordination, including the date the next 5 year action is due. The first MAXIMO work order is set for 36 months to initiate the analysis required and the second MAXIMO work order is set for 60 months for confirmation; 5) utilizes software for compliance to track each NERC standard by requirement. The software records are assigned by the Superintendent of Compliance and populated by the subject matter expert during the monitor period and annual Self-Certification. This is noted in the CWLP Internal Compliance Program; and 6) utilizes the SERC FAQ process to remain aware of Implementation Plan effective dates and associated % completion thresholds. CWLP revised the CWLP TD-SOP-025 Impact Analysis Form Item 6 with the notation, “(Note: The SERC FAQ site and process shall be reviewed and utilized for guidance on associated NERC Implementation Plan(s). https://www.serc1.org/outreach/faq-lessons-learned/faq)”.
2018-09-27 | SERC Reliability Corporation (SERC) | City of Springfield, IL - CWLP (CWLP) | NCR01328 | SERC2018019108 | PRC-024-2 | R1 | On February 2, 2018, CWLP submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. CWLP did not verify that it set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1 in accordance with the NERC implementation plan. During the fall of 2012, CWLP completed an extensive dynamics data collection project as part of the MOD-026 Standards. In the fall of 2015, CWLP initiated the PRC-024-2 study with a third party vendor to ensure it completed the analysis and implemented any setting changes prior to the 40% implementation plan requirement. CWLP believed the MOD-026 data collection project included all of the data required for the PRC-024-2 analysis. In February 2016, the vendor provided final reports for some units and draft reports for other units where additional unit data necessary to complete the analysis. CWLP collected the required data it had internally but also had to work with various generator manufactures to collect the remaining data. During this time, CWLP also initiated a controls system scheduled upgrade which required coordination with the PRC-024-2 analysis data. In April 2017, CWLP provided the additional required data to the vendor to enable the vendor to complete the required PRC-024-2 analysis. In late 2017, CWLP attended an industry meeting that included a discussion of the PRC-024-2 implementation plan. During the discussion, a PRC subject matter expert discussed the July 1, 2016 40% compliance requirement. CWLP interpreted the implementation plan to require 40% compliance within two years of the July 1, 2016 effective date of PRC-024-2, or July 1, 2018. CWLP contacted SERC to confirm the PRC-024-2 Implementation Plan date for 40% complete by July 1, 2018 and SERC replied stating the PRC-024-2 implementation plan was the same as PRC-024-1, which required 40% completion by July 1, 2016. On July 1, 2016, two of the five CWLP units were compliant with no changes required, which met the July 1, 2016 40% implementation plan requirement. On July 1, 2017, only two of the five CWLP units were compliant, therefore CWLP did not meet the 60% implementation plan requirement. The primary cause of this issue was CWLP’s misunderstanding that the implementation plan allowed two years from the effective date of PRC-024-2. CWLP did not understand that the PRC-024-1 implementation plan dates remained in effect for PRC-024-2. In addition, CWLP’s misunderstanding that the data collected for MOD-026 included the all of data required for the PRC-024-2 analysis contributed to the noncompliance. This noncompliance started on July 1, 2017, when the CWLP did not meet the 60% requirement in the NERC implementation plan, and ended on January 10, 2018, when 60% of the CWLP units were compliant. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CWLP’s failure to verify that the generator frequency relays are set not trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, CWLP met the 40% implementation plan requirement to confirm coordination of two of its five units. On January 23, 2018, CWLP confirmed coordination for two additional units. CWLP did not require any relay setting changes on the four units for compliance. No harm is known to have occurred. SERC considered CWLP’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, CWLP: 1) completed the required assessment and determined no coordination changes were required; 2) conducted training for engineers and I&C Technicians on the Ovation excitation system for the applicable units. This training will allow CWLP to provide the necessary excitation system settings file and other data to the vendor for the next PRC-024 analysis; 3) coordinates major projects and or changes to the CWLP generation including protection system applicable to PRC-024 during the routine CWLP Compliance Committee meetings as referenced in the CWLP Internal Compliance Program on Page 8, Section 5.13.4. The CWLP generation department is represented by the General Superintendent of Generation who will inform the CWLP Compliance Committee of any scheduled/unscheduled generation projects including the protection system that may impact CWLP Compliance and require coordination. The Superintendent of Substation Engineering & Maintenance and Communications, who directly supervises the Relay Department and Planning Department, participates in these meetings. In addition, the Superintendent of Compliance meets with the Subject Matter Experts (SME) for the NERC Functional Types such as PRC. The Superintendent of Compliance directly interacts with the SMEs for further coordination and interpretation of the NERC Standards and Requirements. This structure provides oversight to maintain and enforce an effective compliance management program to address PRC-024-2 Requirement R3.1 and R4; and 4) utilizes the SERC FAQ process to remain aware of Implementation Plan effective dates and associated % completion thresholds. CWLP revised the CWLP TD-SOP-025 Impact Analysis Form Item 6 with the notation, “(Note: The SERC FAQ site and process shall be reviewed and utilized for guidance on associated NERC Implementation Plan(s). https://www.serc1.org/outreach/faq-lessons-learned/faq)”.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Roxboro) (Roxboro) | NCR09021 | SERC2017018612 | MOD-025-2 | R1 | On November 8, 2017, Roxboro submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Roxboro did not meet the MOD-025-2 implementation schedule to provide its Transmission Planner (TP) with verification of the Real Power capability of its applicable Facility in accordance with Attachment 1 by July 1, 2016. On May 30, 2016, Roxboro’s work order management system initiated a work order for verification of real power capability with a due date of June 29, 2016, however Roxboro did not complete that work order. According to corporate compliance, on August 3, 2016, the site and the corporate compliance analyst at the time discussed the open work order, however this discussion was after the required compliance date and after the work order due date. Corporate compliance advised the site that the work order could remain open because the corporate compliance analyst incorrectly believed that Roxboro had until July 1, 2019 to be compliant. On February 2, 2017, during a site compliance review by new corporate compliance personnel, Roxboro determined that it did not complete this work order and might not be compliant with MOD-025-2 R1 based on the new compliance personnel’s understanding of the implementation plan. On February 23, 2017, Roxboro confirmed that its prior testing was not sufficient to meet the requirements of MOD-025-2 R1. Corporate compliance stated that it did not Self-Report at this time due to the misunderstanding of the new compliance personnel that the mitigation plan must be complete in order to self-report. The primary causes of noncompliance were Roxboro’s failure to complete the work order initiated on May 30, 2016 and due on June 29, 2016, and Roxboro’s belief that it had until the 100% completion date of July 1, 2019 to be compliant. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on October 3, 2017, when Roxboro provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Roxboro’s failure to provide the required Real Power capability information to the TP on the timeframe required by the MOD-025-2 implementation schedule could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Roxboro completed the required testing by August 15, 2017 and gave the required testing information to its Transmission Planner by October 3, 2017. Although Roxboro was late in completing verification of the Real Power capability of its generating units pursuant to the MOD-025-2 implementation plan, it completed verification of 100% of its units before larger entities with more generating units are required to complete verification of 100% of their units. Roxboro is a single generator, 46 MW facility with a 12-month capacity factor of 93% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Roxboro‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Roxboro: 1) completed the verification of the Real Power capability study; 2) provided the study results to the TP; 3) scheduled a reoccurring five year Preventative Maintenance (PM) work order in the work planning software. The PM is set to populate beginning of March 2022 with a +30 days due date; 4) scheduled quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open PMs, new standards etc.); 5) engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference; 6) created a documented procedure for sites outlining process for editing work orders in work planning software; 7) provided site personnel with 'planning' access (ability to modify work order) procedure and required to attest to adherence to go-forward; and 8) require plants to pull any open work orders tagged with 'SERC' and submit to corporate compliance on a monthly basis.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Roxboro) (Roxboro) | NCR09021 | SERC2018019558 | MOD-025-2 | R2 | On April 18, 2018, Roxboro submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Roxboro did not meet the MOD-025-2 implementation schedule to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its applicable Facility in accordance with Attachment 1 by July 1, 2016. Roxboro self-reported the instant noncompliance after SERC requested Roxboro confirm compliance with MOD-025-2 R2 as a result of SERC’s review of an earlier Roxboro Self-Report involving MOD-025-2 R1 (NERC Violation ID SERC2017018612). On May 30, 2016, Roxboro’s work order management system initiated a work order for verification of reactive power capability with a due date of June 29, 2016, however Roxboro did not complete that work order. According to corporate compliance, on August 3, 2016, the site and the corporate compliance analyst at the time discussed the open work order, however that discussion was after the required compliance date and after the work order due date. Corporate compliance advised the site that the work order could remain open because the corporate compliance analyst incorrectly believed that Roxboro had until July 1, 2019 to be compliant. On February 2, 2017, during a site compliance review by new corporate compliance personnel, Roxboro determined that it did not complete this work order and may not be in compliance with MOD-025-2 R2 based on the new compliance personnel’s understanding of the implementation plan. On February 23, 2017, Roxboro confirmed that its prior testing was not sufficient to meet the requirements of MOD-025-2 R2. The primary causes of noncompliance were Roxboro’s failure to complete the work order initiated on May 30, 2016 and due on June 29, 2016, and Roxboro’s belief that it had until the 100% completion date of July 1, 2019 to be compliant. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on October 3, 2017, when Roxboro provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Roxboro’s failure to provide the required Reactive Power capability information to the TP on the timeframe required by the MOD-025-2 implementation schedule could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Roxboro completed the required testing by August 15, 2017 and gave the required testing information to its Transmission Planner by October 3, 2017. Although Roxboro was late in completing verification of the Reactive Power capability of its generating units pursuant to the MOD-025-2 implementation plan, it completed verification of 100% of its units before larger entities with more generating units are required to complete verification of 100% of their units. Roxboro is a single generator 46 MW facility with a 12-month capacity factor of 93% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Roxboro‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Roxboro: 1) completed the verification of the Reactive Power capability study; 2) provided the study results to the TP; 3) scheduled a reoccurring five year Preventative Maintenance (PM) work order in the work planning software. The PM is set to populate beginning of March 2022 with a +30 days due date; 4) scheduled quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open PMs, new standards etc.); 5) engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference; 6) created a documented procedure for sites outlining process for editing work orders in work planning software; 7) provided site personnel with 'planning' access (ability to modify work order) procedure and required to attest to adherence to go-forward; and 8) require plants to pull any open work orders tagged with 'SERC' and submit to corporate compliance on a monthly basis.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Roxboro) (Roxboro) | NCR09021 | SERC2018019422 | PRC-019-2 | R1 | On March 21, 2018, Roxboro submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Roxboro did not coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions in accordance with the NERC implementation plan for PRC-019-2. Roxboro self-reported the instant noncompliance after SERC requested Roxboro confirm compliance with PRC-019-2 R1 as a result of SERC’s review of an earlier Roxboro Self-Report involving MOD-025-2 R1 (NERC Violation ID SERC2017018612). Roxboro initially believed it was in compliance because the settings had not changed and the engineering subject matter expert (SME) completed a high-level calculation to support this belief. However, after SERC requested confirmation of compliance, Roxboro engaged a contractor to perform an analysis of the coordination of the voltage regulating system controls with applicable equipment. Roxboro has no documentation that it completed a high-level calculation. Roxboro stated that when it determined that the high-level calculation did not meet the intent of the Standard, Roxboro did not retain the record. The causes of this noncompliance were due to Roxboro’s misinterpretation of the language included in the Standard and a misinterpretation of the implementation plan. Roxboro inaccurately believed that the Standard placed a maximum frequency allowance for coordination but not a minimum. Roxboro also misunderstood the implementation plan and believed that the 40% to 80% compliance implementation plan applied to those larger facilities that could comply in such a manner. Roxboro believed that 100% compliance by July 1, 2019 was the date to be concerned with, as it was applicable to all Facilities regardless of size or number of units. SERC determined that Roxboro’s lack of understanding of the Requirements was also a cause as the SME did not understand the Requirements for compliance and believed a high-level overview was sufficient to meet the Requirement. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on March 26, 2018, when Roxboro completed the required coordination of its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Roxboro’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems on the timeframe required by the PRC-019-2 implementation schedule could lead to a generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, no coordination changes were necessary to meet the Requirement. Roxboro completed the required coordination by March 26, 2018. Although Roxboro was late in completing the coordination of its applicable Facilities pursuant to the PRC-019-2 implementation plan, it completed coordination of 100% of its applicable Facilities before larger entities with more generating units are required to complete coordination of 100% of their applicable Facilities. Roxboro is a single generator 46 MW facility with a 12-month capacity factor of 93% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Roxboro‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Roxboro: 1) engaged a third party contractor to perform the coordination analysis; 2) scheduled Preventative Maintenance (PM) work order in the work planning software with enough lead time to allow for scheduling with the TP. This PM will notify plant personnel when coordination is due in five years. PM is set to populate beginning of January 2023 with a +30 days due date. This will prompt plant to start process of securing a third party to complete the coordination; 3) created a recurring email to support PM. Scheduled a recurring email from general corporate compliance to recur every five years in January and be sent to all stakeholders; 4) conduct quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open PMs, new standards etc.); and 5) corporate compliance engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Roxboro) (Roxboro) | NCR09021 | SERC2018019418 | PRC-024-2 | R1 | On March 21, 2018, Roxboro submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Roxboro did not set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit within the “no trip zone” of PRC-024 Attachment 1 in accordance with the NERC implementation plan. Roxboro self-reported the instant noncompliance after SERC requested Roxboro confirm compliance with PRC-024-2 R1 as a result of SERC’s review of an earlier Roxboro Self-report involving MOD-025-2 R1 (NERC Violation ID SERC2017018612). The Roxboro facility has one generator unit with two frequency relays. Roxboro did not set the two frequency relays in accordance with PRC-024-2-R1. The cause of this noncompliance was Roxboro’s misinterpretation of the PRC-024-2 implementation plan. Roxboro misunderstood the implementation plan and believed that the 40% to 80% compliance implementation plan applied to those larger facilities that could comply in such a manner. Roxboro believed that 100% compliance by July 1, 2019 was the date to be concerned with, as it was applicable to all Facilities regardless of size or number of units. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on March 5, 2018, when Roxboro changed the relay settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Roxboro’s failure to verify that the generator frequency relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. The over-frequency setting was set to trip at or above 60.5 Hz after 10 seconds of time delay and the under-frequency setting was set to trip at or below 59.5 Hz after 10 seconds of time delay. Roxboro changed the over-frequency setting to trip at or above 61.81 Hz after 0.033 seconds and the under-frequency setting to trip at or below 57.70 Hz after 0.033 seconds of time delay. However, Roxboro did not have any unit trips due to the frequency protective relaying during the noncompliance. Roxboro completed the required setting of its generator frequency protective relaying by March 5, 2018. Although Roxboro was late in completing the required relay settings for its applicable generating units pursuant to the PRC-024-2 implementation plan, it completed relay settings for 100% of its applicable generating units before larger entities with more generating units are required to have completed relay settings for 100% of their applicable generating units. Roxboro is a single generator, 46 MW facility with a 12-month capacity factor of 93% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Roxboro‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Roxboro: 1) hired a third party contractor to change relay settings; 2) conducts quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open preventative maintenance work orders, new standards etc.); and 3) corporate compliance engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Roxboro) (Roxboro) | NCR09021 | SERC2018019681 | PRC-024-2 | R2 | On May 11, 2018, Roxboro submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Roxboro did not verify that it set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit within the “no trip zone” of PRC-024 Attachment 2 in accordance with the NERC implementation plan. Roxboro self-reported the instant noncompliance after SERC requested Roxboro confirm compliance with PRC-024-2 R1as a result of SERC’s review of an earlier Roxboro Self-Report involving MOD-025-2 R1 (NERC Violation ID SERC2017018612). The Roxboro facility has one generator unit, with two voltage relays. On March 5, 2018, Roxboro verified that its generator voltage protective relaying settings were in compliance with PRC-024-2 R2 attachment 2, almost two years after the implementation plan date of July 1, 2016 for verification of 40% of the applicable units. On May 1, 2018, Roxboro responded to a Request for Information stating that it was compliant with PRC-024-2 R2 because when it did verify the relay settings on March 5, 2018, the settings were compliant with PRC-024-2 R2, and thus Roxboro was compliant with PRC-024-2 R2. On May 8, 2018, SERC informed Roxboro that in order to be compliant with PRC-024-2 R2, Roxboro must have verified compliance with the requirement prior to July 1, 2016. Roxboro then self-reported the noncompliance. The cause of the noncompliance was Roxboro’s misinterpretation of the implementation plan. Roxboro misunderstood the implementation plan and believed that the 40% to 80% compliance implementation plan applied to those larger facilities that could comply in such a manner. Roxboro believed that 100% compliance by July 1, 2019 was the date to be concerned with, as it was applicable to all Facilities regardless of size or number of units. In addition, Roxboro did not Self-Report the noncompliance until required to by SERC because it incorrectly believed that if the settings were correct once it completed the analysis, there was no instance of noncompliance. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on March 5, 2018, when Roxboro verified the relay settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Roxboro’s failure to verify that the generator voltage relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, no relay setting changes were required. Roxboro did not have any unit trips due to the voltage protective relaying during the noncompliance. Roxboro completed the required setting of its generator voltage protective relaying by March 5, 2018. Although Roxboro was late in completing the required relay settings for its applicable generating units pursuant to the PRC-024-2 implementation plan, it completed relay settings for 100% of its applicable generating units before larger entities with more generating units are required to have completed relay settings for 100% of their applicable generating units. Roxboro is a single generator 46 MW facility with a 12-month capacity factor of 93% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Roxboro’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Roxboro: 1) verified relay settings; 2) conducts quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open preventative maintenance work orders, new standards etc.); and 3) corporate compliance engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Southport) (Southport) | NCR09020 | SERC2017018613 | MOD-025-2 | R1 | On November 8, 2017, Southport submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Southport did not meet the MOD-025-2 implementation plan to provide its Transmission Planner (TP) with verification of the Real Power capability of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. On May 30, 2016, Southport’s work order management system initiated a work order for verification of real power capability with a due date of June 29, 2016 however Southport did not complete that work order. According to corporate compliance, on August 4, 2016, the site and the corporate compliance analyst at the time discussed the open work order, however this discussion was after the required compliance date and after the work order due date. Corporate compliance advised the site that the work order could remain open because the corporate compliance analyst incorrectly believed that Southport had until July 1, 2019 to be compliant. On February 2, 2017, during a site compliance review by new corporate compliance personnel, Southport determined that it did not complete this work order and might not be compliant with MOD-025-2 R1 based on the new compliance personnel’s understanding of the implementation plan. On February 23, 2017, Southport confirmed that its prior testing was not sufficient to meet the requirements of MOD-025-2 R1. Corporate compliance stated that it did not Self-Report at that time due to the misunderstanding of the new compliance personnel that the mitigation plan must be complete in order to self-report. The primary causes of noncompliance were Southport’s failure to complete the work order initiated on May 30, 2016 and due on June 29, 2016, and Southport’s belief that it had until the 100% completion date of July 1, 2019 to be compliant. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on October 3, 2017, when Southport provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Southport’s failure to provide the required Real Power capability information to the TP on the timeframe required by the MOD-025-2 implementation schedule could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Southport completed the required testing by August 16, 2017 and gave the required testing information to its Transmission Planner by October 3, 2017. Although Southport was late in completing verification of the Real Power capability of its generating units pursuant to the MOD-025-2 implementation plan, it completed verification of 100% of its units before larger entities with more generating units are required to complete verification of 100% of their units. Southport is a two generator, 88 MW facility with a 12-month capacity factor of 72% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Southport‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Southport: 1) completed the verification of the Real Power capability study; 2) provided the study results to the TP; 3) scheduled a reoccurring five year Preventative Maintenance (PM) work order in the work planning software. The PM is set to populate beginning of March 2022 with a +30 days due date; 4) scheduled quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open PMs, new standards etc.); 5) engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC Compliance conference and is scheduled to attend October 2018 NAGF conference; 6) created a documented procedure for sites outlining process for editing work orders in work planning software; 7) provided site personnel with 'planning' access (ability to modify work order) procedure and required to attest to adherence to go-forward; and 8) require plants to pull any open work orders tagged with 'SERC' and submit to corporate compliance on a monthly basis.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Southport) (Southport) | NCR09020 | SERC2018019557 | MOD-025-2 | R2 | On April 18, 2018, Southport submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Southport did not meet the MOD-025-2 implementation plan to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. Southport self-reported the instant noncompliance after SERC requested Southport confirm compliance with MOD-025-2 R2 as a result of SERC”s review of an earlier Southport Self-Report involving MOD-025-2 R1 (NERC Violation ID SERC2017018613) On May 30, 2016, Southport’s work order management system initiated a work order for verification of reactive power capability with a due date of June 29, 2016, however Southport did not complete that work order. According to corporate compliance, on August 4, 2016, the site and the corporate compliance analyst at the time discussed the open work order, however this discussion was after the required compliance date and after the work order due date. Corporate compliance advised the site that the work order could remain open because the corporate compliance analyst incorrectly believed that Southport had until July 1, 2019 to be compliant. On February 2, 2017, during a site compliance review by new corporate compliance personnel, Southport determined that it did not complete this work order and might not be compliant with MOD-025-2 R2 based on the new compliance personnel’s understanding of the implementation plan. On February 23, 2017, Southport confirmed that its prior testing was not sufficient to meet the requirements of MOD-025-2 R2. The primary causes of noncompliance were Southport’s failure to complete the work order initiated on May 30, 2016 and due on June 29, 2016, and Southport’s belief that it had until the 100% completion date of July 1, 2019 to be compliant. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on October 3, 2017, when Southport provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Southport’s failure to provide the required Reactive Power capability information to the TP on the timeframe required by the MOD-025-2 implementation schedule could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Southport completed the required testing by August 16, 2017 and gave the required testing information to its Transmission Planner by October 3, 2017. Although Southport was late in completing verification of the Reactive Power capability of its generating units pursuant to the MOD-025-2 implementation plan, it completed verification of 100% of its units before larger entities with more generating units are required to complete verification of 100% of their units. Southport is a two generator, 88 MW facility with a 12-month capacity factor of 72% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Southport‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Southport: 1) completed the verification of the Reactive Power capability study; 2) provided the study results to the TP; 3) scheduled a reoccurring five year Preventative Maintenance (PM) work order in the work planning software. The PM is set to populate beginning of March 2022 with a +30 days due date; 4) scheduled quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open PMs, new standards etc.); 5) engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC Compliance conference and is scheduled to attend October 2018 NAGF conference; 6) created a documented procedure for sites outlining process for editing work orders in work planning software; 7) provided site personnel with 'planning' access (ability to modify work order) procedure and required to attest to adherence to go-forward; and 8) require plants to pull any open work orders tagged with 'SERC' and submit to corporate compliance on a monthly basis.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Southport) (Southport) | NCR09020 | SERC2018019423 | PRC-019-2 | R1 | On March 21, 2018, Southport submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Southport did not coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions in accordance with the NERC implementation plan. Southport self-reported the instant noncompliance after SERC requested Southport confirm compliance with PRC-019-2 R1 as a result of SERC’s review of an earlier Southport Self-Report involving MOD-025-2 R1 (NERC Violation ID SERC2017018613) Southport initially believed it was in compliance because the settings had not changed and the engineering subject matter expert (SME) completed a high-level calculation to support this belief. However, after SERC requested confirmation of compliance, Southport engaged a contractor to perform an analysis of the coordination of the voltage regulating system controls with applicable equipment. Southport has no documentation that it completed a high-level calculation. Southport stated that when it determined that the high-level calculation did not meet the intent of the Standard, Southport did not retain the record. The causes of the noncompliance were due to Southport’s misinterpretation of the language included in the Standard, and a misinterpretation of the implementation plan. Southport inaccurately believed that the Standard placed a maximum frequency allowance for coordination but not a minimum. Southport also misunderstood the implementation plan and believed that the 40% to 80% compliance implementation plan applied to those larger facilities that could comply in such a manner. Southport believed that 100% compliance by July 1, 2019 was the date to be concerned with, as it was applicable to all Facilities regardless of size or number of units. SERC determined that Southport’s lack of understanding of the Requirements was also a cause as the SME did not understand the Requirements for compliance and believed a high-level overview was sufficient to meet the Requirement. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on March 26, 2018, when Southport completed the required coordination of its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Southport’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems on the timeframe required by the PRC-019-2 implementation schedule could lead to a generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, no coordination changes were necessary to meet the Requirement. Southport completed the required coordination by March 26, 2018. Although Southport was late in completing the coordination of its applicable Facilities pursuant to the PRC-019-2 implementation plan, it completed coordination of 100% of its applicable Facilities before larger entities with more generating units are required to complete coordination of 100% of their applicable Facilities. Southport is a two generator, 88 MW facility with a 12-month capacity factor of 72% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Southport‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Southport: 1) engaged a third party contractor to perform the coordination analysis; (completed March 26, 2018) 2) scheduled Preventative Maintenance (PM) work order in the work planning software with enough lead time to allow for scheduling with the TP. This PM will notify plant personnel when coordination is due in five years. PM is set to populate beginning of January 2023 with a +30 days due date. This will prompt plant to start process of securing a third party to complete the coordination; 3) created a recurring email to support PM. Scheduled a recurring email from general corporate compliance to recur every five years in January and be sent to all stakeholders; 4) conduct quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open PMs, new standards etc.); and 5) corporate compliance engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Southport) (Southport) | NCR09020 | SERC2018019421 | PRC-024-2 | R1 | On March 21, 2018, Southport submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Southport did not set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1 in accordance with the NERC implementation plan. Southport self-reported the instant noncompliance after SERC requested Southport confirm compliance with PRC-024-2 R1 as a result of SERC’s review of an earlier Southport Self-Report involving MOD-025-2 R1 (NERC Violation ID SERC2017018613). The Southport facility has two generator units with one frequency relay each. Southport did not set the two frequency relays in accordance with PRC-024-2-R1. The cause of this noncompliance was Southport’s misinterpretation of the PRC-024-2 implementation plan. Southport misunderstood the implementation plan and believed that the 40% to 80% compliance implementation plan applied to those larger facilities that could comply in such a manner. Southport believed that 100% compliance by July 1, 2019 was the date to be concerned with, as it was applicable to all Facilities regardless of size or number of units. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on March 14, 2018, when Southport changed the relay settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Southport’s failure to verify that the generator frequency relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. The over-frequency setting was set to trip at or above 60.5 Hz after 2 seconds of time delay and the under-frequency setting was set to trip at or below 59.5 Hz after 0.2 seconds of time delay. Southport changed the over-frequency setting to trip at or above 61.81 Hz after 0.033 seconds and the under-frequency setting to trip at or below 57.59 Hz after 0.033 seconds of time delay. However, Southport did not have any unit trips due to the frequency protective relaying during the period of noncompliance. Southport completed the required setting of its generator frequency protective relaying by March 14, 2018. Although Southport was late in completing the required relay settings for its applicable generating units pursuant to the PRC-024-2 implementation plan, it completed relay settings for 100% of its applicable generating units before larger entities with more generating units are required to have completed relay settings for 100% of their applicable generating units. Southport is an 88 MW facility with a 12-month capacity factor of 72% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Southport‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Southport: 1) hired a third party contractor to change relay settings; 2) conducts quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open preventative maintenance work orders, new standards etc.); and 3) corporate compliance engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference.
2018-09-27 | SERC Reliability Corporation (SERC) | CPI USA North Carolina LLC (Southport) (Southport) | NCR09020 | SERC2018019680 | PRC-024-2 | R2 | On May 11, 2018, Southport submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Southport did not verify that it set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit within the “no trip zone” of PRC-024 Attachment 2 in accordance with the NERC implementation plan. Southport self-reported the instant noncompliance after SERC requested Southport confirm compliance with PRC-024-2 R2 as a result of SERC’s review of an earlier Southport Self-Report involving MOD-025-2 R1 (NERC Violation ID SERC2017018613). The Southport facility has two generator units with one voltage relay each. On March 14, 2018, Southport verified that its generator voltage protective relaying settings were in compliance with PRC-024-2 R2 attachment 2, almost two years after the implementation plan date of July 1, 2016 for verification of 40% of the applicable units. On May 1, 2018, Southport responded to a Request for Information stating that it was compliant with PRC-024-2 R2 because when it did verify the relay settings on March 14, 2018, the settings were compliant with PRC-024-2 R2, and thus Southport was compliant with PRC-024-2 R2. On May 8, 2018, SERC informed Southport that in order to be compliant with PRC-024-2 R2, Southport must have verified compliance with the requirement prior to July 1, 2016. Southport then self-reported the noncompliance. The cause of the noncompliance was Southport’s misinterpretation of the PRC-024-2 implementation plan. Southport misunderstood the implementation plan and believed that the 40% to 80% compliance implementation plan applied to those larger facilities that could comply in such a manner. Southport believed that 100% compliance by July 1, 2019 was the date to be concerned with, as it was applicable to all Facilities regardless of size or number of units. In addition, Southport did not Self-Report the noncompliance until required to by SERC because it incorrectly believed that if the settings were correct once it completed the analysis, there was no instance of noncompliance. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on March 14, 2018, when Southport verified the relay settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Southport’s failure to verify that the generator voltage relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, no relay setting changes were required. Southport did not have any unit trips due to the voltage protective relaying during the noncompliance. Southport completed the required setting of its generator voltage protective relaying by March 14, 2018. Although Southport was late in completing the required relay settings for its applicable generating units pursuant to the PRC-024-2 implementation plan, it completed relay settings for 100% of its applicable generating units before larger entities with more generating units are required to have completed relay settings for 100% of their applicable generating units. Southport is a two generator, 88 MW facility with a 12-month capacity factor of 72% for the period spanning April 2017 to March 2018. No harm is known to have occurred. SERC considered Southport‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Southport: 1) verified relay settings; 2) conducts quarterly compliance meetings to discuss current and upcoming compliance matters (i.e. open preventative maintenance work orders, new standards etc.); and 3) corporate compliance engaged in ongoing education activities in order to avoid future misinterpretation of Standards or implementation dates. The Senior Specialist, Compliance attended November 2017 WECC compliance conference and is scheduled to attend October 2018 NAGF conference.
2018-09-27 | SERC Reliability Corporation (SERC) | Craven County Wood Energy Limited Partnership (Craven) | NCR01212 | SERC2017017673 | PRC-005-2(i) | R3 | On May 31, 2017, Craven submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R3. Craven did not maintain the station DC supply battery within the six-month interval defined in Table 1-4(b). SERC staff determined that this noncompliance began under PRC-005-2(i) R3 and spanned into PRC-005-6 R3. In April 2017, during preparation for the submission of its Self-Certification, Craven identified that it did not measure its valve-regulated lead-acid battery cell/unit internal ohmic values on a six-month schedule on two separate occasions. Prior to this Self-Report, Craven contracted a third party to measure ohmic values of its DC battery systems while the contractor was on site for scheduled shutdowns. However, during its internal review, Craven identified that it did not measure the ohmic values within the required six-month intervals ending on October 14, 2015 and February 1, 2017. Craven conducted an internal review of all PRC-005-6 applicable elements and did not identify any additional instances of noncompliance. The primary causes of the noncompliance were lack of sufficient contractor oversight and a miscalculation of the six-month due date. The confusing configuration of the Protection System Maintenance Program (PSMP) spreadsheet’s layout and columns caused field personnel to misread the column values and determine incorrect scheduling dates. This noncompliance started on October 15, 2015, when Craven did not conduct the six-month activity within the interval and ended on March 10, 2016, when Craven conducted the six-month activity, and again on February 2, 2017, when Craven did not conduct the six-month activity within the interval and ended on June 2, 2017, when Craven conducted the six-month activity. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Craven’s failure to conduct maintenance on the battery could result in a battery failure that could trip a unit offline or prevent a trip when necessary. Also, a failure of a battery that supplies power to other devices for the protection scheme could affect the interconnected and neighboring Transmission Operators. However, the noncompliance was limited to two non-sequential six-month activities to inspect the condition of all individual units by measuring battery cell/unit internal ohmic values. Craven did not identify any battery degradation through the remaining performance testing, which showed acceptable performance. The battery is alarmed to a system that Craven continuously monitors. Craven is a 50 MW bio-mass facility in the Duke Energy Progress Balancing Area with a 92.96% capacity factor in 2017. No harm is known to have occurred. SERC determined that Craven‘s PRC-005 compliance history should not serve as a basis for applying a penalty. The prior noncompliance (NERC Violation ID SERC2012011533) involved a misinterpretation of the definition of DC circuitry and was mitigated more than three years prior to the start of the instant noncompliance. The mitigation for the prior noncompliance would not have prevented a failure to conduct specific testing on batteries on a six-month interval. | To mitigate this noncompliance, Craven: 1) edited the Protection System Maintenance Program spreadsheet to show the next scheduled due date to measure its battery cell/unit internal ohmic values on a six-month schedule; 2) purchased required equipment and began using Craven personnel to conduct testing; 3) created a task in the plant computerized maintenance management system/compliance tracking database to remind employees to complete this maintenance task; 4) revised the PSMP spreadsheet layout to improve clarity; and 5) provided training to the plant employees on battery testing methods.
2018-09-27 | SERC Reliability Corporation (SERC) | Duke Energy Progress, LLC (DEP) | NCR01298 | SERC2017018086 | MOD-001-1a | R8; R8.2 | On July 31, 2017, DEP submitted a Self-Report stating that, as a Transmission Service Provider (TSP), it was in noncompliance with MOD-001-1a R8.2. DEP reported that it did not calculate a daily Available Transmission Capacity (ATC). DEP uses a ‘cloud-based’ software program that performs the ATC calculation. Other TSPs use the same engine independently, and DEP’s use does not affect the other users. DEP calculates the Available Flowgate Capacity (AFC) for each monitored Flowgate. The calculation of ATC occurs when DEP submits the results of its AFC calculation from the DEP AFC servers to the cloud-based engine. This ‘resync’ prompts the AFC engine to perform an ‘initialization.’ If the cloud-based engine does not initialize then the ATC calculation does not occur. Also, at 3:00 a.m. each morning, the DEP cloud-based engine does a ‘hard-restart’ and reinitializes all ATC values for all time calculation horizons using the most recently submitted AFC data. Also, DEP submits Daily AFC data “payloads” at 5:30 am, 1:30 pm, and 9:30 pm each day. On Friday, November 25, 2016 at 9:31 pm, a payload Daily AFC data was a part of DEP’s normally scheduled upload. The AFC Calculator re-initialized the Daily ATC values normally. But, on Saturday, November 26, 2016, the 3:00 a.m. ‘hard-restart’ process did not complete. The operator was unaware of that fact at that time. During the day, DEP’s scheduled Daily AFC payloads were sent and received by the calculator, but the calculator did not re-initialize and recalculate ATC. On Sunday morning, November 27, 2016, while attempting to evaluate a Transmission Service Reservation (TSR), a System Operator observed issues with the calculator and notified application support staff that the calculator was providing a message of INPROG (in progress) on AFC/ATC validation checks. This message was abnormal because the INPROG state for a TSR usually completes very quickly. At 9:52 a.m., ATC application support staff discovered that the DEP AFC/ATC tasks were running normally but there was no corresponding indication that the process was initializing and properly performing the calculation of ATC. DEP ATC application support staff made attempts to manually initialize the process, but was unsuccessful and contacted the vendor for support. At 12:49 p.m. the vendor was able to initiate a manual restart that returned the process to normal for calculating all ATC values. The apparent cause of this noncompliance is that the ATC calculator did not properly restart and DEP did not have controls in place to verify that the restart occurred. This noncompliance started on November 26, 2016, when the ATC calculator failed to perform a hard restart and DEP did not recalculate ATC daily values, and ended on November 27, 2016, when the vendor restored ATC calculator service and DEP was able to recalculate ATC daily values. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Incorrect ATCs could result in over-selling or under-selling the actual capacity of the Flowgate. However, while DEP could have ‘over-sold’ Daily ATC, which could impact transmission line facility loading levels, DEP’s monitoring of real-time conditions and its use of the Real-Time Contingency Analysis application was unaffected and System Operators would have been aware of potential overloads in real time, in contingency, and any interchange planned for implementation. During this noncompliance, there were no System Operating Limit (SOL) exceedances in the DEP TOP footprint and no Transmission Loading Relief (TLR) procedures implemented affecting the DEP TOP footprint. In addition, DEP did not reject TSRs because of incorrect ATC postings. No harm is known to have occurred. SERC considered DEP’s compliance history and the compliance history of its affiliates and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, DEP: 1) ATC application support staff contacted the vendor and the vendor successfully returned the process to normal; 2) Added an item to the checklist for System Operators working on the TSP function desk for the Operator to verify the WebTrans AFC process had initialized during each control room shift; 3) ATC application support staff initiated discussions with the vendor for an alarm and/or other notification functionality being established for stalled initializations like the one that caused this event; and 4) The vendor implemented a notification process for the vendor and DEP TSP staff when the ATC engine fails to restart as planned.
2018-09-27 | SERC Reliability Corporation (SERC) | Effingham County Power, LLC (Effingham) | NCR11597 | SERC2018019642 | VAR-002-4.1 | R3 | On May 4, 2018, Effingham submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with VAR-002-4.1 R3. Effingham did not notify its Transmission Operator (TOP) of a status change on the power system stabilizer (PSS) within 30 minutes of the change and it did not restore the status within 30 minutes. The Effingham facility consists of two 235 MVA combustion turbines (CT) and one 230 MVA steam turbine. On November 13, 2017, Effingham performed a restart of the CT control system computer following the implementation of a technical information letter (TIL) from the supplier of the control system. Effingham did not restart the control system for the steam turbine as it was not part of the TIL. On May 1, 2018, while preparing to perform the required model verification testing for MOD-026 and MOD-027, the engineering contractor performing the test notified Effingham that the PSSs on CT1 and CT2 were disabled. Effingham determined the PSS status for the CTs changed to disabled after the control system restart in November. Because Effingham did not restart the control system for the steam turbine, the PSS for the steam turbine never became disabled. Facility personnel were unaware that the restart had affected the status of the CT PSSs. Effingham stated this was an unexpected result of restarting the CT control system as it had restarted the control system in the past without disabling the PSS. The TIL from the supplier of the CT control system did not identify the possibility of disabling the PSS upon restart. This noncompliance started on November 13, 2017, when the system restart disabled the PSS, and ended on May 1, 2018, when Effingham returned the PSS to service and notified the TOP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Effingham’s failure to notify the TOP of the change of state of reactive devices could lead to inappropriate voltage-control action by the TOP. However, the CT1 and CT2 automatic voltage regulators remained in automatic controlling voltage during the noncompliance. Effingham also maintained the assigned voltage schedules during the noncompliance. The capacity factors from May 2017 through April 2018 for CT1 and CT2 were 41% and 42% respectively. No harm is known to have occurred. SERC considered Effingham‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Effingham: 1) returned the PSS to service and immediately notified the TOP of the status of the PSS; 2) added verification of the "enabled" status of the PSS to the facility's pre-start checklist as well as each individual unit's start-up checklist. Effingham completes the pre-start checklist for each CT unit start. The checklists are performed independently at different times, and generally by different operators, which adds an additional layer of assurance for the required status; 3) added an electronic operations logging program (ELogger) which requires each 12-hour shift to acknowledge that the PSS is enabled at the beginning of each shift; 4) educated the operators on the event; and To mitigate this noncompliance, Effingham will complete the following mitigation activities by December 31, 2018: 5) add alarms to the control system which will alert the operators to any status change of the PSS.
2018-09-27 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2017017855 | VAR-002-4 | R2 | On June 29, 2017, LGE and KU submitted a Self-Log stating that, as a Generator Operator, it was in noncompliance with VAR-002-4 R2. LGE and KU did not maintain the generator voltage within the assigned voltage schedule at Cane Run Unit 7. On December 14, 2016, a communications card for Cane Run Unit 7 that was located inside a cabinet between the switchyard and the Distributed Control System (DCS) malfunctioned and began sending a stale signal to the plant DCS. On January 13, 2017, LGE and KU took the unit offline for scheduled maintenance. On January 23, 2017, while the unit was still offline, plant personnel noticed that the bus voltage readout was a flat line at 141kV. The stale signal had been indicating that the voltage was within the voltage schedule. An investigation of the equipment between the switchyard and the DCS identified that a red LED light was on for one of the communications cards, indicating an error. The red LED was enclosed in a cabinet that houses the communication card and was not immediately detectable by plant personnel. Following an inspection, LGE and KU rebooted the communications card, at which time the LED light switched from red to green, indicating proper functioning. The DCS bus voltage readout immediately displayed the correct voltage signal from the 138kV bus. LGE and KU determined that as a result of the communications card failure, the Cane Run Plant Bus A voltage was outside of the voltage schedule tolerance band for a total of 104 hours between the period of December 17, 2016 and January 3, 2017. The voltage excursions ranged between 0.52 and 1.44 kV above the tolerance band. The primary cause of the noncompliance was an issue with the communication card providing the voltage signal to the DCS and a lack of an internal control to detect the stale voltage signal. This noncompliance started on December 14, 2016, when a communications card for Cane Run Unit 7 that was located in a cabinet between the switchyard and the DCS malfunctioned and began sending a stale signal to the plant DCS that resulted in excursions from the voltage schedule, and ended on January 13, 2017, when LGE and KU took Cane Run Unit 7 offline and ended the excursions from the voltage schedule. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LGE and KU’s failure to maintain the assigned voltage schedule could result in equipment damage or insufficient reactive resource for reliable system operation. LGE and KU’s Transmission Operations was monitoring the system during the period the voltage excursions occurred and could have implemented several options if the voltage at the bus was causing any issues on the transmission system. However, there was no identified need to implement any of those options. LGE and KU’s Transmission Operations reviewed system operations for the periods the voltage excursions occurred and found there were no impacts on the Transmission system. In addition, the LGE and KU EMS receives its signal from a different communication path whose elements were working properly. Cane Run Unit 7 has an alarm for both the EMS, which alarms to the Transmission Operator (TOP) at the transmission control center, and the DCS, which alarms to the GOP at the plant control room. Transmission Operations was receiving a live, accurate reading from the EMS and the EMS was alarming when out of schedule; however, because the voltage was not impacting reliability of the system, no action was necessary by the TOP. The DCS was not receiving a live reading and therefore did not trigger an out of schedule alarm to the GOP. The minimum total available generation during the noncompliance was 7,271 MWs; Cane Run Unit 7 is approximately 696 MWs gross. No harm is known to have occurred. SERC determined that LGE and KU‘s VAR-002 compliance history should not serve as a basis for applying a penalty. LGE and KU’s relevant noncompliance with VAR-002 included SERC200800209, SERC200900423, SERC201000578, SERC2012011080, and SERC2015014780. The instant noncompliance impacted a single unit and was caused by an equipment failure that resulted in a stale signal to the DCS that indicated Cane Run Unit 7 was operating within the voltage schedule. In addition, an error light on the communication card was not visible to plant personnel. The mitigation activities for the prior noncompliances focused on ensuring alarms for voltage schedule excursions would be visible to plant operators via the DCS, and thus would not have prevented the instant noncompliance. | To mitigate this noncompliance, LGE and KU: 1) rebooted the communications card; 2) conducted a survey that consisted of making inquiry of all plant personnel across entire fleet about communication paths to determine if a similar scenario could occur at the other plants; 3) updated the monthly VAR-002 audit procedure to a include review of constant bus voltage in plant bus voltage. The monthly VAR-002 audit is a detective internal control that consists of reviewing the prior month’s bus voltage readings. LGE and KU researches voltage readings that are out of band to determine any VAR-002 impact. Prior to the potential violation, the objective of the audit was to identify and research the out of band voltage readings. The potential violation expanded the objective of the monthly VAR-002 audit to identify and research stagnant voltage readings; 4) used the updated VAR-002 Audit procedures to review plant records for the three months prior to beginning date of the violation to determine if issue previously existed. LGE and KU selected three months because it was a reasonable amount of time to detect any prior occurrences. LGE and KU would have extended the review period had additional problems been identified; 5) developed Generation Compliance Alarm Testing procedures. The procedures include stale plant bus voltage signal monitors; 6) trained designated plant personnel on the VAR-002 Generation Compliance Alarm Testing procedures; 7) tested all VAR-002 alarms fleet wide to ensure all are functioning properly; 8) reviewed preliminary bus voltage signal monitor results to determine whether the communications and/or DCS logic configurations at any plants need modifications. The basis for modifying the logic configuration would have been a “failed” (test did not result in an instantaneous alarm); 9) reviewed plant drawings and discuss communications paths with plant personnel; and 10) tested stale plant bus voltage signal monitors fleet-wide to ensure that failure at any point on the data path will initiate an alarm.
2018-09-27 | SERC Reliability Corporation (SERC) | Mobile Energy L L C (Mobile) | NCR11482 | SERC2017018904 | MOD-032-1 | R2 | On December 26, 2017, Mobile submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-032-1 R2. Mobile did not provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) according to the data requirements and reporting procedures developed by its TP and PC in Requirement R1 or a written confirmation that the data has not changed. On June 30, 2016, Mobile received an email from its TP and PC providing the TP and PC MOD-032 process. For data that has not changed since the last submission, this process required the GO to submit a written confirmation to the TP and PC stating that the data has not changed. The GO must submit the notification between October 1st and November 1st of each year. On September 19, 2017, during an internal review of the MOD-032 requirements and documentation for a third-party gap analysis, Mobile determined that it did not have evidence of a notification to its TP and PC in the October to November 2016 timeframe. Mobile verified with its TP and PC that Mobile did not provide notification to the TP and PC. Mobile determined the primary cause of the noncompliance was lack of sufficient training and failure to adequately track the MOD-032 submission requirements. This noncompliance started on November 1, 2016, when Mobile missed the modeling data submission date, and ended on October 2, 2017, when Mobile submitted the required information to its TP and PC. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Mobile’s failure to provide modeling data could result in the TP and PC incorrectly modeling the Mobile facility’s capabilities. However, the Mobile facility’s capabilities had not changed since the prior data submission. Therefore, the data previously provided to and used by the TP and PC in models was accurate. Mobile is a 232 MW facility that operated at a capacity factor of 37% for the 12 months ending June 30, 2017. No harm is known to have occurred. SERC considered Mobile‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Mobile: 1) provided a confirmation of no changes on October 2, 2017 to its Transmission Planner and Planning Coordinator; 2) created a reminder in its Monthly NERC PM stating the annual period data is requested by the Transmission Planner/Planning Coordinator; and 3) perform supplemental training on the noncompliance for the operating staff involved with verifying the generator’s modeling data.
2018-09-27 | SERC Reliability Corporation (SERC) | Santa Rosa Energy Center, LLC (SREC) | NCR11483 | SERC2017018905 | MOD-032-1 | R2 | On December 26, 2017, SREC submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-032-1 R2. SREC did not provide steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) according to the data requirements and reporting procedures developed by its TP and PC in Requirement R1 or a written confirmation that the data has not changed. On June 30, 2016, SREC received an email from its TP and PC providing the TP and PC MOD-032 process. For data that has not changed since the last submission, this process required the GO to submit a written confirmation to the TP and PC stating that the data has not changed. The GO must submit the notification between October 1st and November 1st of each year. On September 19, 2017, during an internal review of the MOD-032 requirements and documentation for a third-party gap analysis, SREC determined that it did not have evidence of a notification to its TP and PC in the October to November 2016 timeframe. SREC verified with its TP and PC that SREC did not provide notification to the TP and PC. SREC determined the primary cause of the noncompliance was lack of sufficient training and failure to adequately track the MOD-032 submission requirements. This noncompliance started on November 1, 2016, when SREC missed the modeling data submission date, and ended on October 2, 2017, when SREC submitted the required information to its TP and PC. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SREC’s failure to provide modeling data could result in the TP and PC incorrectly modeling the SREC facility’s capabilities. However, the SREC facility’s capabilities had not changed since the prior data submission. Therefore, the data previously provided to and used by the TP and PC in models was accurate. SREC is a 236 MW facility that operated at a capacity factor of 51% for the 12 months ending June 30, 2017. No harm is known to have occurred. SERC considered SREC‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SREC: 1) provided a confirmation of no changes on October 2, 2017 to its Transmission Planner and Planning Coordinator; 2) created a reminder in its Monthly NERC PM stating the annual period data is requested by the Transmission Planner/Planning Coordinator; and 3) perform supplemental training on the noncompliance for the operating staff involved with verifying the generator’s modeling data.
2018-09-27 | Texas Reliability Entity (Texas RE) | Electric Transmission Texas, LLC (ETT) | NCR10211 | TRE2017018444 | MOD-026-1 | R6 | On October 6, 2017, ETT submitted a Self-Report stating that, as a Transmission Planner (TP), ETT was in noncompliance with MOD-026-1 R6. Specifically, ETT failed to provide a written response to two Generator Owners (GOs) within 90 calendar days of receiving verified excitation control system or plant volt/var control function model information, stating that the models are usable or not usable. On February 28, 2017, ETT received two GOs’ functional models for six units. As a result, ETT should have provided a written response to the GOs regarding the usability of the models by May 29, 2017, the 90-calendar day deadline for responses pursuant to MOD-026-1 R6. However, ETT did not provide its written response until June 9, 2017. The root cause of the noncompliance was that ETT had an insufficient process to ensure compliance with MOD-026-1 R6. In particular, ETT did not have a sufficient process in place to properly track deadlines pertaining to MOD-026-1. When this issue occurred, ETT was using a manual process for compliance with MOD-026-1 R6. ETT determined that the manual process was not sufficient to ensure compliance with MOD-026-1 R6 and was in the process of transitioning to a new automated system to better track submissions and response deadlines. When ETT began utilizing the new tool in late March of 2017, the two submissions at issue were not entered into the new system and were not being tracked. As a result, ETT missed the deadline to respond to the February 28, 2017 submissions. The issue was discovered when the GOs at issue contacted ETT to ask about the status of the February 28, 2017 submissions. This noncompliance started on May 30, 2017, the day after the written response was due to the GOs, and ended on June 9, 2017, when ETT provided a written response to the GOs stating that the models were usable. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to adequately review and correct models could result in the use of inaccurate modeling information in system planning. However, the risk was reduced by the following factors. First, ETT determined that the information provided by the GOs was usable and did not require modification, reducing the risk that inaccurate information would be used in system planning. Second, the duration of the noncompliance was short, lasting less than two weeks. No harm is known to have occurred. Texas RE considered ETT’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETT: 1) provided a written response to the GOs stating that the models were usable; 2) implemented an automated tracking tool for compliance with MOD-026-1 that utilizes dedicated tracking software to track submissions, track response deadlines, and send bi-weekly internal notifications; 3) created a document detailing the tracking tool process for compliance with MOD-026-1; and 4) established a monthly task for ETT personnel to manually review and confirm that submissions are included in the tracking tool. Texas RE has verified the completion of all mitigation activity.
2018-09-27 | Texas Reliability Entity (Texas RE) | Electric Transmission Texas, LLC (ETT) | NCR10211 | TRE2017018445 | MOD-027-1 | R5 | On October 6, 2017, ETT submitted a Self-Report stating that, as a Transmission Planner (TP), ETT was in noncompliance with MOD-027-1 R5. Specifically, ETT failed to provide a written response to two Generator Owners (GOs) within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information, stating that the models are usable or not usable. On February 28, 2017, ETT received two GOs’ functional model for four units. As a result, ETT should have provided a written response to the GO regarding the usability of the model by May 29, 2017, the 90-calendar day deadline for responses pursuant to MOD-027-1 R5. However, ETT did not provide its written response until June 9, 2017. The root cause of the noncompliance was that ETT had an insufficient process to ensure compliance with MOD-027-1 R5. In particular, ETT did not have a sufficient process in place to properly track deadlines pertaining to MOD-027-1. When this issue occurred, ETT was using a manual process for compliance with MOD-027-1 R5. ETT determined that the manual process was not sufficient to ensure compliance with MOD-027-1 R5 and was in the process of transitioning to a new automated system to better track submissions and response deadlines. When ETT began utilizing the new tool in late March of 2017, the two submissions at issue were not entered into the new system and were not being tracked. As a result, ETT missed the deadline to respond to the February 28, 2017 submissions. The issue was discovered when the GOs at issue contacted ETT to ask about the status of the February 28, 2017 submissions. This noncompliance started on May 30, 2017, the day after the written response was due to the GO, and ended on June 9, 2017, when ETT provided a written response to the GO stating that the model was usable. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to adequately review and correct models could result in the use of inaccurate modeling information in system planning. However, the risk was reduced by the following factors. First, ETT determined that the information provided by the GO was usable and did not require modification, reducing the risk that inaccurate information would be used in system planning. Second, the duration of the noncompliance was short, lasting less than two weeks. No harm is known to have occurred. Texas RE considered ETT’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETT: 1) provided a written response to the GO stating that the model was usable; 2) implemented an automated tracking tool for compliance with MOD-027-1 that utilizes dedicated tracking software to monitor submissions, track response deadlines, and send bi-weekly notifications; 3) created a document detailing the tracking process for compliance with MOD-026-1; and 4) established a monthly task for ETT personnel to manually review and confirm that submissions are included in the tracking tool. Texas RE has verified the completion of all mitigation activity.
2018-09-27 | Texas Reliability Entity (Texas RE) | Rattlesnake Wind I LLC (RSWILLC) | NCR11547 | TRE2018019449 | PRC-004-5(i) | R1 | During a Compliance Audit conducted from February 6, 2018 through March 29, 2018, Texas RE determined that RSWILLC, as a Generator Owner (GO), was in noncompliance with PRC-004-5(i) R1. Specifically, RSWILLC failed to identify whether its Protection System components caused a Misoperation within 120 calendar days of a BES interrupting device operation. Therefore, RSWILLC discovered this issue as a result of a Compliance Audit. On March 28, 2017, a BES interrupting device owned by RSWILLC operated at 7:50 p.m. RSWILLC’s logs demonstrate that within five minutes of the BES interrupting device operation it contacted both the Electric Reliability Council of Texas (ERCOT) and its Transmission Planner. The Transmission Planner is a joint owner, with RSWILLC, of the Composite Protection System that caused the operation of the BES interruption device. Pursuant to PRC-004-5(i) R1 RSWILLC was required to identify whether the Protection System components at issue caused a Misoperation within 120 calendar days, by July 26, 2017. However, RSWILLC failed to perform the required analysis until March 6, 2018. The root cause of the noncompliance was that RSWILLC had an insufficient process for compliance with PRC-004-5(i) R1. RSWILLC’s written process required a determination of whether its Protection System caused the BES interrupting device operation; but, the written process did not require a determination of whether a Misoperation occurred within 120 calendar days of a BES interrupting device operation. Additionally, RSWILLC personnel did not follow its documented process for investigating BES interrupting device operations. Specifically, RSWILLC did not timely identify whether its Protection System device caused the BES interrupting device operation. This noncompliance started on July 27, 2017, 121 days after the BES interrupting device operation occurred. The noncompliance ended on March 6, 2018, when RSWILLC determined and documented that the Protection System component at issue did not cause a Misoperation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by a failure to timely investigate a BES interrupting device operation is that RSWILLC would not be aware of a Protection System Misoperation and would therefore be unable to remediate the issue. However, RSWILLC performed several actions that reduced the risk of this issue. First, although did RSWILLC did not timely perform a sufficient investigation to identify whether or not a Protection System Misoperation occurred, RSWILLC took immediate steps to determine the cause of the BES interrupting device operation. Specifically, RSWILLC contacted its Transmission Provider and ERCOT to address possible causes of the fault and which entity’s Protection System may have caused the operation of the BES interrupting device. Second, the RSWILLC March 6, 2018 analysis shows that RSWILLC determined that no Misoperation occurred and that its Protection System performed as designed. No harm is known to have occurred. Texas RE considered RSWILLC’s PRC-004 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, RSWILLC: 1) completed the required PRC-004-5(i) R1 misoperation determination; 2) conducted training for impacted personnel regarding compliance with PRC-004-5(i); 3) revised its documented process for compliance with PRC-004-5(i) to specify that within 120 days of an applicable BES interrupting device operation it must identify whether its Protection System component(s) caused a Misoperation; and 4) developed a new form for documenting the investigation of a BES interrupting device operation. Texas RE verified the completion of all mitigation activity.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Gila Bend Operations Company (GBOC) | NCR11372 | WECC2017017685 | PRC-024-2 | R1 | On May 31, 2017, GBOC submitted Self-Reports stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1 and R2. Specifically, GBOC reported that in April 2016, it contracted with a third-party engineer to set the generator voltage protective relaying not to trip the applicable generating units, as required by PRC-024-2 R1 and R2. GBOC owns 12 generating Facilities, arranged in four blocks. Each of the four blocks consists of two combustion turbines and one steam turbine which were applicable to this issue. For R1, the four steam turbines had their frequency relays set correctly but the eight combustion turbines had a transformer frequency protection relay that was set to operate at 58.5 Hz at 15 seconds outside of the “no trip zone.” For R2, two of the relays on each of the four power blocks were not verified according to the requirements of the Standard until November 2016. The third-party engineer submitted a report in September 2016 which failed to confirm that 40 percent of the Protection System devices were verified, according to the requirements of the Standard. In December 2016, the third-party engineer report was edited, testing was completed, and then submitted to GBOC, as required by PRC-024-2 R1, Attachment 1 and R2, Attachment 2. After reviewing all the relevant information, WECC determined that GBOC failed to set its protective relaying such that the generator frequency and voltage protective relaying does not trip the applicable generating units within the "no trip zone", as required by PRC-024-2 R1, Attachment 1 and R2, Attachment 2, for 40 percent of the applicable devices, by the mandatory and enforceable date, July 1, 2016, as set-forth in the implementation plan for version 2 of the Standard. The root cause of the issue was lack of work planning coordination between GBOC departments. GBOC did not correctly interpret the implementation plan and did not instruct the engineering department to complete applicable testing by the due date. WECC determined that this issue began on July 1, 2016, when the Standard became mandatory and enforceable. WECC determined that the end date of this issue is December 19, 2016, when GBOC set its protective relays not to trip the applicable generating units within the "no trip zone" in all its applicable Facilities, for a total of 172 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, GBOC failed to set its protective relaying such that the generator frequency and voltage protective relaying does not trip the applicable generating units within the "no trip zone", as required by PRC-024-2 R1, Attachment 1 and R2, Attachment 2, for 40 percent of the applicable devices, by the mandatory and enforceable date, July 1, 2016, as set-forth in the implementation plan for version 2 of the Standard. Such failure could result in the premature tripping of the generating unit offline due to frequency excursions within the "no trip zone." GBOC owns 12 generating Facilities, arranged in four blocks. Each of the four blocks consists of two combustion turbines and one steam turbine. Each combustion turbine is rated at 170 MW and each steam turbine is rated at 180 MW, giving a total plant capability of 2,080 MW. Each generator has a primary generator protection relay and a backup relay with the same settings for a total of 8 relays. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, the Facilities have generator protection relays with frequency protection enabled. Although redundant, only one frequency protection system relay change was required on eight transformers. In addition, only one voltage protection system setting change was required on eight relays. The voltage relay was set incorrectly to trip at 0.9 pu at 1 second and was adjusted to trip at 5 seconds outside the “no trip zone.” Additionally, GBOC did not have effective internal controls to prevent or detect this issue. Based on this, WECC determined that there was a moderate likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, GBOC: a. set its voltage protective relays not to trip the applicable generating units within the "no trip zone" in all its applicable Facilities. The transformer frequency protection relays in the scope of the issue were deemed excessive and were disabled; b. set its protective relays not to trip the applicable generating units within the "no trip zone" in all its applicable facilities. The voltage relay setting that had been set incorrectly to trip at 0.9 pu at 1 second was adjusted to operate at 0.9 pu at 5 seconds outside the “no trip zone”; c. created a performance document that will be attached to future purchase orders with timelines to ensure that there are no misunderstandings with the selected vendor; and d. established a calendar reminder on managerial and staff calendars to ensure continuous compliance with the Standard.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Gila Bend Operations Company (GBOC) | NCR11372 | WECC2017017686 | PRC-024-2 | R2 | On May 31, 2017, GBOC submitted Self-Reports stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1 and R2. Specifically, GBOC reported that in April 2016, it contracted with a third-party engineer to set the generator voltage protective relaying not to trip the applicable generating units, as required by PRC-024-2 R1 and R2. GBOC owns 12 generating Facilities, arranged in four blocks. Each of the four blocks consists of two combustion turbines and one steam turbine which were applicable to this issue. For R1, the four steam turbines had their frequency relays set correctly but the eight combustion turbines had a transformer frequency protection relay that was set to operate at 58.5 Hz at 15 seconds outside of the “no trip zone.” For R2, two of the relays on each of the four power blocks were not verified according to the requirements of the Standard until November 2016. The third-party engineer submitted a report in September 2016 which failed to confirm that 40 percent of the Protection System devices were verified, according to the requirements of the Standard. In December 2016, the third-party engineer report was edited, testing was completed, and then submitted to GBOC, as required by PRC-024-2 R1, Attachment 1 and R2, Attachment 2. After reviewing all the relevant information, WECC determined that GBOC failed to set its protective relaying such that the generator frequency and voltage protective relaying does not trip the applicable generating units within the "no trip zone", as required by PRC-024-2 R1, Attachment 1 and R2, Attachment 2, for 40 percent of the applicable devices, by the mandatory and enforceable date, July 1, 2016, as set-forth in the implementation plan for version 2 of the Standard. The root cause of the issue was lack of work planning coordination between GBOC departments. GBOC did not correctly interpret the implementation plan and did not instruct the engineering department to complete applicable testing by the due date. WECC determined that this issue began on July 1, 2016, when the Standard became mandatory and enforceable. WECC determined that the end date of this issue is December 19, 2016, when GBOC set its protective relays not to trip the applicable generating units within the "no trip zone" in all its applicable Facilities, for a total of 172 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, GBOC failed to set its protective relaying such that the generator frequency and voltage protective relaying does not trip the applicable generating units within the "no trip zone", as required by PRC-024-2 R1, Attachment 1 and R2, Attachment 2, for 40 percent of the applicable devices, by the mandatory and enforceable date, July 1, 2016, as set-forth in the implementation plan for version 2 of the Standard. Such failure could result in the premature tripping of the generating unit offline due to frequency excursions within the "no trip zone." GBOC owns 12 generating Facilities, arranged in four blocks. Each of the four blocks consists of two combustion turbines and one steam turbine. Each combustion turbine is rated at 170 MW and each steam turbine is rated at 180 MW, giving a total plant capability of 2,080 MW. Each generator has a primary generator protection relay and a backup relay with the same settings for a total of 8 relays. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, the Facilities have generator protection relays with frequency protection enabled. Although redundant, only one frequency protection system relay change was required on eight transformers. In addition, only one voltage protection system setting change was required on eight relays. The voltage relay was set incorrectly to trip at 0.9 pu at 1 second and was adjusted to trip at 5 seconds outside the “no trip zone.” Additionally, GBOC did not have effective internal controls to prevent or detect this issue. Based on this, WECC determined that there was a moderate likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, GBOC: a. set its voltage protective relays not to trip the applicable generating units within the "no trip zone" in all its applicable Facilities. The transformer frequency protection relays in the scope of the issue were deemed excessive and were disabled; b. set its protective relays not to trip the applicable generating units within the "no trip zone" in all its applicable facilities. The voltage relay setting that had been set incorrectly to trip at 0.9 pu at 1 second was adjusted to operate at 0.9 pu at 5 seconds outside the “no trip zone”; c. created a performance document that will be attached to future purchase orders with timelines to ensure that there are no misunderstandings with the selected vendor; and d. established a calendar reminder on managerial and staff calendars to ensure continuous compliance with the Standard.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Gila Bend Operations Company (GBOC) | NCR11372 | WECC2017017687 | MOD-025-2 | R2 | On May 31, 2017, GBOC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Specifically, GBOC reported that it believed that through testing performed for MOD-026 and MOD-027 in March 2016, for the maximum load under and over excitation for 50% of its Facilities (Power Blocks 3 &4), it was also compliant with MOD-025-2 R2. However, it had not performed the Reactive Power verification. On August 31, 2016, GBOC performed the verification of Reactive Power for MOD-025-2 R2.1 and Attachment 1 was completed. Then in September 2016, GBOC submitted the MOD-025-2 R2.2, Attachment 2 forms to its Transmission Planner (TP) but without the minimum load condition. On May 17, 2017 GBOC submitted an updated Attachment 2, including the minimum load conditions for all applicable Facilities, to its TP. GBOC owns 12 generating Facilities, arranged in four blocks. Each of the four block consists of two combustion turbines and one steam turbine. Two of the four blocks were applicable to this issue. After reviewing all relevant information, WECC determined that GBOC failed to verify the Reactive Power Capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 of the Standard and failed to submit a completed Attachment 2 to its TP with the correct load condition as required by MOD-025-2 R2, by the mandatory and enforceable date of July 1, 2016, as set-forth in the implementation plan for version 2 of the Standard. The root cause of the issue was GBOC’s misunderstanding of the Standards. GBOC incorrectly assessed that meeting the requirements for MOD-026 and MOD-027 would satisfy the requirements for MOD-025 R2. WECC determined that this issue began on July 1, 2016, when the Standard became mandatory and enforceable. WECC determined that the end date of this issue is May 17, 2017, when GBOC submitted the updated Attachment 2 to its TP, for a total of 321 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, GBOC failed to verify the Reactive Power Capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 of the Standard and failed to submit a completed Attachment 2 to its TP with the correct load condition, as required by MOD-025-2 R2, by the mandatory and enforceable date of July 1, 2016, as set-forth in the implementation plan for version 2 of the Standard. Such failure could result in inaccurate information used in planning models. The BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, but the generator may not completely mitigate the contingency. GBOC owns 12 generating Facilities, arranged in four blocks. Each of the four blocks consists of two combustion turbines and one steam turbine. Each combustion turbine is rated at 170 MW and each steam turbine is rated at 180 MW, giving a total plant capability of 2,080 MW. However, only two of the four blocks were applicable to this issue. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, as compensating controls, GBOC had verified Real Power capability for 50 percent of the applicable facilities before July 1, 2016 and submitted the data to the TP, but had just not performed Reactive Power verification. Additionally, GBOC did not have effective internal controls to prevent or detect this issue. Based on this, WECC determined there was a moderate likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, GBOC: a. completed the testing required to verify the Reactive Power capability of at least 40 percent of applicable Facilities in accordance with Attachment 1; b. submitted a corrected form containing the same information as identified in Attachment 2 to the Transmission Planner for at least 40 percent of its applicable Facilities, within 90 days of verifying the Reactive Power capability; c. completed the testing required to verify the Reactive Power capability of at least 60 percent of applicable Facilities in accordance with Attachment 1; and d. created a document to clarify the Standard’s requirements for future testing of MOD-025-2. The document will be attached to future purchase orders for vendors performing Real and Reactive Power capability verification for MOD-025.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Arizona Electric Power Cooperative, Inc. (AEPC) | NCR05015 | WECC2017017675 | PRC-002-2 | R1 | On May 30, 2017, AEPC submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-002-2 R1. Specifically, AEPC reported that in 2016, the employee responsible for completing the analysis and steps required for compliance with PRC-002-2 R1 Parts 1.1 and 1.2 did not identify Bulk Electric System (BES) buses for which sequence of events recording (SER) and fault recording (FR) data were required. AEPC did not adequately track the progress of the responsible employee’s compliance tasks and then the responsible employee retired unexpectedly. On March 27, 2017, the new responsible employee discovered it did not have the evidence for completing the analysis associated with PRC-002-2 R1 Part 1.1. The new employee then performed the analysis on the same day and identified two BES Elements requiring SER and FR data. On May 2, 2017, AEPC notified the other owner of the BES Elements connected to the BES buses that those BES Elements require SER data and/or FR data, as required by Part 1.2, within 90 days of completing Part 1.1. After reviewing all relevant information, WECC determined that AEPC failed to perform the tasks and analysis necessary to identify BES buses for which SER and FR data is required by using the methodology in PRC-002-2 R1 Attachment 1, as required by Part 1.1. The root cause of the issue was due to lack a of progress tracking to ensure completion of the compliance tasks and analysis associated with the Standard. WECC determined that this issue began on July 1, 2016, when AEPC failed to perform the tasks and analysis for BES buses for which SER and FR data is required for compliance with PRC-002-2 R1 Part 1.1. WECC determined that the end date of this issue is March 27, 2017 when AEPC completed the methodology outlined in Attachment 1, for a total of 270 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AEPC failed to perform the tasks and analysis necessary to identify BES buses for which SER and FR data is required by using the methodology in PRC-002-2 R1 Attachment 1, as required by Part 1.1. Such failure could result in having inadequate data available to facilitate analysis of BPS Disturbances and implement changes that could reduce the likelihood of a similar event from occurring. This could potentially lead to loss of BPS elements. AEPC owns over 500 miles of BES transmission lines and 640 MW of BES generation capacity. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as negligible. However, APEC also conducts quarterly standards and compliance meetings to discuss upcoming standards that will be implemented in the coming months and any changes or impact they may have. In this instance, the SER and FR data recorded would be used to facilitate analysis post disturbance and used for long-term planning so immediate impacts to the BPS are significantly reduced. Based on this, WECC determined that there was a remote likelihood of causing negligible harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, AEPC: a. completed the analysis as described in Attachment 1 of the Standard to identify BES buses that require SER and/or FR data; b. created an internal process document for ensuring compliance with Standard; c. established periodic emails sent to the subject matter experts to ensure they have reviewed and are aware of their assignments and responsibilities for each standard; and d. created calendar reminder to prevent potential issue.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2018018911 | EOP-005-2 | R2 | On December 27, 2017, AZPS submitted a Self-Report stating that, as a Transmission Operator, (TOP) it was in noncompliance with EOP-005-2 R2. Specifically, AZPS reported that on June 21, 2017, the Reliability Coordinator (RC) approved an updated AZPS restoration plan with an effective date of July 1, 2017. On November 9, 2017, while conducting an internal assessment of AZPS's compliance with NERC standard EOP-005-2, as part of its annual internal self-certification program, AZPS discovered that the latest version of its restoration plan was not available to its System Operators. Additionally, on November 14, 2017, as part of its review of the issues identified on November 9, 2017, AZPS identified that the RC approved restoration plan was not provided to entities identified therein until July 24, 2017. As specific tasks had changed for four of the nine entities in the approved July 1, 2017 restoration plan, the plan should have been provided to these entities prior to the effective date of the updated plan. Changes to entity tasks included delineation of TOP and GOP tasks for entities from which AZPS is contracting Blackstart Resources, a change in the bus that one entity must energize, and the retirement of one entity's role from the plan. After reviewing all relevant information, WECC determined that AZPS failed to provide copies of its approved restoration plan with a description of any changes to their roles and specific tasks to each of the entities identified in the plan, prior to the effective date of the updated plan. The root cause of this issue was due to change related training and/or retraining not performed or not adequate. Specifically, the Lead System Operator responsibilities were not adequately transitioned to the new incoming System Operator before pending retirement. As such, there was a lack of knowledge on what was expected in the new role. WECC determined that this issue began on July 1, 2017, when AZPS failed to provide copies of its approved restoration plan to each of the entities identified in the plan as required by EOP-005-2 R2. WECC determined that the end date of this issue is July 24, 2017, when AZPS provided the entities identified in its RC approved restoration plan a copy of the plan, for a total of 23 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AZPS failed to provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the updated plan. Such failure could result in either ineffective or prolonged restoration activities as four entities involved would not be aware of their new roles relating to system restoration. AZPS is a large Balancing Authority (BA) and TOP with a diverse geography and a system peak load of 4,922 MW. AZPS owns 6,258 MW and has 11,831 MW of generation within its BA footprint. Additionally, AZPS owns and operates 2,937 miles (including 1,413 miles of 525kV, 578 miles of 345kV, and 787 miles of 230kV) of transmission lines. Therefore, WECC assessed the potential harm to the reliability and security of the BPS as intermediate. However, AZPS provides annual training to its System Operators as required under EOP-005-2, R10 and ensures its System Operators participate in the RC’s annual restoration drill. As part of this restoration training, the entity's System Operators are trained on restoration principles and strategies so they are equipped to restore the system if the restoration plan cannot be executed as expected. Based on this, WECC determined that there was a low likelihood of causing intermediate harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, AZPS: a. AZPS has provided the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks; b. implemented a time-based control to ensure AZPS's annual approved restoration plan is provided to the entities with identified roles and specific tasks prior to the implementation date of its plan; c. updated APS System Restoration Plan Update Procedure to clarify which entities shall receive a copy of the updated restoration plan and the timeline within which it must be provided. WECC verified AZPS’s mitigating activities.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2018018912 | EOP-005-2 | R5 | On December 27, 2017, AZPS submitted a Self-Report stating that, as a Transmission Operator, (TOP) it was in noncompliance with EOP-005-2 R5. Specifically, AZPS reported that on June 21, 2017, the RC approved an updated AZPS restoration plan with an effective date of July 1, 2017. On November 9, 2017, while conducting an annual internal self-certification program, AZPS discovered that the latest version of the restoration plan was not available to System Operators within its primary and backup control rooms. AZPS immediately ordered two hard copies of the restoration plan on the same day from the AZPS print shop, and on November 17, 2017, placed the hard copies of the approved July 1, 2017 restoration plan in the AZPS primary and backup control rooms. After reviewing all relevant information, WECC determined that AZPS failed to have a copy of its latest RC approved restoration plan within its primary and backup control rooms prior to the effective date of the updated plan, as required by EOP-005-2 R5. The root cause of this issue was due to change related training / retraining not performed or not adequate. Specifically, the Lead System Operator responsibilities were not adequately transitioned to the new incoming System Operator before pending retirement. As such, there was a lack of knowledge on what was expected in the new role. WECC determined that this issue began on July 1, 2017, when AZPS failed to have a copy of its latest RC approved restoration plan within its primary and backup control rooms prior to the effective date of the updated plan. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AZPS failed to provide the entities identified in its approved restoration plan with a description of any changes to their roles and specific tasks prior to the effective date of the updated plan. Such failure could result in either ineffective or prolonged restoration activities as four entities involved would not be aware of their new roles relating to system restoration. AZPS is a large Balancing Authority (BA) and TOP with a diverse geography and a system peak load of 4,922 MW. AZPS owns 6,258 MW and has 11,831 MW of generation within its BA footprint. Additionally, AZPS owns and operates 2,937 miles (including 1,413 miles of 525kV, 578 miles of 345kV, and 787 miles of 230kV) of transmission lines. Therefore, WECC assessed the potential harm to the reliability and security of the BPS as intermediate. However, AZPS provides annual training to its System Operators as required under EOP-005-2, R10 and ensures its System Operators participate in the RC’s annual restoration drill. As part of this restoration training, the entity's System Operators are trained on restoration principles and strategies so they are equipped to restore the system if the restoration plan cannot be executed as expected. Based on this, WECC determined that there was a low likelihood of causing intermediate harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, AZPS: a. uploaded a copy of AZPS's 2017 restoration plan to AZPS's internal Transmission Operations SharePoint site; b. printed and delivered hard copies of AZPS's 2017 restoration plan to the primary and back-up control centers; c. Implemented a time-based control to ensure AZPS's annual approved restoration plan is uploaded to its Transmission Operators Share Point site and to place hard copies in its primary and back-up control centers; and d. updated AZPS System Restoration Plan Update Procedure to clarify the relevant time-based requirements.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC2017018317 | PRC-024-2 | R1 | On September 11, 2017, AVGO submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-024-2 R1. Specifically, AVGO reported that on July 20, 2017 it discovered that during the processing of a previous Self-Report (WECC2016016544), the scope of the violation was limited to three out of four over-frequency protection relays for each of three units (two combustions, one steam) at a 580 MW combined cycle generation plant. The mitigation plan was accepted by WECC based on the initial scope. WECC then issued a CE for the issue. However, when evidence of mitigation completion was submitted to WECC, the fourth over-frequency protection relay, for each unit, was added to the scope of the original issue, even though WECC had already issued the CE. Thus, AVGO submitted a new Self-Report to capture the additional over-frequency protection relay setting issue and associated mitigation. The over-frequency relay setting was 61.6 Hz with a 15 second time delay as opposed to a required 30 second time delay. After reviewing all relevant information, WECC determined that AVGO failed to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units with the “no trip zone” in the fourth over-frequency protection relay for each of three units of AVGOs combined cycle generation plant. The root cause of the issue was due to a lack of clarity in communication. The original engineering assessment report did indicate the relay settings in question needed to be modified, but did not clearly indicate noncompliance, therefore the devices were not included in the scope of the original Self-Report. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of AVGO’s applicable Facilities, and ended on March 8, 2017, when AVGO set its frequency protective relaying in accordance with Attachments 1, for a total of 250 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AVGO failed to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units with the “no trip zone” in the fourth over-frequency protection relay for each of three units of AVGOs combined cycle generation plant. Such failure could potentially result in the premature tripping of one or more generating units offline due to frequency excursions within the "no trip zone". AVGO is a single combined cycle generation plant consisting of two combustion units and one steam unit with a combined capacity of 580 MW. There was one over frequency relay set to trip at 61.6 Hz at 15 seconds that was reset to trip at 30 seconds. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, for this instance, the additional scope of over-frequency protection relays was modified to have their settings to be compliant during the mitigation of the previous Self-Report (WECC2016016544). Based on this, WECC determined that there was a remote likelihood of causing minor harm to the BPS. No harm is known to have occurred | To mitigate this noncompliance, AVGO: a. determined the appropriate settings for the protective relays in scope and implemented all recommended settings changes on all units during a scheduled outage; b. created preventative maintenance assignments in their computer maintenance management system to generate notification reminders for annual reviews of settings changes during the past year and to verify that those settings have not impacted any Reliability Standards coordination; and c. created preventative maintenance assignments in its computer maintenance management system to generate notification reminders for 5-year interval PRC-024 specific compliance studies.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Blythe Energy Inc. (BLYT) | NCR11433 | WECC2018019290 | PRC-005-6 | R3 | On February 23, 2018, BLYT submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R3. Specifically, BLYT reported that it missed the six-month interval testing requirements for three of its Protection System ohmic batteries in accordance with minimum maintenance and maximum maintenance interval prescribed within PRC-005-6 R3, Table 1-4(b). The testing was due October 31, 2017, six months after the previous test in April 2017. BLYT had previously conducted the testing concurrent with planned outages. The planned outage that was scheduled to coincide with the six-month interval ohmic battery testing in October 2017 was delayed, causing the ohmic battery testing to be scheduled outside of the six-month interval. The generating Facility that BLYT owns and operates is rated at 520 MVA. The batteries provide DC supply to elements of the protection system for their respective generating units. After reviewing all relevant information, WECC determined that BLYT failed to maintain its Protection System ohmic batteries that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance interval prescribed within PRC-005-6 R3, Table 1-4(b). The root cause of the issue was less than adequate controls for scoping and scheduling. Specifically, BLYT incorrectly assessed that the testing for its batteries should coincide with planned outages and had not implemented an independent procedure that reflected the time-based maintenance program associated with the requirements of the Standard. WECC determined that this issue began on October 31, 2017, the seventh month after BLYT failed to complete the six-month internal ohmic testing on three Protection System ohmic batteries. WECC determined that the end date of this issue is November 11, 2017, when BLYT completed internal ohmic tests on three Protection System ohmic batteries, for a total of 12 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, BLYT failed to maintain its Protection System ohmic batteries that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance interval prescribed within PRC-005-6 R3, Table 1-4(b). Such failure could result in local service interruption, considerable damage to Generation equipment and loss of ability to provide peaking support. The generating Facility that this entity owns and operates is rated 520 MVA. The three Protection System batteries provide DC supply to elements of the protection system for their respective Generating Units. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, BLYT did not have effective internal controls to prevent or detect this issue. Based on this, WECC determined that there was a moderate likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, BLYT: a. completed six-month internal ohmic tests on three of its batteries; b. implemented a Compliance Tracker as an internal control which will send reminder emails to the Compliance Manager and Maintenance Personnel for all required battery maintenance and testing, assuring that the maintenance and testing will be performed on schedule; and c. sent a clarifying email informing personnel that maintenance and testing are due by the end of the sixth month after the last test, without regard to the schedule of planned outages. The email included an explanation of the compliance tracker that will generate an email notification to the Maintenance Manager, Compliance Manager and Electrical personnel when a scheduled task is scheduled to start.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Gila Bend Operations Company (GBOC) | NCR11372 | WECC2017017684 | PRC-019-2 | R1 | On May 31, 2017, GBOC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, GBOC reported that in April 2016, it contracted with a third-party engineer to perform the necessary coordination studies to verify relay voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices and setting verification, as required by PRC-019-2 R1. On September 23, 2016, the third-party engineer submitted its field work report to GBOC. The report was not reviewed to ensure that GBOC had been in compliance with the Standard by the enforceable date of July 1, 2016. In April 2017, a new GBOC employee discovered there was no evidence prior to the report issued September 23, 2016 to demonstrate that 40 percent of the Protection System devices were verified, as required by PRC-019-2 R1, by the mandatory and enforceable date, July 1, 2016, as set-forth in the implementation plan for version 2 of the Standard. GBOC owns 12 generating Facilities, arranged in four blocks. Each block consists of two combustion turbines and one steam turbine. Only two of the four blocks were applicable to this issue. After reviewing all relevant information, WECC determined that GBOC failed to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions in at least 40 percent of its applicable Facilities, as required by PRC-019-2 R1 and its sub requirements, as set-forth in the implementation plan for version 2 of the Standard by the enforceable date of the Standard. The root cause of the issue was lack of work planning coordination between relevant GBOC departments. GBOC did not correctly interpret the implementation plan and did not instruct its engineering department to complete applicable testing by the due date. WECC determined that this issue began on July 1, 2016, when the Standard became mandatory and enforceable for 40 percent of the applicable Facilities. WECC determined that the end date of this issue is September 23, 2016, when GBOC coordinated the voltage regulating system with its generator capabilities and Protection System devices for at least 40 percent of its applicable Facilities, for a total of 85 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, GBOC failed to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions in at least 40 percent of its applicable Facilities, as required by PRC-019-2 R1, and its sub requirements, as set-forth in the implementation plan for version 2 of the Standard. Such failure could result in an inadvertent generator trip during a system event. GBOC consists of 12 generating facilities, arranged in 4 blocks. Each block consists of 2 combustion turbines and one steam turbine. Each combustion turbine is rated at 170 MW and each steam turbine is rated at 180 MW, giving a total plant capability of 2,080 MW. As GBOC coordinated and established the in-service limiters and Protection Systems, it determined that no settings changes were needed. The voltage regulating system control settings had been set correctly. In addition, each generator has an under-excitation limiter (UEL) and an SEL-300G relay for protection. In addition, only two of the four blocks were applicable to this issue. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, GBOC did not have effective internal controls to prevent or detect this issue. Based on this, WECC determined that there was a moderate likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, GBOC: a. coordinated the voltage regulating system with its generator capabilities and Protection System devices in all its applicable facilities; b. created a performance document that will be attached to future purchase orders with timelines to ensure that there are no misunderstandings with the selected vendor; and c. established a calendar reminder on managerial and staff calendars to ensure future 5-year coordination intervals are met.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Mt. Poso Cogeneration Co. (MTPO) | NCR05254 | WECC2017018892 | PRC-024-2 | R2 | On December 22, 2017, MTPO submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Specifically, MTPO reported that on October 5, 2017, it contracted with a third-party Engineering firm to conduct testing to verify compliance with PRC-024-2 as well as MOD-025-2, PRC-019-2, PRC-024-2, and PRC-025-1. On December 20, 2017 MTPO received the test results which indicated that 27 generator protection under-voltage protection relay settings did not meet the requirements of PRC-024-2, Attachment 2. MTPO contracted with another third-party contractor to modify the settings during the next scheduled outage on February 15, 2018. MTPO owns and operates a 63.3 MVA Biomass plant with the associated generator protection under-voltage protection relays, subject to this issue. After reviewing all relevant information, WECC determined that MTPO failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit as a result of a voltage excursion (at the point of interconnection) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024-2 R2, Attachment 2. The root cause of the issue was less than adequate follow-up by MTPO with its third-party Engineering firm. MTPO did not confirm that the original work of its third-party contractors met the protective relaying requirements of PRC-024-2 R2, Attachment 2. WECC determined that this issue began on July 1, 2016, when MTPO failed to have its under voltage protective relays set consistent with the requirements of PRC 024-2 R2, Attachment 2. WECC determined that the end date of this issue was February 15, 2018, when a third-party contractor modified the under voltage protective relays settings during a scheduled generator outage, for a total of 595 days of noncompliance. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, MTPO failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit as a result of a voltage excursion (at the point of interconnection) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024-2 R2, Attachment 2. Such failure could result in the premature tripping of one or more generating units offline due to voltage excursions within the “no trip zone.” If the Facility had experienced a frequency or voltage excursion, its settings would trip the generator at 1 second for .9pu instead of 3 or more seconds. The relay’s instantaneous trip would also trip the generator early for .4pu. A potentially early trip of the generator could affect the reliability of the BPS. The 27 generator protection under-voltage Alstom MiCOM P343 relays are for a 63.3 MVA Biomass plant that are subject to this instance. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as negligible. However, MTPO had weak controls in place to prevent or detect the noncompliance timely. Based on this, WECC determined that there was a moderate likelihood of causing negligible harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, MTPO: a. tested and reset the under-voltage protection relay settings to disable the generator; b. reported changes made to the under-voltage protection relay settings and that the generator had been disabled; and c. developed a task in MTPO’s regulatory tracking program to review all relay settings completed by MTPO and third-party contractors in accordance with PRC-018-1, PRC-019-2, PRC-023-4 and PRC-024-2 to be completed by the relevant Subject Matter Experts to ensure compliance.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Nevada Irrigation District (NID) | NCR11469 | WECC2017018398 | PRC-019-2 | R1 | On September 27, 2017, NID submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-019-2 R1. Specifically, NID reported that it scheduled PRC-019-2 verification activities for R1.1.1 for one 25 MW hydroelectric generation Facility with a third-party contractor, to be completed in April 2017. Verifying the in-service limiters of this Facility would ensure that NID was compliant with the PRC-019-2 implementation plan expectations of 60 percent of applicable Facilities verified by July 1. However, the contractor was unable to complete the entire verification. They could not verify that the under-excitation limiter (UEL) curve was above the stator limiting curve and protective trip elements so that it would operate before the Protection System at the Facility in scope, in order to avoid disconnecting the generator unnecessarily. Unfortunately, the UEL could not be verified due to insufficient documentation provided by NID to the contractor. All other limiters of the Facility were able to be verified, as required by PRC-019 R1.1.1. After reviewing all relevant information, WECC determined that NID failed to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions, for 60 percent of its applicable Facilities, as stated in the implementation plan for version 2 of the Standard, when it was unable to verify the in-service limiters were set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily, as required byPRC-019-2 R1.1.1. The root cause of the noncompliance was due to NID not scheduling its compliance activities far enough in advance. Specifically, when NID discovered it needed to replace an excitation system in order to implement the required settings in PRC-019, NID did not have enough time to get everything done prior to the 60 percent implementation plan expectation of PRC-019-2. WECC determined that this issue began on July 1, 2017, when implementation of PRC-019-2 became mandatory and enforceable for 60 percent of NID’s applicable Facilities, and ended November 27, 2017, when NID verified the settings on applicable Facilities in accordance with the expectations described in R1.1.1, for a total of 149 days of noncompliance | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, NID failed to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions, for 60 percent of its applicable Facilities, as stated in the implementation plan for version 2 of the Standard, when it was unable to verify the in-service limiters were set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily, as required byPRC-019-2 R1.1.1. This could result in the facility being disconnected prematurely from the BES. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as negligible. However, this single 25 MW capacity hydroelectric generation Facility serves no load and is in an area with significant generation resources. This Facility is barely over the NERC registration criteria and has been operated since 1965 with no events or disturbances caused by UEL. Based on the controls analyzed and the nature of the violation, WECC determined that there was a remote likelihood of causing negligible harm to the BPS. No harm is known to have occurred | To mitigate this noncompliance, NID: a. replaced and upgraded the Facilities excitation system. This outage was completed in October of 2017. Following the outage, NID re-contracted the same engineering firm to re-perform the PRC-019 analysis, and verify that the in-service limiters were set to operate before the Protection System at the Facility in order to avoid disconnecting the generator unnecessarily; and b. created a master compliance calendar that highlights upcoming enforcement dates and Standard revisions so that the necessary compliance activities can be acted upon well in advance of critical compliance dates, which is utilized by the Reliability Oversight Compliance Committee during its quarterly meeting
2018-09-27 | Western Electricity Coordinating Council (WECC) | New Harquahala Generating Company, LLC (HGMA) | NCR05263 | WECC2017018356 | PRC-005-1b | R2 | On September 13, 2017, HGMA submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC 005-1b R2. Specifically, HGMA reported that during an internal compliance review on November 1, 2016 for one generating station it acquired from another entity, it identified missing maintenance and testing records for 27 protection system devices. The missing maintenance and testing records are from the period of June 18, 2012 to November 1, 2016. The 27 Protection System devices account for 2.4 percent of the 1,113 devices subject to this instance and the requirements of PRC 005-1b R2. After reviewing all relevant information, WECC determined that HGMA failed to implement its Protection System maintenance and testing program and maintain evidence of the implementation of that program for 27 Protection System devices, as required by PRC-005-1b R2 and its sub requirement 2.1. The root cause of the issue was due to improperly tracking the Protection System maintenance and testing evidence. Additional contributing causes include, staff turnover and a change in ownership at the plant. WECC determined that this issue began on June 18, 2012, for 27 Protection System devices. WECC determined that the end date of this issue was August 15, 2017 when HGMA implemented it Protection System maintenance and testing program for the 27 Protection System devices and completed maintenance testing, for a total of 1885 days of issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, HGMA failed to implement its Protection System maintenance and testing program and maintain evidence of the implementation of that program for 27 Protection System devices, as required by PRC-005-1b R2 and its sub requirement 2.1. Such failure could lead to the Protection System devices not operating as intended, potentially leading to false trips, remote clearing, delayed clearing, the overreach of protective relays or reliance on the interconnecting Transmission Owner’s Protection System devices to respond to a fault. Protection System devices could fail to operate when they are designed to operate and expose the BPS to fault conditions requiring the function of secondary protection systems and isolation devices. The 27 Protection System devices account for 2.4 percent of the 1,113 devices subject to this instance and the requirements of PRC 005-1b R2. HGMA operates 1,325 MW of generation. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, HGMA had backup relays and breakers with documented maintenance and test records in place during the scope of this issue. These backup devices can protect the system if the primary devices fail. There have been no misoperations of facility protection systems that have resulted in issues for maintaining the stability of the BES since the effective date of the Standard at the Facility. Based on this, WECC determined that there was a low likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, HGMA: a. conducted training on its Protection System maintenance and testing program and the updated Monthly Checklist includes internal monthly compliance controls; and b. required contractors to use the Protection System maintenance and testing program standardized test report forms for performing maintenance and testing of Protection System devices. c. implemented it Protection System maintenance and testing program for the 27 Protection System devices and completed maintenance testing.
2018-09-27 | Western Electricity Coordinating Council (WECC) | ProEnergy Services (PRSV) | NCR11550 | WECC2017018051 | PRC-024-2 | R2 | On July 27, 2017, PRSV submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 Requirement 2. Specifically, PRSV reported that during a mock audit conducted in July and August of 2016, it discovered that for one generation plant unit, it did not set its protective relaying so that it would not trip within the “no trip zone” of Attachment 2.4 of the Standard. The overvoltage protective relay setting was set to trip at 1.14 pu at 0.1 seconds. After reviewing all relevant information, WECC determined that PRSV failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection3) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2.4, for its single applicable Facility. The root cause of the noncompliance was a less than adequate understanding of the Standard and Requirement. Specifically, PRSV misunderstood the implementation plan as it related to entities with a single applicable facility. This misunderstanding led to the incorrect identification of when the relay settings needed to be reviewed for proper voltage ride-through as presented in PRC-024-2 Attachment 2.4. This led to the late detection of the need to modify the relay settings. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for PRSV’s single applicable Facility, and ended on January 13, 2018, when PRSV reset the overvoltage protective relaying setting, for a total of 551 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, PRSV failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection3) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2.4, for its single applicable Facility. Such failure could cause the generating unit to prematurely trip offline from a voltage excursion within the "no trip zone." Its overvoltage protective relay setting was set to trip at 1.14 pu at 0.1 seconds. Therefore, WECC assess the potential harm to the security and reliability of the BPS as negligible. However, PRSV’s inherent risk to the BPS is low. PRSV’s single Facility is a 69.5 MVA combined cycle generator. Based on this, WECC determined that the noncompliance had a low likelihood of causing negligible harm to the BPS. No harm is known to have occurred. | To mitigate this issue, PRSV: a. reset the overvoltage protective relaying setting on the relay in scope; b. developed a plant procedure which demonstrates that coordination of protective relaying is crucial such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the "no trip zone" of PRC-024 Attachment 2.4, as well as when the coordination must take place.; c. annually review the internal plant procedure, while also updating upon any standard revisions; d. added PRC-024 to its internal software product for tracking of compliance reporting functions and deadlines that are deemed appropriate; and e. holds monthly compliance calls to ensure plant staff are aware of upcoming deadlines and compliance obligations.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC2017018514 | MOD-026-1 | R6 | On October 24, 2017, CHPD submitted a Self-Report stating that, as a Transmission Planner (TP), it was in potential noncompliance with MOD-026-1 R6. Specifically, CHPD being a vertically integrated entity, reported that on April 14, 2017 and April 24, 2017, its Generator Owner (GO) submitted to its TP the modeling verification report for a new exciter and governor for one generating unit and the modeling verification report for a new exciter only for another generating unit. The two generating units had nameplate capacities of approximately 51 MVA and 114 MVA, respectively, and are located at two separate facilities. The TP provided a written response to the GO on August 21, 2017 regarding the data for both units, 120 days and 130 days after receiving the information, failing to meet the 90-day requirement of MOD-026-1 R6. Additionally, on April 30, 2018 CHPD notified WECC that it had discovered an additional instance of noncompliance that occurred on January 11, 2015. Specifically, on October 13, 2014, CHPD’s GO submitted to its TP, the verified excitation control system or plant volt/var control function model information for another generating unit. The nameplate for the additional unit was 54 MVA. The TP provided a written response to the GO on January 29, 2015, 109 days after receiving the information, failing to meet the 90-day requirement of MOD-026-1 R6. After reviewing all relevant information, WECC determined that in all three instances CHPD’s TP failed to provide a written response to its GO within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information, that the model is usable or not usable, as required by MOD-026-1 R6. The root cause of the noncompliance was a less than adequate process for tracking tasks and the status of critical tasks by the TP. WECC determined that these issues began on January 11, 2015, July 14, 2017 and July 24, 2017, respectively, when CHPD’s TP failed to respond to its GO within 90 days of receiving the modeling information. WECC determined that the end date of the first instance was January 29, 2015 for a total of 19 days. The end date for the second and third instances was August 21, 2017 when CHPD’s TP provided a response to its GO notifying them that the models received are usable, for a total of 39 days and 29 days, respectively. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). CHPD’s TP failed to provide a written response to its GO within 90 calendar days of receiving the verified excitation control system or plant volt/var control function model information, that the model is usable or not usable. Such failure could potentially lead to a misunderstanding of whether new models were incorporated and could potentially result in an inaccurate representation of the generating units in planning models or dynamic simulations. The exciter models for three generating units at two facilities with a total nameplate capacity of 228 MVA were affected. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as negligible. However, CHPD did not have any controls in place that could reduce the likelihood of occurrence. Based on this, WECC determined that there was moderate likelihood of causing negligible harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, CHPD: a. verified the received models and provided a written response to the GO; b. configured its maintenance management software to display preventative maintenance records in the “Start Center”; c. created a work order process to track the status of the job plan created for each maintenance record; and d. created an email template for MOD notices. WECC verified CHPD’s mitigating activities.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC2017018526 | MOD-027-1 | R5 | On October 24, 2017, CHPD submitted a Self-Report stating that, as a Transmission Planner (TP), it was in potential noncompliance with MOD-027-1 R5. Specifically, CHPD being a vertically integrated entity, reported that on April 14, 2017, its Generator Owner (GO) submitted to its TP, the turbine/governor and load control or active power/frequency control system verified model information for one generation unit with a nameplate capacity of 51 MVA. The TP provided a written response to the GO on August 21, 2017 regarding the data for the unit, 130 days after receiving the information, failing to meet the 90-day requirement of MOD-027-1 R5. Additionally, on April 30, 2018 CHPD notified WECC that it had discovered an additional instance of noncompliance that occurred on January 11, 2015. Specifically, on October 13, 2014, CHPD’s GO submitted to its TP, the turbine/governor and load control or active power/frequency control system verified model’s information, for one generation unit with a nameplate capacity of 54 MVA. The TP provided a written response to the GO on January 29, 2015, 109 days after receiving the information, failing to meet the 90-day requirement of MOD-027-1 R5. After reviewing all relevant information, WECC determined that CHPD’s TP failed to provide a written response to its GO within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information, and that the model is usable or not usable, as required by MOD-027-1 R5. The root cause of the noncompliance was a less than adequate process for tracking tasks and the status of critical tasks. WECC determined that the first instance began on January 11, 2015 and the second instance began July 14, 2017, when CHPD’s TP failed to respond to its GO within 90 days of receiving the model information. WECC determined that the end date of the first instance is January 29, 2015 for a total of 19 days of noncompliance. The end date for the second instance was August 21, 2017 when CHPD’s TP provided a response to its GO notifying them the models received are usable, for a total of 39 days. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In both instances, CHPD’s TP failed to provide a written response to its GO within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information that the model is usable or not usable, in accordance with MOD-027-1 R5. Such failure could potentially lead to a misunderstanding of whether new models were incorporated and could potentially result in an inaccurate representation of the generating units in planning models of dynamic simulations. The governor models for two generating units with a total nameplate capacity of 108 MVA was affected. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as negligible. However, CHPD did not have any controls in place that could reduce the likelihood of occurrence. Based on this, WECC determined that there was moderate likelihood of causing negligible harm to the BPS. No harm is known to have occurred. | To remediate and mitigate this issue, CHPD: a. verified the received models and provide a written response to the GO; b. configured its maintenance management software to display preventative maintenance records in the “Start Center”; c. created a work order process to track the status of the job plan created for each maintenance record; and d. created an email template for MOD notices. WECC verified CHPD’s mitigating activities.
2018-09-27 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC2017018847 | PRC-024-2 | R2 | On December 12, 2017, SNPD submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-024-2 R2. Specifically, SNPD reported that it set eight generator voltage protective relays for a "no trip zone" based on the low side of the generator step-up (GSU) transformer instead of the high side as defined by footnote 3, as required by PRC-024-2 R2 Attachment 2.4. SNPD hired a protection systems consultant to perform the relay calculations required to comply with this Standard. The consultant set the relays to match the exact settings of the Attachment 2 - Voltage Ride-Through Time Duration Curve. Based on discussions with the consultant, the consultant interpreted the Standard language to mean that the relay should be set to exactly match the Attachment 2 - Voltage Ride-Through Time Duration Curve. The consultant was unaware of the footnote in the Requirement that detailed that the relay settings should be based on the high side of the GSU. The eight relays were associated with four generating units at SNPD’s124 MVA (plant output varies between 15 MW and 100 MW) hydroelectric generating facility. After reviewing all relevant information, WECC determined that SNPD failed to set its protective relays such that the generator voltage protective relaying does not trip within the “no trip zone” as detailed in Attachment 2.4, as required by PRC-024-2 R2. The root cause of the noncompliance was due to a less than adequate check of work. Specifically, SNPD relied on the expertise of a consultant hired to perform the relay settings changes without verifying the accuracy or validity of the settings changes. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of SNPD’s generating units, and ended on March 30, 2018, when SNPD updated the protective relaying settings for the eight affected relays, for a total of 637 days. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, SNPD failed to set its protective relays so that they would not trip within the “no trip zone” of Attachment 2.4, as required by PRC-024-2 R2. Such failure could result in the generating units being inadvertently tripped off-line for a voltage excursion in which the voltage at the high side of the GSU transformer is within the "no trip zone." The entity owns and operates the 124 MVA (plant output varies between 15 MW and 100 MW) hydroelectric generating facility comprised of four generating units that were subject to this instance. Therefore, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, SNPD had implemented good controls to mitigate the risk. Although the generating facility was capable of outputting 100 MW, the average output was approximately 35 MW. This is primarily dependent on water availability. Additionally, should the generating units experience a voltage excursion, its previous settings would have enabled them to trip their associated generating units within the "no trip zone" of the PRC-024 Voltage Ride-Through Time Duration Curve for high voltage conditions. SNPD’s undervoltage relay elements were used for alarming only and could not trip their generating units for low voltage conditions. For Units 1 and 2, the overvoltage relay elements would have operated at 107.3% for 1 second delay, 112.4% for a 0.5 second delay, 115% for a 0.2 second delay, and 117.5% for a 0.03 second delay. For Units 3 and 4, the overvoltage relay elements would have operated at 108.1% for a 1 second delay, 113.1% for a 0.5 second delay, 115.7% for a 0.2 second delay, 118.2% for a 0.03 second delay. Based on this, WECC determined that there was a low likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To mitigate this issue, SNPD: a. adjusted the relay settings for the eight relays in scope; and b. updated language in its contracts to: i. specifically state that applicable Standard attachments and footnotes should be verified for compliance ii. require contractors to perform internal peer reviews iii. require contractors to demonstrate their qualifications iv. require SNPD’s District Standard Leads review the work submitted by the contractor for compliance with the Standards
2018-09-27 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Desert Southwest Region (WALC) | NCR05461 | WECC2017017621 | PRC-002-2 | R1 | On May 18, 2017, WALC submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-002-2 R1. Specifically, WALC reported that during a mock audit, it discovered a mathematical error had occurred when the median Mega Volt Amp (MVA) level in step 4 of Attachment 1, in response to Requirement 1, had been calculated. This calculation error caused the number of Bulk Electric System (BES) buses, for which sequence of events recordings (SER) and fault recording (FR) data was required, to be calculated as five instead of the actual nine buses that WALC owns and were applicable to PRC-002-2 R1.1. Additionally, as a result of the calculation error, WALC did not notify the owners of the BES Elements connected to the additional four busses, as required by PRC-002-2 R1.2. After reviewing all relevant information, WECC determined that WALC failed to identify BES buses for which SER and FR data was required, by using the methodology in PRC-002-2, Attachment 1, and failed to notify other owners of BES Elements connected to those BES buses, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data, as required by PRC-002-2 R1 The root cause of the issue was due to less than adequate internal controls to prevent or detect calculation errors. WECC determined that this issue began on July 1, 2016, when WALC incorrectly calculated the median MVAs, and ended on May 12, 2017, when WALC emailed the updated notifications to the all owners of the BES elements, for a total of 315 days. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, WALC failed to identify BES buses for which SER and FR data was required, by using the methodology in PRC-002-2, Attachment 1, and failed to notify other owners of BES Elements connected to those BES buses, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data, as required by PRC-002-2 R1, Such failure could potentially result in having inadequate data available to facilitate analysis of BES disturbances from SER and FR and implement changes that could reduce the likelihood of a similar disturbance event from occurring. Since this would be post disturbance analysis, WECC assessed the potential harm to the security and reliability of the BPS as minor. However, WALC implemented a good detective control in the form of a mock audit which is what identified this issue. Based on this, WECC determined that there was a low likelihood of causing minor harm to the BPS. No harm is known to have occurred. | To mitigate this issue, WALC: a. recalculated the median MVA and revaluated the BES buses; b. notified all owners of BES elements that require SER data and/or FR data; c. implemented a worksheet to assist employees responsible for calculating the median MVA and the correct BES buses per Attachment 1; and d. implemented a procedure document that demonstrates how the new worksheet should be used.
2018-08-30 | Florida Reliability Coordinating Council, Inc. (FRCC) | Vandolah Power Company, LLC (VPC) | NCR00078 | FRCC2018019877 | PRC-019-2 | R1. (P1.1) | On June 20, 2018, VPC submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-019-2 R1, P1.1. This noncompliance started on July 1, 2016, when the Standard became enforceable and VPC did not have verification of coordination evidence and ended on April 4, 2018, when VPC verified settings, tested and developed documentation validating its coordination. Specifically, during a recent internal self-assessment on October 4, 2017, VPC discovered a deficiency with its documentation to accurately illustrate the verification of coordination with items listed in requirements 1.1.1 and 1.1.2. The cause for this noncompliance was due to not having a control for maintaining documentation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because VPC's verification of its facility limiters demonstrated they were coordinated with its protective relay elements and did not require any changes to the facility. The risk was further reduced because the total generation output of 680 MW’s represents only .013% of the Region. No harm is known to have occurred. | To mitigate this noncompliance, VPC: 1) evaluated the results of the internal self-assessment; 2) contracted a third-party source to re-perform the coordination study; 3) provided documentation following the examples shown in section G of the Standard; and 4) updated its internal processes to specify the documentation required following a coordination study.
2018-08-30 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2018019529 | PRC-004-5(i) | R1 | On April 10, 2018, NSP, a Coordinated Oversight Program participant, submitted a self-log to MRO stating that, as a Transmission Owner, it was in noncompliance with PRC-004-5(i) R1. NSP, Public Service Company of Colorado (PSCO) (NCR05521), and Southwestern Public Service Company (SPS) (NCR01145) (hereafter referred to collectively as Xcel Energy) are Xcel Energy companies monitored together under the Coordinated Oversight Program. Xcel Energy stated that the noncompliance involved PSCO. Specifically, Xcel Energy failed to identify whether its Protection System Component caused a Misoperation within 120 days after a July 14, 2017 breaker operation on a 115kV line. Xcel Energy stated that it discovered the noncompliance during the review of a subsequent operation of the same breaker. The cause of the noncompliance was that the breaker operation was incorrectly documented by the operator, resulting in the breaker operation not being reviewed by the System Protection Engineer group (SPE). The event was logged in the daily operations log at the time of the occurrence, but the operator failed to check the “Disturbance” box, which is how the SPE identifies operations to review for PRC-004-5(i). The noncompliance started on November 11, 2017, 121 days after the breaker operation, and ended on December 20, 2017, when Xcel Energy identified that the breaker caused a Misoperation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance was limited to a 115 kV line that was not part of a blackstart cranking path, RAS, IROL, or WECC path. An extent of conditions analysis in PSCO, and a sampling of relevant logs in NSP and SPS, indicated that this was the only instance of noncompliance caused by a failure to flag a Protection System operation. The Misoperation that occurred did not result in any overloads, adverse conditions on the system, or loss of load. No harm is known to have occurred. | To mitigate this noncompliance, Xcel Energy: 1) reviewed the breaker operation and determined that it was a Misoperation; 2) conducted an extent of conditions analysis where it reviewed all PSCO logs back to April 1, 2017, and a sampling of NSP and SPS logs to determine if operations were being properly flagged in the log, and no additional instances of noncompliance were detected; 3) the PSCO Control Center Manger issued an email reminding System Operators of the need to make proper log entries; 4) the PSCO Transmission Control Center implemented a control where the Network Reliability Lead will review all daily logs at midnight for the prior day's entries; and 5) the PSCO Control Center Senior Trainer performed training for all six crews during the Winter Training sessions.
2018-08-30 | Midwest Reliability Organization (MRO) | Lincoln Electric System (LES) | NCR01001 | MRO2016016703 | FAC-009-1 | R1 | On October 19, 2016, the entity submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with FAC-009-1 R1. Specifically, LES did not incorporate transfer bus stations that are utilized during maintenance into its Facility Ratings Methodology. LES has two transfer busses that could impact the Facility Ratings of three lines. The cause of the noncompliance was that LES’ Facility Ratings Methodology and associated procedures were not specific enough to adequately address transfer buses. This noncompliance started on June 18, 2007, when the Standard and Requirement became mandatory and ended on November 21, 2016, when LES updated its Facility Ratings to include transfer buses. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. By definition transfer buses (utilized commonly only during maintenance) are not typically in-service; per LES, the transfer buses were only in-service four times since January 1, 2013. Further, while the transfer buses were not in LES’ Facility Ratings, LES stated that it did set MVA alarms on the three lines. Per LES, the alarming was correct for two out of the three lines, but the Summer Emergency rating of the third line was set at 120 MVA, when it should have been alarmed at 113 MVA. LES stated that it reviewed its historical ratings since 2013 and states that the highest rating for that line while utilizing a transfer bus was 44.3 MVA. Finally, the three lines are not associated with an IROL or a Cranking Path. No harm is known to have occurred. MRO determined that LES’ compliance history should not serve as a basis for applying a penalty. LES’ compliance history includes two Compliance Exceptions with FAC-008-3 R6 (MRO2016015899 & MRO2013013185). In MRO2016015899, LES replaced breakers and disconnect switches at a 115 kV substation (that were rated higher than the prior elements). The cause of the noncompliance was weak procedures that did not ensure recalculation of Facility Ratings prior to energizing the facility. In MRO2013013185, LES identified discrepancies in source documentation and the Facility Rating database that caused changes to the overall ratings of the facilities; however, the largest change was 6 MVA or .4% of the rating. MRO determined that the current noncompliance was not caused by a failure to mitigate the prior noncompliance, and that all issues have distinct causes. | To mitigate the noncompliance, LES: 1) performed field verifications at both substations in order to verify all equipment associated with the transfer buses and update the Facility Rating documentation; and 2) updated its Facilities Rating Methodology documentation to include direction on how to implement ratings associated with a transfer bus.
2018-08-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Essential Power Massachusetts, LLC | NCR00374 | NPCC2018019152 | PRC-005-2(i) | R3. | During a Compliance Off-site Audit conducted from October 19, 2017 through February 9, 2018, NPCC determined that Essential Power Massachusetts, LLC ("the Entity"), as a Generator Owner (GO), was in noncompliance with standard PRC-005-2(i) [Requirement R3.]. More specifically, the Entity failed to perform required testing for the trip coils and the unmonitored control circuitry associated with two lockout relays associated with the protection of the Generator Step-Up transformer (GSU) of GT2, one of the two generating units that they own and operate. Requirement 3 of the standard requires that trip coils and unmonitored control circuitry be tested with a maximum periodicity of six (6) calendar years and twelve (12) calendar years, respectively. This noncompliance started on May 29, 2015, when the standard and requirement became enforceable, and ended on March 16, 2017, when the required maintenance was completed at the time of commissioning for two new lockout relays that were installed to replace the older untested relays as part of comprehensive switchyard upgrades undertaken by the host Transmission Owner (TO). The root cause of this instance of non-compliance was the Entity's failure to recognize its responsibilities for performing maintenance on trip coils and unmonitored control circuitry associated with two noncompliant lockout relays and, additionally, for similar testing of a tripping relay associated with the protection system of its other generating unit (G3), which had been historically maintained by the Entity's host TO. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity owns and operates two generating units: GT2 (a Gas Turbine rated at 71.2 MVA) and G3 (a Steam Turbine rated at 133.7 MVA). The two noncompliant relays were part of the protection system of the GSU of generator GT2. However, two real-time events that took place on 8/7/2012 (a line trip caused by a line fault associated with generator GT2) and 7/4/2015 (a trip of the GSU itself, caused by a crack in one of the GSU's Current Transformers) are indirect evidence of the correct operation of the trip coils and control circuitry associated with the two untested lockout relays, both of which correctly operated on these occasions to open appropriate breakers in order to isolate faulted elements. Historical data shows that the operating capacity factor for generator GT2 were 3.47% (in 2016) and 2.87% (in 2017). Moreover, as the rated capacity of the affected generator (GT2) is less than 3% of the Entity's Reliability Coordinator's (ISO-NE) required Operating Reserve (approximately 2600 MW), if this instance of noncompliance had caused the unwarranted loss of generator GT2, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) corrected the noncompliance by causing the required tests to be completed at the time of commissioning for two new lockout relays that were installed to replace the older untested devices. To prevent a recurrence of similar instances of noncompliance, the Entity: 1) implemented changes to its existing maintenance procedures that define its responsibility for the performance of required tests on the aforementioned two lockout relays (associated with GT2) and the single tripping relay (associated with G3). NPCC has verified the completion of all mitigation activity.
2018-08-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Massachusetts Municipal Wholesale Electric Company | NCR07136 | NPCC2018018939 | EOP-005-2 | R17. | On October 19, 2017, Massachusetts Municipal Wholesale Electric Company ("the Entity") submitted a log stating that, as a GOP, it was in noncompliance with EOP-005-2, R17. As part of an internal compliance review of EOP-005 in 2017, the Entity discovered it did not have training records for two of its 26 operating personnel of its black-start resource generating units located at its Stony Brook Power Plant site for the years 2015 and 2016. R17 requires that appropriate training be provided to responsible personnel every two calendar years. These two individuals had last received the required training in 2014, according to documented evidence provided by the Entity. This noncompliance started on December 31, 2016, when the required periodic training was due for the two individuals, and ended on January 23, 2017, when they received the training for the startup of black-start resource generating units and energizing a bus. The root cause of this instance of noncompliance has multiple aspects: 1) The plant training matrix, used to schedule and track all personnel training, did not indicate that this black-start training was required every two calendar years; 2) In the past, the Entity has mostly relied on the participation of all its operating personnel to the annual testing of its black-start facilities as an opportunity to fulfill its black-start training requirements at that time. However, vacation time schedules, sick leave and other time-off requirements have resulted in two individuals missing their participation in black-start testing for more than two consecutive years; 3) Plant management was not adequately informed of training timeline requirements; 4) There was not a regularly scheduled internal review of training fulfillment within the two calendar year period. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity owns and operates the Stony Brook Power Plant, which is composed of five peaking units and one steam unit. The plant is radially interconnected to the host TO's 345kV substation via a 5-mile 345kV transmission line. Two of the five peaking units have an aggregate net Capacity of 172 MW of black-start capability and are part of the local TOP Restoration Plan and, as such, their operating personnel must comply with the requirements of this standard. All Stony Brook units are operated from a single control room by single four-member crews on a 12-hour rotating shift. Each crew consists of a Shift Supervisor, Control Room Operator, Assistant Control Room Operator and Auxiliary Operator. The Entity has four regular crews plus additional spare personnel, all of which receive black-start training. Therefore, although there was no evidence of timely training provided to two of its 26-member operating staff, there was a redundancy of trained personnel in each of the four-member crews that normally operate the Stony Brook Power Plant. The duration of the noncompliance was 23 days. Additionally, the two black-start units have not been required to operate in that capacity, for system restoration purposes, during the years 2015, 2016 and 2017. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) corrected the noncompliance by providing to the two individuals the training prescribed by the standard and requirement for the startup of black-start resource generating units and energizing a bus. To prevent a recurrence of similar instances of noncompliance, the Entity: 1) modified the plant training matrix to indicate that black-start training is required every two years; 2) created a new task in the scheduling and tracking system to schedule biennial training for EOP-005 R17; and 3) created a new task in the scheduling and tracking system to periodically review training records for operators for EOP-005 R17 and other NERC-required training. NPCC has verified the completion of all mitigation activity.
2018-08-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Massachusetts Municipal Wholesale Electric Company | NCR07136 | NPCC2017017829 | COM-002-4 | R3. | During a Compliance Spot Check conducted from April 25, 2017 to June 30, 2017, NPCC determined that Massachusetts Municipal Wholesale Electric Company ("the Entity"), as a Generator Operator (GOP), was in noncompliance with COM-002-4 R3. In reviewing the Entity's 2nd Quarter 2017 compliance Guided Self-Certification submittal for the reporting period 4/1/2016 to 3/24/2017 (effected on April 24, 2017), NPCC discovered that an employee had been promoted to a position of Assistant Control Room Operator (ACRO), where he's authorized to receive oral two-party, person-to-person Operating Instructions. However, this individual did not receive a three-part communication initial training prior to taking that position, as prescribed by Requirement R3 of the standard. This noncompliance started on November 30, 2016, when the individual was promoted to ACRO, and ended on April 8, 2017, when the individual received, for the first time, a Supply Resource Operator Training (SROT) provided by the Entity's Reliability Coordinator, the ISO-NE. The SROT is provided annually to operating personnel that may receive oral two-party, person-to-person Operating Instructions from transmission operators or balancing authorities and, as such, it includes a three-part communications training module. The root cause of this instance of non-compliance was that the Entity's training protocol for new operators did not include a specific task requiring completion of the ISO-NE operator training, or, alternatively, specific training for three-part communications. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity owns and operates the Stony Brook Power Plant, which is composed of five peaking units and one steam unit. The plant is radially interconnected to the host TO's 345kV substation via a 5-mile 345kV transmission line. The aggregate gross rated Capacity of the six units is approximately 670 MW with an combined average capacity factor of 5%, 2.5% and 2.3%, respectively for the years 2015, 2016 and 2017. The Capacity Factors of the Stony Brook units during winter (the period affected by this noncompliance) is lower, typically 1%, which results in fewer opportunities for Operating Instructions to be issued to Stony Brook operators. All Stony Brook units are operated from a single control room by single four-member crews on a 12-hour rotating shift. Each crew consists of a Shift Supervisor, Control Room Operator, Assistant Control Room Operator and Auxiliary Operator. The Entity has four regular crews plus additional spare personnel, all of which receive SROT training annually from the Entity's Reliability Coordinator, the ISO-NE. Therefore, although one individual did not take an initial communication training prior to receiving a promotion to a position of ACRO, there was a redundancy of fully trained personnel in each of the four-member crews that normally operate the Stony Brook Power Plant. The duration of the noncompliance was a little over four months, during which the untrained individual did not receive any Operating Instructions, according to historical operating logs. Moreover, as the aggregate rated capacity of the Stony Brook Power Plant units is less than 26% of the Entity's Reliability Coordinator's (ISO-NE) required Operating Reserve (approximately 2600 MW), if an operating error (due to miscommunication) had caused the loss of the entire Stony Brook Power Plant, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) corrected the noncompliance by causing the individual to receive its first Supply Resource Operator Training (SROT), which is provided by the Entity's Reliability Coordinator (ISO-NE) and includes a three-part communications training module. To prevent a recurrence of similar instances of noncompliance, the Entity: 1) added a new task to its existing training protocol for newly hired personnel or personnel promoted to the position of Control Room Operator or Assistant Control Room Operator at its Stony Brook station. The new task specifies that completion of ISO-NE's SROT is a prerequisite for promotion to the aforementioned positions. NPCC has verified the completion of all mitigation activity.
2018-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Sapphire Power Marketing LLC (Sapphire) | NCR00838 | RFC2018020032 | PRC-005-6 | R3 | On June 30, 2018, the entity submitted a self-log stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R3. At Pedricktown, VRLA Batteries' 6 month ohmic measurements were missed because the 6 month checks were not on the maintenance form. At Camden and Newark Bay, annual maintenance for battery terminal connection resistance was not documented. The annual maintenance reports indicate that battery terminal connection resistance checks were performed for Camden (two NERC batteries, both VLA) and Newark Bay (two NERC batteries, both VLA), but these readings have not been found. Cell-to-cell (strap) resistance readings were taken (PRC-005-6 Table 1-4a, max-18-month task 4), but the reports do not include measurements for the battery bank positive and negative end-connections (PRC-005-6 Table 1-4a, max-18-month task 3). This noncompliance involves the management practice of verification as the entity failed to verify that the 6 month ohmic measurements were on the maintenance form at Pedricktown and that the battery terminal connection resistance checks were documented on the annual maintenance report at Camden and Newark Bay. That failure to verify is a root cause of this noncompliance. This noncompliance began on April 4, 2018, when the entity first missed the 6 month ohmic measurements at Pedricktown, and ended on April 13, 2018 when the entity completed the overdue maintenance and testing activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this noncompliance is the failure of battery related equipment caused by a lack of maintenance which could cause a generator to trip offline. The risk is minimized because although the entity missed the VRLA Batteries' 6 month ohmic measurements at Pedricktown and could not find the documentation for the annual maintenance for battery terminal connection resistance at Camden and Newark Bay, the entity did timely complete all other required PRC-005-6 R3 maintenance and testing at both plants. Specifically, the entity timely completed DC supply voltage, electrolyte level, battery rack, and float voltage testing among others at all three plants. Lastly, the entity quickly identified, assessed, and corrected these issues as the duration of this noncompliance was only nine days. ReliabilityFirst also notes that all three of these units run infrequently. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) corrected the VRLA battery test forms so that the 6 month battery checks were added to the forms. This new test form is based on a Talen (Sapphire's parent company) fleet-standard format; and 2) tested the VLA batteries and provided training to staff through a teleconference with the entity plant managers to explain the use of the new test forms. The new forms are now in use.
2018-08-30 | Texas Reliability Entity (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2018019844 | EOP-006-2 | R5; R5.1 | On June 11, 2018, ERCOT submitted a Self-Log stating that, as a Reliability Coordinator (RC), it was in noncompliance with EOP-006-2 R5, Part 5.1. In particular, ERCOT failed to approve or disapprove the Transmission Operators’ (TOPs) submitted restoration plans within 30 calendar days of receipt of the TOP restoration plans in 2013, 2015, 2016, and 2017. ERCOT reported that it received 17 TOP restoration plans between October 5, 2017 and November 9, 2017, but failed to approve the restoration plans until December 13, 2017. As a result, ERCOT was in noncompliance with EOP-006-2 R5, Part 5.1 between 4-39 days in 2017. Subsequently, ERCOT determined that it also failed to meet the 30 calendar day approval or disapproval requirement pertaining to EOP-006-2 R5, Part 5.1 in 2013, 2015, and 2016. In 2013, ERCOT received its first restoration plan on October 14, 2013, and approved all restoration plans on December 16, 2013. This 2013 approval process took 63 days from submittal. ERCOT also determined that it exceeded the 30 calendar day deadline in 2015 and 2016 due to approving plans on a timeline similar to 2013 and 2017. In all four instances of noncompliance, ERCOT approved the plans prior to the January 1 effective date of the restoration plans. This root cause of this noncompliance was that ERCOT lacked a sufficient process to ensure compliance with EOP-006-2 R5, Part 5.1. Specifically, ERCOT failed to ensure that its process for submittal and review of restoration plans aligned with the Standard requirements. ERCOT’s procedures stated that the annual deadline for restoration plan submittal is November 1, and restoration plans are deemed submitted upon transmittal to ERCOT. To confirm that all TOP restoration plans are coordinated and compatible, ERCOT performs a comprehensive review of all TOP restoration plans that begins once all plans are submitted. As a result of these combined processes, ERCOT’s approval of early individual restoration plan submittals took more than 30 days to complete. This noncompliance began on November 14, 2013, 31 days after the first restoration plan was submitted by a TOP, and ended on December 13, 2017, when ERCOT approved all applicable TOP restoration plans. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The delay in approving or disapproving the restoration plans within 30 calendar days of receipt did not impact planning in the ERCOT Region. Specifically, ERCOT approved all submitted restoration plans so there was no additional time needed for corrections. Additionally, the plans were approved before their effective date of January 1. For example in 2017, the plans were approved eighteen days prior to January 1, 2018. No harm is known to have occurred. Texas RE considered ERCOT’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ERCOT: 1) reviewed and approved all applicable TOP restoration plans; and 2) revised its procedure to specify that all restoration plans submitted prior to November 1 are deemed submitted on November 1. This will facilitate ERCOT’s comprehensive and timely review of TOP restoration plans. Texas RE has verified the completion of all mitigation activity.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Aragonne Wind LLC (AGW) | NCR05014 | WECC2017016996 | PRC-024-2 | R1 | On February 14, 2017, AGW submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Specifically, AGW reported that it failed to set its generator frequency protective relays so that they would not trip within the “no trip zone” of Attachment 1 of the Standard. The overfrequency protective relaying was set to trip at 61.0 Hz at .30 seconds and the underfrequency protective relaying was set to trip at 59.0 Hz at .30 seconds; both settings were within the “no trip zone” detailed in the Standard. After reviewing all the relevant information, WECC determined that AGW’s Mitsubishi wind turbine generators had both the overfrequency and underfrequency protective relays set to trip within the “no trip zone” in violation of the Standard. AGW failed to set its generator frequency protective relays so that they would not trip within the “no trip zone” of Attachment 1 of the Standard. The root cause of the noncompliance was AGW management’s failure to instruct generator personnel to set generator frequency protective relays in accordance with the new Standard prior to the enforcement date of the Standard. WECC determined that this issue began on July 1, 2016, when PRC-024-2 became mandatory and enforceable for AGW’s applicable Facility. WECC determined that the end date of this issue was January 29, 2018, when the original equipment manufacturer reprogramed the Generator Frequency Protective Relays, for a total of 577 days of noncompliance. WECC notes that AGW does not have any relevant previous violations of this or similar Standards and Requirements. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AGW failed to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating Facility within the “no trip zone” of Attachment 1 of the Standard. Incorrect frequency protective relay settings may cause the 90 MW wind Facility to prematurely trip offline from a frequency excursion within the “no trip zone.” However, the likelihood of the risk occurring was reduced because the Facility in scope is a 90 MW wind facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that wind generation may be unavailable at any given time, so in the unlikely event that AGW experienced a loss of its wind facility, system reliability would not be compromised. Additionally, AGW found that it had only one overfrequency and one underfrequency protective relay set to trip within the “no trip zone.” Specifically, the overfrequency protective relaying was set to trip at 61.0 Hz at .30 seconds and the underfrequency protective relaying was set to trip at 59.0 Hz at .30 seconds. No harm is known to have occurred. WECC notes that AGW does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, AGW: a. contracted with a third-party contractor to identify any frequency or voltage relaying settings that were not in compliance; b. notified its Transmission Planner of the settings found to be noncompliant; c. contracted with the original equipment manufacturer to reset the frequency and voltage protective relay settings found to be noncompliant; d. implemented a process to track and assign new regulatory commitments to management and responsible personnel with enough time to ensure compliance with new Standards and Requirements. This is implemented through a weekly meeting with the Director of Compliance, the third-party NERC compliance contractor, and all managers associated with NERC compliance activities; and e. notified the Transmission Planner of the updated settings. WECC verified completion of AGW's Mitigation Plan.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Aragonne Wind LLC (AGW) | NCR05014 | WECC2017016997 | PRC-024-2 | R2 | On February 14, 2017, AGW submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Specifically, AGW reported that it failed to set its generator voltage protective relays so that they would not trip within the “no trip zone” of Attachment 1 of the Standard. The undervoltage protective relaying was set to trip at .85 pu at .5 seconds; .70 pu at .2 seconds; and .60 pu at .1 seconds, all within the “no trip zone” detailed in the Standard. After reviewing all the relevant information, WECC determined that AGW’s Mitsubishi wind turbine generators had three undervoltage protective relays settings set to trip within the “no trip zone” in violation of the Standard. AGW failed to set its generator voltage protective relays so that they would not trip within the “no trip zone” of Attachment 1 of the Standard. The root cause of the noncompliance was AGW management’s failure to instruct generator personnel to set generator voltage protective relays in accordance with the new Standard prior to the enforcement date of the Standard. WECC determined that this issue began on July 1, 2016, when PRC-024-2 became mandatory and enforceable for AGW’s applicable Facility. WECC determined that the end date of this issue was January 29, 2018, when the original equipment manufacturer reprogramed the generator voltage protective relays, for a total of 577 days of noncompliance. WECC notes that AGW does not have any relevant previous violations of this or similar Standards and Requirements. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, AGW failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating Facility within the “no trip zone” of Attachment 1 of the Standard. Incorrect voltage protective relay settings may cause the 90 MW wind Facility to prematurely trip offline from a voltage excursion within the “no trip zone.” However, the likelihood of the risk occurring was reduced because the Facility in scope is a 90 MW wind facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that wind generation may be unavailable at any given time, so in the unlikely event that AGW experienced a loss of its wind facility, system reliability would not be compromised. Additionally, AGW found that it only had three undervoltage protective relays set to trip within the “no trip zone” in violation of the Standard. Specifically, the undervoltage protective relaying was set to trip at .85 pu at .5 seconds; .70 pu at .2 seconds; and .60 pu at .1 seconds. No harm is known to have occurred. WECC notes that AGW does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, AGW: a. contracted with a third-party contractor to identify any frequency or voltage relaying settings that were not in compliance; b. notified its Transmission Planner of the settings found to be noncompliant; c. contracted with the original equipment manufacturer to reset the frequency and voltage protective relay settings found to be noncompliant; d. implemented a process to track and assign new regulatory commitments to management and responsible personnel with enough time to ensure compliance with new Standards and Requirements. This is implemented through a weekly meeting with the Director of Compliance, the third-party NERC compliance contractor, and all managers associated with NERC compliance activities; and e. notified the Transmission Planner of the updated settings. WECC verified completion of AGW's Mitigation Plan.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Cedar Creek Wind Energy, LLC (CCWE) | NCR10165 | WECC2017016988 | PRC-024-2 | R1 | On February 10, 2017, CCWE submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. Specifically, CCWE reported that it failed to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024-2 Attachment 1, by the effective date of the Standard. After reviewing the relevant information, WECC determined that CCWE did not have evidence of its frequency protective relaying settings to verify that the frequency protective relaying would not trip within the “no trip zone” of the Standard for its single Facility. CCWE was unaware of its settings at the time the Standard became mandatory and enforceable. The root cause of this issue was a less than adequate process to ensure CCWE’s management of relay requirements to the new Standard, to generator personnel; thus, failing to verify appropriate relay settings by the effective date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for CCWE’s applicable Facility. WECC determined that the end date of this issue was January 29, 2018, when the original equipment manufacturer reprogramed the non-compliant relay settings and verified that they would not trip within the “no trip zone,” for a total of 758 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bilk Power System (BPS). CCWE failed to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024-2 Attachment 1 by the effective date of the Standard. CCWE had one overfrequency relay set to trip at 61.0 Hz at .30 seconds and one underfrequency relay set to trip at 59.0 Hz at .30 seconds. Such failure could result in a premature trip of the generating units due to frequency excursions within the “no trip zone”. However, the likelihood of the risk occurring was reduced because the Facility in scope was a 300 MW intermittent wind Facility, therefore, system reliability would not likely be compromised, as wind generation is not typically utilized as a firm resource. System Operators plan and operate the grid with the expectation that the generation may be unavailable at any given time. Further, this issue was discovered during an internal compliance review, which was conducted following organizational changes and expansion of CCWE’s compliance staff. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that CCWE does not have previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, CCWE: a. hired an engineering consultant to verify its generator frequency protective relay settings as required in PRC-024-2; b. reprogramed its noncompliant generator frequency protective relay settings, as identified by the engineering consultant, in accordance to PRC-024-2 R1. c. notified its Transmission Planner of the reprogramed generator frequency protective relay settings; d. hired a contractor to assist with its NERC Compliance Program by implementing a tracking system; and e. started conducting weekly meetings to review and discuss its NERC Compliance Program. WECC verified completion of CCWE's Mitigation Plan.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Cedar Creek Wind Energy, LLC (CCWE) | NCR10165 | WECC2017016989 | PRC-024-2 | R2 | On February 10, 2017, CCWE submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R2. Specifically, CCWE reported that it failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024-2 Attachment 2 by the effective date of the Standard. After reviewing the relevant information, WECC determined that CCWE did not have evidence of its voltage protective relaying settings to verify that the voltage protective relaying would not trip within the “no trip zone” of the Standard for its single Facility. CCWE was unaware of its settings at the time the Standard became mandatory and enforceable. The root cause of this issue was a less than adequate process to ensure CCWE’s management of relay requirements to the new Standard to generator personnel, thus failing to verify appropriate relay settings by the effective date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for CCWE’s applicable Facility. WECC determined that the end date of this issue was January 29, 2018, when the original equipment manufacturer reprogramed the non-compliant relay settings and verified that they would not trip within the “no trip zone,” for a total of 758 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bilk Power System (BPS). CCWE failed to set its voltage protective relaying such that the generator voltage protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024-2 Attachment 2 by the effective date of the Standard. CCWE had five undervoltage and one overvoltage generator protection system relay settings out of compliance as described below: Equipment and setting % of rated Voltage Time delay (seconds) Mitsubishi Wind Turbine Setting – Undervoltage 85 1.00 Mitsubishi Wind Turbine Setting – Undervoltage 70 .25 Mitsubishi Wind Turbine Setting – Undervoltage 60 .15 General Electric Wind Turbine Setting - Overvoltage 116 .20 General Electric Wind Turbine Setting - Undervoltage 75 .02 General Electric Wind Turbine Setting - Undervoltage 69 .20 Such failure could result in a premature trip of the generating units due to voltage excursions within the “no trip zone”. However, the likelihood of the risk occurring was reduced because the Facility in scope was a 300 MW intermittent wind Facility, therefore, system reliability would not be compromised, as wind generation is not typically utilized as a firm resource. System Operators plan and operate the grid with the expectation that the generation may be unavailable at any given time. Further, this issue was discovered during an internal compliance review, which was conducted following organizational changes and expansion of CCWE’s compliance staff. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that CCWE does not have previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, CCWE: a. hired an engineering consultant to verify its generator voltage protective relay settings as required in PRC-024-2; b. reprogramed its noncompliant generator voltage protective relay settings, as identified by the engineering consultant, in accordance to PRC-024-2 R2. c. notified its Transmission Planner of the reprogramed generator voltage protective relay settings; d. hired a contractor to assist with its NERC Compliance Program by implementing a tracking system; and e. started conducting weekly meetings to review and discuss its NERC Compliance Program. WECC verified completion of CCWE's Mitigation Plan.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Comanche Solar PV, LLC (CMCH) | NCR11665 | WECC2017017530 | FAC-008-3 | R6 | On May 3, 2017, CMCH submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with FAC-008-3 R6. Specifically, CMCH reported that during an internal investigation of its NERC compliance program, it discovered that it failed to have Facility Ratings for its new constructed, solely owned Facility, consistent with its Facility Ratings methodology or documentation, as required by FAC-008-3 R6. CMCH failed to ensure that the construction and commissioning of the Facility was compliant with NERC Standards. CMCH partnered with a third-party to oversee the construction and commissioning of the facility, but third-party went out of business prior to completion, causing the construction and commissioning responsibilities to default back to CMCH, which then discovered the noncompliance. After reviewing all the relevant information, WECC determined that CMCH did not have a documented methodology for determining Facility Ratings, and therefore, did not have documented Facility Ratings of its solely owned generator Facility at the time of registration. The root cause of this issue was a lack of compliance oversight during the construction and commissioning process of the Facility in scope. WECC determined that this issue began on August 17, 2016, when CMCH was registered with NERC as a Generator Owner, while at the same time failed to have Facility Ratings for its applicable Facility. This issue ended on March 15, 2017, when CMCH developed and documented its Facility Ratings for its applicable Facility, for a total of 210 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, CMCH failed to have Facility Ratings for its newly constructed, solely owned Facility, consistent with its Facility Ratings methodology or documentation, as required by FAC-008-3 R6. Unknown and undocumented System Operating Limits (SOL’s) as determined by the Facilities Ratings methodology may negatively affect reliable planning and operation of the Bulk Electric System (BES). Incorrect ratings and limits could cause system instability because planning models and SOL’s would not accurately reflect the true limits of the interconnect, and would not reliably indicate pre-contingency or post-contingency limits These are important to determine system stability and to prevent overloads, cascading, and uncontrolled separation of the BES. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 156 MW solar facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that CMCH experienced a loss of its solar installation, system reliability would not be compromised. For these reasons, WECC determined that the potential impact had a low likelihood of causing intermediate harm. No harm is known to have occurred. WECC notes that CMCH does not have previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, CMCH: a. Developed and documented its Facility Ratings Methodology for its applicable Facility; b. developed and documented its Facility Ratings following the Facility Ratings methodology for its applicable Facility; and c. hired a contractor to oversee its NERC Compliance Program to ensure future compliance is maintained. WECC verified CMCH completed its Mitigation Activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Comanche Solar PV, LLC (CMCH) | NCR11665 | WECC2017017537 | PRC-005-6 | R1 | On May 3, 2017, CMCH submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-005-6 R1. Specifically, CMCH reported that during an internal investigation of its NERC compliance program, it discovered that it failed to establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying as identified in Section 4.2. Facilities, of the Standard. CMCH failed to ensure that the construction and commissioning of the Facility was compliant with NERC Standards. CMCH partnered with a third-party to oversee the construction and commissioning of the facility, but third-party went out of business prior to completion, causing the construction and commissioning responsibilities to default back to CMCH, which then discovered the noncompliance. After reviewing all the relevant information, WECC determined that CMCH did not have a documented PSMP that identifies which maintenance method is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. Additionally, CMCH does not have a PSMP that includes the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. The root cause of this issue was a lack of compliance oversight during the construction and commissioning process of the Facility in scope. WECC determined that this issue began on August 17, 2016, when CMCH was registered with NERC as a Generator Owner, while at the same time, failed to establish a PSMP for its Protection Systems identified in Section 4.2. Facilities, of the Standard. WECC determined that the end date of this issue was March 15, 2017, when CMCH created and established a PSMP, for a total of 210 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, CMCH failed to establish a PSMP for its Protection Systems as identified in Section 4.2. Facilities, of the Standard. CMCH does not operate any automatic reclosing or sudden pressure relaying systems. Failure to have an established PSMP could potentially result in degradation of equipment and/or the misoperation of the associated Protection System devices, resulting in the loss of its 156 MW Facility. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 156 MW solar facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that CMCH experienced a loss of its solar installation, system reliability would not be compromised. For these reasons, WECC determined that the potential impact had a low likelihood of causing intermediate harm. No harm is known to have occurred. WECC notes that CMCH does not have previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, CMCH: a. contracted with a third-party contractor to create a site-specific PSMP in accordance to PRC-005-6; and b. contracted with a third-party to oversee its NERC Compliance Program to ensure future compliance is maintained. WECC verified CMCH completed its Mitigation Activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Comanche Solar PV, LLC (CMCH) | NCR11665 | WECC2017017533 | PRC-019-2 | R1 | On May 3, 2017, CMCH submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, CMCH reported that during an internal investigation of its NERC compliance program it discovered that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its applicable Facility. CMCH failed to ensure that the construction and commissioning of the Facility was compliant with NERC Standards. CMCH partnered with a third-party to oversee the construction and commissioning of the facility, but third-party went out of business prior to completion, causing the construction and commissioning responsibilities to default back to CMCH, which then discovered the noncompliance. After reviewing all the relevant information, WECC determined that CMCH failed to verify that its in-service limiters are set to operate before the Protection System of the Facility and in-service Protection System devices are set to operate to isolate or de-energize equipment of its applicable Facility when they became registered. The root cause of this issue was a lack of compliance oversight during the construction and commissioning process for the Facility in scope. WECC determined that this issue began on August 17, 2016, when CMCH was registered with NERC as a Generator Owner, while at the same time, failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its applicable Facility. This issue ended on April 24, 2017, when CMCH completed coordination activities for its applicable Facility, for a total of 250 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, CMCH failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its one applicable Facility. Such failure could result the loss of the generator field and cause system instability, resulting in the loss of its 156 MW Facility. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 156 MW solar facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that CMCH experienced a loss of its solar installation, system reliability would not be compromised. Additionally, no inverter or relay settings changes were identified during the verification. For these reasons, WECC determined that the potential impact had a low likelihood of causing intermediate harm. No harm is known to have occurred. WECC notes that CMCH does not have previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, CMCH: a. completed coordinating its voltage regulating system with its generator capabilities and Protection System devices for its applicable Facility; b. contracted with a third-party to oversee its NERC Compliance Program to ensure future compliance is maintained; and c. contracted with a third-party to create a site-specific PRC-019 procedure. WECC verified CMCH completed its Mitigation Activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Comanche Solar PV, LLC (CMCH) | NCR11665 | WECC2017017531 | PRC-024-2 | R1 | On May 3, 2017, CMCH submitted Self-Certifications stating that, as a Generator Owner, it had possible issues of noncompliance with PRC-024-2 R1. Specifically, CMCH reported that during an internal investigation of its NERC compliance program, it discovered that it failed to set its frequency protective relaying in accordance with Attachment 1 and its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The “as found” settings of the noncompliant devices are described below: Device Type As Found Frequency Setting As Found Trip Time Inverter – Overfrequency 60.5kV .16 Second Relay – Overfrequency 60.5kV .66 Second Inverter – Underfrequency 59.3kV .16 Second Relay – Underfrequency 59.3kV .66 Second CMCH failed to ensure that the construction and commissioning of the Facility was compliant with NERC Standards. CMCH partnered with a third-party to oversee the construction and commissioning of the facility, but third-party went out of business prior to completion, causing the construction and commissioning responsibilities to default back to CMCH, which then discovered the noncompliance. After reviewing all relevant information, WECC determined that CMCH failed to set its frequency protective relaying in accordance with Attachment 1 and its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The root cause of this issue was a lack of compliance oversight during the construction and commissioning process for the Facility in scope. WECC determined that these issues began August 17, 2016, when CMCH was registered with NERC as a Generator Owner, while at the same time, failed to set its frequency and voltage protective relaying in accordance with PRC-024-2. WECC determined that the end date of this issue was April 3, 2017, when CMCH made settings changes to its frequency and voltage protective relaying to return to compliance, for a total of 229 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, CMCH failed to set its frequency and voltage protective relaying such that it would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to frequency or voltage excursions within the “no trip zone”. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 156 MW solar facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that CMCH experienced a loss of its solar installation, system reliability would not be compromised. For these reasons, WECC determined that the potential impact had a low likelihood of causing intermediate harm. No harm is known to have occurred. WECC notes that CMCH does not have previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, CMCH: a. completed the required verification activities and set its protective relay settings in accordance with PRC-024-2 Attachments 1 and 2 for its applicable Facility; b. contracted with a third-party to oversee its NERC Compliance Program to ensure future compliance is maintained; and c. contracted with a third-party to create a site-specific PRC-024 procedure. WECC verified CMCH completed its Mitigation Activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Comanche Solar PV, LLC (CMCH) | NCR11665 | WECC2017017532 | PRC-024-2 | R2 | On May 3, 2017, CMCH submitted Self-Certifications stating that, as a Generator Owner, it had possible issues of noncompliance with PRC-024-2 R2. Specifically, CMCH reported that during an internal investigation of its NERC compliance program, it discovered that it failed to set its frequency protective relaying in accordance with Attachment 1 and its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The “as found” settings of the noncompliant devices are described below: Device Type As Found Voltage Setting As Found Trip Time Inverter – Undervoltage 50% pu .1 Second Inverter – Undervoltage 88% pu 2 Seconds Relay – Undervoltage 88% pu 2.5 Seconds CMCH failed to ensure that the construction and commissioning of the Facility was compliant with NERC Standards. CMCH partnered with a third-party to oversee the construction and commissioning of the facility, but third-party went out of business prior to completion, causing the construction and commissioning responsibilities to default back to CMCH, which then discovered the noncompliance. After reviewing all relevant information, WECC determined that CMCH failed to set its frequency protective relaying in accordance with Attachment 1 and its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The root cause of this issue was a lack of compliance oversight during the construction and commissioning process for the Facility in scope. WECC determined that these issues began August 17, 2016, when CMCH was registered with NERC as a Generator Owner, while at the same time, failed to set its frequency and voltage protective relaying in accordance with PRC-024-2. WECC determined that the end date of this issue was April 3, 2017, when CMCH made settings changes to its frequency and voltage protective relaying to return to compliance, for a total of 229 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, CMCH failed to set its frequency and voltage protective relaying such that it would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to frequency or voltage excursions within the “no trip zone”. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 156 MW solar facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that CMCH experienced a loss of its solar installation, system reliability would not be compromised. For these reasons, WECC determined that the potential impact had a low likelihood of causing intermediate harm. No harm is known to have occurred. WECC notes that CMCH does not have previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, CMCH: a. completed the required verification activities and set its protective relay settings in accordance with PRC-024-2 Attachments 1 and 2 for its applicable Facility; b. contracted with a third-party to oversee its NERC Compliance Program to ensure future compliance is maintained; and c. contracted with a third-party to create a site-specific PRC-024 procedure. WECC verified CMCH completed its Mitigation Activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2017018851 | MOD-026-1 | R4 | On December 14, 2017, IPCO submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-026-1 R4. Specifically, IPCO reported that on December 8, 2016 a generation technician inadvertently made setting changes to the Power System Stabilizers (PSS) that altered the equipment response characteristics on Unit #1 at Hells Canyon Power Plant (HCPR) and did not provide revised model data to its Transmission Planner of the change to the excitation control system. This occurred when the technician installed and commissioned a new generator step-up (GSU) transformer at the facility. While troubleshooting an auto-sync issue following the installation of the GSU transformer, the technician unintentionally made changes to the generating unit's PSS power threshold settings that altered the equipment response characteristics. IPCO discovered this this issue on September 12, 2017 when the PSS for Unit #1 were not operating as expected. After reviewing all relevant information, WECC determined that IPCO failed to provide revised model data to its Transmission Planner within 180 calendar days of making changes to the excitation control system that alter the equipment’s response characteristic, as required by MOD-026-1 R4. The root cause of the noncompliance was due to infrequently performed steps being performed incorrectly. Specifically, the installation and commissioning of a new transformer does not happen very often at this plant therefore, an inadvertent change was made to the power system stabilizer (PSS) settings that was not readily noticed. WECC determined that this issue began on June 7, 2017, 181 days after IPCO adjusted the setting, and ended on September 12, 2017, when IPCO corrected the settings that were inadvertently changed, for a total of 97 days of noncompliance. Since the PSS settings were set back to the original setting, no notification to the Transmission Planner was necessary. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, IPCO failed to provide revised model data to its Transmission Planner within 180 calendar days of making changes to the excitation control system that alter the equipment’s response characteristic. Such failure could result in inaccurate representations of the unit’s excitation control system in IPCO’s Transmission Planning models. IPCO owns and operates approximately 3,740 MVA of generating capacity. However, a single generating unit at one facility with a nameplate rating of 145 MVA was subject to this instance. Therefore, WECC assessed the potential harm to the reliability and security of the BPS as minor. Additionally, IPCO’s Transmission Planning Engineer identified that the planning models do not utilize the lower ranges that were impacted by the modifications to the settings. Based on this, WECC determined that there was a low likelihood of causing minor harm. No harm is known to have occurred. | To remediate and mitigate this issue, IPCO: 1) corrected the PSS settings to what they were before they were inadvertently changed; 2) provided a copy of the Power Plant Control Equipment Change Procedure to all regional generation technicians and instructed them to read it; and 3) had the Power Supply Engineering Leader provide on-site training to all regional generation technicians on the Procedure to ensure that the requirements and implications were understood when changes to settings in control equipment are performed.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Power Watch, LLC (GWA) (NPGW) | NCR10395 | WECC2017017636 | BAL-002-2 | R2 | On May 23, 2017, NPGW submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-001-2 Requirement 2. Specifically, NPGW reported that it failed to operate such that its clock-minute average of reporting Area Control Error (ACE) did not exceed its clock-minute Balancing Authority ACE limit (BAAL) for more than 30 consecutive clock-limits. After reviewing all the relevant information, WECC determined that NPGW failed to operate such that its clock-minute average of reporting Area Control Error (ACE) did not exceed its clock-minute Balancing Authority ACE limit (BAAL) for more than 30 consecutive clock-limits. The first clock-minute started at 16:20 and the last consecutive clock-minute ended at 16:49. Starting at 16:35 and lasting for 12 minutes, the System Operator attempted to curtail all schedules reducing the Net Scheduled Interchange (NSI) to 0 MW for the purpose of avoiding reporting ACE exceeding its BAAL for more than 30 consecutive clock-minutes. However, there was a file transfer failure between NPGW’s internal tagging system to its Energy Management System (EMS). The new NSI should have been achieved at minute 28, however, this was not reflected in its EMS. During the 30th minute, the System Operator realized that the new schedules were not being pushed to the EMS properly, he implemented a manual interchange adjustment to force the 0 MW schedule. The noncompliance was identified during the 30th minute. The root cause of the noncompliance was the System Operator on duty’s failure to follow procedures. The System Operator assumed that the Reporting ACE calculation was fully implemented immediately after the data transfer and, therefore, did not verify the file transfer’s success. Had the System operator followed the documented procedure and verified the file transfers success, he would have immediately known it was unsuccessful and immediately implemented the EMS backup scheduler. This instance was not the first time there was a file transfer error and should have been more closely monitored. WECC determined that this issue began on December 22, 2016, when the clock-minute average of reporting ACE exceeded the clock-minute BAAL for more than 30 consecutive minutes. WECC determined that the end date of this issue is December 22, 2016, when the 0 MW ESI was manually pushed to the EMS, bringing the reporting ACE below the BAAL. This noncompliance lasted less than 60 seconds. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, NPGW failed to operate such that its clock-minute average of reporting Area Control Error (ACE) did not exceed its clock-minute Balancing Authority ACE limit (BAAL) for more than 30 consecutive clock-limits. Such failure could potentially result in an excursion of interconnection frequency out of defined limits. The main purpose of monitoring BAAL is to ensure Interconnection frequency is maintained by an entity balancing its resources and demand in Real-time so that its clock-minute average of its ACE does not exceed its BAAL for more than 30 consecutive minutes. Exceeding the BAAL for more than 30 consecutive clock-minutes could be due to an imbalance of resources and load. NPGW is responsible for balancing 206 MW of wind generation within its BA footprint. An imbalance of 206 MW of resource to load would be a minimal impact on Interconnection frequency. However, NPGW implemented good detective controls as NPGW's System Operators use EMS to calculate Reporting ACE and track the BAAL clock-minutes, and were actively monitoring the status of BAAL. If a frequency excursion was detected, NPGW would likely have corrected the condition as it was actively monitoring ACE and taking actions to reduce generation, and would have continued were a frequency excursion to occur. The scope of this noncompliance is 206 MW of wind generation. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that NPGW does not have any relevant previous violations of these or similar Standards and Requirements. | To mitigate this noncompliance, NPGW: 1) issued instructions to the System Operator to use the Backup Scheduler EMS function at least twice per shift to reinforce proper use; 2) created two separate alarms in EMS to alert if an issue arises from the file transfer process from the internal tagging system to the EMS; 3) conducted a meeting with senior management and System Operators to review processes and clarify that reliability remains paramount to the System Operator’s duties; and 4) System Operators were required to attend a BAAL incident avoidance training class. WECC verified the completion of all mitigation activity.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Power Watch, LLC (GWA) (NPGW) | NCR10395 | WECC2017017637 | BAL-004-WECC-02 | R1 | On May 23, 2017, NPGW submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-004-WECC-02 Requirement 1. Specifically, NPGW reported that it failed to verify that the absolute value of its Accumulated Primary Inadvertent Interchange (PIIaccum) for both the monthly On-Peak period was less than or equal to 150% of the its previous calendar year's integrated hourly peak generation. In September 2016, NPGW’s Accumulated On-peak monthly WECC Interchange Tool (WIT) inadvertent was greater than its allowed Pllaccum value. Late September 30, 2016, NPGW discovered its inadvertent energy values in EMS were reflecting different values than the WECC Interchange Tool (WIT). NPGW researched and discovered that the inadvertent accumulations for the portion of September 2016 that had already elapsed as of September 21, 2016, the date NPGW took over the BA function, were different than the accumulations as those reflected in WIT. NPGW had received the values representing the time before taking on the BA role from its prior third-party BA-service provider. NPGW worked with its prior third-party BA-service provider and its RC to try and resolve the discrepancy, but efforts to fully explain the difference were unsuccessful. NPGW's analysis concluded, however, that had the difference between the two accumulated values been reconciled on September 21, 2016, NPGW's margin of control would have resulted in full compliance with the Standard for September 2016. After reviewing all the relevant information, WECC determined that NPGW failed to verify that the absolute value of its Accumulated Primary Inadvertent Interchange (PIIaccum) for the monthly On-Peak period was individually less than or equal to 150% of the its previous calendar year's integrated hourly peak generation. The root cause of the noncompliance NPGW’s failure to train its System Operators to properly monitor the Accumulated Inadvertent values. NPGW System Operators were looking at the WIT, and not the EMS, when monitoring the Accumulated Inadvertent values. Additionally, when NPGW took over the BA function, it relied on the historical values provided by the former third-party BA services provider, however, these values were calculated in a different way than NPGW uses, and therefore, were not accurate for the purposes of calculating Pllaccum. WECC determined that this issue began on October 1, 2016, the first day of the month after NPGW failed to maintain the absolute value of its Accumulated Primary Inadvertent Interchange (PIIaccum) for both the monthly On-Peak period and the monthly Off-Peak period are each individually less than or equal to 150% of the previous calendar year's integrated hourly peak generation for the month of September 2016. WECC determined that the end date of this issue is November 1, 2016, the first day of the month after NPGW maintained the absolute value of its Accumulated Primary Inadvertent Interchange (PIIaccum) for both the monthly On-Peak period and the monthly Off-Peak period are each individually less than or equal to 150% of the previous calendar year's integrated hourly peak generation, for a total of 30 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NPGW failed to verify that the absolute value of its Accumulated Primary Inadvertent Interchange (PIIaccum) for the monthly On-Peak period was less than or equal to 150% of the its previous calendar year's integrated hourly peak generation. Such failure could potentially result in the excessive accumulation of Primary Inadvertent Interchange and the need for frequent manual time error corrections. Manual time error corrections have a likelihood of increasing frequency deviations and put the Interconnection at risk for other events However, NPGW implemented good detective controls to detect the above non-compliance. Specifically, NPGW's System Operator noticed that the Accumulated On-Peak and Off-Peak PII balances were not agreeing with the WIT values and began investigating the cause. Additionally, the Real-Time Manger monitors these values continuously during each shift to aid in detection of abnormal or excessive PIIaccum. The scope of this noncompliance is 206 MW of wind generation. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that NPGW does not have any relevant previous violations of these or similar Standards and Requirements. | To mitigate this noncompliance, NPGW: 1) Trained system operators on the transfer of accurate historical WIT data to the EMS and the proper way to monitor inadvertent values in the WIT with respect to time zones; and 2) trained System Operators of the proper settings configuration to view WIT and the proper criteria for making adjustments. WECC verified the completion of all mitigation activity.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Power Watch, LLC (GWA) (NPGW) | NCR10395 | WECC2017017638 | BAL-004-WECC-02 | R3 | On May 23, 2017, NPGW submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-004-WECC-02 Requirement 3. Specifically, NPGW reported that it failed to keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. NPGW’s ATEC was out of service for a total of 30 hours from October 3, 2016 at 06:50 PPT until October 4, 2016 at 12:59 PPT in Q4 of 2016. After reviewing all the relevant information, WECC determined that on September 30, 2016, NPGW discovered that the inadvertent energy value its EMS was reflecting and the value being reflected by the WECC Interchange Tool (WIT) were different, resulting in a potential noncompliance of BAL-004-WECC-02, R1. In an attempt to resolve the issue, NPGW decided to change the EMS inadvertent source configuration setting from official to non-official. At 17:04 on October 1, 2016, ATEC started to calculate a zero-inadvertent energy value. NPGW did not realize that this setting would cause ATEC to calculate a zero value. At 21:24 on October 1, 2016, the System Operator noticed ATEC reporting as zero and contacted the IT/OT department to try and resolve the issue. The System Operator also contacted the RC to inform them that NPGW was not participating in ATEC due to an EMS IT issue. In an attempt to fix the ATEC zero reporting issue, the Operations department, with the help of IT/OT department, disabled ATEC on October 3 at 06:50 PPT. NPGW had various internal and external meetings including with its third-party tagging service provider and EMS Vendor to try and find the cause of the issue and rectify the problem. During discussions with its EMS vendor, NPGW learned that the non-official inadvertent setting was causing the ATEC to calculate zero, and in light thereof, NPGW switched the inadvertent setting back to the official setting and enabled ATEC at 12:59 PPT on October 4, which resulted in ATEC being accurately calculated, and the RC was notified of the change. The root cause of the noncompliance was NPGW’s failure to understand the correlation between the EMS settings and the ATEC calculation. This issue happened within the first month of NPGW taking over the BA function and can be attributed to its lack of experience. WECC determined that this issue began on October 2, 2016, when the 25th hour of its Automatic Time Error Correction (ATEC) was out of service for the calendar quarter. WECC determined that the end date of this issue is January 1, 2017, when the next calendar quarter started, for a total of 91 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NPGW failed to keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. Such failure could potentially result in the excessive accumulation of Primary Inadvertent Interchange and the need for frequent manual time error corrections. Manual time error corrections have a likelihood of increasing frequency deviations and put the Interconnection at risk for other events. However, NPGW implemented good detective controls to detect the above non-compliance. A NPGW System Operator noticed that ATEC was reporting a zero value and contacted IT/OT to resolve the issue. The System Operator also contacted the RC to inform them that NPGW was not participating in ATEC due to an EMS IT issue. NPGW has implemented good compensating controls as NPGW’s System Operators continued to monitor ACE and Primary Inadvertent Interchange. The scope of this noncompliance is 206 MW of wind generation. Based on this, WECC determined that the potential harm had a moderate likelihood of occurring. No harm is known to have occurred. WECC notes that NPGW does not have any relevant previous violations of these or similar Standards and Requirements. | To mitigate this noncompliance, NPGW: 1) worked with OATI and its RC so that the inadvertent energy value is viewed with specific settings enabled in WIT for it to accurately reflect monthly accumulated inadvertent energy values and to ensure that the EMS configuration option setting used for inadvertent energy value is the official setting; 2) created an ATEC downtime tracking tool which is monitored by the Operations department that provides visibility to the Operations department and Compliance department; 3) issued a reminder to the System Operators of the Operations department's written procedure regarding the importance of tracking ATEC issues. Either the Compliance Manger of the Real-Time Manager discussed this reminder with each System Operator individually; and 4) provided initial training and continues providing monthly training on the documented procedures. WECC verified the completion of all mitigation activity.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Power Watch, LLC (GWA) (NPGW) | NCR10395 | WECC2017017639 | BAL-004-WECC-02 | R4 | On May 23, 2017, NPGW submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-004-WECC-02 Requirement 4. Specifically, NPGW reported that it failed to calculate its Automatic Time Error Correction term (IATEC) by 50 minutes after each hour. NPGW’s ATEC calculated a zero value from October 1, 2016 at 17:04 until October 3, 2016 at 06:50 and was not calculated at all from October 3, 2016 at 06:50 until October 4, 2016 at 12:59 due to EMS inadvertent source configuration settings changes. After reviewing all the relevant information, WECC determined that on September 30, 2016, NPGW discovered that the inadvertent energy value its EMS was reflecting and the value being reflected by the WECC Interchange Tool (WIT) were different, resulting in a potential noncompliance of BAL-004-WECC-02, R1. In an attempt to resolve the issue, NPGW decided to change the EMS inadvertent source configuration setting from official to non-official. At 17:04 on October 1, 2016, ATEC started to calculate a zero value, making the Automatic Time Error Correction term (IATEC) impossible to calculate 50 minutes after each hour. NPGW did not realize that this setting would cause IATEC to calculate a zero value. At 21:24 on October 1, 2016, the System Operator noticed IATEC reporting as zero and contacted the IT/OT department to try and resolve the issue. The System Operator also contacted the RC to inform them that NPGW was not participating in IATEC due to an EMS IT issue. In an attempt to fix the IATEC zero reporting issue, the Operations department, with the help of IT/OT department, disabled IATEC on October 3 at 06:50 PPT. NPGW had various internal and external meetings including with its third-party tagging service provider and EMS Vendor to try and find the cause of the issue and rectify the problem. During discussions with its EMS vendor, NPGW learned that the non-official inadvertent setting was causing the inadvertent energy value to calculate zero, and in light thereof, NPGW switched the inadvertent setting back to the official setting and enabled IATEC at 12:59 PPT on October 4, which resulted in IATEC again being calculated, and the RC was notified. The root cause of the noncompliance was NPGW’s failure to understand the correlation between the EMS settings and the IATEC calculation. This issue happened within the first month of NPGW taking over the BA function and can be attributed to its lack of experience. WECC determined that this issue began on October 1, 2016, when NPGW made EMS settings changes causing the ATEC to report a zero value and fail. WECC determined that the end date of this issue is October 4, 2016, when NPGW enabled the ATEC, for a total of 4 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NPGW failed to calculate its Automatic Time Error Correction term (IATEC) by 50 minutes after each hour. Such failure could potentially result in the incorrect calculation of Primary Inadvertent Interchange and the need for frequent manual time error corrections. Manual time error corrections have a likelihood of increasing frequency deviations and put the Interconnection at risk for other events. However, NPGW implemented good detective controls. Specifically, NPGW's System Operator noticed that ATEC was reporting a zero value and contacted IT/OT to resolve the issue. The System Operator also contacted the RC to inform them that NPGW was not participating in ATEC due to an EMS IT issue. Additionally, NPGW has implemented good compensating controls. Specifically, the NPGW's System Operator continued to monitor ACE and Primary Inadvertent Interchange. The scope of this noncompliance is 206 MW of wind generation. Based on this, WECC determined that the potential harm had a moderate likelihood of occurring. No harm is known to have occurred. WECC notes that NPGW does not have any relevant previous violations of these or similar Standards and Requirements. | To mitigate this noncompliance, NPGW: 1) worked with OATI and its RC so that inadvertent energy value is viewed with specific settings enabled in WIT for it to accurately reflect monthly accumulated inadvertent energy and to ensure that the EMS configuration option setting used for inadvertent energy value is the official setting; 2) issued a reminder to the System Operators of the Operations department's written procedure regarding the importance of tracking ATEC issues. Either the Compliance Manger or the Real-Time Manager discussed this reminder with each System Operator individually. 3) created an ATEC downtime tracking tool which is monitored by the Operations department that provides visibility to the Operations department and Compliance department; and 4) Provided initial training and continues providing monthly training on the documented procedures. WECC verified completion of all mitigation activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Power Watch, LLC (GWA) (NPGW) | NCR10395 | WECC2016016578 | EOP-008-1 | R1 | During a Compliance Audit conducted from October 4, 2016 through October 5, 2016, WECC determined that NPGW, as a Balancing Authority, was in noncompliance with EOP-008-1 Requirement 1. WECC found that NPGW failed to have an Operating Plan that met the minimum requirements for backup functionality and performance of the functional obligations with regards to the reliable operations of the BES in the event that its primary control center functionality is lost. Specifically, NPGW did not identify the power source(s) or physical and cyber security elements required to support the backup functionality. Additionally, NPGW did not identify the transition period between the loss of primary control center functionality and the time to implement the backup functionality to specify that it is less than or equal to two hours. Lastly, NPGW failed to identify the required actions to be taken during the period between the loss of primary control center functionality and the time to fully implement backup functionality. The minimal required transitional actions include: a list of entities to notify when there is a change in operating locations; actions to manage the risk to the BES during the transition from primary to backup functionality as well as during outages of either control center; and identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. After reviewing all the relevant information, WECC determined that NPGW outsources its BA backup functions to a third-party, which was also found in violation of this Standard and Requirement. While NERC allows BA’s to contract backup control center functionality, NPGW is still responsible for ensuring that the contracted backup control center functionality is compliant with the standard1. Additionally, the Operating Plan presented at audit outlined that backup functionality will be transferred to a dedicated laptop, however, the Standard and NERC Order2 state that backup functionality must be at a “facility.” The use of a laptop computer does not meet the requirement that backup functionality be “capable of operating for a prolonged period, and providing functionality sufficient to maintain compliance with all Reliability Standards that depend on primary control functionality.” The root cause of the noncompliance NPGW’s failure to ensure that the contracted backup control center functionality met the requirements of the Standard. WECC determined that this issue began on July 1, 2013, when the Standard became mandatory and enforceable. WECC determined that the end date of this issue is September 21, 2016, when NPGW took the backup control center functionality inhouse, for a total of 1,178 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, NPGW failed to have an Operating Plan that met the minimum requirements for backup functionality and performance of the functional obligations with regards to the reliable operations of the BES in the event that its primary control center functionality is lost. Such failure would not fully implement the backup functionality within the required transition period. Specifically, the contracted entity will not be able to have power sources and physical and cyber security controls in place within two hours. Additionally, the personnel tasked with transferring functions to the backup control center may not understand the time requirement, personnel roles or who to notify of the change, prolonging the risk of a loss of generation or load. However, failure to fully implement the backup functionality within an adequate timeframe could potentially result in the delay or failure in performing BA functional obligations for 206 MW of generation. This may in turn result in the loss of 206 MW of generation/load due to failure in scheduling the generation appropriately. The contracted entity had an interim plan in place to mitigate risk to the BPS while it was in the process of making the backup control center fully functional. Based on this, WECC determined that the potential harm had a moderate likelihood of occurring. No harm is known to have occurred. WECC notes that NPGW does not have any relevant previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, NPGW: 1) performed a corporate risk analysis to identify risks associated with outsourcing the backup control center functionality to a third party; 2) decided to bring in the BA in-house and purchased an EMS; 3) hired, trained, and certified System Operators; and 4) obtained WECC certification for the BA function. WECC verified completion of the Mitigation Plan.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Wind Watch, LLC (NWIND) | NCR11382 | WECC2017017640 | BAL-001-2 | R2 | On May 23, 2017, NWIND submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-001-2 Requirement 2. Specifically, NWIND reported that it failed to operate such that its clock-minute average of reporting Area Control Error (ACE) did not exceed its clock-minute Balancing Authority ACE limit (BAAL) for more than 30 consecutive clock-limits. Specifically, NWIND reported four separate instances where its BAAL exceeded its ACE for at least 30 consecutive clock minutes: 1. October 4, 2016 for 30 minutes – the BAAL timer reset in the 30th minute; 2. October 14, 2016 for 35 minutes; 3. October 19, 2016 for 30 minutes – the BAAL timer reset in the 30th minute; and 4. March 6, 2017 for 32 minutes. Instance 1: On October 4, 2016 NWIND's ACE exceeded its BAAL for slightly greater than 30 consecutive clock-minutes. The first clock-minute started at 05:06PPT and the last consecutive clock-minute ended at 05:35PPT. At 05:29PPT NWIND's the System Operator submitted a tag curtailment. This curtailment was implemented into NWIND's Energy Management System (EMS) at 05:32PPT, however, an additional tag curtailment was necessary and submitted at 05:34PPT to ensure that ACE was within BAAL, the updated Net Scheduled Interchange (NSI) did not get transferred into the EMS until 05:35PPT. The reset of the BAAL timer occurred in minute 30. Instance 2: On October 14, 2016 a significant and unexpected loss of wind event occurred. Due to the inability to call on reserves as a "loss of fuel event" for such events, NWIND was forced to quickly curtail schedules. NWIND's ACE exceeded its BAAL for 35 consecutive clock-minutes. The first clock-minute started at 20:39PPT and the last consecutive clock-minute ended at 21:13PPT. The System Operator curtailed schedules which reduced ACE but the System Operator was concerned the curtailments were not being implemented properly in EMS so he then utilized the Backup Scheduler EMS function around 21:08. However, the System Operator entered the current NSI value in the Backup Scheduler and EMS did not reflect the additional curtailments. If the System Operator had not enabled Backup Scheduler, it appears the BAAL consecutive clock-minutes would have cleared prior to 30 consecutive minutes. The System Operator had initially curtailed the appropriate amount of schedules. However, with the Backup Scheduler in place, the BAAL timer did not clear until minute 35. Instance 3: On November 19, 2016 NWIND's ACE exceeded its BAAL for slightly greater than 30 consecutive clock minutes. The first clock-minute started at 22:12PPT and the last consecutive clock-minute ended at 22:41PPT. This event was caused by a problem which appeared during an automatic failover from the primary EMS to the secondary EMS. When this occurred, the secondary EMS failed to send the AGC set point to the generators' PLCs. The System Operator noticed that AGC was not reducing generation to recover NWIND's ACE to zero. The System Operator decided to take AGC into manual control to mitigate the issue by trying to reduce generation. Even in AGC manual control, the reduction of generation was still unsuccessful at 22:40 PPT (i.e., 29 consecutive clock minutes). Once the System Operator determined AGC was unable to move generation, the System Operator decided to control the facilities through the Wind Farm Management SCADA system which can be used as a backup system. By using SCADA, NWIND generation was reduced to the appropriate level, resetting the BAAL consecutive clock minutes to zero. However, the BAAL timer reset did not occur until minute 30. Instance 4: On March 6, 2017 NWIND's ACE exceeded its BAAL for 32 consecutive clock minutes. The first clock minute started at 22:58PPT and the last consecutive clock minute ended at 23:29 PPT. At 23:20 PPT, the System Operator attempted to curtail multiple schedules through NWIND's internal tagging system. However, the System Operator noticed the system's rapid curtailment feature, which allows System Operators to cut multiple tags at once, did not curtail the schedules at 23:22 PPT due to an entry error by the System Operator. The System Operator then decided to start to curtail schedules individually. The EMS Backup Scheduler function was also enabled to ensure the new schedules' updated NSI were represented in EMS. However, the System Operator entered the incorrect date (March 22, 2017 instead of March 6, 2017) at 23:26 PPT. The System Operator subsequently discovered the mistake and corrected the date in the EMS Backup Scheduler function at 23:29 PPT. At 23:29 PPT (i.e., consecutive minute 32), the BAAL consecutive clock minutes reset to zero. After reviewing all the relevant information, WECC determined that NWIND failed to operate such that its clock-minute average of reporting ACE did not exceed its clock-minute BAAL for more than 30 consecutive clock-limits on four occasions. The root cause of each instance of noncompliance was NWIND’s failure to act promptly when addressing the BAAL exceedances. Had the System Operator reacted more promptly to the BAAL exceedances, the actions taken would have remediated the issues prior to the ACE exceeding the BAAL for more than 30 clock-minutes. Additionally, Instances one, two, and four were further exacerbated due to the System Operator was not properly trained to curtail scheduling once the issues were identified. Lastly, instance four was exacerbated due to human error, as the System Operator entered the incorrect date into NSI. WECC determined that each of the four instances of noncompliance started and ended on different dates as outlined in the table below: Instance Number Start Date End Date Noncompliance Duration 1 October 4, 2016 October 4, 2016 Less than one minute 2 October 14, 2016 October 14, 2016 Five minutes 3 October 19, 2016 October 19, 2016 Less than 1 minute 4 March 6, 2017 March 6, 2017 Two minutes | WECC determined that these instances of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, NWIND failed to operate such that its clock-minute average of reporting ACE did not exceed its clock-minute BAAL for more than 30 consecutive clock-limits on four occasions. Such failure could potentially result in an excursion of interconnection frequency out of defined limits. The main purpose of monitoring BAAL is to ensure Interconnection frequency is maintained by an entity balancing its resources and demand in Real-time so that its clock-minute average of its ACE does not exceed its BAAL for more than 30 consecutive minutes. Exceeding the BAAL for more than 30 consecutive clock-minutes could be due to an imbalance of resources and load. However, NWIND implemented good preventative controls to prevent the above consequence from occurring. Specifically, NWIND’s System Operators were monitoring the Reporting ACE and the BAAL, even though weren't able to recover the ACE prior to exceeding 30 consecutive clock-minutes due to their lack of training. Additionally, NWIND implemented good detective controls as NWIND's System Operators use EMS to calculate Reporting ACE and track the BAAL clock-minutes, and were actively monitoring the status of BAAL. If a frequency excursion was detected, NWIND would likely have corrected the condition as it was actively monitoring ACE and taking actions to reduce generation and would have continued were a frequency excursion to occur. NWIND is responsible for balancing 186 MW of wind generation within its BA footprint. An imbalance of 186 MW of resource to load would be a minimal impact on Interconnection frequency. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that NWIND does not have any relevant previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, NWIND: a. issued instructions to the System Operator to use the Backup Scheduler EMS function at least twice per shift to reinforce proper use; b. created three separate alarms in EMS initiated by the BAAL clock-minute that sound continuously until acknowledged by the System Operator; c. created two separate alarms in EMS to alert if an issue arises from the file transfer process from the internal tagging system to the EMS; d. conducted a meeting with senior management and System Operators to review processes and clarify that reliability remains paramount to the System Operator’s duties; and e. System Operators were required to attend a BAAL incident avoidance training class. WECC verified completion of the Mitigating Activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Wind Watch, LLC (NWIND) | NCR11382 | WECC2017017641 | BAL-004-WECC-02 | R3 | On May 23, 2017, NWIND submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-004-WECC-02 Requirement 3. Specifically, NWIND reported that it failed to keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. NWIND’s ATEC was out of service for a total of 30 hours from October 3, 2016 at 06:50 PPT until October 4, 2016 at 12:59 PPT in Q4 of 2016. After reviewing all the relevant information, WECC determined that on September 30, 2016, NWIND discovered that the inadvertent energy value its EMS was reflecting and the value being reflected by the WECC Interchange Tool (WIT) were different. In an attempt to resolve the issue, NWIND decided to change the EMS inadvertent source configuration setting from official to non-official. At 17:04 on October 1, 2016, ATEC started to calculate a zero-inadvertent energy value. NWIND did not realize that this setting would cause ATEC to calculate a zero value. At 21:24 on October 1, 2016, the System Operator noticed ATEC reporting as zero and contacted the IT/OT department to try and resolve the issue. The System Operator also contacted the RC to inform them that NWIND was not participating in ATEC due to an EMS IT issue. In an attempt to fix the ATEC zero reporting issue, the Operations department, with the help of IT/OT department, disabled ATEC on October 3 at 06:50 PPT. NWIND had various internal and external meetings including with its third-party tagging service provider and EMS Vendor to try and find the cause of the issue and rectify the problem. During discussions with its EMS vendor, NWIND learned that the non-official inadvertent setting was causing the ATEC to calculate zero, and in light thereof, NWIND switched the inadvertent setting back to the official setting and enabled ATEC at 12:59 PPT on October 4, which resulted in ATEC being accurately calculated, and the RC was notified of the change. The root cause of the noncompliance was NWIND’s failure to understand the correlation between the EMS settings and the ATEC calculation. This issue happened within the first month of NWIND taking over the BA function and can be attributed to its lack of experience. WECC determined that this issue began on October 2, 2016, when the 25th hour of its Automatic Time Error Correction (ATEC) was out of service for the calendar quarter. WECC determined that the end date of this issue is January 1, 2017, when the next calendar quarter started, for a total of 91 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NWIND failed to keep its Automatic Time Error Correction (ATEC) in service, with an allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter for ATEC to be out of service. Such failure could potentially result in the excessive accumulation of Primary Inadvertent Interchange and the need for frequent manual time error corrections. Manual time error corrections have a likelihood of increasing frequency deviations and put the Interconnection at risk for other events. However, NWIND implemented good detective controls to detect the above non-compliance. A NWIND System Operator noticed that ATEC was reporting a zero value and contacted IT/OT to resolve the issue. The System Operator also contacted the RC to inform them that NWIND was not participating in ATEC due to an EMS IT issue. NWIND has implemented good compensating controls as NWIND’s System Operators continued to monitor ACE and Primary Inadvertent Interchange. The scope of this noncompliance is 206 MW of wind generation. Based on this, WECC determined that the potential harm had a moderate likelihood of occurring. No harm is known to have occurred. WECC notes that NWIND does not have any relevant previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, NWIND: a. worked with OATI and its RC so that the inadvertent energy value is viewed with specific settings enabled in WIT for it to accurately reflect monthly accumulated inadvertent energy values and to ensure that the EMS configuration option setting used for inadvertent energy value is the official setting; b. created an ATEC downtime tracking tool which is monitored by the Operations department that provides visibility to the Operations department and Compliance department; c. issued a reminder to the System Operators of the Operations department's written procedure regarding the importance of tracking ATEC issues. Either the Compliance Manger of the Real-Time Manager discussed this reminder with each System Operator individually; and d. provided initial training and continues providing monthly training on the documented procedures. WECC verified completion of the Mitigation Plan.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Wind Watch, LLC (NWIND) | NCR11382 | WECC2017017642 | BAL-004-WECC-02 | R4 | On May 23, 2017, NWIND submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-004-WECC-02 Requirement 4. Specifically, NWIND reported that it failed to calculate its Automatic Time Error Correction term (IATEC) by 50 minutes after each hour. NWIND’s ATEC calculated a zero value from October 1, 2016 at 17:04 until October 3, 2016 at 06:50 and was not calculated at all from October 3, 2016 at 06:50 until October 4, 2016 at 12:59 due to EMS inadvertent source configuration settings changes. After reviewing all the relevant information, WECC determined that on September 30, 2016, NWIND discovered that the inadvertent energy value its EMS was reflecting and the value being reflected by the WIT were different. In an attempt to resolve the issue, NWIND decided to change the EMS inadvertent source configuration setting from official to non-official. At 17:04 on October 1, 2016, ATEC started to calculate a zero value, making the Automatic Time Error Correction term (IATEC) impossible to calculate 50 minutes after each hour. NWIND did not realize that this setting would cause IATEC to calculate a zero value. At 21:24 on October 1, 2016, the System Operator noticed IATEC reporting as zero and contacted the IT/OT department to try and resolve the issue. The System Operator also contacted the RC to inform them that NWIND was not participating in IATEC due to an EMS IT issue. In an attempt to fix the IATEC zero reporting issue, the Operations department, with the help of IT/OT department, disabled IATEC on October 3 at 06:50 PPT. NWIND had various internal and external meetings including with its third-party tagging service provider and EMS Vendor to try and find the cause of the issue and rectify the problem. During discussions with its EMS vendor, NWIND learned that the non-official inadvertent setting was causing the inadvertent energy value to calculate zero, and in light thereof, NWIND switched the inadvertent setting back to the official setting and enabled IATEC at 12:59 PPT on October 4, which resulted in IATEC again being calculated, and the RC was notified. The root cause of the noncompliance was NWIND’s failure to understand the correlation between the EMS settings and the IATEC calculation. This issue happened within the first month of NWIND taking over the BA function and can be attributed to its lack of experience. WECC determined that this issue began on October 1, 2016, when NWIND made EMS settings changes causing the ATEC to report a zero value and fail. WECC determined that the end date of this issue is October 4, 2016, when NWIND enabled the ATEC, for a total of 4 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NWIND failed to calculate its Automatic Time Error Correction term (IATEC) by 50 minutes after each hour. Such failure could potentially result in the incorrect calculation of Primary Inadvertent Interchange and the need for frequent manual time error corrections. Manual time error corrections have a likelihood of increasing frequency deviations and put the Interconnection at risk for other events. However, NWIND implemented good detective controls. Specifically, NWIND's System Operator noticed that ATEC was reporting a zero value and contacted IT/OT to resolve the issue. The System Operator also contacted the RC to inform them that NWIND was not participating in ATEC due to an EMS IT issue. Additionally, NWIND has implemented good compensating controls. Specifically, the NWIND's System Operator continued to monitor ACE and Primary Inadvertent Interchange. The scope of this noncompliance is 206 MW of wind generation. Based on this, WECC determined that the potential harm had a moderate likelihood of occurring. No harm is known to have occurred. WECC notes that NWIND does not have any relevant previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, NWIND: a. worked with OATI and its RC so that inadvertent energy value is viewed with specific settings enabled in WIT for it to accurately reflect monthly accumulated inadvertent energy and to ensure that the EMS configuration option setting used for inadvertent energy value is the official setting; b. issued a reminder to the System Operators of the Operations department's written procedure regarding the importance of tracking ATEC issues. Either the Compliance Manger or the Real-Time Manager discussed this reminder with each System Operator individually. c. created an ATEC downtime tracking tool which is monitored by the Operations department that provides visibility to the Operations department and Compliance department; and d. Provided initial training and continues providing monthly training on the documented procedures. WECC verified completion of the Mitigating Activities.
2018-08-30 | Western Electricity Coordinating Council (WECC) | NaturEner Wind Watch, LLC (NWIND) | NCR11382 | WECC2016016579 | EOP-008-1 | R1 | During a Compliance Audit conducted from October 4, 2016 through October 5, 2016, WECC determined that NWIND, as a Balancing Authority, was in noncompliance with EOP-008-1 Requirement 1. WECC found that NWIND failed to have an Operating Plan that met the minimum requirements for backup functionality and performance of the functional obligations with regards to the reliable operations of the BES in the event that its primary control center functionality is lost. Specifically, NWIND did not identify the power source(s) or physical and cyber security elements required to support the backup functionality. Additionally, NWIND did not identify the transition period between the loss of primary control center functionality and the time to implement the backup functionality to specify that it is less than or equal to two hours. Lastly, NWIND failed to identify the required actions to be taken during the period between the loss of primary control center functionality and the time to fully implement backup functionality. The minimal required transitional actions include: a list of entities to notify when there is a change in operating locations; actions to manage the risk to the BES during the transition from primary to backup functionality as well as during outages of either control center; and identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. After reviewing all the relevant information, WECC determined that NWIND outsources its BA backup functions to a third-party, which was also found in violation of this Standard and Requirement. While NERC allows BA’s to contract backup control center functionality, NWIND is still responsible for ensuring that the contracted backup control center functionality is compliant with the standard. Additionally, the Operating Plan presented at audit outlined that backup functionality will be transferred to a dedicated laptop, however, the Standard and NERC Order state that backup functionality must be at a “facility.” The use of a laptop computer does not meet the requirement that backup functionality be “capable of operating for a prolonged period, and providing functionality sufficient to maintain compliance with all Reliability Standards that depend on primary control functionality.” The root cause of the noncompliance NWIND’s inadequate oversight of the third-party backup control center function provider to ensure the requirements of the Standard were met. WECC determined that this issue began on October 2, 2013, when NWIND registered as a Balancing Authority. WECC determined that the end date of this issue is September 21, 2016, when NWIND took the backup control center functionality inhouse, for a total of 1,085 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NWIND failed to have an Operating Plan that met the minimum requirements for backup functionality and performance of the functional obligations with regards to the reliable operations of the BES in the event that its primary control center functionality is lost. Such failure would not fully implement the backup functionality within the required transition period. Specifically, the contracted entity will not be able to have power sources and physical and cyber security controls in place within two hours. Additionally, the personnel tasked with transferring functions to the backup control center may not understand the time requirement, personnel roles or who to notify of the change, prolonging the risk of a loss of generation or load. Failure to fully implement the backup functionality within an adequate timeframe could potentially result in the delay or failure in performing BA functional obligations for 206 MW of generation. This may in turn result in the loss of 206 MW of generation/load due to failure in scheduling the generation appropriately. However, the contracted entity had a sufficient interim plan in place to mitigate risk to the BPS while it was in the process of making the backup control center fully functional. Based on this, WECC determined that the potential harm had a moderate likelihood of occurring. No harm is known to have occurred. WECC notes that NWIND does not have any relevant previous violations of these or similar Standards and Requirements. | To remediate and mitigate this issue, NWIND: a. performed a corporate risk analysis to identify risks associated with outsourcing the backup control center functionality to a third party; b. decided to bring in the BA in-house and purchased an EMS; c. hired, trained, and certified System Operators; and d. obtained WECC certification for the BA function. WECC verified completion of the Mitigation Plan.
2018-08-30 | Western Electricity Coordinating Council (WECC) | USACE - Walla Walla District (UNWW) | NCR05540 | WECC2017017158 | MOD-025-2 | R1 | On February 28, 2017, UNWW submitted Self-Certifications stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 R1 and R2. Specifically, UNWW reported that It had failed to verify the Real Power and Reactive Power capabilities of at least 40% of its applicable facilities in accordance with Attachment 1 of the Standard. After reviewing all relevant information, WECC determined that UNWW failed to verify the Real Power and Reactive Power capabilities of its applicable facilities, in accordance with Attachment 1 of the Standard. The root cause of these issues of noncompliance was UNWW’s misunderstanding of the Standard’s requirements. Specifically, UNWW thought that its implementation of the WECC Generating Unit Model Validation Program met the requirements of these Standard. WECC determined that these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for UNWW’s applicable facilities, and ended on May 25, 2017 when UNWW completed verification activities, for a total of 329 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In these instances, UNWW failed to verify the Real Power and Reactive Power capabilities for at least 17 of its 41 applicable facilities in accordance with Attachment 1 of the Standard. Such failures could potentially result in inaccurate information of generator gross and net Real Power and Reactive Power capabilities used in planning models to assess BPS reliability. Inaccurate information would result in inaccurate models; therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, UNWW has implemented the WECC Generating Unit Model Validation testing for its applicable facilities in the past; therefore, if a real-time contingency that required the generating unit to respond were to occur, the current data would be satisfactory for mitigating the contingency. Additionally, UNWW has previously provided the Transmission Planner with the required model information for all units conducted for previous testing. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, UNWW: 1.) created test schedule for each unit to include tested and future scheduled test dates; 2.) verified Real Power and Reactive Power capabilities for 29 applicable facilities; 3.) generated report results and submitted its verifications to its Transmission Planner; and 4.) created a testing schedule for the remaining 12 facilities to prevent recurrence of missed test. WECC verified completion of the Mitigation Activities on July 14, 2017.
2018-08-30 | Western Electricity Coordinating Council (WECC) | USACE - Walla Walla District (UNWW) | NCR05540 | WECC2017017159 | MOD-025-2 | R2 | On February 28, 2017, UNWW submitted Self-Certifications stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 R1 and R2. Specifically, UNWW reported that It had failed to verify the Real Power and Reactive Power capabilities of at least 40% of its applicable facilities in accordance with Attachment 1 of the Standard. After reviewing all relevant information, WECC determined that UNWW failed to verify the Real Power and Reactive Power capabilities of its applicable facilities, in accordance with Attachment 1 of the Standard. The root cause of these issues of noncompliance was UNWW’s misunderstanding of the Standard’s requirements. Specifically, UNWW thought that its implementation of the WECC Generating Unit Model Validation Program met the requirements of these Standard. WECC determined that these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for UNWW’s applicable facilities, and ended on May 25, 2017 when UNWW completed verification activities, for a total of 329 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In these instances, UNWW failed to verify the Real Power and Reactive Power capabilities for at least 17 of its 41 applicable facilities in accordance with Attachment 1 of the Standard. Such failures could potentially result in inaccurate information of generator gross and net Real Power and Reactive Power capabilities used in planning models to assess BPS reliability. Inaccurate information would result in inaccurate models; therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, UNWW has implemented the WECC Generating Unit Model Validation testing for its applicable facilities in the past; therefore, if a real-time contingency that required the generating unit to respond were to occur, the current data would be satisfactory for mitigating the contingency. Additionally, UNWW has previously provided the Transmission Planner with the required model information for all units conducted for previous testing. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, UNWW: 1.) created test schedule for each unit to include tested and future scheduled test dates; 2.) verified Real Power and Reactive Power capabilities for 29 applicable facilities; 3.) generated report results and submitted its verifications to its Transmission Planner; and 4.) created a testing schedule for the remaining 12 facilities to prevent recurrence of missed test. WECC verified completion of the Mitigation Activities on July 14, 2017.
2018-07-31 | Florida Reliability Coordinating Council, Inc. (FRCC) | General Electric International - Shady Hills (GEI-SH) | NCR00069 | FRCC2018019575 | PRC-005-6 | R3. | On April 23, 2018, GEI-SH submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-005-6 R3. This noncompliance started on January 1, 2018, while the plant was being operated by NAES Corp. and registered under the name NAES Corporation – Shady Hills (NCSH), when NCSH failed to complete a relay calibration within the 6-year time frame. General Electric International assumed operation of the plant on February 12, 2018, registering as GO under the name of General Electric International – Shady Hills (GEISH), and the violation continued until the relay calibration was performed on April 25, 2018. Specifically, during a review of PRC-005 requirements on April 23, 2018, GEI-SH discovered that one (1) of 204 (.5%) protection system devices for an unmonitored analog relay calibration was not performed as required by PRC-005-6 R3, Table 1-1. The device, a 230 kV MFAC 87 Bus Differential relay, was one of four required to be tested within a six (6) calendar year time frame. All four 6-year relays were calibrated in 2011 and due for calibration in the fall of 2017 but were rescheduled based on the new PRC-005-6 periodicity requirements (i.e. 12-year for monitored relays). However, only three of the four relays that were rescheduled fell under the new PRC-005-6 frequency (Table 1-1). The 230 kV MFAC 87 Bus Differential relay does not fall under the new 12-year periodicity since it is an unmonitored analog relay. The scheduled testing date for the relay in question was inadvertently pushed out with the other three digitally monitored relays. Once discovered, the relay was tested/calibrated on April 25, 2018 (113 days late). The root cause for this noncompliance was personnel confusion in the different PRC-005-6 implementation requirements for relay calibration testing of monitored and unmonitored relays. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because upon testing of the relay the results were all within the relay specifications. In addition, all other relays within this protection zone were current with their testing, as well as the associated current transformers and potential transformers. The entity did not experience a loss of load, generation or transmission elements, no system disturbances, protection system operations or misoperations, and no BES emergency condition prior to, during, or as a result of the delayed testing. GEI-SH’s total generation output of 540 MWs represents only 1.04% of the Region. FRCC determined that GEI-SH's compliance history should not serve as a basis for applying a penalty. No harm is known to have occurred. | To mitigate this noncompliance, GEI-SH: 1) calibrated the 230 kV MFAC 87 Bus Differential relay; 2) contacted the TO, Duke Energy, to coordinate the relay testing and to verify the test method; and 3) created a task in the web-based automated compliance tool to review the spreadsheet containing the list of relays during the first quarter of each year to allow the site to determine what relays need to be tested the following year, and to identify any relays that require scheduling during the current years' Fall outage.
2018-07-31 | Florida Reliability Coordinating Council, Inc. (FRCC) | Lake Worth, City of (LWU) | NCR00043 | FRCC2018019602 | EOP-004-3 | R1. | On April 30, 2018, LWU submitted a Self-Report stating that, as a Generation Owner, Generation Operator, Transmission Owner, and a Distribution Provider, it was in noncompliance with EOP-004-3 R1. This noncompliance started on April 1, 2017 (Standard Enforcement Date), when LWU failed to have an Event Reporting Operating Plan (plan) that included all elements as required by EOP-004-3 R1 Attachment 1 and ended on December 6, 2017, when LWU revised the plan. Due to LWU’s size and registrations, the plan should have included Electric Reliability Organization (ERO) and Florida Reliability Coordinating Council (RRO) reporting protocols of multiple event types such as damage or destruction of a facility, physical threats to a facility or BES emergency requiring public appeal for load reduction. The cause for this noncompliance was staffing turnover in the area of compliance oversight and lack of management oversight to ensure Standards/Requirements are being reviewed and appropriate controls being put in place to address. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was minimal as LWU had an operating plan based on an inactive Standard that did not include all of the elements required by EOP-004-3. LWU has a peak load of 100MW, less than 50MW of UFLS, and less than 30,000 customers. FRCC determined that LWU's compliance history should not serve as a basis for applying a penalty. No harm is known to have occurred. | To mitigate this noncompliance, LWU: 1) revised and implemented the Event Reporting Operating Plan; 2) hired a 3rd party vendor to assist in development and implementation of a systematic tracking of the NERC standards; 3) established a reminder through its asset management software, set to display at a 9 calendar month interval from the date of last EOP-004-3 review; and 4) updated the compliance team consisting of two primary compliance officers instead of a single compliance officer to assure redundancy.
2018-07-31 | Florida Reliability Coordinating Council, Inc. (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2018019358 | PRC-006-1 | R9. | On March 5, 2018, VERO submitted a Self-Certification stating that, as a Transmission Owner and Distribution Provider (DP), it was in noncompliance with PRC-006-1 R9. This noncompliance started on October 1, 2013, when VERO failed to properly set the time delay of their Under-Frequency Load Shedding (UFLS) relays to provide automatic tripping of load in accordance with the UFLS program as determined by its Planning Coordinator (PC). The noncompliance ended on February 23, 2018 (1606 days), when VERO adjusted the time delay for the UFLS relays to meet Planning Coordinator parameters. Specifically, VERO’s relay test records indicate that, of the 16 UFLS relays, eight (8) (50%) had a total time delay greater than 0.28 seconds as tested and thus were outside of tripping testing parameter limits as required by PRC-006 R9 and the limits set by the FRCC UFLS program of 0.1-0.28 seconds (where the total time delay = intentional delay + relay delay + breaker delay). The cause for this noncompliance was the failure of VERO to recognize the relays were incorrectly set not recognizing the individual time delays would exceed the required total time delay. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because if a UFLS event had occurred all the required load would have shed just not within the proper time requirement. 50% of VERO's UFLS relays would have shed load within the 0.1 to 0.28 second time delay requirement, while the remaining 50% would have shed load slower (.38 seconds) than required. Furthermore, there were no UFLS events during the period of noncompliance. VERO’s 92 MWS of UFLS load shed represents 1.07% of the Regional UFLS load shed. FRCC determined that VERO's compliance history should not serve as a basis for applying a penalty. No harm is known to have occurred. | To mitigate this noncompliance, VERO: 1) updated relay settings and performed the required testing using the actual ranges for the time delays; and 2) instituted an annual meeting to verify the underfrequency relay settings.
2018-07-31 | Midwest Reliability Organization (MRO) | American Transmission Co. LLC (ATC) | NCR00685 | MRO2017017988 | FAC-008-3 | R6 | On July 17, 2017, ATC, a Coordinated Oversight Program participant, submitted a self-log to MRO stating that, as a Transmission Owner, it was in noncompliance with FAC-008-3 R6. ATC is registered in the ReliabilityFirst (RF) Region under the same name and NCR ID, and both are monitored under the Coordinated Oversight Program. The noncompliance occurred in the MRO and RF Regions. In February 2017, ATC identified an instance where a line section rating was not properly documented in its Facility Ratings database. ATC determined that the error occurred during a time that ATC was implementing an improved Facility Rating process. ATC's project plan for improved Facility Rating verification was developed in April 2012. ATC conducted an extent of conditions on all Facility Ratings that were updated in the database during this implementation process. The extent of conditions identified a total of 24 additional instances of improper documentation (14 additional line sections, 5 bus sections, 2 transformer sections, and three shunt device sections) in addition to the original line section. The cause of the noncompliance was a failure to timely complete the ratings validation process while ATC was implementing an improved Facility Rating process. This resulted in ATC's Facility Rating database not utilizing the updated information that resulted from the new process. While ATC has strong internal controls, the design failed to anticipate this mode of failure. The noncompliance began on November 18, 2013, when the first change in a Facility Rating was not properly updated in the database, and on August 15, 2017 when the Facility Ratings were corrected in its Facility Ratings database. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Per ATC, 21 of the 25 errors led to an overall Facility Ratings increase; four Facilities had a decrease, and those were 138 kV Facilities. Additionally, ATC utilizes a five percent circuit ratings margin when performing planning studies. Per ATC, three of the four Facility Ratings were within the five percent margin. Per ATC, it observed no possible over-loading within the corrected Facility Rating on the line section that had an eight percent decrease after it reviewed all contingencies that produced the highest potential loading. Finally, none of the four Facilities impacted are not associated with any IROLs. No harm is known to have occurred. | To mitigate the noncompliance, ATC: 1) corrected all 25 instances; 2) added additional internal controls to its processes; and 3) developed and implemented a process to further take advantage of its tools to monitor Facility Rating discrepancies using its SELD tools.
2018-07-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Essential Power Newington, LLC | NCR00540 | NPCC2017018176 | VAR-002-4 | R2. | On August 15, 2017, Essential Power Newington, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Operator (GOP), it was in noncompliance with VAR-002-4 [Requirement R2.]. Per Requirement R2, the Entity is required to comply with instructions contained in the ISO-NE's operating procedure for voltage and reactive control (OP-12). OP-12 requires that, within 15 minutes following a voltage excursion (measured at the high side of a generating unit's GSU) outside of a pre-scheduled tolerance band, the GOP shall either act to reestablish voltage within that band or it shall immediately inform its Local Control Center if it is not able to do so. While doing a spot check of its own historical PI data, the Newington Operations Manager determined that the Entity was in noncompliance with the standard/requirement because, during low voltage conditions on February 13, 2016, its on-shift operator failed to perform both aforementioned tasks within the permissible 15 minute timeframe. This noncompliance started on February 13, 2016 at 16:33, when the duration of low voltage conditions exceeded 15 minutes, and ended at 16:56 of the same day, when the Entity restored voltage at the high side of its generating units' GSUs to within the normal operating voltage bandwidth established by procedure OP-12 (354kV - 360kV). The root cause of this instance of non-compliance was two-fold in that the on-shift operator: 1) did not attempt to raise the voltage until 23 minutes past the 15-minute permissible timeframe to restore voltage at the high-side of the interconnection within the normal operating voltage band-with established by the ISO-NE OP-12 procedure; and 2) did not alert the Local Control Center. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity owns three generating units, each of which has a single dedicated Step-Up transformer (GSU) that raises the output voltage from 18kV to 345kV. The plant is interconnected to its host TO's substation through a 1 mile-long 345kV feeder. The three units (two Gas Turbines and one Steam Unit) are operated as one single Combined Cycle (CC) unit with a combined Gross Capacity of 647 MW. The CC unit was operated at capacity factors of 23% (in 2016) and 15% (in 2017). The noncompliance consisted of the Entity's failure to operate its CC unit within the normal operating voltage bandwidth established by procedure OP-12 (354kV - 360kV) for a period of approximately 23 minutes. The lowest operating voltage experienced in that time interval was 352 kV, or 2 kV lower than the minimum pre-scheduled value. The rated capacity of the CC unit is less than 25% of the Entity's Reliability Coordinator's (ISO-NE) required Operating Reserve (approximately 2600 MW). There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. Therefore, if this instance of non-compliance had caused an unacceptable low voltage conditions on the interconnected system, the Entity's Reliability Coordinator would have been able to resolve the issue by providing adequate voltage support. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) corrected the noncompliance by restoring voltage at the high side of its generating units' GSUs to within the normal operating voltage bandwidth established by procedure OP-12 (354kV - 360kV). To prevent a recurrence of similar instances of noncompliance, the Entity: 1) using an existing NERC compliance event calendar, set-up reminders for annual VAR-002 procedure trainings for Operations staff; 2 ) created a Priority 1 alarm on the Distributed Control System (DCS) console when the units' operating voltage is outside the normal bandwidth for a period exceeding 13 minutes, thus prompting operators to take immediate corrective actions; 3) posted the prescribed voltage schedule and tolerance band along with min/max values on the DCS console to remind Operators of voltage operating ranges and corrective actions required; and 4) discussed this operating event and associated self-reported noncompliance with responsible staff as part of a Root Cause Assessment exercise and training tool. NPCC has verified the completion of all mitigation activity.
2018-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Dominion Energy Fairless, LLC (Fairless) | NCR00780 | RFC2018019384 | PRC-024-2 | R1 | On March 1, 2018, Fairless submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. In June 2016, the entity hired a third party engineering firm to identify and review the settings of its generator voltage and frequency protective relaying. On December 21, 2017, while reviewing the results of the study performed by the engineering firm, the entity discovered that six Voltz/Hertz protection relays were not included in the initial study. All six Voltz/Hertz protection relays should have been included in the initial study. The entity performed an investigation to determine why the six Voltz/Hertz protection relays were not included in the initial study and determined that the entity provided both inadequate guidance and an inadequate scope of work to the engineering firm. The entity also discovered that its internal subject matter experts did not evaluate the engineering firm’s study results in a timely manner, which delayed discovery of this noncompliance. This noncompliance involves the management practices of validation, verification, and external interdependencies. The entity did not verify that it provided adequate guidance and a correct scope of work to the engineering firm to perform the study. The entity also did not validate that the study the engineering firm produced included all of the relays that needed to be evaluated. That failure to validate and verify is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R1 and ended on January 29, 2018, when the engineering firm evaluated the six omitted relays and provided a new PRC-024 Compliance Report to Fairless. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone,” a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized here because the entity timely and correctly evaluated the over frequency and under frequency protective relays; the entity only missed the six Voltz/Hertz protection relays. Also, when the engineering firm evaluated the originally missed relay settings, the engineering firm determined that all of the relay settings set points were compliant. Additionally, ReliabilityFirst notes that the entity (which contributes approximately 1240 MWs to the grid and operated at approximately a 72% capacity factor during the noncompliance) identified no system events where any units were prematurely removed from service due to the settings. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed an internal review of program documents, including but not limited to, NERC Compliance Procedures, guidance documents, job aids, and process maps; 2) created and reviewed the scope of work for the third party engineering firm to ensure correct methodology; 3) had the engineering firm evaluate the six omitted relays and provide a new PRC-024 Compliance Report; 4) created an Internal Controls document that identifies roles and responsibilities with regard to PRC-024 program management. This document provides details to ensure the identification, assessment, submittal and documentation of protective relays for compliance with PRC-024; 5) updated program documents to address weaknesses identified during the extent of condition assessment; and 6) provided training to staff regarding the Internal Controls document and lessons learned. ReliabilityFirst has verified the completion of all mitigation activity.
2018-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Dominion Energy Fairless, LLC (Fairless) | NCR00780 | RFC2018019385 | PRC-024-2 | R2 | On March 1, 2018, Fairless submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. In June 2016, the entity hired a third party engineering firm to identify and review the settings of its generator voltage and frequency protective relaying. On December 21, 2017, while reviewing the results of the engineering study performed by the engineering firm, the entity discovered that calculations used to verify the voltage protective relay settings were incorrect and needed to be redone. The entity performed an investigation to determine why the calculations used to verify the voltage protective relay settings were incorrect. The entity determined that it provided both inadequate guidance and an inadequate scope of work to the engineering firm. The entity also discovered that its internal subject matter experts did not evaluate the engineering firm’s study results in a timely manner, which delayed entity personnel in discovering this noncompliance. This noncompliance involves the management practices of validation, verification, and external interdependencies. The entity did not verify that it provided adequate guidance and a correct scope of work to the engineering firm to perform the study. The entity also did not validate that the study the engineering firm produced used correct calculations to verify the voltage protective relay settings. That failure to validate and verify is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R2 and ended on February 21, 2018, when the engineering firm redid the calculations used to verify the voltage protective relay settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone,” a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized here because when the engineering firm performed the study using the correct calculations, the engineering firm determined that all of the relay settings set points were compliant. Additionally, ReliabilityFirst notes that the entity (which contributes approximately 1240 MWs to the grid and operated at approximately a 72% capacity factor during the noncompliance) identified no system events where any units were prematurely removed from service due to the relay settings. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed an internal review of program documents, including but not limited to, NERC Compliance Procedures, guidance documents, job aids, and process maps; 2) created and reviewed the scope of work for the third party engineering firm; 3) had the engineering firm reevaluate the voltage protective relays and produced a new PRC-024 Compliance Report; 4) created an Internal Controls document for use internally that identifies roles and responsibilities with regard to PRC-024 program management. This document provides details to ensure the identification, assessment, submittal and documentation of protective relays for compliance with PRC-024; 5) updated program documents to address weaknesses identified during the extent of condition assessment; and 6) provided training to relevant staff regarding the Internal Controls document and lessons learned. ReliabilityFirst has verified the completion of all mitigation activity.
2018-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Springdale Energy, LLC (Springdale) | NCR11822 | RFC2018019459 | PRC-024-2 | R1 | On March 21, 2018, Springdale submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. On December 13, 2017, LS Power purchased Springdale from FirstEnergy and registered the entity as a new Registered Entity. LS Power did not receive compliance documentation from FirstEnergy until mid-January 2018. Once it received the files, it discovered that FirstEnergy had provided PRC-024-2 R1 documentation for Units 1 and 2, but not documentation for Units 3, 4, and 5. LS Power hired a contractor to provide the analysis for PRC-024-2 and during that analysis, the contractor verified the settings for Unit 1 and 2 were correct and outside of the no trip zone for both frequency and voltage. LS Power had a contractor complete the initial analysis for Units 3, 4, and 5 on February 18, 2018. The entity did not meet the implementation timeline for the Standard and was not 60% compliant with the Standard on its date of registration. The contractor discovered that settings changes are required for frequency settings for Units 3, 4, and 5 at the plant. The entity submitted these changes to FirstEnergy (Transmission Owner) and PJM (Transmission Operator) for review. The entity will implement these new settings changes as part of its mitigation. This noncompliance involves the management practices of validation and verification. LS Power did not validate and verify that FirstEnergy would provide it with all of the documentation necessary to show that the entity was compliant with PRC-024 during the sale. That failure to validate and verify that FirstEnergy would provide LS Power with all of the necessary documentation is a root cause of this noncompliance. This noncompliance started on December 13, 2017, when the entity was required to comply with PRC-024-2 R1 and ended on April 19, 2018, when the entity completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. Entity Units 3, 4, and 5 each had two CTG frequency protective relay settings that were not compliant and the STG5 frequency protective relay settings were also not compliant for Units 3, 4, and 5. The risk is minimized because the entity (which has a total generating capacity of 677 MVA and operated at an approximately 75% capacity factor during the noncompliance) was 40% compliant with PRC-024-2 when LS Power purchased the facility from FirstEnergy, meaning two of the five units were always compliant. Specifically, Units 1 and 2 were compliant and required no changes. Additionally, LS Power exhibited strong detective controls as they discovered the problems with the relay settings for Units 3, 4, and 5 shortly after acquiring Springdale and promptly self-reported them to ReliabilityFirst. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed the analysis for Units 3, 4 and 5; 2) made setting changes for these three units for the frequency settings for the units to be compliant and not trip within the no trip zone; and 3) has submitted the new settings for review to both PJM and FirstEnergy for their review and approval. The entity then received notification from both PJM and FirstEnergy that they are both satisfied with the new settings and the entity then made arrangements to have the settings updated within those affected relays. The entity completed settings changes for all three units before July 1, 2018. The entity now monitors new standard development and works to ensure new standards are implemented before the compliance date. ReliabilityFirst has verified the completion of all mitigation activity.
2018-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Springdale Energy, LLC (Springdale) | NCR11822 | RFC2018019460 | PRC-024-2 | R2 | On March 21, 2018, Springdale submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. On December 13, 2017, LS Power purchased Springdale from FirstEnergy and registered the entity as a new Registered Entity. LS Power did not receive compliance documentation from FirstEnergy until mid-January 2018. Once it received the files, it discovered that FirstEnergy had provided PRC-024-2 R2 documentation for entity Units 1 and 2, but not documentation for Units 3, 4, and 5. The entity hired a contractor to provide the analysis for PRC-024-2 R2 and during that analysis, the contractor verified the settings for Unit 1 and 2 were correct and outside of the no trip zone for both frequency and voltage. The entity did not find any records for Units 3, 4, and 5 in the documentation from FirstEnergy. After this discovery, the entity had a contractor complete the initial analysis for Units 3, 4, and 5 on February 18, 2018. The contractor found that all of the voltage settings for the facility are outside of the no trip zone, so the plant met compliance with R2 once the contractor completed the analysis. The entity submitted this information to FirstEnergy (Transmission Owner) and PJM (Transmission Operator). The entity was out of compliance because the entity did not meet the implementation timeline for the Standard and was not 60% compliant with the Standard on its date of registration as it had not completed the analysis as of its registration date. This noncompliance involves the management practices of validation and verification. LS Power did not validate and verify that FirstEnergy would provide it with all of the documentation necessary to show that the entity was compliant with PRC-024 during the sale. That failure to validate and verify that FirstEnergy had all of the necessary documentation to show compliance is a root cause of this noncompliance. This noncompliance started on December 13, 2017, when the entity was required to comply with PRC-024-2 R2 and ended on February 18, 2018, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because the contractor found that all of the voltage settings for each of the entity’s five units are outside of the no trip zone. The entity (which has a total generating capacity of 677 MVA and operated at an approximately 75% capacity factor during the noncompliance) merely failed to timely conduct the analysis and submit that information to FirstEnergy and PJM. Lastly, LS Power quickly identified, assessed, and corrected this noncompliance at Springdale after acquiring the entity from FirstEnergy, which evidences effective detective and corrective controls. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity completed the analysis/coordination study for Units 3, 4 and 5. Setting changes were not required for compliance with PRC-024-2 R2. The entity now monitors new standard development and works to ensure new standards are implemented before the compliance date. ReliabilityFirst has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | EDP Renewables North America LLC (EDPR) | NCR11662 | TRE2017017737 | PRC-019-2 | R1. | On June 14, 2017, EDP Renewables North America LLC (EDPR) submitted a Self-Report through an existing multi-region registered entity agreement stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1 for its three wind generation Facilities in the Northeast Power Coordinating Council (NPCC) region. Specifically, Flat Rock Windpower, LLC and Marble River, LLC failed to properly coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions before July 1, 2016. Additionally, Jericho Rise Wind Farm, LLC failed to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions before first synching to the grid on December 8, 2016. For Flat Rock Windpower, LLC the noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on June 27, 2017, when the Entity completed the required coordination to ensure its compliance with the standard/requirement. For Marble River, LLC this noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on June 30, 2017, when the Entity completed the required coordination to ensure its compliance with PRC-019. For Jericho Rise Wind Farm, LLC this noncompliance started on December 8, 2016 when its GO registration took effect, and ended on June 28, 2017, when the Entity competed the required coordination to ensure its compliance with the standard/requirement. The root cause of this instance of noncompliance for Flat Rock Windpower, LLC and Marble River, LLC were the Entities’ incomplete review and verification during the voltage regulating control system review period prior to the beginning of the July 1, 2016 phased in implementation of PRC-019-2. The root cause of this instance of noncompliance for Jericho Rise Wind Farm, LLC was the Entity's incomplete review and verification during the relay setting review period prior to December 8, 2016. During the year following the July 1, 2016 enforcement date, a fleet wide review of relay settings was performed in which the Entity discovered the lack of voltage regulating controls coordination and/or documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk electric system (BES). The capacity factor of Flat Rock Windpower L.L.C.’s generation facility for the years 2016 and 2017 was 27% and 28%. The capacity factor of the Marble River LLC’s generation facility for the years 2016 and 2017 was 28% and 29%. The capacity factor of the Jericho Rise Wind Farm LLC’s generation facility in 2017 was 36%. For all three Facilities, the capacity factor is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The RC/BA/TOP (NYISO) are aware of and plan for the characteristics and nuances of wind generation. The rated capability of the Flat Rock Windpower L.L.C.’s Wind Farm generation is 320 MVA, which is less than 16% of the NYISO's required Operating Reserve (approximately 1965 MW). The rated capability of the Marble River, LLC's Wind Farm generation is 215 MVA, which is 11% of the NYISO's required Operating Reserve (approximately 1965 MW). The rated capability of the Jericho Rise Wind Farm LLC’s Wind Farm generation is 80 MVA, which is 4% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if these instances of noncompliance had caused any of the entire generating facilities to individually trip unnecessarily during a system voltage event, the NYISO (the Entity's RC/BA/TOP) would have been able to replace the lost capacity. In addition, during the period in question no significant misoperations occurred at any of EDPR NA's NPCC facilities which jeopardized the reliability of neighboring entities. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, each of the Entities completed the following: 1) corrected the noncompliance by completing the coordination of the required voltage regulating system controls. 2) to prevent a recurrence of similar instances of noncompliance, each of the Entities: (i) has created a review system. For all future setting and coordination reviews, the Director of Control Center and HV Operations will review and approve all summary sheets which document that coordination activity has taken place to meet the attachments of PRC-019-2. This is memorialized in EDPR NA's Regulatory Compliance Procedure RCP-PRC-019-2; and (ii) has also entered 5 year reviews into the SAP maintenance tracking system that will create work orders to verify proper coordination. NPCC has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2017017258 | PRC-024-2 | R1 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Top of the World Wind Energy, LLC (TOW), as a Generator Owner, was in noncompliance with PRC-024-2 R1 in the Western Electricity Coordinating Council (WECC) region. In particular, TOW (NCR11090) failed to set its frequency protective relays to not trip within the “no trip zone” for its wind generation Facility by July 1, 2016. During late 2016, TOW engaged a third-party contractor to review its frequency trip settings at its single wind generation Facility. On February 20, 2017, the contractor determined that TOW’s existing relay trip settings were within the “no trip zone.” Following this discovery, TOW implemented all required setting changes during a planned outage in July 2017. On July 25, 2017, TOW verified that the revised settings were compliant with the Standard, ending the PRC-024-2 R1 issue. The root cause of this noncompliance was a misunderstanding of the required date for TOW to set the frequency trip settings outside the “no trip zone” for its wind generation Facility. In particular, TOW mistakenly believed that because it only owned a single generation Facility, it did not need to ensure its frequency trip settings were outside the “no trip zone” until July 1, 2019, the date entities are required to be 100% compliance with the PRC-024-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and ended on July 25, 2017, when TOW verified its frequency protective relays were set to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, several factors mitigated the risk posed by this issue. First, TOW produced a relatively small amount of power contributing an average of only 69 MW to the grid with a 34% capacity factor during the issue duration. Second, when TOW operated during the period of noncompliance no trips occurred due to the applicable relay trip settings being within the “no trip zone.” Lastly, the issue only impacted TOW’s over frequency protection relay settings and the incorrect settings would have allowed the relays to operate up to 61.50 Hz for 31 seconds before tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered TOW’s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TOW: 1) implemented settings that were compliant with PRC-024-2 R1; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018020004 | PRC-024-2 | R1 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to set the frequency trip settings outside the no trip zone for their single generation Facilities by July 1, 2016. Subsequently, on July 10, 2018, Texas RE determined that all issues described in the original self-report applied to Conetoe II Solar, LLC (Conetoe) as a GO in the SERC Reliability Corporation (SERC) region under NCR11622. Accordingly, Texas RE is processing this PRC-024-2 R1 issue for Conetoe likewise under Notrees Windpower, LP. In September 2016, Conetoe engaged a third-party contractor to review its frequency trip settings at its single solar generation Facility. On September 28, 2016, the contractor determined that Conetoe’s existing relay trip settings were within the “no trip zone.” Conetoe then determined that it failed to set its protective relaying such that the generator frequency protective relaying would not trip the applicable generating unit within the “no trip zone” of PRC-024 Attachment 1 prior to the July 1, 2016 deadline. Following this discovery, Conetoe implemented all required setting changes on November 18, 2016, ending the PRC-024-2 R1 issue. The root cause of this noncompliance was a misunderstanding of the required date for Conetoe to set the frequency trip settings outside the “no trip zone” for its solar generation Facility. In particular, Conetoe mistakenly believed that because it only owned a single generation Facility, it did not need to ensure its frequency trip settings were outside the “no trip zone” until July 1, 2019, the date entities are required to be 100% compliance with the PRC-024-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and ended on November 18, 2016, when Conetoe set its frequency protective relays to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, several factors mitigated the risk posed by this issue. First, Conetoe produced a relatively small amount of power contributing an average of only 19 MW to the grid with a 24% capacity factor during the issue duration. Second, when Conetoe operated during the period of noncompliance, no trips occurred due to the applicable relay trip settings being within the “no trip zone.” Lastly, Conetoe’s under frequency protection relay settings would have allowed the relays to operate up to 59.3 Hz for .08 seconds before tripping within the “no trip zone” and the over frequency protection relay settings would have allowed the relays to operate up to 60.5 Hz for .08 seconds before tripping within the “no trip zone.” No harm is known to have occurred. Texas RE considered Conetoe‘s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Conetoe: 1) implemented settings that were compliant with PRC-024-2 R1; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018020003 | PRC-024-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint failed to set the voltage trip settings outside the no trip zone for their single generation Facilities by July 1, 2016. Subsequently, on July 10, 2018, Texas RE determined that all issues described in the original self-report applied to Conetoe II Solar, LLC (Conetoe) as a GO in the SERC Reliability Corporation (SERC) region under NCR11622. Accordingly, Texas RE is processing this PRC-024-2 R2 issue for Conetoe under Notrees Windpower, LP. In September 2016, Conetoe engaged a third-party contractor to review its voltage trip settings at its single solar generation Facility. On September 28, 2016, the contractor determined that Conetoe’s existing relay trip settings were within the “no trip zone.” Following this discovery, Conetoe implemented all required setting changes on November 18, 2016, ending the PRC-024-2 R2 issue. The root cause of this noncompliance was a misunderstanding of the required date for Conetoe to set its voltage trip settings outside the “no trip zone” for its solar generation Facility. In particular, Conetoe mistakenly believed that because it only owned a single generation Facility, it did not need to ensure its voltage trip settings were outside the “no trip zone” until July 1, 2019, the date entities are required to be 100% compliance with the PRC-024-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on November 18, 2016, when Conetoe set its voltage protective relays to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, several factors mitigated the risk posed by this issue. First, Conetoe produced a relatively small amount of power contributing an average of only 19 MW with a 24% capacity factor during the issue duration. Second, when Conetoe operated during the period of noncompliance no trips occurred due to the applicable relay trip settings being within the “no trip zone.” Lastly, Conetoe’s under voltage protection relay setting settings would have allowed the under voltage relays to operate up to .88 pu for .08 seconds before tripping within the “no trip zone” and the over frequency protection relay settings would have allowed the relays to operate up to 1.1 pu for .08 seconds before tripping within the “no trip zone.” No harm is known to have occurred. Texas RE considered Conetoe‘s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Conetoe: 1) implemented settings that were compliant with PRC-024-2 R2; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018020006 | PRC-024-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint failed to set the voltage trip settings outside the no trip zone for their single generation Facilities by July 1, 2016. Subsequently, on July 10, 2018, Texas RE determined that all issues described in the original self-report applied to Ironwood Windpower, LLC (Ironwood) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11257. Accordingly, Texas RE is processing this PRC-024-2 R2 issue for Ironwood under Notrees Windpower, LP. During late 2016, Ironwood engaged a third-party contractor to review its voltage protective relay trip settings at its single wind generation Facility. On February 6, 2017, the contractor determined that Ironwood’s existing voltage protective relay trip settings were within the “no trip zone.” Following this discovery, Ironwood implemented all required setting changes during a planned outage in September 2017. On September 19, 2017, Ironwood verified that the revised settings were compliant with the Standard, ending the PRC-024-2 R2 issue. The root cause of this noncompliance was a misunderstanding of the required date for Ironwood to set its voltage trip settings outside the “no trip zone” for its wind generation Facility. In particular, Ironwood mistakenly believed that because it only owned a single generation Facility it did not need to ensure its voltage protective relay trip settings were outside the ‘no trip zone” until July 1, 2019, the date entities are required to be 100% in compliance with PRC-024-2 R2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on September 19, 2017, when Ironwood verified its voltage protective relays were set to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, several factors mitigated the risk posed by this issue. First, during the period of noncompliance Ironwood contributed an average of only 7 MW with approximately a 4% capacity factor. Second, when Ironwood operated during the period of noncompliance, no trips occurred due to the applicable relay trip settings being set within the “no trip zone.” Lastly, the issue only impacted Ironwood’s under voltage protection relay settings and the incorrect settings would have allowed the relays to operate up to .75 pu for 1 second before tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered Ironwood‘s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Ironwood: 1) implemented settings that were compliant with PRC-024-2 R2; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018020005 | PRC-024-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint failed to set the voltage trip settings outside the no trip zone for their single generation Facilities by July 1, 2016. Subsequently, on July 10, 2018, Texas RE determined that all issues described in the original self-report applied to Cimarron Wind Power II, LLC (Cimarron) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11240. Accordingly, Texas RE is processing this PRC-024-2 R2 issue for Cimarron under Notrees Windpower, LP. During late 2016, Cimarron engaged a third-party contractor to review its voltage protective relay trip settings at its single wind generation Facility. On January 23, 2017, the contractor determined that Cimarron’s existing voltage protective relay trip settings were within the “no trip zone.” Following this discovery, Cimarron implemented all required setting changes during a planned outage in September 2017. On September 12, 2017, Cimarron verified the revised settings were compliant with the Standard, ending the PRC-024-2 R2 issue. The root cause of this noncompliance was a misunderstanding of the required date for Cimarron to set its voltage trip settings outside the “no trip zone” for its wind generation Facility. In particular, Cimarron mistakenly believed that because it only owned a single generation Facility it did not need to ensure its voltage protective relay trip settings were outside the ‘no trip zone” until July 1, 2019, the date entities are required to be 100% in compliance with the PRC-024-2 R2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on September 12, 2017, when Cimarron verified its voltage protective relays were set to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, several factors mitigated the risk posed by this issue. First, during the period of noncompliance Cimarron contributed an average of only 61 MW with approximately a 46% capacity factor. Second, when Cimarron operated during the period of noncompliance, no trips occurred due to the applicable trip settings being set within the “no trip zone.” Lastly, this issue only impacted Cimarron’s under voltage protection relay settings and the incorrect settings would have allowed the relays to operate up to .75 pu for 1 second before tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered Cimarron‘s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Cimarron: 1) implemented settings that were compliant with PRC-024-2 R2; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018020001 | PRC-024-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint failed to set the voltage trip settings outside the no trip zone for their single generation Facilities by July 1, 2016. Subsequently, on July 10, 2018, Texas RE determined that all issues described in the original self-report applied to Top of the World Wind Energy, LLC (TOW) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR11090. Accordingly, Texas RE is processing this PRC-024-2 R2 issue for TOW under Notrees Windpower, LP. During late 2016, TOW engaged a third-party contractor to review its voltage protective relay trip settings at its single wind generation Facility. On February 20, 2017, the contractor determined that Ironwood’s existing voltage protective relay trip settings were within the “no trip zone.” Following the discovery, TOW implemented all required setting changes during a planned outage in July 2017. On July 25, 2017, Ironwood verified that the revised settings were compliant with the Standard, ending the PRC-024-2 R2 issue. The root cause of this noncompliance was a misunderstanding of the required date for TOW to set its voltage trip settings outside the “no trip zone” for its wind generation Facility. In particular, TOW mistakenly believed that because it only owned a single generation Facility it did not need to ensure its voltage protective relay trip settings were outside the ‘no trip zone” until July 1, 2019, the date entities are required to be 100% in compliance with PRC-024-2 R2. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on July 25, 2017, when TOW verified its voltage protective relays were set to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, several factors mitigated the risk posed by this issue. First, during the period of noncompliance, TOW contributed an average of only 69 MW with approximately a 34% capacity factor. Second, when TOW operated during the period of noncompliance, no trips occurred due to the applicable trip settings being set within the “no trip zone.” Lastly, this issue only impacted TOW’s under voltage protection relay settings and the incorrect settings would have allowed the relays to operate up to .75 pu for 1 second before tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered TOW’s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TOW: 1) implemented settings that were compliant with PRC-024-2 R2; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-07-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018020002 | PRC-024-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint failed to set the voltage trip settings outside the no trip zone for their single generation Facilities by July 1, 2016. Subsequently, on July 10, 2018, Texas RE determined that all issues described in the original self-report applied to Three Buttes Windpower, LLC (Three Buttes) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR10345. Accordingly, Texas RE is processing this PRC-024-2 R2 issue for Three Buttes under Notrees Windpower, LP. During late 2016, Ironwood engaged a third-party contractor to review its voltage protective relay trip settings at its single wind generation Facility. On March 6, 2017, the contractor determined that Three Butte’s existing voltage protective relay trip settings were within the “no trip zone.” Following this discovery, Three Buttes implemented all required setting changes during a planned outage in July 2017. On July 17, 2017, Three Buttes verified that the revised settings were compliant with the Standard, ending the PRC-024-2 R2 issue. The root cause of this noncompliance was a misunderstanding of the required date for Three Buttes to set its voltage trip settings outside the “no trip zone” for its wind generation Facility. In particular, Three Buttes mistakenly believed that because it only owned a single generation Facility it did not need to ensure its voltage protective relay trip settings were outside the ‘no trip zone” until July 1, 2019, the date entities are required to be 100% in compliance with PRC-024-2 R2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on July 17, 2017, when Three Buttes verified its voltage protective relays were set to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, several factors mitigated the risk posed by this issue. First, during the period of noncompliance, Three Buttes contributed an average of only 36 MW with approximately a 37% capacity factor. Second, when Three Buttes operated during the period of noncompliance no trips occurred due to the applicable trip settings being set within the “no trip zone.” Lastly, the issue only impacted Three Buttes’ under voltage protection relay settings and the incorrect settings would have allowed the relays to operate up to .8 pu for 1 second before tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered Three Buttes‘ and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Three Buttes: 1) implemented settings that were compliant with PRC-024-2 R2; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-07-31 | Western Electricity Coordinating Council | AES Alamitos, LLC (ALGS) | NCR05002 | WECC2018019059 | MOD-025-2 | R1 | On January 26, 2018, ALGS submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-2 Requirement 1.2. Specifically, ALGS reported and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. The root cause of these issues of noncompliance was ALGS’s failure to monitor the communication with the TP to ensure that the Attachment 2 was provided in accordance with the Standard. WECC determined that these issues began on May 12, 2017, the 91st day after Real Power Capabilities were verified for at least 40% of ALGS’s applicable Facilities. WECC determined that the end date of these issues is January 5, 2018, when ALGS provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 238 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In these instances, ALGS failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. Such failure could result in the Transmission Planner having inaccurate information regarding the applicable Facilities’ Real Power and Reactive Power capabilities for use in its planning models for assessing BPS reliability. However, the 370 MVA Facility in scope has had a Net Capacity Factor of five percent for at least the last six years. Additionally, these issues were identified during a mock audit and immediately remediated. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, ALGS provided the Attachment 2 form to its TP. The applicable Facility will be decommissioned in 2019 so no further activities will be required to ensure future compliance with this Standard.
2018-07-31 | Western Electricity Coordinating Council | AES Alamitos, LLC (ALGS) | NCR05002 | WECC2018019060 | MOD-025-2 | R2 | On January 26, 2018, ALGS submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-2 Requirement 2.2. Specifically, ALGS reported and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. The root cause of these issues of noncompliance was ALGS’s failure to monitor the communication with the TP to ensure that the Attachment 2 was provided in accordance with the Standard. WECC determined that these issues began on May 12, 2017, the 91st day after Reactive Power Capabilities were verified for at least 40% of ALGS’s applicable Facilities. WECC determined that the end date of these issues is January 5, 2018, when ALGS provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 238 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In these instances, ALGS failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. Such failure could result in the Transmission Planner having inaccurate information regarding the applicable Facilities’ Real Power and Reactive Power capabilities for use in its planning models for assessing BPS reliability. However, the 370 MVA Facility in scope has had a Net Capacity Factor of five percent for at least the last six years. Additionally, these issues were identified during a mock audit and immediately remediated. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, ALGS provided the Attachment 2 form to its TP. The applicable Facility will be decommissioned in 2019 so no further activities will be required to ensure future compliance with this Standard.
2018-07-31 | Western Electricity Coordinating Council | AES Huntington Beach, LLC (AESH) | NCR05004 | WECC2018019062 | MOD-025-2 | R1 | On January 26, 2018, AESH submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-2 Requirements 1.2. Specifically, AESH reported and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. The root cause of these issues of noncompliance was AESH’s failure to monitor the communication with the TP to ensure that the Attachment 2 was provided in accordance with the Standard. WECC determined that this issue began on July 25, 2017, the 91st day after Real Power Capabilities were verified for at least 40% of AESH’s applicable Facilities WECC determined that the end date of this issue is December 22, 2017, when AESH provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 150 days of noncompliance. | WECC determined that this issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AESH failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. Such failure could result in the Transmission Planner not having the most accurate and up to date models used to assess BPS Reliability. However, the Real Power capabilities has remained relatively static since AESH purchased the Facility from its TP in 1998. The applicable Facility in scope is a 250 MW gas fired steam turbine that is primarily used during the summer peak season. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, AESH provided the Attachment 2 form to its TP. The applicable Facility will be decommissioned in 2019 so no further activities will be required to ensure future compliance with this Standard.
2018-07-31 | Western Electricity Coordinating Council | AES Huntington Beach, LLC (AESH) | NCR05004 | WECC2018019063 | MOD-025-2 | R2 | On January 26, 2018, AESH submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-2 Requirements 2.2. Specifically, AESH reported and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. The root cause of these issues of noncompliance was AESH’s failure to monitor the communication with the TP to ensure that the Attachment 2 was provided in accordance with the Standard. WECC determined that this issue began on July 25, 2017, the 91st day after Reactive Power Capabilities were verified for at least 40% of AESH’s applicable Facilities WECC determined that the end date of this issue is December 22, 2017, when AESH provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 150 days of noncompliance. | WECC determined that this issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AESH failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. Such failure could result in the Transmission Planner not having the most accurate and up to date models used to assess BPS Reliability. However, the Reactive Power capabilities have remained relatively static since AESH purchased the Facility from its TP in 1998. The applicable Facility in scope is a 250 MW gas fired steam turbine that is primarily used during the summer peak season. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, AESH provided the Attachment 2 form to its TP. The applicable Facility will be decommissioned in 2019 so no further activities will be required to ensure future compliance with this Standard.
2018-07-31 | Western Electricity Coordinating Council | AES Redondo Beach LLC (AESR) | NCR05007 | WECC2018019057 | MOD-025-2 | R1 | On January 26, 2018, AESR submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-2 Requirements 1.2. Specifically, AESR reported and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. The root cause of these issues of noncompliance was AESR’s failure to monitor the communication with the TP to ensure that the Attachment 2 was provided in accordance with the Standard. WECC determined that this issue began on November 15, 2017, the 91st day after Real Power capabilities were verified for at least 40% or AESR’s applicable Facilities. WECC determined that the end date of this issue is December 20, 2017, when AESH provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 35 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In these instances, AESR failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. Such failure could result in the Transmission Planner not having the most accurate and up to date models used to assess BPS Reliability. However, AESR’s has a single applicable Facility rated at 475 MW that is rarely utilized, which has operated at a Net Capacity Factor of less than five percent for at least the last three years. Additionally, these issues were identified during a mock audit and immediately remediated. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, AESR provided the Attachment 2 form to its TP. The applicable Facility will be decommissioned in 2020 so no further activities will be required to ensure future compliance with this Standard.
2018-07-31 | Western Electricity Coordinating Council | AES Redondo Beach LLC (AESR) | NCR05007 | WECC2018019058 | MOD-025-2 | R2 | On January 26, 2018, AESR submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-2 Requirements 2.2. Specifically, AESR reported and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. The root cause of these issues of noncompliance was AESR’s failure to monitor the communication with the TP to ensure that the Attachment 2 was provided in accordance with the Standard. WECC determined that these issues began on November 15, 2017, the 91st day after Reactive Power capabilities were verified for at least 40% or AESR’s applicable Facilities. WECC determined that the end date of these issues is December 20, 2017, when AESH provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 35 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In these instances, AESR failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. Such failure could result in the Transmission Planner not having the most accurate and up to date models used to assess BPS Reliability. However, AESR’s has a single applicable Facility rated at 475 MW that is rarely utilized, which has operated at a Net Capacity Factor of less than five percent for at least the last three years. Additionally, these issues were identified during a mock audit and immediately remediated. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate this issue, AESR provided the Attachment 2 form to its TP. The applicable Facility will be decommissioned in 2020 so no further activities will be required to ensure future compliance with this Standard.
2018-07-31 | Western Electricity Coordinating Council | California Department of Water Resources (CDWR) | NCR05047 | WECC2017017193 | MOD-025-2 | R1 | On March 1, 2017, CDWR submitted a Self-Certification stating that, as Generator Owner, it was in noncompliance with MOD-025-2 Requirement 1. Specifically, CDWR reported that it failed to verify the Real Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard, by the effective date of the Standard. CDWR also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner by the effective date of the Standard. Specifically, CDWR believed that the requirements of the "WECC Generating Unit Model Validation Policy" and "WECC Guideline: Generating Facility Data, Testing and Model Validation Requirements" (WECC Generator Testing Program) satisfied all the requirements for MOD-025-2 Requirement 1.1. Regarding Requirement 1.2 of the Standard, CDWR reported that an independent consultant informed CDWR that verification studies it had previously submitted to its Transmission Planners (TPs) did not include all the required data identified in MOD-025-2 Attachment 2. WECC determined that CDWR failed to verify Real Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard. Any prior testing or validation performed did not fully comply with the Standard. CDWR also failed to submit to its TPs a completed Attachment 2 (or form containing the same information identified in Attachment 2) by the effective date of the Standard. Because all identified information of Requirement 1.1 was not confirmed, it was not available to provide to the TPs in accordance with Requirement 1.2 and Attachment 2. The root cause of this noncompliance was CDWR’s failure to accurately identify the verification and reporting tasks required in MOD-025-2. This occurred because the entity failed to verify that the generating unit studies performed and subsequently reported to the TPs complied with MOD-025-2. Additionally, extreme drought conditions in California prevented CDWR from performing the verifications at its applicable hydro Facilities prior to the effective date of the Standard. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for CDWR’s applicable Facilities. WECC determined that the end date of this issue was June 23, 2017, when the Attachment 2 form for Real Power capabilities was sent to CDWR’s TPs for at least 40% of its applicable Facilities, for a total of 358 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, CDWR failed to verify the Real Power capabilities of at least 40% of its applicable Facilities, in accordance with Attachment 1 of the Standard. CDWR also failed to submit a completed Attachment 2 form, (or form containing the same information identified in Attachment 2), to its Transmission Planners by the effective date of the Standard. Such failure could result in inaccurate information used in planning models. Therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a system contingency, but it may not be capable of completely mitigating the contingency. However, all CDWR’s BPS Facilities had previously been tested per the requirements of the WECC Generator Testing Program, which included verifying Real Power capabilities, since WECC implemented its program in 2003. As soon as CDWR became aware that verification was needed, it made the necessary arrangements to conduct Real Power capability verifications. Scheduling of the additional testing was complicated by environmental factors, but verification was completed for 56% of CDWR’s applicable Facilities approximately one month after the effective date of the Standard. There are 32 applicable Facilities in the scope of these issues that have a combined capacity of 1198 MVA. Furthermore, none of the Facilities tested have been found to have any diminished capacity and no harm is known to have occurred. | To mitigate these issues, CDWR: 1)conducted Real Power capability verifications to meet the phase 1 requirement (>40% of applicable Facilities) for the MOD-025-2 implementation plan; 2)provided updated MOD-025-2 phase 1 generator verification reports containing all required information of Attachment 2 to the TPs; 3)developed a tracking spreadsheet with a schedule to ensure that all remaining Facilities were verified by the required dates in the MOD-025-2 implementation plan; 4)conducted generator capability verifications to meet the phase 2 requirement (>60% of applicable Facilities) for the MOD-025-2 implementation plan. 5)provided phase 2 generator verification reports containing all required information of Attachment 2 to the TPs; and 6)developed a written generator verification technical guide outlining the requirements of MOD-025-2.
2018-07-31 | Western Electricity Coordinating Council | California Department of Water Resources (CDWR) | NCR05047 | WECC2017017194 | MOD-025-2 | R2 | On March 1, 2017, CDWR submitted a Self-Certification stating that, as Generator Owner, it was in noncompliance with MOD-025-2 Requirement 2. Specifically, CDWR reported that it failed to verify the Reactive Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard, by the effective date of the Standard. CDWR also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner by the effective date of the Standard. Specifically, CDWR believed that the requirements of the "WECC Generating Unit Model Validation Policy" and "WECC Guideline: Generating Facility Data, Testing and Model Validation Requirements" (WECC Generator Testing Program) satisfied all the requirements for MOD-025-2 Requirement 2.1. Regarding Requirement 2.2 of the Standard, CDWR reported that an independent consultant informed CDWR that verification studies it had previously submitted to its Transmission Planners (TPs) did not include all the required data identified in MOD-025-2 Attachment 2. WECC determined that CDWR failed to verify Reactive Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard. Any prior testing or validation performed did not fully comply with the Standard. CDWR also failed to submit to its TPs a completed Attachment 2 (or form containing the same information identified in Attachment 2) by the effective date of the Standard. Because all identified information of Requirement 2.1 was not confirmed, it was not available to provide to the TPs in accordance with Requirements 2.2 and Attachment 2. The root cause of this noncompliance was CDWR’s failure to accurately identify the verification and reporting tasks required in MOD-025-2. This occurred because the entity failed to verify that the generating unit studies performed and subsequently reported to the TPs complied with MOD-025-2. Additionally, extreme drought conditions in California prevented CDWR from performing the verifications at its applicable hydro Facilities prior to the effective date of the Standard. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for CDWR’s applicable Facilities. WECC determined that the end date of this issue was June 23, 2017, when the Attachment 2 form for Reactive Power capabilities was sent to CDWR’s TPs for at least 40% of its applicable Facilities, for a total of 358 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, CDWR failed to verify the Reactive Power capabilities of at least 40% of its applicable Facilities, in accordance with Attachment 1 of the Standard. CDWR also failed to submit a completed Attachment 2 form, (or form containing the same information identified in Attachment 2), to its Transmission Planners by the effective date of the Standard. Such failure could result in inaccurate information used in planning models. Therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a system contingency, but it may not be capable of completely mitigating the contingency. However, all CDWR’s BPS Facilities had previously been tested per the requirements of the WECC Generator Testing Program, which included verifying Reactive Power capabilities, since WECC implemented its program in 2003. As soon as CDWR became aware that verification was needed, it made the necessary arrangements to conduct Reactive Power capability verifications. Scheduling of the additional testing was complicated by environmental factors, but verification was completed for 56% of CDWR’s applicable Facilities approximately one month after the effective date of the Standard. There are 32 applicable Facilities in the scope of these issues that have a combined capacity of 1198 MVA. Furthermore, none of the Facilities tested have been found to have any diminished capacity and no harm is known to have occurred. | To mitigate these issues, CDWR: 1)conducted Reactive Power capability verifications to meet the phase 1 requirement (>40% of applicable Facilities) for the MOD-025-2 implementation plan; 2)provided updated MOD-025-2 phase 1 generator verification reports containing all required information of Attachment 2 to the TPs; 3)developed a tracking spreadsheet with a schedule to ensure that all remaining Facilities were verified by the required dates in the MOD-025-2 implementation plan; 4)conducted generator capability verifications to meet the phase 2 requirement (>60% of applicable Facilities) for the MOD-025-2 implementation plan. 5)provided phase 2 generator verification reports containing all required information of Attachment 2 to the TPs; and 6)developed a written generator verification technical guide outlining the requirements of MOD-025-2.
2018-07-31 | Western Electricity Coordinating Council | Copper Mountain Solar 3, LLC (CMSOL) | NCR11476 | WECC2017018730 | MOD-025-2 | R1 | On November 28, 2017, CMSOL submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 Requirement 1.2. Specifically, CMSOL reported that and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. The root cause of these issues of noncompliance was CMSOL management’s failure to oversee and ensure that the staff member responsible for providing the Attachment 2 to the TP completed the task within 90 days. WECC determined that these issues began on January 4, 2017, the 91st day after Real Power and Reactive Power Capabilities were verified for at least 40% of CMSOL’s applicable Facilities. WECC determined that the end date of these issues is November 28, 2017, when CMSOL provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 328 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, CMSOL failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Real Power Capabilities. Such failure could potentially result in inaccurate information of generator gross and net Real Power capability used in planning models which are used to assess BES Reliability therefore, the BES could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, CMSOL’s single applicable Facility is a 255 MW solar installation that is not typically utilized as a firm resource, therefore, CPWL’s Balancing Authority, Transmission Planner, and Transmission Operator plan and operate the grid with the expectation that solar generation may be unavailable at any given time. Additional, this issue were discovered during an internal NERC compliance self-assessment. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, CMSOL: a. submitted the Attachment 2 to its Transmission Planner; and b. implemented a compliance notification tickler system to notify management and staff of various compliance obligations prior to their due dates.
2018-07-31 | Western Electricity Coordinating Council | Copper Mountain Solar 3, LLC (CMSOL) | NCR11476 | WECC2017018731 | MOD-025-2 | R2 | On November 28, 2017, CMSOL submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 Requirement 2.2. Specifically, CMSOL reported that and WECC verified that it failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. The root cause of these issues of noncompliance was CMSOL management’s failure to oversee and ensure that the staff member responsible for providing the Attachment 2 to the TP completed the task within 90 days. WECC determined that these issues began on January 4, 2017, the 91st day after Real Power and Reactive Power Capabilities were verified for at least 40% of CMSOL’s applicable Facilities. WECC determined that the end date of these issues is November 28, 2017, when CMSOL provided its Attachment 2 form to its TP for at least 40% of its applicable Facilities, for a total of 328 days of noncompliance. | WECC determined that these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, CMSOL failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for the staged test of its Reactive Power Capabilities. Such failure could potentially result in inaccurate information of generator gross and net Reactive Power capability used in planning models which are used to assess BES Reliability therefore, the BES could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, CMSOL’s single applicable Facility is a 255 MW solar installation that is not typically utilized as a firm resource, therefore, CPWL’s Balancing Authority, Transmission Planner, and Transmission Operator plan and operate the grid with the expectation that solar generation may be unavailable at any given time. Additional, this issue were discovered during an internal NERC compliance self-assessment. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this issue, CMSOL: a. submitted the Attachment 2 to its Transmission Planner; and b. implemented a compliance notification tickler system to notify management and staff of various compliance obligations prior to their due dates.
2018-07-31 | Western Electricity Coordinating Council | Equilon Enterprises, LLC (MPCC) | NCR05232 | WECC2017017174 | MOD-025-2 | R1 | On March 1, 2017, MPCC submitted a Self-Certification stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 Requirement 1. Specifically, MPCC reported that it failed to verify Real Power capabilities of at least 40% of its applicable Facilities, in accordance with Attachment 1 of the Standard by the effective date of the Standard. Additionally, MPCC also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) by the effective date of the Standard. WECC reviewed the Self-Certification and all applicable data and determined that MPCC failed to verify Real Power capabilities of at least 40% its applicable Facilities, in accordance with Attachment 1; and further failed to submit verification results to its TP (or a form containing the same information as identified in Attachment 2) by the effective date of the Standard. The root cause of the noncompliance was that personnel responsibilities were not well-defined. Specifically, MPCC changed the compliance personnel responsibilities prior to the effective date of the Standard, and MOD-025-2 compliance was overlooked in the transition. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for MPCC’s applicable Facilities. WECC determined that this issue ended on August 22, 2017, when MPCC provided verification of Real Power capabilities of its applicable Facilities to its TP in accordance with the required information identified in Attachment 2, for a total of 418 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). MPCC failed to verify the Real Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard, which could potentially result in inaccurate information of generator gross and net Real Power capabilities used in planning models which are used to assess BPS reliability. Inaccurate planning models could allow the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, but these issues may prevent it from completely mitigating the contingency. However, these issues would not likely have significantly affected current planning models as MPCC tested its Facilities in accordance with the WECC Model Validation Policy prior to the effective date of the standard. Therefore, if a real-time contingency occurred requiring the generating unit to respond, the current data would be satisfactory for mitigating that contingency. Additionally, the combined capacity for all three facilities in scope of these issues is 120 MW. No Harm is known to have occurred. | 1. To remediate and mitigate this issue, MPCC: a. completed the required verification testing for MOD-025-2 R1; b. submitted the completed testing results to its TP in accordance with the Standard and Requirements; and c. contracted with a third-party provider to implement a NERC compliance oversight program to schedule and complete verification testing.
2018-07-31 | Western Electricity Coordinating Council | Equilon Enterprises, LLC (MPCC) | NCR05232 | WECC2017017175 | MOD-025-2 | R2 | On March 1, 2017, MPCC submitted a Self-Certification stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 Requirement 2. Specifically, MPCC reported that it failed to verify Reactive Power capabilities of at least 40% of its applicable Facilities, in accordance with Attachment 1 of the Standard by the effective date of the Standard. Additionally, MPCC also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) by the effective date of the Standard. WECC reviewed the Self-Certification and all applicable data and determined that MPCC failed to verify Reactive Power capabilities of at least 40% its applicable Facilities, in accordance with Attachment 1; and further failed to submit verification results to its TP (or a form containing the same information as identified in Attachment 2) by the effective date of the Standard. The root cause of the noncompliance was that personnel responsibilities were not well-defined. Specifically, MPCC changed the compliance personnel responsibilities prior to the effective date of the Standard, and MOD-025-2 compliance was overlooked in the transition. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for MPCC’s applicable Facilities. WECC determined that this issue ended on August 22, 2017, when MPCC provided verification of Reactive Power capabilities of its applicable Facilities to its TP in accordance with the required information identified in Attachment 2, for a total of 418 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). MPCC failed to verify the Reactive Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard, which could potentially result in inaccurate information of generator gross and net Reactive Power capabilities used in planning models which are used to assess BPS reliability. Inaccurate planning models could allow the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, but these issues may prevent it from completely mitigating the contingency. However, these issues would not likely have significantly affected current planning models as MPCC tested its Facilities in accordance with the WECC Model Validation Policy prior to the effective date of the standard. Therefore, if a real-time contingency occurred requiring the generating unit to respond, the current data would be satisfactory for mitigating that contingency. Additionally, the combined capacity for all three facilities in scope of these issues is 120 MW. No Harm is known to have occurred. | 1. To remediate and mitigate this issue, MPCC: a. completed the required verification testing for MOD-025-2 R2; b. submitted the completed testing results to its TP in accordance with the Standard and Requirements; and c. contracted with a third-party provider to implement a NERC compliance oversight program to schedule and complete verification testing.
2018-07-31 | Western Electricity Coordinating Council | Imperial Valley Solar 1, LLC (IVSO) | NCR11427 | WECC2017017162 | MOD-025-2 | R1 | On March 1, 2017, IVSO submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, IVSO reported that it failed to verify Real Power capabilities of its single applicable Facility, in accordance with Attachment 1 of the Standard, by the effective date of the Standard. Additionally, IVSO failed to Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) by the effective date of the Standard. WECC determined that IVSO failed to verify Real Power capabilities of its applicable Facility in accordance with Attachment 1, and failed to submit verification results to its TP in accordance with Attachment 2, by the effective date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for MOD-025-2. Specifically, IVSO believed that because it had only one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for IVSO’s applicable Facility. WECC determined that the end date of this issue was July 5, 2017, when IVSO provided verification of its Real Power capabilities to its Transmission Planner; for a total of 370 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, IVSO failed to verify the Real Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard. IVSO also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its TP within 90 calendar days of completing the verification. This failure could potentially result in inaccurate information of generator gross and net Real Power capabilities used in planning models which are used to assess BPS Reliability. Therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 207 MW solar installation. Therefore, system reliability would not be compromised as solar generation is not typically utilized as a firm resource. System Operators plan and operate the grid with the expectation that the generation may be unavailable at any given time. Additionally, the Facility is not operated at or near its Real Power capabilities. No harm is known to have occurred. | To remediate and mitigate this issue, IVSO: a. completed verification of the Real Power capabilities of its applicable Facility in accordance to the Standard and Requirements; b. submitted testing results to its TP within 90 days of testing completion, in accordance with the Standard and Requirements; c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming NERC Standards, obligations, and events with the intent to prevent incorrect interpretations of implementation plans going forward; and d. created a compliance calendar to track upcoming and ongoing compliance obligations, including NERC regulatory compliance.
2018-07-31 | Western Electricity Coordinating Council | Imperial Valley Solar 1, LLC (IVSO) | NCR11427 | WECC2017017163 | MOD-025-2 | R2 | On March 1, 2017, IVSO submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Specifically, IVSO reported that it failed to verify Reactive Power capabilities of its single applicable Facility, in accordance with Attachment 1 of the Standard, by the effective date of the Standard. Additionally, IVSO failed to Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) by the effective date of the Standard. WECC determined that IVSO failed to verify Reactive Power capabilities of its applicable Facility in accordance with Attachment 1, and failed to submit verification results to its TP in accordance with Attachment 2, by the effective date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for MOD-025-2. Specifically, IVSO believed that because it had only one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for IVSO’s applicable Facility. WECC determined that the end date of this issue was July 5, 2017, when IVSO provided verification of its Reactive Power capabilities to its Transmission Planner; for a total of 370 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, IVSO failed to verify the Reactive Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard. IVSO also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its TP within 90 calendar days of completing the verification. This failure could potentially result in inaccurate information of generator gross and net Real Power capabilities used in planning models which are used to assess BPS Reliability. Therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 207 MW solar installation. Therefore, system reliability would not be compromised as solar generation is not typically utilized as a firm resource. System Operators plan and operate the grid with the expectation that the generation may be unavailable at any given time. Additionally, the Facility is not operated at or near its Reactive Power capabilities. No harm is known to have occurred. | To remediate and mitigate this issue, IVSO: a. completed verification of the Reactive Power capabilities of its applicable Facility in accordance to the Standard and Requirements; b. submitted testing results to its TP within 90 days of testing completion, in accordance with the Standard and Requirements; c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming NERC Standards, obligations, and events with the intent to prevent incorrect interpretations of implementation plans going forward; and d. created a compliance calendar to track upcoming and ongoing compliance obligations, including NERC regulatory compliance.
2018-07-31 | Western Electricity Coordinating Council | Imperial Valley Solar 1, LLC (IVSO) | NCR11427 | WECC2017017164 | PRC-019-2 | R1 | On March 1, 2017, IVSO submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, a third-party review of the self-certification identified that IVSO failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices by the enforcement date of the Standard. WECC determined that IVSO failed to verify and coordinate its voltage regulating system with its generator capabilities and Protection System devices in at least 40% of its applicable Facilities. Additionally, IVSO failed to verify the in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. IVSO also failed to verify the applicable in-service Protection System devices were set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. The root cause of this issue was a misunderstanding of the phased-in implementation plan for PRC-019-2. Specifically, IVSO believed that because it only had one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for IVSO’s applicable Facility. WECC determined that the end date of this issue is January 25, 2018, when IVSO completed verifying coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices, for a total of 573 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, IVSO failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices of its applicable Facility by the enforcement date of the Standard. Additionally, IVSO failed to verify the in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. IVSO also failed to verify the applicable in-service Protection System devices were set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. Because verification had not been completed, IVSO was unaware of the coordination of its voltage regulating system controls. Such failures could potentially result in the loss of the generator field, instability, and/or damage to the turbines. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 207 MW solar installation. Therefore, system reliability would not be compromised as solar generation is not typically utilized as a firm resource. System Operators plan and operate the grid with the expectation that the generation may be unavailable at any given time. Further, this Facility does not operate in a manner that would approach the voltage or equipment limitations of the Facility. IVSO has not experienced a Protection System trip or equipment failure due to miscoordination. The Relay Coordination Study performed January 25, 2018 indicated no settings changes were required for IVSO’s single applicable facility. No harm is known to have occurred. | To remediate and mitigate this issue, IVSO: a. engaged a third-party engineering contractor to complete the required coordination of the voltage regulating system controls with the applicable equipment capabilities and Protection System settings; b. implemented a regulatory compliance calendar with at least monthly review of upcoming obligations to prevent similar violations; and c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming NERC Standards, obligations, and events with the intent to prevent incorrect interpretations of implementation plans going forward.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Aragonne Wind LLC (AGW) | NCR05014 | WECC2017018316 | PRC-005-2(i) | R3 | On September 7, 2017, AGW submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-005-2(i) R3. Specifically, AGW reported that during a comprehensive review of its PRC-005 program, it discovered it failed to perform minimal maintenance activities within the maximum maintenance intervals for two Vented Lead-Acid (VLA) battery banks and two communication channels, as prescribed in Table 1-4(a) and Table 1-2, respectively. The Director of Regulatory Compliance and other plant personnel, at the time of this noncompliance, believed the intent of PRC-005-2(i) R3 was partially satisfied during AGW’s monthly substation inspections; however, it did not document the performance of those inspections for evidence of compliance. After reviewing all the relevant information, WECC determined that AGW failed to perform the minimal maintenance activities within the maximum maintenance intervals for two VLA battery banks and two communication channels as prescribed in Table 1-4(a) and Table 1-2, respectively. The root cause of the noncompliance was due to an oversight by AGW’s previous NERC Compliance team. Specifically, the previous AGW NERC Compliance team did not document performance of inspections for evidence of compliance. For the VLA battery banks, WECC determined that the issue began on October 1, 2015 and April 1, 2017, when completion of the maintenance activities was due, and ended on September 25, 2017, when AGW completed the testing requirements prescribed in Table 1-4(a), for a total of 752, and 177 days of noncompliance, respectively. For the communication channels, WECC determined that the issue began on October 1, 2015, when completion of the maintenance activities was due, and ended on September 25, 2017, when AGW completed the testing requirements prescribed in Table 1-2, for a total of 177 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, AGW failed to perform minimal maintenance activities within the maximum maintenance intervals for two VLA battery banks and two communication channels as prescribed in Table 1-4(a) and Table 1-2. Such failure could result in the potential degradation or premature failure of the Protection System devices. However, AGW implemented good preventive controls. Specifically, all applicable personnel received initial roles and responsibility training at least once every two years. Additionally, the Facility in scope was a 90 MW intermittent wind generating facility, which reduced its risk to the reliability of the BES. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this noncompliance, AGW: 1) completed maintenance tasks for the batteries and communication channels; 2) hired a third-party consultant to support its NERC Compliance program. 3) conducted training for applicable personnel on its Internal Compliance Program and procedures applicable to them; and 4) added PRC-005 testing and maintenance tasks to an automated work scheduling database to ensure activities are issued to the Plant Managers for completion.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Arizona Electric Power Cooperative, Inc. (AEPC) | NCR05015 | WECC2018019134 | COM-002-4 | R1; R1.5; R1.6 | During a Compliance Audit conducted from January 22, 2018 through February 2, 2018, WECC determined that AEPC, as a Transmission Operator (TOP), was in noncompliance with COM-000-2-4 R1, sub requirements 1.5. and 1.6. After reviewing all the relevant information, WECC determined that AEPC failed to have documented communications protocols for its operating personnel when issuing oral or written Operating Instructions. AEPC purchased assets outside of its TOP footprint and expanded its footprint on October 1, 2017. It was discovered that AEPC did not have appropriate documentation for its Communications Protocol for the new assets. For R1.5., AEPC did not specify the “format for . . . time identification” in the Communications Protocol. For R1.6., AEPC’s nomenclature was inconsistent for Transmission Interface Elements and Transmission Interface Facilities when issuing an oral or written Operating Instruction. AEPC's breaker labeling was not consistent with its one-line diagrams. During the transfer of ownership, AEPC identified that it used a different nomenclature and format for time identification than the previous owner, it determined that this practice should continue. AEPC created a document for System Operators to reference when issuing or receiving written or oral communications with the personnel at the newly acquired assets. AEPC also specified which instances required time identification and nomenclature when issuing an oral or written Operating Instruction in its communications protocols; as this is how it erroneously interrupted the Standard. The root cause of the noncompliance was due to a misinterpretation of what was required by the Standard. WECC determined that this issue began on October 1, 2017 when AEPC registered as TOP for the geographic footprint within the scope of this noncompliance. WECC determined that the end date of this issue is February 15, 2018, when AEPC updated its Communications Protocol document to include the “format for . . . time identification” and cross-referenced its Transmission System Number Scheme and Transmission System One-Line Diagram, for a total of 138 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, AEPC failed to have documented communications protocols that included sub-requirements 1.5 - 1.6 for its operating personnel when issuing oral or written Operating Instructions. Such failure may result in a misunderstanding of the time between entities operating in different time zones or misunderstanding due to inconsistent nomenclature between Facilities. AEPC assumed TOP responsibilities which resulted in an inconsistent labeling scheme. This could lead to BPS elements being removed or restored behind schedule or prematurely which could result in unexpected outages, delay in system restoration, or damage to equipment. However, AEPC has implemented good compensating controls. Specifically, AEPC Power System Controllers (PSCs) specified time identification and nomenclature for Transmission interface Elements and Transmission interface Facilities, as necessary. AEPC uses the nomenclature as the former TOP and it was determined that the Facilities’ number scheme should remain unchanged as they are intertwined with the former TOP’s Facilities. For personnel safety, it was concluded that device labeling should remain consistent with current practices because of the need for inter-company switching efforts and switching program coordination. AEPC uses different nomenclature as the former TOP and retraining the System Operators could result in errors. Moreover, AEPC owns and operates 526 miles of BPS transmission lines (including 500 kV and 345 kV lines) and has 640 MW of generation capacity that were subject to the scope of noncompliance. For these reasons, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, AEPC: a. cross-referenced its Transmission System Number Scheme and Transmission System One-Line Diagrams for consistency; b. completed the internal review and revisions to the Communications Protocol to clarify time identification and nomenclature; c. incorporated revisions and updates to the Communications Protocol V12 including specifying a 24-hour time format and clear nomenclature references for Facilities; and d. developed and implemented training to address the changes made to the Communications Protocol for System Operators to better understand the requirements of the Standard.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Avangrid Renewables (PPME) | NCR10259 | WECC2017016845 | MOD-025-2 | R1 | On January 23, 2017, PPME submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1 . Specifically, PPME reported that it failed to verify Real Power capabilities of at least 40 percent of its Facilities, in accordance with Attachment 1 of the Standard, by the effective date of the Standard. Additionally, PPME failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner by the effective date of the Standard. Specifically, PPME started the verification process for its 18 Facilities prior to the deadline but was unsuccessful in completing verification for at least eight of the facilities prior to the July 1, 2016, the effective date of the Standard. WECC determined that although PPME was in the process of performing the Real Power capability verification studies, it was unable to complete verification of Real Power capabilities for at least 40 percent of its Facilities by the Standard’s effective date. Furthermore, PPME was unable to provide its TPs with an Attachment 2 form for each of its Facilities as required by Requirements 1.2 , by the effective date of the Standard. The root cause of this issues of noncompliance was PPME’s underestimation of the time and resources required to be compliant with the Standard by the July 1, 2016 enforcement date. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for 40 percent of PPME’s Facilities. WECC determined that the end date of this issue is June 27, 2017, when PPME provided the Attachment 2 form to its TPs for more than 40% of its Facilities, for a total of 362 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, PPME failed to verify is Real Power capabilities by the Standard’s enforcement date. Additionally, PPME failed to provide the Attachment 2 form for each applicable Facility to its TPs prior to the Standard’s enforcement date. Such failures could result in use of untimely or inaccurate information in planning models used to assess BPS reliability, therefore, the BPS could be planned with the expectation that a generation facility has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, the likelihood of these risks occurring was reduced because 16 of the 18 applicable Facilities are wind facilities; wind generation is not typically utilized as a firm resource, therefore, PPME’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that wind generation may be unavailable at any given time. The remaining two Facilities are a combined cycle plant rated at 490 MW and a 100MW peaking generator. At the time of the Standard effective date, 14.7% of PPME’s applicable Facilities had Real Power capabilities verified per Attachment 1 and had an Attachment 2 form provided to the TPs. When PPME discovered that it was not on track to complete the verifications by the enforcement date, it increased its resources dedicated to completing the work in an effort to meet the Standard Requirements. These issues posed a low risk of causing intermediate harm, and therefore, would pose a minimal risk to the Reliability of the BPS. No harm is known to have occurred. WECC considered PPME's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, PPME: 1) determined the Facilities not yet verified; 2) created a schedule to complete the verifications for all Facilities to ensure another milestone date is not missed; 3) conducted Real Power capability verification of at least 60% of its Facilities in the WECC footprint; 4) provided Attachment 2 forms for each completed Facility verification to its TPs; and 5) is utilizing GenSuite tracking software to track future verification dates and set reminders for upcoming compliance deadlines.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Avangrid Renewables (PPME) | NCR10259 | WECC2017016846 | MOD-025-2 | R2 | On January 23, 2017, PPME submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Specifically, PPME reported that it failed to verify Reactive Power capabilities of at least 40 percent of its Facilities, in accordance with Attachment 1 of the Standard, by the effective date of the Standard. Additionally, PPME failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner by the effective date of the Standard. Specifically, PPME started the verification process for its 18 Facilities prior to the deadline but was unsuccessful in completing verification for at least eight of the facilities prior to the July 1, 2016, the effective date of the Standard. WECC determined that although PPME was in the process of performing the Reactive Power capability verification studies, it was unable to complete verification of Reactive Power capabilities for at least 40 percent of its Facilities by the Standard’s effective date. Furthermore, PPME was unable to provide its TPs with an Attachment 2 form for each of its Facilities as required by R2.2, by the effective date of the Standard. The root cause of this issue of noncompliance was PPME’s underestimation of the time and resources required to be compliant with the Standard by the July 1, 2016 enforcement date. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for 40 percent of PPME’s Facilities. WECC determined that the end date of this issue is June 27, 2017, when PPME provided the Attachment 2 form to its TPs for more than 40% of its Facilities, for a total of 362 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, PPME failed to verify its Reactive Power capabilities by the Standard’s enforcement date. Additionally, PPME failed to provide the Attachment 2 form for each applicable Facility to its TPs prior to the Standard’s enforcement date. Such failures could result in use of untimely or inaccurate information in planning models used to assess BPS reliability, therefore, the BPS could be planned with the expectation that a generation facility has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, the likelihood of these risks occurring was reduced because 16 of the 18 applicable Facilities are wind facilities; wind generation is not typically utilized as a firm resource, therefore, PPME’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that wind generation may be unavailable at any given time. The remaining two Facilities are a combined cycle plant rated at 490 MW and a 100MW peaking generator. At the time of the Standard effective date, 14.7% of PPME’s applicable Facilities had Reactive Power capabilities verified per Attachment 1 and had an Attachment 2 form provided to the TPs. When PPME discovered that it was not on track to complete the verifications by the enforcement date, it increased its resources dedicated to completing the work in an effort to meet the Standard Requirements. These issues posed a low risk of causing intermediate harm, and therefore, would pose a minimal risk to the Reliability of the BPS. No harm is known to have occurred. WECC considered PPME's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, PPME: 1) determined the Facilities not yet verified; 2) created a schedule to complete the verifications for all Facilities to ensure another milestone date is not missed; 3) conducted Reactive Power capability verification of at least 60% of its Facilities in the WECC footprint; 4) provided Attachment 2 forms for each completed Facility verification to its TPs; and 5) is utilizing GenSuite tracking software to track future verification dates and set reminders for upcoming compliance deadlines.
2018-07-31 | Western Electricity Coordinating Council (WECC) | CalPeak Power Panoche LLC (CPPA) | NCR05053 | WECC2017018109 | PRC-019-2 | R2 | On August 1, 2017, CPPA submitted a Self-Certification stating that, as a Generation Owner, it was in noncompliance with PRC-019-2 R2. Specifically, CPPA reported that it failed to coordinate its Protection System settings or component changes within 90 calendar days following the identification or implementation of systems, equipment, or setting changes that would affect the coordination described in Requirement 1 of the Standard. After reviewing all relevant information, WECC determined that CPPA failed to perform PRC-019-2 R2 as described in its Self-Report. The root cause of the noncompliance was insufficient time allotted for the task. Specifically, CPPA contacted its Transmission Owner (TO) to obtain approval/confirmation to make the changes to its Protection Systems; however, due to the slow response from its TO, the coordination within 90 calendar days as required by PRC-019-2 R2 was not met. WECC determined that this issue began on June 5, 2017, 90 days after CPPA identified the necessary protection system changes, but failed to implement those changes and coordination as defined in Requirement 1 of the Standard, and ended on September 27, 2017, when all identified Protective System changes were completed and coordinated, for a total of 114 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, CPPA failed to coordinate its Protection System settings or component changes within 90 calendar days following the identification or implementation of systems, equipment, or setting changes that would affect the coordination described in Requirement 1 of the Standard. Such failure could result in damage to the generators and potential loss of 71MW of generation. However, CPPA’s inherent risk to the BPS is minimal as it owns one Facility with one 71 MW generator with respective Protection Systems. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, CPPA: 1) received approval from its TO and updated its Protection System settings; 2) created obligation notification reminders for PRC-019 to review, verify, and coordinate as necessary at least once every 5 years. If the identification or implementation of systems, equipment, or setting changes occur, it will perform a coordination as described in R1; 3) added language to the DocMinder obligation reminder to address the 90 calendar day time constraints stated in R2; and 4) set up reminders for PRC-19, each month, beginning 12 months before its due date. WECC has verified the completion of all mitigation activity.
2018-07-31 | Western Electricity Coordinating Council (WECC) | CalPeak Power Vaca-Dixon LLC (CVPD)) | NCR05054 | WECC2017018110 | PRC-019-2 | R2 | On August 1, 2017, CVPD submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-019-2 R2. Specifically, CVPD reported that it failed to coordinate its Protection System settings or component changes within 90 calendar days following the identification or implementation of systems, equipment, or setting changes that would affect the coordination described in Requirement 1 of the Standard. After reviewing all relevant information, WECC determined that CVPD failed to perform PRC-019-2 R2 as described in its Self-Report. The root cause of the noncompliance was insufficient time allotted for the task. Specifically, CVPD contacted its Transmission Owner (TO) to obtain approval/confirmation to make the changes to its Protection Systems; however, due to the slow response from its TO, the coordination within 90 calendar days as required by PRC-019-2 R2 was not met. WECC determined that this issue began on May 28, 2017, 90 days after CVPD identified the necessary protection system changes, but failed to implement those changes and coordination as defined in Requirement 1 of the Standard, and ended on October 10, 2017, when all identified Protective System changes were completed and coordinated, for a total of 135 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, CVPD failed to coordinate its Protection System settings or component changes within 90 calendar days following the identification or implementation of systems, equipment, or setting changes that would affect the coordination described in Requirement 1 of the Standard. Such failure could result in damage to the generators and potential loss of 71MW of generation. However, CVPD’s inherent risk to the BPS is minimal as it owns one Facility with one 71 MW generator with respective Protection Systems. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To mitigate this noncompliance, CVPD: 1) received approval from its TO and updated its Protection System settings; 2) created obligation notification reminders for PRC-019 to review, verify, and coordinate as necessary at least once every 5 years. If the identification or implementation of systems, equipment, or setting changes occur, it will perform a coordination as described in R1; 3) added language to the DocMinder obligation reminder to address the 90 calendar day time constraints stated in R2; and 4) set up reminders for PRC-19, each month, beginning 12 months before its due date. WECC has verified the completion of all mitigation activity.
2018-07-31 | Western Electricity Coordinating Council (WECC) | El Paso Electric Company (EPE) | NCR05140 | WECC2017018292 | PRC-005-6 | R3 | On August 30, 2017, EPE submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R3. Specifically, EPE reported that it failed to complete the 18-month maintenance activities for nine of its Vented Lead-Acid (VLA) batteries. After reviewing all the relevant information, WECC determined that EPE failed to maintain nine VLA batteries within the time-based maintenance intervals prescribed within PRC-005-6 Table 1-4(a). The 18-month maintenance requirement was incorrectly calculated to be due in May 2017, but should have been March 2017 and, therefore, entered incorrectly into EPE’s maintenance spreadsheet. The root cause of the noncompliance was EPE’s failure to verify that the maintenance due dates were calculated accurately prior to entering them into the maintenance spreadsheet. WECC determined that this issue began on April 1, 2017, the 19th month after EPE failed to perform maintenance on nine VLA batteries. WECC determined that the end date of this issue is April 21, 2017, when EPE performed maintenance on the nine VLA station batteries for a total of 21 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, EPE failed to maintain some of its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance interval prescribed within Table 1-4(a) of the Standard. Specifically, EPE failed to maintain nine of 64 VLA batteries that were on the 18-month maintenance cycle at two different generating facilities. The generating facilities have a combined capacity of 824 MW. The VLA batteries provide DC supply to the control functions, as well as all elements of the protection system for their respective Generating Units. Such failure could result in local service interruption, considerable damage to Generation equipment, and in some cases, wide spread outages. However, EPE has several good detective controls that identified this issue soon after the noncompliance began. The issues were discovered during an internal audit of the generation maintenance summary spreadsheet. Specifically, EPE performed an annual review of the Protection System Maintenance Program (PSMP) which is used to create the maintenance schedule for the upcoming year. The annual review was triggered using the OATI tracking tool. The tool helps facilitate the PSMP review if maintenance intervals have changed. Additionally, EPE uses the WECC PSMP maintenance summary document as its primary database and continuously updates the document. The nine VLA batteries are associated with two of nine generators, and the batteries were not utilized during the time of noncompliance. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that EPE does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, EPE: a. completed the maintenance activity of the nine VLA batteries; and b. reviewed and adjusted 18-month maintenance dates for the batteries in the scheduling software.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Energy Northwest - Columbia | NCR00209 | WECC2017017342 | EOP-004-2 | R3 | On April 5, 2017, ENWC submitted a Self-Report stating that, as a Generator Owner, and Generator Operator, it was in noncompliance with EOP-004-2 R3. Specifically, ENWC reported that during its 2016 WECC Self-Certification, it discovered that documentation for its annual validation of contact information per EOP-004-2 R3 could not be found for the years 2014, 2015, and 2016. After reviewing all the relevant information, WECC determined that ENWC failed to perform the annual validation of contact information as required by EOP-004-2 R3 for the years 2014, 2015, and 2016. The root cause of the noncompliance was due to ENWC not implementing a process to perform or document the annual validation of contact information found within its Operating Plan. WECC determined that this issue began on January 1, 2015, when a validation of all contact information contained in the Operating Plan should have been performed for 2014, and ended on May 31, 2017, when ENWC verified the contact information contained in its Operating Plan, for a total of 882 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, ENWC failed to perform the annual validation of contact information as required by EOP-004-2 R3 for the years 2014, 2015, and 2016. Such failure could result in reportable events not being reported; not being reported to all applicable registered entities, or the events being reported to the wrong contacts. However, due to the nature of ENWC’s facility, its security personnel are in daily contact with local law enforcement, thus the contact information was verified daily. ENWC’s operations department also maintained contact with the Department of Energy and with its Balancing Authority regularly. The only number that had changed since 2014 was that of the Reliability Coordinator (RC). Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that ENWC does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this noncompliance ENWC: 1) added the correct contact information for the RC to its Operating Plan; 2) verified, and documented the verification, of all contact information contained in its Operating Plan; 3) updated its plant procedure to include the annual validation of contact information; and 4) created a reoccurring assignment within the work management program to validate the contact information annually.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Energy Northwest - Columbia (ENWC) | NCR00209 | WECC2017017187 | MOD-025-2 | R1; R1.1, 1.2 | On March 1, 2017, ENWC submitted Self-Certifications stating that, as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. ENWC reported that it failed to verify the Real Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard. After reviewing all the relevant information, WECC determined that ENWC failed to verify the Real Power capabilities of at least 40% of its applicable facilities in accordance with Attachment 1 of the Standard, as required by R1.1. Additionally, ENWC failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 days of verification, as required by R1.2. The root cause of the noncompliance was ENWC’s misunderstanding of the enforceable date for the Requirement. Specifically, ENWC misunderstood the "two years after regulatory approval" as being two years from the Standards effective date. WECC determined that these issues began on July 1, 2016 when implementation of MOD-025-2 R1 became mandatory and enforceable for ENWC’s applicable Facilities. WECC determined that the end date of these issues was December 18, 2017, when ENWC submitted an attachment 2 form to its TP, for a total of 535 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, ENWC failed to verify the Real Power Capabilities of its applicable facilities by the enforceable date of MOD-025-2 R1. This data is used for planning purposes to improve the accuracy of the system models. System models are used to develop contingencies and operating limits. Inaccurate information could result in inaccurate models; therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, ENWC had reviewed five years of historical operational data to determine the maximum real power Columbia's generator has operated and sent that data to its TP. Additionally, ENWC held discussions with its TP, which is also ENWC’s designated Planning Coordinator (PC). The technical staff of the TP/PC stated that it had sufficient operational data from the station as well as design data and original commissioning testing to develop applicable planning models. ENWC has one applicable facility consisting of one generating unit with a total nameplate capacity of approximately 1200 MW. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, ENWC: 1.) conducted self-assessment using experienced external vendor to evaluate applicable NERC Requirements and Standards for gaps; 2.) revised ENWC’s General Business Procedures to align the Compliance Program Plan with current NERC Reliability Compliance Program Plan document; and 3.) conducted Real Power and Reactive Power capabilities testing and provided results to the TP using Attachment 2.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Energy Northwest - Columbia (ENWC) | NCR00209 | WECC2017017188 | MOD-025-2 | R2, 2.1, 2.2 | On March 1, 2017, ENWC submitted Self-Certifications stating that, as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. ENWC reported that it failed to verify the Reactive Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard. After reviewing all the relevant information, WECC determined that ENWC failed to verify the Reactive Power capabilities of at least 40% of its applicable facilities in accordance with Attachment 1 of the Standard, as required by R2.1. Additionally, ENWC failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) within 90 days of verification, as required by R2.2. The root cause of the noncompliance was ENWC’s misunderstanding of the enforceable date for the Requirement. Specifically, ENWC misunderstood the "two years after regulatory approval" as being two years from the Standards effective date. WECC determined that these issues began on July 1, 2016 when implementation of MOD-025-2 R2 became mandatory and enforceable for ENWC’s applicable Facilities. WECC determined that the end date of these issues was December 18, 2017, when ENWC submitted an attachment 2 form to its TP, for a total of 535 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, ENWC failed to verify the Reactive Power Capabilities of its applicable facilities by the enforceable date of MOD-025-2 R2. This data is used for planning purposes to improve the accuracy of the system models. System models are used to develop contingencies and operating limits. Inaccurate information could result in inaccurate models; therefore, the BPS could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, ENWC had reviewed five years of historical operational data to determine the maximum reactive power Columbia's generator has operated and sent that data to its TP. Additionally, ENWC held discussions with its TP, which is also ENWC’s designated Planning Coordinator (PC). The technical staff of the TP/PC stated that it had sufficient operational data from the station as well as design data and original commissioning testing to develop applicable planning models. ENWC has one applicable facility consisting of one generating unit with a total nameplate capacity of approximately 1200 MW. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, ENWC: 1.) conducted self-assessment using experienced external vendor to evaluate applicable NERC Requirements and Standards for gaps; 2.) revised ENWC’s General Business Procedures to align the Compliance Program Plan with current NERC Reliability Compliance Program Plan document; and 3.) conducted Real Power and Reactive Power capabilities testing and provided results to the TP using Attachment 2.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Hetch Hetchy Water and Power (HHWP) | NCR05182 | WECC2017017889 | PRC-005-2(i) | R3 | On July 7, 2017, HHWP submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-005-2(i) R3. Specifically, HHWP reported that it failed to maintain a battery charger in accordance with the maximum maintenance interval as prescribed on Table 1-4(a). In preparation for its 2017 audit, HHWP found a work order that was closed even though the maintenance was not completed. Additionally, the tracking system used for keeping testing records did not identify the missing test for the battery charger. HHWP included the battery chargers on the work order for testing, but the work order was closed prior to completion. HHWP did not verify that the battery banks and battery chargers were tested at the same time. After reviewing all the relevant information, WECC determined that HHWP failed to meet the 18-month maintenance interval for a battery charger in accordance with the maximum maintenance interval as prescribed on Table 1-4(a). The root cause of the noncompliance was HHWP Maintenance Engineering’s failure to ensure all tasks had been completed prior to closing out the work order. WECC determined that this issue began on August 20, 2016, the 19th month after HHWP failed to maintain a battery charger in its Protection System that is included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-4(a). WECC determined that the end date of this issue was May 9, 2017 when HHWP completed testing for the battery charger, for a total of 263 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, HHWP failed to maintain one of the battery chargers within the Protection System as required in Table 1-4(a). Such failure could lead to local service interruption, considerable damage to substation equipment, and loss of load. However, HHWP implemented strong preventative controls to prevent future noncompliance. HHWP owns and operates approximately 400 MW of hydroelectric generation. Approximately 75% of HHWP's generating capacity is connected to its 230 kV switchyard, where the battery charger in scope is located, however, HHWP has redundant battery chargers at the switchyard. The potential failure of one battery charger should not impact the BPS. Based on this, WECC determined that the potential harm has a low likelihood of occurring. No harm is known to have occurred. WECC notes that HHWP does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, HHWP: a. created work order structure issuing annual battery bank work orders concurrently with annual battery charger work orders; b. developed revised workflow and approval process for battery bank and battery charger testing; c. identified HHWP staff who will require training to the revised workflow and approval process for battery bank and battery charger testing; d. developed training content for HHWP identified staff requiring training for the revised workflow and approval process for battery bank and battery charger testing; e. completed training for identified staff requiring training to the revised workflow and approval process for battery bank and battery charger testing; f. modified HHWP's Protection System Maintenance and Testing Program based on revised workflow process and any feedback received during the revised battery bank and battery charger workflow process training; and g. completed and finalized HHWP's Protection System Maintenance and Testing Program.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Midway Peaking, LLC (MIDP) | NCR10323 | WECC2017018108 | PRC-019-2 | R2 | On August 1, 2017, MIDP submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with PRC-019-2 R2. Specifically, MIDP reported that it failed to coordinate its Protection System settings or component changes within 90 calendar days following the identification or implementation of systems, equipment, or setting changes that would affect the coordination described in Requirement 1 of the Standard. After reviewing all relevant information, WECC determined that MIDP failed to perform PRC-019-2 R2 as described in its Self-Report. The root cause of the noncompliance was insufficient time allotted for the task. Specifically, MIDP contacted its Transmission Owner (TO) to obtain approval/confirmation to make the changes to its Protection Systems; however, due to the slow response from its TO, the coordination within 90 calendar days as required by PRC-019-2 R2 was not met. WECC determined that this issue began on April 19, 2017, 90 days after MIDP identified the necessary protection system changes, but failed to implement those changes and coordination as defined in Requirement 1 of the Standard, and ended on June 29, 2017, when all identified Protective System changes were completed and coordinated, for a total of 71 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, MIDP failed to coordinate its Protection System settings or component changes within 90 calendar days following the identification or implementation of systems, equipment, or setting changes that would affect the coordination described in Requirement 1 of the Standard. Such failure could result in damage to the generators and potential loss of 140MW of generation. However, MIDP’s inherent risk to the BPS is minimal as it owns one Facility with two 70 MW generators with respective Protection Systems. Additionally, MIDP has not experienced any unit trips due to miss-coordination between the generating units’ voltage regulating system controls and the applicable equipment capabilities. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, MIDP: 1) received approval from its TO and updated its Protection System settings; 2) created obligation notification reminders for PRC-019 to review, verify, and coordinate as necessary at least once every 5 years. If the identification or implementation of systems, equipment, or setting changes occur, it will perform a coordination as described in R1; 3) added language to the DocMinder obligation reminder to address the 90 calendar day time constraints stated in R2; and 4) set up reminders for PRC-19, each month, beginning 12 months before its due date. WECC has verified the completion of all mitigation activity.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Modesto Irrigation District (MID) | NCR05244 | WECC2017017298 | PRC-004-4(i) | R1 | On March 24, 2017, MID submitted a Self-Report stating that, as a Distribution Provider, Generator Owner and Transmission Owner, it was in noncompliance with PRC-004-4(i) R1. Specifically, MID reported that it failed to analyze five Bulk Electric System (BES) interrupting device operations to identify whether the Protection System components caused Misoperations, within 120 calendar days. After reviewing all the relevant information, WECC determined that MID failed to identify, within 120 calendar days of the BES interrupting device operation, whether its Protection System components caused a Misoperation. The root cause of the noncompliance was MID’s failure to have sufficient staffing, which resulted in decreased focus on compliance with NERC standards. WECC determined that the dates of noncompliance, BES interrupting device operation, and remediation date are as follows: First Instance: Date of Noncompliance- November 9, 2016 Date of BES interrupting device operation- July 12, 2016 Remediation Date- February 22, 2017 Total Days of Noncompliance- 106 days Second Instance: Date of Noncompliance- February 9, 2017 Date of BES interrupting device operation- October 12, 2016 Remediation Date- February 22, 2017 Total Days of Noncompliance- 14 Third Instance: Date of Noncompliance- February 9, 2017 Date of BES interrupting device operation- October 12, 2016 Remediation Date- February 22, 2017 Total Days of Noncompliance- 14 Fourth Instance: Date of Noncompliance- February 12, 2017 Date of BES interrupting device operation- October 15, 2016 Remediation Date- February 22, 2017 Total Days of Noncompliance- 11 Fifth Instance: Date of Noncompliance- February 13, 2017 Date of BES interrupting device operation- October 16, 2016 Remediation Date- February 22, 2017 Total Days of Noncompliance- 10 | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. On five instances, MID failed to identify, within 120 calendar days of the BES interrupting device operation, whether its Protection System components caused a Misoperation. Such failure could result in continued Protection System Misoperation and the loss of two 230kV and two 115 kV transmission elements. However, MID had a Senior Protection Engineer working on the system operation events analysis, who was aware of the PRC-004 reporting requirements, but due to under staffing, was unable to complete the analysis on time. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that MID does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, MID: a. performed operation analysis for the missing devices; b. hired additional engineers for transmission and distribution; c. assigned back-up subject matter experts (SMEs) to support the primary SME’s duties for associated Standards; d. created automatic reminders that will be sent via email directly to the primary SME each month as a reminder to review all relay operations, identify any BES operations, and perform and document the analysis. If the due date is missed, a daily reminder will be sent and escalated to include the SME's Manager and the Compliance Analyst; e. implemented training for the Transmission and Distribution Engineering department including how to analyze relay operations and to determine if a Misoperation occurred, how to document the analysis, and make the necessary notifications required if a Misoperation is identified; and f. added monthly review for the Transmission and Distribution Engineering Manager to review the BES Breaker Operation Report. The report compiles all 230kV and 115kV relay operations and will be forwarded to the Transmission and Distribution Engineers as a reminder to perform the analysis in the event of a relay operation.
2018-07-31 | Western Electricity Coordinating Council (WECC) | NAES Corporation - Pio Pico Energy Center (NAES-PP) | NCR11651 | WECC2018018914 | TOP-001-3 | R5 | On December 29, 2017, NAES-PP submitted a Self- Report stating that, as a Generator Operator, it was in noncompliance with TOP-001-3 R5. Specifically, NAES-PP reported that on December 14, 2017 at 18:50 Pacific Standard Time (PST) the NAES-PP Operator prepared a unit to start operations at 19:00 PST for a 30-minute operation, forecasted at 50 MW, per the Automated Dispatch System (ADS). At 19:30 PST, the NAES-PP Operator shutdown the unit, per the original instructions in the ADS. An additional instruction had been sent from the BA to extend the operating duration from 19:30 PST to 20:15 PST. The NAES-PP Operator began the shutdown process before he realized that a new instruction had been received from the BA. When the NAES-PP Operator realized the shutdown error, he coordinated with the BA to keep the unit offline. After reviewing all the relevant information, WECC determined that NAES-PP Operator failed to comply with an Operating Instruction issued by its BA. Specifically, it failed to adhere to instructions in ADS from its BA to increase the operating duration from 30 minutes to one hour and 15 minutes, prematurely shutting down the unit. The root cause of the noncompliance was lack of training on the use and operation of the ADS. Additionally, NAES-PP had a lack of internal controls to ensure all operating instructions received appropriate actions. WECC determined that this issue began on December 14, 2017 at 19:30 PST, when NAES-PP failed to adhere to the operating instructions of its BA. WECC determined that the end date of this issue is December 14, 2017 at 20:15 PST, when NAES-PP’s Operator coordinated with its BA to keep the unit offline, for a total of 45 minutes of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, NAES-PP failed to comply with an Operating Instruction issued by its BA. NAES-PP owns and operates a 465 MVA natural gas generating facility which was subject to the noncompliance. Such failure could result in the BA lacking the generation it needs in its area to balance load and generation to maintain the reliability of the BPS. 9. However, NAES-PP was in communication with its BA for the duration of the event, which allowed the BA to make necessary adjustments. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. | To remediate and mitigate this issue, NAES-PP: a. coordinated with the BA to determine that the unit in the scope of the noncompliance should remain off; b. conducted one-on-one trainings with the Plant Manager and each Operator to review the details of this noncompliance, the requirements of TOP-001-3, as well as startup and shutdown checklist and procedures; and c. updated the alarm system to signal every 5 minutes to indicate new instructions or load changes, and the Operator will have to acknowledge the alarm or it will continue. The “Commitment” box will turn red for a “Startup” or “Shutdown” order.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC2017018229 | PER-003-1 | R2 | On August 22, 2017, PGAE submitted a Self-Report stating that, as a Transmission Operator, it was in noncompliance with PER-003-1 R2.2. Specifically, PGAE reported that on April 20, 2017, it discovered that one of its System Dispatcher failed to complete the renewal process for his NERC Certification. After reviewing all the relevant information, WECC determined that PGAE failed to ensure one individual on its Real-time operating staff maintained a valid NERC certification while performing Transmission Operator reliability-related tasks. The root cause of the noncompliance was a less than adequate process for ensuring applicable employees maintained NERC certifications. WECC determined that this issue began on September 2, 2015, when the certification expired, and ended April 20, 2017, when the System Dispatcher’s roles were changed so that he no longer worked on the Real-time desk, for a total of 596 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGAE failed to ensure one individual on its Real-time operating staff maintained a valid NERC certification while performing Transmission Operator reliability-related tasks. Such failure could limit PGAE’s ability to ensure that the individual in question was competent to perform Real-time reliability-related tasks. However, this issue was limited to one previously-certified individual with six years of operator experience, who had completed sufficient training hours to renew certification prior to the certification’s expiration. Additionally, PGAE normally has a minimum of three NERC-certified employees performing reliability-related tasks at any given time. Based on this, WECC determined that the potential harm had a remote likelihood of occurring. No harm is known to have occurred. WECC notes that PGAE does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this noncompliance, PGAE: 1) changed the role of the operator in scope to no longer operate the system; 2) instructed all applicable employees via its Training Newsletter, details of the expectations for maintaining certification, with a link to the NERC site; 3) formalized the process for certification renewal for applicable staff; and 4) strengthened its internal controls to ensure employees maintain job qualifications, including applicable NERC certifications by: a. reviewing all employee records for accurate credential maintenance; b. evaluating all certificates expiring within the next 12 months at a minimum of a bi-annual bases, with the expectation to renew within three months of expiration; c. reviewing all internal records for accuracy, in comparison with the NERC database and establish a process of uploading and updating all records; and d. maintaining a copy of active NERC certificate for all staff in a Real-time operating position.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Placer County Water Agency (PCWA) | NCR11420 | WECC2017016982 | MOD-025-2 | R1 | On February 10, 2017, PCWA submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, PCWA reported that on June 21, 2016, it was advised by a third-party contractor that its previous Generating Unit Model Validation study completed by an independent engineering contractor in 2012 would not be sufficient to use as verification of its Real Power capabilities per MOD-025-2 R1. The contractor further reported that it would not be possible to become compliant prior to the enforcement date of the Standard. Therefore, PCWA reported that it failed to verify Real Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard by the effective date of the Standard. Additionally, PCWA also failed to Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) by the effective date of the Standard. WECC determined that PCWA failed to verify the Real Power capabilities of at least 40 percent of its applicable Facilities, in accordance with Attachment 1 of the Standard. PCWA also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its TP by the effective date of the Standard. The root cause of these issues of noncompliance was a misunderstanding of the Standard. Specifically, PCWA did not accurately verify whether the Generating Unit Model Validation study performed in 2012 would sufficiently meet all the requirements of MOD-025-2. WECC determined that these issues began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for 40 percent of PPME’s applicable Facilities. WECC determined that the end date of these issues was December 14, 2017, when PCWA provided its Real Power capabilities to its TP, for a total of 531 days of noncompliance. | WECC determined these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PCWA failed to verify the Real Power capabilities of at least 40 percent of its applicable Facilities in accordance with Attachment 1 of the Standard, which could potentially result in inaccurate information of generator gross and net Real Power capabilities used in planning models which are used to assess BES reliability. Inaccurate planning models could allow the BPS to be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, PCWA implemented good compensating controls. Specifically, BCWA implemented Generator Unit Model Validation testing for its Facilities in 2012. If a real-time contingency that required the generating units to respond were to have occurred, the 2012 data would have been satisfactory for mitigating the contingency. There are three hydro Facilities in the scope of these issues; two rated at 68 MVA each and the third rated at 88 MVA. No harm is known to have occurred. WECC considered PCWA's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, PCWA: 1) contracted with a third-party to verify the Real Power capabilities for its applicable Facilities; 2) sent the completed Attachment 2 form to its TP; 3) added recurring MOD-025 verifications at intervals less than five years to its compliance calendar; and 4) conducted an in-depth review of applicable Reliability Standards to prevent future noncompliance.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Placer County Water Agency (PCWA) | NCR11420 | WECC2017017338 | MOD-025-2 | R2 | On March 31, 2017, PCWA submitted a Self-Report stating that as a GO, it was also in noncompliance with MOD-025-2 R2. Specifically, PCWA reported that on June 21, 2016, it was advised by a third-party contractor that its previous Generating Unit Model Validation study completed by an independent engineering contractor in 2012 would not be sufficient to use as verification of its Reactive Power capabilities per MOD-025-2 R1 and R2. The contractor further reported that it would not be possible to become compliant prior to the enforcement date of the Standard. Therefore, PCWA reported that it failed to verify Reactive Power capabilities of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard by the effective date of the Standard. Additionally, PCWA also failed to Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner (TP) by the effective date of the Standard. WECC determined that PCWA failed to verify the Reactive Power capabilities of at least 40 percent of its applicable Facilities, in accordance with Attachment 1 of the Standard. PCWA also failed to submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its TP by the effective date of the Standard. The root cause of these issues of noncompliance was a misunderstanding of the Standard. Specifically, PCWA did not accurately verify whether the Generating Unit Model Validation study performed in 2012 would sufficiently meet all the requirements of MOD-025-2. WECC determined that these issues began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for 40 percent of PPME’s applicable Facilities. WECC determined that the end date of these issues was December 14, 2017, when PCWA provided its Reactive Power capabilities to its TP, for a total of 531 days of noncompliance. | WECC determined these issues of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PCWA failed to verify the Real Power and Reactive Power capabilities of at least 40 percent of its applicable Facilities in accordance with Attachment 1 of the Standard, which could potentially result in inaccurate information of generator gross and net Reactive Power capabilities used in planning models which are used to assess BES reliability. Inaccurate planning models could allow the BPS to be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. However, PCWA implemented good compensating controls. Specifically, BCWA implemented Generator Unit Model Validation testing for its Facilities in 2012. If a real-time contingency that required the generating units to respond were to have occurred, the 2012 data would have been satisfactory for mitigating the contingency. There are three hydro Facilities in the scope of these issues; two rated at 68 MVA each and the third rated at 88 MVA. No harm is known to have occurred. WECC considered PCWA's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, PCWA: 1) contracted with a third-party to verify the Reactive Power capabilities for its applicable Facilities; 2) sent the completed Attachment 2 form to its TP; 3) added recurring MOD-025 verifications at intervals less than five years to its compliance calendar; and 4) conducted an in-depth review of applicable Reliability Standards to prevent future noncompliance.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Public Service Company of New Mexico (PNM) | NCR05333 | WECC2017017463 | EOP-005-2 | R11 | On April 25, 2017, PNC submitted a Self-Report stating that, as a Distribution Provider, Transmission Owner and Transmission Operator, it was in noncompliance with EOP-005-2 R11. PNM reported that it had failed to provide a minimum of two hours of System restoration training every two calendars years to their field switching personnel identified as performing unique tasks associated with the TOP’s restoration plan that are outside of their normal tasks. The training tasks for System restoration include manual island synchronization, substation manning for the relaying of operating information to System Operators, and verifying and maintaining substation battery reserves. After reviewing all the relevant information, WECC determined that PNM failed to provide a minimum of two hours of System restoration training every two calendar years to its field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks as required by EOP-005-2 R11, The root cause of the noncompliance was PNM’s failure to track this training task which resulted in a failure to conduct training pursuant to EOP-005-2 R11. WECC determined that this issue began on January 1, 2016 when PNM failed to provide a minimum of two hours of System restoration training as required every two calendars years pursuant to EOP-005-2 R11. WECC determined that the end date of this issue was March 3, 2016, when PNM provided training to applicable personnel for a total of 62 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PNM failed to provide System restoration training every two calendars years to its field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks pursuant to EOP-005-2 R11. Such failure could potentially result in switching personnel being unable to perform, or inadequately performing, the tasks associated with the TOP's restoration plan. These tasks enable System restoration from Blackstart resources to assure reliability is maintained during restoration and priority is placed on restoring the Interconnection. However, the unique tasks have not changed since the April 2013 training. Additionally, these tasks are performed periodically as a part of normal system responsibilities and therefore are not exclusively performed during a complete system restoration event. The likelihood that these field personnel would not be able to successfully perform these tasks in the event of a complete system blackout is unlikely given their performance on a periodic basis. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that PNM does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, PNM: 1.) Conducted training to applicable staff; 2.) Added training to its training database for tracking; and 3.) Set automated reminders to training department at 6 months, 12 weeks and 30 days prior to due date within its task management tool, with automated escalation reminders to additional personnel and management. WECC verified completion of the identified mitigation activities.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC2017018580 | FAC-008-1 | R1 | On November 2, 2017, CHPD submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with FAC-008-1 R1. Specifically, CHPD reported that while performing a risk-based internal review for FAC-008-3, CHPD discovered that its Bottleneck Report did not list Ratings for its internal bushing current transformers (CTs). CHPD used its Bottleneck Report as a repository of its equipment and the associated Ratings for that equipment. CHPD’s Ratings Methodology did include a methodology for rating CTs, but it was applicable to free-standing CTs, which are the primary current-carrying device, rather than the bushing CTs internal to circuit breakers and power transformers, which do not carry primary current. After reviewing all the relevant information, WECC determined that CHPD failed to document its current methodology used for developing Facility Ratings of its solely and jointly owned Facilities. Specifically, the CHPD’s methodology did not include analyzing and rating internal bushing CTs as part of the rating process. The root cause of the noncompliance was due to CHPD’s incorrect understanding of the methodology for determining the rating for circuit breakers and power transformers, whereby it used only the nameplate rating of the equipment. WECC determined that this issue began on June 18, 2007, when CHPD utilized an incomplete methodology for developing Facility Ratings of its solely and jointly owned Facilities, and ended on October 24, 2017, when CHPD developed an accurate methodology for calculating Facility Ratings for internal bushing CTs, for a total of 3,781 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CHPD failed to document its current methodology used for developing Facility Ratings of its solely and jointly owned Facilities. Specifically, the CHPD’s methodology did not include analyzing and rating internal bushing CTs as part of the rating process. Such failure could result in Transmission Planners and Grid Operators having incorrect ratings in the planning studies and in the databases, utilized for real-time operation of the grid. This could reduce situational awareness and could lead to possible System Operating Limits violations; loss of load; loss of generation; and/or damage to equipment. However, upon calculating the internal bushing CT ratings under the new Methodology, CHPD discovered only 20 bushing CTs out of 267 transmission sets of CTs that became the most limiting element. Of these, 14 had either a low or no impact. Specifically, for nine of the 14 bushing CTs, CHPD was only impacted operationally if the line were on the transfer breaker. For the remaining five, two were on metering circuits which provided indication only (no control), two were on a generation line whereby the CT ratio was 25% above the generation capability, and one was on a transmission line whereby historical stressed loads were significantly below the CT ratio. Based on this, WECC determined that the potential harm had a remote likelihood of occurring. No harm is known to have occurred. WECC notes that CHPD does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this noncompliance CHPD: 1) updated its Facility Ratings Methodology to include calculating the rates for internal bushing CTs; 2) conducted a physical walkthrough of all its Facilities to inspect the nameplate ratings of all internal bushing CTs on breakers and transformers to ensure the CTs were included in the Bottleneck Report with correct tap settings and thermal rating factors. As part of this process, it recalculated the internal bushing CT ratings based on the new methodology and determined whether any become the most limiting element and revised the settings for any equipment that was impacted.; and 3) distributed its updated methodology document to its Reliability Coordinator and neighboring entities, and notified them of the changes made to the ratings.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC2017018581 | FAC-009-1 | R1 | On November 2, 2017, CHPD submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with FAC-009-1 R1. Specifically, CHPD reported that while performing a risk-based internal review for FAC-008-3, CHPD discovered that its Bottleneck Report did not list Ratings for its free-standing current transformers (CTs) at four locations. CHPD used its Bottleneck Report as a repository of its equipment and the associated Ratings for that equipment. The CTs at three of the four locations were equal to or greater than the most limiting elements, and at the four locations, the CT became the most limiting rating at an ambient temperature of -22F, by approximately 5% of the previous limit. Additionally, CHPD discovered that six disconnect switches listed in its Bottleneck Report showed an incorrect ampacity rating. The higher ampacity rating for four of the disconnect switches, located at Rocky Reach and Andrew York substations, increased the Rating for the Facility, which was being operated below the actual limiting element. The lower ampacity rating for two of the disconnect switches, located at the Anderson Canyon substation, did not decrease the Rating for the Facility, as the two disconnect switches were not previously the most limiting element, and the update did not make the switches the most limiting element. After reviewing all the relevant information, WECC determined that CHPD failed to establish Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings Methodology for four free-standing CTs and six disconnect switches. The root cause of the noncompliance related to the free-standing CTs was due to too much activity occurring, and errors made in problem solving. Specifically, its engineers, at the time, believed that the CTs were included in the Bottleneck Report, and with all the activity around ensuring compliance with the new Reliability Standards effective in 2007, this error was overlooked. The root cause of the noncompliance related to the disconnect switches was due to incorrect nameplate ratings on the station prints. WECC determined that this issue began on June 18, 2007, when Facility Ratings for the free-standing CTs and disconnect switches should have been consistent with the associated Facility Ratings Methodology, and ended on October 23, 2017, when CHPD updated its Bottleneck Report with the ratings of its free-standing CTs, and correct ratings for its disconnect switches, for a total of 3,780 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CHPD failed to establish Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings Methodology for four free-standing CTs and six disconnect switches. Such failure could result in equipment being operated at higher ratings than the most limiting piece of equipment, which could potentially cause damage to equipment. However, CHPD implemented a "change in ownership" section to its Bottleneck Report in 2015. When there was a shared ownership of devices, CHPD reviewed this shared ownership prior to making updates to its Bottleneck Report. Additionally, CHPD implemented updates to its system data documents, including its bottleneck documents, when equipment was added, changed, or removed. CHPD had implemented good compensating controls. Specifically, the ratings for three of the free-standing CTs were equal to or greater than the most limiting element; therefore, the system was already operating to the most limiting element. The fourth free-standing CT in scope only became the most limiting element at an ambient temperature of -22 degrees Fahrenheit. This CT was rated at its nameplate value which was calculated at much warmer temperatures, and since the IEEE standard for rating CTs allows an increase in rating for colder temperatures, this CT would not have been damaged if its nameplate rating was exceeded. Additionally, four of the disconnect switches had an increase in ampacity rating so the facility was already being operated below the actual limit. The last two disconnect switches had a decrease in ampacity rating, however, they were not the most limiting elements so they did not decrease the rating for the facility. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that CHPD does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this noncompliance CHPD: 1) updated the Bottleneck Report with ratings for the four free-standing CTs and corrected ratings for the six disconnect switches in scope; 2) reviewed station prints and visited each of its substations and switchyards to assess whether there was additional equipment missing from the Bottleneck Report. Specifically, CHPD verified that all free-standing CTs were included in the Bottleneck Report, and that the disconnect switch ratings in the Bottleneck Report were accurate; 3) updated the station prints as needed; and 4) notified its Reliability Coordinator and neighboring entities of the changes made to the ratings to ensure its neighbors have the most accurate data for their system models.
2018-07-31 | Western Electricity Coordinating Council (WECC) | PUD No. 1 of Douglas County (DOPD) | NCR05343 | WECC2017018367 | PER-005-1 | R3 | During a Compliance Audit conducted from August 21, 2017 through September 1, 2017 WECC determined that DOPD, as a Balancing Authority and Transmission Operator, was in noncompliance with PER-005-1 R3.1. Specifically, WECC auditors evaluated DOPD’s System Operator training records and identified one System Operator for which DOPD had not provided an adequate training record for 2014. The training record provided as evidence was a summary training record which was not sufficient enough in detail to demonstrate compliance with the requirement. After reviewing all the relevant information, WECC determined that DOPD failed to provide evidence that, at least every 12 months, operations training applicable to its organization that reflects emergency operations topics, which includes system restoration using drills, exercises or other training to maintain qualified personnel for one System Operator for the year 2014. The root cause of the noncompliance was less than adequate tracking system for System Operator training. Specifically, the Chief System Operator was tracking System Operator training on a spreadsheet. The Chief System Operator retired and the tracking mechanism was lost. WECC determined that this issue began on May 16, 2014, when annual training should have been performed, and ended March 27, 2015, when the employee in scope completed appropriate training, for a total of 315 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, DOPD failed to provide system restoration training for one of seven (14%) System Operators for 2014, using drills, exercises or other training required to maintain qualified personnel. Such failure could result in the operator’s inability to perform all duties as required during system restoration. However, the issue was limited to one operator who had completed the training in 2013. Based on this, WECC determined that the potential harm had a remote likelihood of occurring. No harm is known to have occurred. WECC notes that DOPD does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this noncompliance, DOPD provided system restoration training to the operator in scope. NERC has since retired this Standard and Requirement. WECC auditors were informed by DOPD during the audit that since 2014, it has implemented a compliance tracking list in SharePoint. This is a separate tracking list from the NERC continuing education hours for System Operator certification. Additionally, for every training interval requirement listed in the Standards there is a SharePoint task list to capture those assigned training tasks in order to send notifications to key training/compliance personnel when those task dates are approaching. Additionally, DOPD has at least one person and a backup person that receives via email a notification of upcoming tasks that are due. These individuals are responsible for tracking, and adequately documenting, all training received by DOPD operations personnel. The Compliance Manager also receives a copy of these email notifications at intervals of 60 days, 3 days, 2 days, and past due. These notices continue until the Compliance Manager marks each as completed. Prior to marking the training records as complete, the Compliance Manager performs one last review of the records for completeness and adequacy for compliance. This provides a multi-level check/approval process and ensures adequate documentation of training records even when key personnel are unavailable due to illness, vacation, attrition, etc.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2017017339 | COM-002-4 | R1.4 | On April 5, 2017, PSE submitted a Self-Report stating that, as a Balancing Authority and Transmission Operator, it was in noncompliance with COM-002-4 R1. PSE reported that it had inadvertently omitted documenting the COM-002-4 R1.4 communications protocol in the Load Office Manual. Specifically, it failed to develop a documented communications protocols for its operating personnel that issue and receive Operating Instructions when the entity did not include the requirement for its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. After reviewing all the relevant information, WECC determined that PSE failed to develop a documented communications protocols for its operating personnel that issue and receive Operating Instructions when the entity did not include the requirement for its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. The root cause of the noncompliance was a less than adequate process for ensuring its documented procedures are compliant pursuant to COM-002-4 R1 Part 1.4. WECC determined that this issue began on July 1, 2016, when the Standards became mandatory and enforceable to PSE. WECC determined that the end date of this issue is April 1, 2017, when it updated its communications protocol documents to include Part 1.4 requirements for a total of 274 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PSE failed to develop a documented communications protocols for its operating personnel that issue and receive Operating Instructions when the entity did not include the requirement for its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. Such failure could potentially result in a miscommunication in an Operating Instruction that could lead to BES elements being removed, operated, or restored in a premature or delayed manner. Unexpected system conditions can result in an unexpected outage, delay in system restoration or damage to Transmission Elements. However, PSE had implemented continuing training for its System Operators that included three-part communications for training, drills and simulators. Additionally, this was a documentation error. Load Office personnel with real-time responsibilities are familiar with the protocols. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that PSE does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, PSE: 1.) add requirement R1.4 verbiage to the documented Load Office Manual – Communications Protocol 2.) create a tool to be used for assessing and documenting the application of each Standard Requirement or sub-requirement; and 3.) mandatory review for all applicable personnel. PSE submitted Mitigation Plan and WECC verified PSE’s Completion of Mitigation Plan.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Red Horse III, LLC (RHIII) | NCR11630 | WECC2017017190 | PRC-024-2 | R2 | On March 1, 2017, RHIII submitted a Self-Certification stating that, as Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R2. Specifically, RHIII did not set its protective relaying such that the generator voltage protective relaying would not trip the applicable generating unit(s) as a result of a voltage excursion within the "no trip zone" of PRC-024-2 Attachment 2. WECC reviewed the Self-Certification and determined that RHIII did not set its protective relaying such that the generator voltage protective relaying would not trip the applicable generating unit(s) as a result of a voltage excursion within the “no trip zone” of PRC-024-2 Attachment 2. The root cause of the issue was RHIII did not ensure coordination between its Project NERC Compliance team, Engineering Procurement and Construction (EPC) contractor, and inverter manufacturer, to ensure PRC-024-2 compliance at the time of commissioning. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for RHIII’s applicable solar installation. This issue ended June 6, 2017 when the inverter settings were updated for a total of 340 days of noncompliance. | WECC determined that this issue posed a minimal likelihood of causing minor harm and therefore is a minimal risk to the reliability of the bulk power system (BPS). In this instance, RHIII failed to set its voltage protective relaying such that it would not trip its applicable Facility within the “no trip zone.” Such failure could result in the premature trip of RHIII’s applicable Facility due to a voltage excursion. There was one inverter setting change required as the under-voltage setting was set to trip at .9 V at 2 seconds However, the applicable Facility is a solar installation not typically utilized as a firm resource. The Planning Coordinator, Transmission Owner, and Transmission Operator plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that RHIII experienced a loss of its solar installation, system reliability would not be compromised. No harm is known to occur. WECC considered the RHIII's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, RHIII: 1) updated the settings to become compliant with PRC-024-2 R2; and 2) revised its standard EPC contracts to address communication between the EPC, inverter manufacturer and Project NERC compliance team to ensure compliance at the commissioning stage of a facility in the future. The contract updates include: adding milestones to the EPC schedule, NERC consultant signature requirements on inverter commissioning efforts, and re-verifying settings after the site goes into commercial operation.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Red Horse Wind 2, LLC (RHWII) | NCR11578 | WECC2017017191 | PRC-024-2 | R1 | On March 1, 2017, RHWII submitted a Self- Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. Specifically, RHWII did not set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion caused by a system event that remains within the "no trip zone" of PRC-024. WECC reviewed the self-certification and determined that RHWII did not set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion caused by a system event that remains within the "no trip zone" of PRC-024. The root cause of the issue was RHIII did not ensure coordination between its Project NERC Compliance team, Engineering Procurement and Construction (EPC) contractor, and inverter manufacturer, to ensure PRC-024-2 compliance at the time of commissioning. WECC determined that this issue began on began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for RHIII’s applicable combined solar and wind installation. WECC determined that the end date of this issue is June 29, 2017 when the inverter settings were updated for a total of 364 days of noncompliance. | WECC determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). In this instance, RHWII failed to set its frequency protective relaying such that it would not trip its applicable generating unit unnecessarily. Such failure could result in the premature trip of RHWII’s generating unit, causing it to go offline due to frequency excursions within the “no trip zone.” RHWII had one inverter with both over and under frequency setting changes required as it was set to trip at 60.5 Hz and 57 Hz at .1 seconds. However, the applicable Facility is a combined wind and solar generation plant consisting of 55 MW solar and 30 MW wind not typically utilized as a firm resource. The Planning Coordinator, Transmission Owner, and Transmission Operator plan operate the grid with the expectation that solar and wind generation may be unavailable at any given time, so in the unlikely event that RHIII experienced a loss of its solar installation, system reliability would not be compromised. No harm is known to occur. WECC considered the RHWII's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, RHWII: 1) updated the settings to become compliant with PRC-024-2 R1; and 2) revised its standard EPC contracts to address communication between the EPC, inverter manufacturer and Project NERC compliance team to ensure compliance at the commissioning stage of a facility in the future. The contract updates include: adding milestones to the EPC schedule; NERC consultant signature requirements on inverter commissioning efforts; and re-verifying settings after the site goes into commercial operation.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Seattle City Light (SCL) | NCR05382 | WECC2017017443 | FAC-008-3 | R6 | On April 17, 2017, SCL submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with FAC-008-3 R6. Specifically, SCL reported that Facility Ratings for its two Blackstart Resources were not developed consistently with the SCL Generation Facility Ratings Methodology Rev 4 (Methodology). In preparation for the new Bulk Electric System (BES) definition, SCL began including the Blackstart Resources within its Facility Rating's program on June 27, 2014. At the time, SCL included two hydroelectric turbine-generators as Blackstart Resources, as indicated in the Facility Ratings Tables dated June 27, 2014, (Tables). Previously these units had not been included in SCL’s Facility Ratings because of their isolation from the BES and their very small size of 1.5 MVA each. On March 3, 2017, SCL discovered that the Facility Ratings for the Blackstart Resources were not developed consistent with the Methodology utilized for rating BES resources. SCL used the nameplate rating of the two-hydroelectric turbine-generators rather than the more limiting step-down transformer ratings. After reviewing all the relevant information, WECC determined that SCL failed to have Facility Ratings for its solely and jointly owned Facilities that were consistent with the associated Facility Ratings Methodology or documentation for determining its Facility Ratings, per FAC-008-3 R6. The root cause of the noncompliance was an incomplete understanding of how SLC should have applied its Facility Rating process to its Blackstart resources. WECC determined that this issue began on July 1, 2016, when the new BES definition went into effect for the Blackstart generators, and ended on March 9, 2017, when SCL updated its Facility Ratings Tables to included revised Facility Ratings of the Blackstart Resources consistent with the Methodology Revision 5, for a total of 251 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SCL failed to have Facility Ratings for its solely and jointly owned Facilities that were consistent with the associated Facility Ratings Methodology or documentation for determining its Facility Ratings relating to its Blackstart Resources. Such failure could increase the potential for the Blackstart generators to be operated in excess of the facilities most limiting element, thereby creating the opportunity for equipment damage and failure to provide Blackstart operations. However, an incorrect rating would not impact the units' ability to provide station service as it is only .25 MW during start-up, which is less than the most limiting elements, the step-down transformer’s ratings of 1.0 MW each. Additionally, SCL had implemented an ongoing review and update to the Methodology and Tables for Facility Ratings. Based on this, WECC determined that the potential harm had a remote likelihood of occurring. No harm is known to have occurred. WECC notes that SCL does not have any relevant previous violations of this or similar Standards and Requirements | To mitigate this noncompliance SCL: 1) updated its Facility Ratings Tables to included revised Facility Ratings of the Blackstart Resources consistent with the Methodology Revision 5; 2) developed a process that ensures BES element changes are incorporated throughout its entire compliance program. The process will prevent future recurrence and provide direction on making program changes through to completion; and 3) provided training to all applicable departments on the new process developed. The training included the newly developed process; the specifics of the Self-Report for FAC-008-3 R6, and how it is impacted by Element changes, such as the ones that occurred with the BES definition changed.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Solar Star California XIII, LLC (SXIII) | NCR11549 | WECC2017018357 | PRC-005-6 | R3 | On September 16, 2017, SXIII submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC 005-6 R3. Specifically, SXIII reported that it failed to meet the 18-month maintenance requirement for its battery terminal and intercell resistance testing in accordance with the minimum maintenance activities and maximum maintenance interval prescribed within Table 1-4(a). Specifically, the third-party contractor indicated that it completed work, but failed to notify SXIII that it did not perform all the required testing for "Battery terminal connection resistance" and "Battery intercell or unit-to-unit connection resistance." Additionally, the third-party contractor did not attempt to schedule this testing in the future. After reviewing all the relevant information, WECC determined that SXIII failed to meet the 18-month interval for "Battery terminal connection resistance" and "Battery intercell or unit-to-unit connection resistance" tests prescribed within Table 1-4(a). The root cause of the noncompliance was SXIII’s failure to verify that all work was completed by a third-party contractor at the end of the scheduled maintenance and testing. WECC determined that this issue began on May 31, 2017, the 19th month after SXIII failed to conduct "Battery terminal connection resistance" and "Battery intercell or unit-to-unit connection resistance" tests. WECC determined that the issue ended on June 30, 2017, when SXIII completed the "Battery terminal connection resistance" and "Battery intercell connection resistance" tests for a total of 31 days of noncompliance. | WECC determined this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SXIII failed to maintain its protection system in accordance with the minimum maintenance activities and maximum maintenance interval prescribed within Table 1-4(a), “Battery terminal connection resistance” and “Battery intercell or unit-to-unit connection” resistance tests. SXIII owns and operates a Solar PV Installation with a gross nameplate rating of 108 MVA that is directly connected to the BPS at 230 kV. The 125 Volt DC System supplies operational power to SCADA, protective relays, metering and control circuits. Such failure could result in battery degradation, which could cause the misoperation of associated Protection Systems devices because the batteries are providing power to these devices. Loss of situational awareness could also occur as loss of DC power could lead to SCADA outages. In the event of a fault, if the DC supply was compromised, and the batteries were not tested for operations, the Protection System might not operate to isolate the fault, leading to a cascading outage on the 230 kV system. However, SXIII discovered the noncompliance quickly. The batteries are alarmed and constantly monitored by a 24/7 control center. All the battery alarms are treated as “high priority” and most require a technician to be dispatched to the substation when an alarm is activated. SXIII requires other tests on a weekly and quarterly basis that ensure there are not battery connectivity issues. With a capacity of 107.6 MW, the solar installation represents less than 0.04% of the net generation capacity on the Western Interconnection. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that SXIII does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, SXIII: a. completed testing for "Battery terminal connection resistance" and "Battery intercell connection resistance" to meet requirements according to Table 1-4(a); b. created an exit briefing attestation to be completed by all third-party contractors. The attestation will include the completed work, unexpected results, incomplete action items, open maintenance and/or testing issues prior to the contractor leaving the site; c. instituted a new preventative control in MetricStream, a governance risk compliance software tool used by SXIII. This system will deliver automatic notifications every 6 months, informing responsible personnel of maintenance deadlines due in the next 12 months. Responsible personnel will send notifications to responsible parties to complete the tasks before the due date; d. created color coded identifiers using the Protection System Maintenance Program (PSMP) to identify upcoming due dates. The Plant Managers or Lead PV site technicians will maintain the PSMP. Evidence of completion will be provided to Operational Compliance quarterly, as the MetricStream tests are scheduled, and Plant Managers or Lead PV site technicians will be responsible for reporting; and e. included the last date that the annual maintenance was performed on the front of the report form used for all battery inspections and testing.
2018-07-31 | Western Electricity Coordinating Council (WECC) | Tucson Electric Power (TEPC) | NCR05434 | WECC2017017958 | EOP-005-2 | R17, R17.1 and 17.2 | On July 12, 2017, TEPC submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with EOP-005-2 R17. TEPC reported that it failed to provide a minimum of two hours of training, per EOP-005-2 R17 on procedures documented under EOP-005-2 R14, every two calendar years for one Generation System Control Operator responsible for the startup of its Blackstart resource units and energizing a bus. The procedure specific to EOP-005-2 R14 for the Operator is TEPC's Black Start Guidelines Procedure. After reviewing all the relevant information, WECC determined that TEPC failed to provide a minimum of two hours of mandatory training every two calendar years for one of its operating personnel responsible for the startup of its Blackstart resource generation units. The root cause of the noncompliance was TEPC’s failure to implement processes and procedures to accurately track Blackstart training for its operating personnel that require two hours of training per every two calendar years. WECC determined that this issue began on January 1, 2017, when it failed to provide a minimum of two hours of mandatory training every two calendar years for one of its operating personnel responsible for the startup of its Blackstart resource generation units. WECC determined that the end date of this issue was July 6, 2017 when the System Operator was provided training, for a total of 185 days of noncompliance. | WECC determined that this noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, TEPC failed to provide a minimum of two hours of mandatory training every two calendar years for one Generation System Control Operator responsible for the startup of its Blackstart resource units and energizing a bus. Such failure could potentially result in a delay in the re-energization of TEPC's system as the operator re-familiarized themselves with the Blackstart procedure. However, TEPC's training records show that the Operator attended Restoration training on October 28, 2014 and there were no material changes to the Procedure from the time when the Operator took the training in 2014 to the time the subsequent training was conducted in 2017. Additionally, the Operator routinely starts the TEPC Blackstart units for reliability purposes. There are only minor differences in starting the Blackstart units in a Blackstart scenario versus routine operation of the black start units. The operator in question is one of 14 that may be tasked with Blackstart operations. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that TEPC does not have any relevant previous violations of this or similar Standards and Requirements. | To remediate and mitigate this issue, TEPC: 1.) provided System Operator with the required training; 2.) update its training program to include a Trainers Checklist as an appendix to track the training requirements; 3.) created an automatic quarterly notification utilizing their Service Now workflow management system to alert the trainer to review and update the Trainers Checklist with the status of operator training; and 4.)update its training program to include Blackstart guideline procedures annually with TEPC’s restoration training. WECC verified the completion of identified mitigation activities
2018-07-31 | Western Electricity Coordinating Council (WECC) | Tucson Electric Power (TEPC) | NCR05434 | WECC2016016512 | MOD-025-2 | R2 | On November 11, 2016, TEPC submitted a Self-Report stating that, as a Generation Owner, it was in noncompliance with MOD-025-2 R2.1. TEPC reported that it failed to verify the Reactive Power Capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. TEPC does not own any synchronous condensers. 1. Specifically, prior to the enforceable date of MOD-025-2, TEPC was in compliance with the WECC Generator Testing and Validation Policy (WGTVP), received guidance from a WECC presentation, and subsequent confirmation, which stated that the WGTVP was more rigorous than the new Standard; therefore, it believed it was in compliance with the Standard. In August 2016, TEPC became aware that the WGTVP did not demonstrate compliance with MOD-025-2 R2.1. TEPC then reviewed its existing data and discovered that it could not demonstrate compliance with the Standard. Attachment 2.1.1 requires holding generator load for at least one hour to test the capability of VAR output, however, minimum and maximum VAR capability had previously been tested for only a few minutes. After reviewing all the relevant information, WECC determined that TEPC failed to verify the Reactive Power capability of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard as required by the implementation plan. The root cause of the noncompliance was due to TEPC incorrectly identifying the requirements of the MOD-025-2 R2.1. WECC determined that this issue began on July 1, 2016, when the Standard and Requirement became mandatory and enforceable for 40 percent of TEPC’s generating units, and ended on March 1, 2017, when TEPC tested three of its seven generators, for a total of 243 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, TEPC failed to verify the Reactive Power capability of at least 40% of its applicable Facilities in accordance with Attachment 1 of the Standard as required by the implementation plan. Such failure could potentially result in inaccurate information of generator gross and net Reactive Power capability used in planning models used to assess BES Reliability. However, this issue would not likely have significantly affected current planning models as TEPC tested its units in accordance with the WECC Generator Testing and Validation Policy prior to the effective date of MOD-025-2. The capacity of the units in scope is approximately 1446 MVA and TEPC verified one 472 MVA unit by the enforcement date of the Standard. Based on this, WECC determined that the potential harm had a low likelihood of occurring. No harm is known to have occurred. WECC notes that TEPC does not have any relevant previous violations of this or similar Standards and Requirements. | To mitigate this issue, TEPC: 1) completed testing of 40 percent of its applicable Facilities; 2) scheduled generating testing for all remaining applicable units for compliance with MOD-025-2 rather than with the WECC Generating Unit Model Validation certification; and 3) implemented ServiceNow as a compliance tracking tool to track reliability compliance deadlines. Future testing date reminders have been added to ServiceNow to ensure future testing deadlines are met.
2018-06-28 | Midwest Reliability Organization (MRO) | Lincoln Electric System (LES) | NCR01001 | MRO2018019518 | TOP-002-4 | R1 | On April 9, 2018, LES submitted a self-log stating that, as a Transmission Operator, it was in noncompliance with TOP-002-4 R1. Specifically, LES did not perform an Operational Planning Analysis (OPA) for Thursday, October 12, 2017 to assess whether its planned operations within its TOP area would exceed any of its System Operating Limits (SOLs). OPAs are performed on a rotating basis by four engineers. The noncompliance was caused by a staff absence and a sub-optimal internal control, a shared calendar, that did not provide daily individual notifications to the engineer responsible for performing the OPA. The noncompliance started on October 11, 2017, when LES did not have a next-day study for October 12, 2017, and ended on October 12, 2017, when LES had a next-day study for October 13, 2017. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LES has real-time contingency analysis capability available to its system operators, which has tools related to identifying future potential post-contingent transmission issues or SOL exceedances. Additionally, LES' Reliability Coordinator utilizes market management tools that provide additional capability to monitor and control system conditions, further reducing the impact of a single missed OPA. Further, LES rarely identifies potential SOL exceedances in its OPAs. Finally, there are no IROLs associated with LES' system. LES conducted an after-the-fact OPA for October 12, 2017 that demonstrated that the system conditions were similar to the previous day. No harm is known to have occurred. | To mitigate this noncompliance, LES: 1) performed the next-day study for October 13, 2017; and 2) retired the shared calendar, replacing it with a re-occurring event on each of the applicable engineer's calendars, with an event reminder displayed on the applicable engineer's computer and synced with any applicable mobile device.
2018-06-28 | Midwest Reliability Organization (MRO) | Lindahl Wind Project, LLC (LIND) | NCR11699 | MRO2017018313 | VAR-002-4 | R1 | On July 24, 2017, LIND submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with VAR-002-4 R1. Specifically, LIND did not operate each generator in the automatic voltage control mode or inform its Transmission Operator (TOP) that the generator is not being operated in automatic voltage control mode. On July 10, 2017, LIND's TOP requested that voltage at LIND's generating facility be raised. LIND attempted to modify the voltage set point through its central control room SCADA system, only to discover that the voltage controller was not active in the local SCADA system at the generating facility. The control room operator initiated an investigation with the local operations group at the generating facility. Per LIND, it discovered that the voltage controller had been disabled since June 30, 2017, after restoration of the facility following an event. LIND determined that the local SCADA was not correctly updating the control room, therefore no alarms were provided and the control room believed the voltage controller was enabled. The noncompliance was caused by inadequate training regarding LIND procedures that were designed to prevent or detect this noncompliance. As a preventative measure, LIND had a status check related to checking the voltage controller prior to restoration from an outage that was not completed by staff. As a detective measure, LIND also has a documented procedure applicable to the central control room to check the voltage control status in the central and local SCADA system that was not completed by control room staff. The noncompliance began on June 30, 2017, when the generator stopped being operated in automatic voltage control mode, and ended on July 10, 2017, when LIND informed its TOP that the generator stopped operating in automatic voltage control mode. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Wind generation facilities have limited voltage control capabilities compared to conventional dispatchable generation, and are not relied upon for voltage regulation by TOPs. Additionally, the generating facility's small size (150 MW) could only have a minor impact on the BPS's ability to respond to reactive power demands. No harm is known to have occurred. LIND has no relevant history of noncompliance. | To mitigate this noncompliance, LIND: 1) informed its TOP of the issue, then re-enabled the voltage controller later that day; 2) created a redundant DNP communication path direct from the Real-Time Automation Controller to the Network Manager for local SCADA indications; 3) updated the existing daily, weekly, and monthly checks to include voltage control status checks; 4) integrated the updated periodic and start up voltage control status check procedures into existing procedures; and 5) trained local and control room personnel on the updated "Start Up and Shut Down" procedure and updated voltage control status checks.
2018-06-28 | Midwest Reliability Organization (MRO) | Lindahl Wind Project, LLC (LIND) | NCR11699 | MRO2017018314 | VAR-002-4 | R2 | On July 24, 2017, LIND submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with VAR-002-4 R2. Specifically, LIND failed to utilize an alternative method to meet the voltage schedule provided by LIND's Transmission Operator (TOP). On July 10, 2017, LIND's TOP requested that voltage at LIND's generating facility be raised. LIND attempted to modify the voltage set point through its central control room SCADA system, only to discover that the voltage controller was not active in the local SCADA system at the generating facility. The control room operator initiated an investigation with the local operations group at the generating facility. Per LIND, it discovered that the voltage controller had been disabled since June 30, 2017 after restoration of the facility following an event. LIND determined that the local SCADA was not correctly updating the control room, therefore no alarms were provided and the control room believed the voltage controller was enabled. The noncompliance was caused by inadequate training regarding LIND procedures that were designed to prevent or detect this noncompliance. As a preventative measure, LIND had a status check related to checking the voltage controller prior to restoration from an outage that was not completed by staff. As a detective measure, LIND also has a documented procedure applicable to the central control room to check the voltage control status in the central and local SCADA system that was not completed by control room staff. The noncompliance began on June 30, 2017, when the generator stopped being operated in automatic voltage control mode, and ended on July 10, 2017, when LIND began utilizing an alternative method to meet the voltage schedule. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Wind generation facilities have limited voltage control capabilities compared to conventional dispatchable generation, and are not relied upon for voltage regulation by TOPs. Additionally, the generating facility's small size (150 MW) could only have a minor impact on the BPS's ability to respond to reactive power demands. No harm is known to have occurred. LIND has no relevant history of noncompliance. | To mitigate this noncompliance, LIND: 1) informed its TOP of the issue, then re-enabled the voltage controller later that day; 2) created a redundant DNP communication path direct from the Real-Time Automation Controller to the Network Manager for local SCADA indications; 3) updated the existing daily, weekly, and monthly checks to include voltage control status checks; 4) integrated the updated periodic and start up voltage control status check procedures into existing procedures; and 5) trained local and control room personnel on the updated "Start Up and Shut Down" procedure and updated voltage control status checks.
2018-06-28 | Midwest Reliability Organization (MRO) | Lindahl Wind Project, LLC (LIND) | NCR11699 | MRO2017018315 | VAR-002-4 | R3 | On July 24, 2017, LIND submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with VAR-002-4 R3. Specifically, LIND did not inform its Transmission Operator (TOP) of the change in the generator's automatic voltage regulator (AVR) within 30 minutes. On July 10, 2017, LIND's TOP requested that voltage at LIND's generating facility be raised. LIND attempted to modify the voltage set point through its central control room SCADA system, only to discover that the voltage controller was not active in the local SCADA system at the generating facility. The control room operator initiated an investigation with the local operations group at the generating facility. Per LIND, it discovered that the voltage controller had been disabled since June 30, 2017 after restoration of the facility following an event. LIND determined that the local SCADA was not correctly updating the control room, therefore no alarms were provided and the control room believed the voltage controller was enabled. The noncompliance was caused by inadequate training regarding LIND procedures that were designed to prevent or detect this noncompliance. As a preventative measure, LIND had a status check related to checking the voltage controller prior to restoration from an outage that was not completed by staff. As a detective measure, LIND also has a documented procedure applicable to the central control room to check the voltage control status in the central and local SCADA system that was not completed by control room staff. The noncompliance began on June 30, 2017, when the generator stopped being operated in automatic voltage control mode, and ended on July 10, 2017, when LIND informed its TOP of the change to its AVR. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Wind generation facilities have limited voltage control capabilities compared to conventional dispatchable generation, and are not relied upon for voltage regulation by TOPs. Additionally, the generating facility's small size (150 MW) could only have a minor impact on the BPS's ability to respond to reactive power demands. No harm is known to have occurred. LIND has no relevant history of noncompliance. | To mitigate this noncompliance, LIND: 1) informed its TOP of the issue, then re-enabled the voltage controller later that day; 2) created a redundant DNP communication path direct from the Real-Time Automation Controller to the Network Manager for local SCADA indications; 3) updated the existing daily, weekly, and monthly checks to include voltage control status checks; 4) integrated the updated periodic and start up voltage control status check procedures into existing procedures; and 5) trained local and control room personnel on the updated "Start Up and Shut Down" procedure and updated voltage control status checks.
2018-06-28 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC) | NCR00824 | MRO2018019520 | PRC-004-5(i) | R6 | On April 10, 2018, MEC submitted a self-log stating that, as a Generator Owner, it was in noncompliance with PRC-004-5(i) R6. MEC did not implement or update the Corrective Action Plan (CAP) for a wind farm substation collector bus Misoperation before the target completion date of December 31, 2017. MEC failed to update the CAP completion date to reflect the new timeline for a contractor review of switch contacts. The cause of the noncompliance was a lack of a review process to verify the status of CAPs with upcoming completion dates. The noncompliance began on January 1, 2018, when MEC failed to update the CAP prior to its scheduled completion, and ended on February 27, 2018, when MEC updated the CAP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance can be accurately regarded as a documentation issue, as the steps in the CAP allowing for the wind farm to return to service were completed. MEC conducted an extent of conditions review and determined that this was the only CAP that was not updated prior to the completion date, and the only CAP that was not updated when a target completion date changed. No harm is known to have occurred. | To mitigate this noncompliance, MEC: 1) updated the CAP target completion date via the NERC MIDAS Portal; and 2) added CAP target completion dates to its Legal Regulatory Information System to ensure notifications related to upcoming CAP due dates are provided to the relevant subject matter expert or compliance contact.
2018-06-28 | Midwest Reliability Organization (MRO) | Minnesota Power (Allete, Inc.) (MP) | NCR00674 | MRO2017016772 | PRC-005-1.1b | R2 | On November 30, 2016, MP submitted a Self-Report stating that, as a Distribution Provider, Generator Owner, and Transmission Owner, it was in noncompliance with PRC-005-1.1b R2. In the Self-Report, MP identified four instances of noncompliance related to failures to perform battery maintenance activities per the interval required by its Protection System Maintenance Program (PSMP). Three of the instances related to issues at customer owned 115 kV or 138 kV substations. MP took over compliance responsibility for customer-owned assets on October 8, 2014. In the first instance, on July 13, 2016, MP discovered lapses in maintenance and testing activities associated with two customer-owned substations. Specifically, MP was unaware that these customer owned substations each had a second battery (all references to "battery" is a reference to a bank of six-volt batteries) feeding the bus-differential relay. MP conducted an extent of conditions analysis to identify batteries that were not captured in MP's asset and maintenance management software tool. That analysis discovered a second and third instance of noncompliance at customer-owned substations. The second instance of noncompliance involved MP performing maintenance and testing on the wrong battery at a customer owned 115 kV substation after the customer gave MP incorrect information regarding the battery's location. The third instance of noncompliance involved MP not being able to produce sufficient maintenance and testing records for two batteries at a customer owner substation. The fourth instance of noncompliance involved a configuration issue with MP's asset and maintenance management software that it utilized to track battery maintenance. MP's asset and maintenance management software was incorrectly configured to track batteries that were on a four month testing interval. The tool only required that testing occur once in each four month interval, not that testing occur every four months, allowing up to seven months to elapse between testing. (i.e. the tool would allow a battery to be tested in January and in August). An extent of condition analysis demonstrated that while the four-month interval had been successfully maintained more often than not, the four-month interval had been missed a total of 69 times, affecting a total of 37 batteries. There were unique causes for the four instances of noncompliance. The first instance of noncompliance was caused by poor-quality and outdated drawings that resulted in MP not being aware of the second set of batteries feeding the bus-differential relays, which would have been subject to the Standard and Requirement. The second instance of noncompliance was caused by incorrect information from the customer's plant electrician regarding the location of the battery. The third instance of noncompliance was caused by MP's failure to implement its procedures and add the batteries to its PSMP when it took over compliance responsibility of the customer owned substation. The fourth instance of noncompliance was caused by an incorrect configuration in its asset and maintenance management tool that maintained a fixed state (allowing testing to occur at any point in each four-month cycle) as opposed to resetting the four month cycle when a test was completed. The noncompliance began on October 8, 2014, when MP assumed compliance responsibilities for the customer owned substations, and ended on October 13, 2016, when all required testing had been completed. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Regarding instances one through three, the scope of the noncompliance related to untracked batteries is relatively small. A comprehensive review only identified a total of five batteries at four substations that were not tracked in its asset management system. Additionally, these batteries support protection of the customer owned substations that are operated at 138 kV or 115 kV. The loss of these substations would have a limited potential impact on the BPS; a study of delayed remote clearing confirmed that a loss of these customer owned substations would not affect the BPS, and would only affect the customer's industrial operations. Regarding instance number four, the noncompliance related to 37 batteries with a four-month testing interval. MP identified 69 total instances where the four-month testing interval was missed, but did not go past seven months. Subsequent re-inspections established there were no required maintenance activities. Additionally, 26 of the 37 batteries were monitored by a heart beat alarm that would have notified system operators. Further, utility technicians check electrolyte levels during monthly substation inspections, meaning that the only maintenance activity that was not completed within the four month interval for these 26 batters was the inspection for unintentional grounds. Regarding the remaining 11 batteries, seven were at customer owned facilities and could have only caused loss of customer load. The remaining four batteries were located at a substation that was part of a 138 kV loop. Planning studies identified no adverse effect on the BPS related to the loss of that substation as the impact would be limited to a single 138 kV line. No harm is known to have occurred. MRO determined that MP's compliance history should not serve as a basis for applying a penalty. MP's prior compliance history includes a moderate risk violation of PRC-005-1 R2 (MRO2012011503) that was discovered in a 2012 audit. Comparing the current noncompliance and the prior noncompliance, it is reasonable to conclude that the current noncompliance was not caused by the failure to mitigate the prior noncompliance. Additionally, the scope of the current noncompliance is limited, and was caused by unique challenges in performing maintenance on assets owned by third parties and configuration settings in MP's asset and maintenance management system. Further, MP self-detected the noncompliance and displayed a commitment to reliability by conducting an extent of conditions analysis to uncover similar issues in its PSMP. | To mitigate this noncompliance, MP: 1) performed all required maintenance and testing; 2) cutover customer-owned batteries at the substations identified in instance number one to MP batteries; 3) conducted a comprehensive review to identify any batteries that were not included in its asset management system; 4) added the five batteries to its asset management tool and PSMP; 5) placed labels on all batteries in the PSMP program subject to the NERC Reliability Standards to ensure testing on the correct batteries; 6) reconfigured the asset and maintenance management system to, at the beginning of every month, provide technicians with a list of batteries that must be tested by the end of the month; and 7) reconfigured the asset and maintenance management system testing cycle in its asset management tool to enable a strict enforcement of the four month interval.
2018-06-28 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2018018969 | MOD-025-2 | R1 | On January 10, 2018, NSP, a Coordinated Oversight Program participant, submitted a self-log to MRO stating that, as a Generator Owner, it was in noncompliance with MOD-02502 R1. NSP, Public Service Company of Colorado (PSCO) (NCR05521), and Southwestern Public Service Company (SPS) (NCR01145) (hereafter referred to collectively as Xcel Energy) are Xcel Energy companies monitored together under the Coordinated Oversight Program. Xcel Energy stated that the noncompliance occurred in the PSCO operating area. Xcel Energy stated that it had deficiencies in the custom forms used by its Generation Department to communicate to the Xcel Energy business unit responsible for performing the Transmission Planner (TP) function. The custom reporting form omitted Scheduled Voltage, Transformer Voltage Ratio, Transmission Tap Settings, and the value of gross Reactive Power. This information is listed in Attachment 2 and is required to be included by R1.2. The cause of the noncompliance was a lack of diligence in creating the custom reporting form and this information was inadvertently omitted from the custom reporting form. This noncompliance started on July 1, 2016, the Standard and Requirement's first phased implementation date, and ended on November 15, 2017, when the missing data was submitted to the TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PSCO is a vertically integrated utility performing both the GO and TP functions; it is reasonable to assume that a vertically integrated TP has access to generator capability information outside the formal MOD-025-2 R1 submittal process. Further, Xcel Energy was not operating in an invalid modeled state, as per Xcel Energy, the missing data did not impact any Real or Reactive Power calculations for the TP, nor did it result in any changes to the TP's planning models. No harm is known to have occurred. Xcel Energy has no relevant history of noncompliance for MOD-025-2 R1. | To mitigate this noncompliance, Xcel Energy: 1) supplied the missing data to the TP; 2) PSCO began utilizing a contractor to perform MOD-025-2 testing, and while the contractor has its own MOD-025-2 form, PSCO confirmed that the contractor's form contains all information required by Attachment 2; 3) SPS reviewed its custom reporting form for MOD-025-2; and 4) NSP continues to use the Attachment 2 form that is attached to MOD-025-2.
2018-06-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Astoria Energy, LLC | NCR00538 | NPCC2018019626 | PRC-024-2 | R1. | On May 3, 2018, Astoria Energy, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 [Requirement R1.]. Specifically, the Entity failed to implement relay settings that would ensure that its generator frequency protective relaying does not trip its applicable generating facilities within the "No Trip zone" of PRC-024-2 Attachment 1. Per the phased-in Implementation Plan of the Standard and Requirement, implementation of appropriate frequency relay settings for the Entity's two out of its three generating assets was required by 7/1/2017. This noncompliance started on July 1, 2017, when Phase II of the Implementation Plan for the standard and requirement became enforceable, and ended on April 17, 2018, when the Entity implemented new settings for Over-Frequency relays (Device 81O) that would not trip its applicable generating facilities within the "No Trip zone" of PRC-024-2 Attachment 1. The root cause of this instance of noncompliance was the Entity's misinterpretation of the Implementation Plan of the Standard. The Entity incorrectly assumed that the phased-in Implementation Plan was based on the number of compliant voltage protective relays installed and activated on its generating Facilities instead of the number of applicable generating Facilities owned by the Entity. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity owns three generating units, two Gas Turbines, or GTs (GTC101 & GTC201), and one steam unit (STG001) that are operated as a single Combined Cycle (CC) plant interconnected at a 138 kV substation owned by its host TO. Phase II of the implementation plan of the Standard and Requirement required the Entity to rectify frequency settings on two of its three units by July 1, 2017. The noncompliance consisted of incorrect settings for each of its two GTs' Secondary protection packages (two relays in all) and for its Steam Unit's Primary and Secondary protection packages (another two relays in all) that were erroneously set to trip the units within the overfrequency portion of the "No Trip zone" of Attachment 1.The underfrequency aspect of those 4 relays were verified to be correct. It is noted, however, that both of the Primary protection packages on CT1 and CT2 were both verified correct for 81O and 81U. Additionally, the CC generating plant is rated at 570 MW and was operated at capacity factors of 65% and 63%, respectively in 2016 and 2017; the capacity factor in 2018 (to date) is approximately 68%. The rated capability of the CC plant is less than 30% of the Entity's Reliability Coordinator's (NYISO) required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire CC plant to trip unnecessarily during a system frequency event, the NYISO (the Entity)'s Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by implementing new settings for Over-Frequency relays (Device 81O) that would not trip its applicable generating facilities within the "No Trip zone" of PRC-024-2 Attachment 1; and 2. To prevent a recurrence of similar instances of noncompliance, provided training to responsible personnel in order to clarify the correct implementation of the standard and its requirement. NPCC has verified the completion of all mitigation activity.
2018-06-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Norwood Municipal Light Department | NCR00415 | NPCC2018019628 | PRC-005-6 | R3. | During a Compliance Off-site Audit conducted from December 11, 2017 through April 25, 2018, NPCC determined that Norwood Municipal Light Department (the Entity), as a Transmission Owner (TO), was in noncompliance with standard PRC-005-6 [Requirement R3.]. In accordance with the Implementation Plan of the standard/requirement, the Entity was required to complete certain specific tests for its VLA batteries by April 1, 2017. Instead, the Entity failed to perform on time those periodic maintenance items for VLA batteries that have a time-based maximum interval of 18 calendar months, as specified in PRC-005-6 Table 1-4a. This noncompliance started on April 1, 2017, when the Entity was required to complete VLA battery tests with an 18-month periodicity, and ended on December 28, 2017, when the Entity actually completed all the aforementioned maintenance activities for its VLA batteries at its two BES Substations. The root cause of this instance of noncompliance was the Entity's misinterpretation of the standard's Implementation Plan with respect to VLA batteries testing. The Entity incorrectly assumed that the 18-calendar month maintenance/testing schedule of Table 1-4a was required to be implemented 18 months after the Entity's registration as a TO, which occurred on July 1, 2016. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Norwood Municipal Light Department is a public power utility that does not own/operate any generating facilities and only serves local commercial, industrial and residential load. The Entity's all-time peak load was approximately 80 MW in 2011. The Entity owns two 115kV substations from which it serves its customer load. These two substations are radially interconnected to the Entity's Transmission Operator (NSTAR) via two identically-rated, 3-mile spans of 115kV transmission feeders. Documentation provided to NPCC shows that the duration of the noncompliance was eight (8) months. However, except for minor repair activities, tests indicated that the batteries were in good operating condition. A potential loss of the Entity's customer load resulting from this instance of noncompliance would have been resolved by the Entity's Reliability Coordinator (ISO-NE) by reducing the power output of on-line generation. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by completing all the VLA battery tests with an 18-month periodicity at its two BES Substations; and 2. To prevent a recurrence of similar instances of noncompliance, decided to formally adopt a more conservative maintenance schedule interval for the aforementioned activities ranging from a minimum of 12 months to a maximum of 18 months. Additionally, to ensure adherence to the new schedule, the Entity implemented an internal control that utilizes the Google Calendar application to alert responsible staff of impending maintenance tasks for its VLA batteries. NPCC has verified the completion of all mitigation activity.
2018-06-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Norwood Municipal Light Department | NCR00415 | NPCC2018019627 | FAC-008-3 | R6. | During a Compliance Off-site Audit conducted from December 11, 2017 through April 25, 2018, NPCC determined that Norwood Municipal Light Department (the Entity), as a Transmission Owner (TO), was in noncompliance with standard FAC-008-3 [Requirement R6.]. More specifically, in some instances, inaccuracies due to rounding and/or transcription errors caused two of its 115kV transmission facilities' ratings to be incorrect and/or not respect the most limiting rating of individual pieces of equipment that comprise said facilities. This noncompliance started on July 1, 2016, the Entity's official registration date as a TO, and ended on March 27, 2018, when the Entity, in order to eliminate any inaccuracies and inconsistencies among rating values, ceased its practice of rounding numerical values and corrected its rating spreadsheets accordingly. The root cause of this instance of noncompliance was the Entity's practice of approximating numerical values of equipment ratings by rounding them to the nearest 5 amperes and, additionally, making occasional transcription errors that caused equipment ratings to not respect the most limiting element in a circuit. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Norwood Municipal Light Department is a public power utility that does not own/operate any generating facilities and only serves local commercial, industrial and residential load. The Entity owns two 115kV substations from which it serves its customer load. These two substations are radially interconnected to the Entity's Transmission Operator (NSTAR) via two identically-rated, 3-mile spans of 115kV transmission feeders. Documentation provided to NPCC shows that the noncompliance consists in artificially higher Summer and Winter Long Term Emergency (LTE) ratings for these two transmission facilities. This noncompliance would not have caused real-time loadings to exceed the two transmission facilities' true LTE ratings as the Entity's all time peak load (approximately 80MW, in 2011) is less than 20% of the combined true LTE Summer ratings of the two circuits (440 MVA), and less than 15% of the combined true LTE Winter ratings of the two circuits (552 MVA). No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by immediately ceasing its practice of rounding numerical values and rectifying its calculations accordingly in its rating spreadsheets; and 2. To prevent a recurrence of similar instances of noncompliance, the Entity inserted mathematical formulas in its rating spreadsheets to automatically recognize and display the correct rating values for its transmission facilities. This strategy eliminates occasional transcription errors and enforces the Entity's new policy of reporting all facilities' ratings to its Reliability Coordinator and Transmission Operator using single digit accuracy. NPCC has verified the completion of all mitigation activity.
2018-06-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Pinetree Power - Tamworth, Inc. | NCR10342 | NPCC2017018603 | PRC-024-2 | R2. | On November 13, 2017, Pinetree Power - Tamworth, Inc. (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 [Requirement R2.]. Specifically, the Entity failed to implement relay settings that would ensure that its generator voltage protective relaying does not trip its applicable generating facility within the "No Trip zone" of PRC-024-2 Attachment 2. Per the phased-in Implementation Plan of the Standard and Requirement, implementation of appropriate voltage relay settings for the Entity's single generating asset was required by 7/1/2016. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on May 18, 2018, when the Entity implemented new settings for one Over-Voltage relay (Device 59) that would not trip its applicable generating facility within the "No Trip zone" of PRC-024-2 Attachment 2. The root cause of this instance of noncompliance was the Entity's failure to enter PRC-024-2 implementation plan dates as work orders into its maintenance management system. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This noncompliance consisted of incorrect voltage protective relaying settings that would trip the Entity's single generating unit within the "No Trip zone" of Attachment 2. To achieve compliance, the Entity implemented changes to the tripping point of the aforementioned Over-Voltage relay, as summarized below: Non-compliant Setting (existing) Compliant Setting (implemented) 1.078V (at POI) @ 0.896 sec. 1.1V (at POI) @ 1.03 sec. The Entity owns a single wood-fired generating unit that has been operated at capacity factors of 70% and 87%, respectively in 2016 and 2017; the capacity factor in 2018 (to date) is approximately 70%. The rated capability of the generating unit (20 MW) is less than 0.8% of the Entity's Reliability Coordinator's (ISO-NE) required Operating Reserve (approximately 2600 MW). Therefore, if this instance of noncompliance had caused the entire generating unit to trip unnecessarily during a system voltage event, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by implementing new settings for one Over-Voltage relay (Device 59) that would not trip its applicable generating facilities within the "No Trip zone" of PRC-024-2 Attachment 2; and 2. To prevent a recurrence of similar instances of noncompliance, entered future NERC Reliability Standards required implementation dates as work orders into the plant’s maintenance management system ("Maximo"). NPCC has verified the completion of all mitigation activity.
2018-06-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Pinetree Power - Tamworth, Inc. | NCR10342 | NPCC2017018602 | PRC-024-2 | R1. | On November 13, 2017, Pinetree Power - Tamworth, Inc. (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 [Requirement R1.]. Specifically, the Entity failed to implement relay settings that would ensure that its generator frequency protective relaying does not trip its applicable generating facility within the "No Trip zone" of PRC-024-2 Attachment 1. Per the phased-in Implementation Plan of the Standard and Requirement, implementation of appropriate frequency relay settings for the Entity's single generating asset was required by 7/1/2016. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on May 2, 2018, when the Entity implemented new settings for one Over-Frequency relay (Device 81O) that would not trip its applicable generating facility within the "No Trip zone" of PRC-024-2 Attachment 1. The root cause of this instance of noncompliance was the Entity's failure to enter PRC-024-2 implementation plan dates as work orders into its maintenance management system. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This noncompliance consisted of incorrect frequency protective relaying settings that would trip the Entity's single generating unit within the "No Trip zone" of Attachment 1. To achieve compliance, the Entity implemented changes to the tripping point of the aforementioned Over-Frequency relay, as summarized below: Non-compliant Setting (existing) Compliant Setting (implemented) 61HZ @ 1 sec. 61.8HZ @ 1.03 sec The Entity owns a single wood-fired generating unit that has been operated at capacity factors of 70% and 87%, respectively in 2016 and 2017; the capacity factor in 2018 (to date) is approximately 70%. The rated capability of the generating unit (20 MW) is less than 0.8% of the Entity's Reliability Coordinator's (ISO-NE) required Operating Reserve (approximately 2600 MW). Therefore, if this instance of noncompliance had caused the entire generating unit to trip unnecessarily during a system frequency event, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by implementing new settings for one Over-Frequency relay (Device 81O) that would not trip its applicable generating facilities within the "No Trip zone" of PRC-024-2 Attachment 1; and 2. To prevent a recurrence of similar instances of noncompliance, entered future NERC Reliability Standards required implementation dates as work orders into the plant’s maintenance management system ("Maximo"). NPCC has verified the completion of all mitigation activity.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Commonwealth Chesapeake Company, LLC (Chesapeake) | NCR10229 | RFC2018019078 | PRC-019-2 | R1 | On January 19, 2018, Chesapeake submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Upon an internal review of relay settings for PRC-001 and in preparation for testing to meet compliance with the implementation timelines of MOD-026/MOD-027, the entity discovered that voltage regulating system controls at all seven facility units were not coordinated with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. Individual reports for each of the seven units detail the specific non-compliant settings: (a) V/Hz (24) setpoints and limiters currently in place are not adequately coordinated with generator and/or transformer capabilities during certain operating conditions. During these conditions, the associated generator and/or transformer is potentially unprotected or protected by relay setpoints beyond each unit's limitations; (b) Loss of field (40) setpoints are not fully coordinated with the Under-Excitation Limiters (UEL) throughout the entire load range. At certain low loads, which are not typically operated at, it would be possible for a loss of field (40) relay to trip the associated unit prior to reaching the UEL; and (c) Loss of field (40) setpoints are not properly coordinated with the steady state stability limits (SSSL) for each generator. There is potential, although very unlikely, that the generator could reach an out-of-step condition should the Automatic Voltage Regulator (AVR) have to be operated in manual and the UEL failed to activate. The entity contracted with a third-party contractor to perform its PRC-019-2 study. The entity received the final reports on June 30, 2016, for Units 4, 5, 6, 7 and on August 31, 2016 for units 1, 2, 3 from the contractor. The entity failed to address the conclusions and recommendations made in the reports because the entity did not fully understand the conclusions in the reports. Entity personnel did not understand the conclusions in the reports because they did not fully understand the requirements and implementation steps associated with PRC-019-2. Therefore, the entity did not act on the conclusions and recommendations made in the report until 2018. This noncompliance involves the management practices of validation and verification. Entity personnel did not validate that they understood the need to take action upon the recommendations made in the PRC-019-2 study conducted by the contractor. Additionally, entity personnel did not verify that they fully understood the requirements and implementation steps associated with PRC-019-2. That failure to understand what PRC-019-2 required is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-019-2 R1 and ended on March 12, 2018, when the entity completed its Mitigating Activities by making all required settings changes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because the entity’s plant voltage was within the voltage schedule for this area before, during, and after this event. The entity staying within its voltage schedule for the duration of the noncompliance reduces the risk of a possible discoordination of voltage control based on the existing settings at the entity. (The entity validated this through a review of PI data of the plant voltage during the relevant timeframe on December 1, 2017.) Lastly, the entity contributes approximately 315 MWs to the grid and operated at less than a 3% capacity factor during the noncompliance. The entity has a low 3% capacity factor because it is a peaking facility that operates when demand in PJM reaches a point that makes it economically viable for the entity to operate. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) obtained quotes to evaluate/make the required setting changes; 2) selected the vendor and made the required setting changes; and 3) obtained an updated study/report from the vendor showing compliant settings. ReliabilityFirst has verified the completion of all mitigation activity.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Commonwealth Chesapeake Company, LLC (Chesapeake) | NCR10229 | RFC2018019079 | PRC-024-2 | R1 | On January 19, 2018, Chesapeake submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. The entity completed an evaluation of voltage and frequency relay settings in accordance with PRC-024-2 on June 30, 2016. The evaluation revealed that all seven units at the entity had both frequency and voltage setpoints that did not meet the criteria of R1/R2 respectively. The setpoints that fell within the no-trip zone are Frequency Setpoints (R1) -- 2 of 4 for each generator (14 of 28). Following this evaluation, the entity reviewed associated unit limitations, and in accordance with PRC-024-2 R3, documented what the entity believed to be known equipment limitations that prevented the applicable generating units with generator frequency or voltage protective relays from meeting the relay setting criteria in R1/R2. The entity provided notification to PJM of these equipment limitations for the applicable generating units within 30 calendar days as required by PRC-024-2 R3. During a third party vendor’s recent review of the entity’s protection systems in preparation for MOD-026/27 testing, the vendor and the entity discovered that the justification used for the limitations under R3 were related to continuous voltage and frequency limits and do not apply to short duration events such as excursions outlined in PRC-024-2. Specifically, the entity determined that the perceived equipment limitations were not valid as the equipment limitations were for long-term voltage and frequency and voltage deviations, not the short time frames prescribed in R1 and R2 of PRC-024-2. As a result of this review, the entity learned that its existing equipment limitations did not prevent implementation of the required relay setting criteria. Following from this discovery, the entity hired a contractor to evaluate the entity’s settings and to determine if any settings changes would be required. The contractor determined that no settings changes were required as all of the entity’s seven units do meet the PRC-024 requirements. This noncompliance involves the management practice of verification. Entity personnel did not verify that its understanding of PRC-024-2 was correct which caused the entity to communicate an improper equipment limitation to PJM. The entity’s failure to verify that it fully understood PRC-024-2 and the applicable limitations of its own equipment is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R1 and ended on March 12, 2018, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because the entity identified no system events where any units were prematurely removed from service due to the voltage setpoints currently in place which indicates that the entity is not tripping incorrectly in response to system events. When the entity’s contractor performed the verification study, the contractor determined that no relay settings changes were required. Lastly, the entity contributes approximately 315 MWs to the grid and operated at less than a 3% capacity factor during the noncompliance. The entity has a low 3% capacity factor because it is a peaking facility that operates when demand in PJM reaches a point that makes it economically viable for the entity to operate. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) obtained quotes to evaluate/make required setting changes; 2) selected a vendor to make the required setting changes if any; and 3) obtained an updated study/report from the vendor showing compliant settings and submitted that information to PJM. In sum, the entity hired a contractor to evaluate the entity’s settings and to determine if any settings changes would be required. The contractor determined that no settings changes were required as the current settings for all of the entity’s seven units do meet the PRC-024 requirements. ReliabilityFirst has verified the completion of all mitigation activity.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Commonwealth Chesapeake Company, LLC (Chesapeake) | NCR10229 | RFC2018019080 | PRC-024-2 | R2 | On January 19, 2018, Chesapeake submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. The entity completed an evaluation of voltage and frequency relay settings in accordance with PRC-024-2 on June 30, 2016. The evaluation revealed that all seven units at the entity had both frequency and voltage setpoints that did not meet the criteria of R1/R2 respectively. The current setpoints that fall within the no-trip zone are Voltage Setpoints (R2) -- 1 of 3 for each generator (7 of 21). Following this evaluation, the entity reviewed associated unit limitations, and in accordance with PRC-024-2 R3, documented what the entity believed to be known equipment limitations that prevented the applicable generating units with generator frequency or voltage protective relays from meeting the relay setting criteria in R1/R2. The entity provided notification to PJM of these equipment limitations for the applicable generating units within 30 calendar days as required by PRC-024-2 R3. During a third party vendor’s recent review of the entity’s protection systems in preparation for MOD-026/27 testing, the vendor and the entity discovered that the justification used for the limitations under R3 were related to continuous voltage and frequency limits and do not apply to short duration events such as excursions outlined in PRC-024-2. Specifically, the entity determined that the perceived equipment limitations were not valid as the equipment limitations were for long-term voltage and frequency and voltage deviations, not the short time frames prescribed in R1 and R2 of PRC-024-2. As a result of this review, the entity learned that its existing equipment limitations did not prevent implementation of the required relay setting criteria. Following from this discovery, the entity hired a contractor to evaluate the entity’s settings and to determine if any settings changes would be required. The contractor determined that no settings changes were required as all of the entity’s seven units do meet the PRC-024 requirements. This noncompliance involves the management practice of verification. Entity personnel did not verify that its understanding of PRC-024-2 R3 was correct which caused the entity to communicate an improper equipment limitation to PJM. The entity’s failure to verify that it fully understood PRC-024-2 and the applicable limitations of its own equipment is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 2 and ended on March 12, 2018, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because the entity identified no system events where any units were prematurely removed from service due to the voltage setpoints currently in place which indicates that the entity is not tripping incorrectly in response to system events. When the entity performed the verification study in 2018, no relay settings changes were required. Lastly, the entity contributes approximately 315 MWs to the grid and operated at less than a 3% capacity factor during the noncompliance. The entity has a low 3% capacity factor because it is a peaking facility that operates when demand in PJM reaches a point that makes it economically viable for the entity to operate. No harm is known to have occurred. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) obtained quotes to evaluate/make required setting changes; 2) selected a vendor to make the required setting changes if any; and 3) obtained an updated study/report from the vendor showing compliant settings and submitted that information to PJM. In sum, the entity hired a contractor to evaluate the entity’s settings and to determine if any settings changes would be required. The contractor determined that no settings changes were required as the current settings for all of the entity’s seven units do meet the PRC-024 requirements. ReliabilityFirst has verified the completion of all mitigation activity.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Nuclear as agent for FirstEnergy Nuclear Generation, LLC; FirstEnergy Nuclear Operating Company (FE Nuclear) | NCR11316 | RFC2018019504 | PRC-005-6 | R3 | On March 29, 2018, FE Nuclear submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R3. The entity discovered an instance where a PRC-005-6 R3, Table 1-4(a), time-based maintenance interval was not met. The entity discovered this issue while doing a periodic update on scheduled completion dates of Maintenance Plans for PRC-005-6. Specifically, the entity missed an 18 calendar month interval for Station Vented Lead-Acid (VLA) battery maintenance by 7 days. Table 1-4(a) requires the entity to perform 6 activities on this Station VLA battery pursuant to an 18 calendar month interval. The entity timely completed four of the six activities. The two missed activities were battery terminal and intercell connection resistance testing. The entity conducted an investigation to determine why these two activities were not timely performed and discovered that the two activities at issue had been inadvertently left off the tracking list of Maintenance Plans needed to comply with PRC-005-6 for this Station VLA battery. The entity inadvertently leaving the two activities at issue off the tracking list is a direct cause of this noncompliance. The Maintenance Plan for each battery is supposed to list all specific activities that are required by PRC-005-6. The omission stemmed from an entity Project Management optimization study that changed Maintenance Plans from a 12-month to a 24-month frequency on non-safety batteries. Further investigation found the optimization study changed 3 Station VLA Maintenance Plans, including the one in question. The entity confirmed the other 2 Station VLA batteries were within their maintenance interval. The other 2 Station VLA batteries were not missed because their testing dates had not yet come due. The entity performed a comprehensive review on the remaining 11 Station VLA Maintenance Plans in the entity’s fleet and confirmed they were on a 12-month frequency and all batteries were within their maintenance intervals. This noncompliance involves the management practices of validation and verification. Validation and verification are involved because the entity did not validate and verify that all applicable maintenance activities remained in the Maintenance Plans after the Maintenance Plans were changed from a 12-month to a 24-month frequency. That failure to validate and verify is a root cause of this noncompliance. This noncompliance started on February 1, 2018, when the entity was required to have performed the battery terminal and intercell connection resistance testing on the one Station VLA battery and ended on February 8, 2018, when the entity completed the overdue testing. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that the failure to timely maintain and test Protection System devices could negatively affect the reliable operation of the BPS. The risk is minimized because only one out of the entity’s 14 VLA Station batteries were affected. The one VLA Station battery at issue was outside of its 18-month interval by just seven days. The entity also quickly identified, assessed, and corrected this issue due to a periodic update of scheduled completion dates for PRC-005-6 Maintenance Plans, which evidences strong detective and corrective controls. The VLA Station battery at issue was also only overdue on 2 out of the 6 required activities. When the entity tested for the two overdue activities on the VLA Station battery, the battery passed on both activities. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed the overdue maintenance and testing on the one VLA battery at issue; 2) updated Maintenance Plans of 3 Station VLA batteries from 24-months back to 12-months. This will ensure that the 18-month maximum maintenance interval is met in case of delays; and 3) added a warning statement to each Maintenance Plan that emphasized that these activities are NERC required activities and must be completed on time. (The Warning Statement reads "WARNING: Completion of this Maintenance Plan is necessary for compliance with NERC Standard PRC-005 Protection System, Automatic Reclosing, and Sudden Pressure Relaying. Maximum allowed time interval to perform this Maintenance Plan is 18 calendar months.") ReliabilityFirst has verified the completion of all mitigation activity.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Helix Ironwood LLC (Helix Ironwood) | NCR11749 | RFC2018018933 | PRC-019-2 | R1 | On December 21, 2017, Helix Ironwood submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. The entity was acquired by LS Power Equity Advisors LLC (“LS Power”) on June 2, 2017, from TransCanada Corporation (“TransCanada”). After the acquisition, LS Power performed a voluntary self-audit to determine the entity’s compliance with PRC-019-2 R1. During this self-audit, LS Power could not find the coordination study (that requires coordination of the voltage regulating system controls, (including in-service (Limiters or protection functions that are installed and activated on the generator or synchronous condenser.) limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions) required by PRC-019-2 R1. LS Power was able to find some documentation and a graph that would be a part of the completed coordination study, but could not find the completed coordination study. This noncompliance involves the management practices of external interdependencies, verification, and asset and configuration management. External interdependencies is involved because LS Power did not verify that TransCanada had all of the documentation in place to demonstrate compliance with PRC-019-2 R1 before LS Power purchased the entity. This is evidenced by the fact that LS Power was only able to find some documentation and a graph that would be part of the completed coordination study while performing a self-audit after the acquisition of the entity. LS Power’s failure to verify before the sale was completed that TransCanada would provide all of the relevant documentation for PRC-019-2 to LS Power is a root cause of this noncompliance. This noncompliance started on July 1, 2017, when the entity was required to comply with PRC-019-2 R1 and will end by July 31, 2018, when the entity completes its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because after taking ownership of the entity, LS Power conducted a thorough review of the entity’s PRC-019-2 R1 compliance and notified ReliabilityFirst of this noncompliance which evidences effective detective controls and a strong internal compliance program. The entity contributes approximately 660 MWs to the grid and operated at approximately a 92% capacity factor during the noncompliance. ReliabilityFirst also notes that the entity has not experienced any generator trips caused by incorrect coordination of the voltage regulating system control and protective systems. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity will complete the following mitigation activities by July 31, 2018: 1) has contracted with a firm to perform the required coordination study. Once the study results are available, the entity will determine if any relay settings need to be adjusted. If any adjustments are required, these relay settings changes will be implemented at the entity’s next planned outage. Currently, the entity has approval from its Balancing Authority to take an outage wherein it can make all required settings changes; 2) to prevent recurrence, the entity has created a NERC Preventive Maintenance task in its compliance management tool (Infor EAM) requiring a coordination study and any needed changes identified in that study per PRC-019; and 3) will also provide supplemental training to the plant personnel involved in the PRC-019 processes to ensure personnel are familiar with PRC-019 and its impacts. To complete the mitigation activities, Helix Ironwood must take an outage and Helix Ironwood's next scheduled outage is in the summer of 2018. That is why these mitigation activities will not be completed until July 31, 2018.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Helix Ironwood LLC (Helix Ironwood) | NCR11749 | RFC2018018934 | PRC-024-2 | R2 | On December 21, 2017, Helix Ironwood submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. The entity was acquired by LS Power Equity Advisors LLC (“LS Power”) on June 2, 2017 from TransCanada Corporation (“TransCanada”). After the acquisition, LS Power performed a voluntary self-audit to determine the entity’s compliance with PRC-024-2 R2. During this self-audit, LS Power discovered that the settings required by PRC-024-2 had not been implemented at the entity. The previous owner of the entity had studied the settings related to PRC-024-2 and documented in an internal memo dated August 11, 2016 that relay settings were not in compliance with PRC-024-2. (Specifically, Generator CTs and an ST and 230kv bus under voltage protection (element 27) were found in the no trip zone at 2 seconds and the proposed change was to 3 seconds.) Following this internal memo, the previous owner of the entity communicated the incorrect settings to the Balancing Authority (BA) on April 20, 2017 with a request that the BA and the Transmission Operator (TOP) approve the proposed settings change prior to the entity implementing the change. Approximately four months after LS Power’s acquisition of the entity on June 2, 2017, on November 3, 2017, the BA and TOP responded to the previous owner that the changes were acceptable. Entity employees under the new owner (LS Power), however, were only made aware of the BA and TOP approval on November 27, 2017 due to a lag in receiving information because of employees’ email address changes following the ownership change. The entity will make the required changes at its next planned outage (currently scheduled for May 4-13, 2018). This noncompliance involves the management practices of external interdependencies, asset and configuration management, and verification. External interdependencies is involved because LS Power did not verify that TransCanada had all of the documentation in place and had completed all of the steps necessary to demonstrate compliance with PRC-024-2 R2 before LS Power purchased the entity. LS Power’s failure to verify before the sale was completed that TransCanada would provide all of the relevant documentation for PRC-024-2 to LS Power and that TransCanada had completed all of the necessary steps to ensure compliance with PRC-024-2 is a root cause of this noncompliance. This noncompliance started on July 1, 2017, when the entity was required to comply with PRC-024-2 R2 and will end by July 31, 2018, when the entity completes its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because only one relay setting needs to be changed by 1% which reduces the risk of a generator incorrectly tripping due to an incorrect setting because only one relay setting was incorrectly set near the margin of the “no trip zone.” ReliabilityFirst also notes that after taking ownership of the entity, LS Power conducted a thorough review of the entity’s PRC-019-2 R1 compliance and notified ReliabilityFirst of this noncompliance which evidences effective detective controls and a strong internal compliance program. No harm is known to have occurred. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity will complete the following mitigation activities by July 31, 2018: 1) plans to take an outage and has approval from its BA/TOP to do so. The entity has contracted with a firm to perform the relay settings change during that outage. The entity is also discussing the change process with its contractor to determine if the settings change can be made earlier in the event the units come off for unplanned issues. The entity will make all required settings changes; and 2) to prevent recurrence, the entity will provide supplemental training to the plant personnel involved in the PRC-024 processes to ensure personnel are familiar with PRC-024 and its impacts. To complete the mitigation activities, Helix Ironwood must take an outage and Helix Ironwood's next scheduled outage is in the summer of 2018. That is why these mitigation activities will not be completed until July 31, 2018.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Raven FS Property Holdings LLC | NCR11308 | RFC2018019621 | PRC-005-6 | R3 | On December 31, 2017, Raven FS Property Holdings LLC submitted a self-log stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R3. R3 of PRC-005-6 requires performing the work stated in the Protection System Maintenance Program (PSMP). The entity could not produce evidence that showed it completed making battery positive terminal resistance verifications. Talen, the entity's holding company, discovered this during an annual review of its battery maintenance and testing records at the end of 2017. This noncompliance involves the management practices of verification and validation. Verification is involved because the entity did not verify that it had completed battery positive terminal resistance verifications. The entity did not have an effective validation and verification control in place to ensure the tests were performed and that lack of a control is a root cause of this noncompliance. This noncompliance started on April 1, 2017, when the entity was required to comply with PRC-005-6 R3 and ended on November 27, 2017, when the entity completed performing the connection resistance measurements. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). It was determined that this issue posed a minimal risk to the BPS because the batteries were maintained according to all the PRC-005 requirements with the exception of the positive terminal resistance. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) performed annual battery checks, including terminal connection resistance measurements; 2) implemented a new organizational electronic data filing system that will help minimize the potential for this noncompliance to recur; and 3) adopted the use of fleet wide battery forms that are more prescriptive and will be used both by contractors and plant staff.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Raven FS Property Holdings LLC | NCR11308 | RFC2018019622 | PRC-005-1b | R2 | On December 31, 2017, Raven FS Property Holdings LLC submitted a self-log stating that, as a Generator Owner, it was in noncompliance with PRC-005-1b R2. R3 of PRC-005-1 requires performing the work stated in the Protection System Maintenance Program (PSMP). The entity tested the Potential Transformers (PT) Signals before 2015 but could not provide evidence that the PT Signals were tested before 2015. The entity can only document the testing of the PT Signals in 2015. This noncompliance involves the management practices of verification and validation. Verification is involved because the entity did not verify that it had completed battery positive terminal resistance verifications. The entity did not have an effective validation and verification control in place to ensure the tests were performed and that lack of a control is a root cause of this noncompliance. This noncompliance started on January 15, 2013, when the entity was required to comply with PRC-005-1b R2, and ended on March 17, 2015, when the entity completed performing the overdue connection resistance measurements. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). It was determined that this issue posed a minimal risk to the BPS because these were historical paper findings. PT signals were successfully tested in 2015 under PRC-005-2. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) performed annual battery checks, including terminal connection resistance measurements; 2) implemented a new organizational electronic data filing system that will help minimize the potential for this noncompliance to recur. Test reports will be scanned and stored electronically going forward, and a new, explicit format will be used; and 3) adopted the use of fleet wide battery forms that are more prescriptive and will be used both by contractors and plant staff.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Talen Generation, LLC | NCR11362 | RFC2018019623 | VAR-002-4.1 | R1 | On December 31, 2017, Talen Generation, LLC submitted a self-log stating that, as a Generator Owner and Generator Operator, it was in noncompliance with VAR-002-4.1 R1. VAR-002-4 R1 requires the entity to place its Automatic Voltage Regulator (AVR) into automatic mode unless the entity notifies the Transmission Operator (TOP) that the AVR is not in automatic or the unit is in startup or shut down. On October 2, 2017, the entity’s night-shift control room operator came on-duty at 6 PM and began the shift-transfer process, which includes reviewing the alarm sequence display. At 6:12 PM, the night-shift control room operator noticed that the alarm sequence display showed the AVR of Unit 2 at the Lower Mount Bethel Power Plant (LMBE) in manual (instead of in automatic) and immediately notified his supervisor. At 6:17 PM, the entity returned the AVR to automatic mode and communicated the change in status to PJM (the TOP) at 6:31 PM. Upon further investigation, the entity discovered that the AVR had tripped to manual mode at 8:31 AM on October 12, 2017. The day-shift control room operator saw that the Unit 2 AVR had tripped to manual, knew of the NERC obligations, and thought he had returned the AVR to automatic before the deadline (VAR-002 R3 does not require notifying the TOP if the auto mode is restored within 30 minutes). The day shift operator, however, only turned the sub-loop controller back “on” at the DCS screen, believing that the resultant “auto” display meant that the AVR had been returned to the automatic control mode. This indication shows only, however, that going to the auto mode is not inhibited. The operator must then switch to the automatic mode at the AVR module to fully get the AVR back in automatic mode. This noncompliance involves the management practice of workforce management because the day-shift control room operator was not effectively trained on how to put the AVR back into automatic mode after it tripped into manual mode. That ineffective training is a root cause of this noncompliance. This noncompliance started on October 2, 2017, when the AVR tripped into manual mode and ended on October 2, 2017, when the entity put the AVR back into automatic mode. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not being in the automatic mode reduced the degree of control over the system voltage, but the AVRs of the other two units at LMBE remained in auto, and the system voltage continued well within the schedule limits. Straying near the voltage schedule limits could in fact have been beneficial, since it would have triggered another alarm (audible and visual), helping the operator to recognize that the U-2 AVR was still in manual. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) made AVR tripping to manual an alarm (red text in the ASD), with audible annunciation. The ASD text, which was not very informative before, now says “CT1 (or 2 or STG) AVR NOT IN AUTO” “CALL TR DISPATCH”. The operator can silence the alarm, but the red indication on the ASD remains until the unit is back in automatic; and 2) conducted incident-review training for the operators, and the findings herein were communicated throughout the entity fleet to ensure that corrective action is taken at any facilities with similar control system arrangements.
2018-06-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Talen Generation, LLC | NCR11362 | RFC2018019624 | VAR-002-4.1 | R3 | On December 31, 2017, Talen Generation, LLC submitted a self-log stating that, as a Generator Owner and Generator Operator, it was in noncompliance with VAR-002-4.1 R3. VAR-002-4 R3 requires the entity to notify its Transmission Operator (TOP) within 30 minutes of any change in status on the entity’s Automatic Voltage Regulator (AVR). On October 2, 2017, the entity failed to notify its TOP within 30 minutes of making a status change on its AVR. On October 2, 2017, the entity’s night-shift control room operator came on-duty at 6 PM and began the shift-transfer process, which includes reviewing the alarm sequence display. At 6:12 PM, the night-shift control room operator noticed that the alarm sequence display showed the AVR of Unit 2 at the Lower Mount Bethel Power Plant (LMBE) in manual (instead of in automatic) and immediately notified his supervisor. At 6:17 PM, the entity returned the AVR to automatic mode and communicated the change in status to PJM (the TOP) at 6:31 PM. Upon further investigation, the entity discovered that the AVR had tripped to manual mode at 8:31 AM on October 12, 2017. The day-shift control room operator saw that the Unit 2 AVR had tripped to manual, knew of the NERC obligations, and thought he had returned the AVR to automatic before the deadline (VAR-002 R3 does not require notifying the TOP if the auto mode is restored within 30 minutes). The day shift operator, however, only turned the sub-loop controller back “on” at the DCS screen, believing that the resultant “auto” display meant that the AVR had been returned to the automatic control mode. This indication shows only, however, that going to the auto mode is not inhibited. The operator must then switch to the auto mode at the AVR module to fully return the AVR to automatic mode. This noncompliance involves the management practice of workforce management because the day-shift control room operator was not effectively trained on how to put the AVR back into automatic mode after it tripped into manual mode. That ineffective training is a root cause of this noncompliance. This noncompliance started on October 2, 2017, when the AVR tripped into manual mode and the entity failed to notify PJM of that change in AVR status within 30 minutes of the change and ended on October 2, 2017, when the entity put the AVR back into automatic mode and notified PJM. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not being in the automatic mode reduced the degree of control over the system voltage, but the AVRs of the other two units at LMBE remained in auto, and the system voltage continued well within the schedule limits. Straying near the voltage schedule limits could in fact have been beneficial, since it would have triggered another alarm (audible and visual), helping the operator to recognize that the U-2 AVR was still in manual. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) made AVR tripping to manual an alarm (red text in the ASD), with audible annunciation. The ASD text, which was not very informative before, now says “CT1 (or 2 or STG) AVR NOT IN AUTO” “CALL TR DISPATCH”. The operator can silence the alarm, but the red indication on the ASD remains until the unit is back in automatic; and 2) conducted incident-review training for the operators, and the findings herein were communicated throughout the entity fleet to ensure that corrective action is taken at any facilities with similar control system arrangements.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2017017980 | PRC-005-6 | R3 | On July 24, 2017, AECC submitted a Self-Report stating that, as a Distribution Provider (DP), Generator Owner (GO) and Transmission Owner (TO), it was not compliant with PRC-005-6 R3 because it failed to verify testing of two underfrequency relays. Specifically, during an internal Quality Evidence Review (QER) AECC discovered that it did not have documentation of functional testing from the September 16, 2016 commissioning of two UFLS relays at the Clarksville distribution station. On June 5, 2017, AECC verified the UFLS relays had power, the correct set points had been installed, and the UFLS protection relay elements were functioning properly. This noncompliance started on the September 16, 2016, commissioning date and ended on June 5, 2017, the date the UFLS relay tests were performed and AECC confirmed the UFLS protection relay elements were properly functioning. The root cause of this noncompliance was human error in that documentation was either not produced or not retained after the relay testing on September 16, 2016; and lack of internal controls to insure that proper documentation is prepared and retained after relay testing is performed. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform UFLS Protection System relay testing has the potential to affect the reliability of the BPS by increasing the risk that the UFLS Protection System relay would not operate to reduce load during an underfrequency event. The failure to shed load automatically during an underfrequency event can decrease the time available for operators to respond to such an event and could further aggravate system underfrequency and lead to the loss of additional generation resources. Notwithstanding, this noncompliance was a documentation error and the UFLS tests performed on June 5, 2017, verified that the UFLS protection relays were correctly connected and the UFLS protection relay elements were properly functioning. No harm is known to have occurred. A Settlement Agreement covering violation of PRC-05-1 R2 (SPP2012010432) for AECC was filed with FERC under NP17-7-000 on November 30, 2016. On January 3, 2017, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE considered AECC’s compliance history and determined that the instant noncompliance was appropriate for Compliance Exception treatment because it was a documentation error whereas the prior noncompliance dealt with protection system relays exceeding maintenance and testing intervals at a hydroelectric facility. | To mitigate this noncompliance, AECC: 1) performed and documented the testing on the UFLS relays at the Clarksville distribution station; and 2) implemented additional procedures which require work plans be created for all major projects such as equipment testing, repair or replacement, as well as, required tests and acceptable evidence to verify performance. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2017018739 | VAR-002-4.1 | R2 | On December 4, 2017, AECC submitted a Self-Report stating that, as a Generator Operator, it had an issue of noncompliance with VAR-002-4.1 R.2 because it did not notify its Transmission Operator (TOP) of a deviation from its generator voltage schedule. Specifically, on October 17, 2017 at 2:32 pm, the Control Room Operator (CRO) at AECC’s Whillock Hydroelectric Generating Station, discovered that the timestamp reading on the point of Interconnection (POI) Voltage Intranet Webpage did not reflect the correct time. The CRO compared the POI Voltage Intranet Webpage reading (164.75 kV) to the distributed control systems (DCS) voltage (163.3 kV) and determined that the POI Voltage Intranet Webpage had frozen at 3:08 pm on October 15, 2017. During an internal review, the Plant Manager discovered 45 instances during the POI Voltage Intranet Webpage malfunction where the POI voltage dropped below the TOP’s voltage schedule lower limit. This noncompliance started on October 16, 2017 at 11:45 am, the first time the POI voltage dropped below the scheduled voltage lower limit during the webpage malfunction and the TOP was not notified; and ended on October 17, 2017 at 11:00 am, when the POI voltage returned to within the TOP’s voltage schedule limits. The root cause of this instance of noncompliance was both that the POI Voltage Internet Webpage froze, preventing the voltage POI display from reflecting actual POI voltage; and lack of internal controls to provide additional methods to monitor POI voltage. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Whillock units were in automatic voltage control mode during this period of noncompliance and were working to maintain system voltage within the acceptable range. The plant voltage regulator continued to control generator voltage during each of these excursions, keeping system voltage within 1.3 kV, or approximately 0.8%, of the lower voltage limit. The Whillock units have very little reactive capability and therefore have a very limited effect on the Bulk Electric System. No harm is known to have occurred. | To mitigate this noncompliance, AECC: 1) installed communications wiring from the Whillock kWh billing meter (the POI voltage source) to a plant Digital Control system (DCS) controller and set up the communications port to digitally receive the real-time POI voltage data into the DCS; 2) added three-phase line voltages and average voltage to operator displays and historical trends; 3) added alarming for the average voltage so the operators can monitor voltage readings on the DCS and the POI Voltage Intranet Webpage; and 4) retrained operators on DCS changes. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Noble Great Plains Windpark, LLC (Noble) | NCR11070 | SPP2018019513 | MOD-025-2 | R1; R1.1, R1.2 | On April 9, 2018, Noble submitted a Self-Report stating that, as a Generator Owner, it was not compliant with MOD-025-2 R1, R1.1, R1.2 because it failed to verify the Real Power capability of its 114 MW wind generation facility (R1.1) and submit the information to its Transmission Planner (TP) by July 1, 2016 (R1.2). Upon discovery of the missed compliance obligation, Noble scheduled a test when sufficient wind would meet the Standard's parameters and verified the wind generation facility’s Real Power capabilities in accordance with the MOD-025-2 Standard. This noncompliance started on July 1, 2016, the date MOD-025-2 R2 became enforceable for the Noble wind generation facility, and ended on January 4, 2018, the date Noble provided its TP with the Real Power capability of its wind generation facility. The root cause of this noncompliance was a misunderstanding of the phased-in implementation plan for MOD-025-2 (i.e. at least 40% of applicable Facilities by July 1, 2016). Notwithstanding owning multiple wind generation facilities, each of the Noble wind generation facilities is registered separately and is considered one Facility, requiring verification of the Real Power capability of all seven of the Noble Facilities by July 1, 2016. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate long-term decisions affecting the reliability of the BPS. Notwithstanding, the risk is minimal because Noble is an 114 MW intermittent wind generation facility that operates at a capacity factor of 37%. No harm is known to have occurred. Noble has no relevant prior violations of MOD-025-2 or any other standards that are similar in nature. | To mitigate this noncompliance, Noble: 1) verified the Real Power capability of its wind generation facility; 2) submitted a completed Attachment 2 to its TP; 3) hired a NERC consultant; 4) scheduled monthly update calls with the NERC consultant to review upcoming deadlines and changes in standards; and 5) scheduled an annual procedure review. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Noble Great Plains Windpark, LLC (Noble) | NCR11070 | SPP2018019514 | MOD-025-2 | R2; 2.1, 2.2 | On April 9, 2018, Noble submitted a Self-Report stating that, as a Generator Owner it was not compliant with MOD-025-2 R2, R2.1, R2.2 because it failed to verify the Reactive Power capability of its 114 MW wind generation facility (R2.1) and submit the information to its Transmission Planner (TP) by July 1, 2016 (R2.2). Upon discovery of the missed compliance obligation, Noble scheduled a test and verified the Reactive Power capabilities of its wind generation facility in accordance with the MOD-025-2 Standard. This noncompliance started on July 1, 2016, the date MOD-025-2 R2 became enforceable for the Noble wind generation facility, and ended on January 4, 2018, the date Noble provided its TP with the Reactive Power capability of its wind generation facility. The root cause of this noncompliance was a misunderstanding of the phased-in implementation plan for MOD-025-2 (i.e. at least 40% of applicable Facilities by July 1, 2016). Notwithstanding owning multiple wind generation facilities, each of the Noble wind generation facilities is registered separately and is considered one Facility, requiring verification of the Reactive Power capability of all seven of the Noble Facilities by July 1, 2016. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate long-term decisions affecting the reliability of the BPS. Notwithstanding, the risk is minimal because Noble is an 114 MW intermittent wind generation facility that operates at a capacity factor of 37%. Also, it is unlikely that Noble will operate at the maximum reactive-power output or be called upon to provide reactive support to the BPS. No harm is known to have occurred. Noble has no relevant prior violations of MOD-025-2 or any other standards that are similar in nature. | To mitigate this noncompliance, Noble: 1) verified the Reactive Power capability of its wind generation facility; 2) submitted a completed Attachment 1 to its TP; 3) hired a NERC consultant; 4) scheduled monthly update calls with the NERC consultant to review upcoming deadlines and changes in standards; and 5) scheduled an annual procedure review. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Noble Great Plains Windpark, LLC (Noble) | NCR11070 | SPP2018019499 | PRC-024-2 | R2 | On April 9, 2018, Noble submitted a Self-Report stating that, as a Generator Owner, it was not compliant with PRC-024-2 R2 because it did not verify its protective relays were set to not trip as a result of a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. Noble determined that four relay, SEL-351/SITE 2, SEL-351/SITE 4 (primary and secondary), and SEL-351-1/SITE 4 overvoltage settings were not in compliance with PRC-024-2. This noncompliance started on July 1, 2016, the date PRC-024-2 R2 became enforceable for Noble, and ended on March 28, 2018, the date Noble changed the overvoltage settings of its relays to be in compliance with PRC-024-2. The root cause of this noncompliance was a misunderstanding of the phased-in implementation plan for PRC-024-2 (i.e. at least 40% of applicable Facilities by July 1, 2016). Notwithstanding owning multiple wind generation facilities, each of the Noble wind generation facilities is registered separately and is considered one Facility, requiring verification of the voltage relay settings for all seven of the Noble Facilities by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, the four relays identified by Noble with overvoltage set points inside the no trip zone were only marginally inside the no trip zone (average < 3%) and all were set with a five second delay. A minor voltage event would have cleared before expiration of the five second delay, avoiding an unnecessary unit trip. Additionally, Noble is a 114 MW variable generation wind farm that operates at a 37% capacity factor. No harm is known to have occurred. Noble has no relevant prior violations of PRC-024-2 or any other standards that are similar in nature. | To mitigate this noncompliance, Noble: 1) changed the overvoltage settings of the four relays found noncompliant with PRC-024-2 so as to prevent a trip as a result of a voltage excursion within the no trip zone; 2) hired a NERC consultant to assist in managing NERC Compliance; and 4) scheduled monthly update calls with the NERC consultant to provide: i. a general NERC/FERC update; ii. pending or proposed changes to NERC standards; iii. applicable standards effective dates and impact on Noble; and iv. a general review of any action items. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2017018225 | TOP-001-3 | R14 | During a Compliance Audit conducted from August 15, 2017, through August 17, 2017, SPP RE determined that SPA, as a Transmission Operator, was not compliant with TOP-001-3 R14. SPP RE determined that SPA did not develop an Operating Plan to mitigate the Sikeston – Idalia thermal SOL exceedance for a New Madrid – Essex 345 kV contingency identified in SPA’s May 10, 2017, 7:30 am Real Time Contingency Analysis (RTCA). On November 2, 2017, SPA submitted a Self-Certification indicating that it had identified additional instances of noncompliance with TOP-001-3 R14. SPA reviewed its RTCA results between July 1, 2017, and December 31, 2017, and identified 1900 thermal and 828 voltage contingencies. Ninety-one of the thermal contingencies and 136 of the voltage contingencies were identified as requiring Operating Plans. SPA determined that Operating Plans were not developed for 59 of the 227 contingencies requiring Operating Plans. This noncompliance started on July 6, 2017, the date the SPA System Operators first failed to develop an Operating Plan for an SOL exceedance identified in its RTCA and ended on September 27, 2017, the last instance of SPA System Operators failing to develop an Operating Plan for an SOL exceedance identified in a RTCA. The root cause of this noncompliance was a combination of human error and a lack of management controls to ensure Operating Plans were created for SOL exceedances identified in RTCAs. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to develop operating plans for contingencies identified in a RTCA increases the risk that System Operators would not be prepared to respond to the system contingencies, should they occur. Here, the risk to the BPS is mitigated because: the 59 contingencies without Operating Plan only involved 11 monitored elements and most were repetitive occurrences within a short period of time; the average thermal exceedance identified in the RTCA was less than 5%; the average voltage exceedance identified in the RTCA was less than 7%; all of the exceedances identified in the RTCAs were at the lower 161 kV transmission voltage; most of the contingencies were known to the SPA System Operators and Operating Plans had previously been developed; the SPA System Operators continued to monitor the SPA transmission system and would have responded to the contingencies; and none of the contingencies identified in the RTCAs occurred. No harm is known to have occurred. SPA has no relevant prior violations of TOP-001-3 or any other standards that are similar in nature. | To mitigate this noncompliance, SPA: 1) investigated the scope of the noncompliance and determined the root cause; 2) reprimanded an offending employee; 3) conducted additional System Operator training emphasizing the importance of creating Operating Plans for any thermal contingency at 100% or above and any voltage contingency that is + or – 5% of nominal during peak months of the year and + 8% and – 5% in the shoulder months of March, April, May, September, October, and November 4) revised the Dispatch Standing Order “Transmission Studies Desk Procedure” to more clearly state that all contingencies that meet the threshold must have an Operating Plan; 5) added performance of the Transmission Studies Desk Procedures to the individual performance standards for System Operators; and 6) supplemented the Chief Dispatcher daily review of the Dispatcher electronic logs by having a contract compliance analyst conduct a review of the Contingency log and submit a report to the Compliance Department every month. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2018019560 | TOP-001-3 | R13 | On April 20, 2018, SPA submitted a Self-Certification stating that, as a Transmission Operator, it was not compliant with TOP-001-3 R13. Specifically, on the morning of February 18, 2018, SPA System Operators, on two occasions, at 7:00 am and 9:10 am, failed to evaluate a Real-time Assessment once every 30 minutes. SPA contracts with the Southwest Power Pool (SPP) to perform the required Real-Time Assessments to determine if there are any contingencies that could result in instability, uncontrolled separation, or cascading outages. SPA receives the Real-Time Contingency Analysis (RTCA) from SPP every ten minutes. On the morning of February 18, 2018, in addition to their normal duties, both the SPA System Operators that were on duty were assigned mandatory Department of Energy online training. As a result, the SPA System Operators were focused on the mandatary training and failed to assess the three real-time contingencies identified in the SPP RTCA on two occasions. This noncompliance started on February 18, 2018, the date the SPA System Operators failed to perform a Real-time Assessment once every 30 minutes, and ended on February 18, 2018, when the SPA System Operators resumed performance of the real-time assessments. The root cause of this noncompliance was a combination of human error and a lack of administrative controls to prevent both of the on-duty SPA System Operators from engaging in administrative tasks simultaneously. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform a Real-time Assessment once every 30 minutes has the potential to affect the reliability of the BPS by increasing the risk that System Operators would fail to establish an operating plan for contingencies identified in a RTCA which could result in instability, uncontrolled separation, or cascading outages. Here, the risk to the BPS is mitigated because: the post-contingent issues identified in the RTCAs did not rise to the level of a thermal or voltage SOL violation; no operating plan for the contingencies identified in the RTCAs was required; only two assessments in a twenty-four hour period were missed; and the SPA System Operators continued to monitor the SPA system and would have responded to system alarms. No harm is known to have occurred. SPA has no relevant prior violations of TOP-001-3 or any other standards that are similar in nature. | To mitigate this noncompliance, SPA: 1) amended the Dispatch Standing Order for Dispatch Duties and Desk Turnover to limit online training to one System Operator at a time; and 2) disciplined the on-duty operators. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP2017018392 | PRC-005-6 | R3 | On September 28, 2017, WR submitted a Self-Report stating that, as a Generator Owner and Transmission Owner it was not compliant with PRC-005-6 R3. WR discovered it had not performed all battery maintenance activities in accordance with the maximum maintenance intervals defined in WR’s protection system maintenance and testing program (PSMTP). Specifically, one valve regulated lead-acid (VRLA) battery bank that was installed on April 17, 2015 had not been tested within the eighteen-month interval specified in the PSMTP. The newly installed VRLA battery bank was one of 209 (<1%) of battery banks in WR’s PSMTP. This noncompliance started on April 1, 2017, the date WR should have had 100% of its battery banks tested per the Implementation Plan of the standard, and ended on August 29, 2017, the date the VRLA battery bank was tested. The root cause of this noncompliance was human error. The WR scheduler/planner did not follow WR’s procedure to retire the original vented lead acid (VLA) battery bank record and create the VRLA battery bank record in the Cascade system. Therefore, the eighteen month maintenance trigger of the VRLA battery bank was not triggered by the Cascade system, causing WR to not test the VRLA battery bank within 18 months as required by its PSMTP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform timely battery maintenance has the potential to affect the reliability of the BPS by increasing the risk that the batteries will fail and not provide power when needed. Notwithstanding, the risk was minimal. WR was checking and servicing all battery banks at four month intervals. Less than 1% of WR’s battery banks were affected by the noncompliance and the issue was promptly mitigated upon discovery. The new VRLA battery bank was installed in 2015 and was less than three years old when it was tested per the PSMTP. No harm is known to have occurred. WR has no relevant prior violations of PRC-005-6 R3 or any other standards that are similar in nature. | To mitigate this noncompliance, WR: 1) retired and created in Cascade the battery banks per WR’s procedure (8/25/2017); 2) performed battery testing on the one VRLA battery bank (8/29/2017); 3) conducted refresher training to the WR scheduler/planners on the procedure for properly retiring and creating battery assets in the Cascade system (8/30/2017); and, 4) implemented monthly comparisons using a Cascade report to compare battery type to battery maintenance triggers (9/14/2017). SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP2018018919 | COM-002-4 | R3 | On January 2, 2018, WR submitted a Self-Report stating that, as a Distribution Provider and Generator Operator, it was not compliant with COM-002-4 R3. During an internal review, WR discovered that four out of 851 (<1%) individual operators did not receive initial training prior to the individual operators receiving an oral two-party, person-to-person Operating Instruction. This noncompliance started on July 1, 2016, the date COM-002-4 became mandatory and enforceable, and ended on November 17, 2017, the date the last operator received training. The root cause of this noncompliance was a lack of internal controls to verify that operators received initial training prior to receiving two-party person operating instructions. In this case, one operator was on medical leave when the initial training was performed prior to the July 1, 2016, reliability standard effective date. The three other individuals that did not receive initial training were either new hires or transfers into operator jobs that were required to take the training. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to provide initial training to operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an Operating Instruction could limit operators’ awareness of predefined communications procedures, which could increase the possibility of miscommunication between the operator and other parties. Notwithstanding, the actual risk was minimal. Only eight instances of two way communication of an Operating Instruction occurred between the four operators who did not receive the initial training during the noncompliance. In each of the eight instances correct oral, two-party person-to-person communication was executed per WR’s process. No harm is known to have occurred. Westar has no relevant prior violations of COM-002-4 R3 or any other standards that are similar in nature. | To mitigate this noncompliance, WR: 1) completed initial training for the four operators; and, 2) included a step for training on receiving operating instructions in the employee new hire and transfer training requirements. SPP RE has verified the completion of all mitigation activity.
2018-06-28 | Texas Reliability Entity (Texas RE) | Consolidated Edison Development, Inc. (CED) | NCR11605 | TRE2017018102 | BAL-001-TRE-1 | R6; R6.1 | On August 2, 2017, CED submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with BAL-001-TRE-1 R6. In particular, CED discovered that the maximum deadband setting for its solar generation Facility was not correctly set in accordance with BAL-001-TRE-1 R6.1. Pursuant to the Governor deadband settings set forth in BAL-001-TRE-1 R6.1, solar generating Facilities should be set with a maximum deadband of +/- 0.017 Hz. In this instance, CED determined during a compliance review of a newly acquired solar generation Facility that the maximum deadband setting for that single solar generation Facility was incorrectly set to a maximum of +/- 0.036 Hz. On November 3, 2016, CED changed the deadband settings to the proper +/- 0.017 Hz settings, ending the issue. The root cause of this issue was an insufficient process to evaluate and determine all generating unit Governor types and their corresponding deadband settings for all of its applicable Facilities. In particular, CED failed to review the deadband settings prior to acquiring the single solar generation Facility at issue. This noncompliance started on July 12, 2016, when CED’s solar generation Facility was registered as a GO under NCR11605, and ended on November 3, 2016, when CED updated the Governor settings for the Facility at issue from +/- 0.036 Hz to +/-0.017 Hz. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CED’s failure to properly set its generator Governor parameters could result in an unacceptable frequency response during a system frequency excursion. However, the risk associated with this issue was mitigated by the following factors. First, the single solar Facility normally operates at maximum output based on available sunlight at any given time and is therefore not expected to provide Primary Frequency Response (PFR) unless in a curtailed state. Second, the issue was limited to a single solar generation Facility and CED’s other two generation Facilities were compliant with BAL-001-TRE-1 R6. Finally, the overall market frequency response in ERCOT is robust enough to ensure sufficient frequency response is available to respond to Frequency Measureable Events. In particular, for 2016 the ERCOT Interconnection minimum Frequency Response was 381 and the average Interconnection Frequency Response for that period was 886. No harm is known to have occurred. Texas RE considered CED’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, CED: 1) updated the frequency deadband to comply with BAL-001-TRE-1 R6; 2) revised its NERC Questionnaire templates to include checks for frequency control deadband and droop settings as required by BAL-001-TRE1 R6; and 3) removed an HMI link that allowed individuals to change the deadband setting. Texas RE has verified the completion of all mitigation activity.
2018-06-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IA, LLC (LVWIA) | NCR11267 | TRE2017017266 | PRC-024-2 | R1 | On March 20, 2017, LVWIA submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. In particular, LVWIA failed to set its frequency protective relays to not trip within the “no trip zone” for its wind generation Facility by July 1, 2016. During late 2016, LVWIA engaged a third-party contractor to review its frequency trip settings at its single wind generation Facility. On December 21, 2016, the contractor determined that LVWIA’s existing relay trip settings were within the “no trip zone.” Following this discovery, LVWIA implemented all required setting changes during a planned outage on October 12, 2017, ending the PRC-024-2 R1 issue. The root cause of this noncompliance was a misunderstanding of the required date for LVWIA to set the frequency trip settings outside the “no trip zone” for its wind generation Facility. In particular, LVWIA mistakenly believed that because it only owned a single generation Facility, it did not need to ensure its frequency trip settings were outside the “no trip zone” until July 1, 2019, the date entities are required to be 100% compliant with the PRC-024-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and ended on October 12, 2017, when LVWIA set its frequency protective relays to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, a several factors mitigated the risk posed by this issue. First, LVWIA produced a relatively small amount of power, contributing an average of only 71 MW with a 36% capacity factor, during the issue duration. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” Lastly, the issue only impacted LVWIA’s over frequency relay settings, and these over frequency settings would have allowed the relays to operate up to 61.50 Hz for 30 seconds before tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered LVWIA’s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIA: 1) implemented settings that were compliant with PRC-024-2 R1; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-06-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IB, LLC (LVWIB) | NCR11266 | TRE2017017270 | PRC-024-2 | R1 | On March 20, 2017, LVWIB submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. In particular, LVWIB failed to set its frequency protective relays to not trip within the “no trip zone” for its wind generation Facility by July 1, 2016. During late 2016, LVWIB engaged a third-party contractor to review its frequency trip settings at its single wind generation Facility. On December 21, 2016, the contractor determined that LVWIB’s existing relay trip settings were within the “no trip zone.” Following this discovery, LVWIB implemented all required setting changes during a planned outage on October 16, 2017, ending the PRC-024-2 R1 issue. The root cause of this noncompliance was a misunderstanding of the required date for LVWIB to set the frequency trip settings outside the “no trip zone” for its wind generation Facility. In particular, LVWIB mistakenly believed that because it only owned a single generation Facility, it did not need to ensure its frequency trip settings were outside the “no trip zone” until July 1, 2019, the date entities are required to be 100% compliant with the PRC-024-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and ended on October 16, 2017, when LVWIB set its frequency protective relays to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, a several factors mitigated the risk posed by this issue. First, LVWIB produced a relatively small amount of power, contributing an average of only 64 MW with a 32% capacity factor. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” Lastly, the issue only impacted LVWIB’s over frequency relay settings, and these over frequency settings would have allowed the relays to operate up to 61.50 Hz for 30 seconds before tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered LVWIB’s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIB: 1) implemented settings that were compliant with PRC-024-2 R1; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-06-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IV, LLC (LVIV) | NCR11635 | TRE2017017275 | PRC-024-2 | R2 | On March 20, 2017, LVIV submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. In particular, LVIV failed to set its voltage protective relays to not trip within the “no trip zone” for its wind generation Facility by July 1, 2016. During late 2016, LVIV engaged a third-party contractor to review its voltage protective relay trip settings at its single wind generation Facility. On January 19, 2017, the contractor determined that LVIV’s existing voltage protective relay trip settings were within the “no trip zone.” Following this discovery, LVIV implemented all required setting changes during a planned outage on November 29, 2017, ending the PRC-024-2 R2 issue. The root cause of this noncompliance was a misunderstanding of the required date for LVIV to set the voltage protective relay trip settings outside the “no trip zone” for its wind generation Facility. In particular, LVIV mistakenly believed that because it only owned a single generation Facility, it did not need to ensure its voltage protective relay trip settings were outside the “no trip zone” until July 1, 2019, the date entities are required to be 100% compliant with the PRC-024-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on November 29, 2017, when LVIV set its voltage protective relays to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, a several factors mitigated the risk posed by this issue. First, LVIV produced a relatively small amount of power, contributing an average of only 75 MW with a 37% capacity factor, during the period of noncompliance. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” Lastly, the issue only impacted LVIV’s under voltage protection relay settings, and these incorrect settings would have allowed the relays to operate up to .85 pu for 2 seconds before impermissibly tripping the single wind generation Facility at issue. No harm is known to have occurred. Texas RE considered LVIV’s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVIV: 1) implemented settings that were compliant with PRC-024-2 R2; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-06-28 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2017017259 | PRC-024-2 | R2 | On March 20, 2017, NWLP submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. In particular, NWLP failed to set its voltage protective relays to not trip within the “no trip zone” for its wind generation Facility by July 1, 2016. During late 2016, NWLP engaged a third-party contractor to review its voltage protective relay trip settings at its single wind generation Facility. On November 2, 2016, the contractor determined that NWLP’s existing voltage protective relay trip settings were within the “no trip zone.” Following this discovery, NWLP implemented all required setting changes during a planned outage on November 7, 2016, ending the PRC-024-2 R2 issue. The root cause of this noncompliance was a misunderstanding of the required date for NWLP to set the voltage protective relay trip settings outside the “no trip zone” for its wind generation Facility. In particular, NWLP mistakenly believed that because it only owned a single generation Facility, it did not need to ensure its voltage protective relay trip settings were outside the “no trip zone” until July 1, 2019, the date entities are required to be 100% compliant with the PRC-024-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on November 7, 2016, when NWLP set its voltage protective relays to not trip within the “no trip zone.” | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. However, a several factors mitigated the risk posed by this issue. First, NWLP produced a relatively small amount of power, contributing an average of only 48 MW with a 31% capacity factor, during the period of noncompliance. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” Lastly, the issue only impacted NWLP’s under voltage protection relay settings, and these incorrect settings would have allowed the relays to operate up to .8 pu for 1 second before impermissibly tripping the single wind generation Facility at issue. Texas RE considered NWLP’s and its affiliates’ PRC-024 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, NWLP: 1) implemented settings that were compliant with PRC-024-2 R2; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; and 3) created a procedure detailing the process to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with PRC-019, PRC-024, and MOD-025. Texas RE has verified the completion of all mitigation activity.
2018-06-28 | Texas Reliability Entity (Texas RE) | Oxy Vinyls LP (OVLP) | NCR04110 | TRE2018019487 | MOD-025-2 | R1 | During a Compliance Audit conducted from March 13, 2018 through April 6, 2018, Texas RE determined that OVLP, as a Generator Owner (GO), had a possible noncompliance with MOD-025-2 R1 relating to the verification of Real Power capability. In particular, OVLP did not timely perform the requisite Real Power capability verifications for its four generating units prior to the effective date of the Reliability Standard or provide the results of those verifications to its Transmission Planner (TP) as required. During the Compliance Audit, Texas RE determined that OVLP had not completed the required Real Power capability verification testing by the July 1, 2016 deadline. In particular, OVLP provided evidence that it did not complete the required Real Power capability verification for at least 40% of its applicable units until August 24, 2016. In addition, OVLP could not provide evidence that it submitted the test results to its TP within 90 days of completing testing. On June 30, 2017, OVLP submitted its Real Power capability testing results to its TP, ending the issue. The root cause of this issue is that OVLP lacked a sufficient process to ensure compliance with all applicable requirements in MOD-025-2. In particular, OVLP lacked a process to track, review, and communicate compliance responsibilities regarding the MOD-025-2 Real Power verification capability requirements. This noncompliance began on July 1, 2016, when MOD-025-2 became enforceable, and ended on June 30, 2017, when OVLP provided the required Real Power verifications to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, OVLP previously provided Real Power verifications under substantially similar region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, OVLP’s Facility is a Private Use Network (PUN) that primarily serves its internal load. Net positive injection to the grid is typically below 50 MVA, and represented only a 6% net capacity factor during the duration of OVLP’s MOD-025 issues. Accordingly, the lack of OVLP’s Real Power capability verification information would have only a minimal impact on planning results. No harm is known to have occurred. Texas RE considered OVLP’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, OVLP: 1) completed required Real Power verifications for all units; 2) provided Real Power verifications to its TP; 3) adopted a documented process for compliance with MOD-025-2; 4) created automatic reminders to notify OVLP personnel one year prior to the date on which future required tests are due; 5) conducted a training regarding the new documented process for compliance with MOD-025-2; and 6) conducted a training designed to address compliance issues in light of the 2018 Compliance Audit. Texas RE has verified the completion of all mitigation activity.
2018-06-28 | Texas Reliability Entity (Texas RE) | Oxy Vinyls LP (OVLP) | NCR04110 | TRE2018019488 | MOD-025-2 | R2 | During a Compliance Audit conducted from March 13, 2018 through April 6, 2018, Texas RE determined that OVLP, as a Generator Owner (GO), had a possible noncompliance with MOD-025-2 R2 relating to the verification of Reactive Power capability. In particular, OVLP did not timely perform the requisite Reactive Power capability verifications for its four generating units prior to the effective date of the Reliability Standard or provide the results of those verifications to its Transmission Planner (TP) as required. During the Compliance Audit, Texas RE determined that OVLP had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline. In particular, OVLP provided evidence that it did not complete the required Reactive Power capability verifications for its applicable units until October 25, 2017. In addition, OVLP could not provide evidence that it submitted the test results to its TP within 90 days of completing testing. On March 21, 2018, OVLP submitted its Reactive Power capability testing results to its TP, ending the issue. The root cause of this issue is that OVLP lacked a sufficient process to ensure compliance with all applicable requirements in MOD-025-2. In particular, OVLP lacked a process to track, review, and communicate compliance responsibilities regarding the MOD-025-2 Reactive Power verification capability requirements. This noncompliance began on July 1, 2016, when MOD-025-2 became enforceable, and ended on March 21, 2018, when OVLP provided the required Reactive Power verifications to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, OVLP previously provided Reactive Power verifications under substantially similar region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, OVLP’s Facility is a Private Use Network (PUN) that primarily serves its internal load. Net positive injection to the grid is typically below 50 MVA, and represented only a 6% net capacity factor during the duration of OVLP’s MOD-025 issues. Accordingly, the lack of OVLP’s Reactive Power capability verification information would have only a minimal impact on planning results. No harm is known to have occurred. Texas RE considered OVLP’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, OVLP: 1) completed required Reactive Power verifications; 2) provided all required Reactive Power verifications to its TP; 3) adopted a documented process for compliance with MOD-025-2; 4) created automatic reminders to notify OVLP personnel one year prior to the date on which future required tests are due; 5) conducted a training regarding the new documented process for compliance with MOD-025-2; and 6) conducted a training designed to address compliance issues in light of the 2018 Compliance Audit. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Midwest Reliability Organization (MRO) | American Transmission Co. LLC (ATC) | NCR00685 | MRO2018019018 | NUC-001-3 | 4 | On January 16, 2018, ATC, a Multi-Region Registered Entity program participant, submitted a self-log to MRO stating that, as a Transmission Owner, Transmission Operator, and Transmission Planner, it was in noncompliance with NUC-001-3 R4. ATC is registered in the ReliabilityFirst Region under the same name and NCR ID, and are both monitored under the Coordinated Oversight Program. The noncompliance occurred in the MRO Region. ATC discovered that it had two switches incorrectly modeled in its EMS system that led to two station service loads not being properly modeled. ATC made an EMS system revision on January 18, 2017. After the revision, the switches changed position in the system. ATC discovered the issue on October 4, 2017 and notified the Nuclear Plant Generator Operator of the issue on November 14, 2017. The cause of the noncompliance was ATC did not contemplate the switch positons could be changed during the EMS system revision, and thus did not perform a sufficient review of the position of the switches associated with the four unit-trip contingencies after the EMS system revision had been completed. This noncompliance started on January 18, 2017, when the switches became incorrectly modeled, and ended on November 14, 2017, when the switch positions were corrected and ATC informed the Nuclear Plant Generator Operator of the issue. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The model issue did not cause an issue in monitoring the actual system conditions of the NPIR facilities associated with the nuclear power plant. The error resulted in a small error on ATC's modeling of the post-contingent generator service loads. Depending on the contingency being analyzed, the error in service loads would have been 26 MW and 14 Mvar on the 19 kV bus and/or 13.5 MW and 7.4 Mvar on the 13.8 kV bus. No harm is known to have occurred. | To mitigate this noncompliance, ATC: 1) corrected the contingency switch position in its EMS systems and in the offline EMS modeling tool to ensure the correct status of switches online during future changes; 2) informed the Nuclear Plant Generator Operator of the issue; and 3) created an automatic email notification to identify any instance where one or more of the nuclear facilities' loads that are modeled for a contingency are disconnected, which will alert ATC personnel to identify and correct any errors in the position of the switches.
2018-05-31 | Midwest Reliability Organization (MRO) | Basin Electric Power Cooperative (BEPC) | NCR00102 | MRO2017018094 | FAC-003-4 | R6 | On August 4, 2017, BEPC submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with FAC-003-4 R6. Specifically, BEPC did not perform a Vegetation Inspection of the Judson-Williston 230 kV line in the 2016 calendar year. The line received its first vegetation inspection on November 17, 2015 shortly before the line was energized. The line is approximately 2 miles long and cannot be aerially inspected because the line is located in an industrial portion of Williston, North Dakota. BEPC discovered the noncompliance on June 13, 2017 during an internal audit of its 2016 Vegetation Inspections, which was a detective internal control that BEPC used to identify any missed Vegetation Inspections in 2016. The cause of the noncompliance was BEPC's failure to update its 2016 Work Plan to include a non-aerial inspection of the line. BEPC did incorporate the line into its 2017 Work Plan, and performed a Vegetation Inspection of the line in 2017 prior to discovering the noncompliance. This noncompliance started on January 1, 2017, when it failed to inspect the line in calendar year 2016 and ended on June 8, 2017, when BEPC performed a Vegetation Inspection on the line. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential risk of a vegetation contact on this line is low because the line is located in an industrial portion of Williston, ND and the ground is mostly covered with concrete. Additionally, the line was less than two years old, limiting the potential risk that vegetation had grown into the Minimum Vegetation Clearance Distance. Further, the noncompliance was detected by an internal audit, a functioning detective control, and this was the only instance of noncompliance detected by the internal audit. Moreover, while BEPC missed conducting an inspection in every calendar year, BEPC only missed an 18-month interval (which is an acceptable interval under the requirement provided at least one inspection is completed in every calendar year) by 7 days. Finally, BEPC does not own any facilities that are part of an IROL. No harm is known to have occurred. BEPC has no relevant history of noncompliance. | To mitigate this noncompliance, BEPC: 1) performed the Vegetation Inspection on the line; 2) updated its annual work plan process to specifically take into consideration the facilities that cannot be aerially patrolled; and 3) created a post-inspection Ground Tree Patrol Checklist that will inform the Annual Work Plan and a compliance monitoring tool.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | National Grid USA | NCR11171 | NPCC2018019382 | PRC-005-6 | R3. | On March 15, 2018, National Grid USA (the Entity) submitted a self-log stating that, as a TO, it was in noncompliance with PRC-005-6 R3. Due to an incomplete verification of required maintenance for 115kV substations during calendar-year 2017, the Entity failed to perform on time periodic maintenance for seven protection relays that provide differential overcurrent protection at a bus located within one of its 115kV substation in the New York Control Area. Per the time-based maximum interval of six calendar years, as specified in PRC-005-6 Table 1-1, maintenance on these devices was required by December 31, 2017. This noncompliance started on January 1, 2018, the day after the date when the periodic maintenance for the seven relays was required by, and ended on January 20, 2018, when the Entity completed testing of the aforementioned devices. The root cause of this instance of noncompliance was an incomplete review and verification of required maintenance for protection devices at one 115kV substation during calendar-year 2017. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The seven noncompliant relays represent 0.037 % of the total number of relays owned by the Entity at its 282 BES substations, and remained in noncompliance for a period of twenty days. When the seven relays were tested, on January 20, 2018, they were found to be operating correctly. Additionally, as the bus is designed with overlapping zones of protection, it would not have been left unprotected if the noncompliant relays had failed. No operations or misoperations of the protective relays occurred during the twenty days of noncompliance. A small hydro generating plant, interconnected to the 115kV substation, is rated at 34.4 MW, which is less than 2.0% of the Entity's Reliability Coordinator's (NYISO) required summer Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to unnecessarily trip during a system event, the NYISO would have been able to replace the lost capacity. No harm is known to have occurred as a result of this instance of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by completing testing of the seven noncompliant relays; and 2. To prevent a recurrence of similar instances of noncompliance, reviewed relay maintenance requirements with Protection & Telecom Operations supervisors, highlighting the importance that a thorough verification of timely completion of periodic maintenance for protection devices is paramount to ensure compliance with the standard and requirement. NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | New York Power Authority | NCR07161 | NPCC2017018294 | PRC-019-2 | R1. | On September 1, 2017, New York Power Authority (the Entity) submitted a self-log stating that, as a TO, it was in noncompliance with PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for 40% of its applicable generating units by 7/1/2016 as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on January 4, 2017, when the Entity completed its coordination verification by adjusting the Volt/Hz relay setting on the last of its applicable generating units. The root cause of this instance of noncompliance was the failure of the Entity's Protection & Control Engineering department to timely issue a work order to site personnel for completing the coordination of voltage regulating system controls of applicable generating facilities by the required date. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity needed to verify voltage coordination on 24 generating units to satisfy its 40% requirement by July 1, 2016. Having completed work on 23 of these units by the required date, only one (1) generating unit was temporarily noncompliant for a period of six months. The noncompliant generator is rated at 25 MW, and was operated at a low capacity factor of 13% in 2016, where most of the duration of the noncompliance period occurred. Additionally, the generator's rated capacity is less than 2.0% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the noncompliant generator to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal impact on the reliable operation of the BPS system. No harm is known to have occurred as a result of this instance of noncompliance. | To mitigate this noncompliance, the Entity: 1) corrected the noncompliance by completing its coordination verification by adjusting the Volt/Hz relay setting on the last of its applicable generating units. 2) To prevent a recurrence of similar instances of noncompliance: a) implemented an internal procedure documenting the compliance process related to the standard; b) provided awareness to all NYPA personnel with responsibilities associated with PRC-019-2 requirements; and c) will ensure, going forward, a timely coordination of voltage regulating system controls for applicable generating facilities through the use of its automated asset management system, MAXIMO, to issue work orders to site personnel consistent with required implementation schedules NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2018019157 | MOD-025-2 | R1 | On February 12, 2018, Noble Altona Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the real power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 13, 2017 when the Entity provided the real power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was a failure in the MOD-025 review process that management had in place to timely recognize that the annual market based real power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 98 MW wind facility that has an annual capacity factor of approximately 20%. Failure to perform this test has minimal impact on reliability because of the known intermittent real power supplied by a wind facility. Prior real power capability data was provided to the TP as a by-product NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. Finally, the NYISO operating personnel had awareness of the Entity's real power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Real Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP. 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2018019158 | MOD-025-2 | R2 | On February 12, 2018, Noble Altona Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the reactive power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 13, 2017 when the Entity provided the reactive power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based reactive power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 98 MW wind facility that has an annual capacity factor of approximately 20% and failure to perform this test has minimal impact on reliability because of the known intermittent reactive power supplied by a wind facility. Prior reactive power capability tests have occurred through the NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. Finally, the NYISO operating personnel had awareness of the Entity's reactive power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Reactive Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC | NCR10271 | NPCC2018019159 | MOD-025-2 | R1 | On February 12, 2018, Noble Bliss Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the real power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 8, 2017 when the Entity provided the real power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based real power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 100 MW wind facility that has an annual capacity factor of approximately 30% and failure to perform this test has minimal impact on reliability because of the known intermittent real power supplied by a wind facility. Prior real power capability data was provided to the TP as a by-product NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. Finally, the NYISO operating personnel had awareness of the Entity's real power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Real Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Bliss Windpark, LLC | NCR10271 | NPCC2018019160 | MOD-025-2 | R2 | On February 12, 2018, Noble Bliss Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the reactive power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 8, 2017 when the Entity provided the reactive power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based reactive power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 100 MW wind facility that has an annual capacity factor of approximately 30% and failure to perform this test has minimal impact on reliability because of the known intermittent reactive power supplied by a wind facility. Prior reactive power capability tests have occurred through the NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. Finally, the NYISO operating personnel had awareness of the Entity's reactive power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Reactive Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC | NCR10367 | NPCC2018019161 | MOD-025-2 | R1 | On February 12, 2018, Noble Chateaugay Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the real power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 14, 2017 when the Entity provided the real power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based real power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 107 MW wind facility that has an annual capacity factor of approximately 22% and failure to perform this test has minimal impact on reliability because of the known intermittent real power supplied by a wind facility. Prior real power capability data was provided to the TP as a by-product NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. Finally, the NYISO operating personnel had awareness of the Entity's real power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Real Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC | NCR10367 | NPCC2018019162 | MOD-025-2 | R2 | On February 12, 2018, Noble Chateaugay Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the reactive power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 14, 2017 when the Entity provided the reactive power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based reactive power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 107 MW wind facility that has an annual capacity factor of approximately 22% and failure to perform this test has minimal impact on reliability because of the known intermittent reactive power supplied by a wind facility. Prior reactive power capability tests have occurred through the NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. Finally, the NYISO operating personnel had awareness of the Entity's reactive power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Reactive Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC | NCR10272 | NPCC2018019163 | MOD-025-2 | R1 | On February 12, 2018, Noble Clinton Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the real power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 14, 2017 when the Entity provided the real power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based real power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 100 MW wind facility that has an annual capacity factor of approximately 20% and failure to perform this test has minimal impact on reliability because of the known intermittent real power supplied by a wind facility. Prior real power capability data was provided to the TP as a by-product NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. Finally, the NYISO operating personnel had awareness of the Entity's real power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Real Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC | NCR10272 | NPCC2018019164 | MOD-025-2 | R2 | On February 12, 2018, Noble Clinton Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the reactive power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on December 14, 2017 when the Entity provided the reactive power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based reactive power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 100 MW wind facility that has an annual capacity factor of approximately 20% and failure to perform this test has minimal impact on reliability because of the known intermittent reactive power supplied by a wind facility. Prior reactive power capability tests have occurred through the NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. Finally, the NYISO operating personnel had awareness of the Entity's reactive power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Reactive Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC | NCR10273 | NPCC2018019165 | MOD-025-2 | R1 | On February 12, 2018, Noble Ellenburg Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the real power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on November 14, 2017 when the Entity provided the real power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based real power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 81 MW wind facility that has an annual capacity factor of approximately 24% and failure to perform this test has minimal impact on reliability because of the known intermittent real power supplied by a wind facility. Prior real power capability data was provided to the TP as a by-product NYISO Voltage Support Services program.. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. Finally, the NYISO operating personnel had awareness of the Entity's real power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Real Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC | NCR10273 | NPCC2018019166 | MOD-025-2 | R2 | On February 12, 2018, Noble Ellenburg Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the reactive power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on November 14, 2017 when the Entity provided the reactive power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based reactive power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 81 MW wind facility that has an annual capacity factor of approximately 24% and failure to perform this test has minimal impact on reliability because of the known intermittent reactive power supplied by a wind facility. Prior reactive power capability tests have occurred through the NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. Finally, the NYISO operating personnel had awareness of the Entity's reactive power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Reactive Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2018019167 | MOD-025-2 | R1 | On February 12, 2018, Noble Weathersfield Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the real power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on November 29, 2017 when the Entity provided the real power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based real power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 126 MW wind facility that has an annual capacity factor of approximately 24% and failure to perform this test has minimal impact on reliability because of the known intermittent real power supplied by a wind facility. Prior real power capability data was provided to the TP as a by-product NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. Finally, the NYISO operating personnel had awareness of the Entity's real power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Real Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2018019168 | MOD-025-2 | R2 | On February 12, 2018, Noble Weathersfield Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, while preparing for a 2017 audit, the Entity discovered that the facility did not meet the reactive power testing requirements of MOD-025-2 Attachment 1. This noncompliance started on July 1, 2016, the enforcement date of the Standard and Requirement, and ended on November 29, 2017 when the Entity provided the reactive power test data to the Transmission Planner (TP) (NYISO). The root cause of this instance of noncompliance was the failure in the MOD-025 review process that management had in place to timely recognize that the annual market based reactive power testing that is performed through the NYISO program did not fulfill MOD-025 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability. These models and test results feed into the RC/BA/TOP Energy Management System. The Entity is a 126 MW wind facility that has an annual capacity factor of approximately 24% and failure to perform this test has minimal impact on reliability because of the known intermittent reactive power supplied by a wind facility. Prior reactive power capability tests have occurred through the NYISO Voltage Support Services program. The Entity's BA (NYISO) required operating reserves are approximately 2600 MW. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. Finally, the NYISO operating personnel had awareness of the Entity's reactive power capabilities due to testing history. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Reactive Power Capability of the facility, and submitting, within the required 90 days, all testing results to its TP 2) to prevent a recurrence of similar instances of noncompliance: (i) has started using a compliance software program to track the various due date requirements for general Federal, State, Financial covenant requirements as well as all NERC requirements (ii) conducts monthly FERC/NERC calls with a 3rd party NERC consultant that reviews all applicable standards and pending/proposed changes NPCC has verified the completion of all mitigation activity.
2018-05-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Pittsfield Generating Company LP | NCR07195 | NPCC2017018466 | PRC-005-2(i) | R3. | During a Compliance Off-site Audit conducted from July 27, 2017 through October 13, 2017, NPCC determined that Pittsfield Generating Company, LP (the Entity), as a Generator Owner (GO), was in noncompliance with standard PRC-005-2(i) R3. The Entity self-identified an issue associated with battery testing at its single generating plant. Specifically, with regard to Valve Regulated Lead-Acid (VRLA) batteries, the Entity failed to perform measurements of internal ohmic values for individual battery cells at intervals no longer than six calendar months, as required by Table 1-4(b) of the standard. Additionally, with regard to Vented Lead-Acid (VLA) batteries, the Entity could not provide adequate corroborating documentation of specific maintenance activities (station DC supply voltage, electrolyte level, unintentional ground) that are required to be performed at intervals no longer than four calendar months, as required by Table 1-4(a) of the standard. This noncompliance started on October 1, 2015, when the Entity should have been compliant with respect to the aforementioned periodic maintenance activities in accordance with the Standard's implementation plan, and ended on October 9, 2017, when the Entity completed its required testing of VRLA and VLA batteries in the manner described by the Standard and Requirement. The root cause of this instance of noncompliance was the Entity's failure to recognize that the ohmic value of each individual cell of each VRLA battery bank needed to be verified at least every six months. Instead, the Entity believed that continuously monitoring the ohmic value of each VRLA battery bank was sufficient to prove compliance. Additionally, poor documentation was the root cause of the noncompliance associated with VLA batteries' inspection activities above described. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Documentation provided to NPCC shows that the Entity had been testing internal ohmic values of individual VRLA battery cells on 18-month intervals (i.e. less frequently than required by the standard), in conjunction with other periodic maintenance activities. The Entity's noncompliant facility consists of three gas turbines and one steam unit with a combined rated capability of 202 MVA at a 90% power factor. In 2015 and 2016, the four generators, which are operated as one single combined cycle facility, experienced an 18% capacity factor. In 2017, the four generators operated at a capacity factor of approximately 12%. By comparison, the Entity's RC (ISO-NE) required winter operating reserves are approximately 2600 MW. The RC has comparable summer operating reserves requirements. In conclusion, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily for a battery malfunction affecting all four generating units, the RC would have been able to replace the lost capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by completing its required testing of VRLA and VLA batteries in the manner described by the standard/requirement; and 2. To prevent a recurrence of similar instances of noncompliance: a) Created a new preventative maintenance work order to inspect/measure VRLA individual battery cells' ohmic values every six (6) calendar months, and a new 4-month battery inspection form that includes prescriptive details of the maintenance activities prescribed in Table 1-4(a) for VLA batteries. Both work orders are referenced in the recently revised Protection System Maintenance Program internal document. b) Expanded the scope of the existing contract with an outside vendor to perform 6-month measurements of individual cells' internal ohmic values. NPCC has verified the completion of all mitigation activity.
2018-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Armstrong Power, LLC (Armstrong Power) | NCR11760 | RFC2018019386 | VAR-002-4.1 | R2 | On March 6, 2018, Armstrong Power submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with VAR-002-4.1 R2. On December 28, 2017, the entity was experiencing some issues with its equipment. Specifically, the entity suffered a lean blowout trip event and entity personnel were working with the original equipment manufacturer to schedule remote combustion tuning while the voltage dropped under the entity’s assigned voltage schedule. These issues pre-occupied the operator on duty from tending to his normal duties. As a result, the entity went outside of its voltage schedule limits for the following brief periods: (a) From 10:00 AM to 10:15 AM; (b) At 10:50 AM for less than one minute; (c) From 11:10 to 11:15 AM; and (d) At 11:30 AM for less than one minute. The entity notified PJM (their Transmission Operator) and FirstEnergy (their Transmission Owner) at 11:33 AM of these voltage schedule deviations. The entity’s voltage schedule requires the entity to notify PJM and FirstEnergy within 30 minutes of a voltage schedule exceedance. For the first two outages, from 10:00 AM to 10:15 AM and at 10:50 AM for less than one minute, the entity did not notify PJM and FirstEnergy within 30 minutes of the entity’s voltage schedule deviation. In short, the entity notified PJM and FirstEnergy of its voltage schedule deviation approximately one hour late. This noncompliance involves the management practice of workforce management through ineffective training. The entity already has an alarm system in place to alert the operator when the entity deviates from its voltage schedule. The issue here is that the operator did not take the proper action once the alarm sounded due to ineffective training. Even though the operator was distracted, he should have been trained to immediately respond to the alarm as a top priority. That ineffective training is a root cause of this noncompliance. This noncompliance started on December 28, 2017, when the entity deviated from its voltage schedule and did not notify PJM and FirstEnergy within 30 minutes of that deviation and ended on December 28, 2017 when the entity completed its notifications to PJM and FirstEnergy. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is a negative impact on the reliable operation of the BPS by allowing detrimental levels of generator voltage or reactive power output. The risk is minimized because the voltage schedule deviation was small (.5 kV) especially given that the entity’s voltage schedule for the duration of the noncompliance was 526 kV +/- 5 kV. Additionally, the deviations were for a very short amount of time – less than 30 minutes total. The entity operator also quickly identified and corrected this noncompliance by increasing MVAR output to maximum and notifying PJM and FirstEnergy of the deviations. No harm is known to have occurred. ReliabilityFirst considered the entity’s VAR-002-4.1 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) conducted training with the plant personnel concerning the following: (a) NERC standard VAR-002; (b) entity Plant Manager Standing Orders; and (c) the plant specific VAR-002 procedure (BRP NERC VAR-002); and 2) implemented the Plant Managers Standing Orders, the NERC Program document (BRP NERC VAR-002), and an improved daily validation report. ReliabilityFirst has verified the completion of all mitigation activity.
2018-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Troy Energy, LLC (Troy) | NCR11759 | RFC2017018501 | PRC-024-2 | R2 | On October 16, 2017, Troy submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. The entity failed to meet the implementation timeline for PRC-024-2 R2 because several changes in ownership occurred, which delayed a scheduled outage by several months. In 2015, the entity had a vendor come out to assess its frequency and voltage settings for its four units. The resulting report indicated that the entity had to make setting changes to its four units to meet the PRC-024-2 Standard. The entity scheduled and completed the setting changes on two of the four units on October 19, 2016. The entity planned to complete the remaining two units during a scheduled outage on May 9, 2017. However, the plant was sold several times in early and mid-2017, which delayed this scheduled outage. The first sale of the facility was completed by Engie NA to Dynegy Inc. on February 7, 2017. The second sale was completed by Dynegy Inc. to LS Power on July 11, 2017. ReliabilityFirst notes that, as a part of the Engie NA registration, the entity was compliant in having 40% of the setting changes completed by July 1, 2016. But, due to the changing ownership, the entity missed the second interval, due by July 1, 2017. The root cause of this noncompliance was the fact that the outage originally scheduled for May 2017 was delayed for several months due to the various sales of the generating facility. This major contributing factor involves the management practices of grid maintenance, in that the noncompliance arose out of the failure to change settings on pieces of equipment, and planning, in that the noncompliance involved the failure to execute a planned outage. This noncompliance started on July 11, 2017, when the entity was required to have completed 60% of the setting changes and ended on November 29, 2017, when the entity completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although total plant capacity is approximately 936 MVA, the entity generating facility operates at less than a 5% capacity factor. Each of the four generating units are Blackstart Resources and part of the Transmission Operator’s System Restoration Plan. Second, the entity had timely completed the first 50% of setting changes. It was prevented from completing the remainder on time due to the numerous sales of the facility to different owners. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-024 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) installed and tested new settings in Units 2 and 3; and 2) notified PJM as the Planning Coordinator and Transmission Planner of the changes. As an additional step to help prevent recurrence, the entity hired an additional compliance manager to monitor new standards and generally support the compliance program at the entity. ReliabilityFirst has verified the completion of all mitigation activity.
2018-05-31 | SERC Reliability Corporation (SERC) | South Carolina Electric & Gas Company (SCEG) | NCR00915 | SERC2016016193 | PRC-005-1 | R2 | On September 23, 2016, SCEG submitted a Self-Report stating that, as a Transmission Owner (TO), it was in noncompliance with PRC-005-1 R2.1. SCEG did not perform the Protection System maintenance and testing requirements on three relays that were not properly identified as Protection System devices. On July 7, 2016, SCEG employees reviewing plans for an upcoming job at a 115kV substation identified three relays not tagged for maintenance. SCEG determined that the relays were within the scope of PRC-005 and should have maintenance and testing records. SCEG reviewed its PRC-005 maintenance and testing tracking system and determined that there were no maintenance and testing records for the three relays. SCEG also discovered that it omitted the three relays from the original inventory process used to identify PRC-005 components. Prior to the current tracking system, SCEG used a spreadsheet to track maintenance and testing schedules of PRC-005 applicable components. In January of 2010, SCEG transferred the protection system components listed in the spreadsheet to its current tracking system. SCEG did not identify these three relays on the original spreadsheet and therefore did not enter them into the current tracking system. As a result, SCEG has no maintenance and testing records for the three relays. As of March 1, 2018, SCEG has completed a scope assessment of 100 percent of its TO and Generator Owner (GO) PRC-005 devices, with the exception of the physical verification against the drawings for two relays at a nuclear plant, which requires a unit outage to access the relays. This assessment included verification of physical devices against the current drawings, verification that all devices are in the appropriate database, verification that all required maintenance activities under PRC-005-1b/2/6 are in the appropriate database with the correct assigned intervals, and verification of accurate completion documentation of activities as required by PRC-005-1b/2/6 requirements. SCEG has not identified any additional instances of noncompliance as part of this scope assessment. SCEG will complete its review of the two relays at the nuclear plant by December 31, 2018. The cause of this noncompliance was inadequate processes to identify all Protection System devices when developing a database of all Protection System devices subject to PRC-005. This noncompliance started on June 18, 2007, when PRC-005-1 became mandatory and enforceable and SCEG had not performed the required relay maintenance and testing activities on the three relays, and ended on August 26, 2016, when SCEG performed the maintenance and testing on the three relays. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCEG’s failure to perform the maintenance and testing of the Protection System relays could lead to the device not operating as intended, potentially leading to false trips, remote clearing, delayed clearing, the overreach of protective relays or reliance on the interconnecting TO’s Protection System device to respond to a fault. However, the three relays were single-phase bus differential relays protecting a small section of 115 kV bus connected to one of the main 115 kV buses at the station and the high side of two gas turbine step-up transformers, approximately 50 MVA each. If a fault had occurred and one of the faulted phase relays failed to operate, the time-delayed 18-cycle distance elements would have operated at the remote ends. SCEG’s Transmission Planning Department studied various scenarios where the time-delayed relays cleared the fault and determined that an event of this nature would be very similar to the three-phase case evaluated for the FERC Order 754 Single Point of Relay Failure study, which showed minimal system impact. Failure of a single-phase bus differential relay is less severe than the three-phase fault studied in the FERC Order 754 Single Point of Relay Failure study. No harm is known to have occurred. SERC considered SCEG’s PRC-005-1 R2 compliance history in determining the disposition track. SCEG’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID SERC2014014125, and SERC2012010790. SERC determined that SCEG’s PRC-005-1 R2 compliance history should not serve as a basis for applying a penalty. In both SERC2014014125 and SERC2012010790, the scope assessment and mitigating actions addressed PRC-005 components in the SCEG database. The instant noncompliance involved relays that SCEG incorrectly identified as non-PRC-005 relays in its original PRC-005 identification process. Therefore, SCEG did not enter the relays into the database. The scope assessments and mitigation activities for the previous two noncompliance would not have identified or prevented the instant noncompliance. | To mitigate this noncompliance, SCEG: 1) added the three relays to the Protection System database; and 2) performed maintenance and testing on the three relays in accordance with SCEG’s PRC-005 maintenance and testing procedure. To mitigate this noncompliance, SCEG will complete the following mitigation activities by December 31, 2018: 1) conduct an assessment of all TO and GO Protection System components that includes verification of physical devices against the current drawings, verification that all devices are in the appropriate database, verification that all required maintenance activities under PRC-005-1b/6 are in the appropriate database with the correct assigned intervals, and verification of accurate completion documentation of maintenance and testing activities as required by PRC-005-1b/6. As of March 1, 2018, SCEG has completed a scope assessment of 100% of its TO and GO PRC-005 devices, with the exception of the physical verification against the drawings for two relays at a nuclear plant, which requires a unit outage to access the relays. SCEG will complete its review of the two relays at the nuclear plant by December 31, 2018.
2018-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Board Of Public Utilities (Kansas City KS) (BPU) | NCR01061 | SPP2016015825 | PRC-005-2(i) | R3 | During a Compliance Audit conducted June 6, 2016 to June 9, 2016, SPP RE determined that BPU, as a Generator Owner, was in noncompliance with PRC-005-2(i), R3. The BPU Protection System Maintenance Program (PSMP) requires that checks for battery system unintentional grounds be performed every four months and documented in its work order system. BPU could not provide evidence that it performed the required checks for unintentional grounds for its four generation facility battery banks. This noncompliance started on October 1, 2015, the date the four calendar month inspection for unintentional grounds of Table 1-4(a) in PRC-005-2(i) became enforceable under the PRC-005-2(i) Implementation Plan, and ended on November 4, 2016, the date BPU completed its mitigation of the noncompliance. The root cause of this noncompliance was ineffective internal controls to ensure protection system maintenance and testing was being documented in accordance with the BPU PSMP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. The failure to adequately test station batteries increases the risk that the batteries will be unable to supply the required Direct Current (DC) power when necessary. The partial or complete loss of DC power can potentially render protection systems inoperable, further aggravating system events; cause system operators to lose system awareness, and result in equipment damage. BPU states that it was performing the checks for generator battery system unintentional grounds but failed to include documentation of the check for unintentional grounds on its work orders. No harm is known to have occurred. A Settlement Agreement covering violation of PRC-005-1 R2, R2.1, and R2.2 (SPP2013011830) was filed with FERC under NP16-6-000 on December 30, 2015. On January 29, 2016, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Between February 25, 2010, and September 26, 2013, 254 of the 1,279, or 19.8% of BPU’s protection system devices were not maintained or tested according to the intervals prescribed in BPU’s PSMP. The protection system devices not maintained or tested within the prescribed intervals included 91 DC control circuits, 19 current and potential transformers, 99 protective relays, 25 communications devices, and 20 battery banks. Although the prior violation of PRC-005-1 included BPU’s failure to maintain its battery banks, the SPP RE has determined that the instant violation is eligible for compliance exception disposition because it involves BPU’s failure to adequately document tasks in its PSMP resulting from the implementation of PRC-005-2(i). | To mitigate its noncompliance with PRC-005-2(i)i R3, BPU: 1. Updated the "KCBPU Stationary Battery System Visual and Mechanical Inspection Checklist" form that is used to document the required visual and mechanical inspections for batteries; 2. Updated the work orders for Nearman and Quindaro to reflect the missing line items for checking for unintentional grounds; and 3. Completed checks for unintentional grounds for each of the four BPU Bulk Electric System generating units (Nearman Unit #1 N1, Nearman combustion Turbine #4 CT4, Quindaro Unit #2 Q2 and Quindaro Combustion Turbine #3 CT3). SPP RE has verified the completion of all mitigation activity.
2018-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (Chisholm) | NCR11291 | SPP2017017049 | VAR-002-4 | R2 | On February 22, 2017, Chisholm View Wind Project, LLC (Chisholm) submitted a Self-Certification stating that, as a Generator Operator (GOP) it was not compliant with VAR-002-4 R2. On January 9, 2017, at 9:16 a.m. Oklahoma Gas and Electric, Chisholm’s Transmission Operator (TOP), notified Chisholm that it was operating at 356 kV, 4.2 kV above the TOP’s Winter Voltage Schedule high limit of 351.8 kV. Chisholm subsequently determined that on December 12, 2016, at 5:16 p.m., during the commission testing of the Chisholm View II facility, a contractor mistakenly entered 352.0 kV and not 342.0 kV as the generator voltage set point in the facility Voltage Controller. Chisholm and Chisholm View II share the same generator interconnection and Voltage Controller. At the time of the generator voltage set point error, voltage alarms had not been enabled for Chisholm in the Enel Green Power North America Control Center, i.e., the generator control room for Chisholm. The duration of this instance of noncompliance was from December 12, 2016, the date the contractor entered an incorrect set point in the Voltage Controller at Chisholm, through January 9, 2017, the date the correct set point was entered in the Chisholm Voltage Controller. The root cause of this instance of noncompliance was a combination of lack of controls to ensure contractors do not make incorrect changes to control system settings and failure to enable voltage alarms for Chisholm at the Enel Green Power North America Control Center. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to maintain the TOP’s voltage schedule has the potential to affect the reliability of the BPS by causing system voltage to deviate from acceptable levels. Here the risk to the BPS is minimal because Chisholm has limited VAR capability, +/- 60 to +/- 120 MVAR and voltage at its point of interconnection is generally beyond Chisholm’s control. Notwithstanding operating at its maximum VAR capability, system conditions frequently cause the voltage at Chisolm’s point of interconnection to be outside the TOP’s voltage schedule. The set point error entered in Chisholm’s voltage controller on December 12, 2016, resulted in a less than 1 kV change in the voltage at Chisholm’s point of interconnection. Both before and after the set point change, the voltage at the point of interconnection exceeded the TOP voltage schedule. When the voltage controller set point error was corrected on January 9, 2017, the voltage at Chisholm’s point of interconnection changed 8.4 kV but remained 1.8 kV outside the TOP’s voltage schedule due to system conditions. Chisholm is a 235 MW wind-powered generating facility. No harm is known to have occurred as a result of this noncompliance. Chisholm has no relevant prior violations of VAR-002-4 R2 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, Chisholm: 1) changed the template for vendor contracts to require contractors to receive approval from the Enel Green Power Control Center for changes to generator control systems ; 2) enabled voltage alarms for the Chisholm point of interconnection voltage; 3) enabled alarms for changes between the Winter and Summer voltage schedule; 4) added notes to the voltage alarms regarding the voltage schedule requirements; and 5) amended the Substation Shutdown/Startup Procedure to ensure correct settings are not altered during the commissioning process. SPP RE has verified the completion of all mitigation activity.
2018-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Cleco Corporate Holdings LLC (Cleco) | NCR01083 | SPP2017018448 | VAR-002-4 | R1 | On October 11, 2017, Cleco submitted a Self-Report stating that, as a Generator Operator it was not compliant with VAR-002-4 R1 because the Nesbitt Unit #1 (Unit #1) generator’s Automatic Voltage Regulator (AVR) switched to manual mode during startup and Cleco did not inform its Transmission Operator (TOP) of the change. During startup of Unit #1 on September 18, 2017, the operating staff supervisor (OS supervisor) made multiple unsuccessful attempts to adjust generator voltage with the generator AVR in both automatic and manual control mode. Following multiple AVR panel resets, generator synchronization voltage was achieved. The OS supervisor placed the AVR in automatic control mode and verified the AVR was in automatic control mode on the operator control board. Subsequently, Unit #1 was brought online and released to dispatch control at 8:58 a.m. On September 19, 2017, at 12:00 p.m., the Unit #1 shift supervisor discovered that although the AVR selector switch was in automatic control mode, the indicating light on the operator control board showed the AVR to be in manual control mode. The shift supervisor confirmed that the voltage regulator was in manual control mode at the AVR control panel. After further investigation, Cleco discovered that the AVR automatically switched from automatic to manual control mode when Unit 1 synchronized to the grid on September 18, 2017. At approximately 1 p.m., the shift supervisor notified the Cleco Transmission Operations Center (CTOC) that Unit #1’s AVR had been in manual control mode since Unit #1 came online on September 18, 2017. This noncompliance started on September 18, 2017 at 5:36 a.m., when Unit #1 operators should have notified the CTOC that the AVR was in manual control mode, and ended on September 19, 2017 at 1:00 p.m., when the Unit #1 shift supervisor notified the CTOC that the AVR was in manual control mode. The root cause of this noncompliance was insufficient controls to ensure the AVR was in automatic control mode following Unit 1 startup. Cleco did not have a step in its operator checklist for the plant operator to verify the AVR status once Unit #1 came online. Additionally, Cleco did not have its Digital Control System (DCS) programmed to alarm if the AVR was not operating in automatic voltage control mode. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with VAR-002-4 R1 has the potential to affect the reliability of the BPS by preventing a generating facility from responding automatically to system voltage excursions, which could limit the TOP’s ability to recover from system voltage events. Notwithstanding, the actual risk was minimal because Unit #1 AVR was in manual mode for a short duration and two of the three Cleco generating units (Rodemacher #2, and Madison #3) that were online during the noncompliance had their AVRs in automatic control mode and would have responded to system voltage events. Additionally, Unit #1 did not deviate from its voltage schedule and no system voltage events occurred while the Unit #1 AVR was in manual control mode. No harm is known to have occurred. Cleco has no relevant prior violations of VAR-002-4 R1 or any other standards that are similar in nature. | To mitigate this noncompliance, Cleco: 1) called the CTOC to tell the system operator that the Unit #1 AVR was operating in manual mode; 2) installed new alarms to indicate to COTC and generator operators when a unit is online and the AVR is not in automatic control mode; 3) added new display features that makes it easier for generator operators to recognize when the AVR is not operating in automatic mode; 4) updated the operator startup checklist to include a step for generator operators to check the AVR status; and, 5) sent a written reminder to operations personnel of the 30 minute reporting requirement to notify the CTOC when an AVR is not operating in automatic control mode. SPP RE has verified the completion of all mitigation activity.
2018-05-31 | Southwest Power Pool Regional Entity (SPP RE) | EASTMAN Cogeneration Limited Partnership (EASTMAN) | NCR01092 | SPP2016015921 | PRC-019-2 | R1; R1.1, R1.1.1, R1.1.2 | On July 21, 2016, EASTMAN submitted a Self-Report stating that, as a Generator Owner, it was not compliant with PRC-019-2 R1, R1.1, R1.1.1, and R1.1.2. EASTMAN did not perform the required coordination study to verify (R.1.1) that its in-service limiters are set to operate before its protection systems (R1.1.1), and its protection system devices are set to operate to limit the extent of damage when operating conditions exceed equipment capabilities (R1.1.2). On June 13, 2016, EASTMAN initiated a generation coordination study, but the settings for the in-service limiters in the excitation system were not available. On that same day, EASTMAN contacted the original equipment manufacturer (OEM) to get the settings for the in-service limiters in the excitation system. On July 11, 2016, the OEM provided the requested settings data. As a result, EASTMAN was not able to verify coordination of all voltage regulating system controls with the applicable equipment capabilities by the standard effective date of July 1, 2016. The root cause of this issue of noncompliance was lack of managerial oversight to ensure all data needed for the coordination study was available to conduct the study prior to the effective date of the standard, July 1, 2016. The noncompliance started on July 1, 2016, the effective date of the standard, and ended on December 21, 2017, the date EASTMAN completed the coordination studies of the voltage regulating system controls, (including in-service limiters and protection functions) with the equipment capabilities and settings of the applicable Protection System devices and functions according to PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly coordinate exciter limiters and generator protection relays can cause the generator AVR to impose unacceptable operating conditions on the generator. Such conditions, i.e. overexcitation and underexcitation, have the potential to affect the reliability of the BPS by decreasing the generator’s ability to withstand system voltage events and increasing the probability of generator trips due to loss of synchronism and generator field overloads. Notwithstanding, EASTMAN attested that its generation facility has operated with the current setting of the limiters and protective devices without experiencing any automatic voltage regulator, excitation system, or PRC-019 related issues since its 2001 commissioning. Additionally, EASTMAN Chemical manufacturing facility consumes 200 MW of the available generation from its cogeneration facility, leaving only 268 MW going to the bulk electric system. No harm is known to have occurred. EASTMAN has no relevant prior violations of PRC-019-2 R1 or any other standards that are similar in nature. | To mitigate this noncompliance, EASTMAN: 1) completed a coordination study of the voltage regulating system controls, (including in-service limiters and protection functions) with the equipment capabilities and settings of the applicable Protection System devices; to 100% completion; 2) developed an action item in its tracking system (Mainsaver) that assigns responsibility, identifies actions, monitors status (notifications), and tracks studies and verifications to completion on a five year frequency; and 3) reviewed and trained appropriate staff on corrective actions regarding PRC-019-2. SPP RE has verified the completion of these mitigation activities.
2018-05-31 | Southwest Power Pool Regional Entity (SPP RE) | EASTMAN Cogeneration Limited Partnership (EASTMAN) | NCR01092 | SPP2016016119 | PRC-005-2 | R1; R1.1, R1.2 | During a Compliance Audit conducted from September 7, 2016 through September 8, 2016, SPP RE determined that EASTMAN, as a Generator Owner (GO), had an issue of noncompliance with PRC-005-2 R1. EASTMAN’s Protection System Maintenance Program (PSMP) did not have time based intervals consistent with the PRC-005-2 and PRC-005-6 tables. Specifically, prior to March 29, 2016, communication system device maintenance intervals were not in the PSMP and battery maintenance intervals exceeded the defined intervals in the Standard. Additionally, prior to March 29, 2016, EASTMAN’s PSMP did not include sudden pressure relays as required in PRC-005-6, which became enforceable on January 1, 2016. These issues of noncompliance affected 16 of EASTMAN's 210 (7.6%) protection system devices. The duration of this instance of noncompliance was from April 1, 2015, the effective date of PRC-005-2, through August 25, 2016, the date EASTMAN completed mitigation. The root cause of this instance of noncompliance was that EASTMAN had not implemented in its Internal Compliance Program (ICP) steps to interpret and train staff on the Reliability Standards and did not have a process in place to monitor changes to the Reliability Standards. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to test and maintain protection system equipment has the potential to affect the reliability of the BPS by increasing the risk of protection system misoperations, cascading outages, and equipment failure. Notwithstanding, EASTMAN is up to date on its four month battery tests as required by PRC-005-2 Table 1-4(a) and the batteries were functioning properly at the time of the tests. Additionally, the 16 Protection System devices had no known failures during the time of noncompliance and the devices omitted from EASTMAN's PSMP only represented 7.6% of EASTMAN’s total Protection System devices. No harm is known to have occurred. EASTMAN has no relevant prior violations for PRC-005-2 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this noncompliance, EASTMAN: 1) created a new PSMP that complied with PRC-005-6 by including sudden pressure relays and the appropriate time based intervals for batteries and communication systems; 2) developed an assessment process to review changes made to NERC reliability standards; 3) modified its internal compliance program to interpret changes to the Standards and train applicable individuals on these changes; and 4) scheduled recurring training on NERC Standards. SPP RE has verified the completion of all mitigation activity.
2018-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Eastman Cogeneration Limited Partnership (Eastman) | NCR01092 | SPP2016016117 | FAC-009-1 | R1 | During a Compliance Audit conducted from September 7, 2016 through September 8, 2016, SPP RE determined that EASTMAN, as a Generator Owner (GO), had an issue of noncompliance with FAC-009-1 R1 because Eastman did not establish Facility Ratings that were consistent with its Facility Rating Methodology (FRM). Eastman’s FRM establishes the boundary for generator facility ratings as from the generator to the high-side of the main step-up transformer. The boundary for transformer facility ratings is from the high side of the main step-up transformer to the point of interconnection. Eastman failed to rate its generator and transformer facilities independently as required by its FRM and in doing so, failed to identify the most limiting element for its transformer facilities. Additionally, Eastman failed to include the ratings for two elements, a conductor and jumper, in the transformer facility rating for the North Texas Eastman interconnection. The duration of this instance of noncompliance was from December 16, 2011, the day after completion of mitigation for a prior violation, through March 16, 2017, the date EASTMAN revised its FRM and spreadsheet to comply with FAC-009-1. The root cause of this instance of noncompliance was a combination of human error and lack of internal controls. EASTMAN’s Internal Compliance Manager incorrectly applied the facility boundaries in its FRM and there was no verification process in place. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Eastman’s failure to develop Facility Ratings consistent with its FRM could have resulted in errors in the planning and operational models utilized by the Transmission Operator, Reliability Coordinator, and Planning Authority and could have led to equipment damage, unplanned outages, or reduced equipment lifetimes. Here, the risk to the BPS is mitigated because notwithstanding EASTMAN’s failure to rate its generator and transformer facilities independently and include a conductor and jumper in its transformer facility rating, the combined rating of its generator and transformer facilities did not change. No harm is known to have occurred. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including EASTMAN’s noncompliance with FAC-009-1 R1 (SPP201000295) was filed with FERC under RC12-10-00 on March 30, 2012. The 60-day review period passed on April 29, 2012. SPP RE considered EASTMAN’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment because although the two instances of noncompliance were of the same Standard and Requirement, the underlying conduct of the two instances was different. The prior violation was related to not having Facility Ratings for its facilities, while the instant noncompliance was related to failing to include all elements and failing to following its FRM. | To mitigate this minimal risk instance of noncompliance, EASTMAN: 1) added the missing elements and rated them on separate Facility Ratings spreadsheets; 2) revised its FRM to ensure compatibility and consistency with the new Standard by comparison reviews; 3) trained applicable individuals on the revised FRM; and, 4) issued the definition of “facility” found in the Standard to individuals who perform the facility ratings. SPP RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IA, LLC (LVWIA) | NCR11267 | TRE2017017265 | PRC-019-2 | R1 | On March 21, 2017, LVWIA submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. In particular, LVWIA did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its wind generation Facility by July 1, 2016 as required. Following discussions with Texas RE and other regulated entities in early 2017, LVWIA determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, LVWIA engaged a third-party contractor to perform a voltage coordination verification study for its Facility. LVWIA’s contractor completed the requisite voltage coordination verifications for LVWIA’s single wind generation Facility on September 8, 2017, ending the issue. The root cause of this noncompliance was a misunderstanding of the required date for LVWIA to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, LVWIA mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on September 8, 2017, when LVWIA verified the coordination of its voltage and generation protection settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, when LVWIA performed the required voltage and generation protection verifications through a coordination study, the study confirmed that no changes were required to its voltage controls and generation protection settings. Second, during the period of noncompliance, LVWIA contributed an average of only 71 MW to the grid and operated at approximately a 36% capacity factor. Finally, when LVWIA operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered LVWIA’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIA: 1) verified the coordination of its voltage controls and generation protection devices; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 3) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 4) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IB, LLC (LVWIB) | NCR11266 | TRE2017017269 | PRC-019-2 | R1 | On March 21, 2017, LVWIB submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. In particular, LVWIB did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its wind generation Facility by July 1, 2016 as required. Following discussions with Texas RE and other regulated entities in early 2017, LVWIB determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, LVWIB engaged a third-party contractor to perform a voltage coordination verification study for its Facility. LVWIB’s contractor completed the requisite voltage coordination verifications for LVWIB’s single wind generation Facility on September 8, 2017, ending the issue. The root cause of this noncompliance was a misunderstanding of the required date for LVWIB to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, LVWIB mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on September 8, 2017, when LVWIB verified the coordination of its voltage and generation protection settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, when LVWIB performed the required voltage and generation protection verifications through a coordination study, the study confirmed that no changes were required to its voltage controls and generation protection settings. Second, during the period of noncompliance, LVWIB contributed an average of only 64 MW to the grid and operated at approximately a 32% capacity factor. Finally , when LVWIB operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered LVWIB’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIB: 1) verified the coordination of its voltage controls and generation protection devices; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 3) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 4) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower III, LLC (LVWPIII) | NCR11538 | TRE2017017273 | PRC-019-2 | R1 | On March 21, 2017, LVWPIII submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. In particular, LVWPIII did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its wind generation Facility by July 1, 2016 as required. Following discussions with Texas RE and other regulated entities in early 2017, LVWPIII determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, LVWPIII engaged a third-party contractor to perform a voltage coordination verification study for its Facility. LVWPIII’s contractor completed the initial voltage coordination verifications for LVWPIII’s single wind generation Facility on August 25, 2017. However, the study included a possible typo in the wind turbine manufacturer given frequency limits. LVWPIII then re-performed its coordination study on November 21, 2017, which verified the coordination of its voltage and generation protection settings as required by PRC-019-2 R1. The root cause of this noncompliance was a misunderstanding of the required date for LVWPIII to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, LVWPIII mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on November 21, 2017, when LVWPIII verified the coordination of its voltage and generation protection settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, when LVWPIII performed the required voltage and generation protection verifications through a coordination study, the study confirmed that no changes were required to its voltage controls and generation protection settings. Second, during the period of noncompliance, LVWPIII contributed an average of only 74 MW to the grid and operated at approximately a 37% capacity factor. Finally, when LVWPIII operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered LVWPIII’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWPIII: 1) verified the coordination of its voltage controls and generation protection devices; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 3) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 4) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IV, LLC (LVIV) | NCR11635 | TRE2017017274 | PRC-019-2 | R1 | On March 21, 2017, LVIV submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. In particular, LVIV did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its wind generation Facility by July 1, 2016 as required. Following discussions with Texas RE and other regulated entities in early 2017, LVIV determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, LVIV engaged a third-party contractor to perform a voltage coordination verification study for its Facility. LVIV’s contractor completed the required coordination study on November 22, 2017. In doing so, LVIV determined that its under and overvoltage protection system settings were not coordinated with in-service limiters. On November 29, 2017, LVIV completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for LVIV to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, LVIV mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on November 29, 2017, when LVIV updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, although LVIV’s voltage protective system settings required adjustment, LVIV’s settings were set to operate too early. In particular, LVIV adjusted its undervoltage protective relay settings downward 0.21 pu. LVIV likewise adjusted its overvoltage protective relay settings upwards by 0.1 pu to ensure proper coordination with its in-service limiters. Given the nature of these changes, there was little risk the single generating unit at issue would experience significant equipment damage and, correspondingly, an extended outage. Second, during the period of noncompliance, LVIV contributed an average of only 75 MW to the grid and operated at approximately a 37% capacity factor. Finally, when LVIV operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered LVIV’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVIV: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower V, LLC (LVWV) | NCR11603 | TRE2017017276 | PRC-019-2 | R1 | On March 21, 2017, LVWV submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. In particular, LVWV did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its wind generation Facility by July 1, 2016 as required. Following discussions with Texas RE and other regulated entities in early 2017, LVWV determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, LVWV engaged a third-party contractor to perform a voltage coordination verification study for its Facility. LVWV’s contractor completed the required coordination study on November 21, 2017. In doing so, LVWV determined that its under and overvoltage protection system settings were not coordinated with in-service limiters. On November 30, 2017, LVWV completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for LVWV to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, LVWV mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on November 30, 2017, when LVWV updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, although LVWV’s voltage protective system settings required adjustment, LVWV’s settings were set to operate too early. In particular, LVWV adjusted its undervoltage protective relay settings downward 0.06 pu. LVWV likewise adjusted its overvoltage protective relay settings upwards by 0.11 pu to ensure proper coordination with its in-service limiters. Given the nature of these changes, there was little risk the single generating unit at issue would experience significant equipment damage and, correspondingly, an extended outage. Second, during the period of noncompliance, LVWV contributed an average of only 42 MW to the grid and operated at approximately a 38% capacity factor. Finally, when LVWV operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered LVWV’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWV: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Mesquite Creek Wind LLC (MCW) | NCR11511 | TRE2017017262 | PRC-019-2 | R1 | On March 21, 2017, MCW submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. In particular, MCW did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its wind generation Facility by July 1, 2016 as required. Following discussions with Texas RE and other regulated entities in early 2017, MCW determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, MCW engaged a third-party contractor to perform a voltage coordination verification study for its Facility. MCW’s contractor completed the requisite voltage coordination verifications for MCW’s single wind generation Facility on August 2, 2017, ending the issue. The root cause of this noncompliance was a misunderstanding of the required date for MCW to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, MCW mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on August 2, 2017, when MCW verified the coordination of its voltage and generation protection settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, when MCW performed the required voltage and generation protection verifications through a coordination study, the study confirmed that no changes were required to its voltage controls and generation protection settings. Second, during the period of noncompliance, MCW contributed an average of only 78 MW to the grid and operated at approximately a 37% capacity factor. Finally, when MCW operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered MCW’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, MCW: 1) verified the coordination of its voltage controls and generation protection devices; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 3) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 4) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | NAES Corporation - Quail Run Energy Center (NCQREC) | NCR11508 | TRE2017018898 | TOP-003-3 | R5 | On December 27, 2017, NCQREC submitted a Self-Report stating that, as a Generator Operator (GOP), it was in noncompliance with TOP-003-3 R5. According to NCQREC, it failed to provide data to its Transmission Operator (TOP) in accordance with its TOP's documented specifications. On August 4, 2017, NCQREC’s TOP informed NCQREC personnel that it was not receiving Real-time data from the NCQREC generation Facility’s Remote Terminal Unit (RTU). NCQREC began an investigation into the issue and determined that the communications link between its RTU and the TOP’s RTU was not functioning. On March 7, 2018, NCQREC restored the communications link with its TOP, ending the issue. The root cause of this noncompliance was that NCQREC did not have a process to ensure that the TOP was receiving all specified data from its Facility. In particular, NCQREC did not have a process to periodically verify that the TOP received all data specified in its data specification. This noncompliance started on April 1, 2017, when TOP-003-3 R5 became mandatory and enforceable, and ended on March 7, 2018, when NCQREC restored the communication line and began providing Real-time data to its TOP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, throughout the issue duration, the TOP in question continued to receive Real-time data for the NCQREC generation Facility at issue from the TOP’s metering and monitoring equipment, reducing the risk that the TOP would be unaware of any line overloading or other operational issues. Second, NCQREC continued to provide required Real-time data to its Reliability Coordinator (RC) throughout the issue duration. Pursuant to the 2017 Electric Reliability Council of Texas (ERCOT) TOP Coordinated Functional Registration (CFR) matrix, the regional RC has assumed sole responsibility for performing required Real-time Assessments and Operational Planning Analysis. As a result, the RC would have had the information necessary to identify and address any Real-time contingency or loading issues had they occurred. No harm is known to have occurred. Texas RE considered NCQREC’s and its affiliate’s compliance history and determined there were no relevant instances of noncompliance related to TOP-003-3 R5. | To mitigate this noncompliance, NCQREC: 1) installed a new communications link with its TOP; 2) verified with its TOP that the required data is being received; 3) established a process that requires NCQREC personnel perform a monthly verification that NCQREC’s TOP is receiving all specified data as scheduled; 4) updated its list of Applicable Standards and Internal Controls to include an annual verification of communication with its TOP and RC; and 5) documented the network drawing of the communication system to enhance internal visibility regarding the communications link with its TOP in case of future issues. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2017017257 | PRC-019-2 | R1 | On March 21, 2017, NWLP submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. In particular, NWLP did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its wind generation Facility by July 1, 2016 as required. Following discussions with Texas RE and other regulated entities in early 2017, NWLP determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, NWLP engaged a third-party contractor to perform a voltage coordination verification study for its Facility. NWLP’s contractor completed the requisite voltage coordination verifications for NWLP’s single wind generation Facility on October 16, 2017, ending the issue. The root cause of this noncompliance was a misunderstanding of the required date for NWLP to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, NWLP mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on October 16, 2017, when NWLP verified the coordination of its voltage and generation protection settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, when NWLP performed the required voltage and generation protection verifications through a coordination study, the study confirmed that no changes were required to its voltage controls and generation protection settings. Second, during the period of noncompliance, NWLP contributed an average of only 48 MW to the grid and operated at approximately a 31% capacity factor. Finally, when NWLP operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered NWLP’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, NWLP: 1) verified the coordination of its voltage controls and generation protection devices; 2) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 3) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 4) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018019652 | PRC-019-2 | R1 | On March 21, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify the coordination of their respective voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions by July 1, 2016. Subsequently, on May 9, 2018, Texas RE determined that all issues described in the original self-report applied to Conetoe II Solar, LLC (Conetoe) as a GO in the SERC Reliability Corporation (SERC) region under NCR11622. Accordingly, Texas RE is processing this PRC-019-2 R1 issue for Conetoe likewise under Notrees Windpower, LP. Following discussions with Texas RE and other regulated entities in early 2017, Conetoe determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single solar generation Facility. Following this discovery, Conetoe engaged a third-party contractor to perform a voltage coordination verification study for its Facility. Conetoe completed its coordination study on April 4, 2017, which identified voltage protection system settings that were not coordinated with in-service limiters. On June 6, 2017, Conetoe completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for Conetoe to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, Conetoe mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on June 6, 2017, when Conetoe updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, Conetoe’s voltage protective system settings were set to operate at the same time as its in-service limiters. To address the issue, Conetoe adjusted its undervoltage protective relay settings downward 0.025pu and delayed their operation by 0.1 seconds. Conetoe likewise adjusted its overvoltage protective relay settings upwards 0.025pu and also delayed their operation by 0.1 seconds. Given the nature of these changes, there was little risk the single generating unit at issue would experience significant equipment damage and, correspondingly, an extended outage. Second, during the period of noncompliance, Conetoe contributed an average of only 19 MW to the grid and operated at approximately a 24% capacity factor. Finally, when Conetoe operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered Conetoe’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Conetoe: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018019653 | PRC-019-2 | R1 | On March 21, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify the coordination of their respective voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions by July 1, 2016. Subsequently, on May 9, 2018, Texas RE determined that all issues described in the original self-report applied to Frontier Windpower, LLC (Frontier) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11692. Accordingly, Texas RE is processing this PRC-019-2 R1 issue for Frontier likewise under Notrees Windpower, LP. Following discussions with Texas RE and other regulated entities in early 2017, Frontier determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, Frontier engaged a third-party contractor to perform a voltage coordination verification study for its Facility. Frontier completed its coordination study on August 28, 2017, which identified voltage protection system settings that were not coordinated with in-service limiters. On October 5, 2017, Frontier completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for Frontier to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, Frontier mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on October 5, 2017, when Frontier updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, although Frontier’s voltage protection system settings required adjustment, Frontier’s settings were set to operate to early. In particular, Frontier’s undervoltage protection systems were adjusted by delaying the operation 8.25 seconds at a 0.75pu voltage level. Frontier likewise adjusted its overvoltage protective relay settings upwards by 0.20pu at a 0.4 second time delay and 0.10pu at a two second time delay to ensure proper coordination with its in-service limiters. Given the nature of these changes, there was little risk the single generating unit at issue would experience significant equipment damage and, correspondingly, an extended outage. Second, during the period of noncompliance, Frontier contributed an average of only 74 MW to the grid and operated at approximately a 37% capacity factor. Finally, when Frontier operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered Frontier’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Frontier: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018019654 | PRC-019-2 | R1 | On March 21, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify the coordination of their respective voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions by July 1, 2016. Subsequently, on May 9, 2018, Texas RE determined that all issues described in the original self-report applied to Ironwood Windpower, LLC (Ironwood) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11257. Accordingly, Texas RE is processing this PRC-019-2 R1 issue for Ironwood likewise under Notrees Windpower, LP. Following discussions with Texas RE and other regulated entities in early 2017, Ironwood determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, Ironwood engaged a third-party contractor to perform a voltage coordination verification study for its Facility. Ironwood completed its coordination study on August 1, 2017, which identified voltage protection system settings that were not coordinated with in-service limiters. On September 19, 2017, Ironwood completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for Ironwood to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, Ironwood mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on September 19, 2017, when Ironwood updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, although Ironwood’s voltage protection system settings required adjustment, Ironwood’s applicable settings were set to operate too early. In particular, the undervoltage protection system settings in question were set to operate 1.6 seconds too early at a 0.65pu voltage level. Correspondingly, Ironwood adjusted the undervoltage relay settings downward 0.10pu at an 11.5 second time delay to ensure proper coordination. Additionally, Ironwood adjusted its overvoltage protection system settings upwards by 0.05pu to ensure proper coordination with its in-service limiters. Given the nature of these changes, there was little risk the single generating unit at issue would experience significant equipment damage and an extended outage. Second, during the period of noncompliance, Ironwood contributed an average of only 7 MW to the grid and operated at approximately a 4% capacity factor. Finally, when Ironwood operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered Ironwood’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Ironwood: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018019655 | PRC-019-2 | R1 | On March 21, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify the coordination of their respective voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions by July 1, 2016. Subsequently, on May 9, 2018, Texas RE determined that all issues described in the original self-report applied to Cimarron Wind Power II, LLC (Cimarron) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11240. Accordingly, Texas RE is processing this PRC-019-2 R1 issue for Cimarron likewise under Notrees Windpower, LP. Following discussions with Texas RE and other regulated entities in early 2017, Cimarron determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, Cimarron engaged a third-party contractor to perform a voltage coordination verification study for its Facility. Cimarron completed its coordination study on August 1, 2017, which identified voltage protection system settings that were not coordinated with in-service limiters. On September 12, 2017, Cimarron completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for Cimarron to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, Cimarron mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on September 12, 2017, when Cimarron updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, although Cimarron’s voltage protection system settings required adjustment, Cimarron’s settings were set to operate too early. In particular, the undervoltage protection systems in question were set to operate two seconds earlier than the corresponding in-service limiters at a 0.65pu voltage level. Cimarron also adjusted the undervoltage relay settings downward 0.10pu at an 11.5 second time delay to ensure proper coordination. Cimarron likewise adjusted its overvoltage protective relay settings upwards by 0.05pu to ensure proper coordination with its in-service limiters. Given the nature of these changes, there was little risk the single generating unit at issue would experience significant equipment damage and, correspondingly, an extended outage. Second, during the period of noncompliance, Cimarron contributed an average of only 61 MW to the grid and operated at approximately a 46% capacity factor. Finally, when Cimarron operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered Cimarron’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Cimarron: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018019656 | PRC-019-2 | R1 | On March 21, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify the coordination of their respective voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions by July 1, 2016. Subsequently, on May 9, 2018, Texas RE determined that all issues described in the original self-report applied to Three Buttes Windpower, LLC (Three Buttes) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR10345. Accordingly, Texas RE is processing this PRC-019-2 R1 issue for Three Buttes likewise under Notrees Windpower, LP. Following discussions with Texas RE and other regulated entities in early 2017, Three Buttes determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, Three Buttes engaged a third-party contractor to perform a voltage coordination verification study for its Facility. Three Buttes completed its coordination study on July 7, 2017, which identified voltage protection system settings that were not coordinated with in-service limiters. On July 17, 2017, Three Buttes completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for Three Buttes to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, Three Buttes mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on July 17, 2017, when Three Buttes updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, although Three Buttes undervoltage protection system settings required adjustment, Three Butte’s undervoltage settings were set to operate too early. In particular, Three Buttes adjusted its undervoltage protection system settings by delaying protection system operations at 0.65pu by two seconds and at 0.8pu by eight seconds. Second, during the period of noncompliance, Three Buttes contributed an average of only 36 MW to the grid and operated at approximately a 37% capacity factor. Finally, when Three Buttes operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered Three Buttes’ and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Three Buttes: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NWLP) | NCR10276 | TRE2018019657 | PRC-019-2 | R1 | On March 21, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify the coordination of their respective voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions by July 1, 2016. Subsequently, on May 9, 2018, Texas RE determined that all issues described in the original self-report applied to Top of the World Wind Energy, LLC (TOW) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR11090. Accordingly, Texas RE is processing this PRC-019-2 R1 issue for TOW likewise under Notrees Windpower, LP. Following discussions with Texas RE and other regulated entities in early 2017, TOW determined that it failed to verify the coordination of its voltage controls and generation protection devices in accordance with PRC-019-2 R1 by the July 1, 2016 deadline for its single wind generation Facility. Following this discovery, TOW engaged a third-party contractor to perform a voltage coordination verification study for its Facility. TOW completed its coordination study on July 7, 2017, which identified voltage protection system settings that were not coordinated with in-service limiters. On July 25, 2017, TOW completed all required setting changes, ending the noncompliance. The root cause of this noncompliance was a misunderstanding of the required date for TOW to complete the initial voltage coordination verifications specified in PRC-019-2. In particular, TOW mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required voltage coordination verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. This noncompliance started on July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, and ended on July 25, 2017, when TOW updated its voltage protection system settings in accordance with PRC-019-2 R1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, although TOW’s voltage protection system settings required adjustment, TOW’s settings were set to operate too early. In particular, the undervoltage protection systems in question were set to operate 1.2 seconds earlier than the corresponding in-service limiters at a 0.65pu voltage level. TOW also adjusted the undervoltage relay settings downward 0.10pu at an 11 second time delay to ensure proper coordination. TOW likewise adjusted its overvoltage protective relay settings upwards by 0.05pu to ensure proper coordination with its in-service limiters. Given the nature of these changes, there was little risk the single generating unit at issue would experience significant equipment damage and, correspondingly, an extended outage. Second, during the period of noncompliance, TOW contributed an average of only 69 MW to the grid and operated at approximately a 34% capacity factor. Finally, when TOW operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm is known to have occurred. Texas RE considered TOW’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, TOW: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) updated its voltage protection system settings in accordance with PRC-019-2 R1; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform periodic generator verifications, including reviews when changes occur at its Facility, to ensure voltage controls and generation protection devices remain properly coordinated; and 5) created automatic reminders that notify applicable staff members when to perform the next coordination study. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | Quail Run Energy Partners, LP (QREP) | NCR11525 | TRE2017018897 | TOP-003-3 | R5 | On December 21, 2017, QREP submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with TOP-003-3 R5. According to QREP, it failed to provide data to its Transmission Operator (TOP) in accordance with its TOP's documented specifications. On August 4, 2017, QREP’s TOP informed applicable personnel that it was not receiving Real-time data from the QREP generation Facility’s Remote Terminal Unit (RTU). QREP began an investigation into the issue and determined that the communications link between its RTU and the TOP’s RTU was not functioning. On March 7, 2018, QREP restored the communications link with its TOP, ending the issue. The root cause of this noncompliance was that QREP did not have a process to ensure that the TOP was receiving all specified data from its Facility. In particular, QREP did not have a process to periodically verify that the TOP is receiving all data specified in its data specification. This noncompliance started on April 1, 2017, when TOP-003-3 R5 became mandatory and enforceable, and ended on March 7, 2018, when QREP restored the communication line and began providing Real-time data to its TOP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, throughout the issue duration, the TOP in question continued to receive Real-time data for the QREP generation Facility at issue from the TOP’s metering and monitoring equipment, reducing the risk that the TOP would be unaware of any line overloading or other operational issues. Second, QREP continued to provide required Real-time data to its Reliability Coordinator (RC) throughout the issue duration. Pursuant to the 2017 Electric Reliability Council of Texas (ERCOT) TOP Coordinated Functional Registration (CFR) matrix, the regional RC has assumed sole responsibility for performing required Real-time Assessments and Operational Planning Analysis. As a result, the RC would have had the information necessary to identify and address any Real-time contingency or loading issues had they occurred. No harm is known to have occurred. Texas RE considered QREP’s and its affiliate’s compliance history and determined there were no relevant instances of noncompliance related to TOP-003-3 R5. | To mitigate this noncompliance, QREP: 1) installed a new communications link with its TOP; 2) verified with its TOP that the required data is being received; 3) established a process that requires applicable personnel perform a monthly verification that its TOP is receiving all specified data as scheduled; 4) updated its list of Applicable Standards and Internal Controls to include an annual verification of communication with its TOP and RC; and 5) documented the network drawing of the communication system to enhance internal visibility regarding the communications link with its TOP in case of future issues. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | The Dow Chemical Co (DOWTXO) | NCR04146 | TRE2017017825 | MOD-025-2 | R1 | On June 23, 2017, DOWTXO submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, DOWTXO did not verify the Real Power capability of its applicable generating units in accordance with MOD-025-2, Attachment 1 by July 1, 2016. In March 2017, DOWTXO became aware that it needed to complete Real Power capability verifications for its generating Facilities. However, DOWTXO was not able to perform these verifications until July 7, 2016. DOWTXO then submitted its Real Power capability verifications to its Transmission Planner (TP) on September 22, 2016. However, these initial submissions only included generic one-line diagrams rather than the required entity-specific diagrams. DOWTXO then submitted revised information containing the required one-line diagrams to its TP on March 26, 2018, ending the issue. The root cause of this noncompliance was insufficient internal controls to ensure DOWTXO complied with all newly applicable NERC Reliability Standards in a timely manner. In particular, DOWTXO lacked adequate compliance procedures to monitor new compliance obligations and then perform all newly required reliability tasks. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on March 26, 2018, when DOWTXO submitted complete Real Power capability verification forms to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, DOWTXO previously provided Reactive power verifications under substantially similar region-specific output conditions in 2012 and 2014, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, DOWTXO is typically a net importer of power and most of DOWTXO’s generation is to serve its internal load. Accordingly, the loss of this generation would likely have a small impact on the Bulk Electric System. Accordingly, the lack of DOWTXO’s Real Power capability verification information would have only a minimal impact on planning results. No harm is known to have occurred. Texas RE considered DOWTXO’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, DOWTXO: 1) performed all required Real Power testing for the five generation units at issue; 2) submitted its Real Power verification testing results to its TP for the five generation units at issue; 3) contracted a third-party compliance consultant to provide a quarterly report that addresses new NERC Reliability Standards and the enforcement dates, as well as monitor NERC and Regional Standards development, upcoming regional compliance outreach activities, and provide compliance activity recommendations; and 4) created an automated task reminder to notify applicable staff members of upcoming MOD-025 deadlines. Texas RE has verified the completion of all mitigation activity.
2018-05-31 | Texas Reliability Entity (Texas RE) | The Dow Chemical Co (DOWTXO) | NCR04146 | TRE2018019625 | MOD-025-2 | R2 | On June 23, 2017, DOWTXO submitted a Self-Report stating that, as a Generator Owner (GO), it had a possible noncompliance with MOD-025-2 R1 relating to the verification of Real Power capability. Subsequently, on May 1, 2018, Texas RE determined that the issues described in DOWTXO's MOD-025-2 R1 Self-Report also applied to DOWTXO’s Reactive Power capability verifications. In particular, DOWTXO did not verify the Reactive Power capability of its applicable generating units in accordance with MOD-025-2, Attachment 1 by July 1, 2016. In March 2017, DOWTXO became aware that it needed to complete Reactive Power capability verifications for its generating Facilities. However, DOWTXO was not able to perform these verifications until July 7, 2016. DOWTXO then submitted its Reactive Power capability verifications to its Transmission Planner (TP) on September 22, 2016. However, these initial submissions only included generic one-line diagrams rather than the required entity-specific diagrams. DOWTXO then submitted revised information containing the required one-line diagrams to its TP on March 26, 2018, ending the issue. The root cause of this noncompliance was insufficient internal controls to ensure DOWTXO complied with all newly applicable NERC Reliability Standards in a timely manner. In particular, DOWTXO lacked adequate compliance procedures to monitor new compliance obligations and then perform all newly required reliability tasks. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on March 26, 2018, when DOWTXO submitted complete Reactive Power capability verification forms to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, DOWTXO previously provided Reactive power verifications under substantially similar region-specific output conditions in 2012 and 2014, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, DOWTXO is typically a net importer of power and most of DOWTXO’s generation is to serve its internal load. Accordingly, the loss of this generation would likely have a small impact on the Bulk Electric System. Accordingly, the lack of DOWTXO’s Reactive Power capability verification information would have only a minimal impact on planning results. No harm is known to have occurred. Texas RE considered DOWTXO’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, DOWTXO: 1) performed all required Reactive Power testing for the five generation units at issue; 2) submitted its Reactive Power verification testing results to its TP for the five generation units at issue; 3) contracted a third-party compliance consultant to provide a quarterly report that addresses new NERC Reliability Standards and the enforcement dates, as well as monitor NERC and Regional Standards development, upcoming regional compliance outreach activities, and provide compliance activity recommendations; and 4) created an automated task reminder to notify applicable staff members of upcoming MOD-025 deadlines. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Midwest Reliability Organization (MRO) | Omaha Public Power District (OPPD) | NCR00860 | MRO2017018490 | COM-002-4 | R4 | On October 16, 2017, OPPD submitted a self-log stating that, as a Transmission Operator, it was in noncompliance with COM-002-4 R4. OPPD stated that it did not, at least once every 12 calendar months, assess adherence to the documented communications protocols by its operating personnel that issue and receive Operating Instructions. Per OPPD, it assessed its operating personnel prior to the requirement's mandatory enforcement date. OPPD failed to assess its operating personnel within 12 months of July 1, 2016 (P4.1), and hence also did not assess the effectiveness of its documented communications protocols (P4.2). OPPD discovered the issue on July 5, 2017. The cause of the noncompliance was a lack of ownership between the Operations Support Department and Transmission Operations Department of the assessment process. This noncompliance started on July 1, 2017, 12 calendar months after the enforceability of the standard, and ended on August 30, 2017, when OPPD completed the annual assessment for all transmission system operators. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OPPD stated that its transmission system operators used and adhered to the documented communications protocols, which was confirmed when it conducted its assessment. Finally, the noncompliance was self-detected. No harm is known to have occurred. | To mitigate this noncompliance OPPD: 1) completed the annual assessment for all transmission system operators; 2) completed an assessment of program effectiveness and updated the documented protocols as necessary; and 3) updated the documented communications protocols to designate the responsibility to conduct assessments under the standard to the Transmission Operations lead; and 4) reviewed the NERC Reliability Standards Matrix to ensure that all TOP function responsibilities were properly assigned.
2018-04-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2017018463 | MOD-025-2 | R1 | On October 12, 2017, Plainfield Renewable Energy, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. Specifically, the Entity failed to verify the Real Power capability of its single generating facility in accordance with Attachment 1 of the standard and submit a completed Attachment 2 to its Transmission Planner within 90 calendar days of the tests. Per the phased-in implementation plan of the Standard and Requirement, the above verification for the Entity's single generating asset was required by 7/1/2016. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on February 28, 2018, when the Entity provided its Transmission Planner with verification of the Real Power capability of its applicable Facilities. The root cause of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan of the Standard and Requirement would apply to their single generating asset. Subsequently, based on information issued by NERC, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by 7/1/2016. Upon discovery of this missed compliance obligation, the Entity contracted a third-party vendor to perform an evaluation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Prior to the effective date of the standard, the Entity's single generating asset had already been tested twice for its active (and reactive) capability (in 2013 and 2014), albeit in a less rigorous and comprehensive manner than the standard currently requires. The Entity's single generating asset has a net rated capability of 37.5 MW, and it operated at a capacity factor of 72% and 62% for the years 2016 and 2017, respectively. By comparison, the Entity's Reliability Coordinator's (ISO-NE) required winter operating reserves are approximately 2600 MW. The RC has comparable summer operating reserves requirements. In conclusion, the Entity's temporary noncompliance, consisting of a late verification test of its unit's real power capability, could have been mitigated in real-time by its RC during a contingency event resulting in the loss of the Entity's entire generating capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by verifying the Real Power Capability of its generating asset during a staged verification, and subsequently providing required test data to its TP; and 2. To prevent a recurrence of similar instances of noncompliance, implemented calendar reminders for responsible personnel to complete the required 5-year re-verifications in a timely manner. Calendar reminders are planned for four (4) years and again at four (4) years and nine (9) months after the initial submittal date of the real power verification. NPCC has verified the completion of all mitigation activity.
2018-04-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2017018464 | MOD-025-2 | R2 | On October 12, 2017, Plainfield Renewable Energy, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, the Entity failed to verify the Reactive Power capability of its single generating facility in accordance with Attachment 1 of the standard and submit a completed Attachment 2 to its Transmission Planner within 90 calendar days of the tests. Per the phased-in implementation plan of the Standard and Requirement, the above verification for the Entity's single generating asset was required by 7/1/2016. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on February 28, 2018, when the Entity provided its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities. The root cause of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan of the Standard and Requirement would apply to their single generating asset. Subsequently, based on information issued by NERC, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by 7/1/2016. Upon discovery of this missed compliance obligation, the Entity contracted a third-party vendor to perform an evaluation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Prior to the effective date of the standard, the Entity's single generating asset had already been tested twice for its reactive (and active) capability (in 2013 and 2014), albeit in a less rigorous and comprehensive manner than the standard currently requires. The Entity's single generating asset has a net rated capability of 37.5 MW, and it operated at a capacity factor of 72% and 62% for the years 2016 and 2017, respectively. By comparison, the Entity's Reliability Coordinator's (ISO-NE) required winter operating reserves are approximately 2600 MW. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. The RC has comparable summer operating reserves requirements. In conclusion, the Entity's temporary noncompliance, consisting of a late verification test of its unit's reactive power capability, could have been mitigated in real-time by its RC during a contingency event resulting in the loss of the Entity's entire generating capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by verifying the Reactive Power Capability of its generating asset during a staged verification, and subsequently providing required test data to its TP; and 2. To prevent a recurrence of similar instances of noncompliance, implemented calendar reminders for responsible personnel to complete the required 5-year re-verifications in a timely manner. Calendar reminders are planned for four (4) years and again at four (4) years and nine (9) months after the initial submittal date of the real power verification. NPCC has verified the completion of all mitigation activity.
2018-04-30 | Northeast Power Coordinating Council, Inc. (NPCC) | PSEG Fossil LLC | NCR00893 | NPCC2017018214 | VAR-002-4 | R1. | On August 17, 2017, PSEG Fossil, LLC (the Entity) submitted a Self-Report stating that, as a Generator Operator (GOP), it was in noncompliance with VAR-002-4 R1. Specifically, during the 2017 Reactive Power Audit tests, the Entity failed to operate its three generating assets (New Haven Harbor Station units 2, 3 and 4) in the automatic voltage control mode - AVC - (with its automatic voltage regulator (AVR) in service and controlling voltage) as instructed by its Transmission Operator (TOP), the ISO-NE. The three units are normally operated with their AVR in the AVC mode. However, prior to conducting each unit’s test, PSEG Fossil plant personnel erroneously changed each unit’s Automatic Voltage Regulator (AVR) operating mode from Automatic controlling voltage (AVC) to Automatic controlling MVARs, in order to maximize the unit's lagging and leading VAR output, as measured at the unit's maximum and minimum MW outputs. This noncompliance started on June 13, 2017, when the first unit's (Unit #2) AVR was placed in Automatic controlling MVARs mode (for testing purposes), and ended on June 15, 2017, when the last unit's (Unit #4) AVR was restored to AVC mode (after completion of the test). The duration of the noncompliance was less than 2 hours each day. The root cause of this instance of noncompliance was lack of clarity in the Entity's internal testing guidance document with respect to maintaining the tested unit's AVR in the (normally employed) AVC mode during TOP-mandated periodic Reactive Power Audit tests. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This instance of noncompliance had a short duration of less than six hours distributed over a three-day time period. During this time, although the three noncompliant units were not operated with their AVR in the customary AVC mode, the units' respective AVRs were functional and set in the MVAR controlling mode, thus still providing some reactive support to the interconnected system. Moreover, each of the three generating units has a net Summer Claimed Capability of 43 MW and approximately 25 MVAR lagging capability and was operated at a capacity factor of 0.2% in 2017. By comparison, the Entity's Reliability Coordinator's (ISO-NE) required winter operating reserves are approximately 2600 MW, a value which is often exceeded by a margin of about 2000 MW above that requirement. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. The RC has comparable summer operating reserves requirements. Therefore, if this instance of noncompliance had caused the generating assets to not properly control the correct voltage, the ISO-NE would have been able to compensate for this deficiency. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by restoring the AVC mode on the AVRs of each generating unit's AVR at completion of the Reactive Power Audit test; and 2. To prevent a recurrence of similar instances of noncompliance, it enhanced its internal testing guidance document by adding a prominent reminder notification textbox that clearly states the ISO-NE requirements for keeping the generating units' AVR system in the AVC mode throughout the duration of periodic Reactive Power Audit tests. NPCC has verified the completion of all mitigation activity.
2018-04-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Waterbury Generation, LLC | NCR10339 | NPCC2018019187 | PRC-019-2 | R1. | On February 16, 2018, Waterbury Generation, LCC (the Entity) submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2, R1. During an internal assessment performed in the 4th Quarter 2017, the Entity determined it had not coordinated it's voltage regulating system controls in the timeframe required by the PRC-019-2 Implementation Plan. In accordance with the standard's Implementation Plan, the Entity's sole generating asset was required to be compliant by July 1, 2016. The noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on September 12, 2016, when the Entity confirmed the voltage regulating system controls had been coordinated properly after a staged test conducted on August 13, 2016. The root cause of this instance of noncompliance was the Entity’s lack of a clear understanding of how the phased-in implementation plan for the Standard and Requirement would apply to their asset. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A plant such as Waterbury Generation, LLC (100 MW and 5% capacity factor, 40 MVAR Lagging and 13 MVAR Leading) being noncompliant for 73 days is a minimal risk. Waterbury Generation's BA/TOP (ISONE) carries operating reserves of approximately 2300 MW. There's a corresponding amount of reactive capability associated with the MW operating reserves that is determined by individual (on-reserve) generators' capability curves. As such, the BA/TOP would have been able to replace the MW and reactive loss of Waterbury without an issue. There has never been a known reliability issue due to voltage control system regulating coordination at Waterbury Generation, LLC. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered Waterbury Generation, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by completing the voltage regulating system control coordination as specified. To prevent future occurrences, the Entity 2. Entered Future Preventative Maintenance (PM) work orders into it’s work maintenance management system with proper due dates to alert in advance of coming compliance related maintenance due dates; and 3. Developed a SharePoint application and calendar for fleet personnel that shows compliance dates to ensure continued focus and awareness, began sending email summaries once a week to fleet personnel, and began monthly NERC related calls between compliance and plant management. NPCC has verified the completion of all mitigation activity.
2018-04-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Waterbury Generation, LLC | NCR10339 | NPCC2018019224 | MOD-025-2 | R1.1 | On February 23, 2018, Waterbury Generation, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2, R1. During an internal assessment performed in the 4th Quarter 2017, the Entity determined it did not perform the proper real power testing and provide the results to the Transmission Planner in the timeframe required by the MOD-025-2 Implementation Plan. In accordance with the standard's Implementation Plan, the Entity's sole generating asset was required to be compliant by July 1, 2016. The noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on September 12, 2016, when the Entity provided the real power test results to its Transmission Planner (ISO-NE) containing the information required by Attachment 2 after a staged test was conducted on August 13, 2016. The root cause of this instance of noncompliance was the Entity’s lack of a clear understanding of how the phased-in implementation plan for the Standard and Requirement would apply to their asset. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A plant such as Waterbury Generation, LLC (100 MW and 5% capacity factor, 40 MVAR Lagging and 13 MVAR Leading) being noncompliant for 73 days is a minimal risk. Waterbury Generation has historically performed the required real power tests through the NPCC Directory 9 (Real Power Verification) program administered by ISONE (Base Load Real Power to the system for 1 hour). There has never been a known reliability issue due to the real power verification tests that were not performed by Waterbury Generation, LLC No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered Waterbury Generation, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Completed the real power tests required by the standard on August 13, 2016 and provided the Attachment 2 information to the Transmission Planner (ISONE). To prevent future occurrences, the Entity: 2. Entered Future Preventative Maintenance (PM) work orders into it’s work maintenance management system with proper due dates to alert in advance of coming compliance related maintenance due dates; and 3. Developed a SharePoint application and calendar for fleet personnel that shows compliance dates to ensure continued focus and awareness, began sending email summaries once a week to fleet personnel, and began monthly NERC related calls between compliance and plant management. NPCC has verified the completion of all mitigation activity.
2018-04-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Waterbury Generation, LLC | NCR10339 | NPCC2018019225 | MOD-025-2 | R2.1 | On February 23, 2018, Waterbury Generation, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2, R2. During an internal assessment performed in the 4th Quarter 2017, the Entity determined it did not perform the proper reactive power testing and provide the results to the Transmission Planner in the timeframe required by the MOD-025-2 Implementation Plan. In accordance with the standard's Implementation Plan, the Entity's sole generating asset was required to be compliant by July 1, 2016. The noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on September 12, 2016, when the Entity provided the reactive power test results to its Transmission Planner (ISO-NE) containing the information required by Attachment 2 after a staged test was conducted on August 13, 2016. The root cause of this instance of noncompliance was the Entity’s lack of a clear understanding of how the phased-in implementation plan for the Standard and Requirement would apply to their asset. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A plant such as Waterbury Generation, LLC (100 MW and 5% capacity factor, 40 MVAR Lagging and 13 MVAR Leading) being noncompliant for 73 days is a minimal risk. Waterbury Generation has historically performed the required real and reactive power tests through the NPCC Directory 10 (Reactive Power Verification) program administered by ISONE (Base Load Real Power/Max MVAR Output to system for 1 hour, Base Load Real Power/Max MVAR Absorb from system for 15 minutes). There has never been a known reliability issue due to the reactive power tests that were not performed by Waterbury Generation, LLC as the No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered Waterbury Generation, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Completed the reactive power tests required by the standard on August 13, 2016 and provided the Attachment 2 information to the Transmission Planner (ISONE). To prevent future occurrences, the Entity: 2. Entered Future Preventative Maintenance (PM) work orders into it’s work maintenance management system with proper due dates to alert in advance of coming compliance related maintenance due dates; and 3. Developed a SharePoint application and calendar for fleet personnel that shows compliance dates to ensure continued focus and awareness, began sending email summaries once a week to fleet personnel, and began monthly NERC related calls between compliance and plant management. NPCC has verified the completion of all mitigation activity.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2017018566 | PRC-019-2 | R1 | On October 26, 2017, EPOPP submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. While the entity was reviewing the reports in 2017 that it had received from Tangibl (a third-party engineering group that the entity had previously contracted to perform PRC-019/PRC-024 coordination analysis), the entity discovered that Tangibl had failed to consider the Volts/Hertz exciter setting in the relay/exciter coordination study. This failure to consider the Volts/Hertz exciter setting means that the study Tangibl performed in 2016 for PRC-019/PRC-024 compliance purposes was insufficient. This noncompliance involves the management practice of verification. Verification is involved because the entity did not have a verification process in place to verify that Tangibl completed the PRC-019/PRC-024 coordination analysis correctly. The entity’s lack of an internal control to verify that third-party contractors correctly complete their work is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-019-2 R1, and ended on March 31, 2018, when the entity assessed the overlooked setting. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage controls which can result in a generator falsely tripping. The risk is minimized because the entity timely performed all other parts of the PRC-019/PRC-024 coordination analysis except for considering the Voltz/Hertz exciter setting in the relay/exciter coordination study. This means that the maintenance and testing the contractor performed is valid for all other equipment types considered in the study which lessens the risk of a generator falsely tripping because of improper coordination. The only issue is with the Voltz per Hertz limiter because the contractor did not consider the Volts/Hertz exciter setting in the relay/exciter coordination study. ReliabilityFirst notes that the entity generated approximately 340 MW and operated at approximately a 14% capacity factor during the noncompliance. ReliabilityFirst also notes that there was no actual impact as there were no voltage or frequency excursions occurring that led to a unit trip during the time frame of this noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-019 R1 compliance history in determining the disposition track. The entity’s relevant prior noncompliances with PRC-019 R1 include: a. RFC2016016344. A Compliance Exception addressing a noncompliance with PRC-019 R1 was posted on the NERC website on December 28, 2017. The prior noncompliance is distinguishable from the instant noncompliance because the noncompliance arose from Essential Power believing that they could show PRC-019 compliance at the fleet level rather than at the Registered Entity level. In contrast, the instant noncompliance arose from Essential Power’s Contractor (Tangibl) failing to consider the Voltz/Hertz exciter setting in EPOPP’s relay/exciter coordination study for PRC-019/PRC-024 compliance. b. RFC2016016345. A Compliance Exception addressing a noncompliance with PRC-019 R1 was posted on the NERC website on December 28, 2017. The prior noncompliance is distinguishable from the instant noncompliance because the noncompliance arose from Essential Power believing that they could show PRC-019 compliance at the fleet level rather than at the Registered Entity level. In contrast, the instant noncompliance arose from Essential Power’s Contractor (Tangibl) failing to consider the Voltz/Hertz exciter setting in EPOPP’s relay/exciter coordination study for PRC-019/PRC-024 compliance. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity will complete the following mitigation activities by July 30, 2018: 1) researched and selected a vendor to perform the analysis required in PRC-019-2; 2) will submit all requested information to the selected vendor to complete the analysis; 3) will perform the PRC-019-2 evaluation by the end of the first quarter in 2018; 4) will create a notification in the form of a recurring Preventive Maintenance work order or as an obligation that escalates until completed in the Company Obligation Tracking System to ensure the 5 year review occurs according to PRC-019-2; 5) will have Cogentrix’s engineering department review the PRC-019-2 study to ensure that all required parts are covered; and 6) will perform setting changes required in the PRC-019-2 coordination analysis. As a result of the steps taken in this Mitigation Plan, the entity has developed a more robust oversight plan for all NERC compliance with additional resources to verify proper enforcement and effective dates of the Reliability Standards and Implementation Plans. The entity requires an extended period of time to complete this Mitigation Plan because it must take an outage to perform the settings changes and the entity is waiting for the next scheduled outage after it completes the previous mitigating actions to perform the settings changes.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2017018567 | PRC-024-2 | R1 | On October 26, 2017, EPOPP submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. While the entity was reviewing the reports in 2017 that it had received from Tangibl (a third-party engineering group that the entity had previously contracted to perform PRC-019/PRC-024 coordination analysis), the entity discovered that Tangibl had failed to consider the Volts/Hertz exciter setting in the relay/exciter coordination study. This failure to consider the Volts/Hertz exciter setting means that the study Tangibl performed in 2016 for PRC-019/PRC-024 compliance purposes was insufficient. This noncompliance involves the management practice of verification. Verification is involved because the entity did not have a verification process in place to verify that Tangibl completed the PRC-019/PRC-024 coordination analysis correctly. The entity’s lack of an internal control to verify that third-party contractors correctly complete their work is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R1, and ended on March 31, 2018, when the entity assessed the overlooked setting. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is minimized because the entity timely performed all other parts of the PRC-019/PRC-024 coordination analysis except for considering the Voltz/Hertz exciter setting in the relay/exciter coordination study. This means that the maintenance and testing the contractor performed is valid for all other equipment types considered in the study which lessens the risk of a generator falsely tripping because of improper coordination. The only issue is with the Voltz per Hertz limiter because the contractor did not consider the Volts/Hertz exciter setting in the relay/exciter coordination study. ReliabilityFirst notes that the entity generated approximately 340 MW and operated at approximately a 14% capacity factor during the noncompliance. ReliabilityFirst also notes that there was no actual impact as there were no voltage or frequency excursions occurring that led to a unit trip during the time frame of this noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-024 R1 compliance history in determining the disposition track. The entity’s relevant prior noncompliances with PRC-024 R1 include: a. RFC2016016346. A Compliance Exception addressing a noncompliance with PRC-024 R1 was posted on the NERC website on December 28, 2017. The prior noncompliance is distinguishable from the instant noncompliance because the instant noncompliance arose from Essential Power’s Contractor (Tangibl) failing to consider the Voltz/Hertz exciter setting in EPOPP’s relay/exciter coordination study for PRC-019/PRC-024 compliance. b. RFC2016016347. A Compliance Exception addressing a noncompliance with PRC-024 R1 was posted on the NERC website on December 28, 2017. The prior noncompliance is distinguishable from the instant noncompliance because the instant noncompliance arose from Essential Power’s Contractor (Tangibl) failing to consider the Voltz/Hertz exciter setting in Lakewood and EPOPP’s relay/exciter coordination study for PRC-019/PRC-024 compliance. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity will complete the following mitigation activities by July 30, 2018: 1) researched and selected a vendor to perform the analysis required in PRC-024-2; 2) will submit all requested information to the selected vendor to complete the analysis; 3) will perform the PRC-024-2 evaluation by the end of the first quarter in 2018; 4) will have Cogentrix’s engineering department review the PRC-024-2 study to ensure that all required parts are covered; and 5) will perform setting changes required in the PRC-024-2 coordination analysis. As a result of the steps taken in this Mitigation Plan, the entity has developed a more robust oversight plan for all NERC compliance with additional resources to verify proper enforcement and effective dates of the Reliability Standards and Implementation Plans. The entity requires an extended period of time to complete this Mitigation Plan because it must take an outage to perform the settings changes and the entity is waiting for the next scheduled outage after it completes the previous mitigating actions to perform the settings changes.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Lakewood Cogeneration, LP (Lakewood) | NCR00168 | RFC2017018565 | PRC-019-2 | R1 | On October 26, 2017, Lakewood submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. While the entity was reviewing the reports in 2017 that it had received from Tangibl (a third-party engineering group that the entity had previously contracted to perform PRC-019/PRC-024 coordination analysis), the entity discovered that Tangibl had failed to consider the Volts/Hertz exciter setting in the relay/exciter coordination study. This failure to consider the Volts/Hertz exciter setting means that the study Tangibl performed in 2016 for PRC-019/PRC-024 compliance purposes was insufficient. This noncompliance involves the management practice of verification. Verification is involved because the entity did not have a verification process in place to verify that Tangibl completed the PRC-019/PRC-024 coordination analysis correctly. The entity’s lack of an internal control to verify that third-party contractors correctly complete their work is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-019-2 R1, and ended on March 31, 2018, when the entity assessed the overlooked setting. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage controls which can result in a generator falsely tripping. The risk is minimized because the entity timely performed all other parts of the PRC-019/PRC-024 coordination analysis except for considering the Voltz/Hertz exciter setting in the relay/exciter coordination study. This means that the maintenance and testing the contractor performed is valid for all other equipment types considered in the study which lessens the risk of a generator falsely tripping because of improper coordination. The only issue is with the Voltz per Hertz limiter because the contractor did not consider the Volts/Hertz exciter setting in the relay/exciter coordination study. ReliabilityFirst notes that the entity generated approximately 250 MW and operated at approximately a 55% capacity factor during the noncompliance. ReliabilityFirst also notes that there was no actual impact as there were no voltage or frequency excursions occurring that led to a unit trip during the time frame of this noncompliance. No harm is known to have occurred. ReliabilityFirst considered Lakewood’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity will complete the following mitigation activities by July 30, 2018: 1) researched and selected a vendor to perform the analysis required in PRC-019-2; 2) will submit all requested information to the selected vendor to complete the analysis; 3) will perform the PRC-019-2 evaluation by the end of the first quarter in 2018; 4) will create a notification in the form of a recurring Preventive Maintenance work order or as an obligation that escalates until completed in the Company Obligation Tracking System to ensure the 5 year review occurs according to PRC-019-2; 5) will have Cogentrix’s engineering department review the PRC-019-2 study to ensure that all required parts are covered; and 6) will perform setting changes required in the PRC-019-2 coordination analysis. As a result of the steps taken in this Mitigation Plan, the entity has developed a more robust oversight plan for all NERC compliance with additional resources to verify proper enforcement and effective dates of the Reliability Standards and Implementation Plans. The entity requires an extended period of time to complete this Mitigation Plan because it must take an outage to perform the settings changes and the entity is waiting for the next scheduled outage after it completes the previous mitigating actions to perform the settings changes.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Lakewood Cogeneration, LP (Lakewood) | NCR00168 | RFC2017018564 | PRC-024-2 | R1 | On October 26, 2017, Lakewood submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. While the entity was reviewing the reports in 2017 that it had received from Tangibl (a third-party engineering group that the entity had previously contracted to perform PRC-019/PRC-024 coordination analysis), the entity discovered that Tangibl had failed to consider the Volts/Hertz exciter setting in the relay/exciter coordination study. This failure to consider the Volts/Hertz exciter setting means that the study Tangibl performed in 2016 for PRC-019/PRC-024 compliance purposes was insufficient. This noncompliance involves the management practice of verification. Verification is involved because the entity did not have a verification process in place to verify that Tangibl completed the PRC-019/PRC-024 coordination analysis correctly. The entity’s lack of an internal control to verify that third-party contractors correctly complete their work is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when the entity was required to comply with PRC-024-2 R1, and ended on March 31, 2018, when the entity assessed the overlooked setting. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is minimized because the entity timely performed all other parts of the PRC-019/PRC-024 coordination analysis except for considering the Voltz/Hertz exciter setting in the relay/exciter coordination study. This means that the maintenance and testing the contractor performed is valid for all other equipment types considered in the study which lessens the risk of a generator falsely tripping because of improper coordination. The only issue is with the Voltz per Hertz limiter because the contractor did not consider the Volts/Hertz exciter setting in the relay/exciter coordination study. ReliabilityFirst notes that the entity generated approximately 250 MW and operated at approximately a 55% capacity factor during the noncompliance. ReliabilityFirst also notes that there was no actual impact as there were no voltage or frequency excursions occurring that led to a unit trip during the time frame of this noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity will complete the following mitigation activities by July 30, 2018: 1) researched and selected a vendor to perform the analysis required in PRC-024-2; 2) will submit all requested information to the selected vendor to complete the analysis; 3) will perform the PRC-024-2 evaluation by the end of the first quarter in 2018; 4) will have Cogentrix’s engineering department review the PRC-024-2 study to ensure that all required parts are covered; and 5) will perform setting changes required in the PRC-024-2 coordination analysis. As a result of the steps taken in this Mitigation Plan, the entity has developed a more robust oversight plan for all NERC compliance with additional resources to verify proper enforcement and effective dates of the Reliability Standards and Implementation Plans. The entity requires an extended period of time to complete this Mitigation Plan because it must take an outage to perform the settings changes and the entity is waiting for the next scheduled outage after it completes the previous mitigating actions to perform the settings changes.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2017017651 | EOP-005-2 | R4 | On May 23, 2017, PJM submitted a Self-Report stating that, as a Transmission Operator, it was in noncompliance with EOP-005-2 R4. AEP failed to update its restoration plan before implementing a planned Bulk Electric System modification. As background, on November 19, 2016, an outage to replace a transformer and also replace a motor-operated switch with a circuit breaker at AEP’s Robison Park Station began as scheduled under an approved entity Electronic Dispatcher Application and Reporting Tool (eDART) outage ticket submitted by AEP. This outage ticket was submitted with a “cut-in” (new construction) designation, which triggered an alert to AEP and the entity that the procedure also required AEP, the Transmission Owner, to review, and potentially revise, its system restoration plan prior to energizing the new equipment per EOP-005-2 R4 as well as entity Manual 36 Attachment G. The eDART system also sent automatic reminders to the entity and AEP each day once the ticket was within the 30 day window of completion. The entity separately sent an email to AEP on February 1, 2017 reminding AEP that it needed to review and potentially revise its System Restoration Plan. On February 3, 2017, AEP completed construction at the AEP Robison Park Station, and the eDART ticket was closed, but AEP did not update its System Restoration Plan until four days later. The goal of the original System Restoration Plan was to develop a path between the Blackstart unit and the Cook nuclear plant, and the construction project did not change that path. Rather, it required AEP to make a minor modification to the more detailed process in the plan relating to a switching step process. More specifically, for one step in the System Restoration Plan, the plan now references the circuit breaker instead of the motor-operated switch. The root cause was insufficient verification controls to require the updated system restoration plan prior to closing the eDART ticket. Additionally, because of the large volume of eDART notifications that AEP receives, some of which relate to projects that do not require updated system restoration plans, AEP missed the entity’s request for the updated System Restoration Plan. Accordingly, this noncompliance involves the management practices of verification and work management. This issue started on February 3, 2017, when the entity made a system change without having an updated System Restoration Plan, and ended on February 7, 2017, when AEP submitted a revised System Restoration Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Although AEP did not update its System Restoration Plan prior to energizing the equipment, AEP was familiar with the minor change it made to the system and thus would have been able to implement the changes despite not having the updated System Restoration Plan. Additionally, the minor change did not impact the entity’s System Restoration Plan because the goal of the entity’s System Restoration Plan is to develop a path between the Blackstart unit and the Cook nuclear plant. The use of a circuit breaker instead of a motor-operated switch did not change this path. Finally, AEP updated the System Restoration Plan only four days late, which reduced the amount of time there was any increased risk to the BPS as a result of not having an updated System Restoration Plan. No harm is known to have occurred. ReliabilityFirst considered the entity’s EOP-005 R4 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) made enhancements to the cut-in process to incorporate task status with respect to readiness of a Restoration Plan associated with a ticket. This will prevent a ticket from being completed without an updated System Restoration Plan; 2) worked with AEP to establish a formal plan to review cut-in tickets associated with their System Restoration Plan; 3) conducted updated training on entity Manual 36: System Restoration emphasizing that the entity will not allow equipment cut-ins without corresponding System Restoration Plan review; 4) made enhancements to the eDART Web and Power Builder applications to prohibit the entity from taking action on tickets with System Restoration Plan updates that have not been reviewed and/or completed, and to provide better visibility to members that additional actions are needed prior to equipment energization; and 5) enhanced emails associated with eDART tickets covering projects nearing energization to heighten awareness of the need to complete System Restoration Plan review and possible update before energization. ReliabilityFirst has verified the completion of all mitigation activity.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Rockford Generation, LLC (Rockford) | NCR11660 | RFC2017018008 | EOP-004-2 | R1 | On July 14, 2017, Rockford submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it was in noncompliance with EOP-004-2 R1. During an internal review, the entity discovered that the contact information for all of the required parties was not verified for 2017. NRG Energy (NRG) verified all of the contact information in 2016. NRG corporate compliance performed the verification for all contacts except law enforcement. Because the corporate office verified all of the other contacts, the local procedure only required plant personnel to verify the law enforcement contact. Consequently, when the entity took over operations for the plant, the plant personnel followed the existing procedure, which only required them to verify the law enforcement contact information. Moreover, the entity was required to update the event reporting Operating Plan to include protocols for plant personnel actually performing the verification. The root cause of this noncompliance was the entity’s lack of familiarity with NRG’s previous procedures. This major contributing factor involves the management practice of verification, in that the entity failed to verify all of the requisite information. This noncompliance started on July 23, 2016, when the entity was required to have validated the contact information and ended on June 8, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This noncompliance is an isolated incident tied to the timing of the acquisition of this generating unit. The entity acquired the unit days before it was required to perform the annual verification of the units operating plan and, as a result, the entity performed its predecessor’s operating plan. While the operating plan did have the requisite contact information, its verification process did not include the verification of all of its contact information. Thereafter, and within less than a year of acquiring this generating unit, the entity performed a complete review of its predecessor’s operating plan and self-identified the fact that it did not require the verification of all contact information. It then self-reported this noncompliance, promptly verified all of the operating plan’s contact information, and revised its process to require the verification of all contact information. ReliabilityFirst also notes that the contact information for all external organizations did not change after verification. No harm is known to have occurred. ReliabilityFirst considered the entity’s EOP-004-2 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) put into service a New Event Reporting Procedure with new plant contact information; and 2) generated a work order in its work management system (as a preventive measure) to ensure that the Event Reporting Procedure gets reviewed annually to ensure it still meets compliance with the standard and is the correct document for enforcement.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Rockford Generation, LLC (Rockford) | NCR11660 | RFC2017018007 | EOP-004-2 | R3 | On July 14, 2017, Rockford submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it was in noncompliance with EOP-004-2 R3. During an internal review, the entity discovered that the contact information for all of the required entities was not verified for 2017. NRG Energy (NRG) verified all of the contact information in 2016. However, NRG corporate compliance performed that task for all contacts except law enforcement. Therefore, the existing procedure for plant personnel only required them to verify the law enforcement contact information. Consequently, when the entity took over operations for the plant, the plant personnel followed the existing procedure, meaning that they only verified the law enforcement contact information. Moreover, the entity was required to update the event reporting Operating Plan to include protocols for plant personnel actually performing the verification. The root cause of this noncompliance was the entity’s lack of familiarity with NRG’s previous procedures. This major contributing factor involves the management practice of verification, in that the entity failed to verify all of the requisite information. This noncompliance started on July 23, 2016, when the entity was required to have validated the contact information and ended on June 8, 2017, when the entity completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This noncompliance is an isolated incident tied to the timing of the acquisition of this generating unit. The entity acquired the unit days before it was required to perform the annual verification of the units operating plan and, as a result, the entity performed its predecessor’s operating plan. While the operating plan did have the requisite contact information, its verification process did not include the verification of all of its contact information. Thereafter, and within less than a year of acquiring this generating unit, the entity performed a complete review of its predecessor’s operating plan and self-identified the fact that it did not require the verification of all contact information. It then self-reported this noncompliance, promptly verified all of the operating plan’s contact information, and revised its process to require the verification of all contact information. ReliabilityFirst also notes that the contact information for all external organizations did not change after verification. No harm is known to have occurred. ReliabilityFirst considered the entity’s EOP-004-2 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) put into service a New Event Reporting; and 2) generated a work order in its work management system (as a preventive measure) to ensure that the Event Reporting Procedure gets reviewed annually to ensure it still meets compliance with the standard and is the correct document for enforcement.
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Susquehanna Nuclear LLC (Susquehanna) | NCR00889 | RFC2018019407 | PRC-005-6 | R1 | On April 1, 2017, Susquehanna submitted a Self-Log stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R1. Susquehanna Units 1 and 2 each have one vented lead-acid (VLA) battery subject to PRC-005-6. Table 1.4(a) of the standard specifies the periodic maintenance for unmonitored VLA batteries; with max-4-month, max-18-month and max-6-years periodicity categories. Table 1.4(f) of the standard allows for "continuous monitoring" in lieu of several max-4-month and max-18-month tasks if certain prerequisites ("Component attributes") are met. Some periodic maintenance is always required, and Table 1-4(f) applies on an individual-task basis - an entity can have a partly-monitored/partly-hands-on program. The entity claimed "continuous monitoring" in its Protection System Maintenance Program (PSMP), and took the Table 1-4(f) allowance, for the Table 1-4(a) tasks of (1) verifying DC supply voltage (max 4 months if unmonitored), (2) inspecting for unintentional grounds (max 4 months), (3) verifying charger float voltage (max 18 months), (4) verifying battery connection resistance (max 18 months) and (5) verifying battery intercell connection resistance (max 18 months), but only the parameters 1, 2 and 3 were in fact being monitored. Listing inapplicable Component attributes for parameters 4 and 5 caused the PSMP to not conform to R1.2. R1.1 of PRC-005-6 states that "All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3." The Entity stated in the PSMP that the tasks of (1) inspecting cell condition of all individual battery cells where cells are visible or measuring battery cell/unit internal ohmic values where the cells are not visible and (2) inspecting the physical condition of the battery rack were performed with max-18-month periodicity (per Table 1-4(a)). These tasks were addressed in a plant procedure that was performed only every 24 months, however; so, while they were in a time-based program, it was not, "as described in Table 1-4 and Table 3." Susquehanna is a subsidiary of Talen Energy (Talen). This noncompliance involves the management practice of asset and configuration management as Talen did not follow its own PRC-005 Maintenance and Testing program for the entity. Talen did not have an effective program in place to ensure that the entity followed its own PRC-005 Maintenance and Testing program and that lack of an effective program is a root cause of this noncompliance. This noncompliance began on October 1, 2016, when the entity first failed to follow its PRC-005 program in regards to testing and ended on March 29, 2017, when the entity finished completing the missed tests. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The entity has a strong battery maintenance program that meets all NRC & IEEE requirements, satisfying requirements for a highly reliable DC Supply system. The entity conducts daily visual inspections, monitoring several physical parameters to ensure high reliability. In addition, other voltage & specific gravity checks are performed on increased frequency for trending the health of the batteries. Monthly & quarterly battery rack inspections include a look at the housekeeping of equipment. The entity performs surveillance outside of standard range and potential deviation is documented and reported. No nuclear operability concerns have been reported with any of the batteries subject to these NERC requirements. All NRC surveillance requirements were satisfactorily completed. No compliance or performance issues occurred during the time frame of this violation. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) revised the entity's DC Supply PSMP and maintenance procedures; 2) tested and inspected the Unit 1 batteries and they are currently meeting the 18 month frequency requirement; and 3) completed the missed Unit 2 maintenance tasks (completed during the Unit 2 RIO outage scope).
2018-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Susquehanna Nuclear LLC (Susquehanna) | NCR00889 | RFC2018019408 | PRC-005-6 | R3 | On April 1, 2017, Susquehanna submitted a Self-Log stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R6. Susquehanna did perform the hands-on work for which continuous monitoring was incorrectly claimed, but for Unit 2 the tasks specified in Table 1-4(a) of (1) verify battery terminal connection resistance, (2) verify battery intercell or unit-to-unit connection resistance, (3) Inspect cell condition of all individual battery cells where cells are visible – or measure battery cell/unit internal ohmic values where the cells are not visible, and (4) inspect physical condition of battery rack were each missed for one, max-18-months interval since the plant transitioned from PRC-005-1 to PRC-005-2 (now PRC-005-6). Susquehanna is a subsidiary of Talen Energy (Talen). This noncompliance involves the management practice of asset and configuration management as Talen did not follow its own PRC-005 Maintenance and Testing program for the entity. Talen did not have an effective program in place to ensure that the entity followed its own PRC-005 Maintenance and Testing program and that lack of an effective program is a root cause of this noncompliance. This noncompliance began on October 1, 2016, when the entity first failed to follow its PRC-005 program in regards to testing and ended on March 29, 2017, when the entity finished completing the missed tests. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The entity has a strong battery maintenance program that meets all NRC & IEEE requirements, satisfying requirements for a highly reliable DC Supply system. The entity conducts daily visual inspections, monitoring several physical parameters to ensure high reliability. In addition, other voltage & specific gravity checks are performed on increased frequency for trending the health of the batteries. Monthly & quarterly battery rack inspections include a look at the housekeeping of equipment. The entity performs surveillance outside of the standard range and potential deviation is documented and reported. No nuclear operability concerns have been reported with any of the batteries subject to these NERC requirements. All NRC surveillance requirements were satisfactorily completed. No compliance or performance issues occurred during the time frame of this compliance violation. No harm is known to have occurred. | To mitigate this noncompliance, the entity: 1) revised the entity's DC Supply Protection System Maintenance Program and maintenance procedures; 2) tested and inspected the Unit 1 batteries and they are currently meeting the 18 month frequency requirement; and 3) completed the missed Unit 2 maintenance tasks (completed during the Unit 2 RIO outage scope).
2018-04-30 | SERC Reliability Corporation (SERC) | James River Genco, LLC (JamesRv) | NCR01262 | SERC2016016376 | PRC-024-2 | R1 | On October 18, 2016, JamesRv submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. JamesRv did not meet the NERC implementation schedule for verifying 40 percent of its applicable Facilities' protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1. JamesRv incorrectly believed that the implementation schedule required that 40 percent of all relay functions at the Facility be compliant, as opposed to 40 percent of all units. The JamesRv facility consists of two steam turbine generators, each of which has one multifunction digital relay with six relay functions, for 12 relay functions at the facility. The frequency protection relay function for each generator did not comply with PRC-024-2 on July 1, 2016. On August 24, 2016, while reviewing the PRC-024-2 Reliability Standard Audit Worksheet, JamesRv identified its misinterpretation of the implementation schedule, and thus its noncompliance. JamesRv determined that the main cause of the noncompliance was its misunderstanding of the meaning of the defined term of “Applicable Facility.” This noncompliance started on July 1, 2016, when JamesRv did not meet the implementation schedule, and ended on October 8, 2016, when JamesRv changed the relay settings to meet the “no trip zone” requirement. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. JamesRv’s failure to verify that the frequency relays are set to not trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, the JamesRv facility consists of two steam turbine generators with output capacity of 57 MW per unit, with capacity factors of 5.04% and 3.35% respectively, in the PJM Region, which has more than 176,500 MW of installed generation. Therefore, the two 57 MW units that were noncompliant would have a minimal impact if they tripped offline. JamesRv revised the generator overfrequency and underfrequency settings to add additional trip points at various frequencies. JamesRv revised the line overfrequency setting from >/= 61.4 Hz at 2 seconds to >/= 61.8 Hz at 0.5 seconds and revised the line underfrequency setting from >/= 57.6 Hz at 1 second to >/= 57.8 Hz at 0.5 seconds. The existing settings for all other voltage and frequency protection functions were set outside of the no-trip zone of operation and therefore no additional setting changes were necessary. JamesRv reported that there have been no unit trips based on incorrect frequency relay settings. No harm is known to have occurred. SERC considered JamesRv compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, JamesRv: 1) changed the relay settings at all JamesRv units; 2) created a notification in the form of a recurring preventive maintenance work order or as an obligation that escalates until completed in the JamesRv tracking system for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable standards incorporating the NERC initial notification of confirmation of the implementation or due date(s); and 3) created a tracking spreadsheet to monitor compliance deadlines and status for responsible parties. The Corporate Reliability Standards Compliance Group will coordinate all new or modified standards with the necessary engineering groups within the Cogentrix organization, to include, but not limited to, submittal of verification to the region (SERC) to ensure the understanding of all aspects of the Reliability Standard including Requirements, implementation plans, and schedules, as necessary. The objective is to ensure JamesRv develops a complete implementation strategy to convey acceptable approaches with clear understanding, responsibilities, and timelines.
2018-04-30 | SERC Reliability Corporation (SERC) | Oglethorpe Power Corporation (OPC) | NCR01287 | SERC2016016192 | PRC-024-2 | R2 | On September 22, 2016, Oglethorpe Power Corporation (OPC) submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. SERC later determined that OPC self-reported under the wrong requirement and that it should have reported a noncompliance with PRC-024-2 R2. OPC did not meet the NERC implementation schedule for verifying its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 2 for 40 percent of its applicable Facilities by July 1, 2016. On September 7, 2016, OPC, based on SERC’s response to a similar noncompliance with PRC-019, identified that it mistakenly interpreted the implementation plan as verifying settings for 40 percent of the Facilities by July 1, 2016 and implementing necessary setting changes within 90 days of July 1, 2016. OPC completed the assessment for four of its nine facilities by July 1, 2016; however, based on its incorrect interpretation, OPC deferred implementing the necessary setting changes for the two Facilities that required setting changes until the next maintenance outage of each unit, which was after July 1, 2016. This noncompliance started on July 1, 2016, when OPC did not meet the implementation schedule, and ended on October 1, 2016, when OPC changed the relay settings to meet the “no trip zone” requirement. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OPC’s failure to set protective relaying such that the generator voltage protective relaying does not trip the applicable generating units within the “no trip zone” could lead to an individual generator tripping for a system event that should not have caused the generator to trip. However, the instant noncompliance includes nine units at two sites representing approximately 1,090 MW of OPC’s 7,972 MW in the Southern Company Services area. The incorrect relay settings were 1.18 pu for overvoltage. OPC changed the overvoltage relay settings by adding a two second time delay. The average site capacity factors for the two sites were 82 percent and five percent. No harm is known to have occurred. SERC considered Oglethorpe Power Corporation’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, OPC: 1) implemented the setting changes; 2) reviewed schedules for the additional phases of implementation of PRC-024-2 to ensure both the studies and the setting changes for the designated percentage of facilities are completed in the increments due; and 3) implemented a process to ensure all key parties to Standards compliance and implementation of compliance with new standards fully understand and agree regarding what action is required and when by discussion of applicable standards: a. when filed with FERC approval, with follow-up to confirm mutual understanding of required activities, milestones, and documentation. b. upon the issuance of FERC Order approving a new or revised Reliability Standard.
2018-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Borger Energy Associates, LP (BOEA) | NCR01062 | SPP2016016132 | PRC-019-2 | R.1; R1.1, 1.1.1, 1.1.2 | On September 8, 2016, BOEA submitted a Self-Report stating that, as a Generator Owner, it was not compliant with PRC-019-2 R1, R1.1, R1.1.1, and R1.1.2 because it failed to verify the coordination of the voltage regulating system controls, (including in-service limiters and protection functions) with the equipment capabilities and settings of the Protection System devices for Gas Turbine Generator 1 (CTG1). Specifically, during a PRC-019 program assessment in September 2016, BOEA discovered that (1) the V/Hz exciter limiter for CTG1 was not set to operate prior to a generator V/Hz protection relay at V/Hz ratios greater than 1.14 pu. and (2) the loss of excitation relay’s zone 2 element was set to trip CTG1 before the under excitation limiter could act when generator load is in the range of 0 – 25 MW. The root cause of this instance of noncompliance was a combination of human error and ineffective controls. BOEA plant personnel incorrectly assumed that the MOD-025, MOD-026 and MOD-027 Model Validation and Reactive Capability Testing performed in 4th quarter of 2015 and April 2016 fulfilled the requirements of PRC-019. Further, BOEA scheduled its PRC-019 program assessment after the PRC-019 July 1, 2016, effective date, thereby discovering the noncompliance after the standard effective date. The noncompliance started on July 1, 2016, the effective date of PRC-019-2 R1, and ended April 20, 2017, the date BOEA completed the coordination studies of the voltage regulating system controls, (including in-service limiters and protection functions) according to the requirement of PRC-019-2 R1. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly coordinate limiters and generator protection relays can cause the generator Automatic Voltage Regulator to impose unacceptable operating conditions on the generator. Such conditions, i.e. over excitation and under excitation, have the potential to affect the reliability of the BPS by decreasing the generator’s ability to withstand system voltage events and increasing the probability of generator trips due to loss of synchronism and generator field overloads. As to the V/Hz protection relay that was set to operate before the V/Hz limiter, the limiter was set to operate before the protection relay under steady-state system operating condition, i.e., V/Hz ratios between 105 and 110 percent of the normal V/Hz value. As to the loss of excitation relay’s zone 2 element that was set to operate before the under excitation limiter, the incorrect setting was limited to a range of 0 – 25 MW, which is below the minimum load of CTG1. CTG1 is a small 115 MW gas combustion turbine generator. No harm is known to have occurred. BOEA has no relevant prior violations for PRC-019-2 R1 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance BOEA: 1. performed an internal review to assess the root cause of the noncompliance; 2. evaluated current settings to ensure proper coordination and compliance with PRC-019-2; 3. performed a relay coordination study; 4. made appropriate relay setting changes; and 5. increased corporate oversight by adding a new position, Director of NERC/FERC Compliance. SPP RE has verified the completion of all mitigation activity.
2018-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Caprock Wind LLC (Caprock) | NCR05059 | SPP2017018216 | VAR-002-4 | R4 | On August 18, 2017, Caprock submitted a Self-Report stating that, as a Generator Operator, it was not compliant with VAR-002-4 R4 because it did not notify its Transmission Operator (TOP) within 30 minutes of a change in its reactive capability. Specifically, on July 14, 2017, Caprock removed capacitors 5 – 9 from service at its wind farm in order to facilitate repairs to one of the 3.6 MVAR capacitors. When the Caprock Plant Manager notified the Caprock control center of the required outage, the Plant Manager mistakenly informed the control center that notification of the TOP was unnecessary because reactive capacity above what was then being delivered was available. The control center did not notify the Caprock TOP, Xcel Energy of the capacitor bank outage. The capacitors were out of service from 12.49 p.m. to 2:16 p.m. that day. This noncompliance started at 1:09 p.m. on July 14, 2017, when Caprock failed to notify its TOP of the change in reactive capability, and ended at 2:16 p.m. on July 14, 2017, when the reactive capability of Caprock was restored. The root cause of this noncompliance was failure to adequately disseminate operational procedures and ensure plant staff are trained on such procedures. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to notify the TOP of changes in reactive capability has the potential to affect the reliability of the BPS by limiting the TOPs situational awareness of reactive capacity available to support system voltage contingencies. Here the risk to the BPS is mitigated because Caprock: is an 80 MW wind farm, capable of providing minimal real and reactive capacity; utilizes Dynamic Volt-Amp Reactive compensation to stabilize and regulate voltage; and was maintaining its voltage schedule and providing 12.49 MVAR of reactive support. Additionally, the duration of the capacitor bank outage was short, one hour and 27 minutes and an additional 76 MVAR of reactive capacity was available if needed. No harm is known to have occurred. Caprock has no relevant prior violations of VAR-002-4 R4 or any other standards that are similar in nature. | To mitigate this noncompliance, Caprock: 1) reviewed the event with appropriate staff on its August 22, 2017 Operations Call; 2) provided the event presentation, the Reactive Capability Outage Reporting Procedure and the VAR-002-4 Standard to all Plant Managers and control center Operators; and 3) required acknowledgement of the aforementioned materials from the affected staff. SPP RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | City of College Station (COCS) | NCR04032 | TRE2017017520 | EOP-008-1 | R7; R7.2 | During a Compliance Audit conducted from March 20, 2017 through May 1, 2017, Texas RE determined that COCS, as a Transmission Operator (TOP), was in noncompliance with EOP-008-1 R7.2. In particular, COCS failed to conduct and document results of an annual test of its Operating Plan that demonstrates the backup functionality for a minimum of two continuous hours. On August 12, 2015, COCS conducted its annual EOP-008-1 R7.2 Backup Control Center (BUCC) functionality test. Among other things, the functionality test required COCS to operate from its BUCC for two continuous hours. While performing the 2015 test, however, COCS only operated from its BUCC for one hour and 38 minutes, 22 minutes less that the required continuous operating time. The root cause of this noncompliance was a misunderstanding regarding how to calculate the two-hour continuous operating requirement. Specifically, COCS mistakenly believed that the two-hour operating requirement applied to the entire BUCC functionality testing exercise, including the time to transition to the BUCC. As such, COCS personnel incorrectly believed that they had operated at the BUCC for sufficient time when they ended the exercise. This noncompliance started on January 1, 2016, the first day following the 2015 calendar year in which COCS failed to perform the required annual BUCC functionality test by operating at the BUCC for at least two continuous hours, and ended on December 20, 2016, when COCS successfully performed the next required annual BUCC functionality test for at least two hours. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, COCS successfully transferred to and operated from the BUCC for one hour and 38 minutes, limiting the potential risk that COCS personnel could not successfully transfer to the BUCC or that the BUCC would not function properly following loss of the primary Control Center. Second, during COCS’s subsequent 2016 BUCC functionality test, COCS successfully transferred to and operated from its BUCC for two hours and 25 minutes, demonstrating that the COCS personnel and the BUCC could perform critical reliability functions in the event of the loss of the primary Control Center. No harm is known to have occurred. Texas RE considered COCS’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, COCS: 1) successfully performed the next required annual BUCC functionality test in 2016, including operating from the BUCC for more than two continuous hours; and 2) asserted that it conducted a meeting with applicable personnel regarding BUCC functionality testing requirements. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT) | NCR04056 | TRE2017017792 | BAL-001-TRE-1 | R2 | On June 20, 2017, ERCOT submitted a Self-Report stating that, as a Balancing Authority (BA), it was in noncompliance with BAL-001-TRE-1 R2. Specifically, ERCOT did not calculate the Primary Frequency Response (PFR) of generators for two Frequency Measureable Events (FMEs). In order to calculate accurate generator PFR scores, ERCOT uses a 2-second scan rate. On March 9, 2017, ERCOT updated its Energy Management System (EMS). In the process, ERCOT personnel manually entered incorrectly formatted Supervisory Control and Data Acquisition (SCADA) scan rate parameters. ERCOT’s EMS failed to recognize these scan rate parameters and reverted to a default 10-second scan rate. Upon reviewing their PFR performance data, two generators notified ERCOT of potential issues with their calculations. ERCOT subsequently determined that because it used a 10-second scan rate, it had failed to accurately calculate generator PFR scores for two FMEs on March 9, 2017 and April 13, 2017 as required. On May 16, 2017, ERCOT personnel revised the scan rate parameter, resetting it to a 2-second interval. The root cause of this noncompliance was an insufficient process to implement updates to the ERCOT EMS. In particular, ERCOT relied on a manual process to enter SCADA scan-rate parameters. As a result, when ERCOT personnel entered an incorrect scan rate, ERCOT’s scan rate reverted to a default 10-second rate. This noncompliance began on March 9, 2017, when ERCOT failed to calculate generator PFR scores for the first FME at issue, and ended on April 13, 2017, when ERCOT failed to calculate generator PFR scores for the last FME at issue. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, this issue does not involve the actual PFR to an FME, but rather the process for measuring individual generator PFR responses. Second, the overall market frequency response in ERCOT is robust. For 2017, the ERCOT Interconnection minimum Frequency Response (IMFR) is 381 and the average for IMFR in the first half of 2017 was 966. Finally, the noncompliance duration was short, impacting only two FMEs out of a total of 29 FMEs in 2017. No harm is known to have occurred. Texas RE considered ERCOT’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, ERCOT: 1) re-set the SCADA scan rate to two seconds; 2) added a step to the automated database sequence to maintain the SCADA parameter at two seconds and eliminate the need to manually enter the scan rate during the post-deployment process; and 3) began reviewing scan rate logs during weekly meetings to serve as an additional check to the new automated process to ensure that the scan rate is maintained at two seconds. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2017017255 | MOD-025-2 | R1 | On March 20, 2017, NOTWIN001 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, NOTWIN001 failed to verify the Real Power capability of its wind generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. NOTWIN001 determined that it had not completed its Real Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, NOTWIN001 performed the required Real Power capability verification testing of its generation Facility on May 23, 2017, and submitted the results to its Transmission Planner (TP) on July 13, 2017. The root cause of this noncompliance was that NOTWIN001 misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, NOTWIN001 mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on July 13, 2017, when NOTWIN001 submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, NOTWIN001 previously provided Reactive Power verifications under region-specific output conditions within five years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, NOTWIN001 provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in 2016 and 2017. These submissions are used to coordinate the development of transmission planning models with regional TPs. Finally, NOTWIN001 has a nameplate capacity of only 153 MW and operated only at approximately a 32% capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered NOTWIN001’s and its affiliates' MOD-025-2 R1 compliance history in determining the disposition track. NOTWIN001 has no relevant prior instances of noncompliance. However, four NOTWIN001 affiliates have relevant prior noncompliance records involving MOD-025-2 R1 (TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Real Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, NOTWIN001: 1) completed the required Real Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2017017256 | MOD-025-2 | R2 | On March 20, 2017, NOTWIN001 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. In particular, NOTWIN001 failed to verify the Reactive Power capability of its wind generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. NOTWIN001 determined that it had not completed its Reactive Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, NOTWIN001 performed the required Reactive Power capability verification testing of its generation Facility on May 23, 2017, and submitted the results to its Transmission Planner (TP) on July 13, 2017. The root cause of this noncompliance was that NOTWIN001 misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, NOTWIN001 mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on July 13, 2017, when NOTWIN001 submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, NOTWIN001 previously provided Reactive Power verifications under region-specific output conditions within five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, NOTWIN001 provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in 2016 and 2017. These submissions are used to coordinate the development of transmission planning models with regional TPs. Finally, NOTWIN001 has a nameplate capacity of only 153 MW and operated only at approximately a 32% capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered NOTWIN001’s and its affiliates' MOD-025-2 R2 compliance history in determining the disposition track. NOTWIN001 has no relevant prior instances of noncompliance. However, four NOTWIN001 affiliates have relevant prior noncompliance records involving MOD-025-2 R2 (TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Reactive Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, NOTWIN001: 1) completed the required Reactive Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019490 | MOD-025-2 | R1 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Real Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report applied to Cimarron Wind Power II, LLC (Cimarron) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11240. Accordingly, Texas RE is processing this MOD-025-2 R1 issue for Cimarron likewise under Notrees Windpower, LP. Cimarron determined that it had not completed its Real Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, Cimarron performed the required Real Power capability verification testing of its generation Facility on November 18, 2016, and submitted the results to its Transmission Planner (TP) on January 10, 2017. The root cause of this noncompliance was that Cimarron misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, Cimarron mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on January 10, 2017, when Cimarron submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. Cimarron is a 131 MW variable generation wind farm that operated only at approximately a 46% capacity factor during the issue period and relies solely on current wind conditions to determine its Real Power capability. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered Cimarron’s and its affiliates' MOD-025-2 R1 compliance history in determining the disposition track. Cimarron has no relevant prior instances of noncompliance. However, four Cimarron affiliates have relevant prior noncompliance records involving MOD-025-2 R1 (TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Real Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, Cimarron: 1) completed the required Real Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019491 | MOD-025-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Reactive Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report applied to Cimarron Wind Power II, LLC (Cimarron) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11240. Accordingly, Texas RE is processing this MOD-025-2 R2 issue for Cimarron likewise under Notrees Windpower, LP. Cimarron determined that it had not completed its Reactive Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, Cimarron performed the required Reactive Power capability verification testing of its generation Facility on November 18, 2016, and submitted the results to its Transmission Planner (TP) on January 10, 2017. The root cause of this noncompliance was that Cimarron misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, Cimarron mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on January 10, 2017, when Cimarron submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. Cimarron is a 131 MW variable generation wind farm that operated only at approximately a 46% capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered Cimarron’s and its affiliates' MOD-025-2 R2 compliance history in determining the disposition track. Cimarron has no relevant prior instances of noncompliance. However, four Cimarron affiliates have relevant prior noncompliance records involving MOD-025-2 R2 (TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Reactive Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, Cimarron: 1) completed the required Reactive Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019492 | MOD-025-2 | R1 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Real Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report properly applied to Ironwood Windpower, LLC (Ironwood) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11257. Accordingly, Texas RE is processing this MOD-025-2 R1 issue for Ironwood likewise under Notrees Windpower, LP. Ironwood determined that it had not completed its Real Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, Ironwood performed the required Real Power capability verification testing of its generation Facility on November 18, 2016, and submitted the results to its Transmission Planner (TP) on January 10, 2017. The root cause of this noncompliance was that Ironwood misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, Ironwood mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on January 10, 2017, when Ironwood submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. Ironwood is a 168 MW variable generation wind farm that operated only at approximately a 43% capacity factor during the issue period and relies solely on current wind conditions to determine its Real Power capability. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered Ironwood’s and its affiliates' MOD-025-2 R1 compliance history in determining the disposition track. Ironwood has no relevant prior instances of noncompliance. However, four Ironwood affiliates have relevant prior noncompliance records involving MOD-025-2 R1 (TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Real Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, Ironwood: 1) completed the required Real Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019493 | MOD-025-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Reactive Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report properly applied to Ironwood Windpower, LLC (Ironwood) as a GO in the Southwest Power Pool Regional Entity (SPP RE) region under NCR11257. Accordingly, Texas RE is processing this MOD-025-2 R2 issue for Ironwood likewise under Notrees Windpower, LP. Ironwood determined that it had not completed its Reactive Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, Ironwood performed the required Reactive Power capability verification testing of its generation Facility on November 18, 2016, and submitted the results to its Transmission Planner (TP) on January 10, 2017. The root cause of this noncompliance was that Ironwood misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, Ironwood mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on January 10, 2017, when Ironwood submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. Ironwood is a 168 MW variable generation wind farm and operated only at approximately a 43% capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered Ironwood’s and its affiliates' MOD-025-2 R2 compliance history in determining the disposition track. Ironwood has no relevant prior instances of noncompliance. However, four Ironwood affiliates have relevant prior noncompliance records involving MOD-025-2 R2 (TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Reactive Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, Ironwood: 1) completed the required Reactive Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019494 | MOD-025-2 | R1 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Real Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report properly applied to Three Buttes Windpower, LLC (Three Buttes) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR10345. Accordingly, Texas RE is processing this MOD-025-2 R1 issue for Three Buttes likewise under Notrees Windpower, LP. Three Buttes determined that it had not completed its Real Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, Three Buttes performed the required Real Power capability verification testing of its generation Facility on September 13, 2017, and submitted the results to its Transmission Planner (TP) on October 13, 2017. The root cause of this noncompliance was that Three Buttes misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, Three Buttes mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on October 13, 2017, when Three Buttes submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. Three Buttes is a 99 MW variable generation wind farm that operated only at approximately a 33% capacity factor during the issue period and relies solely on current wind conditions to determine its Real Power capability. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered Three Buttes’ and its affiliates' MOD-025-2 R1 compliance history in determining the disposition track. Three Buttes has no relevant prior instances of noncompliance. However, four Three Buttes affiliates have relevant prior noncompliance records involving MOD-025-2 R1 (TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Real Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, Three Buttes: 1) completed the required Real Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019495 | MOD-025-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Reactive Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report properly applied to Three Buttes Windpower, LLC (Three Buttes) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR10345. Accordingly, Texas RE is processing this MOD-025-2 R2 issue for Three Buttes likewise under Notrees Windpower, LP. Three Buttes determined that it had not completed its Reactive Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, Three Buttes performed the required Reactive Power capability verification testing of its generation Facility on September 13, 2017, and submitted the results to its Transmission Planner (TP) on October 13, 2017. The root cause of this noncompliance was that Three Buttes misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, Three Buttes mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on October 13, 2017, when Three Buttes submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. Three Buttes is a 99 MW variable generation wind farm that operated only at approximately a 33% capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered Three Buttes’ and its affiliates' MOD-025-2 R2 compliance history in determining the disposition track. Three Buttes has no relevant prior instances of noncompliance. However, four Three Buttes affiliates have relevant prior noncompliance records involving MOD-025-2 R2 (TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Reactive Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, Three Buttes: 1) completed the required Reactive Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019496 | MOD-025-2 | R1 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Real Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report properly applied to Top of the World Wind Energy, LLC (TOW) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR11090. Accordingly, Texas RE is processing this MOD-025-2 R1 issue for TOW likewise under Notrees Windpower, LP. TOW determined that it had not completed its Real Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, TOW performed the required Real Power capability verification testing of its generation Facility on November 8, 2017, and submitted the results to its Transmission Planner (TP) on November 10, 2017. The root cause of this noncompliance was that TOW misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, TOW mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline by July 1, 2016. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on November 10, 2017, when TOW submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. TOW is a 200 MW variable generation wind far that operated only at approximately a 33% capacity factor during the issue period and relies solely on current wind conditions to determine its Real Power capability. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered TOW’s and its affiliates' MOD-025-2 R1 compliance history in determining the disposition track. TOW has no relevant prior instances of noncompliance. However, four TOW affiliates have relevant prior noncompliance records involving MOD-025-2 R1 (TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017260, TRE2017017263, TRE2017017267, and TRE2017017271 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Real Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, TOW: 1) completed the required Real Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | TRE2018019497 | MOD-025-2 | R2 | On March 20, 2017, Duke Energy Renewables (DERS) submitted a Self-Report through an existing multi-region registered entity agreement under Notrees Windpower, LP stating that Generator Owners (GOs) located in regions outside of the Texas RE footprint had failed to verify their respective Reactive Power capabilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Subsequently, on April 5, 2018, Texas RE determined that all issues described in the original self-report properly applied to Top of the World Wind Energy, LLC (TOW) as a GO in the Western Electricity Coordinating Council (WECC) region under NCR11090. Accordingly, Texas RE is processing this MOD-025-2 R2 issue for TOW likewise under Notrees Windpower, LP. TOW determined that it had not completed its Reactive Power capability verification testing by the July 1, 2016 deadline for its wind generation Facility as required. As a result, TOW performed the required Reactive Power capability verification testing of its generation Facility on November 8, 2017, and submitted the results to its Transmission Planner (TP) on November 10, 2017. The root cause of this noncompliance was that TOW misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single wind generation Facilities. In particular, TOW mistakenly believed that because it only owned one wind generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on November 10, 2017, when TOW submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system. TOW is a 200 MW variable generation wind farm and operated only at approximately a 33% capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered TOW’s and its affiliates' MOD-025-2 R2 compliance history in determining the disposition track. TOW has no relevant prior instances of noncompliance. However, four TOW affiliates have relevant prior noncompliance records involving MOD-025-2 R2 (TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the previous issues occurred concurrently with this noncompliance, and the mitigation for these previous issues likewise addresses prevention of recurrence of the current instance. Affiliate Compliance History TRE2017017261, TRE2017017264, TRE2017017268, and TRE2017017272 for Mesquite Creek Wind LLC (NCR11511), Los Vientos Windpower IA, LLC (NCR11267), Los Vientos Windpower IB, LLC (NCR11266), and Los Vientos Windpower III, LLC (NCR11538) – In the previous instances of noncompliance, the affiliates also failed to verify the Reactive Power capability of each of its Facilities in accordance with MOD-025-2, Attachment 1 because the affiliates misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation Facilities. | To mitigate this noncompliance, TOW: 1) completed the required Reactive Power capability verification testing; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Meadow Creek Project Company LLC (MCREEK) | NCR11303 | WECC2017017165 | MOD-025-2 | R1 | On March 1, 2017, MCREEK submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, MCREEK reported that it failed to verify Real Power capability of one applicable Facility, in accordance with Attachment 1 of the Standard, by the effective date of the Standard; and therefore, also failed to submit verification results to its Transmission Planner (TP), in accordance with Attachment 2 of the Standard, by the effective date of the Standard. MCREEK reported that it has one applicable Facility, which is a 119.7MW wind facility. MCREEK was under the assumption that because it has only a single applicable Facility, testing of its Real Power Capability would not need to be completed until July 1, 2019, when the Standard requires 100% of applicable Facilities to be complete. Upon review by a an independent contractor, MCREEK became aware that testing had not been completed in accordance with the actual effective date of the Standard and Requirements, which was July 1, 2016. WECC reviewed the Self-Certification and, after further discussions with MCREEK and analysis of data request responses, determined that MCREEK failed to verify Real Power capability of its applicable Facility, in accordance with Attachment 1, by the effective date of the Standard and Requirements, and failed to submit verification results to its TP, in accordance with Attachment 2 of the Standard, by the effective date of the Standard and Requirements. The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, MCREEK did not correctly identify the implementation plan due date and thus did not realize that the Standard was enforceable for their Facility. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MCREEK’s applicable Facility. WECC determined that the end date of this issue is December 1, 2017, when MCREEK completed verification of Real Power capability and submitted the verifications to its TP, in accordance to the Standard and Requirements, for a total of 518 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, MCREEK failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard and Requirements. MCREEK also failed to submit verification results to its Transmission Planner (TP), in accordance with Attachment 2 of the Standard, by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a dispersed wind resource that is not operated at or near its Real Power capability. Additionally, there is a low probability that these issues would cause more than a minimal impact to the reliability of the bulk power system. Further, wind generation is not typically utilized as a firm resource, therefore, MCREEK’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. Further, the capacity of this generating Facility is approximately 119.7 MW; and no harm was known to have occurred. MCREEK does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MCREEK: a. completed verification of the Real Power capability of its applicable Facility in accordance with the Standard; b. submitted verification results to its Transmission Planner in accordance with the Standard; c. engaged an independent utility services contractor to assist in education and awareness of the NERC program, including presentations on current and upcoming Standards, as well as obligations and events within NERC, with the intent to prevent incorrect interpretations of implementation plans going forward; and d. created a calendar to track upcoming and ongoing compliance obligations, including NERC Regulatory Compliance. This calendar will be maintained at the corporate level and presented to each Facility on at least a monthly basis.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Meadow Creek Project Company LLC (MCREEK) | NCR11303 | WECC2017017166 | MOD-025-2 | R2 | On March 1, 2017, MCREEK submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, MCREEK reported that it failed to verify Reactive Power capability of one applicable Facility, in accordance with Attachment 1 of the Standard, by the effective date of the Standard; and therefore, also failed to submit verification results to its Transmission Planner (TP), in accordance with Attachment 2 of the Standard, by the effective date of the Standard. MCREEK reported that it has one applicable Facility, which is a 119.7MW wind facility. MCREEK was under the assumption that because it has only a single applicable Facility, testing of its Reactive Power Capability would not need to be completed until July 1, 2019, when the Standard requires 100% of applicable Facilities to be complete. Upon review by a an independent contractor, MCREEK became aware that testing had not been completed in accordance with the actual effective date of the Standard and Requirements, which was July 1, 2016. WECC reviewed the Self-Certification and, after further discussions with MCREEK and analysis of data request responses, determined that MCREEK failed to verify Reactive Power capability of its applicable Facility, in accordance with Attachment 1, by the effective date of the Standard and Requirements, and failed to submit verification results to its TP, in accordance with Attachment 2 of the Standard, by the effective date of the Standard and Requirements. The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, MCREEK did not correctly identify the implementation plan due date and thus did not realize that the Standard was enforceable for their Facility. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MCREEK’s applicable Facility. WECC determined that the end date of this issue is December 1, 2017, when MCREEK completed verification of Reactive Power capability and submitted the verifications to its TP, in accordance to the Standard and Requirements, for a total of 518 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, MCREEK failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard and Requirements. MCREEK also failed to submit verification results to its Transmission Planner (TP), in accordance with Attachment 2 of the Standard, by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a dispersed wind resource that is not operated at or near its Reactive Power capability. Additionally, there is a low probability that these issues would cause more than a minimal impact to the reliability of the bulk power system. Further, wind generation is not typically utilized as a firm resource, therefore, MCREEK’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. Further, the capacity of this generating Facility is approximately 119.7 MW; and no harm was known to have occurred. MCREEK does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MCREEK: a. completed verification of the Reactive Power capability of its applicable Facility in accordance with the Standard; b. submitted verification results to its Transmission Planner in accordance with the Standard; c. engaged an independent utility services contractor to assist in education and awareness of the NERC program, including presentations on current and upcoming Standards, as well as obligations and events within NERC, with the intent to prevent incorrect interpretations of implementation plans going forward; and d. created a calendar to track upcoming and ongoing compliance obligations, including NERC Regulatory Compliance. This calendar will be maintained at the corporate level and presented to each Facility on at least a monthly basis.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Meadow Creek Project Company LLC (MCREEK) | NCR11303 | WECC2017017167 | PRC-019-2 | R1 | On March 1, 2017, MCREEK submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, MCREEK reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices by the enforcement date of the Standard. WECC reviewed the Self-Certification and determined that MCREEK failed to verify and coordinate their voltage regulating system with their generator capabilities and Protection System devices in at least 40% of their applicable Facilities which could potentially result in the loss of the generator field, instability, and/or damage to the turbine(s). The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, MCREEK incorrectly identified the date that it had to be in compliance with the Standard. Because of this, the entity believed they had to be compliant by July 1, 2019, instead of July 1, 2016. Therefore, the entity did not meet the requirements of this Standard by the enforceable date. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for MCREEK’s applicable Facility. WECC determined that the end date of this issue is December 1, 2017, when MCREEK completed verifying coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices, for a total of 518 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, MCREEK failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices of its applicable Facility by the enforcement date of the Standard. Such failure could potentially result in the loss of the generator field, instability, and/or damage to the turbines. However, the Facility in scope is a dispersed wind resource that is not operated in a manner that would approach the voltage or equipment limitations of the Facility. Additionally, there is a low probability that this issue would cause more than a minimal impact to the reliability of the BES. Further, wind generation is not typically utilized as a firm resource, therefore, MCREEK’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. MCREEK has not experienced a Protection System trip or equipment failure due to miscoordination. The Relay Coordination Study performed on the wind Facility in scope documented that there were no settings changes required to be compliant with the Standard. The capacity of this generating Facility is approximately 120 MW, and no harm is known to have occurred. MCREEK does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MCREEK: a. engaged a independent engineering firm to complete the required coordination of the voltage regulating system controls with the applicable equipment capabilities and Protection System settings; b. implemented usage of a regulatory compliance calendar with at least monthly review of upcoming obligations to prevent similar noncompliances; and c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming Standards, as well as obligations and events within NERC, with the intent to prevent incorrect interpretations of implementation plans going forward.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Milford Wind Corridor Phase I, LLC (MILW) | NCR10394 | WECC2017017168 | MOD-025-2 | R1 | On March 1, 2017, MILW submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, MILW reported that it failed to verify Real Power capability of one applicable Facility in accordance with Attachment 1, and to submit the verifications to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard. MILW reported that it has one applicable Facility, which is a 305MW wind facility. MILW was under the assumption that because it has only a single applicable Facility, testing of its Real Power capability would not need to be completed until July 1, 2019, when the Standard requires 100% of applicable Facilities to be complete. Upon review by an independent contractor, MILW became aware that testing had not been completed in accordance with the actual effective date of the Standard and Requirements, which was July 1, 2016. WECC reviewed the Self-Certification and, after further discussions with MILW and analysis of data request responses, determined that MILW failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verifications to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard. The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, MILW did not correctly identify the implementation plan due date and thus did not realize that the Standard was enforceable for their Facility. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MILW’s applicable Facility. WECC determined that the end date of this issue is December 1, 2017, when MILW completed verification of Real Power capability in accordance to the Standard and Requirements, for a total of 518 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, MILW failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verifications to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard and Requirements. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a dispersed wind resource that is not operated at or near its Real Power capability. Additionally, there is a low probability that these issues would cause more than a minimal impact to the reliability of the bulk power system. Further, wind generation is not typically utilized as a firm resource, therefore, MILW’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. No harm was known to have occurred. MILW does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MILW: a. completed verification of the Real Power capability of its applicable Facility in accordance with the Standard; b. submitted the verification results to its Transmission planner in accordance with the Standard; c. engaged an independent utility services contractor to assist in education and awareness of the NERC program, including presentations on current and upcoming Standards, obligations and events within NERC with the intent to prevent incorrect interpretations of implementation plans going forward; and d. created a calendar to track upcoming and ongoing compliance obligations, including NERC Regulatory Compliance.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Milford Wind Corridor Phase I, LLC (MILW) | NCR10394 | WECC2017017169 | MOD-025-2 | R2 | On March 1, 2017, MILW submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, MILW reported that it failed to verify Reactive Power capability of one applicable Facility in accordance with Attachment 1, and to submit the verifications to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard. MILW reported that it has one applicable Facility, which is a 305MW wind facility. MILW was under the assumption that because it has only a single applicable Facility, testing of its Reactive Power capability would not need to be completed until July 1, 2019, when the Standard requires 100% of applicable Facilities to be complete. Upon review by an independent contractor, MILW became aware that testing had not been completed in accordance with the actual effective date of the Standard and Requirements, which was July 1, 2016. WECC reviewed the Self-Certification and, after further discussions with MILW and analysis of data request responses, determined that MILW failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verifications to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard. The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, MILW did not correctly identify the implementation plan due date and thus did not realize that the Standard was enforceable for their Facility. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MILW’s applicable Facility. WECC determined that the end date of this issue is December 1, 2017, when MILW completed verification of Reactive Power capability in accordance to the Standard and Requirements, for a total of 518 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, MILW failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verifications to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard and Requirements. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a dispersed wind resource that is not operated at or near its Reactive Power capability. Additionally, there is a low probability that these issues would cause more than a minimal impact to the reliability of the bulk power system. Further, wind generation is not typically utilized as a firm resource, therefore, MILW’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. No harm was known to have occurred. MILW does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MILW: a. completed verification of the Reactive Power capability of its applicable Facility in accordance with the Standard; b. submitted the verification results to its Transmission planner in accordance with the Standard; c. engaged an independent utility services contractor to assist in education and awareness of the NERC program, including presentations on current and upcoming Standards, obligations and events within NERC with the intent to prevent incorrect interpretations of implementation plans going forward; and d. created a calendar to track upcoming and ongoing compliance obligations, including NERC Regulatory Compliance.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Milford Wind Corridor Phase I, LLC (MILW) | NCR10394 | WECC2017017170 | PRC-019-2 | R1 | On March 1, 2017, MILW submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, MILW reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices by the enforcement date of the Standard. WECC reviewed the Self-Certification and determined that MILW failed to verify and coordinate their voltage regulating system with their generator capabilities and Protection System devices in at least 40% of their applicable Facilities which could potentially result in the loss of the generator field, instability, and/or damage to the turbine(s). The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, MILW incorrectly identified the date that it had to be in compliance with the Standard. Because of this, the entity believed they had to be compliant by July 1, 2019 instead of July 1, 2016. Therefore, the entity did not meet the requirements of this Standard by the enforceable date. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for MILW’s applicable Facility. WECC determined that the end date of this issue is December 1, 2017, when MILW completed verifying coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices, for a total of 518 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MILW failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices of its applicable Facility by the enforcement date of the Standard. Such failure could potentially result in the loss of the generator field, instability, and/or damage to the turbines. However, the Facility in scope is a dispersed wind resource that is not operated in a manner that would approach the voltage or equipment limitations of the Facility. Additionally, there is a low probability that this issue would cause more than a minimal impact to the reliability of the BES. Further, wind generation is not typically utilized as a firm resource, therefore, MILW’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. MILW has not experienced a Protection System trip or equipment failure due to miscoordination. The Relay Coordination Study performed on the wind Facility in scope documented that there were no settings changes required to be compliant with the Standard. The capacity of this generating Facility is approximately 305MW and no harm is known to have occurred. MILW does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MILW: a. engaged a third-party engineering firm to complete the required coordination of the voltage regulating system controls with the applicable equipment capabilities and Protection System settings; b. implemented usage of a regulatory compliance calendar with at least monthly review of upcoming obligations to prevent similar noncompliances; and c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming Standards, obligations and events within NERC with the intent to prevent incorrect interpretations of implementation plans going forward.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Mt. Poso Cogeneration Co. (MTPO) | NCR05254 | WECC2017017195 | MOD-025-2 | R1 | On March 1, 2017, MTPO submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, MTPO reported that it failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1, and also failed to submit verification results to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard. MTPO reported that it has one applicable Facility, which is a 44MW biomass generating plant reaching its Real Power capacity on a daily basis. MTPO understood that the Standard allowed single entities to be compliant by July 1, 2019, and had been working on an implementation plan to be compliant by that date. However, upon retaining an independent contractor to assist with NERC compliance, MTPO was made aware that single entities needed to be compliant by July 1, 2016. WECC reviewed the Self-Certification, and after further discussions with MTPO and analysis of data request responses, determined that MTPO failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard and also failed to submit verification results to its Transmission Planner in accordance with Attachment 2 by the effective date of the Standard. The root cause of the noncompliance was that MTPO misinterpreted the implementation plan and incorrectly identified the date that it had to be in compliance with the Standard. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MTPO’s applicable Facility. WECC determined that the end date of this issue is December 28, 2017, when MTPO provided to its Transmission Planner the results of the completed testing, verifying the Real Power capability in accordance to the Standard and Requirements, for a total of 545 days of noncompliance. | This noncompliance posed minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system. In this instance, MTPO failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit verification results to its Transmission Planner in accordance with Attachment 2 by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a 62MW biomass generation Facility, that typically operates at 44MW, with a single 115kV connection. MTPO has a robust equipment maintenance program and protection systems maintenance program that limits the risk to the bulk power system associated with MOD 025-2 non-compliance. MTPO has implemented good preventative controls to prevent the noncompliance consequence mentioned above. Based on the severity and controls analysis, this non-compliance has a low probability of causing minor harm. No harm is known to have occurred. MTPO does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MTPO: a. engaged an independent contractor to complete verification of Real Power capability of its applicable Facility in accordance with the Standard and Requirements; b. provided its Transmission Planner with the Real Power capability verification reports in accordance with Standard and Requirements; and c. evaluated other Standards that have similar Requirements and entered those testing Requirements into its project management program which sends reminder alerts to users by email when due dates for tasks need to be completed.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Mt. Poso Cogeneration Co. (MTPO) | NCR05254 | WECC2017017196 | MOD-025-2 | R2 | On March 1, 2017, MTPO submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Specifically, MTPO reported that it failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1, and also failed to submit verification results to its Transmission Planner in accordance with Attachment 2 by the effective date of the Standard. MTPO reported that it has one applicable Facility, which is a 44MW biomass generating plant reaching its Reactive Power capacity on a daily basis. MTPO understood that the Standard allowed single entities to be compliant by July 1, 2019, and had been working on an implementation plan to be compliant by that date. However, upon retaining an independent contractor to assist with NERC compliance, MTPO was made aware that single entities needed to be compliant by July 1, 2016. WECC reviewed the Self-Certification, and after further discussions with MTPO and analysis of data request responses, determined that MTPO failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit verification results to its Transmission Planner in accordance with Attachment 2 by the effective date of the Standard. The root cause of the noncompliance was that MTPO misinterpreted the implementation plan and incorrectly identified the date that it had to be in compliance with the Standard. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MTPO’s applicable Facility. WECC determined that the end date of this issue is December 28, 2017, when MTPO provided to its Transmission Planner the results of the completed testing, verifying the Real Power capability in accordance to the Standard and Requirements, for a total of 545 days of noncompliance. | This noncompliance posed minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system. In this instance, MTPO failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit verification results to its Transmission Planner in accordance with Attachment 2 by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a 62MW biomass generation Facility, that typically operates at 44MW, with a single 115kV connection. MTPO has a robust equipment maintenance program and protection systems maintenance program that limits the risk to the bulk power system associated with MOD 025-2 non-compliance. MTPO has implemented good preventative controls to prevent the noncompliance consequence mentioned above. Based on the severity and controls analysis, this non-compliance has a low probability of causing minor harm. No harm is known to have occurred. MTPO does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MTPO: a. engaged an independent contractor to complete verification of Reactive Power capability of its applicable Facility in accordance with the Standard and Requirements; b. provided its Transmission Planner with the Reactive Power capability verification reports in accordance with Standard and Requirements; and c. evaluated other Standards that have similar Requirements and entered those testing Requirements into its project management program which sends reminder alerts to users by email when due dates for tasks need to be completed.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Mt. Poso Cogeneration Co. (MTPO) | NCR05254 | WECC2017017197 | PRC-019-2 | R1 | On March 1, 2017 MTPO submitted a Self-Certification stating that, as Generator Owner, it was in noncompliance with PRC-019-2 R1. SpMTPO reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices by the enforcement date of the Standard. MTPO reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices by the enforcement date of the Standard. Specifically, MTPO had interpreted the Standard to allow entities with a single applicable Facility to be compliant by July 1, 2019, rather than July 1, 2016. WECC reviewed the Self-Certification and after further discussions with MTPO and analysis of data request responses, determined that MTPO failed to verify and coordinate its voltage regulating system with its generator capabilities and Protection System devices in at least 40% of its applicable Facilities, which could potentially result in the loss of its biomass generating plant. The root cause of the noncompliance was that MTPO misinterpreted the implementation plan and incorrectly identified the WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for MTPO’s applicable Facility. WECC determined that the end date of this issue was December 28, 2017, when MTPO completed verifying coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices, for a total of 545 days of noncompliance. ted oversight agreement, please include an accurate description of the issue/risk/mitigation by providing the non-compliant entity-specific facts and circumstances surrounding the noncompliance, for example: | This noncompliance posed minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, MTPO failed to verify and coordinate its voltage regulating system with its generator capabilities and Protection System devices in at least 40% of its applicable Facilities. Such failure could potentially result in the loss of the generator field, instability, and/or damage to the generating equipment. However, the Facility in scope is a 62 MW biomass generating plant that typically operates at 44 MW. MTPO had implemented good preventative controls to prevent the above consequence from occurring, and was working on an implementation plan to be compliant with the Standard. The Relay Coordination Study showed that there were no settings changes required and that the biomass Facility is in compliance with the Standard. Based on the controls analysis performed, this non-compliance had a low probability of causing minor harm. No harm is known to have occurred. MTPO does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, MTPO: a. engaged a third-party firm to complete the required coordination of the voltage regulating system controls with the applicable equipment capabilities and Protection System settings; and b. evaluated other Standards that have similar Requirements and entered those testing requirements into its project management program. The project management system sends reminder alerts to users by email when due dates for tasks need to be completed.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Rockland Wind Farm LLC (RWFL) | NCR11214 | WECC2017017171 | MOD-025-2 | R1 | On March 1, 2017, RWFL submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, RWFL reported that it failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit completed verification reports in accordance with Attachment 2, by the effective date of the Standard. RWFL reported that it has one applicable Facility which is an 80MW wind facility. RWFL was under the assumption that because it has only a single applicable Facility, testing of its Real and Reactive Power Capability would not need to be completed until July 1, 2019, when the Standard requires 100% of applicable Facilities to be complete. Upon review by a independent contractor, RWFL became aware that testing had not been completed in accordance with the effective date of the Standard and Requirements, which was July 1, 2016. WECC reviewed the Self-Certification and, after further discussions with RWFL and analysis of data request responses, determined that RWFL failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit completed verification reports in accordance with Attachment 2, by the effective date of the Standard. The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, RWFL did not correctly identify the implementation plan due date and thus did not realize that the Standard was enforceable for their Facility. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for RWFL’s applicable Facility. WECC determined that the end date of this issue is November 3, 2017, when RWFL completed verifying the Real and Reactive Power capability in accordance to the Standard and Requirements, for a total of 490 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, RWFL failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit completed verification reports in accordance with Attachment 2 by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System bulk power system reliability. However, the Facility in scope is a dispersed wind resource that is not operated at or near the Real Power capability. Additionally, there is a low probability that these issues would cause more than a minimal impact to the reliability of the bulk power system. Wind generation is not typically utilized as a firm resource, therefore, RWFL’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. No harm was known to have occurred. RWFL does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, RWFL: a. verified Real Power capability in accordance with the Standard and Requirements; b. submitted a completed MOD-025-2 Attachment 2 form to its Transmission Planner; b. implemented usage of a regulatory compliance calendar with at least monthly review of upcoming obligations to prevent similar noncompliances; and c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming Standards, obligations and events within NERC with the intent to prevent incorrect interpretations of implementation plans going forward.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Rockland Wind Farm LLC (RWFL) | NCR11214 | WECC2017017172 | MOD-025-2 | R2 | On March 1, 2017, RWFL submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Specifically, RWFL reported that it failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit completed verification reports in accordance with Attachment 2 by the effective date of the Standard. RWFL reported that it has one applicable Facility which is an 80MW wind facility. RWFL was under the assumption that because it has only a single applicable Facility, testing of its Reactive Power Capability would not need to be completed until July 1, 2019, when the Standard requires 100% of applicable Facilities to be complete. Upon review by a third-party consultant, RWFL became aware that testing had not been completed in accordance with the actual effective date of the Standard and Requirements, which was July 1, 2016. WECC reviewed the Self-Certification and, after further discussions with RWFL and analysis of data request responses, determined that RWFL failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard, and also failed to submit completed verification reports in accordance with Attachment 2 by the effective date of the Standard. The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, RWFL did not correctly identify the implementation plan due date and thus did not realize that the Standard was enforceable for their Facility. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for RWFL’s applicable Facility. WECC determined that the end date of this issue is November 3, 2017, when RWFL completed verification of Reactive Power capability and submitted those results to its Transmission Planner in accordance to the Standard and Requirements, for a total of 490 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, RWFL failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard and also failed to submit completed verification reports in accordance with Attachment 2, by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System bulk power system reliability. However, the Facility in scope is a dispersed wind resource that is not operated at or near the Reactive Power capability. Additionally, there is a low probability that these issues would cause more than a minimal impact to the reliability of the bulk power system. Wind generation is not typically utilized as a firm resource, therefore, RWFL’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. No harm was known to have occurred. RWFL does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, RWFL: a. verified Reactive Power capability in accordance with the Standard and Requirements; b. submitted a completed MOD-025-2 Attachment 2 form to its Transmission Planner; b. implemented usage of a regulatory compliance calendar with at least monthly review of upcoming obligations to prevent similar noncompliances; and c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming Standards, obligations and events within NERC with the intent to prevent incorrect interpretations of implementation plans going forward.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Rockland Wind Farm LLC (RWFL) | NCR11214 | WECC2017017173 | PRC-019-2 | R1 | On March 1, 2017, RWFL submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, RWFL reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices by the enforcement date of the Standard. WECC reviewed the Self-Certification and determined that RWFL failed to verify and coordinate their voltage regulating system with their generator capabilities and Protection System devices in at least 40% of their applicable Facilities which could potentially result in the loss of the generator field, instability, and/or damage to the turbine(s). The root cause of the noncompliance was a misunderstanding of the implementation plan. Specifically, RWFL incorrectly identified the date that it had to be in compliance with the Standard. Because of this, the entity believed they had to be compliant by July 1, 2019 instead of July 1, 2016. Therefore, the entity did not meet the requirements of this Standard by the enforceable date. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for RWFL’s applicable Facility. WECC determined that the end date of this issue is January 19, 2018, when RWFL completed verifying coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices, for a total of 567 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, RWFL failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices of its applicable Facility by the enforcement date of the Standard. Such failure could potentially result in the loss of the generator field, instability, and/or damage to the turbines. However, the Facility in scope is a dispersed wind resource that is not operated in a manner that would approach the voltage or equipment limitations of the Facility. Additionally, there is a low probability that this issue would cause more than a minimal impact to the reliability of the bulk power system. Wind generation is not typically utilized as a firm resource, therefore, RWFL’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. Further, RWFL has not experienced a Protection System trip or equipment failure due to miscoordination. The Relay Coordination Study showed that there were no settings changes required and that the wind facility is in compliance with the Standard. The capacity of this generating Facility is approximately 80 MW and no harm is known to have occurred. RWFL does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, RWFL: a. engaged a third-party engineering firm to complete the required coordination of the voltage regulating system controls with the applicable equipment capabilities and Protection System settings; b. implemented usage of a regulatory compliance calendar with at least monthly review of upcoming obligations to prevent similar noncompliances; and c. engaged a third-party utility services contractor to assist in education and awareness of the NERC program, including monthly presentations on current and upcoming Standards, obligations and events within NERC with the intent to prevent incorrect interpretations of implementation plans going forward.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Watson Cogeneration Company (WCGN) | NCR05454 | WECC2017017110 | MOD-025-2 | R1 | On February 28, 2017, WCGN submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. WCGN reported that it failed to complete verification of the Real Power capability of at least 40% of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard, and also failed to provide its Transmission Planner with complete verification reports in accordance with Attachment 2 by the effective date of the Standard. WECC reviewed the Self-Report, and determined that WCGN failed to verify Real Power capability of its applicable facilities by July 1, 2016, the date MOD-025-2 became mandatory and enforceable. Specifically, after receiving Attachment 2 forms for Real Power capabilities, the Transmission Planner was unable to determine if the full load, overexcited capability test was held for 15 minutes as opposed to 1 hour, no ambient conditions were listed, and no transformer data was included. The root cause of the noncompliance was a misunderstanding of the implementation plan for MOD-025-2 in which WCGN thought that the 5-year WECC model validation program met the Requirements of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable. WECC determined that the end date of this issue was February 23, 2017, when WCGN sent the full attachment to its Transmission Planner, for a total of 238 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WCGN failed to provide its Transmission Planner with verification of the Real Power capability for at least 40% of its applicable Facilities per the MOD-025-2 implementation plan when the entity failed to include three data points in their Attachment 2 submissions to the Transmission Planner. Such failure could result in the use of inaccurate information in planning models used to assess bulk power system reliability. Therefore, the bulk power system could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. The scope of this noncompliance was for 6 facilities with a combined capacity of 405 MW. However, these issues would not likely have significantly affected current planning models as WCGN tested its unit in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The entity had previously provided the Transmission Planner with the required model information for all units based on the 5-year WECC Generating Unit Model Validation. Therefore, there was a low probability that these issues would cause minimal impact to the reliability of the bulk power system. No harm is known to have occurred. WCGN does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, WCGN: a. verified Real Power capabilities in accordance with the Standard and Requirement; b. submitted completed MOD-025-2 Attachment 2 forms to its Transmission Planner for each of its six generators. These updated Attachment 2 forms contained the information missing prior and were in accordance with Attachment 1; and c. updated its process document explaining the requirements for MOD-025-2, clearly stating for each Requirement, what steps need to be taken to maintain compliance with MOD-025-2.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Watson Cogeneration Company (WCGN) | NCR05454 | WECC2017017111 | MOD-025-2 | R2 | On February 28, 2017, WCGN submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. WCGN reported that it failed to complete verification of the Reactive Power capability of at least 40% of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard and also failed to provide its Transmission Planner with complete verification reports in accordance with Attachment 2 by the effective date of the Standard. WECC reviewed the Self-Reports, and determined that WCGN failed to verify Reactive Power capability of its applicable facilities by July 1, 2016, the date MOD-025-2 became mandatory and enforceable. Specifically, after receiving Attachment 2 forms for Reactive Power capabilities, the Transmission Planner was unable to determine if the full load, overexcited capability test was held for 15 minutes as opposed to 1 hour, no ambient conditions were listed, and no transformer data was included. The root cause of the noncompliance was a misunderstanding of the implementation plan for MOD-025-2 in which WCGN thought that the 5-year WECC model validation program met the Requirements of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable. WECC determined that the end date of this issue was February 23, 2017, when WCGN sent the full attachment to its Transmission Planner, for a total of 238 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WCGN failed to provide its Transmission Planner with verification of the Reactive Power capability for at least 40% of its applicable Facilities per the MOD-025-2 implementation plan when the entity failed to include three data points in their Attachment 2 submissions to the Transmission Planner. Such failure could result in the use of inaccurate information in planning models used to assess bulk power system reliability. Therefore, the bulk power system could be planned with the expectation that a generator has the capability to mitigate a modeled system contingency, whereas it may not completely mitigate the contingency. The scope of this noncompliance was for 6 facilities with a combined capacity of 405 MW. However, these issues would not likely have significantly affected current planning models as WCGN tested its unit in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The entity had previously provided the Transmission Planner with the required model information for all units based on the 5-year WECC Generating Unit Model Validation. Therefore, there was a low probability that these issues would cause minimal impact to the reliability of the bulk power system. No harm is known to have occurred. WCGN does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, WCGN: a. verified Reactive Power capabilities in accordance with the Standard and Requirements; b. submitted completed MOD-025-2 Attachment 2 forms to its Transmission Planner for each of its six generators. These updated Attachment 2 forms contained the information missing prior and were in accordance with Attachment 1; and c. updated its process document explaining the requirements for MOD-025-2, clearly stating for each Requirement, what steps need to be taken to maintain compliance with MOD-025-2.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Woodland Biomass Power Ltd. (WDBM) | NCR10047 | WECC2017017198 | MOD-025-2 | R1 | On March 1, 2017, WDBM submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, WDBM reported that it failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verification to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard. WDBM reported that it has one applicable Facility, which is a 25MW net woody biomass generating plant that operates reaching its Real Power capacity on a daily basis. WDBM interpreted the Standard to allow single entities to be compliant by July 1, 2019, and had been working on an implementation plan to be compliant before that date. However, upon retaining an independent consultant to assist with NERC compliance, WDBM was made aware that single entities needed to be compliant by July 1, 2016. WECC reviewed the Self-Certification, and after further discussions with WDBM and analysis of data request responses, determined that WDBM failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verification to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard and Requirements. The root cause of the noncompliance was that WDBM misinterpreted the implementation plan and identified the incorrect date that it had to be in compliance with the Standard. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for WDBM’s applicable Facility. WECC determined that the end date of this issue is December 28, 2017, when WDBM provided its Transmission Planner with the results of the completed Real Power capability verification in accordance with the Standard and Requirements, for a total of 545 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WDBM failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verification to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard and Requirements. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a 25MW biomass generation Facility, with a single 115kV connection. WDBM has a robust equipment maintenance program and protection systems maintenance program that limits the risk to the bulk power system, associated with MOD 025-2 non-compliance. WDBM has implemented good preventative controls to prevent the noncompliance consequence mentioned above. Based on the severity and controls analysis, this non-compliance has a low probability of causing minor harm. No harm is known to have occurred. WDBM does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, WDBM: a. completed verification of Real Power capability in accordance with the Standard; b. provided its Transmission Planner with verification of the Real Power capability in accordance with Standard; and c. evaluated other Standards that have similar testing Requirements and entered them into its project management program which will send reminder alerts to users by email when due dates for tasks need to be completed.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Woodland Biomass Power Ltd. (WDBM) | NCR10047 | WECC2017017199 | MOD-025-2 | R2 | On March 1, 2017, WDBM submitted a Self-Certification stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Specifically, WDBM reported that it failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verification to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard. WDBM reported that it has one applicable Facility, which is a 25MW net woody biomass generating plant that operates reaching its Real Power capacity on a daily basis. WDBM interpreted the Standard to allow single entities to be compliant by July 1, 2019, and had been working on an implementation plan to be compliant before that date. However, upon retaining an independent consultant to assist with NERC compliance, WDBM was made aware that single entities needed to be compliant by July 1, 2016. WECC reviewed the Self-Certification, and after further discussions with WDBM and analysis of data request responses, determined that WDBM failed to verify Real Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verification to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard and Requirements. The root cause of the noncompliance was that WDBM misinterpreted the implementation plan and identified the incorrect date that it had to be in compliance with the Standard. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for WDBM’s applicable Facility. WECC determined that the end date of this issue is December 28, 2017, when WDBM provided its Transmission Planner with the results of the completed Reactive Power capability verification in accordance with the Standard and Requirements, for a total of 545 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WDBM failed to verify Reactive Power capability of its applicable Facility in accordance with Attachment 1, and to submit the verification to its Transmission Planner in accordance with Attachment 2, by the effective date of the Standard and Requirements. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system reliability. However, the Facility in scope is a 25MW biomass generation Facility, with a single 115kV connection. WDBM has a robust equipment maintenance program and protection systems maintenance program that limits the risk to the bulk power system, associated with MOD 025-2 non-compliance. WDBM has implemented good preventative controls to prevent the noncompliance consequence mentioned above. Based on the severity and controls analysis, this non-compliance has a low probability of causing minor harm. No harm is known to have occurred. WDBM does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, WDBM: a. completed verification of Reactive Power capability in accordance with the Standard; b. provided its Transmission Planner with verification of the Reactive Power capability in accordance with Standard; and c. evaluated other Standards that have similar testing Requirements and entered them into its project management program which will send reminder alerts to users by email when due dates for tasks need to be completed.
2018-04-30 | Western Electricity Coordinating Council (WECC) | Woodland Biomass Power Ltd. (WDBM) | NCR10047 | WECC2017017200 | PRC-019-2 | R1 | On March 1, 2017, WDBM submitted a Self-Certification stating that, as a Generator Owner, it was in possible noncompliance with PRC-019-2 R1. WDBM reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices by the enforcement date of the Standard. Specifically, WDBM had interpreted the Standard to allow entities with a single applicable Facility to be compliant by July 1, 2019, rather than July 1, 2016. WECC reviewed the Self-Certification, and after further discussions with WDBM, and analysis of data request responses, determined that WDBM failed to verify and coordinate its voltage regulating system with its generator capabilities and Protection System devices in at least 40% of its applicable Facilities, which could potentially result in the loss of its biomass generating plant. The root cause of the noncompliance was that WDBM misinterpreted the implementation plan and incorrectly identified the date that it had to be in compliance with the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for WDBM’s applicable Facility. WECC determined that the end date of this issue was December 28, 2017, when WDBM completed verifying coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices, for a total of 545 days of noncompliance. | This noncompliance posed minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system. In this instance, WDBM failed to verify and coordinate its voltage regulating system with its generator capabilities and Protection System devices in at least 40% of its applicable Facilities. Such failure could potentially result in the loss of the generator field, instability, and/or damage. However, the Facility in scope is a 24MW biomass generation Facility, with a single 115kV connection. WDBM has a robust equipment maintenance program and protection systems maintenance program that limits the risk to the bulk power system, associated with PRC-019-2 non-compliance. WDBM had implemented good preventative controls to prevent the above consequence from occurring, and was working on an implementation plan to be compliant with the Standard. The Relay Coordination Study showed that there were no settings changes required and that the biomass Facility is in compliance with the Standard. Based on the controls analysis performed, this non-compliance had a low probability of causing minor harm. No harm is known to have occurred. WDBM does not have previous noncompliances of this Standard and Requirement. | To remediate and mitigate this issue, WDBM: a. completed the required coordination of the voltage regulating system controls with the applicable equipment capabilities and Protection System settings; and b. evaluated other Standards that have similar testing Requirements and entered them into its project management program with reminder alerts to users by email when due dates for tasks need to be completed.
2018-03-29 | Florida Reliability Coordinating Council, Inc. (FRCC) | JEA | NCR00040 | FRCC2017018598 | FAC-009-1 | R1. | During a Compliance Audit conducted from November 6, 2017, through November 9, 2017, FRCC determined that JEA, as a Transmission Owner, was in noncompliance with FAC-009-1 R1. This noncompliance started on June 1, 2011, when JEA began using winter ratings and failed to establish Facility Ratings for its solely and jointly owned Facilities that are consistent with their associated Facility Ratings methodology and ended on November 8, 2017, when the Facility Ratings documentation was correctly updated. The nameplate amp rating of both 230 kV circuit breakers at West Jax substation is 1600 Amps, however the Facility Rating in the JEA Facility Ratings had the circuit breakers rated at 2000 Amps. This resulted in a Facility Rating for the Northside to West Jax (circuit 920) that was inconsistent with the JEA Facility Ratings Methodology because the 230 kV breaker with the corrected rating was the most limiting element and reduced the winter rating by 169 Amps. For the West Jax to Normandy (circuit 921), correcting the breaker rating did not change the Facility Rating as the breaker was not the most limiting element. The root cause of this noncompliance was lack of internal controls and management oversight during the data entry process of transferring raw information into the JEA Facility Rating document. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). JEA’s failure to properly document the West Jax Facility Ratings could have caused equipment to be operated above its rated capacity for an extended period of time. The West Jax substation is fed by two 230 kV lines which are transformed to 69 kV to feed the local distribution system. The loss of the 920 circuit would result in one feed into the substation possibly causing a localized distribution issue, but would not impact the reliability of the BPS. In addition, the line loading data for the past seven years showed the equipment remained at or below 500 Amps, thus never exceeded the corrected rating. FRCC determined that JEA does not have any relevant history of noncompliance. No harm is known to have occurred. | To mitigate this noncompliance, JEA: 1) corrected the Facility Rating for the breakers of circuit 920 Facility Rating at West Jax Substation and notified all impacted parties including the FRCC RC; 2) conducted a field inspection to confirm the breakers rating and conductor elements validate the Element Rating utilized in the Facility Rating database for 100% of previously rated Facilities (e.g., a line, a generator, a shunt compensator, transformer, jumpers, etc.) in Bulk Electric System (BES) substations; 3) completed all required engineering analyses of field audit results; 4) developed a form to be completed by engineering to document elements of a facility that were modified or added to the system; 5) added a section to the Facility Rating Methodology procedure for conducting re-rates of Facility Elements that includes field visits to verify the installed rating type; and 6) conducted joint meetings and training sessions with applicable Substation Engineering and Operations personnel to review the revisions/additions to the BES One-Line Diagram.
2018-03-29 | Florida Reliability Coordinating Council, Inc. (FRCC) | Kissimmee Utility Authority (KUA) | NCR00042 | FRCC2017018385 | PRC-002-2 | R1.; P1.2 | On September 27, 2017, KUA submitted a Self-Report stating as a Transmission Operator it was in noncompliance with PRC-002-2 R1 (Part 1.2). The noncompliance started on September 30, 2016 when KUA did not notify three (3) of the four (4) owners at the Cane Island 230 kV Substation within 90-calendar days of completion of Part 1.1, that the BES Elements require Sequence of Events Recording (SER) data and/or Fault Recording (FR) data. The noncompliance ended on June 12, 2017, when KUA notified the other owners (346 days late) as required by PRC-002-2, R1, Attachment 1. The root cause was KUA's difference in interpretation of the Standard from the ERO Enterprise. KUA now correctly interprets the Standard and is therefore self-reporting the violation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). KUA’s failure to notify other owners connected to the BES buses could have caused unnecessary installation delays thus impacting BES reliability. There is was minimal risk to the BPS, as the necessary recording equipment was installed in the fall of 2016, prior to the phased-in implementation date of July 1, 2022 for the PRC-002-2 requirements. Since SER and FR data is recorded at the identified bus, there has been no gap in data as a result of the adjacent entities not being notified. FRCC determined that KUA does not have any relevant history of noncompliance. No harm is known to have occurred. | To mitigate this noncompliance, KUA: 1) compared the original notification recipients to the list of entities who own portions of the Transmission lines connected to the BES bus that was identified in Part 1.1 of R1 to determine the extent of condition; 2) sent a notification email to all of the identified owners of BES Elements connected to the BES bus that was identified in Part 1.1 of R1; 3) created an Outlook calendar meeting that will remind the manager on 2/25/2021, 90 days prior to the 5 year anniversary date (5/26/2021); 4) added a SharePoint Task as a secondary reminder that will alert the manager on 2/25/2021; and 5) implemented a program for an annual review of all applicable compliance documentation (including PRC-002-2) to reassure that notification is completed prior to the 5 year re-evaluation date of 5/26/2021.
2018-03-29 | Midwest Reliability Organization (MRO) | Western Area Power Administration - Upper Great Plains East (WAPA) | NCR01036 | MRO2017017990 | BAL-005-0.2b | R8 | On July 20, 2017, WAPA, a Multi-Region Registered Entity Coordinated Oversight program participant, submitted a Self-Report to MRO stating that, as a Balancing Authority, it was in noncompliance with BAL-005-0.2 R8. The noncompliance occurred in the operating area of the Western Area Power Administration - Upper Great Plains West (NCR05467). WAPA and Western Area Power Administration - Upper Great Plains West are monitored under the Coordinated Oversight Program. The Western Area Power Administration - Upper Great Plains West stated that it was calculating its Area Control Error (ACE) at a rate of less than once every six seconds during the period between seven minutes and eight seconds after each hour, and seven minutes and 30 seconds after each hour. The cause of the noncompliance was that a database configuration change and a version upgrade of the Automatic Generation Control (AGC) software resulted in the error; specifically the ACE would not be calculated during the period of time that the AGC was processing hourly meter data. The noncompliance began on March 29, 2017, when the calculation issue began, and ended on April 7, 2017, when the ACE was calculated at least once every six seconds at all times. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the noncompliance was extremely limited as it only occurred for a brief period once per hour. Further per WAPA, the calculation that occurred during this period was not significantly different from the calculation that occurred at a rate of less than every six seconds. Additionally, Western Area Power Administration - Upper Great Plains West is the Balancing Authority for a small footprint, consisting of only 165 MW of load and up to 563 MVA of generation. Finally, the issue was self-detected. No harm is known to have occurred. WAPA has no relevant history of noncompliance. | To mitigate this noncompliance, Western Area Power Administration - Upper Great Plains West: 1) rolled back the configuration change to correct the issue; and 2) developed a change to the AGC database code that results in the meter history processing to be completed separately from other AGC operations, including the calculation of the ACE.
2018-03-29 | Northeast Power Coordinating Council, Inc. (NPCC) | Bucksport Generation LLC | NCR11459 | NPCC2017017024 | PRC-019-2 | R1 | On January 27, 2017, Bucksport Generation, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as required by PRC-019-2 R1. In accordance with the standard's Implementation Plan, two of the Entity's generating assets (G4 and G5) are required to be compliant by July 1, 2016. Instead, both generating units (G4 and G5) were not fully compliant. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on December 20, 2016, when the Entity brought generating unit G5 into full compliance by changing the time delay setting of the thermal overload relay element. Prior to that, the Entity had remediated the noncompliance on its other generating unit, G4. The root causes of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their assets and the unavailability of qualified resources to conduct engineering studies to timely assess compliance of its generating units. Upon consultation with an outside vendor, the Entity correctly concluded that both its G4 and G5 generating unit needed to be 100% compliant with the standard and requirement by 7/1/2016. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's noncompliant generating assets, G4 and G5, have a rated capability of 217.8 MVA and 28.24 MVA, respectively. Units G4 and G5 operated at a capacity factor of 0.86% and 0.06%, respectively, in the year 2016. Additionally, the Entity's Reliability Coordinator 's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. The RC has comparable summer operating reserves requirements. Therefore, if this instance of noncompliance had caused the two noncompliant generating facilities to trip unnecessarily during a system voltage event, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by first completing a coordination verification of in-service Protection System relays and in-service limiters on its two generating units, and then adjusting the settings of two protection devices on generators G4 and G5 (an overvoltage limiter, and a thermal overload relay); and 2. To prevent a recurrence of similar instances of noncompliance, secured a third-party compliance consultant, created a compliance calendar and a monthly compliance status meeting to track future compliance obligations, and created its own internal compliance procedure that details the process to ensure compliance with PRC-019. NPCC has verified the completion of all mitigation activity.
2018-03-29 | Northeast Power Coordinating Council, Inc. (NPCC) | Bucksport Generation LLC | NCR11459 | NPCC2017017678 | PRC-024-2 | R1. | On June 2, 2017, Bucksport Generation, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. Specifically, the Entity failed to implement frequency relay settings that would ensure that its generator frequency protective relaying does not trip its generating facilities within the "no trip zone" of PRC-024-2 Attachment 1. In accordance with the standard's Implementation Plan, two of the Entity's generating assets (G4 and G5) are required to be compliant by July 1, 2016. Instead, generator G5 was not fully compliant. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on December 20, 2016, when the Entity implemented a change to its over-frequency relay setting for generator G5 to ensure its compliance with the standard/requirement. The root causes of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their assets and the unavailability of qualified resources to conduct engineering studies to timely assess compliance of its generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its G5 generating unit needed to be 100% compliant with the standard and requirement by 7/1/2016. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's noncompliant generating asset (G5) has a rated capability of 28.24 MVA, and it operated at a capacity factor of 0.06% in the year 2016. Additionally, the Entity's Reliability Coordinator 's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. The RC has comparable summer operating reserves requirements. Therefore, if this instance of noncompliance had caused the G5 generating facility to trip unnecessarily during a system frequency event, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by implementing a change to its over-frequency relay setting for generator G5; and 2. To prevent a recurrence of similar instances of noncompliance, secured a third-party compliance consultant, created a compliance calendar and a monthly compliance status meeting to track future compliance obligations, and created its own internal compliance procedure that details the process to ensure compliance with PRC-024. NPCC has verified the completion of all mitigation activity.
2018-03-29 | Northeast Power Coordinating Council, Inc. (NPCC) | Bucksport Generation LLC | NCR11459 | NPCC2017017025 | PRC-024-2 | R2. | On January 27, 2017, Bucksport Generation, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. Specifically, the Entity failed to implement voltage relay settings that would ensure that its generator voltage protective relaying does not trip its generating facilities within the "no trip zone" of PRC-024-2 Attachment 2. In accordance with the standard's Implementation Plan, two of the Entity's generating assets (G4 and G5) are required to be compliant by July 1, 2016. Instead, both generating units (G4 and G5) were not fully compliant. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on November 6, 2017, when the Entity brought generating unit G4 into full compliance by dis-activating the trip function of the ANSI 27 Inverse-time Under-voltage Relay. Prior to that, the Entity had remediated various other noncompliances associated with G4 and G5. The root causes of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their assets and the unavailability of qualified resources to conduct engineering studies to timely assess compliance of its generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its G5 generating unit needed to be 100% compliant with the standard and requirement by 7/1/2016. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's noncompliant generating assets, G4 and G5, have a rated capability of 217.8 MVA and 28.24 MVA, respectively. Units G4 and G5 operated at a capacity factor of 0.86% and 0.06%, respectively, in the year 2016. Additionally, the Entity's Reliability Coordinator 's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. The RC has comparable summer operating reserves requirements. Therefore, if this instance of noncompliance had caused the two noncompliant generating facilities to trip unnecessarily during a system voltage event, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by implementing changes to the settings of under-voltage and over-voltage relays for generators G4 and G5; and 2. To prevent a recurrence of similar instances of noncompliance, secured a third-party compliance consultant, created a compliance calendar and a monthly compliance status meeting to track future compliance obligations, and created its own internal compliance procedure that details the process to ensure compliance with PRC-024. NPCC has verified the completion of all mitigation activity.
2018-03-29 | Northeast Power Coordinating Council, Inc. (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2017018461 | PRC-024-2 | R1. | On October 12, 2017, Plainfield Renewable Energy, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. Specifically, the Entity failed to verify that frequency protection relays for their single generating asset were correctly set to not trip the generating facility within the "no trip zone" of PRC-024-2 Attachment 1. Per the phased-in implementation plan of the Standard and Requirement, the above verification for the Entity's single generating asset was required by 7/1/2016. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on September 25, 2017, when the Entity's consultant's final engineering report concluded that the existing settings of frequency protection relays were in compliance with the standard and requirement. The root cause of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan of the Standard and Requirement would apply to their single generating asset. Subsequently, based on information issued by NERC, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by 7/1/2016. Upon discovery of this missed compliance obligation, the Entity contracted a third-party vendor to perform an evaluation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This instance of noncompliance was, essentially, administrative in nature as the Entity ultimately concluded that its frequency protection relays required no setting changes in order to be compliant. Additionally, the Entity's generating asset has a net rated capability of 37.5 MW, and it operated at a capacity factor of 72% and 62% for the years 2016 and 2017, respectively. By comparison, the Entity's Reliability Coordinator 's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. The RC has comparable summer operating reserves requirements. Therefore, if this instance of noncompliance had caused the generating facility to trip unnecessarily during a system frequency event, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by verifying that the existing settings of its frequency protection relays were in compliance; and 2. To prevent a recurrence of similar instances of noncompliance, implemented calendar reminders for responsible personnel to complete future re-verifications. Calendar reminders are planned for four (4) years and again at four (4) years and nine (9) months after the date the PRC-024-2 verification report is completed. NPCC has verified the completion of all mitigation activity.
2018-03-29 | Northeast Power Coordinating Council, Inc. (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2017018462 | PRC-024-2 | R2. | On October 12, 2017, Plainfield Renewable Energy, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. Specifically, the Entity failed to implement voltage relay settings that would ensure that its generator voltage protective relaying does not trip its single generating facility within the "no trip zone" of PRC-024-2 Attachment 2. Per the phased-in implementation plan of the Standard and Requirement, implementation of appropriate voltage relay settings for the Entity's single generating asset was required by 7/1/2016. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on September 25, 2017, when the Entity's consultant's final engineering report verified that a change implemented to the voltage pickup setting of an under-voltage relay brought the generating asset back into compliance with the standard and requirement. The root cause of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan of the Standard and Requirement would apply to their single generating asset. Subsequently, based on information issued by NERC, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by 7/1/2016. Upon discovery of this missed compliance obligation, the Entity contracted a third-party vendor to perform an evaluation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's generating asset has a net rated capability of 37.5 MW, and it operated at a capacity factor of 72% and 62% for the years 2016 and 2017, respectively. By comparison, the Entity's Reliability Coordinator 's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. The RC has comparable summer operating reserves requirements. Therefore, if this instance of noncompliance had caused the generating facility to trip unnecessarily during a system voltage event, the ISO-NE would have been able to replace the lost capacity. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by verifying that a change implemented to the voltage pickup setting of an under-voltage relay brought its single generating asset back into compliance with the standard and requirement; and 2. To prevent a recurrence of similar instances of noncompliance, implemented calendar reminders for responsible personnel to complete future re-verifications. Calendar reminders are planned for four (4) years and again at four (4) years and nine (9) months after the date the PRC-024-2 verification report is completed. NPCC has verified the completion of all mitigation activity.
2018-03-29 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2017018260 | PRC-001-1.1 | R3 | On August 18, 2017, AEP submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with PRC-001-1.1 R3. On December 9, 2014, AEP Generation completed protective relay settings in connection with the installation of Smith Mountain Unit 5, which is a 70 MW hydro unit. At that time, the engineer completing the settings enabled phase distance protection on two of the relays associated with Unit 5. This type of protection requires coordination with AEP Transmission to ensure the settings are coordinated with AEP Transmission’s other protection system settings. However, coordination did not occur. The entity identified the issue in August of 2015 while preparing to install another unit. In August 2015, while completing the protective relay settings for Smith Mountain Unit 1, an entity engineer compared the settings to the as-installed Smith Mountain Unit 5 relay settings because the generators are similar machines. During that comparison, the engineer discovered that a phase distance protection element was enabled within two of the relays installed for Smith Mountain Unit 5 and, after further investigation, determined that coordination did not occur as required. Thereafter, on October 27, 2015, the entity disabled the phase distance element. This was appropriate because AEP Transmission relays provide sufficient protection without the phase distance protection. The phase distance relay setting provided an additional layer of protection, but this additional protection was unnecessary and not appropriate for this generator pursuant to entity standards because it results in overprotection, which could result in unnecessary tripping. Regarding root cause, an inexperienced engineer completed the relay settings on the unit in 2014 and was not aware of the entity’s process document that describes the process for coordinating relay settings. This noncompliance involves the management practice of workforce management because the entity’s training program was insufficient to ensure that the engineer was fully aware of the coordination process. This noncompliance started on December 9, 2014, the date by which the entity was required to coordinate the backup protection system, and ended October 15, 2015, when the entity disabled the backup protection system. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Here, the phase distance protection system was only a backup protection system for the generating unit, and thus the potential risk of not coordinating with AEP Transmission protection schemes was only that the unit would trip prematurely. This could have resulted in an unexpected loss of 70 MW of generating capacity, which, in the unlikely event that it unexpectedly tripped offline, would have had only minimal, if any, impact to the BPS because the entity has sufficient generating capacity to mitigate the unexpected loss of a 70 MW generator. Additionally, the entity self-identified the noncompliance and thereafter quickly mitigated the noncompliance by removing the secondary protection scheme because the entity determined that it was unnecessary. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-001-1.1 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) made changes and removed the phase distance settings from the AEP Generation owned relays on Smith Mountain Units 5; 2) ensured all applicable generation protection and control engineers reviewed the quality assurance document to ensure they are familiar with the purpose, requirements, scope, responsibilities, and procedures regarding protection system coordination; 3) incorporated protection system coordination as part of the design review phase of the protection system projects process; and 4) conducted a training and awareness session with pertinent protection and control personnel.
2018-03-29 | ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Power Midwest (GenOn Power) | NCR11136 | RFC2017017846 | EOP-005-2 | R17; R17.1; R17.2 | On June 2, 2017, ReliabilityFirst determined that GenOn Power, as a Generator Operator, was in noncompliance with EOP-005-2 R17, R17.1, and R17.2, as identified during a Compliance Audit conducted from May 8, 2017, through May 19, 2017. ReliabilityFirst examined the evidence provided by the entity and concluded that it showed a maximum of 1 hour of training having been provided to operating personnel at the Avon Lake facility. Although the entity indicated that further training was provided, it did not provide evidence to verify that fact. The root cause of this noncompliance was the entity’s lack of awareness regarding the evidence required to demonstrate compliance. This major contributing factor involves the management practices of workforce management, which includes establishing organizational training, education, and awareness needs, and information management, in that the entity failed to properly maintain training records. This noncompliance started on July 1, 2015, when the entity was required to comply with EOP-005-2 R17, R17.1, and R17.2, and ended on December 18, 2017, when the entity completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the fact that the entity provided evidence that its operators were familiar with Blackstart Resources and were able to run and test them during normal system conditions. This fact increases the likelihood that the operators would have been able to take the required actions to start the unit during a blackout. No harm is known to have occurred. ReliabilityFirst considered the entity’s EOP-005-2 R17, R17.1 and R17.2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) created EOP-005 R17 Training template to document required evidence and duration of training; 2) updated the NRG Compliance procedure OCC-EOP-005 to add content for blackstart procedure and coordination with Transmission Owner (TO)/Transmission Operator (TOP) for use during system restoration; 3) reviewed roles and expectations of Avon Lake 10 personnel with FirstEnergy and PJM personnel expected during system event; 4) updated the Avon Lake Blackstart procedure for use at Avon Lake during a system restoration which includes coordination steps with TO/TOP; 5) revised curriculum to include the revised Avon Lake Blackstart procedure; and 6) provided two-hour training of eligible personnel for Blackstart operation to include given procedure to meet all of EOP-005 R17 requirements.
2018-03-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company LLC (NIPSCO) | NCR02611 | RFC2017018691 | PRC-005-2 | R3 | On November 10, 2017, ReliabilityFirst determined that NIPSCO, as a Transmission Owner, was in noncompliance with PRC-005-2 R3; this was identified during a Compliance Audit conducted from October 17, 2017 through October 18, 2017. During the Compliance Audit, ReliabilityFirst determined that the entity lacked adequate evidence to show completion for the Communications Systems, Table 1-2 maintenance activity, “verify that the communications system is functional” for power line carrier systems. PRC-005-2 Table 1‐2 requires 4 calendar month and 6 calendar year interval maintenance for all unmonitored communication systems. In accordance with the entity’s Protection System Maintenance Program (PSMP), the entity performs maintenance on three distinct communication systems (microwave radio stations, microwave relay communication circuits, and power line carriers) at the 4 calendar month and 6 calendar year intervals in order to ensure reliability and to satisfy NERC compliance. The entity could not provide evidence that shows maintenance was being performed on power line carriers at the 4 calendar month and 6 calendar year intervals. The entity was only able to show that the entity monitors power line carriers by logging any observed incidents by exception meaning that any time there was an issue with the power line carriers, the entity would be notified and investigate the issue. Logging incidents by exception does not show that the entity reviewed power line carriers at least every four calendar months as required by the entity’s PSMP. This noncompliance involves the management practices of asset and configuration management and verification. Asset and configuration management is involved because the entity failed to ensure that power line carriers were properly monitored on its maintenance inspection sheets. The entity did not have a specific line on its inspection sheets to mark that power line carriers had been monitored and checked and that lack of a specific line on the inspection sheets is a contributing cause of this noncompliance. Verification is involved because the entity did not verify that it was monitoring and documenting its monitoring of its power line carriers on its maintenance inspection sheets and that failure to verify is a root cause of this noncompliance. This noncompliance started on April 1, 2015, when the entity was required to comply with PRC-005-2 R3 and ended on October 2, 2017, when the entity completed its Mitigating Activities by modifying the inspection sheets. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is allowing important Protection System devices to remain unmaintained and untested could negatively affect the reliable operation of the BPS. The risk is lessened because the entity provided evidence to the Audit Team that it monitored the power line carriers by exception meaning that any time there was an issue with the power line carriers, the entity would be notified and investigate the issue. The entity also provided evidence to the Audit Team that when an issue occurred on the power line carriers or the other monitored communication systems, the entity identified and corrected the issue within 24 hours. Although the entity was not maintaining the power line carriers in accordance with the appropriate intervals, the entity was monitoring the power line carriers by exception for the duration of the noncompliance. The risk is also lessened because the entity performed and documented all required maintenance and testing on its other two distinct communication systems (microwave radio stations and microwave relay communication circuits). This reduces the risk because monitoring the other two communication systems increases the likelihood that the entity would be able to both identify and correct an issue with the entity’s communication systems. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-005 R3 compliance history in determining the disposition track. The entity’s relevant prior noncompliance with PRC-005 R3 includes: RFC2016016663. A Compliance Exception addressing a noncompliance with PRC-005-2(i) R3 was posted on the NERC website on June 29, 2017. The prior noncompliance is distinguishable from the instant noncompliance because the prior noncompliance involved NIPSCO failing to maintain two microwave digital radios within the maximum allowable maintenance interval and arose from NIPSCO not having maintenance triggers to notify of approaching maintenance due dates enabled in its Cascade database. In contrast, the instant noncompliance arose from NISPCO failing to monitor and document monitoring of its power line carrier systems due to NIPSCO using ineffective maintenance inspection sheets that enabled personnel to not monitor power line carrier systems. The instant noncompliance is distinguishable from the prior noncompliance because it did not arise from a lack of warnings about approaching maintenance due dates. These different contributing causes make the prior noncompliance distinguishable. ReliabilityFirst determined that the entity’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) performed the missing verification of power line carrier system functionality according to the relevant intervals; 2) modified its 4 calendar month and 6 calendar year maintenance inspection sheets to also verify the functionality of power line carrier systems. These modified inspection sheets will now ensure that the entity is performing the monitoring of its power line carriers in accordance with its PSMP. This will help prevent recurrence because it ensures entity personnel will check power line carrier systems when performing inspections. The entity trained all relevant personnel on these new maintenance inspection sheets and the importance of ensuring that power line carrier systems are monitored in accordance with the proper intervals; and 3) submitted completed maintenance inspection sheets that show the sheets have been revised and are being filled out by personnel correctly. ReliabilityFirst has verified the completion of all mitigation activity.
2018-03-29 | ReliabilityFirst Corporation (ReliabilityFirst) | West Deptford Energy, LLC (West Deptford) | NCR11391 | RFC2017018068 | PRC-005-6 | R3 | On July 21, 2017, ReliabilityFirst determined that West Deptford, as a Generator Owner, was in noncompliance with PRC-005-6 R3, identified during a Compliance Audit conducted from July 10, 2017 through July 21, 2017. Table 1‐4(b) of PRC‐005‐6 requires entities to “Inspect … the condition of all individual units by measuring battery cell/unit internal ohmic values” at least once every six months for certain Valve Regulated Lead-Acid (VRLA) batteries. The entity owns three sets of batteries, one of which falls under Table 1-4(b). For this set of batteries, the entity missed two six months intervals for the maintenance activities in Table 1-4(b). The entity instead included the required activities as part of its 18-month maintenance activities because it mistakenly believed the six month-interval requirement was not yet effective. The entity timely performed all other maintenance activities as required on these batteries. Regarding the six-month activities for these batteries, the entity inspected the internal ohmic values on these batteries at the time of commissioning on September 30, 2015. Thus, the next six-month interval inspection was due in March, 2016, but the entity did not perform that inspection. The subsequent six-month inspection would have been due in September, 2016, but the entity did not perform the next inspection until November 2, 2016. Accordingly, the entity missed one six month interval, and then was approximately one month late in performing the subsequent six-month inspection. Thus, the entity was noncompliant for approximately seven months. The purpose of the batteries at issue was to power the trip coils so that the protection system would actuate if there was a fault on the line, thus protecting the generators, which are Blackstart Resources. The root cause for the entity not inspecting the internal ohmic values on six-month intervals was that the entity misunderstood the Implementation Plan timelines for PRC-005-6 as they related to VLRA batteries and instead scheduled these inspections for 18-month intervals. The entity realized this mistake as it was preparing for its upcoming compliance audit and notified the auditors. Upon identifying the noncompliance, on May 4, 2017, the entity performed the inspection on the batteries. Because the May 4, 2017 inspection was within six calendar months of the prior inspection, these maintenance activities were performed on time. This noncompliance involves the management practices of planning and information management because the entity’s compliance staff misunderstood the effective dates of the PRC-005-6 requirements for VRLA batteries. This noncompliance started on April 1, 2016, the date by which the entity was required to perform the maintenance activity, and ended on November 2, 2016, when the entity performed the required maintenance activity. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk of not performing the required maintenance on the batteries is that the batteries may not perform as expected, and thus not allow the protection system to operate to protect the generators. The purpose of inspecting the units by measuring battery cell/unit internal ohmic values is to assess degradation over a period of time. The fact that the entity was only seven months late in performing the inspection reduces the likelihood that there would be undetected battery degradation. The most recent inspection prior to the noncompliance, and the subsequent inspection, did not identify any issues with the batteries. Additionally, the entity was performing all other required maintenance activities on the batteries at the correct intervals. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-005-6 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed the testing requirement for the PDC Battery Bank; 2) updated the 6-month Battery Testing activities to include measuring battery cell/unit internal ohmic values on all individual battery cell units; and 3) updated related forms that are part of the work management system to include the 6-month Battery Testing activities. ReliabilityFirst has verified the completion of the above mitigation activity. As an additional mitigation step, the plant’s third-party operator hired a new NERC Manager who is responsible for monitoring new NERC Standards and developing program documents and implementation procedures. This should assist in keeping the facilities up-to-date on NERC Standards and track when new requirements become effective for plants. Monthly conference calls are also held to discuss new standards and implementation dates.
2018-03-29 | Southwest Power Pool Regional Entity (SPP RE) | American Electric Power Corp. as Agent for AEP Oklahoma Transmission Company, Inc., Public Service Company of Oklahoma, and Southwestern Electric Power Company (AEP) | NCR01056 | SPP2017018213 | PRC-005-1.1b | R2; R2.1, R2.2 | On August 18, 2017 AEP submitted a Self-Report stating that, as a Generator Owner, it was not compliant with PRC-005-1.1b R2, inclusive of R2.1 and R2.2. AEP failed to test one instrument transformer in the required 60 month test interval as required by AEP’s Protection System maintenance and testing program (PSMTP). This affected .016% of AEP’s Protection System devices (one of 5990 devices). This noncompliance started on September 28, 2016, the date AEP should have tested the one instrument transformer, and ended on November 17, 2016, the date AEP tested the instrument transformer. The root cause of this noncompliance was lack of communication from the third-party contractor to inform the responsible AEP plant personnel that testing of the one instrument transformer could not be completed within the defined interval. Additionally, AEP did not sufficiently review the completed testing records at the plant to allow for adequate time to resolve any testing issues prior to the end of the maintenance interval. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to test an instrument transformer within the defined interval has the potential to affect the reliability of the BPS by increasing the risk that an instrument transformer may fail and impact a protection system relay which could cause a misoperation. Notwithstanding, the testing of the instrument transformer was missed by only 50 days and no misoperations occurred for the duration of noncompliance or during the 60 month interval. Additionally, the current standard does not require maintenance and testing but every 12 years. Accordingly, the 60 months maintenance and testing interval for this instrument transformer in AEP’s PSMTP greatly exceeds the maintenance and testing requirement for instrument transformers in the current standard. No harm is known to have occurred. On October 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE2012010184, RFC2012010261, and SPP2012010129) was filed with FERC under NP14-4-000. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In the prior violation, AEP Generation did not perform testing on batteries. Mitigation included development and training for generation plant staff and reviewing generation batteries in the Reliability First and SPP regions to identify all batteries. In the Texas RE region, this previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. SPP RE considered AEP’s compliance history and determined that the instant noncompliance was appropriate for Compliance Exception treatment because although the instances of noncompliance were of the same Standard and Requirement, the instant noncompliance only affected .016% of AEP’s Protection System devices and did not impact the BPS. | To mitigate this noncompliance, AEP: 1) performed testing of the missed instrument transformer; and, 2) implemented its PRC-005-2 PSTMP. SPP RE has verified the completion of all mitigation activity.
2018-03-29 | Southwest Power Pool Regional Entity (SPP RE) | Caprock Wind LLC (Caprock) | NCR05059 | SPP2016016220 | MOD-025-2 | R1; R1.1, R1.2 | On September 28, 2016, Caprock submitted a Self-Report stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1. Caprock did not verify the Real Power capability of its generating units in accordance with Attachment 1 (R1.1). As a result, Caprock was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its applicable Facilities (R1.2). The root cause of this instance of noncompliance was Caprock’s lack of understanding of the requirements of MOD-025-2. Specifically, Caprock was not aware of the standard effective date of July 1, 2016 and thus, did not complete its Real Power capability testing by the required date. The noncompliance started on July 1, 2016, the effective date of the standard, and ended February 3, 2017, the date Caprock submitted Attachment 2, verifying the Real Power capability of its applicable Facilities, to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of issues affecting the reliability of the BPS. Notwithstanding, Caprock is an 80 MW wind facility and failure to perform this test has minimal impact on reliability because of the intermittent real power supplied by a wind facility. Additionally, prior capability tests had been performed under Southwest Power Pool Planning Criteria 7.0, Facility Ratings. No harm is known to have occurred. SPP RE reviewed Caprock’s violation history and determined that Caprock has no prior instances of noncompliance with MOD-025-2. | To mitigate this issue, Caprock: 1) conducted Real Power capability tests of its generating units; 2) submitted a verification of the Real Power capability of its generating units to its TP; 3) developed an action tracking system that identifies new standard requirements, monitors activity status, sends notifications to appropriate staff and tracks requirements to completion; and 4) conducted applicable NERC training for Site Operations Managers, Information Technology, Engineering, Chief Executive Officer, Chief Operating Officer, Vice President of Operations and Director of Regulatory Compliance. SPP RE has verified the completion of all mitigation activity.
2018-03-29 | Southwest Power Pool Regional Entity (SPP RE) | Caprock Wind LLC (Caprock) | NCR05059 | SPP2016016222 | MOD-025-2 | R2; R2.1, R2.2 | On September 28, 2016, Caprock submitted a Self-Report stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2. Caprock did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 (R2.1). As a result, Caprock was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its applicable Facilities (R2.2). The root cause of this instance of noncompliance was Caprock’s lack of understanding of the requirements of MOD-025-2. Specifically, Caprock was not aware of the standard effective date of July 1, 2016 and thus, did not complete its Reactive Power capability testing by the required date. The noncompliance started on July 1, 2016, the effective date of the standard, and ended February 3, 2017, the date Caprock submitted Attachment 2, verifying the Reactive Power capability of its applicable Facilities, to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of issues affecting the reliability of the BPS. Notwithstanding, Caprock is an 80 MW wind facility and the failure to perform this test has minimal impact on reliability because of the intermittent Reactive Power supplied by a wind facility. Additionally, prior capability tests had been performed under Southwest Power Pool Planning Criteria 7.0. No harm is known to have occurred. SPP RE reviewed Caprock’s violation history and determined that Caprock has no prior instances of noncompliance with MOD-025-2. | To mitigate this issue, Caprock: 1) conducted Reactive Power capability tests of its generating units; 2) submitted a verification of the Reactive Power capability of its generating units to its TP; 3) developed an action tracking system that identifies new standard requirements, monitors activity status, sends notifications to appropriate staff and tracks requirements to completion; and 4) conducted applicable NERC training for Site Operations Managers, IT, Engineering, Chief Executive Officer, Chief Operating Officer, Vice President of Operations and Director of Regulatory Compliance. SPP RE has verified the completion of all mitigation activity.
2018-03-29 | Southwest Power Pool Regional Entity (SPP RE) | Midwest Energy, Inc. (MIDW) | NCR01118 | SPP2017018661 | MOD-026-1 | R6 | On November 16, 2017, MIDW submitted a Self-Report stating that, as a Transmission Planner, it was not compliant with MOD-026-1 R6 because it failed to provide a written response to the Generator Owner (GO) within 90 calendar days of receiving generator excitation control system or plant volt/var control function models (control system model) that the models are usable or not usable. MIDW received control system model information from one of its GOs on November 11, 2016, and completed testing and extensive dynamic simulations using the information in December of 2016. MIDW should have provided a written response to the GO about the usability of the models by February 9, 2017. However, MIDW did not provide the written response until October 10, 2017. This noncompliance started on February 9, 2017, the date MIDW should have provided the GO with a written response stating if the models provided were usable, and ended on October 10, 2017, the date MIDW provided a written response to the GO stating the models were usable. The root cause of this noncompliance was a combination of human error and inadequate internal controls. The MIDW planning engineer responsible for performing the testing and simulations using the GO’s models failed to notify the GO within 90 calendar days. Additionally, MIDW did not have internal controls in place for the Engineering Manager to ensure that reporting to the GO was completed by the responsible engineer within 90 calendar days. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to notify the GO that the models submitted are usable or not usable creates the potential that the results of dynamic simulations of generator performance would not accurately represent the response of the generator excitation control system or plant volt/var control function to system events. This could result in an inaccurate assessment of dynamic reliability issues and the development of inaccurate corrective action plans to address such issues. Notwithstanding, the risk was minimal because MIDW confirmed that the correct model data was used for dynamic simulation and provided the usable model data to its Planning Coordinator for the TP stability assessments. No harm is known to have occurred. MIDW has no relevant prior violations of MOD-026-1 R6 or any other standards that are similar in nature. | To mitigate this noncompliance, MIDW: 1) provided a written response to the GO stating whether or not the models provided were usable; and, 2) implemented internal controls such as management review and assurance to ensure models submitted by MIDW’s GO are reviewed and a written response is provided within 90 calendar days. SPP RE has verified the completion of all mitigation activity.
2018-03-29 | Southwest Power Pool Regional Entity (SPP RE) | Western Farmers Electric Cooperative (WFEC) | NCR01160 | SPP2017018073 | VAR-002-4 | R3 | On August 1, 2017, WFEC submitted a Self-Certification stating that, as a Generator Operator, it had an issue of noncompliance with VAR-004-2 R3. On June 6, 2017, at 5:12 p.m. the automatic voltage regulator (AVR) for the Hugo Power Plant (Hugo) initiated an alarm due to overheating cause by high ambient temperatures. The problem resulting in the alarm caused the AVR to switch from automatic mode to the test mode. Hugo remained online with the AVR in test mode. Plant staff installed fans to cool the AVR and it was reset to automatic mode at 7:11 p.m. that day. WFEC subsequently determined that the test mode for the AVR is a manual mode of operation and that the plant operators had not notified the WFEC Transmission Operator (TOP) of the Hugo AVR status change. The duration of this instance of noncompliance was one hour and 28 minutes, beginning 5:43 p.m. on June 6, 2017, following the expiration of the required notification period for a change in status of the Hugo AVR and ending at 7:11 p.m., the time WFEC plant operators reset the Hugo AVR to automatic mode of operation. The root cause of this instance of noncompliance was a combination of human error and a lack of training regarding the AVR modes of operation. Although the plant operators were aware that the AVR had switched to the test mode, their attention was directed towards resolving the overheating problem and they were unaware that automatic operation of the AVR had stopped. Additionally, the status change was not readily known until after further investigation by WFEC staff and clarification from the AVR vendor. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to notify the TOP of a change in the status of a generator AVR diminishes the TOP's situational awareness and increases the potential that online reactive capability will be insufficient to respond to voltage excursions during system events. Here, the risk to the BPS is mitigated because the Hugo AVR was in manual mode for less than two hours, plant voltage remained within the voltage schedule, and plant operators were available to respond manually to voltage issues had they occurred. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, WFEC performed the following: 1) WFEC Unit Operators reset the Hugo AVR to automatic mode of operation; 2) the Operations Superintendent reviewed with WFEC staff the requirement to notify the TOP within 30 minutes of a status change of the AVR when the duration will be more than 30 minutes; 3) the Operation Superintendent reviewed with staff how to respond to and reset alarms on the AVR; 4) Hugo Unit Auxiliary Operators are now required to record the temperature of the AVR while making rounds: 5) the E/I Supervisor added "manual" to the indication on the AVR screen in the Distributed Control System (DCS); and 6) added DCS AVR status for Hugo, Anadarko, and Mooreland to the System Operations Center Energy Management System to make Control Area Services aware of AVR status and trigger follow-up by WFEC staff. SPP RE has verified the completion of all mitigation activity.
2018-03-29 | Texas Reliability Entity (Texas RE) | NAES Corporation - Quail Run Energy Center (NCQREC) | NCR11508 | TRE2017017653 | IRO-010-1a | R3 | During a Compliance Audit conducted from May 9, 2017 through May 18, 2017, Texas RE determined that NCQREC, as a Generator Operator (GOP), was in noncompliance with IRO-010-1a R3. In particular, NCQREC did not provide data and information, as specified, to its Reliability Coordinator (RC) with which it had a reliability relationship. As referenced in the Electric Reliability Council of Texas’ (ERCOT) documented data specification for the data necessary to perform Operational Planning Analyses, Real-time monitoring, and Real-time Assessments, ERCOT Nodal Protocol § 3.15.3(4) requires certain generators in the ERCOT interconnection, including NCQREC, to provide their Power System Stabilizer (PSS) status to its RC via telemetry on a continuous basis. However, NCQREC did not provide the correct status of its PSS for a single generation unit via telemetry as specified by its RC on two occasions. First, on January 27, 2016, NCQREC telemetered an offline PSS status to its RC for approximately 15 hours while the PSS at its applicable generating unit remained online and operational. On July 14, 2016, NCQREC again telemetered an offline PSS status to its RC for approximately 8.5 hours while its PSS remained online and operational. On both occasions, NCQREC ended the issue by taking its generating unit and PSS offline. The root cause of this noncompliance was that NCQREC did not have a sufficient process to ensure that its PSS status was being correctly telemetered to its RC. In particular, NCQREC did not have a process in place to review telemetered data provided to its RC, as well as checks to validate that data against its generating unit’s actual operating status. This noncompliance started on January 27, 2016, when the first incorrect PSS status was provided to NCQREC’s RC, and ended on July 14, 2016, when the correct PSS status was provided to NCQREC’s RC in the last instance of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, during both noncompliance periods, NCQREC’s single generation unit’s PSS remained in service and would have likely operated to maintain synchronous operation at the single generating unit at issue under transient conditions. Second, NCQREC maintained the voltage within the ERCOT prescribed deadband of +/- 2% of the target 345 kV voltage during the noncompliance periods. Third, NCQREC’s output during the two occasions in question was small, with the single generating unit producing a maximum of 39 MW and 87 MW on each occasion, respectively. Fourth, NCQREC’s telemetry issues were limited in scope. In particular, NCQREC is required to telemeter 36 data points for each unit under its applicable RC data specifications and the single PSS data point only represents 2.77% of that unit’s overall telemetry obligations. Finally, PSSs do not protect the Bulk Electric System (BES) from generator disturbances but rather serve to protect the generating unit from disturbances on the BES. No harm is known to have occurred. Texas RE considered NCQREC's compliance history in determining the disposition track. NCQREC has one relevant prior noncompliance record involving NCQREC’s failure to notify its associated Transmission Operator (TOP) of a change in status of the PSS within 30 minutes of the change (VAR-002-4 R3, TRE2016016495). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the conduct at issue is distinguishable from the current circumstances. Specifically, the prior noncompliance was caused by a control system that was inadequately configured to notify NCQREC’s plant operators that the PSS was inactive and offline during the generation unit start-up process. In contrast, the current noncompliance related to an insufficient process to ensure the correct information was telemetered to NCQREC’s RC during normal operations. Specifically, NCQREC could not tell if the data being telemetered by NCQREC matched the data being received by ERCOT. | To mitigate this noncompliance, NCQREC: 1) provided the correct PSS status to its RC; 2) implemented a change to the generation unit control screens to show the status of the PSS for all units; 3) established an automated alarming system to indicate to plant operators if any discrepancies occur between the generating unit status and the generating unit status telemetered to the RC; and 4) implemented a written process that requires plant operators to contact management and applicable NCQREC personnel if discrepancies in telemetered data occur. Texas RE has verified the completion of all mitigation activity.
2018-03-29 | Texas Reliability Entity (Texas RE) | Senate Wind, LLC (Senate) | NCR11274 | TRE2017018300 | IRO-010-1a | R3 | During a Compliance Audit conducted from July 25, 2017 through September 6, 2017, Texas RE determined that Senate, as a Generator Operator (GOP), was in noncompliance with IRO-010-1a R3. Senate did not provide data and information, as specified, to its Reliability Coordinator (RC) with which it had a reliability relationship. Specifically, Senate did not provide the status of its Automatic Voltage Regulator (AVR) for a single generation unit via telemetry as specified by its RC. As referenced in the Electric Reliability Council of Texas’ (ERCOT) documented data specification for the data necessary to perform Operational Planning Analyses, Real-time monitoring, and Real-time Assessments, ERCOT Nodal Protocol § 3.15.3(4) requires certain generators in the ERCOT interconnection, including Senate, to provide their AVR status to their RC via telemetry on a continuous basis. Beginning on August 1, 2013, Senate telemetered an offline AVR status to Senate’s RC despite the AVR actually being online and operational. On February 17, 2017, Senate identified the AVR status telemetry issue and corrected it, ending the issue. The root cause of this noncompliance was that Senate did not have a sufficient process to ensure that its AVR status was being correctly telemetered to its RC. In particular, Senate relied solely on verbal communications of its AVR status from operators at its Facility to the personnel responsible for communicating that status to its RC. In addition, Senate lacked a process to verify that the correct AVR status was understood and properly telemetered to its RC. This noncompliance started on August 1, 2013, when the first incorrect AVR status was provided to Senate’s RC, and ended on February 17, 2017, when the correct AVR status was provided to Senate’s RC. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, throughout the duration of the issue, Senate’s generation unit’s AVR remained in service and would have likely operated to mitigate any voltage excursions that could have impacted the Bulk Electric System (BES) from generator disturbances. Second, during the period reviewed in the Compliance Audit, Senate maintained the voltage within the regional prescribed deadband of +/- 2% of the target 345 kV voltage. Third, the single Senate wind generation Facility at issue is small, with a nameplate rating of 150 MW. In 2016 and 2017, the unit operated with an average net capacity factor of only 2.1%. Finally, Senate’s telemetry issues were limited in scope. In particular, Senate is required to telemeter 36 data points under its applicable RC data specifications, and the single AVR data point only represents 2.78% of Senate's overall telemetry obligations. No harm is known to have occurred. Texas RE considered Senate’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance related to IRO-010-1a R3. | To mitigate this noncompliance, Senate: 1) provided the correct AVR status to its RC; 2) provided additional training materials regarding AVR status labels to applicable personnel; 3) implemented an enhanced data point communication process that now permits the Senate personnel responsible for telemetering data points to its RC to view those points, including AVR status, in Real-time; and 4) scheduled reoccurring meetings with applicable personnel to verify multiple items every six months, including the status of all AVR data points. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Florida Municipal Power Agency (FMPA) | NCR00022 | FRCC2017018382 | PRC-002-2 | R1; R1.2 | On September 27, 2017, FMPA submitted a Self-Report stating as a Transmission Operator it was in noncompliance with PRC-002-2 R1 (Part 1.2). The noncompliance started on September 30, 2016, when FMPA did not notify three (3) of the four (4) owners at the Cane Island 230kV Substation bus within 90 calendar days of completion of Part 1.1, that the BES Elements require Sequence of Events Recording (SER) data and/or Fault Recording (FR) data. The noncompliance ended on June 12, 2017, when FMPA notified the other owners (346 days late) as required by PRC-002-2, R1, Attachment 1. The root cause is a difference in interpretation, and because of this FMPA is now self-reporting the violation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FMPA's failure to notify other owners connected to the BES buses could have caused unnecessary installation delays thus impacting BES reliability. The necessary recording equipment was installed in the fall of 2016, prior to the phased-in implementation date of July 1, 2022 for the PRC-002-2 requirements. Since SER and FR data is recorded at the identified bus, there has been no gap in data as a result of the adjacent entities not being notified. FRCC determined that the noncompliance was appropriate for CE treatment because the issue was self-identified, was of minimal risk, and FMPA has not relevant history of noncompliance. No harm is known to have occurred. | To mitigate this noncompliance, FMPA: 1) compared the original notification recipients to the list of entities who own portions of the Transmission lines connected to the BES bus that was identified in Part 1.1 of R1 to determine the extent of condition; 2) sent a notification email to all of the identified owners of BES Elements connected to the BES bus that was identified in Part 1.1 of R1; and 3) enhanced the procedure with instructions on how to determine which entities are required to be notified based on the definition of BES Element; and 4) added tasks to the SharePoint for re-evaluation at least every five (5) years.
2018-02-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Gainesville Regional Utilities (GRU) | NCR00032 | FRCC2017018716 | EOP-010-1 | R3; 3.2 | During a Compliance Audit conducted from November 27, 2017 through November 30, 2017, FRCC determined that GRU, as a Transmission Operator, was in noncompliance with EOP-010-1 R3 (Part 3.2). The first instance of noncompliance started on June 22, 2015, at 15:42 when GRU was notified by the RC of a Geomagnetic Disturbance (GMD) event and ended at 16:32 when GRU returned to Normal Operations. GRU did not have sufficient evidence to demonstrate that GRU implemented System Operator actions required to be initiated based on predetermined conditions identified in GRU's GMD Procedure. Three (3) other instances of noncompliance occurred on October 7, 2015, October 25, 2016, and September 8, 2017 where GRU did not have evidence of implementing the procedure. The root cause for this noncompliance is due to insufficient detail in GMD procedure regarding documentation of response actions. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced by GRU’s geographical location (south of 50-degrees latitude), geology of the soil (sandy), and high-water table. A GMD Operation affecting a 230kV transformer in Florida is an extremely low probability event. GRU has two (2) high side wye-grounded winding power transformers with terminal voltage greater than 200 kV of which neither exceeded 20% of the transformers' MVA rating during the events. FRCC determined that the issue was appropriate for CE treatment because the issue was of minimal risk and GRU has no relevant history of noncompliance. No harm is known to have occurred. | To mitigate this noncompliance, GRU: 1) updated the GMD response procedure to provide specific instructions related to documenting response actions to GMD events; and 2) trained on the revised procedure.
2018-02-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Gainesville Regional Utilities (GRU) | NCR00032 | FRCC2017018717 | TPL-001-4 | R2; R2.3 | During a Compliance Audit conducted from November 27, 2017, through November 30, 2017, FRCC determined that GRU, as a Transmission Planner and Planning Authority, was in noncompliance with TPL-001-4 R2 (Part 2.3). This noncompliance started on January 1, 2016, when GRU, during the short circuit analysis portion of the Planning Assessment, failed to utilize in-service generation and transmission facilities to determine circuit breaker interrupting capability for faults, which could impact the study area as required by TPL-001-4 R2 (Part 2.3) and ended on January 8, 2018, when GRU included the in-service generation and transmission facilities into the System short circuit model for analysis. Specifically, GRU failed to include into the System short circuit analysis the Deerhaven Combustion Turbine (CT) #3 breaker and the J.R. Kelly CT #4 breaker for the 2015 and 2016 Planning Assessments. A second instance occurred when the Deerhaven CT #3 breaker was left out of the System short circuit analysis during the 2017 Planning Assessment. The root cause for this noncompliance is due to insufficient personnel allocated to effectively perform the planning assessment. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GRU’s failure to include in-service generation breakers in the Planning Assessment would have caused an inadequate analysis to be performed and the missing devices would not be analyzed to see if they could interrupt for expected faults. A failure of the Deerhaven CT #3 breaker would open the high-side GSU breaker isolating the generating unit from other BES facilities. A failure of the J.R. Kelly CT #4 breaker would open the high-side GSU breaker and the normal feed breaker for station service isolating the generating unit from other BES facilities. The risk was further reduced because GRU’s total generation output of 521 MWs represents 1% of the Region. FRCC determined that the issue was appropriate for CE treatment because the issue was of minimal risk and GRU has no relevant history of noncompliance. No harm is known to have occurred. | To mitigate this noncompliance, GRU will: 1) create a process to ensure that all breakers are checked for inclusion in annual planning assessment; 2) train applicable personnel on the process; and 3) staff a new position of Transmission Planning Engineer to direct and validate all planning assessments and studies. GRU's expected completion date is September 1, 2018. GRU needs this additional time to complete the final action of filling a new position, which will involve securing authorization and budgeting for the position and then posting and hiring someone for the position.
2018-02-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2017018874 | PRC-024-2 | R1 | On December 22, 2017, SEC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. SEC did not verify that it had set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” as required by PRC-024-2 Attachment 1. This noncompliance started on July 1, 2017, when SEC had not verified 60% of its applicable Facilities, as required by the PRC-024-2 Implementation Plan and ended on December 22, 2017, when SEC verified 100% of its applicable Facilities in advance of the July 1, 2019 Implementation Plan deadline. SEC has two (2) principal generating stations, Seminole Generating Station (SGS) and Midulla Generating Station (MGS) which are comprised of 10 individual units greater than 20 MVA: 1) SGS operates two steam unit generators (ST1 and ST2), each of which had its protective settings verified per the requirement prior to July 1, 2017. 2) MGS has two combustion turbine generators and a steam turbine generator in a two-on-one combined cycle configuration (Units CT1, CT2, and ST3) and five simple-cycle combustion turbine generators (Peakers 4 through 8). MGS Units CT1 and CT2 generators protective settings were verified per the requirement prior to July 1, 2017. MGS ST3 and the Peakers 4 though 8 protective relaying had not been verified. When calculating their compliance obligation, SEC only included six (6) generating units and verified four (4) that would have met the PRC-024-2 requirement of 60% by July 1, 2017. However, SEC actually has 10 generating units so only four (4) or 40% were verified as of July 1, 2017. Five (5) out of 10 generating units that had not been verified were connected to the same bus and SEC believed these were to be counted as one (1) when calculating their compliance. The five (5) Peakers are each greater than 20 MVA and should have been counted individually rather than aggregated. The root cause for this noncompliance was a misunderstanding in the application of the BES definition that resulted in an incorrect inventory of generating units with gross individual nameplate ratings greater than 20 MVA. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SEC’s failure to set its generator frequency protective relays to not trip within the “no trip zone” created an unnecessary risk that could have caused their generating units to improperly isolate during a frequency event. Since SEC had not verified their relays were not set within the “no trip zone,” their generators would have tripped too soon exacerbating the frequency event. SEC’s total generation output of 2,369 MWs represents only 4.59% of the Region. The generating units that were not verified totaled 453 MW representing less than .01% of the Region. No harm is known to have occurred as no frequency events occurred during this time frame. FRCC determined that the issue was appropriate for CE treatment because the issue was self-identified, was of minimal risk and SEC has no relevant history of noncompliance. | To mitigate this noncompliance, SEC: 1) verified that it had set its protective relaying such that the generator frequency protective relaying was not set within the "no trip zone" for the six (6) unverified units bringing them to 100% verification; 2) developed a new Operating Procedure to provide applicable subject matter experts and management specific guidance related to PRC-024-2 compliance implementation steps and dates; 3) delivered training on new Operating Procedure content and expectations to applicable subject matter experts and management; 4) required applicable subject matter expert and management complete an annual re-familiarization with PRC-024-2 requirements; 5) developed a Corporate implementation plan when new requirements are issued, with specific targets for each SEC entity and location; and 6) communicated and review implementations plans with each SEC entity, managers and SMEs .
2018-02-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2017018715 | PRC-002-2 | R1; R1.2 | On November 30, 2017, SEC submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-002-2 R1.2. This noncompliance started on September 30, 2016, when SEC did not notify other owners of BES Elements connected to those BES buses within 90-calendar days of completion of Part 1.1, that those BES Elements require Sequence of Events Recording (SER) data and/or Fault Recording (FR) data, and ended on October 18, 2017, when DEF was notified (389 days late). Specifically, SEC failed to notify Duke Energy Florida (DEF) within 90-calendar days that the Hardee Power Station (HPS) 230kV switchyard bus had been identified as needing SER and/or FR data as required by PRC-002-6, R1, Attachment 1. The root cause for this noncompliance is SEC’s misunderstanding of the Standard language (BES Element ownership) to properly determine appropriate notification applicability. Once clarification was received from FRCC, SEC self-reported the noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SEC’s failure to notify other owners connected to those BES buses could have caused unnecessary installation delays thus impacting BES reliability and/or stability in the area. The risk was reduced because DEF’s analysis had already identified Vandolah substation as containing buses requiring SER and FR data. Since SEC owns the SEC Hardee to DEF Vandolah 230kV line and associated bus elements at Vandolah, DEF had notified SEC on August 9, 2016. Furthermore, the actual installation is not due for another six years, and no events occurred during the noncompliance period. No harm is known to have occurred. FRCC determined that the issue was appropriate for CE treatment because the issue was self-identified, was of minimal risk, and SEC has no relevant history of noncompliance. | To mitigate this noncompliance, SEC: 1) notified DEF of requirement to obtain SER and/or FR equipment for its owned BES Elements connected to HPS Switchyard; 2) modified the PRC-002 process to ensure notification of any entity with a BES Element connected to a SEC substation requiring SER and FR equipment; and 3) trained applicable employees on the new process.
2018-02-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2017018470 | BAL-001-2 | R2 | On October 16, 2017, SEC submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-001-2 R2. This noncompliance started on September 15, 2017, when SEC's Area Control Error (ACE) clock-minute average of Reporting ACE exceeded its clock-minute Balancing Authority ACE Limit (BAAL) for 32 consecutive clock-minutes between 1015 and 1047. This event occurred during restoration efforts associated with hurricane Irma and ended on September 15, 2017, when additional generation was brought online and ACE returned to within the acceptable bounds. Initially, because of hurricane Irma, SEC was experiencing telecommunication issues and suspected a load calculation error due to the telemetry loss. SEC’s system operations personnel began an investigation with EMS support personnel rather than bringing on additional generation to bring their ACE value within acceptable bounds. Upon determination that all data used in calculating ACE was accurate and that the BAAL violation condition was correct, additional generation was placed online to recover ACE. SEC, however, was unable to bring the additional generation online quickly enough and proceeded to exceed their acceptable BAAL by two (2) minutes. The root cause for this violation was the System Coordinator suspected a load calculation error due to telemetry loss due to hurricane Irma and began investigation with EMS personnel rather than bringing on additional generation to bring SEC's ACE value within acceptable bounds. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SEC failed to operate such that its Reporting ACE did not exceed its BAAL for 32 consecutive clock-minutes. Such failure could contribute to a frequency excursion beyond defined limits. The risk was reduced because additional generation was being brought on line to correct the deficiency and a two (2) minute exceedance of the BAAL under hurricane restoration conditions did not have an appreciable effect on the BPS. SEC’s maximum ACE was -92 MWs during the exceedance. SEC's peak load of 4,315 MWs represents approximately 8.96% of the total load in the FRCC region. No harm is known to have occurred. SEC did not identify any real-time overloads, SOL or IROL contingencies during the noncompliance. FRCC determined that the issue was appropriate for CE treatment because the issue was self-identified, was of minimal risk, and SEC has no relevant history of noncompliance. | To mitigate this noncompliance, SEC: 1) conducted on-the-spot review and lessons learned on how and why the low BAAL event occurred; 2) reviewed lessons learned with subsequent teams prior to them assuming shift; 3) enhanced the EMS MapBoard Display to provide additional situational awareness display by adding a new trend showing the correlation between Net Scheduled and Net Actual Interchange; 4) reviewed event at recent monthly System Coordinator Meeting as Lessons Learned to promote situational awareness; 5) modified EMS displays to better identify primary, secondary and tertiary system frequency sources; 6) enhanced EMS alarming to include text message notification to SEC System operations Management personnel of high or low BAAL events at the 10-minute mark of the violation and every 5 minutes after; 7) modified real-time EMS alarming to begin at 5 minutes into a BAAL violation, and repeat every 5 minutes thereafter, rather than at 10 minutes; 8) developed new Control Center Operations Operating Instruction (OI) defining specific operator actions to take to alleviate High / Low BAAL violations; 9) developed new Control Center Operations General Information to provide guidelines to operators in troubleshooting an unaccounted-for ACE deviation from normal; and 10) delivered training on actions in new Operating Instruction.
2018-02-28 | Midwest Reliability Organization (MRO) | Corn Belt Power Cooperative (CBPC) | NCR00977 | MRO2017017861 | EOP-005-2 | R10 | During a Compliance Audit conducted from March 29, 2017 through March 30, 2017, MRO determined that CBPC, as a Transmission Operator, was in noncompliance with EOP-005-2 R10. One of CBPC's seven System Operators did not complete an annual System restoration training to assure the proper execution of its restoration plan. Accordingly, the System Operator did not receive annual training on the System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan (R10.1), Restoration priorities (R10.2), Building of cranking paths (R10.3), and Synchronizing (re-energized sections of the System) (R10.4). The cause of the noncompliance was that CBPC transitioned from one Reliability Coordinator to another Reliability Coordinator. CBPC utilizes participation in its Reliability Coordinator's restoration drill to meet this requirement. The System Operator had planned to perform the training through the previous Reliability Coordinator's fall 2016 restoration drill, but the transition prevented that training, and resulted in the System Operator not being able to perform the training until the new Reliability Coordinator's spring 2017 restoration drill. This noncompliance started on January 1, 2017, when the System Operator failed to take System restoration training in 2016 and ended on March 2, 2017, when the System Operator completed annual System restoration training through a restoration drill provided by the new Reliability Coordinator. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CBPC's system is relatively small (269 miles of 161 kV transmission), limiting its ability to impact the BPS outside of its footprint. Further, CBPC relies on another Transmission Operator as its source of system restoration power and participates in that Transmission Operator's System Restoration Plan. Additionally, the duration of the noncompliance was limited to three months. Finally, CBPC does not own or operate any Blackstart Resources. No harm is known to have occurred. CBPC has no relevant history of noncompliance. | To mitigate this noncompliance, CBPC: 1) had the System Operator participate in a system restoration drill provided by its new Reliability Coordinator; and 2) augmented existing internal controls by having the Compliance Director perform semi-annual follow-up with the CBPC Trainer regarding the status of System Operator training.
2018-02-28 | Midwest Reliability Organization (MRO) | Corn Belt Power Cooperative (CBPC) | NCR00977 | MRO2017017862 | EOP-005-2 | R6 | During a Compliance Audit conducted from March 29, 2017 through March 30, 2017, MRO determined that CBPC, as a Transmission Operator, was in noncompliance with EOP-005-2 R6. CBPC did not perform an analysis of actual events, steady state and dynamic simulations, or testing that verifies its restoration plan accomplishes its intended function. Accordingly, CBPC did not validate its restoration plan by confirming the location and magnitude of Loads required to control voltages and frequency within acceptable operating limits (R6.2) or the capability of generating resources required to control voltages and frequency within acceptable operating limits (R6.3). R6.1 is not applicable to CBPC because it does not own or operate a Blackstart Resource. The cause of the noncompliance was that CBPC did not believe the requirement applied because CBPC did not own or operate a Blackstart Resource. This noncompliance started on July 1, 2013, when the standard became mandatory and enforceable, and is expected to end on or before April 30, 2018 when CBPC completes the mitigating activity. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). CBPC's system is relatively small (269 miles of 161 kV transmission), limiting its ability to impact the BPS outside of its footprint. Further, CBPC relies on another Transmission Operator as its source of system restoration power and participates in that Transmission Operator's System Restoration Plan. Finally, CBPC does not own or operate any Blackstart Resources. No harm is known to have occurred. CBPC has no relevant history of noncompliance. | To mitigate this noncompliance, CBPC will purchase a powerflow program and perform the required analysis in-house using models from its Reliability Coordinator. CBPC expects that this will be completed on or before April 30, 2018. This mitigating activity represents a significant financial investment and needs to go through the proper budgetary procedure to get the funding, along with the required process to select the proper vendor and software package. This mitigating activity represents a significant investment in reliability, and this program will not only bring CBPC into compliance with this NERC Reliability Standard, but will augment its capabilities to perform planning studies and other activities that will enhance compliance and reliability. Many entities of similar size and profile outsource this responsibility, and this investment in an in-house capability represents a significant investment that distinguishes it from its peer group.
2018-02-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Central Hudson Gas & Electric Corporation | NCR07028 | NPCC2017017716 | PRC-006-NPCC-1 | R4 | On June 13, 2017, Central Hudson Gas and Electric Corporation (the Entity) submitted a Self-Report stating that, as a Distribution Provider (DP) and Transmission Owner (TO), it was in noncompliance with PRC-006-NPCC-1 R4. Specifically, the Entity discovered that its 2016 underfrequency load shedding (UFLS) program capability was out of compliance with the required automatic load shedding levels for Steps 1 and 2 of UFLS Table 1 of Attachment C. This noncompliance was caused by the fact that two new UFLS settings included in the program had not been actually implemented in the field. This noncompliance started on January 1, 2016, the enforcement date of the standard & requirement, and ended on May 30, 2017, when the Entity completed implementation of the aforementioned UFLS relay settings for two distribution circuits. The root cause of this instance of noncompliance is the fact that the Entity's Electric System Protection Dept. was not timely instructed by the Electric Transmission Planning Dept. to carry out field work necessary to implement planned modifications to UFLS settings prior to the start of the 2016 summer period. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The total load shedding deficiency of the Entity's 2016 UFLS program was approximately 3 MW, a relatively small amount when compared to the Entity's annual system peak load, which has ranged from 1059 MW to 1202 MW in the years 2012-2016. Additionally, the Entity's Reliability Coordinator's (NYISO) required summer/winter operating reserves are approximately 1965 MWs, a value which is often exceeded by a margin of about 600 MW above that requirement. In conclusion, the Entity's UFLS program's temporary deficiency could have been rectified in real-time by operating personnel during a load shedding event. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by implementating required UFLS relay settings for two distribution circuit; and 2. To prevent a recurrence of similar instances of noncompliance, revised its internal compliance procedure to establish a verification process whereby its Electric Transmission Planning Dept. will coordinate with the Entity's Electric System Protection Dept. all future UFLS scheme changes during the drafting stage of the UFLS program for any given year. Upon completion of all field work, EST will inform EP of all implemented settings modifications, so that EP can issue a final UFLS plan that reflects actual UFLS field settings. NPCC has verified the completion of all mitigation activity.
2018-02-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Rhode Island State Energy Center, LP | NCR11200 | NPCC2017017005 | PRC-019-2 | R1 | On February 14, 2017, Rhode Island State Energy Center, LP (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions by 7/1/2016, as applicable to its facilities. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on December 20, 2016 when the Entity completed coordination verification of in-service Protection System relays and in-service limiters on its three generating units. The coordination study confirmed that all in-service limiters and protection schemes were compliant with the standard, and that no modifications were necessary. The root cause of this instance of noncompliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to its facilities. The Entity erroneously thought that the compliance date for its three generating units would be July 1, 2017. This misunderstanding caused the Entity to fail to achieve timely compliance with the standard and requirement. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's non-compliant facility consists of two combustion turbines and one steam unit with a combined rated capability of close to 700 MVA. In 2016, the three generators, which are operated as one single combined cycle facility, experienced a 42.5% capacity factor. By comparison, the Entity's Reliability Coordinator (RC) (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. There is a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. The RC has comparable summer operating reserves requirements. If this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the RC would have been able to replace the lost capacity. The coordination of voltage regulating system controls confirmed that all in-service limiters and protection schemes were fully compliant with the standard, and that no modifications were necessary. For all the above considerations, this instance of noncompliance represents a minimal impact on the reliable operation of the BPS system. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1. Corrected the noncompliance by completing a coordination verification of in-service Protection System relays and in-service limiters on its three generating units; and 2. To prevent a recurrence of similar instances of noncompliance, hired an engineering consultant to perform a coordination of voltage regulating system controls for its generating units and provide necessary documentation to demonstrate compliance, and added a work order into its maintenance management system to perform a verification of coordination for the next 5-year cycle of review. NPCC has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Armstrong Power, LLC (Armstrong Power) | NCR11760 | RFC2017018535 | MOD-025-2 | R1 | On October 19, 2017, Armstrong Power submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. The entity did not meet the implementation timeline for MOD-025-2 R1 as the entity has four units and the entity did not complete testing of three of the four units by the July 1, 2017 implementation date for MOD-025-2 R1. The entity completed testing of one unit in July 2015, one unit in August 2016, and two units in August 2017. The entity had planned on completing testing of three of its four units before the July 1, 2017 date, but the entity’s testing schedule was impeded by the sale of the facility. First, on February 7, 2017, the entity was sold by Engie North America (Engie NA) to Dynegy. Second, on July 11, 2017, the entity was sold by Dynegy to LS Power. As part of the Engie NA fleet originally on the July 1, 2016 implementation date that required 40% of units to be tested, the entity was compliant in having 40% of the testing completed by July 1, 2016. Due to the ownership change and the entity becoming an independent plant with an independent registration after it was sold to LS Power in July 2017, the entity was not able to complete testing on 60% of its units by the July 1, 2017 deadline and therefore did not meet the Standard Implementation plan for MOD-025-2 R1. Upon completing tests on the entity's Units 3 and 4 in August 2017 and sending the results of those tests to PJM, the entity’s Transmission Planner, the entity is now fully compliant with MOD-025-2. a. On July 25, 2016, the entity performed the required testing on Unit 2 and sent the results of those tests to PJM on July 29, 2015. b. On August 8, 2016, the entity performed the required testing on Unit 4 and sent the results of those tests to PJM on August 31, 2016. c. On August 3, 2017, the entity performed the required testing on Unit 3 and sent the results of those tests to PJM on August 22, 2017. d. On August 10, 2017, the entity performed the required testing on Unit 1 and sent the results of those tests to PJM on August 22, 2017. This noncompliance involves the management practices of verification and external interdependencies. Verification is involved because the entity failed to verify that it would be compliant with the 60% testing requirement in the MOD-025-2 timeline after it was sold to LS Power and became an independent plant. That failure to verify is a root cause of this noncompliance. External interdependencies is involved because the two sales of the entity in 2017 to different owners with different registration strategies made maintaining compliance with MOD-025 difficult for the entity. This noncompliance started on July 11, 2017, when the entity was required to comply with MOD-025-2 R1 by completing the required testing and sending the results of that testing to PJM for 60% of its units and ended on August 22, 2017, when the entity completed performing the testing on 60% of its units and sent the results of that testing to PJM. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because LS Power quickly identified this noncompliance and reported it to ReliabilityFirst after taking ownership of the entity which demonstrates strong detective controls and a strong internal compliance program. Additionally, if the entity had not been sold to LS Power, the plant would have been in compliance with MOD-025-2 R1 under its previous owner’s registration organization. Upon taking ownership of the entity, LS Power quickly remediated this noncompliance by completing the MOD-025-2 testing and sending the results of that testing to PJM. Lastly, ReliabilityFirst notes that the entity operates one four-unit 625 MW gas turbine plant that operated at approximately a 40% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered the entity’s MOD-025-2 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed testing on Units 3 and 1. Completing testing on Unit 3, and sending the results of that testing to PJM, brought the entity back into compliance with the MOD-025-2 implementation timeline; and 2) set up work orders in the plant’s MMS System to ensure the next round of MOD-025 testing occurs on schedule or within 5 years and not to exceed 66 calendar months (to help prevent recurrence). ReliabilityFirst has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017018474 | PRC-005-1b | R2 | On October 11, 2017, Consumers submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-005-1b R2. On December 1, 2015, the entity purchased the Jackson Generating Station from NAES Corporation. In 2017, while transitioning the PRC-005 Protection System Maintenance & Testing Program for Jackson Generation Station to the Consumers Energy PRC-005 Program, the Consumers Energy System Protection Group identified a set of Auxiliary (Aux) Voltage Transformers (VTs) that may have a potential problem. After discovering this potential problem, the entity reviewed this issue with Jackson Generating Station who believed that all facility PRC-005 applicable VTs were tested in 2009 and were not due to be tested again until 2019. The testing interval at the Jackson Generating Station for these VTs was 10 years. During its review, the entity identified that one set of Aux VTs at the Jackson Generating Station did not have any documentation of testing. The entity and Jackson Generating Station personnel concluded that the one set of Aux VTs at issue were not tested in 2009 as scheduled and had not been tested since commissioning of the set of VTs in 2002. When Jackson Generating Station originally developed its PRC-005 program, a variety of personnel and contractors helped identify all applicable components from specific Kinder Morgan drawings of the facility Protection System components. The personnel and contractors never noticed that, in addition to the primary set of VTs supplying the 59BN relay on Unit 7 with ratio 14,400 - 120 Volts Grounded Wye/Grounded Wye, that there was also a set of Aux VTs changing the secondary side input to relay from 120V Grounded Wye to 120V Grounded Open Delta. This was due to the Aux VTs not being listed on the specific drawing used for program development, and also being mounted in an obscure location inside the control cabinet, nowhere in the vicinity of the primary VTs located in the breaker cubicle. An additional GE equipment drawing identified the Aux VTs, from which the Consumers Energy System Protection group made the decision to include them in PRC-005 scope. Consumers Energy Protection Systems Group cross-checked all other historical NAES documentation to ensure the existence of all other necessary testing records and determined that no other discrepancies exist. The entity tested the set of Aux VTs at issue during a scheduled outage on September 21, 2017 and determined that the VTs were performing correctly. This noncompliance involves the management practices of external interdependencies and verification. External independencies is involved because the entity did not confirm with NAES that all VTs at the Jackson Generating Station had been timely tested and documented before purchasing the facility. Verification is involved because the entity did not verify that all tests had been timely performed and documented by NAES before the sale was finalized. This failure to verify is a root cause of this noncompliance. This noncompliance started on March 14, 2012, when the Jackson Generating Station was required to comply with PRC-005-1b R2 and ended on September 21, 2017, when the entity completed the overdue testing of the set of Aux VTs. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that allowing a Protection System device such as an Aux VT to remain untested may result in the failure of that VT which could potentially lead to the loss of approximately 250 MW of generation. The risk is minimized because a subsequent ground fault on the bus would be picked up through generation fault detection or transformer fault detection because of overlapping systems of protection. The entity also discovered this noncompliance after acquiring the Jackson Generating Station from NAES which evidences the entity’s effective detective controls. Additionally, ReliabilityFirst notes that when the entity subsequently tested the set of Aux VTs, the VTs were operational and had no issues. No harm is known to have occurred. ReliabilityFirst considered the entity’s PRC-005 R2 compliance history in determining the disposition track. The entity's relevant prior noncompliance with PRC-005 R2 includes: RFC2015015214. A Compliance Exception addressing a noncompliance with PRC-005-1 R2 was posted on the NERC website on March 31, 2016. The prior noncompliance is distinguishable from the instant noncompliance because the prior noncompliance involved Consumers failing to include two 138kV bus fault detector relays in its PRC-005 maintenance program. A contributing factor to the prior noncompliance was that Consumers did not accurately and completely identify its protection system equipment following its sale of transmission assets to Michigan Transmission Electric Company, LLC (“METC”) in 2002. After this sale, Consumers and METC split all of the assets between the two companies. However, Consumers mistakenly listed METC as the owner of the two relays at issue in the prior noncompliance when, in fact, Consumers owned them. In contrast, the instant noncompliance arose from NAES failing to test a set of Aux VTs back in 2009 when NAES still owned the Jackson Generating Station. The contributing causes are different as in the prior noncompliance, Consumers mistakenly listed METC as the owner of the two relays while in the instant noncompliance NAES failed to test a set of Aux VTs before it sold the Jackson Generating Station to Consumers. ReliabilityFirst determined that Consumers’ compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, the entity: 1) completed the testing for the identified Aux VTs; 2) incorporated any additional equipment into the program; and 3) performed a review of equipment drawings to ensure no other components were not included in Consumers’ Protection System Maintenance and Testing Program. That review found no additional PRC-005 applicable VTs present that were not captured in Jackson Generating Station’s PRC-005 program. ReliabilityFirst has verified the completion of all mitigation activity.
2018-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | METC | NCR00820 | RFC2017017945 | PRC-004-4(i) | R1 | On July 5, 2017, METC submitted a Self-Report on behalf of ITCM stating that, as a Transmission Owner, it was in noncompliance with PRC-004-4(i) R1. ITCM failed to identify whether a Protection System component caused a Misoperation within 120 days of the date of the incident (or Misoperation) occurring. Instead, ICTM initially mistakenly determined that the incident did not qualify as a Misoperation because the relays at issue were not considered “in-service” due to commission testing not being complete at the time of the Misoperation. Regardless, ITCM took immediate action to correct the issue that caused the Misoperation. Through internal reviews, ITCM later determined that the incident should have been identified as a Misoperation. As background, in late 2015 and early 2016, ITCM installed a new relay at Hiawatha to protect a 115 kV capacitor bank, which had a reactive capability of 60 MVAR. Near the end of the construction project, the load check (and resulting setting adjustments) on the new relay did not occur because it required the capacitor bank to be energized, and energizing the capacitor bank could have exposed the system to voltage fluctuations. As a result, the capacitor bank was supposed to remain deenergized until technicians could be onsite to observe and manage the load tests. However, on August 1, 2016, the capacitor bank was ordered to be energized (contrary to ITCM’s procedures regarding commissioning assets) due to lower than normal voltage in the area, but because the relay did not go through final load testing, it misoperated by tripping the capacitor bank during otherwise normal system conditions. No other operations were required as a result of the Misoperation to maintain stability of the Bulk Electric System. Additionally, voltage limits were not violated. Pursuant to PRC-004-4(i) R1, ITCM should have identified the incident as a Misoperation within 120 days from the date of the Misoperation. However, because the relay was not considered “in-service,” ITCM incorrectly determined that the incident did not qualify as a Misoperation, and thus did not, after identifying the cause, create and implement a formal corrective action plan. Regardless, by August 4, 2016 (3 days after the Misoperation), the relay settings were evaluated and corrected. The root cause of the delay in identifying the incident as a Misoperation was confusion regarding whether the status of the relay not being considered in-service constitutes a Misoperation. Additionally, ITCM determined that there was inconsistency internally regarding expectations from ITCM’s commissioning and “in service” processes. Had personnel been onsite during energization as was required, the event would have been considered a commissioning activity as opposed to a Misoperation. This noncompliance involves the management practice of workforce management, including training to ensure all personnel understand the policies regarding commissioning assets. While the noncompliance resulted from ITCM not identifying the instance as a Misoperation within 120 days, RF also recognizes the risk of placing equipment in service before it has been fully tested. METC has provided RF assurance that it enhanced its verification controls to ensure all commissioning activities are formally tracked and completed before placing equipment in service. This noncompliance also involves verification, which includes having controls to verify that all commissioning activities are completed before placing assets in service. This noncompliance started on November 28, 2016, the date by which ITCM was required to identify whether its Protection System component caused a Misoperation, and ended on May 5, 2017, when ITCM identified the Misoperation. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by an entity’s failure to timely identify whether the Protection System component(s) caused a Misoperation is that an entity would not correct the cause of the Misoperation to prevent recurrence. However, this risk was mitigated here because although ITCM did not properly identify the incident as a Misoperation, ITCM nonetheless implemented immediate corrective action by evaluating and correcting the relay settings that caused the Misoperation. Additionally, within approximately nine months of the Misoperation, ITCM self-identified the noncompliance and created a Mitigation Plan to prevent occurrence of future similar Misoperations. The other risk of not timely identifying the Misoperation is that an entity will not provide proper notifications to affected entities pursuant to PRC-004-4(i) R2. However, this risk was mitigated here because there were no other affected entities to which ITCM was required to provide notice. No harm is known to have occurred. ReliabilityFirst considered ITCM's PRC-004 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, ITCM: 1) evaluated and corrected the relay settings at Hiawatha; 2) tagged Hiawatha C1 Capacitor Bank “out of service” (per GAP-013); 3) scheduled testing to complete load checks; 4) discussed changes to procedures to better line up terminology and understanding. The processes were revised to provide consistency regarding commissioning and in-service processes. Had personnel been on site during energization as was desired, this event would not have been categorized as a Misoperation, but as a commissioning activity; and 5) finalized and published changes to the procedures to line up terminology and understanding. ReliabilityFirst has verified the completion of all mitigation activity.
2018-02-28 | SERC Reliability Corporation (SERC) | City of Columbia, MO (CWLD) | NCR01196 | SERC2017016880 | TOP-002-2.1b | R19 | During a Compliance Audit conducted from September 13, 2016 to September 15, 2016, SERC determined that CWLD, as a Transmission Operator (TOP), was in noncompliance with TOP-002-2.1b R19. CWLD did not maintain accurate models of its transmission system when it replaced equipment and used an incorrect Facility Rating in its planning models. In 2014 and 2015, during meetings with an adjacent Transmission Owner (TO), CWLD agreed to replace devices on the McBaine-McBaine tap 161 kV transmission line in order to upgrade the Facility Rating. A 600 A switch and 600 A line trap limited the pre-modification Rating to 167 MVA. Late in 2015, CWLD decided to replace the switch (upgrading to 1200 A) and the wave trap (upgrading to 2000 A). CWLD planned the modifications to increase the capacity of the line to 895 A (249 MVA), the limit established by the conductor. All of the work to complete the modifications occurred during a scheduled outage between January 24, 2016 and January 29, 2016. Beginning February 4, 2016, CWLD communicated the 249 MVA Facility Rating to the adjacent TO and its Reliability Coordinator (RC) for use in planning models. CWLD also used the 249 MVA Facility Rating in its planning models. However, internally, CWLD applied its Facility Rating Methodology and observed that a multi-ratio current transformer limited the Facility Rating to 800 amps (223 MVA) and CWLD had entered that value into its Energy Management System (EMS). In addition, CWLD informed the audit team that, due to an internal failure to communicate, it had incorrectly communicated a Facility Rating of 249 MVA (the planned capacity) to the neighboring TO and RC instead of the correct 223 MVA Rating, and was also using the incorrect value of 249 MVA in its planning models. The audit team reviewed all of the BES Facilities owned by CWLD and found no other noncompliances with TOP-002-2.1b. The primary cause of the noncompliance was inadequate procedures that did not address the current transformer ratio during the modification process and human error resulting in communication of the assumed Facility Rating for use by planners and operators. SERC determined that CWLD was in noncompliance with TOP-002-2.1b R19 because it did not maintain accurate models for planning system operations. This noncompliance started on February 4, 2016, when CWLD began using the incorrect Facility Rating in its planning models, and ended on September 29, 2016, when CWLD changed the Facility Rating to the value that had been previously entered incorrectly into the planning models. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). CWLD’s use of incorrect Facility Ratings in its planning models could result in inadequate outage and contingency planning, resulting in equipment failure and reduced equipment lifetimes. However, in this case, although CWLD was using a Facility Rating value in its plan models that was 112% of the correct Facility Rating, the affected Facility Rating was correctly modeled and alarmed in the EMS, limiting real-time risk to the BPS. The McBaine to McBaine tie networks do not provide load or receive generation directly. If an equipment failure had occurred, no generation or load would have been lost. The planning models were incorrect for approximately eight months. No harm is known to have occurred. SERC considered CWLD’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, CWLD: 1. Sent an email to all parties involved informing them of the rating error and to correct their models to the correct rating of 223 MVA for the McBaine-McBaine Tap. 2. Coordinated with Central Electric Power Cooperative to change the multi-ratio current transformers previously set to 800:5 to 1200:5. In accordance with CWLD's Facilities Rating Methodology a multi-ratio current transformer set at 1200:5 has a rating of 1200 A. Also, in accordance with CWLD's Facilities Rating Methodology, setting the multi-ratio current transformers to 1200:5 changed the most limiting element for the McBaine-McBaine Tap line to the line conductor itself having a rating of 895 A (249 MVA). This completed the original intent of the McBaine-McBaine Tap line upgrade, which replaced a switch (upgraded from 600 A to 1200 A) and a wave trap (upgraded from 600 A to 2000 A) to increase the line rating to 895 A (249 MVA). 3. Sent an email to all parties involved informing them of the changes made and the new rating of 249 MVA for the McBaine-McBaine Tap and to update their models with the new rating. 4. Revised the CLWD Facility Rating Methodology concerning instrument transformers to include an appendix with a workflow process for updating Facility Ratings after there have been physical changes to the CWLD electric system.
2018-02-28 | SERC Reliability Corporation (SERC) | Plum Point Energy Associates (PPEA), LLC - GO (PlumGO) | NCR10385 | SERC2017018515 | PRC-019-2 | R1 | On October 25, 2017, PlumGO submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. PlumGO stated that it had not performed the required coordination of its voltage regulating system controls and its Protection System devices and functions pursuant to the implementation plan of PRC-019-2 R1. The PlumGO facility is a single 800 MW coal-fired generator. NRG Energy Services LLC (NRG), serves as the Generator Operator (GOP) of PlumGO under an operating and maintenance agreement. Therefore, the PlumGO facility is included within NRG Energy, Inc.’s “fleet-wide” compliance approach that combined NRG registrations within the Eastern Interconnection. The implementation plan for PRC-019-2 phased in enforcement over a five-year period beginning July 1, 2014. It requires each GO to have verified at least 40 percent of its applicable Facilities by July 1, 2016. NRG established a plan to verify the coordination of 40 percent of the 172 generators in its operating fleet in the Eastern Interconnection by July 1, 2016, but included the Plum Point facility in its plans for the second increment. On August 6, 2016, PlumGO verified coordination of its voltage regulating system controls and Protection Systems as required by PRC-019-2 R1. On August 25, 2016, SERC posted a response to a question it received and, on March 24, 2017, the ERO distributed a guide for “Phased Implementation Plans with Completion Percentages”. Both documents stated that compliance must be demonstrated on a Registered Entity basis rather than on a “fleet-wide” basis. On September 29, 2017, NRG performed a registration-by-registration compliance assessment and determined that its phased in approach did not meet the published guidance. As soon as NRG learned that its program did not align with the NERC guidance, it changed its approach to accelerate the schedule for the necessary analyses for compliance with PRC-019-2, and PlumGO submitted its Self-Report. The cause of this noncompliance was the adoption of a plan for compliance that was not based on the appropriate registration function. This noncompliance started on July 1, 2016, the date by which PlumGO should have performed the verification, and ended on August 6, 2016, when PlumGO performed the required verification. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PlumGO’s failure to verify the coordination of its voltage regulating system controls and its Protection System devices and functions within the timeframe specified in the PRC-019-2 implementation plan could have resulted in unnecessary tripping of a generation unit which could aggravate a system disturbance. However, PlumGO completed verification of its single unit only 36 days late, and when PlumGO performed its verification, it made no setpoint changes to its voltage regulating system controls or Protection System devices or functions. PlumGO had operated successfully at a 62% capacity factor with no adverse interaction between its voltage regulating system controls and Protection Systems. No harm is known to have occurred. SERC considered PlumGO’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, PlumGO: 1. Completed the tests for PRC-019; 2. Since the March 24, 2017 release of the NERC guidance for determining the percentage completion, NRG, on behalf of its registered entities, including PlumGO, is executing its implementation on a registration basis, consistent with the NERC guidance.
2018-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Eastman Cogeneration Limited Partnership (EASTMAN) | NCR01092 | SPP2016015924 | MOD-025-2 | R1; R1.1, R1.2 | On July 21, 2016, EASTMAN submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. EASTMAN did not verify the Real Power capability of its generating units in accordance with Attachment 1. As a result, EASTMAN was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its applicable Facilities. The root cause of this instance of noncompliance was lack of understanding, by EASTMAN management, of the requirements of MOD-025-2, which prevented it from completing its Real Power testing by the standard effective date of July 1, 2016. EASTMAN is a cogenerating facility consisting of two 170 MW gas turbines and one 128 MW steam turbine. EASTMAN Chemical manufacturing facility consumes 200 MW of the available generation. MOD-025-2 standard states that "It is intended that Real Power testing be performed at the same time as full load Reactive Power capability testing." EASTMAN did not perform Real Power capability testing because of possible unsafe conditions caused by an unplanned shutdown of EASTMAN's chemical process areas, resulting from voltage excursions at the North Texas EASTMAN substation. The noncompliance started on July 1, 2016, the effective date of the standard, and ended September 17, 2017, the date EASTMAN completed mitigation of the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of issues affecting the reliability of the BPS. Notwithstanding, EASTMAN Chemical manufacturing facility consumes 200 MWs of the available generation from its cogeneration facility, leaving only 268 MW going to the bulk electric system. No harm is known to have occurred. SPP RE reviewed EASTMAN’s violation history and determined that EASTMAN has no prior instances of noncompliance with MOD-025-2. | To mitigate this issue, EASTMAN: 1) completed preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conducted tests and verified the Real Power capability of its generating units; 3) submitted a verification of the Real Power capability of its generating units to the TP within 90 days from the test date; and 4) conducted NERC Violation training for appropriate staff. SPP RE has verified the completion of all mitigation activity.
2018-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Eastman Cogeneration Limited Partnership (EASTMAN) | NCR01092 | SPP2016015925 | MOD-025-2 | R2; R2.1, R2.2 | On July 21, 2016, EASTMAN submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2, R2.1 and R2.2. EASTMAN did not verify the Reactive Power capability of its generating units in accordance with Attachment 1. As a result, EASTMAN was unable to provide Attachment 2 to its Transmission Planner (TP) with verification of the Reactive Power capability of its applicable Facilities. The root cause of this instance of noncompliance was lack of understanding, by EASTMAN management, of the requirements of MOD-025-2, which prevented it from completing its Reactive Power testing by the standard effective date of July 1, 2016. MOD-025-2 standard states that "It is intended that Real Power testing be performed at the same time as full load Reactive Power capability testing." EASTMAN did not perform Reactive Power capability testing because of possible unsafe conditions caused by an unplanned shutdown of EASTMAN’s chemical process areas, resulting from voltage excursions at the North Texas EASTMAN substation. The noncompliance started on July 1, 2016, the effective date of the standard, and ended September 20, 2017, the date EASTMAN completed mitigation of the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of issues affecting the reliability of the BPS. Notwithstanding, EASTMAN Chemical manufacturing facility consumes 200 MW of the available generation from its cogeneration facility, leaving only 268 MW going to the bulk electric system. No harm is known to have occurred. SPP RE reviewed EASTMAN’s violation history and determined that EASTMAN has no prior instances of noncompliance with MOD-025-2. | To mitigate this issue, EASTMAN: 1) completed preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conducted tests and verified the Reactive Power capability of its generating units; 3) submitted a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date; and 4) conducted NERC Violation training for appropriate staff. SPP RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | CenterPoint Energy Houston Electric, LLC (CNP) | NCR04028 | TRE2017018429 | PRC-004-5(i) | R2; P2.1 | On October 2, 2017, CNP submitted a Self-Log stating that, as a Transmission Owner (TO), it was in noncompliance with PRC-004-5(i) R2, Part 2.1. In particular, CNP failed to provide notification to a Generator Owner (GO) of a shared Composite Protection System within 120 calendar days of a Bulk Electric System (BES) interrupting device operation on three occasions in 2017. While performing internal controls testing in August 2017, CNP discovered that it experienced an interrupting device operation by a shared Composite Protection System meeting all applicable notification criteria on February 7, 2017. As such, CNP should have provided notification of the operation to the other Composite Protection System owners by June 7, 2017. However, CNP did not provide the required device operation notification until July 12, 2017, 34 days after the required notification deadline. Following its discovery of this initial instance, CNP performed a full internal review and identified two additional instances in which it did not provide notification to the other Composite Protection System owners within 120 calendar days of an applicable interrupting device operation. In the first additional instance, CNP experienced an applicable interrupting device operation on March 5, 2017. Accordingly, CNP should have provided the required notification to the other Composite Protection System owners by July 3, 2017. However, CNP did not provide the required notification until August 10, 2017, 37 days after the required 120 calendar day deadline. In the second additional instance, CNP experienced an applicable interrupting device operation on March 28, 2017. As such, CNP should have provided the requisite notification to the other Composite Protection System owners by July 26, 2017. However, CNP again did not provide the required notification until August 10, 2017, 14 days after the required 120 calendar day deadline. The root cause of this noncompliance was that CNP lacked a sufficient process to ensure its personnel tracked and implemented the appropriate deadlines for the required 120 calendar day interrupting device operations at issue. In particular, CNP relied on a single employee to track the applicable deadlines, and this employee erroneously believed that CNP had 180 calendar days to provide the required notifications. This noncompliance started on June 7, 2017, the day after the first notification was due to the GO (co-owner), and ended on August 10, 2017, when CNP provided the remaining interrupting device operation notifications to the other Composite Protection System owners as required. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, CNP did provide evidence that it performed an analysis of the device operations in question, but failed to timely provide the results of that analysis to the other Composite Protection System owners. Second, after conducting an analysis, CNP did not identify any interrupting device Misoperations in all three instances. Third, in all three instances, the other Composite Protection System owner indicated that it was aware of the CNP interrupting device operations. Fourth, the duration of the noncompliance was relatively short, lasting between 14 days and 37 calendar days. No harm is known to have occurred. Texas RE considered CNP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, CNP: 1) provided notification of the BES interrupting device operations to the other applicable Composition Protection System owner; 2) implemented a process for a designated follow-up team to review notifications for applicable interrupting device operations within 120 days of interrupting device operations; 3) conducted training on PRC-004-5(i) interrupting device operation notification requirements for affected staff; 4) modified its existing outage reporting system to automatically calculate the deadline date for each outage event; and 5) configured its outage reporting system to send email reminders of approaching notification deadlines to two separate department email addresses. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | City of Austin dba Austin Energy (AE1) | NCR04029 | TRE2017018191 | COM-001-2.1 | R9 | On August 11, 2017, AE1 submitted a Self-Log stating that, as a Transmission Operator (TOP), it was in noncompliance with COM-001-2.1 R9. In particular, AE1 did not have evidence that it tested its Alternative Interpersonal Communication (AIC) capability at its Backup Control Center (BUCC) during two calendar months in 2016. While reviewing its records as part of a routine internal review, AE1 determined that it could not locate monthly AIC testing records at its BUCC for April and October 2016. The root cause of this noncompliance was an insufficient process to remind all applicable staff members to conduct and document all required AIC capability testing on a monthly basis. In particular, AE1 did not adequately utilize various reminder tools to ensure its personnel tested and documented all designated AIC capabilities as required. This noncompliance started on May 1, 2016, the day after AE1’s monthly AIC capability testing was due in the first instance of noncompliance, and ended on November 30, 2016, when AE1 successfully completed and documented the testing of its designated AIC capability in the last instance of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, AE1’s primary communications systems were operational during the two months for which AE1 was missing testing records for its designated AIC system. Second, when AE1 performed subsequent AIC capability following each issue, it did not identify any issues with its designated AIC system. Third, even if there had been an issue with both AE1’s primary and AIC communication systems, AE1 possessed additional communications methods that it could have utilized to maintain situational awareness. Fourth, the duration of each testing issue was short, lasting only 15 and 29 days, respectively. No harm is known to have occurred. Texas RE considered AE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, AE1: 1) completed all required monthly AIC capability testing; 2) implemented an additional calendar reminder sent to a supervisor one week after the calendar reminder to on-shift personnel to confirm that the testing was completed; 3) implemented a new electronic log tool for recording the AIC testing; 4) streamlined and modified its AIC testing checklist to facilitate AIC testing and documentation; and 5) conducted training to remind all applicable staff members to conduct and document all required AIC capability testing on a monthly basis. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IA, LLC (LVWIA) | NCR11267 | TRE2017017263 | MOD-025-2 | R1 | On March 20, 2017, LVWIA submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, LVWIA failed to verify the Real Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. LVWIA determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, LVWIA performed the required Real Power capability verification testing of its single generation unit on December 6, 2017, and submitted the results to its Transmission Planner (TP) on December 15, 2017. The root cause of this noncompliance was that LVWIA misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, LVWIA mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on December 15, 2017, when LVWIA submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, LVWIA previously provided passing Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, LVWIA provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in June, September, and December 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Third, LVWIA has a nameplate capacity of only 200 MW and operated only at approximately a 36 percent capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered LVWIA’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIA: 1) completed the required Real Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IA, LLC (LVWIA) | NCR11267 | TRE2017017264 | MOD-025-2 | R2 | On March 20, 2017, LVWIA submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. In particular, LVWIA failed to verify the Reactive Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. LVWIA determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, LVWIA performed the required Reactive Power capability verification testing of its single generation unit on December 6, 2017, and submitted the results to its Transmission Planner (TP) on December 15, 2017. The root cause of this noncompliance was that LVWIA misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, LVWIA mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on December 15, 2017, when LVWIA submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, LVWIA previously provided passing Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, LVWIA provided information similar to the required Reactive Power verification data through other submissions to its Planning Coordinator in June, September, and December 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Third, LVWIA has a nameplate capacity of only 200 MW and operated only at approximately a 36 percent capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered LVWIA’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIA: 1) completed the required Reactive Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IB, LLC (LVWIB) | NCR11266 | TRE2017017267 | MOD-025-2 | R1 | On March 20, 2017, LVWIB submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, LVWIB failed to verify the Real Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1, by July 1, 2016. LVWIB determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, LVWIB performed the required Real Power capability verification testing of its single generation unit on January 10, 2018, and submitted the results to its Transmission Planner (TP) on January 25, 2018. The root cause of this noncompliance was that LVWIB misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, LVWIB mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on January 25, 2018, when LVWIB submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, LVWIB previously provided Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, LVWIB provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in June, September, and December 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Third, LVWIB has a nameplate capacity of only 201 MW and operated only at approximately a 34 percent capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered LVWIB’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIB: 1) completed the required Real Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower IB, LLC (LVWIB) | NCR11266 | TRE2017017268 | MOD-025-2 | R2 | On March 20, 2017, LVWIB submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. In particular, LVWIB failed to verify the Reactive Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1, by July 1, 2016. LVWIB determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, LVWIB performed the required Reactive Power capability verification testing of its single generation unit on January 10, 2018, and submitted the results to its Transmission Planner (TP) on February 22, 2018. The root cause of this noncompliance was that LVWIB misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, LVWIB mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on February 22, 2018, when LVWIB submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, LVWIB previously provided Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, LVWIB provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in June, September, and December 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Third, LVWIB has a nameplate capacity of only 201 MW and operated only at approximately a 34 percent capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered LVWIB’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWIB: 1) completed the required Reactive Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower III, LLC (LVWPIII) | NCR11538 | TRE2017017271 | MOD-025-2 | R1 | On March 20, 2017, LVWPIII submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, LVWPIII failed to verify the Real Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. LVWPIII determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, LVWPIII performed the required Real Power capability verification testing of its single generation unit on March 9, 2017, and submitted the results to its Transmission Planner (TP) on April 4, 2017. The root cause of this noncompliance was that LVWPIII misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, LVWPIII mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on April 4, 2017, when LVWPIII submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, LVWPIII previously provided passing Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, LVWPIII provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in June, September, and December 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Third, LVWPIII has a nameplate capacity of only 201 MW and operated only at approximately a 34 percent capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered LVWPIII’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWPIII: 1) completed the required Real Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Los Vientos Windpower III, LLC (LVWPIII) | NCR11538 | TRE2017017272 | MOD-025-2 | R2 | On March 20, 2017, LVWPIII submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. In particular, LVWPIII failed to verify the Reactive Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. LVWPIII determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, LVWPIII performed the required Reactive Power capability verification testing of its single generation unit on March 9, 2017, and submitted the results to its Transmission Planner (TP) on April 4, 2017. The root cause of this noncompliance was that LVWPIII misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, LVWPIII mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on April 4, 2017, when LVWPIII submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, LVWPIII previously provided passing Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, LVWPIII provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in June, September, and December 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Third, LVWPIII has a nameplate capacity of only 201 MW and operated only at approximately a 34% capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered LVWPIII’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LVWPIII: 1) completed the required Reactive Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Luminant Generation Company, LLC (LGC) | NCR10219 | TRE2017018212 | BAL-001-TRE-1 | R9 | On August 14, 2017, LGC submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with BAL-001-TRE-1 R9. In particular, LGC did not meet a minimum 12-month rolling average initial Primary Frequency Response (PFR) performance of 0.75 on seven generating units, based on participation in at least eight Frequency Measurable Events (FMEs) by October 1, 2016. LGC owns 43 total generating units in the Texas RE region. Beginning on October 1, 2016 and continuing over the next several months, LGC determined that seven generation units had participated in eight FMEs and had likewise not met the required 0.75 initial PFR performance standard. The lowest 12-month rolling average initial PFR for the seven generating units at issue ranged from 0.3064 to 0.7300. LGC subsequently elected to retire six of the seven generating units at issue in January and February 2018. The final generating unit in question has, as of January 2018, an initial PFR of 0.7105, which is below the required 0.75 initial PFR performance threshold. The root cause of this noncompliance was various technical issues at the seven generating units at issue. In particular, the control systems on certain units caused a withdrawing of responses that limited the response when an FME occurred. Additionally, one of the units has a unique fan design that lowered the unit net output by causing an increase in auxiliary load, again negatively impacting its initial PFR performance. This noncompliance started on October 1, 2016, when LGC was required to be compliant with BAL-001-TRE-1 R9 and had a generating unit that had experienced eight FMEs and did not meet the required 0.75 initial PFR, through the present. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the combined average initial PFR for all LGC units with eight or more FMEs over the issue duration is 0.9784, which is above the required 0.75 initial PFR threshold. As such, if LGC had issues providing adequate PFR from one of its generating units, LGC could have likely relied on other generating units in its fleet to provide adequate overall PFR. Second, the overall market frequency response in ERCOT is robust enough to ensure sufficient frequency response is available to respond to the FMEs. In particular, for 2016 and 2017, the ERCOT Interconnection minimum Frequency Response (IMFR) was 381 and the average actual Interconnection Frequency Response over that period was 889. No harm is known to have occurred. Texas RE considered LGC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LGC will: 1) retire six of its units at issue; 2) make incremental adjustments on the control systems pertaining to the one remaining generating unit at issue; and 3) continue to review the performance of the single remaining unit to ensure its 12-month initial PFR rolling average stays above 0.75. LGC needs until November 20, 2018 to complete its mitigation actions in order to make all applicable system adjustments during a scheduled outage and to allow time to monitor its rolling averages.
2018-02-28 | Texas Reliability Entity (Texas RE) | Luminant Generation Company, LLC (LGC) | NCR10219 | TRE2018019123 | BAL-001-TRE-1 | R10 | On August 14, 2017, LGC submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with BAL-001-TRE-1 R9. Specifically, LGC did not meet a minimum 12-month rolling average initial Primary Frequency Response (PFR) performance of 0.75 on seven generating units, based on participation in at least eight Frequency Measurable Events (FMEs) by October 1, 2016. Subsequently, on February 8, 2018, Texas RE determined that the issue described in LGC's BAL-001-TRE-1 R9 Self-Report also constituted a noncompliance with BAL-001-TRE-1 R10. In particular, LGC did not meet a minimum 12-month rolling average sustained PFR performance of 0.75 on six generating units, based on participation in at least eight FMEs by October 1, 2016. LGC owns 43 total generating units in the Texas RE region. Beginning on October 1, 2016 and continuing over the next several months, six LGC generation units had participated in eight FMEs and did not possess the required 0.75 sustained PFR performance level. The lowest 12-month rolling average sustained PFR for the six generating units at issue ranged from 0.4655 to 0.6306. LGC subsequently elected to retire five of the six generating units at issue in January and February 2018. The final generating unit in question has, as of January 2018, a sustained PFR of 0.7196, which is below the required 0.75 initial PFR performance threshold. The root cause of this noncompliance was various technical issues at the six generating units at issue. In particular, the control systems on certain units caused a withdrawing of responses that limited the sustained PFR response when an FME occurred. Additionally, one of the units has a unique fan design that lowered the unit net output by causing an increase in auxiliary load, again negatively impacting its sustained PFR performance. This noncompliance started on October 1, 2016, when LGC was required to be compliant with BAL-001-TRE-1 R10, and had a generating unit that had experienced eight FMEs and did not meet the required 0.75 initial PFR, through the present. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the combined average initial PFR for all LGC units with eight or more FMEs over the issue duration is 0.9784, which is above the required 0.75 initial PFR threshold. As such, if LGC had issues providing adequate PFR from one of its generating units, LGC could have likely relied on other generating units in its fleet to provide adequate overall PFR. Second, the overall market frequency response in ERCOT is robust enough to ensure sufficient frequency response is available to respond to the FMEs. In particular, for 2016 and 2017, the ERCOT Interconnection minimum Frequency Response (IMFR) was 381 and the average actual Interconnection Frequency Response over that period was 889. No harm is known to have occurred. Texas RE considered LGC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, LGC will: 1) retire six of its units at issue; 2) make incremental adjustments on the control systems pertaining to the one remaining generating unit at issue; and 3) continue to review the performance of the single remaining unit to ensure its 12-month initial PFR rolling average stays above 0.75. LGC needs until November 20, 2018 to complete its mitigation actions in order to make all applicable system adjustments during a scheduled outage and to allow time to monitor its rolling averages.
2018-02-28 | Texas Reliability Entity (Texas RE) | Mesquite Creek Wind LLC (MCW) | NCR11511 | TRE2017017260 | MOD-025-2 | R1 | On March 20, 2017, MCW submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, MCW failed to verify the Real Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. MCW determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, MCW performed the required Real Power capability verification testing of its single generation unit on December 5, 2017, and submitted the results to its Transmission Planner (TP) on December 18, 2017. The root cause of this noncompliance was that MCW misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, MCW mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on December 18, 2017, when MCW submitted its Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) for the following reasons. First, MCW previously provided passing Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, MCW provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in March and September 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Third, MCW has a nameplate capacity of only 105 MW and operated only at approximately a 39 percent capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered MCW’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, MCW: 1) completed the required Real Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Mesquite Creek Wind LLC (MCW) | NCR11511 | TRE2017017261 | MOD-025-2 | R2 | On March 20, 2017, MCW submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. In particular, MCW failed to verify the Reactive Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. MCW determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline for its single wind generation Facility as required. As a result, MCW performed the required Reactive Power capability verification testing of its single generation unit on December 5, 2017, and submitted the results to its Transmission Planner (TP) on December 18, 2017. The root cause of this noncompliance was that MCW misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, MCW mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on December 18, 2017, when MCW submitted its Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, MCW previously provided passing Reactive Power verifications under region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, MCW provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in March and September 2016. These submissions are used to coordinate the development of transmission planning models with regional TPs. Finally, MCW has a nameplate capacity of only 105 MW and operated only at approximately a 39% capacity factor during the issue period. As a result, any errors in the Facility's Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered MCW’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, MCW: 1) completed the required Reactive Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) implemented a process that tracks the implementation of new or revised NERC Reliability Standards; 4) created a procedure to perform generator verifications for NERC compliance and manage change to maintain ongoing compliance with MOD-025; 5) created a procedure for completing MOD-025-2 testing, including a requirement that all testing information be submitted to its TP within 90 days of completion; and 6) created automatic reminders that notify applicable staff members to provide the TP with verification of the Real and Reactive Power capability results. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Optim Energy Altura Cogen, LLC (Altura) | NCR10072 | TRE2017018084 | MOD-025-2 | R1 | On July 31, 2017, Altura submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. In particular, Altura failed to verify the Real Power capability of its seven generating units in accordance with MOD-025-2, Attachment 1 by July 1, 2016. On November 11, 2014, Altura received initial information regarding its upcoming compliance responsibilities under the new Real and Reactive Power capability verification standards. Throughout 2015, Altura continued to submit region-specific Real and Reactive Power capability verification information, which did not contain all information set forth in MOD-025-2, Attachment 1. In September 2016, Altura submitted an additional Real and Reactive Power capability verification for one of the generating units at its Facility, again using the region-specific form. Following this submission, Altura learned in December 2016 that the region-specific submissions it had been using did not conform to the requirements set forth in MOD-025-2, Attachment 1. As a result, Altura initiated an internal investigation and determined that it needed to perform new Real and Reactive Power capability verifications for all generating units at its Facility. Over the course of 2017, Altura experienced several significant delays in completing the required Real and Reactive Power capability verifications as a result of outages and a hurricane event. Altura finally completed the required MOD-025 Real and Reactive Power capability verifications for all its applicable generating units on December 11 and 12, 2017. On January 19, 2018, Altura submitted its Real Power capability verification results to its Transmission Planner (TP), ending the issue. The root cause of this noncompliance was the lack of a process to evaluate and prepare for new or revised NERC Reliability Standards. In particular, Altura lacked a process to review compliance documents and/or submissions to ensure they met all applicable NERC Standards, as well as a process to periodically review and communicate compliance responsibilities to applicable personnel. The noncompliance started on July 1, 2016, the enforcement date of the Standard, and ended on January 19, 2018, when Altura submitted its completed Real Power capability verification to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, Altura provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within five years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, Altura provided similar Real Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. No harm is known to have occurred. Texas RE considered Altura’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Altura: 1) completed the required Real Power capability verification for its applicable generation units; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) developed and implemented a written process to assess new or revised NERC Reliability Standards and prepare for compliance, including procedures to develop or update internal documentation to comply with the new Standard and evaluate whether the Standard overlaps with any corresponding regional requirements; 4) developed and implemented a process to assign applicable compliance materials to designated subject matter experts, as well as a review of applicable compliance materials by Altura management; and 5) created a task in its task management program to send a series of reminders to multiple staff members of upcoming MOD-025 deadlines. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Optim Energy Altura Cogen, LLC (Altura) | NCR10072 | TRE2017018085 | MOD-025-2 | R2 | On July 31, 2017, Altura submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. In particular, Altura failed to verify the Reactive Power capability of its seven generating units in accordance with MOD-025-2, Attachment 1 by July 1, 2016. On November 11, 2014, Altura received initial information regarding its upcoming compliance responsibilities under the new Real and Reactive Power capability verification standards. Throughout 2015, Altura continued to submit region-specific Real and Reactive Power capability verification information, which did not contain all information set forth in MOD-025-2, Attachment 1. In September 2016, Altura submitted an additional Real and Reactive Power capability verification for one of the generating units at its Facility, again using the region-specific form. Following this submission, Altura learned in December 2016 that the region-specific submissions it had been using did not conform to the requirements set forth in MOD-025-2, Attachment 1. As a result, Altura initiated an internal investigation and determined that it needed to perform new Real and Reactive Power capability verifications for all generating units at its Facility. Over the course of 2017, Altura experienced several significant delays in completing the required Real and Reactive Power capability verifications as a result of outages and a hurricane event. Altura finally completed the required MOD-025 Real and Reactive Power capability verifications for all its applicable generating units on December 11 and 12, 2017. On January 19, 2018, Altura submitted its Reactive Power capability verification results to its Transmission Planner (TP), ending the issue. The root cause of this noncompliance was the lack of a process to evaluate and prepare for new or revised NERC Reliability Standards. In particular, Altura lacked a process to review compliance documents and/or submissions to ensure they met all applicable NERC Standards, as well as a process to periodically review and communicate compliance responsibilities to applicable personnel. The noncompliance started on July 1, 2016, the enforcement date of the Standard, and ended on January 19, 2018, when Altura submitted its completed Reactive Power capability verification to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, Altura provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, Altura provided similar Reactive Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. Third, Altura did not experience any Reactive Power capability changes during the noncompliance period. Fourth, Altura did not receive any requests to provide Reactive Power support during the issue duration. No harm is known to have occurred. Texas RE considered Altura’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Altura: 1) completed the required Reactive Power capability verification for its applicable generation units; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) developed and implemented a written process to assess new or revised NERC Reliability Standards and prepare for compliance, including procedures to develop or update internal documentation to comply with the new Standard and evaluate whether the Standard overlaps with any corresponding regional requirements; 4) developed and implemented a process to assign applicable compliance materials to designated subject matter experts, as well as a review of applicable compliance materials by Altura management; and 5) created a task in its task management program to send a series of reminders to multiple staff members of upcoming MOD-025 deadlines. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Texas Reliability Entity (Texas RE) | Senate Wind, LLC (Senate) | NCR11274 | TRE2017018299 | TOP-001-1a | R3 | During a Compliance Audit conducted from July 25, 2017 through September 6, 2017, Texas RE determined that Senate, as a Generator Operator (GOP), was in noncompliance with TOP-001-1a R3. In particular, Senate did not comply with a reliability directive issued by its Transmission Operator (TOP) to lower its voltage on August 20, 2016. At 1:49 a.m. on August 20, 2016, Senate’s TOP issued a directive to Senate to lower its voltage by 2 kV. Upon receiving this directive, Senate’s designated point of contact failed to relay the directive to the appropriate Senate personnel. Instead, Senate’s point of contact communicated the directive to personnel that could not perform the voltage action. As a result, Senate was unable to lower its voltage as directed. Senate’s designated contact informed its TOP that it could not lower Senate’s voltage. The TOP then addressed the issue by making other adjustments. The TOP cancelled the directive at 2:52 a.m., ending the issue. The root cause of this noncompliance was an insufficient process to ensure that TOP directives were communicated to the appropriate Senate personnel in all instances. In particular, Senate’s existing communications procedures did not sufficiently identify which personnel should receive directives to adjust voltage levels from Senate’s designated point of contact outside of normal business hours. This noncompliance started at 1:49 a.m. on August 20, 2016, when Senate’s TOP issued the reliability directive, and ended at 2:52 a.m. on August 20, 2016, when the reliability directive ended. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the specific directive at issue called for only a 2 kV reduction in Senate’s voltage levels, an amount unlikely to cause voltage issues on the TOP’s system. Second, Senate personnel informed the TOP that it could not comply with the directive, and the TOP was able to modify voltage levels through other means. Third, Senate only experienced a single issue following TOP directives and properly complied with similar TOP directives on other occasions, indicating this was an isolated and not a systemic issue. Fourth, the generation Facility at issue is small, with a nameplate rating of 150 MW and an average output of 77 MW in 2016, and not directly connected to any regional generic transmission constraints. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. No harm is known to have occurred. Texas RE considered Senate’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Senate: 1) received notice that the directive from its TOP was canceled; 2) clarified its communication process to ensure all voltage directives are relayed to designated Senate plant operational specialists; 3) updated and distributed a contact list to the Reliability Coordinator (RC), TOP, and Senate personnel receiving directives. The list identifies contacts, each contact’s operational role, and the specific circumstances in which designated individuals should be contacted; 4) conducted additional training on communications protocols; and 5) established a routine contact validation process to ensure Senate personnel receiving directives have current and accurate contact information. Texas RE has verified the completion of all mitigation activity.
2018-02-28 | Western Electricity Coordinating Council (WECC) | Midway Peaking, LLC (MIDP) | NCR10323 | WECC2017017002 | PRC-019-2 | R1 | On February 14, 2017, MIDP submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, MIDP reported that it failed to coordinate voltage regulating system controls with equipment capabilities and Protection System device settings for at least 40 percent of its applicable Facilities by the effective date of the Standard. The root cause of this issue was MIDP’s misunderstanding regarding the effective date of the Standard; MIDP believed the 40 percent threshold would not become effective until July 1, 2017. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of MIDP’s Facilities, and ended June 29, 2017, when MIDP completed a study verifying requisite coordination items, for a total of 363 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, MIDP failed to coordinate at least 40 percent of its applicable Facilities in accordance with R1 by the effective date of the Standard. Such failure could result in over-current damage to MIDP’s applicable Facilities, or an unnecessary generator trip. However, this issue was limited to two 70 MW units. MIDP never experienced an unnecessary trip on either unit due to the previous settings, and no harm is known to have occurred. The coordination report showed that no settings changes were needed. Based on this information, WECC determined that this issue power minimal risk to the reliability of the BPS. MIDP does not have previous violations of this Standard and Requirement. | To mitigate this issue, MIDP: 1) revised V/Hz and voltage settings in accordance with the PRC-019-2 R1.1 coordination items; 2) established periodic, escalating notifications to ensure timely tracking and completion of future PRC-019-2 deadlines; 3) created and implemented a quarterly review process to proactively address soon-to-be effective Standards; and 4) assigned responsibility for compliance-related tasks and scheduling to designated staff. WECC verified completion of MIDP’s mitigating activities.
2018-01-31 | Northeast Power Coordinating Council, Inc. (NPCC) | National Grid USA | NCR11171 | NPCC2017018714 | FAC-008-3 | R8.1 | On November 27, 2017, National Grid USA (the Entity) submitted a self-log stating that, as a Transmission Owner, it was in noncompliance with FAC-008-3 R8. Specifically, the Entity failed to provide requested information of a planned upgrade to its Planning Coordinator/Reliability Coordinator (PC/RC) (ISO-NE) at least fifteen (15) business days prior to the expected in-service date of said upgrade, as specified in the "ISO New England Operating Procedure No.16 Transmission System Data". The planned upgrade consisted of replacement of a circuit breaker and associated bus-work at a 115 kV substation. This noncompliance started on September 26, 2017, one day after the date when submittal of the information was due to the PC/RC, and ended on October 11, 2017, when the Entity actually effected the required information submittal. The root cause of this instance of noncompliance was the result of a human error caused by a misunderstanding, on the part of responsible staff, regarding the specific planned in-service date of the aforementioned system upgrade. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This noncompliance did not cause a degradation to the reliability of the bulk power system. In fact, the upgrade implemented at the aforementioned 115 kV Substation increased the ratings of a 115 kV feeder emanating from this substation only under a specific operating scenario where a normally closed breaker within this substation were to be operated in the "open" position. Although the Entity's submittal was not in strict compliance with the 15 day advance timeline established by its RC for planned maintenance, the information was, nevertheless, provided 13 days in advance of the actual in-service date of the upgrade. Additionally, as the system was operated in the normal mode, the increased facility ratings were never needed or implemented during the period of noncompliance. No harm is known to have occurred as a result of this issue of non-compliance. | To mitigate this noncompliance, National Grid USA: 1. Corrected the noncompliance by effecting the required information submittal to the ISO-NE; and 2. To prevent a recurrence of similar instances of noncompliance, the Entity's management completed a review with responsible personnel of the importance of implementing the established practice of creating preliminary ratings during the "As-Planned", or design, phase of any project (or upgrade), to enable the submittal of requested information related to planned upgrades in accordance with the timeline required by the ISO-NE. The review clarified that potential changes during the construction phase can always be communicated to the ISO-NE via subsequent submittals to be effected prior to the actual in service date of the project. NPCC has verified the completion of all mitigation activity.
2018-01-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Pittsfield Generating Company, LP | NCR07195 | NPCC2016016695 | PRC-019-2 | R1 | On December 16, 2016, Pittsfield Generating Company, LP (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1.Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions on 40% of its facilties by 7/1/2016, as required by PRC-019-2 R1 and the corresponding Implementation Plan. Due to the nature of the combined cycle generating equipment at Pittsfield, the voltage regulating system control verification testing needed to be complete on 100% of the Pittsfield generating facilties by 7/1/2016 in order for Pittsfield to meet the 40% obligation. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on January 10, 2018 when the Entity completed coordination verification of its in-service Protection System relays and in-service limiters, and de-activated malfunctioning under-excitation limiters (UELs) on all four combined cycle generating units. The root cause of this instance of non-compliance was, partly, an initial misinterpretation of tests results on the part of the engineering consultant hired by the Entity to test the facility's protection system relays, and, partly, difficulties in achieving compliance related to certain specific limiters, the under excitation limiters, which are integral part of the facility's outdated automatic voltage regulating system. These delays caused the Entity to fail to achieve timely compliance with the 40% deadline in the PRC-019-2 Implementation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity's non-compliant combined cycle facility consists of three gas turbines and one steam unit with a combined rated capability of 202 MVA at a 90% power factor. In 2016, the four generators, which are operated as one single combined cycle facility, experienced an 18% capacity factor (a typical operating factor for this facility). By comparison, the Entity's RC (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. The RC has comparable summer operating reserves requirements. In conclusion, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the RC would have been able to replace the lost capacity. For all the above considerations, this instance of non-compliance represents a minimal impact on the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, Pittsfield Generating Company, LP: 1. Corrected the noncompliance by completimg coordination verification of its in-service Protection System relays and in-service limiters; and 2. To prevent a recurrence of similar instances of noncompliance, requested that its engineering consultant revise its initial report to reflect the correct compliance status of its facility's voltage protection relays while also permanently de-activating nonfunctional UEL devices on all four generating units. NPCC has verified the completion of all mitigation activity.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017018011 | EOP-005-2 | R17 | On July 13, 2017, Consumers submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with EOP-005-2 R17. Consumers failed to fully document two hours of training for the operating personnel of one of its Thetford Generating Stations. The Thetford Generating Stations are Blackstart Resources. On June 9, 2017, while performing a comprehensive compliance review per company guidelines, Consumers discovered this instance of noncompliance. (As part of a deeper dive due to identifying another potential issue, the Compliance Manager reviewed the evidence Consumers used to demonstrate compliance with the NERC Standards. During the review, the Compliance Manager identified the missing portion of the EOP-005 evidence.) Consumers has completed template sign-in sheets for the training and has evidence that the training was completed. Consumers, however, does not have evidence that documents the length of the training. Consumers cannot show that the training lasted the required two hours. While the template sign-in sheets have evidence of the training, there was no place on the sign-in sheets to indicate the length of the training. Thus, the length of training was undocumented. This noncompliance involves the management practices of verification and workforce management. Verification is involved because Consumers Energy failed to verify that the training lasted the required two hours and that lack of verification is a cause of this noncompliance. Workforce management is involved because Consumers did not effectively train its personnel to always document the length of the operating training required by EOP-005-2 R17. This noncompliance started on August 28, 2015, two years after when Consumers could last provide evidence that it completed and documented two hours of training for the operating personnel of the Thetford Generating Station at issue and ended on August 28, 2017, when Consumers completed and documented two hours of training for the operating personnel at the Thetford Generating Station at issue. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that personnel responsible for implementing the system restoration plan have not been trained on the plan, thereby posing a risk that the personnel will not be able to effectively execute the system restoration plan, which could lead to delayed system restoration following an event. The risk is minimized because Consumers has evidence that the training was properly and timely conducted in 2015 and that all relevant operating personnel attended the training in 2015. This reduces the risk because it shows that Consumers operating personnel did receive some training. Consumers is only missing evidence that shows the training in 2015 lasted the required two hours. Further minimizing the risk, Consumers also has evidence that properly documents the two hour duration of the training for the same operating personnel from when Consumers conducted the training in 2013. Lastly, the operating personnel at the Thetford Generating Station properly started the facility and energized the bus using the Blackstart procedures in 2013 and in 2016 as required by EOP-005-2 R17. No harm is known to have occurred. ReliabilityFirst considered Consumers’ EOP-005 R17 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Consumers modified the Blackstart unit personnel training sign-in sheets to contain a specified entry for the duration of the training and a description of activities. The new sign-in sheets are being added to the current plant-specific Blackstart programs through document revisions. (The training documentation for Ludington units 2 and 3 were revised on June 23, 2017, and the training document for Thetford units 2, 3 and 4 were revised on August 23, 2017. The Ludington Unit 5 program was revised on September 1, 2017.) Consumers trained relevant personnel on how to use and document the length of the training using the modified sign-in sheets. The new sign-in sheet will properly capture the duration of the training. In January of 2017, Consumers implemented a more robust process for tracking compliance readiness. This process increases internal oversight related to compliance readiness with new and revised NERC Standards. Specific elements of the process include improved tracking of phased in requirements, business units affirming requirement ownership, collecting evidence of having updated procedures in place, and affirming readiness to comply. The compliance readiness program provides greater visibility to upcoming requirements assigned to Consumers business units and reduces the risk of missing scheduled implementation Standards. ReliabilityFirst has verified the completion of all mitigation activity.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017018014 | MOD-026-1 | R4 | On July 18, 2017, Consumers submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-026-1 R4. Consumers did not provide plans to perform model verification to its Transmission Planner (TP), METC, within 180 calendar days of making changes to its Ludington Pumped Storage Unit 4. Consumers discovered this instance of noncompliance during a comprehensive compliance program review on June 9, 2017. (The noncompliance was identified through an internal discussion of Consumers’ TP registration during an internal audit. The clarification discussion came about through analysis of a previous self-report submitted to ReliabilityFirst. In the discussion, compliance team members identified that although Consumers is a registered TP, and it does enter the test results into the Planning Authority modeling database, the Facilities owned by the company interconnect with another TP, METC. Therefore, Consumers should have submitted the verification plan for MOD-026 to the TP, METC, for the generating units.) The outage necessary to upgrade Unit 4 ended and the unit was offered commercially on May 27, 2016. Based off of the upgrades to Unit 4, Consumers was required to notify the TP of a plan to validate the new model by November 23, 2016. This noncompliance involves the management practices of verification and workforce management. Verification is involved because Consumers failed to verify that it would provide plans to perform a model verification within 180 calendar days after making changes/upgrades to Ludington Pumped Storage Unit 4. Workforce management is involved because Consumers failed to properly train its personnel to perform model verification within the required window. That failure to properly train is a cause of this noncompliance. This noncompliance started on November 23, 2016, when Consumers was required to have notified its TP of a plan to perform model verification within 180 calendar days of Consumers making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic and ended on June 23, 2017, when Consumers notified the TP of a plan to perform model verification. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that not providing accurate generator model information to the TP to include in dynamic simulations that assess Bulk Electric System reliability during frequency variations could potentially cause a system outage due to lack of resources. The risk is minimized because although Consumers did not provide a plan to verify the excitation control model and the model parameters, Consumers did perform initial validation during commissioning of the rebuilt generating unit. Additionally, the generation characteristics of the facilities have not changed dramatically over the lifetime of the equipment, and updates to the system model have been performed annually, so minimal deviations to the generation capability would result in an inconsequential impact to the transmission system model. The models representing the new turbine/governor and load control characteristics were entered into the modeling database used by the TP on September 27, 2016, before this noncompliance even began. Lastly, Consumers’ upgrade of the Ludington Pumped Storage facility is a multi-year project that was approved by the TP. Although the TP was not informed of the specific plan to validate the equipment as required in MOD-026 and MOD-027, the TP was aware of activities occurring at the facility which further reduces the risk as the TP was generally aware of changes occurring at the facility. No harm is known to have occurred. ReliabilityFirst considered Consumers’ MOD-026 R4 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Consumers will complete the following mitigation activities by January 31, 2018: 1) contacted the TP, METC, to coordinate communication of information. The MISO Business Practice Manual requires Generator Owners and Transmission Owners to enter information into the modeling program. To ensure compliance with the NERC Standards and to minimize risk to the Bulk Electric System due to incorrect modeling data, Consumers provided validation tests and updated Modeling information to ITC/METC as well as entered the information into the MISO modeling program; 2) drafted a preliminary overhaul procedure; 3) revised/overhauled the draft procedure, due to Company reorganization; 4) will address procedure comments and finalize the procedure; 5) will approve the procedure; and 6) will implement and train on the new procedure. Consumers’ mitigating actions will ensure validation is performed on the equipment as required. Documented procedures will provide guidance to the current and future business members associated with performing the actions of MOD-026-1 and guidance will ensure proper testing and reporting is performed. In January of 2017, Consumers initiated a compliance readiness program. The program is owned by the regulatory compliance department and the Accountable Authority for NERC. The group monitors new and revised Reliability Standards as they are being created to ensure the appropriate business units and Compliance Assurance Managers are aware and prepared for upcoming changes to the compliance program. Although this program was initiated after the compliance enforcement date for MOD-026-1, it will provide a secondary tracking mechanism for future Standards. On June 20, 2017 Consumers formed a compliance task force to review the company's compliance posture. This team reviewed all of the Standards and the evidence the company uses to demonstrate compliance. Consumers needs until the end of January 2018 to complete these mitigation activities because the process of drafting a new procedure, revising that procedure due to company reorganization, finalizing that procedure, and implementing and training all new relevant personnel on that procedure is a lengthy process that will not be completed until the end of January 2018.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017018015 | MOD-027-1 | R4 | On July 18, 2017, Consumers submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-027-1 R4. Consumers did not provide plans to perform model verification to its Transmission Planner (TP), METC, within 180 calendar days of making changes to its Ludington Pumped Storage Unit 4. Consumers discovered this instance of noncompliance during a comprehensive compliance program review on June 9, 2017. (The noncompliance was identified through an internal discussion of Consumers’ TP registration during an internal audit. The clarification discussion came about through analysis of a previous self-report submitted to ReliabilityFirst. In the discussion, compliance team members identified that although Consumers is a registered TP, and it does enter the test results into the Planning Authority modeling database, the Facilities owned by the company interconnect with another TP, METC. Therefore, Consumers should have submitted the verification plan for MOD-026 to the TP, METC, for the generating units.) The outage necessary to upgrade Unit 4 ended and the unit was offered commercially on May 27, 2016. Based off of the upgrades to Unit 4, Consumers was required to notify the TP of a plan to validate the new model by November 23, 2016. This noncompliance involves the management practices of verification and workforce management. Verification is involved because Consumers failed to verify that it would provide plans to perform a model verification within 180 calendar days after making changes/upgrades to Ludington Pumped Storage Unit 4. Workforce management is involved because Consumers failed to properly train its personnel to perform model verification within the required window. That failure to properly train is a cause of this noncompliance. This noncompliance started on November 23, 2016, when Consumers was required to have notified its TP of a plan to perform model verification within 180 calendar days of Consumers making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic and ended on June 23, 2017, when Consumers notified the TP of a plan to perform model verification. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that not providing accurate generator model information to the TP to include in dynamic simulations that assess Bulk Electric System reliability during frequency variations could potentially cause a system outage due to lack of resources. The risk is minimized because although Consumers did not provide a plan to verify the excitation control model and the model parameters, Consumers did perform initial validation during commissioning of the rebuilt generating unit. Additionally, the generation characteristics of the facilities have not changed dramatically over the lifetime of the equipment, and updates to the system model have been performed annually, so minimal deviations to the generation capability would result in an inconsequential impact to the transmission system model. The models representing the new turbine/governor and load control characteristics were entered into the modeling database used by the TP on September 27, 2016, before this noncompliance even began pursuant to MOD-032-1. Lastly, Consumers’ upgrade of the Ludington Pumped Storage facility is a multi-year project that was approved by the TP. Although the TP was not informed of the specific plan to validate the equipment as required in MOD-026 and MOD-027, the TP was aware of activities occurring at the facility which further reduces the risk as the TP was generally aware of changes occurring at the facility. No harm is known to have occurred. ReliabilityFirst considered Consumers’ MOD-027 R4 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Consumers will complete the following mitigation activities by January 31, 2018: 1) contacted the TP, METC, to coordinate communication of information. The MISO Business Practice Manual requires Generator Owners and Transmission Owners to enter information into the modeling program. To ensure compliance with the NERC Standards and to minimize risk to the Bulk Electric System due to incorrect modeling data, Consumers provided validation tests and updated Modeling information to ITC/METC as well as entered the information into the MISO modeling program; 2) drafted a preliminary overhaul procedure; 3) revised/overhauled the draft procedure, due to Company reorganization; 4) will address procedure comments and finalize the procedure; 5) will approve the procedure; and 6) will implement and train on the new procedure. Consumers’ mitigating actions will ensure validation is performed on the equipment as required. Documented procedures will provide guidance to the current and future business members associated with performing the actions of MOD-026-1 and guidance will ensure proper testing and reporting is performed. In January of 2017, Consumers initiated a compliance readiness program. The program is owned by the regulatory compliance department and the Accountable Authority for NERC. The group monitors new and revised Standards as they are being created to ensure the appropriate business units and Compliance Assurance Managers are aware and prepared for upcoming changes to the compliance program. Although this program was initiated after the compliance enforcement date for MOD-026-1, it will provide a secondary tracking mechanism for future Standards. On June 20, 2017 Consumers formed a compliance task force to review the company's compliance posture. This team reviewed all of the Standards and the evidence the company uses to demonstrate compliance. Consumers needs until the end of January 2018 to complete these mitigation activities because the process of drafting a new procedure, revising that procedure due to company reorganization, finalizing that procedure, and implementing and training all new relevant personnel on that procedure is a lengthy process that will not be completed until the end of January 2018.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Interpower/Ahlcon Partners Limited Partnership (InterPower) | NCR11335 | RFC2017017769 | PRC-001-1.1(ii) | R3 R3.1 | On June 13, 2017, ReliabilityFirst determined that InterPower, as a Generator Operator, was in noncompliance with PRC-001-1.1(ii) R3.1 identified during a Compliance Audit conducted from May 8, 2017, through May 19, 2017. ReliabilityFirst discovered that Interpower failed to coordinate settings changes done for three relays with its Transmission Operator (TOP) and Balancing Authority (BA) before performing these changes in the field on October 2016. However, InterPower later discovered this omission and communicated these changes to its TO, FirstEnergy, in November 2016, one month later. FirstEnergy then communicated these changes to PJM, Interpower’s TOP/BA. The major factor contributing to the cause of this noncompliance was a lack of communication between the group responsible for making the changes and InterPower’s NERC team. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets. This noncompliance started on October 21, 2016, when InterPower made the changes to the relays and ended on May 17, 2017, when InterPower communicated these changes to its TOP and BA. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Generally, the failure to coordinate protective system changes with the applicable TOP/BA could result in the TOP/BA not having an accurate depiction of its system. This risk was mitigated by the following factors. First, InterPower discovered the omission and communicated the changes to FirstEnergy one month later. Second, considering the size of the plant at issue, changes are very infrequent. Therefore, this type of issue is unlikely to occur again. Third, the nature of the changes themselves was not risky, but presumably increased the reliability of the BPS because the changes made to the relays were done to be in compliance with PRC-024. Fourth, the Colver generating unit can contribute up to 110 MW to the grid and operated at a capacity factor of approximately 96%. Therefore, its potential loss would have a minimal impact on the reliability of the BPS. No harm is known to have occurred. ReliabilityFirst considered InterPower’s PRC-001 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Interpower: 1) communicated the changes to its TOP and BA; 2) modified its procedure for PRC-001-1.1 to include a checklist to be completed by the field personnel and the NERC team any time there is a change to, or a replacement of, a protection system relay. This modification specifically outlines the procedure for providing notification to the proper entities; and 3) retrained responsible personnel on the notification requirements of PRC-001-1.1.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Interpower/Ahlcon Partners Limited Partnership (InterPower) | NCR11335 | RFC2017017768 | PRC-019-2 | R1 | On June 13, 2017, ReliabilityFirst determined that InterPower, as a Generator Owner, was in noncompliance with PRC-019-2 R1 identified during a Compliance Audit conducted from May 8, 2017, through May 19, 2017. ReliabilityFirst determined that InterPower failed to coordinate its voltage regulating system controls as required by PRC-019-2 R2. InterPower conducted Siemens voltage regulator testing back in 2014 and believed that would suffice for compliance with PRC-019. The root cause of this noncompliance was InterPower’s mistaken belief that the testing it performed in 2014 would suffice for compliance with PRC-019. This major contributing factor involves the management practice of workforce management in that the responsible personnel at InterPower did not fully understand what was required by PRC-019. This noncompliance started on July 1, 2016, when InterPower was required to comply with PRC-019-2 R1 and ended on May 10, 2017, when InterPower completed the requisite coordination. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the risk posed by this noncompliance is a lack of coordination of voltage regulating controls and Protection System settings which can result in a generator unnecessarily tripping. In this case, that risk was minimized because no changes were required. Second, the Colver generating unit can contribute up to 110 MW to the grid and operated at a capacity factor of approximately 96%. Therefore, its potential loss would have a minimal impact on the reliability of the BPS. No harm is known to have occurred. ReliabilityFirst considered InterPower’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Interpower: 1) hired a consultant who performed the requisite testing and coordination; and 2) trained responsible personnel on the requirements of the Standard.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | KMC Thermo, LLC (KMC) | NCR11475 | RFC2017018009 | PRC-019-2 | R1 | On July 13, 2017, KMC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. A KMC engineer that is no longer with KMC prepared calculations for compliance with PRC-019-2 in preparation for the July 1, 2016 implementation date of PRC-019-2. At the time the engineer made those calculations, KMC believed those calculations were accurate. In 2017, KMC contracted with a third party expert, Kestrel Power Engineering (Kestrel), to perform services for MOD-026-1, MOD-027-1, and PRC-024-2. Due to the related nature of those Standards with PRC-019-2, KMC had Kestrel double check the calculations the KMC engineer performed for PRC-019-2. Kestrel’s review discovered that the engineer did not include the settings for the in service voltz per hertz’s limiters in the original study. When Kestrel included those settings, Kestrel determined that KMC’s limiter was set to a value above the generator’s Protection System settings in the Basler Protection Relay. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the KMC engineer that performed the original PRC-019-2 calculations was not properly trained on how to perform the calculations because he did not include the voltz per hertz limiter settings in his original calculations. Verification is involved because KMC did not have an effective internal control in place to verify that the engineer’s original PRC-019-2 calculations were correct. That lack of an effective verification control is a root cause of this noncompliance. This noncompliance started on July 1, 2016, when KMC was required to comply with PRC-019-2 R1 and ended on July 7, 2017, when Kestrel completed the calculations correctly with the voltz per hertz limiter settings included. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that the uncoordinated voltage regulating system controls could cause a unit outage. The risk is minimized because the setting changes required to insure the in-service limiters are set to operate before the protection system were minimal meaning the devices would still operate properly. Since the setting changes only affected the in-service limiters and did not affect any of the coordinated Protection System devices or settings, there was no need to engage the Host Balancing Authority and Transmission Operator. All other KMC devices are coordinated correctly and consistently with the requirements of PRC-019-2. Lastly, there have been no Protection System operations or generator disconnections as a result of volts per hertz. No harm is known to have occurred. ReliabilityFirst considered KMC’s PRC-019-2 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, KMC: 1) worked with its contractor (Kestrel) to determine the correct setting of the volts per hertz limiter; 2) changed the settings of the volts per hertz limiter; 3) documented the limiter setting changes and engaged the contractor to update the report; and 4) updated its administrative practices to insure that all devices and equipment applicable to a Reliability Standard are listed in the plant's work management system, along with the next required testing date for the Reliability Standard. This work management ticket will ensure that the work order is generated in advance, with sufficient specificity to allow the plant and its owner to have the appropriate budget and subject matter expert resources in place for the study and to have a clear direction for the equipment and device settings that need to be reviewed as part of the study work scope. ReliabilityFirst has verified the completion of all mitigation activity.
2018-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Old Dominion Electric Cooperative (ODEC) | NCR00859 | RFC2017017901 | MOD-032-1 | R2 | On June 29, 2017, ODEC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-032-1 R2. In May and June 2016, the entity attempted to follow the data submittal process outlined by PJM. The entity loaded the information into the appropriate database, which indicated a status of “complete.” Based on that status indication, the entity believed it had satisfied the requirement. In May 2017, the entity began the process of submitting data for 2017. When the entity encountered problems, it corresponded with PJM. Through this correspondence, the entity learned that it never completed the submission process for the 2016 data. The entity was required to have taken one more step to complete the submission process and the status should have indicated “submitted.” At no time did the entity receive any notice from PJM that its 2016 data was not properly submitted. The root cause of this noncompliance was the fact that 2016 was the first year that the entity was required to submit this information to PJM. Previously, the entity would submit this data to the Regions. This was the entity’s first attempt at using the new submission portal and that resulted in the entity being unfamiliar with the proper status of completion. This major contributing factor involves the management practice of external interdependencies, in that the submission process required the entity to interface with another’s entity’s databases. This noncompliance started on August 1, 2016, the date by which the entity was required to have submitted the data to PJM and ended on June 8, 2017, when the entity completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the fact that although the entity failed to complete the submission process for its 2016 data, there was no change to that information, which had already been in PJM’s possession from previous years. Therefore, PJM is, and has been, using the correct data for the entity units. No harm is known to have occurred. ReliabilityFirst considered the entity’s MOD-032 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, the entity: 1) completed the process of submitting the data to PJM until the status indicated “complete” and 2) included a completed instruction package in its MOD-032-1 files which provided a step-by-step process until the PJM portal indicated that the data is “complete.” ReliabilityFirst has verified the completion of all mitigation activity.
2018-01-31 | Southwest Power Pool Regional Entity (SPP RE) | Independence Power & Light (Independence) | NCR01072 | SPP2017017425 | TOP-001-3 | R9 | On April 19, 2017, Independence submitted a Self-Report stating that, as a Transmission Operator, it was in noncompliance with TOP-001-3 R9 for failing to notify its Reliability Coordinator (RC), Southwest Power Pool (SPP) of an unplanned outage of its supervisory control and data acquisition/energy management system (SCADA/EMS), i.e., loss of monitoring capability, which lasted longer than 30 minutes. On April 13, 2017, at 1:18 a.m., Independence’s SCADA/EMS operating console stopped updating, which the on-shift System Operator noticed and recorded in Independence’s electronic operator logging system. At 1:21 a.m., the System Operator contacted Independence SCADA/EMS technicians for assistance, and at 2:15 a.m., the operating console was restored to full capability by switching over to an alternate server. During this time, Independence did not notify SPP of the unplanned outage. This noncompliance started on April 13, 2017, at 1:48 a.m., the date and time Independence was required to have notified SPP of the loss of monitoring capability, and ended on April 13, at 2:15 a.m., the date and time the operator console was restored to full capability. The root cause of this noncompliance was human error. Although the System Operator was trained and knew about the requirement to notify SPP of the unplanned outage, the System Operator continued to believe that the operator system would be promptly restored. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Independence’s failure to notify its RC of the loss of monitoring capability for a period exceeding 30 minutes presented a risk of loss of situational awareness by the RC, thereby increasing the opportunity for the RC to take inappropriate or untimely actions in response to system events. Notwithstanding, Independence’s SCADA/EMS server remained operational throughout the incident, and the System Operator had uninterrupted access to the SPP Real Time Contingency Analysis results; therefore, Independence had situational awareness. Additionally, SPP, as the RC, was monitoring Independence’s transmission system and would have alerted Independence of any issues that could have adversely impacted the reliability of the BPS. Moreover, Independence has a limited inventory of bulk electric system assets, all of which are at 161 kV. No harm is known to have occurred. Independence has no relevant prior violations of TOP-001-3 R9 or any other standards that are similar in nature. | To mitigate this noncompliance, Independence: 1) reinforced with the on-shift System Operator the requirement to notify SPP and known impacted interconnected entities of unplanned outages of 30 minutes or more; 2) reminded all affected System Operators via email of the requirement to notify SPP and known impacted interconnected entities of unplanned outages of 30 minutes or more; and 3) added the System Operations Supervisor to the distribution of SCADA/EMS log entries. SPP RE has verified the completion of all mitigation activity.
2018-01-31 | Southwest Power Pool Regional Entity (SPP RE) | Sunflower Electric Power Corporation (SECI) | NCR01148 | SPP2017017771 | MOD-026-1 | R6 | On June 20, 2017, SECI submitted a Self-Report stating that, as a Transmission Planner (TP), it had an issue of noncompliance with MOD-026-1 R6 because it failed to provide a written response to a Generator Owner (GO) within 90 calendar days of receiving verified generator excitation control system model (control system model) information that the model is usable or not usable. SECI received verified excitation system model data on April 1, 2015. SECI should have provided a written response to the GO as to whether or not the model was usable within 90 days of receiving the data. However, SECI did not provide a written response until June 19, 2017. The duration of this instance of noncompliance was from June 30, 2015, the date SECI should have provided the GO with a written response stating if the model was usable or unusable, through June 19, 2017, the date SECI provided a written response to the GO stating the models were usable. The root cause of this noncompliance was human error. SECI’s Transmission Planning and Distribution Engineer (TP function) failed to follow SECI’s Verification of Models and Data for Generator Controls Functions Operating Procedure and provide written notification to SECI’s Generation Engineer (GO function) that the models were usable. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to notify the GO that the model submitted was either usable or not usable creates the potential that the results of dynamic simulations of generator performance would not accurately represent the response of the generator excitation control system or plant volt/var control function to system events. This could result in an inaccurate assessment of dynamic reliability issues and the development of inaccurate corrective action plans to address such issues. Notwithstanding, the actual risk was minimal. SECI confirmed that the correct excitation model data was used for dynamic simulation and provided the usable model data to its Planning Coordinator for the 2015 and 2016 TP Stability assessments. Additionally, SECI is both the TP and the GO, therefore, SECI was not providing an assessment to an external entity, creating a de minimus potential for an incident to occur. No harm is known to have occurred. SECI has no relevant prior violations of MOD-026-1 R6 or any other standards that are similar in nature. | To mitigate this noncompliance, SECI: 1) confirmed that the model for the excitation system was usable and provided the data to the Generation Engineer; 2) added a procedure element in its Verification of Models and Data for Generator Controls Functions Operating Procedure for Generation Engineers to check back with the Planning Engineers 45-60 days after providing excitation model data to ensure the data has been properly examined; and 3) required its Generation and Planning Engineers to read and sign the updated operating procedure to ensure agreement and understanding of the new process. SPP RE has verified the completion of all mitigation activity.
2018-01-31 | Texas Reliability Entity (Texas RE) | GEN TEX Power Corp (Gen Tex) | NCR04074 | TRE2017017848 | BAL-001-TRE-1 | R6; R6.2 | During a Compliance Audit conducted from June 6, 2017 through July 5, 2017, Texas RE determined that Gen Tex, as a Generator Owner (GO), was in noncompliance with BAL-001-TRE-1 R6. In particular, Texas RE discovered that Gen Tex failed to set its Governor parameters as required by BAL-001-TRE-1 R6.2. Pursuant to the Governor parameters set forth in BAL-001-TRE-1 R6.2, a combustion turbine (combined cycle) should be set with a maximum droop setting of 4%. In this instance, Gen Tex set its Governor settings for two combustion turbines to 5% droop instead of the correct droop setting of 4%. Gen Tex corrected the settings on June 7, 2017. The root cause of this noncompliance was related to Gen Tex’s inadequate review of its settings. Gen Tex originally set its Governor droop settings at 4% in 2010. Gen Tex subsequently updated its Governor deadband and droop settings prior to the effective date of the BAL-001-TRE Standard to align with then-applicable regional requirements. However, Gen Tex failed to identify the droop setting change and also did not review its droop settings prior to the effective date of BAL-001-TRE. This noncompliance started on April 1, 2015, when Gen Tex was required to have 50% of its generation units compliant with BAL-001-TRE-1 R6.2, and ended on June 7, 2017, when Gen Tex corrected the settings on its combustion turbines to comply with BAL-001-TRE-1 R6.2. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Incorrect droop settings could prevent a Facility from properly responding to frequency measurable events (FMEs). However, throughout the issue duration, the evidence indicates that Gen Tex’s Facilities provided appropriate levels of initial and sustained Primary Frequency Response (PFR). Throughout the issue duration, Gen Tex maintained initial and sustained PFR scores well-above the 0.75 threshold set forth in the BAL-001-TRE-1 Standard. In addition, Gen Tex exceeded the required 0.75 PFR thresholds for all individually evaluated FMEs during the issue duration. No harm is known to have occurred. Texas RE considered Gen Tex’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Gen Tex: 1) corrected the settings on its combustion turbines to comply with BAL-001-TRE-1 R6.2; 2) added a specific requirement in its maintenance procedure to check Governor droop and deadband settings during turbine testing and verification; and 3) updated all Job Plans, Preventative Maintenance, and Work Orders associated with Governor testing and verification to include a requirement to check the Governor droop and deadband settings. Texas RE has verified the completion of all mitigation activity.
2018-01-31 | Western Electricity Coordinating Council (WECC) | 62SK 8ME LLC (SBKI) | NCR11634 | WECC2017017182 | PRC-024-2 | R1 | On March 1, 2017, SBKI submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. Specifically, on February 28, 2017, during an internal compliance review, SBKI discovered that it failed to set its frequency protective relaying in accordance with Attachment 1 by the effective date of PRC-024-2. The root cause of this issue was SBKI management's failure ensure its NERC compliance responsibility was coordinated between its Project NERC Compliance team, Engineering Procurement and Construction (EPC) contractor, and inverter manufacturer during commissioning, to ensure it was in NERC compliance by the enforceable date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for SBKI’s applicable generating unit, and ended June 28, 2017, when SBKI adjusted its frequency protective relaying in accordance with Attachment 1, for a total of 362 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SBKI failed to set its frequency protective relaying such that it would not trip its applicable generating unit unnecessarily. Such failure could result in the premature trip of SBKI’s generating unit, causing it to go offline due to frequency excursions within the “no trip zone.” However, the likelihood of the risk occurring was reduced because the Facility in scope is a 108 MW solar facility that is not typically utilized as a firm resource. The Planning Coordinator, Transmission Owner, and Transmission Operator plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that SBKI experienced a loss of its solar installation, system reliability would not be compromised. The two SMA Inverters in scope would have operated up to 60.5 Hz up to .16 seconds before tripping within the "No Trip Zone." Additionally, the same inverters would have operated down to 58.5 Hz for .3 seconds before tripping within the "No Trip Zone." Adjustments were mad to fully comply with the Standard No harm is known to have occurred. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the BPS. WECC determined SBKI had no previous relevant compliance history related to this PRC-024-2 R1 issue of noncompliance. | To mitigate this issue, SBKI: 1) set its protective relaying in accordance with PRC-024-2 for its applicable Facility; and 2) altered its EPC contracts to ensure NERC compliance has been met at the commissioning stage. The EPC contract alterations include, but are not limited to, adding milestones to the EPC schedule, NERC consultant signature requirements on inverter commissioning efforts, and re-verifying settings after the site goes into commercial operations
2018-01-31 | Western Electricity Coordinating Council (WECC) | 62SK 8ME LLC (SBKI) | NCR11634 | WECC2017017183 | PRC-024-2 | R2 | On March 1, 2017, SBKI submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R2. Specifically, on February 28, 2017, during an internal compliance review, SBKI discovered that it failed to set its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The root cause of this issue was SBKI management's failure ensure its NERC compliance responsibility was coordinated between its Project NERC Compliance team, Engineering Procurement and Construction (EPC) contractor, and inverter manufacturer during commissioning, to ensure it was in NERC compliance by the enforceable date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for SBKI’s applicable generating unit, and ended June 28, 2017, when SBKI adjusted its voltage protective relaying in accordance with Attachment 2, for a total of 362 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SBKI failed to set its voltage protective relaying such that it would not trip its applicable generating unit unnecessarily. Such failure could result in the premature trip of SBKI’s generating unit, causing it to go offline due to frequency excursions within the “no trip zone.” However, the likelihood of the risk occurring was reduced because the Facility in scope is a 108 MW solar facility that is not typically utilized as a firm resource. The over-voltage inverter settings had been set correctly to trip outside the no trip zone. If the units had experienced a voltage excursion, its current settings for the under-voltage inverter for each unit would have caused them to operate up to 0.5 pu voltage for .16 seconds before tripping inside the no trip zone. Settings were changed to only enable it to trip outside the no trip zone. The Planning Coordinator, Transmission Owner, and Transmission Operator plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that SBKI experienced a loss of its solar installation, system reliability would not be compromised. No harm is known to have occurred. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the BPS. WECC determined SBKI had no previous relevant compliance history related to this PRC-024-2 R2 issue of noncompliance. | To mitigate this issue, SBKI: 1) set its protective relaying in accordance with PRC-024-2 for its applicable Facility; and 2) altered its EPC contracts to ensure NERC compliance has been met at the commissioning stage. The EPC contract alterations include, but are not limited to, adding milestones to the EPC schedule, NERC consultant signature requirements on inverter commissioning efforts, and re-verifying settings after the site goes into commercial operations
2018-01-31 | Western Electricity Coordinating Council (WECC) | 63SU 8ME LLC (SBKII) | NCR11643 | WECC2017017184 | PRC-024-2 | R1 | On March 1, 2017, SBKII submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. Specifically, on February 28, 2017, during an internal compliance review, SBKII discovered that it failed to set its frequency protective relaying in accordance with Attachment 1 by the effective date of PRC-024-2. The root cause of this issue was SBKII management's failure ensure its NERC compliance responsibility was coordinated between its Project NERC Compliance team, Engineering Procurement and Construction (EPC) contractor, and inverter manufacturer during commissioning, to ensure it was in NERC compliance by the enforceable date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for SBKII’s applicable generating unit, and ended June 28, 2017, when SBKI adjusted its frequency protective relaying in accordance with Attachment 1, for a total of 362 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SBKII failed to set its frequency protective relaying such that it would not trip its applicable generating unit unnecessarily. Such failure could result in the premature trip of SBKII’s generating unit, causing it to go offline due to frequency excursions within the “no trip zone.” The two SMA Inverters in scope would have operated up to 60.5 Hz up to .16 seconds before tripping within the "No Trip Zone." Additionally, the same inverters would have operated down to 58.5 Hz for .3 seconds before tripping within the "No Trip Zone." Adjustments were mad to fully comply with the Standard. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 155 MW solar facility that is not typically utilized as a firm resource. The Planning Coordinator, Transmission Owner, and Transmission Operator plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that SBKII experienced a loss of its solar installation, system reliability would not be compromised. No harm is known to have occurred. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the BPS. WECC determined SBKII had no previous relevant compliance history related to this PRC-024-2 R1 issue of noncompliance. | To mitigate this issue, SBKII: 1) set its protective relaying in accordance with PRC-024-2 for its applicable Facility; and 2) altered its EPC contracts to ensure NERC compliance has been met at the commissioning stage. The EPC contract alterations include, but are not limited to, adding milestones to the EPC schedule, NERC consultant signature requirements on inverter commissioning efforts, and re-verifying settings after the site goes into commercial operations
2018-01-31 | Western Electricity Coordinating Council (WECC) | 63SU 8ME LLC (SBKII) | NCR11643 | WECC2017017185 | PRC-024-2 | R2 | On March 1, 2017, SBKII submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R2. Specifically, on February 28, 2017, during an internal compliance review, SBKII discovered that it failed to set its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The root cause of this issue was SBKII management's failure ensure its NERC compliance responsibility was coordinated between its Project NERC Compliance team, Engineering Procurement and Construction (EPC) contractor, and inverter manufacturer during commissioning, to ensure it was in NERC compliance by the enforceable date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for SBKII’s applicable generating unit, and ended June 28, 2017, when SBKII adjusted its voltage protective relaying in accordance with Attachment 2, for a total of 362 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SBKII failed to set its voltage protective relaying such that it would not trip its applicable generating unit unnecessarily. Such failure could result in the premature trip of SBKII’s generating unit, causing it to go offline due to voltage excursions within the “no trip zone.” However, the likelihood of the risk occurring was reduced because the Facility in scope is a 155 MW solar facility that is not typically utilized as a firm resource. The over-voltage inverter settings had been set correctly to trip outside the no trip zone. If the units had experienced a voltage excursion, its current settings for the under-voltage inverter for each unit would have caused them to operate up to 0.5 pu voltage for .16 seconds before tripping inside the no trip zone and .85 pu Voltage for 2 Seconds. Settings were changed to only enable it to trip outside the no trip zone. The Planning Coordinator, Transmission Owner, and Transmission Operator plan and operate the grid with the expectation that solar generation may be unavailable at any given time, so in the unlikely event that SBKII experienced a loss of its solar installation, system reliability would not be compromised. No harm is known to have occurred. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the BPS. WECC determined SBKII had no previous relevant compliance history related to this PRC-024-2 R2 issue of noncompliance. | To mitigate this issue, SBKII: 1) set its protective relaying in accordance with PRC-024-2 for its applicable Facility; and 2) altered its EPC contracts to ensure NERC compliance has been met at the commissioning stage. The EPC contract alterations include, but are not limited to, adding milestones to the EPC schedule, NERC consultant signature requirements on inverter commissioning efforts, and re-verifying settings after the site goes into commercial operations
2018-01-31 | Western Electricity Coordinating Council (WECC) | Cedar Point Wind, LLC (CPWL) | NCR11271 | WECC2017017093 | MOD-025-2 | R1 | On February 26, 2017, CPWL submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1 . Specifically, CPWL reported that it failed to verify Real Power capabilities of its one applicable Facility in accordance with Attachment 1 by the enforceable date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for MOD-025-2. Specifically, CPWL believed that because it only had one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for CPWL’s applicable Facility, and ended on June 7, 2017, when CPWL completed verification activities, for a total of 341 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, CPWL failed to verify Real Power capability of its one applicable Facility in accordance with Attachment 1 by the enforceable date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess BPS reliability. However, the likelihood of the risk occurring was reduced because the applicable Facility is a 252 MW wind-powered generation site that is not typically utilized as a firm resource, therefore, CPWL’s Balancing Authority, Transmission Planner, and Transmission Operator plan and operate the grid with the expectation that wind generation may be unavailable at any given time. This issue would not likely have significantly affected current planning models as CPWL tested its unit in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2 and is not a black start unit. Additionally, the output averages 128.9 MW during the non-compliance period. There was a low probability that this issue would cause a minimal impact to the reliability of the BPS. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined CPWL had no previous relevant compliance history related to this MOD-025-2 R1 issue of noncompliance. | To remediate and mitigate this issue, CPWL: a. verified Real Power capabilities; b. submitted its Real Power verifications to its Transmission Planner; c. modified its compliance procedure to include MOD-025 testing requirements; and d. implemented calendar reminders to track the required review and ensure proper capability verification is planned and performed at least every five calendar years. WECC verified completion of the Mitigation Plan.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Cedar Point Wind, LLC (CPWL) | NCR11271 | WECC2017017094 | MOD-025-2 | R2 | On February 26, 2017, CPWL submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, CPWL reported that it failed to verify Reactive Power capabilities of its one applicable Facility in accordance with Attachment 1 by the enforceable date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for MOD-025-2. Specifically, CPWL believed that because it only had one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined that this issue began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for CPWL’s applicable Facility, and ended on June 7, 2017, when CPWL completed verification activities, for a total of 341 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CPWL failed to verify Reactive Power capability of its one applicable Facility in accordance with Attachment 1 by the enforceable date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess bulk power system (BPS) reliability. This issue would not likely have significantly affected current planning models as CPWL tested its unit in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2 and is not a black start unit. Additionally, the reactive power averaged 128.9 MW during the non-compliance period. However, the likelihood of the risk occurring was reduced because the applicable Facility is a 252 MW wind-powered generation site that is not typically utilized as a firm resource, therefore, CPWL’s Balancing Authority, Transmission Planner, and Transmission Operator plan and operate the grid with the expectation that wind generation may be unavailable at any given time. This issue would not likely have significantly affected current planning models as CPWL tested its unit in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2 and is not a black start unit. Additionally, the output averages 128.9 MW during the non-compliance period. There was a low probability that this issue would cause a minimal impact to the reliability of the BPS. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined CPWL had no previous relevant compliance history related to this MOD-025-2 R2 issue of noncompliance. | To remediate and mitigate this issue, CPWL: a. verified Reactive Power capabilities; b. submitted its Reactive Power verifications to its Transmission Planner; c. modified its compliance procedure to include MOD-025 testing requirements; and d. implemented calendar reminders to track the required review and ensure proper capability verification is planned and performed at least every five calendar years. WECC verified completion of the Mitigation Plan.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Cedar Point Wind, LLC (CPWL) | NCR11271 | WECC2017017095 | PRC-019-2 | R1 | On February 26, 2017, CPWL submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, CPWL reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its applicable Facility by the enforceable date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for PRC-019-2 R1. Specifically, CPWL believed that because it only had one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined this issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for CPWL’s applicable Facility, and ended on June 15, 2017, when CPWL completed verification activities, for a total of 349 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CPWL failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its applicable Facility by the enforceable date of the Standard. Such failure could potentially result in the loss of the generator field, instability, and/or damage to the turbines. However, the coordination study verified that no modifications were necessary. Additionally, the applicable Facility is a 252 MW wind-powered generation site that is not typically utilized as a firm resource, therefore, CPWL’s Balancing Authority, Transmission Planner, and Transmission Operator plan and operate the grid with the expectation that wind generation may be unavailable at any given time. There was a low probability that this issue would cause a minimal impact to the reliability of the BPS. No harm was known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined CPWL had no previous relevant compliance history related to this PRC-019-2 R1 issue of noncompliance. | To remediate and mitigate this issue, CPWL: a. coordinated the voltage regulating system with its generator capabilities and Protection System devices for its applicable Facility; and b. scheduled future coordination of voltage regulating system controls for every five years. WECC verified completion of CPWL’s remediation and mitigating activities.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Cedar Point Wind, LLC (CPWL) | NCR11271 | WECC2017017096 | PRC-024-2 | R1 | On February 26, 2017, CPWL submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1 . Specifically, CMCH reported that it failed to set its frequency protective relaying in accordance with Attachment 1 by the enforceable date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for PRC-024-2. Specifically, CPWL believed that because it only had one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for CPWL’s applicable Facility, and ended June 8, 2017, when CPWL adjusted its frequency protective relaying in accordance with Attachment 1, for a total of 342 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, CPWL failed to set its frequency protective relaying in accordance with Attachment 1 by the enforceable date of the Standard. Such failures could result in the premature trip of one or more generating units offline due to frequency excursions within the “no trip zone.” However, the likelihood of the risk occurring was reduced because the applicable Facility is a 252 MW wind-powered generation site that is not typically utilized as a firm resource, therefore, CPWL’s Balancing Authority, Transmission Planner, and Transmission Operator plan and operate the grid with the expectation that wind generation may be unavailable at any given time. The two of the three over-frequency relays had been set correctly to trip outside the no trip zone and one of the under-frequency relays were set to operate in compliance with the Standard. So if the units had experienced a frequency excursion, its current settings for one over-frequency and two under-frequency relays would have caused them to trip inside the no trip zone. The three frequency relays would have operated up to 59.4 Hz for 1800 seconds, 57.8 for 2 seconds and 60.6 for 600 seconds. There was a low probability that this issue would cause a minimal impact to the reliability of the BPS. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined CPWL had no previous relevant compliance history related to this PRC-024-2 R1 issue of noncompliance | To remediate and mitigate these issues, CPWL: a. completed the required frequency protection system settings changes for its applicable Facility in accordance with PRC-024-2; and b. modified its compliance procedure to include MOD-025-2 testing requirements. WECC verified completion of the Mitigation Plan.
2018-01-31 | Western Electricity Coordinating Council (WECC) | Cedar Point Wind, LLC (CPWL) | NCR11271 | WECC2017017097 | PRC-024-2 | R2 | On February 26, 2017, CPWL submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R2 . Specifically, CMCH reported that it failed to set its voltage protective relaying in accordance with Attachment 2 by the enforceable date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for PRC-024-2. Specifically, CPWL believed that because it only had one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for CPWL’s applicable Facility, and ended June 8, 2017, when CPWL adjusted its voltage protective relaying in accordance with Attachment 2, for a total of 342 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, the entity failed to set its voltage protective relaying for single applicable Facility such that the generator voltage protective relaying does not trip the applicable generating unit within the "no trip zone." This could potentially result in the premature tripping of one or more generating units offline due to voltage excursions within the "no trip zone." The entity had one 252 MW wind Facility that is subject to this instance. If the Facility had experienced a voltage excursion, its settings would have still tripped just a little delayed. The Undervoltage relay was set at 49.8 V, 15 cycles instead of 40.0 V, 30 cycles, and 49.0 V, 30 cycles instead of 40.0 V, 30 cycles. As compensation, the entity was commissioned four years ago and has not made any changes to the protection device settings since its initial commercial operation testing. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined CPWL had no previous relevant compliance history related to this PRC-024-2 R2 issue of noncompliance. | To remediate and mitigate these issues, CPWL: a. completed the required voltage protection system settings changes for its applicable Facility in accordance with PRC-024-2; and b. modified its compliance procedure to include MOD-025-2 testing requirements. WECC verified completion of the Mitigation Plan.
2017-12-28 | Florida Reliability Coordinating Council, Inc. (FRCC) | Tampa Electric Company (TEC) | NCR00074 | FRCC2017018360 | PRC-006-2 | R9. | On September 20, 2017, TEC submitted a Self-Report stating that, as a Transmission Owner and Distribution Provider, it was in noncompliance with PRC-006-2 R9. The noncompliance started on May 30, 2017, when the incorrect time delay settings for under-frequency load shedding (UFLS) relays were set and ended on June 20, 2017, when TEC corrected the settings. The engineer who performed the UFLS update failed to follow the UFLS procedure. The engineer instead utilized instructions received in an e-mail regarding the use of temporary settings. The settings in the email were for the purpose of verifying under-frequency (UF) functionality on relays for which were not in the UFLS program. Being new to the job, he misinterpreted the email and thought the settings should also be applied to relays in the UFLS program. Therefore, he used this incorrect value for the relays that were added to the 2017 UFLS program. The UF relays for ten new distribution circuits in the UFLS program were programmed to trip after 12 cycles rather than 8 cycles. These time delay errors added 4 cycles or 0.0667 seconds to the total UF trip time for these ten circuits. As a result, the total trip time for these circuits was 0.300 seconds, which was 0.020 seconds above the maximum 0.280 second total time delay that is allowed by the design of FRCC’s UFLS program. The root cause for this noncompliance was an unclear procedure resulting in a misinterpretation by a new engineer. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was a delay in load shed if an under-frequency event occurred. This risk was reduced because the correct amount of load would have been shed and the impact of the delay of 0.020 seconds would have been negligible because of system inertia. The ten relays in question are 3.1% of the 322 relays in the UFLS program. TEC estimates the ten circuits contribute 61.9 MW or 3.7% of the 1662.8 MW in the program. The additional time delay would not have affected subsequent steps or other entities in the FRCC Region. The addition of the ten circuits still improved the capability of TEC’s UFLS program, even during the 21 days the time delays were slightly out of specification. There were no UFLS events during the period and thus no harm is known to have occurred. FRCC considered TEC’s compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, TEC: 1) determined extent of condition; 2) corrected the time delay settings; 3) added a section to UFLS procedure document that emphasizes the importance of the timer settings and the overall time delay; and 4) obtained written confirmation that the users of the procedure have read and understand the new section of the UFLS procedure document.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | National Grid USA | NCR11171 | NPCC2017016878 | FAC-008-3 | R8.1 | On January 30, 2017, National Grid USA (the Entity) submitted a self-log stating that, as a Transmission Owner (TO), it was in noncompliance with FAC-008-3, R8.1. Specifically, the Entity failed to provide requested information of a planned upgrade to its PC/RC (NYISO) at least seven (7) Business Days prior to the expected in-service date, as specified in the NYSIO's "Reliability Analysis Data Manual". The planned upgrade consisted in increased thermal ratings for a 115kV feeder, that resulted from bus work. This noncompliance started on November 12, 2016, one day after the required date for submittal of the information to the PC/RC, and ended on December 2, 2016, when the Entity submitted the information. The root cause of this instance of noncompliance was human error in the inadvertent omission by the Entity's responsible staff to inform both its own system operators and the NYISO of updated feeder ratings. There was a protocol in place, but the department responsible failed on this instance to follow that protocol. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As neither the NYISO nor the Entity's own system operators were timely informed of the increased facility ratings for Transmission Line #15, the transmission system continued to be operated to the lower existing ratings during the brief period of noncompliance, which occurred during the winter operating period. However, this is largely an administrative issue. The Entity is a Summer-peaking utility, and, as such, its customer loads during the period of noncompliance are greatly reduced, thus offsetting the impact of the failure to utilize higher ratings for a single transmission feeder. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, National Grid USA: 1. corrected the noncompliance by effecting the required information submittal to the NYISO; and 2. to prevent a recurrence of similar instances of noncompliance, it created process documents to formalize the existing monthly review processes that the New York and the New England Transmission Planning departments follow with respect to Facility and Equipment Ratings. Each process document is aligned with the structure, job titles, responsibilities and review activities within the two RCs' footprint. Training was also provided to responsible staff. NPCC has verified the completion of all mitigation activity.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2017018460 | PRC-019-2 | R1. | On October 12, 2017, Plainfield Renewable Energy, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions by 7/1/2016, as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on October 23, 2017, when the Entity completed its coordination verification and implemented changes to the settings of two limiters to avoid having the protective relaying system trip the generator unnecessarily. The root cause of this instance of noncompliance was the Entity's initial lack of clear understanding of how the phased-in implementation plan for the Standard and Requirement would apply to their single generating unit. Subsequently, based on information issued by NERC, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by 7/1/2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Entity's generation facility was operated at a capacity factor of 72% for the year 2016, and 62% for the year 2017 to date. The Gross Rated Capability of the Entity's wood-burning generating unit is 53.8 MVA, which is approximately 2.0% of the Entity's RC's (ISO-NE) required winter operating reserves of 2600 MW (a value which is often exceeded by a margin of about 2000 MW above this requirement). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the ISO-NE would have been able to replace the lost capacity. There were setting changes made to two limiters, but there were no changes to protective relaying systems. Due to the above considerations, this instance of noncompliance represents a minimal risk to the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by completing its coordination verification and implementing changes to the settings of two limiters; and 2) to prevent a recurrence of similar instances of noncompliance, the Entity instituted an internal control consisting of two calendar reminders to responsible personnel, one every four years, and the other every four years plus nine months, after the initial verification report was completed. NPCC has verified the completion of all mitigation activity.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2017017407 | PRC-006-NPCC-1 | R13. | On April 10, 2017, Noble Altona Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-006-NPCC-1 R13. Specifically, the Entity discovered that the under-frequency relay setting for its generating facilities' single relay was not in compliance with PRC-006-NPCC-1, R13 (Figure 1). This noncompliance started on July 1, 2015, when the standard and requirement became enforceable, and ended on April 3, 2017, when the Entity implemented the required under-frequency relay setting for its generating assets to ensure its compliance with the standard/requirement. The root cause of this instance of noncompliance was the Entity's reliance on an outside consultant for its NERC Compliance review who failed to advise it that standard PRC-006-NPCC-1 ought to have been included in its program. In January 2017, Noble engaged a new consultant to perform a review of its NERC compliance program and was subsequently advised, on March 16, 2017, that the under-frequency relay setting for its circuit breaker M1 generator relay was not in compliance with the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 19.9%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 97 MW, which is less than 5.0% of the NYISO's required Operating Reserve (approximately 1,965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system frequency event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal risk to the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) implemented the required under-frequency relay setting for its generating facilities' single relay; and 2) contracted with its new consultant to perform an annual review of the Noble NERC Compliance program and all the existing Noble procedures. NPCC has verified the completion of all mitigation activities.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC | NCR10367 | NPCC2017017404 | PRC-006-NPCC-1 | R13. | On April 10, 2017, Noble Chateaugay Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-006-NPCC-1 R13. Specifically, the Entity discovered that the under-frequency relay setting for its generating facilities' single relay was not in compliance with PRC-006-NPCC-1, R13 (Figure 1). This noncompliance started on July 1, 2015, when the standard and requirement became enforceable, and ended on April 3, 2017, when the Entity implemented the required under-frequency relay setting for its generating assets to ensure its compliance with the standard/requirement. The root cause of this instance of noncompliance was the Entity's reliance on an outside consultant for its NERC Compliance review who failed to advise it that standard PRC-006-NPCC-1 ought to have been included in its program. In January 2017, Noble engaged a new consultant to perform a review of its NERC compliance program and was subsequently advised, on March 16, 2017, that the under-frequency relay setting for its circuit breaker M1 generator relay was not in compliance with the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 22.4%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 106 MW, which is less than 5.4% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system frequency event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal risk to the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) implemented the required under-frequency relay setting for its generating facilities' single relay; and 2) contracted with its new consultant to perform an annual review of the Noble NERC Compliance program and all the existing Noble procedures. NPCC has verified the completion of all mitigation activities.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2017017405 | PRC-006-NPCC-1 | R13. | On April 10, 2017, Noble Wethersfield Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-006-NPCC-1 R13. Specifically, the Entity discovered that the under-frequency setting for its generating facilities' relay was not in compliance with PRC-006-NPCC-1, R13 (Figure 1). This noncompliance started on July 1, 2015, when the standard and requirement became enforceable, and ended on April 5, 2017, when the Entity implemented the required under-frequency relay setting for its generating assets to ensure its compliance with the standard/requirement. The root cause of this instance of noncompliance was the Entity's reliance on an outside consultant for its NERC Compliance review who failed to advise it that standard PRC-006-NPCC-1 ought to have been included in its program. In January 2017, Noble engaged a new consultant to perform a review of its NERC compliance program and was subsequently advised, on March 16, 2017, that the under-frequency relay setting for its circuit breaker M1 generator relay was not in compliance with the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 24%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 126 MW, which is less than 6.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system frequency event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal risk to the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) implemented the required under-frequency relay setting for its generating facilities' relay; and 2) contracted with its new consultant to perform an annual review of the Noble NERC Compliance program and all the existing Noble procedures. NPCC has verified the completion of all mitigation activities.
2017-12-28 | Northeast Power Coordinating Council, Inc. (NPCC) | Plattsburgh Municipal Lighting Department | NCR11045 | NPCC2017017360 | PRC-006-NPCC-1 | R12. | On April 5, 2017, Plattsburgh Municipal Lighting Department (the Entity) submitted a Self-Report stating that, as a Distribution Provider (DP), it was in noncompliance with PRC-006-NPCC-1 R12. Specifically, although the Entity did provide to its Planning Coordinator documentation of actual net Load that would have been shed in 2016 by its UFLS relays at each UFLS stage, the coincidence of such net Loads with integrated hourly peak was estimated by its personnel due to the existing meters lacking time-stamping capability. This noncompliance started on July 1, 2015, the enforcement date of the standard & requirement, and ended on December 1, 2017, when the Entity completed installation, at its five affected substations, of multi-function meters capable of storing feeder load data that is fully compliant with all aspects of the standard and requirement. The root cause of this instance of noncompliance was the Entity's reliance on meters that record maximum load demand but do not record and store associated time data. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's UFLS equipment is installed and operational in accordance with the standard, and, therefore, its noncompliance with R12 of the standard would not affect the real-time operation of the system during an under-frequency event. Rather, the Entity's noncompliance consisted of a failure to provide accurate historical timestamps for load shedding that would have taken place in 2016, during a potential load shedding event, in accordance with its UFLS program. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this noncompliance, the Entity: 1) completed installation of fully integrated, multi-function meters that will store Load data and associated dates and times; and 2) with the installation of updated metering, will also prevent a recurrence of similar instances of noncompliance. NPCC has verified the completion of all mitigation activities.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017017788 | MOD-025-2 | R1 | On June 20, 2017, Consumers submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. MOD-025-2 R1 required Consumers, as a Generator Owner, to provide its Transmission Planner (METC) with verification of the Real Power capabilities of Consumers’ applicable Facilities by the July 1, 2016 implementation date. MOD-025-2 R1.1 requires Consumers to verify the Real Power capability of its generating units in accordance with Attachment 1. Consumers discovered this noncompliance with MOD-025-2 on March 29, 2017, while attempting to align capacity testing schedules for MOD-025-2 to ensure compliance with the compliance milestone of 60% or 20 of the 33 generating units owned by Consumers before the July 1, 2017 deadline. During this preparation, a Consumers employee identified that Consumers only performed and submitted to its Transmission Planner verification tests for 9 of 33 of its generating units (27%) before July 1, 2016, therefore not meeting the original 40% compliance milestone. Consumers also discovered that it had submitted the verification tests information incorrectly to its Planning Authority (MISO), rather than to its Transmission Planner. Consumers completed the overdue verification tests to meet the 40% requirement as of June 11, 2017. (Consumers identified the noncompliance through a comparison of the current Standard MOD-025-2 and the retired Standards MOD-024-1 and MOD-025-1. The facilities had used testing and recording methods based on the previous Standards which did not include minimum power VAR testing. A follow up discussion identified that, although Consumers Energy is a registered Transmission Planner and does enter the test results into the Planning Authority Modeling database, the facilities owned by the Company interconnect with another Transmission Operator, METC. Consumers Energy should have provided the validation testing results to METC as its Transmission Planner.) In sum, while preparing for the compliance milestone of 60% in March of 2017, Consumers discovered that it did not achieve compliance for the compliance milestone of 40% which had a July 1, 2016 implementation date. After discovering this issue, Consumers performed all the necessary verifications. This noncompliance involves the management practices of workforce management, planning, and verification. Workforce management and planning are both involved because Consumers’ compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is Consumers’ inability to effectively plan for the July 1, 2016 effective date for MOD-025-2. Consumers did not verify that its understanding of how to comply with the phased in implementation schedule of MOD-025-2 was correct. This noncompliance started on July 1, 2016, when Consumers was required to comply with MOD-025-2 R1 and ended on June 11, 2017, when Consumers completed the overdue verification tests to meet the 40% implementation schedule required as of July 1, 2016 and communicated the results of those verification tests to its Transmission Planner. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. (The purpose of MOD-025-2 is to ensure that accurate information on generator gross and net Real and Reactive Power capability and synchronous condenser Reactive Power capability is available for planning models used to assess BPS reliability. The impact to the BPS revolves around models accurately reflecting the generator's capabilities and operating characteristics. An incorrect portrayal of a generation facility in the System model could potentially cause a system outage due to lack of resources.) The risk is minimized because although Consumers only provided the Transmission Planner documented evidence of the generator capabilities on 9 of its 14 required generation units by July 1, 2016, Consumers did enter the generation characteristic information into the modeling database used by the Transmission Planner by September 27, 2016 (less than three months late). On September 27, 2016, all of Consumers’ generator capabilities as verified by validation testing performed in 2016 had been entered into the MISO modeling system. (The following characteristics were entered: Corresponding generation limits and level for each scenario in the model list (Pmin, Pmax, Qmin, Qmax, Pgen); Generation limits/capabilities to be submitted by Generation Owner. Generator owner shall submit generator capabilities (Pmax/Qmax) that correspond to a point in the reactive capability curve, Generation output to be submitted by Transmission Owners.) This minimizes the risk because it reduces the amount of time that the Transmission Planner and the Planning Authority had incorrect data regarding Consumers’ generating capacity to less than three months. Lastly, old Consumers modeling data did exist in the planning and operations models. When checking and verifying the existing data, Consumers only had to make minimal changes. No harm is known to have occurred. ReliabilityFirst considered Consumers’ MOD-025-2 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Consumers will complete the following mitigation activities by January 31, 2018: 1) submitted to METC the required test information, including one-line diagrams and the test results populated in Attachment 2 of the Standard, for the Zeeland generating Facilities (Completing Milestone 1 ended the noncompliance); 2) populated a test tracking spreadsheet to ensure continued compliance through the implementation period. The verification tests for the remaining facilities are scheduled, performed, and tracked as documented on the spreadsheet; 3) drafted a new procedure to ensure that future verifications and tests are completed on time; 4) routed the revised procedure for review; 5) will address draft procedure comments, finalize the procedure, and route for approval; 6) will obtain procedure approval; and 7) will implement and train on the new procedure. Consumers will ensure validation is scheduled to be performed on the equipment as required. Documented procedures will provide guidance to the current and future business members associated with performing the actions of this Standard. This guidance will ensure proper testing and reporting is performed. The process of drafting a new procedure to ensure that future verifications and tests are completed on time, reviewing that procedure, approving that procedure, implementing that procedure, and training on that procedure is lengthy and explains why mitigation will not be completed until January 2018.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017017789 | MOD-025-2 | R2 | On June 20, 2017, Consumers submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. MOD-025-2 required Consumers, as a Generator Owner, to provide its Transmission Planner (METC) with verification of the Real Power capabilities of Consumers’ applicable Facilities by the July 1, 2016 implementation date. MOD-025-2 R1.2 requires Consumers to submit a completed Attachment 2 to its Transmission Planner within 90 calendar days of either (i) the date that data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. Consumers discovered this noncompliance on March 29, 2017, while attempting to align capacity testing schedules for MOD-025-2 to ensure compliance with the compliance milestone of 60% or 20 of the 33 generating units owned by Consumers before the July 1, 2017 deadline. During this preparation, a Consumers employee identified that Consumers only performed and submitted to its Transmission Planner verification tests for 9 of 33 of its generating units (27%) before July 1, 2016, therefore not meeting the 40% compliance milestone. Consumers also discovered that it had submitted the verification tests information incorrectly to its Planning Authority (MISO), rather than to its Transmission Planner. Consumers completed the overdue verification tests to meet the 40% requirement as of June 11, 2017. (Consumers identified the noncompliance through a comparison of the current Standard MOD-025-2 and the retired Standards MOD-024-1 and MOD-025-1. The facilities had used testing and recording methods based on the previous Standards which did not include minimum power VAR testing. A follow up discussion identified that, although Consumers Energy is a registered Transmission Planner and does enter the test results into the Planning Authority Modeling database, the facilities owned by the Company interconnect with another Transmission Operator, METC. Consumers Energy should have provided the validation testing results to METC as its Transmission Planner.) In sum, while preparing for the compliance milestone of 60% in March of 2017, Consumers discovered that it did not achieve compliance for the compliance milestone of 40% which had a July 1, 2016 implementation date. After discovering this issue, Consumers performed all the necessary verifications. This noncompliance involves the management practices of workforce management, planning, and verification. Workforce management and planning are both involved because Consumers’ compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is Consumers’ inability to effectively plan for the July 1, 2016 effective date for MOD-025-2. Consumers did not verify that its understanding of how to comply with the phased in implementation schedule of MOD-025-2 was correct. This noncompliance started on July 1, 2016, when Consumers was required to comply with MOD-025-2 R2 and ended on June 11, 2017, when Consumers completed the overdue verification tests to meet the 40% implementation schedule required as of July 1, 2016 and communicated the results of those verification tests to its Transmission Planner. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. (The purpose of MOD-025-2 is to ensure that accurate information on generator gross and net Real and Reactive Power capability and synchronous condenser Reactive Power capability is available for planning models used to assess BPS reliability. The impact to the BPS revolves around models accurately reflecting the generator's capabilities and operating characteristics. An incorrect portrayal of a generation facility in the System model could potentially cause a system outage due to lack of resources.) The risk is minimized because although Consumers Energy only provided the Transmission Planner documented evidence of the generator capabilities on 9 of its 14 required generation units by July 1, 2016, Consumers did enter the generation characteristic information into the modeling database used by the Transmission Planner by September 27, 2016 (less than three months late). On September 27, 2016 all of Consumers’ generator capabilities as verified by validation testing performed in 2016 had been entered into the MISO modeling system. (The following characteristics were entered: Corresponding generation limits and level for each scenario in the model list (Pmin, Pmax, Qmin, Qmax, Pgen); Generation limits/capabilities to be submitted by Generation Owner. Generator owner shall submit generator capabilities (Pmax/Qmax) that correspond to a point in the reactive capability curve, Generation output to be submitted by Transmission Owners.) This minimizes the risk because it reduces the amount of time that the Transmission Planner and the Planning Authority had incorrect data regarding Consumers’ generating capacity to less than three months. Lastly, old Consumers modeling data did exist in the planning and operations models. When checking and verifying the existing data, Consumers only had to make minimal changes. No harm is known to have occurred. ReliabilityFirst considered Consumers’ MOD-025-2 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Consumers will complete the following mitigation activities by January 31, 2018: 1) submitted to METC the required test information, including one-line diagrams and the test results populated in Attachment 2 of the Standard, for the Zeeland generating Facilities (Completing Milestone 1 ended the noncompliance); 2) populated a test tracking spreadsheet to ensure continued compliance through the implementation period. The verification tests for the remaining facilities are scheduled, performed, and tracked as documented on the spreadsheet; 3) drafted a new procedure to ensure that future verifications and tests are completed on time; 4) routed the revised procedure for review; 5) will address draft procedure comments, finalize the procedure, and route for approval; 6) will obtain procedure approval; and 7) will implement and train on the new procedure. Consumers will ensure validation is scheduled to be performed on the equipment as required. Documented procedures will provide guidance to the current and future business members associated with performing the actions of this Standard. This guidance will ensure proper testing and reporting is performed. The process of drafting a new procedure to ensure that future verifications and tests are completed on time, reviewing that procedure, approving that procedure, implementing that procedure, and training on that procedure is lengthy and explains why mitigation will not be completed until January 2018.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016016313 | MOD-025-2 | R1 | On October 4, 2016, EPOPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. EPOPP compliance staff misinterpreted MOD-025-2 which led them to believe, incorrectly, that PJM and ISO-NE had incorporated the MOD-025-2 testing requirements in its tariff procedures and that separate MOD-025 demonstration was not necessary. EPOPP compliance staff did not think they needed to perform any other MOD-025 related maintenance and testing to show compliance. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because EPOPP compliance staff misunderstood the requirements of MOD-025-2. EPOPP staff incorrectly believed they did not need to take any other actions to show compliance with MOD-025-2. EPOPP’s misunderstanding of the requirements of MOD-025-2 is a root cause of this noncompliance. This issue started on July 1, 2016, when EPOPP was required to comply with MOD-025-2 R1 and ended on December 29, 2016, when EPOPP submitted the required testing it performed to PJM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized here because each EPOPP unit satisfied its real and reactive power verification requirements put in place by PJM and ISO-NE for the past five years and each unit performed its claimed real power capability testing during the summer of 2016. The risk is further minimized because EPOPP is capable of producing only 166 MW per unit, and the operating capacity factor during the instance of noncompliance was 17.09%. Finally, no unit was requested to operate at its maximum leading or lagging reactive limit from 2014 to 2016. No harm is known to have occurred. ReliabilityFirst considered EPOPP's MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPOPP: 1) determined if the claimed capability test performed in 2016 can be utilized to satisfy the real power verification (R1.1). EPOPP confirmed that the claimed capability tests could be utilized for R1.1. EPOPP also determined that supporting data at the points specified in R1.1 were recorded during the test and could be utilized for MOD-025-2 reporting purposes; 2) scheduled and performed any real power verifications required and reactive power verifications by the end of 2016 to minimally meet the 40% threshold at each facility that was required by July 1, 2016; and 3) published a five-year MOD-025-2 performance schedule for all Essential Power facilities. This five year schedule will help prevent recurrence because EPOPP personnel will know what tasks they need to perform to maintain compliance with MOD-025. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016016348 | MOD-025-2 | R1 | On October 5, 2016, EPOPP, on behalf of Newington Energy, submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. EPOPP submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. Newington Energy compliance staff discovered that at each Essential Power facility, 40% of the applicable units had not performed reactive power verification in accordance with MOD-025-2 R1. Newington Energy compliance staff erroneously believed that PJM and ISO-NE had incorporated the MOD-025 testing requirements in their tariff procedures and that separate MOD-025 demonstration was not necessary. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because Newington Energy compliance staff misunderstood the requirements of MOD-025-2. Newington Energy staff incorrectly believed they did not need to take any other actions to show compliance with MOD-025-2. Newington Energy’s misunderstanding of the requirements of MOD-025-2 is a root cause of this noncompliance. This issue started on July 1, 2016, when Newington Energy was required to comply with MOD-025-2 R1 and ended on December 29, 2016, when Newington Energy completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized here because each Newington Energy unit satisfied its real and reactive power verification requirements put in place by PJM and ISO-NE for the past five years and each unit performed its claimed real power capability testing during the summer of 2016. Finally, no unit was requested to operate at its maximum leading or lagging reactive limit from 2014 to 2016. No harm is known to have occurred. ReliabilityFirst considered Newington Energy's MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Newington Energy: 1) determined if the claimed capability test performed in 2016 can be utilized to satisfy the real power verification (R1.1). Newington Energy confirmed that the claimed capability tests could be utilized for R1.1. Newington Energy also determined that supporting data at the points specified in R1.1 were recorded during the test and could be utilized for MOD-025-2 reporting purposes; 2) scheduled and performed any real power verifications required and reactive power verifications by the end of 2016 to minimally meet the 40% threshold at each facility that was required by July 1, 2016; and 3) published a five-year MOD-025-2 performance schedule for all Essential Power facilities. This five year schedule will help prevent recurrence because Newington Energy personnel will know what tasks they need to perform to maintain compliance with MOD-025. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016016349 | MOD-025-2 | R1 | On October 5, 2016, EPOPP, on behalf of West Springfield, submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. EPOPP submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. West Springfield compliance staff discovered that at each Essential Power facility, 40% of the applicable units had not performed reactive power verification in accordance with MOD-025-2 R1. West Springfield compliance staff erroneously believed that PJM and ISO-NE had incorporated the MOD-025 testing requirements in their tariff procedures and that separate MOD-025 demonstration was not necessary. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because West Springfield compliance staff misunderstood the requirements of MOD-025-2. West Springfield incorrectly believed they did not need to take any other actions to show compliance with MOD-025-2. West Springfield’s misunderstanding of the requirements of MOD-025-2 is a root cause of this noncompliance. This issue started on July 1, 2016, when West Springfield was required to comply with MOD-025-2 R1 and ended on December 29, 2016, when West Springfield completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized here because each West Springfield unit satisfied its real and reactive power verification requirements put in place by PJM and ISO-NE for the past five years and each unit performed its claimed real power capability testing during the summer of 2016. The risk is limited because the West Springfield unit was capable of providing 131.72 MW and 147.582 MW respectively and operated with a capacity factor of less than 3%. When West Springfield operated, no trips occurred due to inadequate coordination and when West Springfield performed the verification, no changes were required. Finally, no unit was requested to operate at its maximum leading or lagging reactive limit from 2014 to 2016. No harm is known to have occurred. ReliabilityFirst considered West Springfield's MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, West Springfield: 1) determined if the claimed capability test performed in 2016 can be utilized to satisfy the real power verification (R1.1). West Springfield confirmed that the claimed capability tests could be utilized for R1.1. West Springfield also determined that supporting data at the points specified in R1.1 were recorded during the test and could be utilized for MOD-025-2 reporting purposes; 2) scheduled and performed any real power verifications required and reactive power verifications by the end of 2016 to minimally meet the 40% threshold at each facility that was required by July 1, 2016; and 3) published a five-year MOD-025-2 performance schedule for all Essential Power facilities. This five year schedule will help prevent recurrence because West Springfield personnel will know what tasks they need to perform to maintain compliance with MOD-025. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016016344 | PRC-019-2 | R1 | On October 5, 2016, EPOPP, on behalf of West Springfield, submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. EPOPP submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. In mid-2015, NERC gave Essential Power approval to combine its five individual registrations into a single consolidated NERC registration. However, ReliabilityFirst informed Essential Power that it must dispose of its outstanding compliance matters before the consolidation could be finalized. Essential Power communicated with other entities and came to the conclusion that PRC-019-2 R1 was an overall compliance assessment which was to be done at the fleet level. Essential Power implemented a process including external consultants to comply with its incorrect interpretation of PRC-019 and to become compliant at the fleet, rather than at the registered entity level. On July 29, 2016, Compliance staff discussed with ReliabilityFirst staff the implementation of the PRC-019-2 standard. ReliabilityFirst stated that enforcement of the PRC standards would be assessed at the registered entity level, not at the fleet level for entities. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because Essential Power compliance staff misunderstood the requirements of PRC-019-2 R1. Essential Power and West Springfield incorrectly believed that they could show compliance at the fleet level rather than at the registered entity level. Essential Power’s misunderstanding of the requirements of PRC-019-2 R1 is a root cause of this noncompliance. This issue started on July 1, 2016, when West Springfield was required to comply with PRC-019-2 R1 and ended on April 18, 2017, when West Springfield completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage controls which can result in a generator falsely tripping. The risk is minimized because West Springfield was capable of providing only 131.72 MW and operated with a capacity factor of 2.94% during the noncompliance. When West Springfield, operated, no trips occurred due to inadequate coordination and when West Springfield performed the verification, no changes were required. Further, this is a one-time event that involves the implementation and interpretation of a new standard. Lastly, the risk is minimized by the fact that if the entity had registered all its units as one registered entity, it would have not been a noncompliance based on the implementation plan. No harm is known to have occurred. ReliabilityFirst considered West Springfield's PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, West Springfield: 1) researched and selected a vendor to perform the analysis required in PRC-019-2; 2) submitted all requested information to the selected vendor to complete the analysis; 3) reviewed the compliance procedure templates for PRC-019 to ensure they sufficiently address the ongoing compliance obligations. West Springfield used the template to create plant procedures that will ensure that Essential Power completes all required testing for and beyond the upcoming five year window; 4) trained site personnel on the procedure and on the timeline required to complete the next review prior to the next five year deadline; 5) added a preventative maintenance activity for 2020 to perform the required five-year coordination review; 6) performed the PRC-019-2 evaluation at West Springfield, Rock Springs, and Newington; and 7) performed setting changes required in the PRC-019-2 coordination analysis. Essential Power completed PRC-019-2 verification on 100% of its units by the end of the first quarter 2017 at each location, which is beyond the required 40% by July 1, 2016 and 100% full compliance milestone of July 1, 2019. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016016345 | PRC-019-2 | R1 | On October 5, 2016, EPOPP, on behalf of Newington Energy, submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. EPOPP submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. In mid-2015, NERC gave Essential Power approval to combine its five individual registrations into a single consolidated NERC registration. However, ReliabilityFirst informed Essential Power that it must dispose of its outstanding compliance matters before the consolidation could be finalized. Essential Power communicated with other entities and came to the conclusion that PRC-019-2 R1 was an overall compliance assessment which was to be done at the fleet level. Essential Power implemented a process including external consultants to comply with its incorrect interpretation of PRC-019 and to become compliant at the fleet, rather than at the registered entity level. On July 29, 2016, Compliance staff discussed with ReliabilityFirst staff the implementation of the PRC-019-2 standard. ReliabilityFirst stated that enforcement of the PRC standards would be assessed at the registered entity level, not at the fleet level for entities. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because Essential Power compliance staff misunderstood the requirements of PRC-019-2 R1. Essential Power and Newington Energy incorrectly believed that they could show compliance at the fleet level rather than at the registered entity level. Essential Power’s misunderstanding of the requirements of PRC-019-2 R1 is a root cause of this noncompliance. This issue started on July 1, 2016, when Newington Energy was required to comply with PRC-019-2 R1 and ended on April 19, 2017, when Newington Energy completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage controls which can result in a generator falsely tripping. Newington Energy was capable of providing only 565 MW and operated with a capacity factor of 24.38% during the noncompliance. When Newington Energy operated, no trips occurred due to inadequate coordination and when Newington Energy performed the verification, no changes were required. Further, this is a one-time event that involves the implementation and interpretation of a new standard. Lastly, the risk is minimized by the fact that if the entity had registered all its units as one registered entity it would have not been a noncompliance based on the implementation plan. No harm is known to have occurred. ReliabilityFirst considered Newington Energy's PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Newington Energy: 1) researched and selected a vendor to perform the analysis required in PRC-019-2; 2) submitted all requested information to the selected vendor to complete the analysis; 3) reviewed the compliance procedure templates for PRC-019 to ensure they sufficiently address the ongoing compliance obligations. Newington Energy used the template to create plant procedures that will ensure that Essential Power completes all required testing for and beyond the upcoming five year window; 4) trained site personnel on the procedure and on the timeline required to complete the next review prior to the next five year deadline; 5) added a preventative maintenance activity for 2020 to perform the required five-year coordination review; 6) performed the PRC-019-2 evaluation at West Springfield, Rock Springs, and Newington; and 7) performed setting changes required in the PRC-019-2 coordination analysis. Essential Power completed PRC-019-2 verification on 100% of its units by the end of the first quarter 2017 at each location, which is beyond the required 40% by July 1, 2016 and 100% full compliance milestone of July 1, 2019. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016016346 | PRC-024-2 | R1 | On October 5, 2016, EPOPP, on behalf of Newington Energy, submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. EPOPP submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. In mid-2015, NERC gave Essential Power approval to combine its five individual registrations into a single consolidated NERC registration. However, ReliabilityFirst informed Essential Power that it must dispose of its outstanding compliance matters before the consolidation could be finalized. Essential Power communicated with other entities and came to the conclusion that PRC-024-2 R1 was an overall compliance assessment which was to be done at the fleet level. Essential Power implemented a process including external consultants to comply with its incorrect interpretation of PRC-024-2 and to become compliant at the fleet, rather than at the registered entity level. On July 29, 2016, Essential Power compliance staff discussed with ReliabilityFirst staff the implementation of the PRC-024-2 standard. ReliabilityFirst stated that enforcement of the PRC standards would be assessed at the registered entity level, not at the fleet level for entities. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because Essential Power compliance staff misunderstood the requirements of PRC-024-2 R1. Essential Power and Newington Energy incorrectly believed that they could show compliance at the fleet level rather than at the registered entity level. Essential Power’s misunderstanding of the requirements of PRC-019-2 R1 is a root cause of this noncompliance. This issue started on July 1, 2016, when Newington Energy was required to comply with PRC-024-2 R1 and ended on April 18, 2017, when Newington Energy completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is minimized because Newington Energy was capable of providing only 565 MW and operates with a capacity factor of 24.38%. Further, when Newington Energy operated, no trips occurred due to inadequate coordination and when Newington Energy performed the verification, no changes were required. This is related to meeting a deadline for a new standard and is not likely to continue to occur or occur again. Lastly, the risk is minimized by the fact that if the entity had registered all its units as one registered entity it would have not been a noncompliance based on the implementation plan. No harm is known to have occurred. ReliabilityFirst considered Newington Energy PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Newington Energy: 1) researched and selected a vendor to perform the analysis required in PRC-024-2; 2) submitted all requested information to the selected vendor to complete the analysis; 3) reviewed the compliance procedure templates for PRC-024 to ensure they sufficiently address the ongoing compliance obligations. Newington Energy used the template to create plant procedures that will ensure that Essential Power completes all required testing for and beyond the upcoming five year window; 4) trained site personnel on the procedure and on the timeline required to complete the next review prior to the next five year deadline; 5) added a preventative maintenance activity for 2020 to perform the required five-year coordination review; 6) performed the PRC-024-2 evaluation at West Springfield, Rock Springs, and Newington; and 7) performed setting changes required in the PRC-024-2 coordination analysis. Essential Power completed PRC-024-2 verification on 100% of its units by the end of the first quarter 2017 at each location, which is beyond the required 40% by July 1, 2016 and 100% full compliance milestone of July 1, 2019. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016016347 | PRC-024-2 | R1 | On October 5, 2016, EPOPP, on behalf of West Springfield, submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. EPOPP submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. In mid-2015, NERC gave Essential Power approval to combine its five individual registrations into a single consolidated NERC registration. However, ReliabilityFirst informed Essential Power that it must dispose of its outstanding compliance matters before the consolidation could be finalized. Essential Power communicated with other entities and came to the conclusion that PRC-024-2 R1 was an overall compliance assessment which was to be done at the fleet level. Essential Power implemented a process including external consultants to comply with its incorrect interpretation of PRC-024-2 and to become compliant at the fleet, rather than at the registered entity level. On July 29, 2016, Essential Power compliance staff discussed with ReliabilityFirst staff the implementation of the PRC-024-2 standard. ReliabilityFirst stated that enforcement of the PRC standards would be assessed at the registered entity level, not at the fleet level for entities. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because Essential Power compliance staff misunderstood the requirements of PRC-024-2 R1. Essential Power and West Springfield incorrectly believed that they could show compliance at the fleet level rather than at the registered entity level. Essential Power’s misunderstanding of the requirements of PRC-019-2 R1 is a root cause of this noncompliance. This issue started on July 1, 2016, when West Springfield was required to comply with PRC-024-2 R1 and ended on April 18, 2017, when West Springfield completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is minimized because West Springfield was capable of providing only 131.72 MW and operated with a capacity factor of 2.94% during the noncompliance. When West Springfield operated, no trips occurred due to inadequate coordination and when West Springfield performed the verification, no changes were required. This is related to meeting a deadline for a new standard and is not likely to continue to occur or occur again. Lastly, the risk is minimized by the fact that if the entity had registered all its units as one registered entity it would have not been a noncompliance based on the implementation plan. No harm is known to have occurred. ReliabilityFirst considered West Springfield's PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, West Springfield: 1) researched and selected a vendor to perform the analysis required in PRC-024-2; 2) submitted all requested information to the selected vendor to complete the analysis; 3) reviewed the compliance procedure templates for PRC-024 to ensure they sufficiently address the ongoing compliance obligations. West Springfield used the template to create plant procedures that will ensure that Essential Power completes all required testing for and beyond the upcoming five year window; 4) trained site personnel on the procedure and on the timeline required to complete the next review prior to the next five year deadline; 5) added a preventative maintenance activity for 2020 to perform the required five-year coordination review; 6) performed the PRC-024-2 evaluation at West Springfield, Rock Springs, and Newington; and 7) performed setting changes required in the PRC-024-2 coordination analysis. Essential Power completed PRC-024-2 verification on 100% of its units by the end of the first quarter 2017 at each location, which is beyond the required 40% by July 1, 2016 and 100% full compliance milestone of July 1, 2019. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power Rock Springs, LLC (EPRS) | NCR00251 | RFC2016016314 | MOD-025-2 | R1 | On October 4, 2016, EPRS submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. EPRS compliance staff misinterpreted MOD-025-2 which led them to believe, incorrectly, that PJM and ISO-NE had incorporated the MOD-025-2 testing requirements in its tariff procedures and that separate MOD-025 demonstration was not necessary. EPRS compliance staff did not think they needed to perform any other MOD-025 related maintenance and testing to show compliance. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because EPRS compliance staff misunderstood the requirements of MOD-025-2. EPRS staff incorrectly believed they did not need to take any other actions to show compliance with MOD-025-2. EPRS’s misunderstanding of the requirements of MOD-025-2 is a root cause of this noncompliance. This issue started on July 1, 2016, when EPRS was required to comply with MOD-025-2 R1 and ended on December 29, 2016, when EPRS submitted the required testing it performed to PJM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized here because each EPRS unit satisfied its real and reactive power verification requirements put in place by PJM and ISO-NE for the past five years and each unit performed its claimed real power capability testing during the summer of 2016. The risk is limited because EPRS’ two units had capabilities of only 166.4 MW and 184.04 MW respectively while operating at capacity factors of only 29.13% and 27.56%. Finally, no unit was requested to operate at its maximum leading or lagging reactive limit from 2014 to 2016. No harm is known to have occurred. ReliabilityFirst considered EPRS' MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPRS: 1) determined if the claimed capability test performed in 2016 can be utilized to satisfy the real power verification (R1.1). EPRS confirmed that the claimed capability tests could be utilized for R1.1. EPRS also determined that supporting data at the points specified in R1.1 were recorded during the test and could be utilized for MOD-025-2 reporting purposes; 2) scheduled and performed any real power verifications required and reactive power verifications by the end of 2016 to minimally meet the 40% threshold at each facility that was required by July 1, 2016; and 3) published a five-year MOD-025-2 performance schedule for all Essential Power facilities. This five year schedule will help prevent recurrence because EPRS personnel will know what tasks they need to perform to maintain compliance with MOD-025. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power Rock Springs, LLC (EPRS) | NCR00251 | RFC2016016315 | PRC-019-2 | R1 | On October 4, 2016, EPRS submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. In mid-2015, NERC gave Essential Power approval to combine its five individual registrations into a single consolidated NERC registration. However, ReliabilityFirst informed Essential Power that it must dispose of its outstanding compliance matters before the consolidation could be finalized. Essential Power communicated with other entities and came to the conclusion that PRC-019-2 R1 was an overall compliance assessment which was to be done at the fleet level. Essential Power implemented a process including external consultants to comply with its incorrect interpretation of PRC-019 and to become compliant at the fleet, rather than at the registered entity level. On July 29, 2016, Compliance staff discussed with ReliabilityFirst staff the implementation of the PRC-019-2 standard. ReliabilityFirst stated that enforcement of the PRC standards would be assessed at the registered entity level, not at the fleet level for entities. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because EPRS compliance staff misunderstood the requirements of PRC-019-2 R1. Essential Power and EPRS incorrectly believed that they could show compliance at the fleet level rather than at the registered entity level. Essential Power’s misunderstanding of the requirements of PRC-019-2 R1 is a root cause of this noncompliance. This issue started on July 1, 2016, when EPRS was required to comply with PRC-019-2 R1 and ended on April 20, 2017, when EPRS completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage controls which can result in a generator falsely tripping. The risk is minimized because EPRS satisfied its 40% obligation at the fleet level, just not at each registered entity facility. The risk is limited because EPRS’ two units had capabilities of only 166.4 MW and 184.04 MW respectively while operating at capacity factors of only 29.13% and 27.56% during the noncompliance. The risk is further minimized by the fact that if the entity had registered all its units as one registered entity it would have not been a noncompliance based on the implementation plan. Finally when EPRS performed the verification, no changes were required. No harm is known to have occurred. ReliabilityFirst considered EPRS' PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPRS: 1) researched and selected a vendor to perform the analysis required in PRC-019-2; 2) submitted all requested information to the selected vendor to complete the analysis; 3) reviewed the compliance procedure templates for PRC-019 and ensured it sufficiently addresses the associated compliance obligations. EPRS used the template to create plant procedures; 4) performed the PRC-019-2 evaluation by the end of the first quarter 2017 at West Springfield, Rock Springs, and Newington; and 5) performed any relay setting changes needed per the PRC-019-2 coordination analysis. Essential Power completed PRC-019-2 verification on 100% of its units by the end of the first quarter 2017 at each location, which is beyond the required 40% by July 1, 2016 and 100% full compliance milestone of July 1, 2019. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power Rock Springs, LLC (EPRS) | NCR00251 | RFC2016016316 | PRC-024-2 | R1 | On October 4, 2016, EPRS submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. In mid-2015, NERC gave Essential Power approval to combine its five individual registrations into a single consolidated NERC registration. However, ReliabilityFirst informed Essential Power that it must dispose of its outstanding compliance matters before the consolidation could be finalized. Essential Power communicated with other entities and came to the conclusion that PRC-024-2 R1 was an overall compliance assessment which was to be done at the fleet level. Essential Power implemented a process including external consultants to comply with its incorrect interpretation of PRC-024-2 and to become compliant at the fleet, rather than at the registered entity level. On July 29, 2016, Essential Power compliance staff discussed with ReliabilityFirst staff the implementation of the PRC-024-2 standard. ReliabilityFirst stated that enforcement of the PRC standards would be assessed at the registered entity level, not at the fleet level for entities. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because Essential Power compliance staff misunderstood the requirements of PRC-024-2 R1. Essential Power and EPRS incorrectly believed that they could show compliance at the fleet level rather than at the registered entity level. Essential Power’s misunderstanding of the requirements of PRC-024-2 R1 is a root cause of this noncompliance. This issue started on July 1, 2016, when EPRS was required to comply with PRC-024-2 R1 and ended on April 20, 2017, when EPRS completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is limited because EPRS’ two units had capabilities of only 166.4 MW and 184.04 MW respectively while operating at capacity factors of only 29.13% and 27.56%. Further, when EPRS operated, no trips occurred due to inadequate coordination and when EPRS performed the verification, no changes were required. This is a one-time event that is related to meeting a deadline for a new standard and is not likely to continue to occur or occur again. Lastly, the risk is minimized by the fact that if the entity had registered all its units as one registered entity it would not have been a violation based on the implementation plan. No harm is known to have occurred. ReliabilityFirst considered EPRS' PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPRS: 1) researched and selected a vendor to perform the analysis required in PRC-024-2; 2) submitted all requested information to the selected vendor to complete the analysis; 3) reviewed the compliance procedure templates for PRC-024 to ensure they sufficiently address the ongoing compliance obligations. EPRS used the template to create plant procedures; 4) performed the PRC-024-2 evaluation at West Springfield, Rock Springs, and Newington; and 5) performed setting changes needed per the PRC-024-2 verification analysis. Essential Power completed PRC-024-2 verification on 100% of its units by the end of the first quarter 2017 at each location, which is beyond the required 40% by July 1, 2016 and 100% full compliance milestone of July 1, 2019. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Grand Ridge Energy LLC (Grand Ridge Energy) | NCR10306 | RFC2017017727 | PRC-019-2 | R1 | On May 31, 2017, ReliabilityFirst determined that Grand Ridge Energy, as a Generator Owner, was in noncompliance with PRC-019-2 R1 identified during a Compliance Audit conducted on May 11, 2017. Grand Ridge Energy did not coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions by the July 1, 2016 implementation date for PRC-019-2 R1. Grand Ridge Energy missed the July 1, 2016 implementation date for PRC-019-2 R1 because Grand Ridge Energy incorrectly believed that the PRC-019-2 Requirements provided a 100% performance deadline of July 1, 2019 and not July 1, 2016. Grand Ridge Energy did not complete the evaluation of its system capabilities and in service protection system devices to determine if any changes were required until March 1, 2017. (Grand Ridge Energy performed the settings review and subsequent coordination for all park turbines, feeder relays, and the main breaker as of March 1, 2017. Grand Ridge Energy completed the coordination by remotely pulling applicable relay settings and turbine settings, and comparing them to the referenced documentation and making the necessary changes. Grand Ridge Energy completed this coordination and review for all 66 wind turbine generators, four feeder relays, and one main breaker relay.) This noncompliance involves the management practices of verification and risk management. Verification is involved because Grand Ridge Energy did not verify that its understanding of PRC-019-2 was correct and Grand Ridge Energy did not have an internal control in place to verify that its understanding of upcoming NERC Standards and Requirements was correct. This lack of an effective internal control is a root cause of this noncompliance. Risk management is involved because Grand Ridge Energy did not effectively plan to become compliant with PRC-019-2 by the July 1, 2016 implementation date. This noncompliance started on July 1, 2016, when Grand Ridge Energy was required to comply with PRC-019-2 R1 and ended on March 1, 2017, when Grand Ridge Energy completed its Mitigating Activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that Grand Ridge Energy’s noncompliance has the potential to harm the BPS by causing a discoordination of voltage controls which can result in a generator falsely tripping. The risk is minimized because when Grand Ridge Energy performed the required coordination and verification, only minor changes were required. ReliabilityFirst notes that Grand Ridge Energy contributes approximately 99 Megawatts to the grid and operated at approximately a 30% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Grand Ridge Energy’s PRC-019-2 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Grand Ridge Energy: 1) performed the settings review and subsequent coordination for all park turbines, feeder relays, and the main breaker; 2) conducted a NERC Standards implementation schedule identification and interpretation training with the responsible Subject Matter Experts (SMEs) to review how NERC performance deadlines are often interpreted and applied (to reduce the likelihood of future reoccurrence); and 3) implemented a NERC Compliance Program wide review of future implementation dates and proactive scheduling of activities that now includes an interpretation verification task with the respective Regional Entity and assigned SMEs, when declared necessary by the Compliance Manager.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Gratiot County Wind LLC (Gratiot County) | NCR11235 | RFC2017017726 | PRC-019-2 | R1 | On May 31, 2017, ReliabilityFirst determined that Gratiot County, as a Generator Owner, was in noncompliance with PRC-019-2 R1, and ReliabilityFirst identified this during a Compliance Audit conducted on May 11, 2017. Gratiot County did not coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions by the July 1, 2016 implementation date for PRC-019-2 R1. Gratiot County missed the July 1, 2016 implementation date for PRC-019-2 R1 because Gratiot County incorrectly believed that the PRC-019-2 Requirements provided a 100% performance deadline of July 1, 2019 and not July 1, 2016. Gratiot County did not complete the evaluation of its system capabilities and in service protection system devices to determine if any changes were required until February 15, 2017. Gratiot County made the necessary changes and completed the coordination effort with its Transmission Owner on February 15, 2017. This noncompliance involves the management practices of verification and risk management. Verification is involved because Gratiot County did not verify that its understanding of PRC-019-2 was correct and Gratiot County did not have an internal control in place to verify that its understanding of upcoming NERC Standards and Requirements was correct. This lack of an effective internal control is a root cause of this noncompliance. Risk management is involved because Gratiot County did not effectively plan to become compliant with PRC-019-2 by the July 1, 2016 implementation date. This noncompliance started on July 1, 2016, when Gratiot County was required to comply with PRC-019-2 R1 and ended on February 15, 2017, when Gratiot County completed its Mitigating Activities by completing its required coordination efforts with its Transmission Owner. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that Gratiot County’s noncompliance has the potential to harm the BPS by causing a discoordination of voltage controls which can result in a generator falsely tripping. The risk is minimized because when Gratiot County performed the coordination and verification, only minor changes were required. ReliabilityFirst notes that Gratiot County contributes approximately 212 Megawatts to the grid and operated at approximately a 30% factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Gratiot County’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Gratiot County: 1) completed the required evaluations, testing, and coordination; 2) conducted a NERC Standards implementation schedule identification and interpretation training with the responsible Subject Matter Experts (“SMEs”) to review how NERC performance deadlines are often interpreted and applied; and 3) implemented a NERC Compliance Program wide review of future implementation dates and proactive scheduling of activities that now includes an interpretation verification task with the respective Regional Entity and assigned SMEs, when declared necessary. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (Rocky Road) | NCR03009 | RFC2016015906 | MOD-025-2 | R1 | On July 11, 2016, Rocky Road submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Rocky Road did not complete its Real Power testing and did not provide its Transmission Planner with the verification of Rocky Road’s Real Power capability of its applicable Facilities by the July 1, 2016 enforcement date for MOD-025-2 R1. While conducting a mock audit in July 2016, Rocky Road and its contractor conducting the mock audit discovered that Rocky Road misinterpreted the MOD-025-2 Standard and Requirements. Rocky Road incorrectly believed that because its MOD-025-2 data did not change, it did not need to submit data again to its Transmission Planner. During that same mock audit, Rocky Road’s contractors explained to Rocky Road that it needed to conduct new testing and that the results should be submitted by the enforcement date for at least two generators (40%) per the implementation plan for MOD-025-2 R1. Rocky Road hired an engineering firm (Kestrel Engineering) to conduct the testing on behalf of Rocky Road. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Rocky Road compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is Rocky Road’s failure to effectively plan for the July 1, 2016 effective date for MOD-025-2. This noncompliance started on July 1, 2016, when Rocky Road was required to comply with MOD-025-2 R1 and ended on February 2, 2017, when Rocky Road completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Rocky Road quickly identified and corrected this noncompliance. Lastly, Rocky Road contributes approximately 349 MW to the grid and operated at less than a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rocky Road’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Rocky Road selected Kestrel Engineering to perform its Real Power Testing to verify output. Rocky Road now understands the requirements of MOD-025 and has developed a plant procedure which demonstrates the verification type and periodicity in which Real and Reactive Power Capability Testing must be completed. The procedure also ensures that Rocky Road completes Attachment 2 of the standard and submits the necessary data within the specified timeframe. Rocky Road also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added to Gensuite with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Rocky Road will also continue to rely on outside mock audits and internal self-assessments to prevent the probability of this noncompliance happening again. Lastly, Rocky Road holds biweekly compliance calls to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (Rocky Road) | NCR03009 | RFC2016015907 | MOD-025-2 | R2 | On July 11, 2016, Rocky Road submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Rocky Road did not complete its Reactive Power testing and did not provide its Transmission Planner with the verification of Rocky Road’s Reactive Power capability of its applicable Facilities by the July 1, 2016 enforcement date for MOD-025-2 R2. While conducting a mock audit in July 2016, Rocky Road and its contractor conducting the mock audit discovered that Rocky Road misinterpreted the MOD-025-2 Standard and Requirements. Rocky Road incorrectly believed that because its MOD-025-2 data did not change, it did not need to submit data again to its Transmission Planner. During that same mock audit, Rocky Road’s contractors explained to Rocky Road that it needed to conduct new testing and that the results should be submitted by the enforcement date for at least two generators (40%) per the implementation plan for MOD-025-2 R1. Rocky Road hired an engineering firm (Kestrel Engineering) to conduct the testing on behalf of Rocky Road. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Rocky Road compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is Rocky Road’s failure to effectively plan for the July 1, 2016 effective date for MOD-025-2. This noncompliance started on July 1, 2016, when Rocky Road was required to comply with MOD-025-2 R2 and ended on February 2, 2017, when Rocky Road completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Rocky Road quickly identified and corrected this noncompliance. Lastly, Rocky Road contributes approximately 349 MW to the grid and operated at less than a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rocky Road’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Rocky Road selected Kestrel Engineering to perform its Reactive Power Testing. Rocky Road now understands the requirements of MOD-025 and has developed a plant procedure which demonstrates the verification type and periodicity in which Real and Reactive Power Capability Testing must be completed. The procedure also ensures that Rocky Road completes Attachment 2 of the standard and submits the necessary data within the specified timeframe. Rocky Road also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added to Gensuite with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Rocky Road will also continue to rely on outside mock audits and internal self-assessments to prevent the probability of this noncompliance happening again. Lastly, Rocky Road holds biweekly compliance calls to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (Rocky Road) | NCR03009 | RFC2016016058 | PRC-019-2 | R1 | On August 19, 2016, Rocky Road submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Rocky Road did not perform the applicable coordination and did not perform the required verification of current data by a third party by the July 1, 2016 implementation date for PRC-019-2 R1. While conducting a mock audit in July 2016, Rocky Road and its contractor conducting the mock audit discovered that Rocky Road misinterpreted the PRC-019-2 Standard and Requirements. Rocky Road incorrectly believed that its existing documentation and data was sufficient to show compliance. After further examining the existing documentation and data, however, Rocky Road discovered that it needed to perform a verification. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Rocky Road compliance staff failed to interpret and implement PRC-019-2 correctly. A root cause of this noncompliance is Rocky Road’s failure to effectively plan for the July 1, 2016 effective date for PRC-019-2. This noncompliance started on July 1, 2016, when Rocky Road was required to comply with PRC-019-2 R1 and ended on February 9, 2017, when Rocky Road completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because when Rocky Road performed the verification and coordination, no changes were required. Additionally, Rocky Road quickly identified and corrected this noncompliance. Lastly, Rocky Road contributes approximately 349 MW to the grid and operated at less than a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rocky Road’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Rocky Road: 1) verified the PRC-019 data on-site; and 2) developed a plant procedure to ensure the coordination of voltage regulating systems and protection. Rocky Road Power now understands the requirements of PRC-019 and has developed a plant procedure which demonstrates that coordination of voltage regulating system controls and protection systems devices must be completed, as well as when the coordination must take place. Rocky Road Power will also rely on outside mock audits and internal self-assessments to prevent the probability of this noncompliance happening again. Lastly, Rocky Road holds biweekly compliance calls to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (Rocky Road) | NCR03009 | RFC2016016435 | PRC-019-2 | R2 | On October 21, 2016, Rocky Road submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R2. Rocky Road did not perform the applicable coordination and did not perform the required verification of current data by a third party by the July 1, 2016 implementation date for PRC-019-2. While conducting a mock audit in July 2016, Rocky Road and its contractor conducting the mock audit discovered that Rocky Road misinterpreted the PRC-019-2 Standard and Requirements. Rocky Road incorrectly believed that its existing documentation and data was sufficient to show compliance. After further examining the existing documentation and data, however, Rocky Road discovered that it needed to perform a verification. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Rocky Road compliance staff failed to interpret and implement PRC-019-2 correctly. A root cause of this noncompliance is Rocky Road’s failure to effectively plan for the July 1, 2016 effective date for PRC-019-2. This noncompliance started on July 1, 2016, when Rocky Road was required to comply with PRC-019-2 R2 and ended on February 2, 2017, when Rocky Road completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because when Rocky Road performed the verification and coordination, no changes were required. Additionally, Rocky Road quickly identified and corrected this noncompliance. Lastly, Rocky Road contributes approximately 349 MW to the grid and operated at less than a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rocky Road’s PRC-019 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Rocky Road verified PRC-019 during its MOD-025 study. Rocky Road Power now understands the requirements of PRC-019 and has developed a plant procedure which demonstrates that coordination of voltage regulating system controls and protection systems devices must be completed, as well as when the coordination must take place. Rocky Road Power will also rely on outside mock audits and internal self-assessments to prevent the probability of this noncompliance happening again. Lastly, Rocky Road holds biweekly compliance calls to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (Rocky Road) | NCR03009 | RFC2017017625 | PRC-024-2 | R1 | On May 16, 2017, Rocky Road submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Rocky Road's owner conducted a mock audit on another plant that it owns in July of 2016. During this audit, the contractors identified that the plant being audited misinterpreted the PRC-024 standard. The contractors also discovered that Rocky Road also misinterpreted the Standard. After discussions with the contractors, Rocky Road realized that testing under MOD-025 needed to take place and coordinating documentation was needed so that verification could be completed under PRC-024. Under the MOD-025 implementation plan, at least two generators (40%) needed to be tested and the coordination studies needed to take place at Rocky Road. At that time, Rocky Road located an engineering firm (Kestrel Power Engineering) to conduct the testing on Units 1 – 4 at Rocky Road on behalf of Rocky Road. (Rocky Road Power conducted testing on all four units and had a PRC-019/PRC-024 coordination study performed in conjunction.) This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Rocky Road compliance staff failed to interpret and implement PRC-024-2 correctly. A root cause of this noncompliance is Rocky Road’s failure to effectively plan for the July 1, 2016 effective date for PRC-024-2. This noncompliance started on July 1, 2016, when Rocky Road was required to comply with PRC-024-2 R1 and ended on February 3, 2017, when Rocky Road completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because when Rocky Road performed the verification study, no changes were required. Lastly, Rocky Road contributes approximately 349 MW to the grid and operated at less than a 5% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Rocky Road’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Rocky Road: 1) conducted testing on all units; and 2) completed the required coordination study and submitted all relevant documentation. Rocky Road now understands the requirements of PRC-024 and has developed a plant procedure which demonstrates that coordination of protective relaying is crucial such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the "no trip zone" of PRC-024 Attachment 1, as well as when the coordination must take place. To prevent the probability of this noncompliance happening again, Rocky Road will annually review the internal plant procedure, while also updating upon any standard revisions. Rocky Road also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added to Gensuite with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Rocky Road will also rely on outside mock audits and internal self-assessments as a second check. Rocky Road holds biweekly compliance calls to ensure plant staff are aware of upcoming deadlines and compliance obligations.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Rocky Road Power, LLC (Rocky Road) | NCR03009 | RFC2017017627 | PRC-024-2 | R2 | On May 16, 2017, Rocky Road submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Rocky Road's owner conducted a mock audit on another plant that it owns in July of 2016. During this audit, the contractors identified that the plant being audited misinterpreted the PRC-024 standard. The contractors also discovered that Rocky Road also misinterpreted the Standard. After discussions with the contractors, Rocky Road realized that testing under MOD-025 needed to take place and coordinating documentation was needed so that verification could be completed under PRC-024. Under the MOD-025 implementation plan, at least two generators (40%) needed to be tested and the coordination studies needed to take place at Rocky Road. At that time, Rocky Road located an engineering firm (Kestrel Power Engineering) to conduct the testing on Units 1 - 4 on behalf of Rocky Road. (Rocky Road Power conducted testing on all four units and had a PRC-019/PRC-024 coordination study performed in conjunction.) This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Rocky Road compliance staff failed to interpret and implement PRC-024-2 correctly. A root cause of this noncompliance is Rocky Road’s failure to effectively plan for the July 1, 2016 effective date for PRC-024-2. This noncompliance started on July 1, 2016, when Rocky Road was required to comply with PRC-024-2 R2 and ended on February 3, 2017, when Rocky Road completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because when Rocky Road performed the verification study, no changes were required. Lastly, Rocky Road contributes approximately 349 MW to the grid and operated at less than a 5% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Rocky Road’s PRC-024 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Rocky Road: 1) conducted testing on all units; and 2) completed the required coordination study and submitted all relevant documentation. Rocky Road now understands the requirements of PRC-024 and has developed a plant procedure which demonstrates that coordination of protective relaying is crucial such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the "no trip zone" of PRC-024 Attachment 1, as well as when the coordination must take place. To prevent the probability of this noncompliance happening again, Rocky Road will annually review the internal plant procedure, while also updating upon any standard revisions. Rocky Road also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added to Gensuite with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Rocky Road Power will also rely on outside mock audits and internal self-assessments as a second check. Rocky Road holds biweekly compliance calls to ensure plant staff are aware of upcoming deadlines and compliance obligations.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Scrubgrass Generating Company, LP (Scrubgrass) | NCR00912 | RFC2017017448 | PRC-024-2 | R1 | On April 13, 2017, Scrubgrass submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Scrubgrass began reviewing PRC-024-2 relay settings in July of 2015. During an initial review of the relay settings, Scrubgrass reached out to the original equipment manufacturer (Bechtel) to identify if any equipment limitations existed. This process to discover if any equipment limitations existed took more than 12 months due to Bechtel being unable to find Scrubgrass’ documentation. Bechtel eventually identified that Scrubgrass’ equipment limitation data had been destroyed. On May 31, 2016, Scrubgrass contracted with PACE Engineering Services to perform a PRC-024-2 analysis at Scrubgrass. PACE Engineering Services issued a draft report to Scrubgrass on July 11, 2016. That draft report identified voltage and frequency settings that encroached inside the “no trip zone” identified in PRC-024-2. After receiving this draft report, Scrubgrass reached out to PJM (the Planning Authority) and FirstEnergy (the Transmission Planner), to inform both of them of the current settings at Scrubgrass and to inform PJM of the efforts at Scrubgrass to correct the settings. As a result of these efforts, Scrubgrass contracted with a second vendor (Ready Technologies) to conduct an independent study in order to determine if there were any equipment limitations that would prevent the Scrubgrass facility from adjusting the relays to outside of the no trip zone, as well as to visit the site to adjust the relay settings as needed. When the vendor completed the study, the vendor determined that there were no equipment limitations preventing Scrubgrass from changing the relays. The study also determined that the existing relays are not capable of being programmed to achieve the settings required for PRC-024-2 and as such need to be replaced with new relays that are capable of being set appropriately. This noncompliance involves the management practices of asset and configuration management, verification, and external interdependencies. Asset and configuration management is involved because Scrubgrass did not know that its existing relays were not capable of being programmed to achieve the settings required for PRC-024-2. Verification is involved because Scrubgrass did not have an internal control in place to verify that its relay settings were compliant with PRC-024-2 as of the July 1, 2016 implementation date. This lack of an effective internal control is a root cause of this noncompliance. External interdependencies is also involved because Scrubgrass could not get the data it needed from its original equipment manufacturer and did not have that data on its own. This noncompliance started on July 1, 2016, when Scrubgrass was required to comply with PRC-024-2 R1 and ended on November 16, 2017, when Scrubgrass installed the new relays during an outage. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “No Trip Zone,” a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because Scrubgrass did not have unit trips based on current frequency relay settings during the noncompliance. The settings changes required in the new relays are also minor. Lastly, ReliabilityFirst notes that Scrubgrass consists of one small approximately 85 MW unit and there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Scrubgrass’ PRC-024-2 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Scrubgrass: 1) conducted a review of plant status to determine if there could be any planned or forced outages that could be an opportunity to install the new relays; and 2) installed new Over/under Voltage (27/59) and Over/under Frequency (81OU) Relays calibrated and set outside the no trip zone per PRC-024, during a plant outage, To prevent reoccurrence of this type of issue Scrubgrass commits to performing better oversight of its contractors. In this instance, the generator original equipment manufacturer deferred the original relay documentation to the construction company. The construction company took a long time determining that the Scrubgrass commissioning documents had been destroyed. Scrubgrass will review all contractor requirements, expectations, and results at least annually.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Scrubgrass Generating Company, LP (Scrubgrass) | NCR00912 | RFC2017017949 | PRC-024-2 | R2 | On July 11, 2017, Scrubgrass submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Scrubgrass began reviewing PRC-024-2 relay settings in July of 2015. During an initial review of the relay settings, Scrubgrass reached out to the original equipment manufacturer (Bechtel) to identify if any equipment limitations existed. This process to discover if any equipment limitations existed took more than 12 months due to Bechtel being unable to find Scrubgrass’ documentation. Bechtel eventually identified that Scrubgrass’ equipment limitation data had been destroyed. On May 31, 2016, Scrubgrass contracted with PACE Engineering Services to perform a PRC-024-2 analysis at Scrubgrass. PACE Engineering Services issued a draft report to Scrubgrass on July 11, 2016. That draft report identified voltage and frequency settings that encroached inside the “no trip zone” identified in PRC-024-2. After receiving this draft report, Scrubgrass reached out to PJM (the Planning Authority) and FirstEnergy (the Transmission Planner), to inform both of them of the current settings at Scrubgrass and to inform PJM of the efforts at Scrubgrass to correct the settings. As a result of these efforts, Scrubgrass contracted with a second vendor (Ready Technologies) to conduct an independent study in order to determine if there were any equipment limitations that would prevent the Scrubgrass facility from adjusting the relays to outside of the no trip zone, as well as to visit the site to adjust the relay settings as needed. When the vendor completed the study, the vendor determined that there were no equipment limitations preventing Scrubgrass from changing the relays. The study also determined that the existing relays are not capable of being programmed to achieve the settings required for PRC-024-2 and as such need to be replaced with new relays that are capable of being set appropriately. This noncompliance involves the management practices of asset and configuration management, verification, and external interdependencies. Asset and configuration management is involved because Scrubgrass did not know that its existing relays were not capable of being programmed to achieve the settings required for PRC-024-2. Verification is involved because Scrubgrass did not have an internal control in place to verify that its relay settings were compliant with PRC-024-2 as of the July 1, 2016 implementation date. This lack of an effective internal control is a root cause of this noncompliance. External interdependencies is also involved because Scrubgrass could not get the data it needed from its original equipment manufacturer and did not have that data on its own. This noncompliance started on July 1, 2016, when Scrubgrass was required to comply with PRC-024-2 R2 and ended on November 16, 2017, when Scrubgrass installed the new relays during an outage. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “No Trip Zone,” a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because Scrubgrass did not have unit trips based on current frequency relay settings during the noncompliance. The settings changes required in the new relays are also minor. Lastly, ReliabilityFirst notes that Scrubgrass consists of one small approximately 85 MW unit and there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Scrubgrass’ PRC-024-2 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Scrubgrass: 1) conducted a review of plant status to determine if there could be any planned or forced outages that could be an opportunity to install the new relays; and 2) installed new Over/under Voltage (27/59) and Over/under Frequency (81OU) Relays calibrated and set outside the no trip zone per PRC-024, during a plant outage, To prevent recurrence of this type of issue, Scrubgrass commits to performing better oversight of its contractors. In this instance, the generator original equipment manufacturer deferred the original relay documentation to the construction company. The construction company took a long time determining that the Scrubgrass commissioning documents had been destroyed. Scrubgrass will review all contractor requirements, expectations, and results at least annually.
2017-12-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Wisconsin Electric Power Company (WEPCO) | NCR00951 | RFC2017017785 | PRC-005-6 | R3 | On June 19, 2017, WEPCO submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-005-6 R3. On May 9, 2017, WEPCO’s Power Generation (PG) NERC Engineer performed a review of the PG Battery Maintenance Report. During this review, the engineer determined that one NERC classified battery at WEPCO’s Oak Creek Power Plant exceeded its NERC compliance testing date. (According to NERC Standard PRC-005-6, Table 1-4(a) testing for this battery should have occurred within 4 calendar months of the previous maintenance activity on this battery. Per footnote 3 to the PRC-005-6 tables, a calendar month starts on the first day of the first month after a maintenance activity has been completed. The previous maintenance activity for this battery was completed on December 14th, 2016, which translated to the due date for completing the required testing as April 30th, 2017.) Following this discovery, the engineer notified the system owner at Oak Creek Power Plant of the missed battery testing requirement and advised that the testing be performed as soon as possible. The system owner at the Oak Creek Power Plant notified the electrical maintenance department of the need to perform the battery maintenance and WEPCO immediately performed the maintenance on May 9, 2017. The battery at issue is the 250v DC source for the DC circuity on Oak Creek Power Plant Units 5 through 8. The Oak Creek Power Plant utilizes the SAP Impact work management system to initiate and manage licensing, inspection, and testing of equipment preventative maintenance work orders. The work orders are automatically generated for the plant to plan and schedule the work to be performed. The maintenance work is documented in WEPCO’s Cascade, a sequel maintenance management system to Impact, and Cascade is WEPCO’s data base for battery compliance (including the battery at issue). For this noncompliance, an Oak Creek Power Plant scheduler incorrectly removed the SAP Impact preventative maintenance activity and placed it into the backlog until the engineer noticed the oversight on May 9, 2017. The scheduler meant to place a different activity into the backlog and placed the maintenance activity at issue into the backlog by accident. The testing for this battery was scheduled to be completed on April 30, 2017. WEPCO completed the maintenance testing on May 9, 2017, nine days late. Upon discovery of the battery testing oversight, WEPCO performed a review of all NERC battery maintenance activities as defined in PRC-005-6 and all other maintenance activities were found to have been completed within the intervals specified within PRC-005-6. This noncompliance involves the management practices of workforce management and verification. Workforce management is involved because the scheduler at Oak Creek Power Plant was not effectively trained on how to correctly schedule preventative maintenance activity. This lack of effective training is a root cause of this noncompliance. Verification is also involved because WEPCO did not have an effective internal control in place to check and ensure that the scheduler correctly scheduled the preventative maintenance activity. This noncompliance started on April 30, 2017, when WEPCO should have performed the testing on the battery at issue and ended on May 9, 2017, when WEPCO completed the overdue testing on the battery nine days late. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is allowing important Protection System devices to remain unmaintained and untested which can negatively affect the reliable operation of those devices and the BPS. The risk is minimized because this noncompliance only affects one battery for a short duration (nine days). WEPCO quickly identified and corrected this noncompliance which demonstrates effective detective and corrective controls. WEPCO has successfully completed more than 400 battery preventative maintenance activities and inspections since PRC-005-6 was adopted in April 2015. Additionally, WEPCO has nearly 700 relays that are all current on their inspection interval and this missed activity represents a very small percentage of PRC-005-6 maintenance activities performed. The battery and battery charger were in service for the duration of the noncompliance, and WEPCO received no alarms related to this battery. Lastly, the battery test performed on May 9, 2017 showed no degradation in battery performance. No harm is known to have occurred. ReliabilityFirst considered WEPCO’s PRC-005-6 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, WEPCO: 1) provided applicable Oak Creek Power Plant (OCPP) personnel with refresher training for identifying and scheduling of Licensing, Inspection and Testing of Equipment Preventative Maintenance Activities within the Impact Preventative Maintenance System; 2) provided applicable OCPP personnel with refresher training on how to execute the NERC Battery Maintenance Report; 3) revised the Compliance Program control activities to review PG fleet battery test records every 30 days and will alert plant senior leadership when batteries are within 30 days of being out of compliance. This is intended to be a back stop for the work management systems in place to manage battery maintenance and to highlight those batteries that are soon to be out of compliance; and 4) shared lessons learned with all power plant Chief Engineers. ReliabilityFirst has verified the completion of all mitigation activity.
2017-12-28 | SERC Reliability Corporation (SERC) | Ameren Missouri (AUE) | NCR10248 | SERC2016016601 | VAR-002-4 | R2 | On November 29, 2016, AUE submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with VAR-002-4 R2. AUE did not maintain the generator voltage schedule provided by its Transmission Operator (TOP) at its Sioux Energy Center (SEC) facility on September 26, 2016. On September 25, 2016, the SEC was operating with unit 1 off-line for a major outage. Unit 2 was operating on-line with plant night shift personnel occupied with two major issues. First, the SEC Distributed Control System (DCS) controls for the coal handling operations were not operating properly, forcing plant operators to control the coal handling system manually to keep unit 2 on-line. Second, plant operators were performing 138 kV switching in order to isolate the unit 1 starting transformer for maintenance and testing work the next day. Around 9:43 p.m., plant operators started the coal crusher which caused the 4 kV bus to briefly drop below 4 kV. The DCS sensed this voltage drop and caused the 138 kV switchyard voltage control (SVC) to switch from automatic to manual. The SVC, in conjunction with the generator exciter automatic voltage regulator (AVR), automatically maintains the SEC 138 kV voltage schedule set by the TOP. The unit 2 generator AVR remained operational and in automatic throughout the event. However, with the SVC in manual, the AVR was not sufficient to keep the 138 kV voltage from slowly drifting higher and eventually above the SEC voltage schedule. The control system had a visual alarm but only on a screen seldom used by the operators. This screen was not in use at the time of the voltage excursion. Around 3:30 a.m. on September 26, 2016, after completing the coal handling and switching activities, the plant operator discovered the SVC was in manual and switched the SVC from manual to automatic. The plant operator identified the issue while reviewing the plant elog, an electronic logging tool, as part of standard processes. The elog was designed with logic to prompt the printout of an alarm whenever the switchyard voltage floats above or below the TOP provided voltage schedule for one hour or longer. The TOP voltage schedule includes instructions to maintain the voltage schedule based on the hourly average voltage. AUE designed the printout of an alarm to serve as a backup means for identifying alarms and other issues relating to plant operations. The primary cause identified in AUE’s corrective action review was the loss of the auto-control for the 138 kV SVC when the voltages dropped on the 4 kV bus. The primary mechanism to monitor for alarms of this nature is through the DCS, which the operators monitor in real-time. However, at the time voltage regulation alarms relating to manual versus automatic operation appeared on subsidiary screens, not the primary screen. Since the operators were working to monitor and manage the emergent issues at the plant, the operators did not see the alarms. The operators reviewed the elog, a backup mechanism for monitoring for plant status issues, and identified the voltage excursion. This noncompliance started on September 26, 2016 at 2:10 a.m., when the voltage exceeded the voltage schedule, and ended on September 26, 2016 at 3:44 a.m., when the voltage returned to within the voltage schedule. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AUE’s failure to maintain the assigned voltage schedule could result in equipment damage or insufficient reactive resource for reliable system operation. However, identified deviations were only 0.3 kV (0.22%) from the voltage schedule and the excursion lasted less than two hours. The automatic voltage regulators were in automatic voltage control mode and there were no instances of voltage excursions causing system voltage problems. The TOP received real-time generator voltage from the generating plant. There were no issues on the transmission system during this noncompliance that prompted corrective action by the TOP. No harm is known to have occurred. SERC considered AUE’s VAR-002-4 R2 compliance history in determining the disposition track. AUE’s relevant prior noncompliance with VAR-002-4 R2 includes: NERC Violation ID SERC2015015384. SERC determined that AUE’s VAR-002-4 R2 compliance history should not serve as a basis for applying a penalty. The primary cause and mitigating activities of the prior noncompliance involved a misunderstanding of a voltage change request and the design of a different facility’s automatic voltage control equipment, which are unrelated to the cause of the instant noncompliance, and resulted in a small drop in voltage below the bottom of the voltage schedule. In addition, the mitigating activities of the prior noncompliance would not address the cause of the instant noncompliance. The instant noncompliance involved a failure to notice a voltage excursion alarm for less than two hours that was identified via a secondary control that printed out alarm information when the switchyard voltage deviated from the voltage schedule for one hour or more. | To mitigate this noncompliance, AUE: 1) improved switchyard voltage control alarm visibility and created new automated elog notifications to the SEC operators and shift supervisor whenever the SVC switches from AUTO to MANUAL mode; 2) reviewed the SVC system alarms across the Ameren fossil steam generator fleet and shared lessons learned at SEC with the other Ameren Energy Centers (Nuclear, hydro and CTG units will not be included since those units do not have SVC systems due to other regulatory requirements, small size, limited hours of operation and unpredictability of operation); 3) conducted refresher training for the SEC control-room personnel on the importance of the voltage schedule and the benefit of the SVC in maintaining the voltage schedule; and 4) conducted refresher training for all Ameren fossil steam Energy Center control-room personnel on the importance of the voltage schedule and the benefit of the SVC in maintaining the voltage schedule.
2017-12-28 | SERC Reliability Corporation (SERC) | Ameren Services Company (Ameren) | NCR01175 | SERC2016015967 | PRC-005-6 | R3 | On August 2, 2016, Ameren submitted a Self-Report stating that, as a Transmission Owner (TO), it was in noncompliance with PRC-005-6 R3. Ameren did not conduct the required four calendar month maintenance and testing for one battery. On July 8, 2016, during a review of battery maintenance and testing records, Ameren discovered that a battery that feeds three 138 kV relays located at a substation missed the required four calendar month battery maintenance and testing interval. At the time of discovery, Ameren had last conducted battery maintenance and testing for this particular battery on January 29, 2016. On July 9, 2016, one day after the discovery, Ameren performed the maintenance and testing. Ameren determined that the missed battery maintenance and testing interval was due to a human data entry error that caused the reoccurring scheduled maintenance job to not create the proper second quarter maintenance job in Ameren's maintenance database and job system. In response to a request for information, Ameren conducted a walk-down of three facilities identified by SERC. Ameren found no additional instances of noncompliance. Additionally, the SERC 2017 audit did not identify any additional instances of noncompliance. This noncompliance started on June 1, 2016, when Ameren exceeded four calendar months on the battery maintenance and testing, and ended on July 9, 2016, when it completed the four calendar month battery maintenance and testing. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Ameren’s failure to conduct the required battery maintenance and testing activities could lead to improper operation of Protection System devices. However, Ameren installed the battery on May 7, 2015 and routine tests on January 29, 2016 and July 9, 2016 indicated strong battery health. Ameren missed the four month battery maintenance and testing interval by approximately one month. No harm is known to have occurred. SERC considered Ameren’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Ameren: 1) performed the maintenance and testing battery test for the Kinmundy battery; 2) performed a review of all batteries in Ameren's TO system to ensure all batteries have been maintained and tested within the required intervals and all maintenance activities have been completed; 3) developed modifications or additions to current management reporting that provides means to detect and correct omitted or erroneous data entries on Protection System components maintenance intervals during monthly reviews; and 4) created and distributed lessons learned.
2017-12-28 | SERC Reliability Corporation (SERC) | Carville Energy LLC (Carville) | NCR11479 | SERC2017018547 | MOD-032-1 | R2 | On October 30, 2017, Carville submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-032-1 R2. In 2016, Carville did not provide confirmation that its steady-state, dynamics, and short circuit modeling data had not changed since its last submission to its Transmission Planner (TP) and Planning Coordinator (PC) according to the data requirements and reporting procedures developed by its PC and TP in Requirement R1. On August 31, 2015, Carville received an email from its PC, forwarded from Carville’s Energy Manager, to confirm or provide the facility’s generator data to the PC. On September 15, 2015, Carville confirmed with its PC that Carville’s data had not changed since the prior submission. On September 25, 2017, during a one-time internal review of the MOD-032 requirements and documentation, Carville could not find documentation that it received a request from its PC or TP or made a submittal to its PC or TP in 2016. Carville confirmed that it did not receive a data request in 2016 and verified that it did not confirm that there had been no changes from the prior data submission. Carville, per the procedure, should have submitted the modeling data by September 15, 2016. Because Carville was not on the PC’s distribution list, it did not get an email asking it to submit the modeling data in 2016. The primary causes of the noncompliance were the lack of a data request from the PC and TP to provide the required data, and the lack of internal controls to submit the required data in the absence of a data request. This noncompliance started on September 15, 2016, when Carville missed the modeling data submission date, and ended on November 6, 2017, when Carville submitted the modeling data to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to provide modeling data could result in the TP and PC incorrectly modeling the Carville facility’s capabilities. However, the Carville facility’s capabilities have not changed since the 2015 data submission. Therefore, the data previously provided and used by the TP and PC in models was accurate. Carville is a 570 MW facility that operated at a capacity factor of 63% for the 12 months ending June 30, 2017. No harm is known to have occurred. SERC considered Carville’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Carville: 1) submitted the modeling data to its PC and TP; 2) subscribed to the PC’s Planning Subcommittee distribution list, which the PC uses to notify entities of the annual MOD-032-1 data collection process requirements; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates that the generator modeling data must be verified in accordance with the process developed by the PC and TP each year. The PM task is designed to notify plant personnel at least three months prior to the due date established by the process; and 4) performed supplemental training on the noncompliance for the operating staff involved with verifying the generator’s modeling data.
2017-12-28 | SERC Reliability Corporation (SERC) | Decatur Energy Center, LLC (Decatur) | NCR11481 | SERC2017018560 | PRC-019-2 | R1 | On November 3, 2017, Decatur submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Decatur did not meet the NERC implementation schedule to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for 40% of its Facilities by July 1, 2016. On June 30, 2016, Decatur completed the coordination study. On October 3, 2016, Decatur completed the setting changes for 100% of its Facilities. On September 13, 2017, Decatur identified the noncompliance when responding to a SERC request-for-information related to a noncompliance with another Standard and Requirement associated with the same implementation schedule. The primary cause of the noncompliance was Decatur’s misinterpretation of the implementation schedule. Decatur incorrectly believed that the study to determine the settings was to cover 40% of the work needed to meet compliance instead of 40% of the Facilities with settings compliant and incorrectly believed that the 40% applied at a fleet level instead of the individual registered entity. The Decatur contractor that operates approximately 40 generating plants subject to NERC Standards assumed that those 40 generating plants comprised the fleet. In March 2016, during participation in regional and national meetings, the Decatur contractor determined that it misinterpreted the implementation schedule and informed the plants. Once Decatur correctly understood the implementation schedule requirements, it attempted to find a contractor to complete the work, but there was very limited availability due to industry-wide efforts to ensure compliance. Upon completion of the study, Decatur attempted to schedule an outage with its Transmission Operator, but the Transmission Operator was unwilling to schedule an outage for the relay setting changes during the summer season. This noncompliance started on July 1, 2016, when Decatur did not meet the NERC implementation schedule for 40% of its units, and ended on October 3, 2016, when it completed the setting changes for 100% of its units. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Decatur’s failure to verify that the voltage regulating system controls were properly coordinated with its Protection Systems could lead to a generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, while Decatur missed the July 1, 2016 deadline to verify coordination of two units, it had an additional year for the coordination verification of the remaining units. Therefore, Decatur’s delay of 94 days for the 40% requirement resulted in minimal additional risk and Decatur verified coordination for 100% of its units on October 3, 2016, further reducing the risk by completing the required coordination for all of its units ahead of the required implementation schedule. Decatur made setting changes to resolve conflicts between its Protection Systems and voltage regulating system controls. These changes included one change to its protective relays and two changes to its automatic voltage regulator (AVR). If the change to the protective relays had not been made, the relays could have tripped for V/Hz excursions greater than 104% and lasting for longer than 100 seconds before the Z/Hz limiter had an opportunity to operate. If the changes to the AVR’s V/Hz limiter had not been made, the AVR’s definite time trip characteristic could have operated for V/Hz excursions ranging from 100% to 120% for durations between 3.5 seconds and 19 seconds. Decatur is a 795 MW 3x1 combined cycle facility that operated at an average capacity factor of 35% for the 12 month period ending June 2017. No harm is known to have occurred. SERC considered Decatur’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Decatur: 1) completed the study and made relay setting changes; 2) created a NERC Preventive Maintenance (PM) task in its compliance management tool (Maximo) requiring a coordination study and any needed changes identified in that study per PRC-019; 3) provided training to plant personnel related to PRC-019 to ensure understanding of the requirements; and 4) revised its Internal Compliance Program (ICP) to ensure the implementation process for new or revised standards are understood or guidance is sought from NERC or the appropriate Regional Entity.
2017-12-28 | SERC Reliability Corporation (SERC) | Decatur Energy Center, LLC (Decatur) | NCR11481 | SERC2017018561 | PRC-024-2 | R2 | On November 3, 2017, Decatur submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Decatur did not meet the NERC implementation schedule to set its protective relaying such that the generator voltage protective relaying does not trip within the “no trip zone” of PRC-024 Attachment 2 for 40% of its Facilities by July 1, 2016. On June 30, 2016, Decatur completed the study. On October 3, 2016, Decatur completed the setting changes for 100% of its Facilities. On September 13, 2017, Decatur identified the noncompliance when responding to a SERC request-for-information related to a noncompliance with another Standard and Requirement associated with the same implementation schedule. The primary cause of the noncompliance was Decatur’s misinterpretation of the implementation schedule. Decatur incorrectly believed that the study to determine the settings was to cover 40% of the work needed to meet compliance instead of 40% of the Facilities with settings compliant and incorrectly believed that the 40% applied at a fleet level instead of the individual registered entity. The Decatur contractor that operates approximately 40 generating plants subject to NERC assumed that those 40 generating plants comprised the fleet. In March 2016, during participation in regional and national meetings, the Decatur contractor determined that it misinterpreted the implementation schedule and informed the plants. Once Decatur correctly understood the implementation schedule requirements, it attempted to find a contractor to complete the work, but there was very limited availability due to industry-wide efforts to ensure compliance. Upon completion of the study, Decatur attempted to schedule an outage with its Transmission Operator, but the Transmission Operator was unwilling to schedule an outage for the relay setting changes during the summer season. This noncompliance started on July 1, 2016, when Decatur did not meet the implementation schedule for 40% of its units, and ended on October 3, 2016, when it completed the setting changes for 100% of its units. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Decatur’s failure to verify that the generator voltage relays are set to not trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, while Decatur missed the July 1, 2016 deadline to verify relay settings of two units, it had an additional year for the coordination verification of the remaining units. Therefore, Decatur’s delay of 94 days for the 40% requirement resulted in minimal additional risk and Decatur completed the relay setting changes for 100% of its units on October 3, 2016, further reducing the risk by completing the required coordination verification for 100% of its units ahead of the required implementation schedule. Only the overvoltage protective relaying required a setting change and was reduced by approximately 10%. Decatur is a 795 MW 3x1 combined cycle facility that operated at an average capacity factor of 35% for the 12 month period ending June 2017. No harm is known to have occurred. SERC considered Decatur‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Decatur: 1) completed the study and made relay setting changes; 2) created a NERC Preventive Maintenance (PM) task in its compliance management tool (Maximo) requiring a coordination study and any needed changes identified in that study per PRC-024; 3) provided training to plant personnel related to PRC-024 to ensure understanding of the requirements; and 4) revised its Internal Compliance Program (ICP) to ensure the implementation process for new or revised standards are understood or guidance is sought from NERC or the appropriate Regional Entity.
2017-12-28 | SERC Reliability Corporation (SERC) | Entergy (Entergy) | NCR01234 | SERC2016016657 | PRC-001-1.1(ii) | R3; R3.2 | On December 15, 2016, Entergy submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in noncompliance with PRC-001-1.1(ii) R3.2. Entergy did not coordinate a new protection system setting with its neighboring TOP and Host Balancing Authority (BA). On July 29, 2016, Entergy performed an internal compliance survey using its Enterprise Compliance and Risk Tool (ECART). ECART is a web-based tool designed to help manage the Entergy overall compliance and risk processes. Initially, the ECART survey identified four changes to relay settings that did not have evidence of coordination with the interconnecting neighbor. However, further review identified three of the four instances involved an Entergy facility or a connection to load, neither of which require coordination of new protection system settings to occur. In the one remaining issue, Entergy did not communicate a change to the relay timer with the neighboring TOP. The cause of the noncompliance was Entergy’s reliance on an inadequate manual process to determine which relay changes required coordination, which resulted in human error. This noncompliance started on May 31, 2016, when Entergy made the uncoordinated change, and ended on August 11, 2016, when Entergy notified the neighboring TOP of the change. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to coordinate relay setpoint changes with neighboring TOPs or host BAs may result in inadequate protection for the interconnecting facility. However, this noncompliance involves only the timing of the primary protection relay of a non-critical 115 kV transmission line. Entergy adjusted the timer to be the same as the timer for the backup relay which had already been properly coordinated with the neighboring TOP. Entergy made the change to prevent a misoperation of the Protection System and this change did not cause a misoperation. The noncompliance and corresponding lack of coordination lasted for less than three months. No harm is known to have occurred. SERC considered Entergy’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Entergy: a) communicated installed relay settings changes with the neighboring TOP and BA; b) modified the settings transmittal work flow in Service Now (SNOW) to recognize PRC-001 terminals and prompt the relay settings engineer to establish communication with neighboring TOP and BA of upcoming approved protective system changes (relay settings). This work flow tool will assign a new task for the engineer to send correspondence email to neighboring TOP and BA prior to installation. In alignment with this modification, Entergy revised the System Protection Coordination procedure. Entergy sent out procedure changes to all involved parties for input and revision prior to the effective date of the new revision; and c) shared internal lessons learned with involved working groups.
2017-12-28 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2017016740 | MOD-030-2 | R10 | On December 29, 2016, LGE and KU submitted a Self-Log stating that, as a Transmission Service Provider, it was in noncompliance with MOD-030-2 R10. LGE and KU did not recalculate Available Flowgate Capability (AFC) for hourly AFC and daily AFC as required. LGE and KU relies upon its Reliability Coordinator (RC) and a third-party independent transmission organization (ITO), which provides independent transmission tariff administration services to LGE and KU, to calculate AFC and post Available Transfer Capability (ATC) on behalf of LGE and KU. On August 19, 2016 at approximately 2:00 p.m., the RC’s File Transfer Protocol (FTP) process that uploads the latest AFC initial values and the Transfer Distribution Factors to the OATI WebTrans program on an hourly basis failed. As a result, the tool used old data to calculate AFC and ATC for hourly and daily values. The ITO’s hourly ATC calculation was incorrect for 267 hours for purposes of MOD-030-2 R10.1. The ITO’s daily ATC calculation was incorrect for 11 days for purposes of MOD-030-2 R10.2. The failure did not affect monthly calculations. On August 29, 2016, the ITO discovered the noncompliance during its AFC verification process. The ITO verification process is an internal control that the ITO implemented to identify any issues in the AFC calculation process. The internal control the ITO had in place was a manual checklist that included a step requiring the ITO to verify the date of the file. The ITO was required to complete the checklist verification on a daily basis but the ITO failed to perform the review daily. Therefore, the ITO did not identify the noncompliance for several days. The cause of this noncompliance was the failure of the FTP process that uploads the latest AFC values and the failure of the ITO’s internal controls to detect the failure of the FTP process. This noncompliance started on August 19, 2016, when LGE and KU began incorrectly calculating hourly and daily AFC and ended on August 30, 2016, when LGE and KU began correctly calculating hourly and daily AFC. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LGE and KU’s failure to recalculate AFC for hourly and daily AFC could have led LGE and KU to erroneously approve or refuse, and subsequently scheduled or not scheduled, a transmission service request based on posted incorrect ATC values, which could contribute to system overload. However, if LGE and KU had erroneously approved transmission service requests, the Balancing Authority (BA) and Reliability Coordinator (RC) have other tools such as Transmission Loading Relief (TLR) and/or redispatch to allow them to both identify and mitigate any operating issue that may have arisen. If LGE and KU had erroneously refused and prevented a load-serving entity from importing needed energy, the BA carries appropriate operating reserves. LGE and KU’s review of operations confirmed that no TLRs or operational issues occurred during the noncompliance. In addition, LGE and KU determined that the correct AFC information would not have changed its decisions to accept or reject transmission service requests during the noncompliance. No harm is known to have occurred. SERC considered LGE and KU’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, LGE and KU: 1) had the ITO add a requirement to its daily AFC checklist to take a screen shot of the RC’s FTP file list showing the update date and time and add this screenshot to an internal ticket that is submitted to ITO management for review each time the checklist is completed; and 2) had the RC implement an alarm that alerts when the FTP process fails to upload current data.
2017-12-28 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2017016787 | PRC-005-1 | R2 | On January 6, 2017, LGE and KU submitted a Self-Report stating that, as a Transmission Owner, it was in noncompliance with PRC-005-1 R2. LGE and KU did not implement its Protection System program for a communication channel device installed on May 21, 2010. SERC determined that this noncompliance spans multiple versions of the Standard, including PRC-005-1, PRC-005-2, and PRC-005-6. On May 13, 2016, as a part of the implementation of the PRC-005-6 maintenance program, LGE and KU performed testing on specific 138 kV Line Differential (LD) and Permissive Overreach Transfer Trip (POTT) protection communication channels. LGE and KU installed these channels in 2010 with the intent that LGE and KU would continuously monitor both channels. Under the LGE and KU PRC-005-1 Protection System and Maintenance Program (PSMP), continuously monitored communication channels were not subject to an annual test. Therefore, LGE and KU did not test these channels on an annual basis. During the May 13, 2016 testing, LGE and KU discovered that it was not continuously monitoring the LD channel. The contractor that installed the device did not wire the alarms for the LD channel into the remote terminal unit (RTU) nor were the RTU points created in the Energy Management System (EMS) used by LGE and KU’s Transmission System Operators. The contractor did wire the alarms for the POTT channel correctly, and therefore LGE and KU was continuously monitoring the POTT channel. The LGE and KU PRC-005-1 PSMP required that it test annually or electronically monitor on a continuous basis all communication systems. The primary causes of the noncompliance were LGE and KU’s lack of a documented process and the EMS programmer’s failure to review and commission the EMS points to ensure the channel alarms were correct. LGE and KU cannot provide evidence that indicates EMS programmers performed the coordination for the installation of the LD communication channel. This noncompliance started on May 21, 2011, one year and one day after LGE and KU failed to continuously monitor or test the Protection System device, and ended on July 18, 2016, when LGE and KU began continuous monitoring. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LGE and KU’s failure to test annually or continuously monitor the protection communication channel could have resulted in failure of the Protection System coordination and unnecessary operation of additional protection systems to isolate a fault. However, LGE and KU had a redundant protection scheme in place that was functioning and properly set-up for alarming. In addition, the relay maintained the ability to alarm if there was an issue with the relay. There was no issue with the functionality of the LD channel. This noncompliance impacted a single communication channel device. No harm is known to have occurred. SERC considered LGE and KU‘s PRC-005-1 R2 compliance history in determining the disposition track. LGE and KU’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation IDs SERC2013012951, SERC2011006699, and SERC200800135. SERC determined that LGE and KU’s PRC-005-1 R2 compliance history should not serve as a basis for applying a penalty. LGE and KU’s prior scope assessments would not have identified the instant noncompliance, which involved a failure to set up monitoring of a single communication channel. LGE and KU’s prior mitigation actions did not address the root cause of the instant noncompliance and therefore would not have prevented it from occurring. | To mitigate this noncompliance, LGE and KU: 1) added alarming to the EMS for the Lexington/Higby Mill 138kV Line Differential protection communication channel; 2) reviewed the ‘standard’ RTU points list to ensure all necessary digital communication channel alarm points are on the list. LGE and KU will use this list to perform RTU check out with the EMS; 3) created the RTU Commission Work Practice document for it to use to verify the communication channel alarms are working in the Energy Management System prior to being put in service; 4) provided training on the RTU Commission Work Practice document; 5) verified that a loss of channel alarm point exists in EMS for each protection communication channel; 6) configured protection communication channels to ensure proper alarming in EMS based on the results of the verification; and 7) added protection communication channels to the database to ensure it records and tracks maintenance tests according to the PSMP.
2017-12-28 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2017018420 | TOP-002-4 | R7 | On September 27, 2017, LGE and KU submitted a self-log stating that, as a Balancing Authority (BA), it was in noncompliance with TOP-002-4 R7. LGE and KU did not provide its Operating Plans for next-day operations identified in Requirement R4 to its Reliability Coordinator (RC) on two days in June 2017. The resource monitor tool is a spreadsheet that details the next-day hourly forecasted load, generation, and Net Scheduled Interchange for the entire LGE and KU Balancing Authority Area (BAA). The resource monitor includes LGE and KU next-day forecasted load, generation, and Net Scheduled Interchange as well as next-day forecasted load, generation and Net Scheduled Interchange for three other entities in the LGE and KU BAA. LGE and KU utilizes the resource monitor to meet the TOP-002-4 R4 requirements. On July 5, 2017, during its regular monthly review, LGE and KU discovered that it did not send its Operating Plans for next-day operations to the RC on June 7, 2017 and June 14, 2017. LGE and KU identified this noncompliance by a detective internal control. The transmission compliance engineer verifies after-the-fact that LGE and KU sent the output of the resource monitor to its RC each day of the previous month. Upon reviewing the generated resource monitor files for the month of June 2017, the transmission compliance engineer determined that LGE and KU did not send the resource monitor output for next-day operations to the RC on June 7, 2017 for June 8, 2017, or on June 14, 2017 for June 15, 2017. LGE and KU has used the resource monitor on the BA desk since 2010. The BA System Operator began sending a PDF copy of the resource monitor output to the RC on March 10, 2017 to prepare for the TOP-002-4 effective date of April 1, 2017. At the time of the noncompliance, LGE and KU had internal controls that issued a single reminder alarm on the Energy Management System (EMS) to occur daily at 11:00 AM EST to serve as a reminder to run the resource monitor and send the file to the RC, and notified the System Operator upon closing the resource monitor tool if it has not been sent to the RC. Those internal controls continue to be in effect, although they did not prevent this noncompliance. LGE and KU determined that, although it trained System Operators to not acknowledge the EMS alarm prior to sending the resource monitor output to its RC, the operational procedure did not specifically instruct the System Operators to send the resource monitor output before acknowledging the EMS alarm. This noncompliance occurred on June 7, 2017 and June 14, 2017, when LGE and KU did not send its Operating Plans for next-day operations to the RC. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LGE and KU’s failure to provide the Operating Plans for next-day operations to its RC could result in the RC not being able to fully assess its next-day ability to operate within the System Operating Limits. However, the LGE and KU Operating Plan for next-day operations included the next-day forecasted load, generation, and Net Scheduled Interchange data for the LGE and KU BA. In addition to the resource monitoring tool and as a part of daily operations, the RC receives the next-day forecasted load and Net Scheduled Interchange. Therefore, the only information the RC did not receive was the generation component of the Operating Plan for next-day operations. However, the RC is aware of any generation that is unavailable or derated via System Operator submission to the RC Coordination of Transmission Reliability (CTR) website. The RC assumes that any generation not submitted as an outage into the RC CTR portal is either in service or readily available for use. According to LGE and KU, the RC verified and confirmed there were no reliability issues on June 8, 2017 and June 15, 2017 as a result of not receiving LGE and KU’s BA Operating Plans for next-day operations. No harm is known to have occurred. SERC considered LGE and KU’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, LGE and KU: 1) set the Windows task scheduler to automatically initiate the resource monitor tool at 11:45 A.M. EST daily to serve as reminder that the resource monitor must be ran daily; 2) established an email reminder notification that occurs daily at 1:00 P.M. EST to serve as final reminder to run the resource monitor and send to the RC; 3) updated the procedure to note that the resource monitor output must be sent to the RC before EMS alarms can be acknowledged; and 4) reviewed the updated procedure with all operators.
2017-12-28 | SERC Reliability Corporation (SERC) | Nelson Industrial Steam Company (NISCO) | NCR09017 | SERC2017018421 | PRC-005-6 | R3 | On October 2, 2017, NISCO submitted a self-log stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-2(ii) R3. NISCO reported it had not maintained Protection System batteries in accordance with Tables 1-4(a) and 1-4(b) of PRC-005-2(ii). SERC determined that based on the time this noncompliance occurred, this noncompliance should be processed under PRC-005-6 R3. NISCO operates two coal-fired power plants that generating steam and power as a cogenerator for an adjacent manufacturer. It uses one vented lead-acid (VLA) battery shared between the two units and two valve-regulated lead-acid (VRLA) batteries, one in each unit. On April 10, 2014, NISCO verified that its Protection System Maintenance Plan (PSMP) under PRC-005-1 met the minimum requirements of PRC-005-2(ii) and it implemented PRC-005-2(ii) via its procedure NIS-PRO-PRC-005, Rev. 4. On September 21, 2017, during an independent internal review of all Protection System maintenance records, NISCO identified a noncompliance of the requirements of PRC-005-2(ii)/PRC-005-6. On March 9, 2015 and March 10, 2015, NISCO’s contractor performed the 18-calendar month battery tests specified for VLA and VRLA NISCO should have performed the next 18-calendar month tests no later than September 30, 2016. However, NISCO’s contractor did not complete the tests until October 10, 2016, ten days late. Therefore, NISCO did not meet the 18-calendar month maximum maintenance interval for these batteries. NISCO performed an extent‐of‐condition review that included the entire population of Protection System devices and confirmed this to be a one‐time occurrence involving no other devices. NISCO did not properly reschedule the battery maintenance to occur within the required interval. NISCO determined that the cause of this noncompliance was partially related to insufficient monitoring of its contractor and was a one-time human error that arose due to transitions to intervals required by PRC-005-2 and PRC-005-6. This noncompliance started on October 1, 2016, the day after the last day NISCO could have performed maintenance within 18 calendar months, and ended on October 10, 2016, when NISCO performed the required maintenance and testing activity. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NISCO’s failure to properly perform generator Protection System maintenance may cause or prevent a generator trip when it is required to protect equipment. However, NISCO performed the required 18-month battery tests only 10 days after the required due date. When tested, the batteries met the test requirements specified in PRC-005-2, Tables 1-4(a) and 1-4(b), demonstrating they maintained the ability to perform their function during the 10 days and likely would have performed as expected if needed. During operation as an independent generator, NISCO provides an average of only 200 MW to its interconnection. Furthermore, NISCO performs their 4-month battery tests according to a monthly schedule, resulting in its awareness of battery conditions between the 18-month tests. The delayed maintenance neither caused nor precluded Protection System functions. No harm is known to have occurred. SERC considered NISCO’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, NISCO: 1) performed the 18-month battery tests; 2) confirmed alignment of future testing schedules with the requirements specified in PRC-005-6; by performing an extent of condition review; 3) scheduled upcoming preventive maintenance activities on an annual basis using action tracking software and PM scheduling, which allows a 6-calendar month margin to the 18-calendar month maximum maintenance interval; and 4) set up a process to review the contractor’s preventive maintenance schedule each month to ensure it complies with the PRC-005-specified maximum maintenance intervals. NISCO will identify any discrepancies between the scheduled date(s) and the PRC-005 interval(s) and communicate with the contractor for resolution.
2017-12-28 | SERC Reliability Corporation (SERC) | Old Dominion Electric Cooperative (ODEC) | NCR00859 | SERC2017017856 | MOD-032-1 | R2 | On June 29, 2017, ODEC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-032-1 R2. ODEC failed to provide steady-state, dynamics, and short circuit modeling data to its Planning Coordinator (PC) according to the data requirements and reporting procedures developed by its PC in R1. On June 8, 2017, after several email exchanges between the PC and ODEC regarding the 2017 data submission, the PC sent ODEC an email stating that the PC did not receive the ODEC 2016 data submittal. ODEC investigated and determined that it failed to submit the data by the submission deadline of July 31, 2016 established by its PC because of ODEC’s confusion around the PC’s data input portal. The portal indicated that the 2016 data submission status was “Complete” and that the dates of submittal were within the deadline set for submittal. ODEC did not understand that the status of “Complete” did not indicate that the data was “Submitted”, which according to the PC was the indication that R2 had been met. ODEC was unaware of the additional process steps it needed to complete in order for the data to be submitted to the PC. The primary cause of this noncompliance was ODEC’s unfamiliarity with the PC’s new data submission tool and process. This noncompliance started on August 1, 2016, when ODEC failed to submit its generation data to its PC by the PC’s July 31, 2016 deadline, and ended on June 8, 2017, when ODEC submitted its generation data to its PC. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ODEC’s failure to submit its generation data by the submission deadline could result in inconsistent modeling data requirements. However, prior to 2016, ODEC submitted its data to SERC per MOD-010-0 and MOD-012-0, which in turn was shared with the PC. ODEC did not have any generation data changes for the 2016 submission, and therefore, the PC had the correct data for the ODEC units. The PC did not notify ODEC that it had not received the ODEC generation data until the review was prompted by ODEC emails for the 2017 data submission. No harm is known to have occurred. SERC considered ODEC‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, ODEC: 1) submitted its generation data to its PC; and 2) created instructions on the finalization of submittal of data and placed the instructions in ODEC's MOD-032-1 files.
2017-12-28 | SERC Reliability Corporation (SERC) | Prairie Power, Inc. (PPI) | NCR09035 | SERC2017018601 | EOP-004-2 | R3 | On November 7, 2017, PPI submitted a Self-Report stating that, as a Transmission Owner, Generator Owner, and Generator Operator, it was in noncompliance with EOP-004-2 R3. PPI reported that it had not annually verified all of the contact information in its Operating Plan. In October 2017, during its annual review of its Event Reporting Operating Plan, PPI determined that it did not have documentation that it verified all of the contact information within the plan. Specifically, PPI did not have evidence that it verified the seven direct telephone numbers for local police and sheriff’s departments during its 2016 review. The cause of this noncompliance was PPI’s failure to specify the appropriate level of detail in its annual review process. This noncompliance started on January 1, 2017, the first day following the 2016 calendar year in which PPI did not verify all the contact information in its Operating Plan, and ended on October 4, 2017, when PPI verified all of the contact information in its Operating Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PPI’s failure to confirm contact data could delay a response to events affecting the reliability of the BPS. However, PPI would only call law enforcement in the event of a physical threat or harm, in which case PPI would dial “911,” not the local police and sheriff department numbers. PPI was able to determine that it verified the other contacts included in the PPI Event Reporting Operating Plan Contact List during 2016 by various methods, including dated voice recordings, emails, operating logs or other communication documents, so PPI would have been able to obtain assistance if it were necessary. No harm is known to have occurred. SERC considered PPI’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, PPI: 1) reviewed and verified its entire Event Reporting Operating Plan Contact List via telephone on October 4, 2017. The telephone numbers for local law enforcement non-emergency numbers had not changed between PPI’s last documented verification; and 2) created an Outlook reminder to verify the Operating Plan phone numbers annually, which will be sent from a regulatory compliance calendar to the EOP-004 subject matter expert, area manager, and reliability compliance coordinator.
2017-12-28 | SERC Reliability Corporation (SERC) | South Carolina Electric & Gas Company (SCEG) | NCR00915 | SERC2017017943 | FAC-010-3 | R4 | On July 12, 2017, SCEG submitted a Self-Report stating that, as a Planning Authority, it was in noncompliance with FAC-010-3 R4. SCEG did not issue its revised System Operating Limit (SOL) Methodology to the applicable Planning Authority, Reliability Coordinator, Transmission Operator, and Transmission Planner prior to the effective date of the change. On June 19, 2017, as part of an annual Standards review, SCEG identified that it did not distribute a revised SOL Methodology to the applicable entities. On April 1, 2017, SCEG put the revised procedure into effect. SCEG updated the SOL Methodology to align with revised NERC definitions and Standard references. All revisions were administrative and not SOL-process related. SCEG stated that at the time of the update, it considered these changes to be administrative and not related to the development of SOLs or the SOL Methodology. None of the updates modified SCEG’s methodology for determining SOLs therefore SCEG made the decision to not distribute to the entities identified in requirement R4. SCEG identified this noncompliance through an internal control. As part of its Internal Compliance Program and as a detective internal control, SCEG performs annual reviews of select Standards. SCEG conducts this process by engaging an independent consultant. During this year’s annual review of FAC-010, the consultant identified a potential noncompliance with FAC-010-3 R4 with not timely distributing the updated document to the entities listed in requirement R4. This noncompliance started on April 1, 2017, when SCEG put the revised SOL Methodology into effect without first providing it to the required entities, and ended on July 14, 2017, when SCEG provided the revised SOL Methodology to the required entities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SCEG’s failure to issue its revised SOL methodology to all applicable entities under FAC-010-3 R4 prior to the effectiveness of a change could result in entities establishing SOLs that are not in accordance with an approved SOL Methodology. However, the updates made to the document in this case were administrative in nature and did not affect the SOL Methodology, and thus would have no risk to the establishment of SOLs by SCEG or applicable Planning Authorities, Reliability Coordinators, Transmission Operators, or Transmission Planners. No harm is known to have occurred. SERC considered SCEG's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SCEG: 1) redistributed the updated FAC-010 Compliance Document to the applicable entities; 2) added a statement to its procedure as a visual reminder to reissue after any update: "This procedure has to be sent to the Supervisor of Transmission Planning Studies for distribution to all applicable entities PRIOR to the signature process"; and 3) updated the checklist in its internal procedure ‘ERO Compliance Internal Procedure ERO 190: Procedures for Revision' to verify if the procedures need to be distributed to entities prior to the effectiveness of the changes. The ERO compliance group uses this procedure and the checklist that is part of the procedure, when it is reviewing all procedures that SCEG is updating or developing. Each time when a procedure will be ready for the signature process, SCEG will check each procedure it is developing or updating against that checklist for prior distribution to the effective date. In addition, SCEG will make a similar note in all ERO Compliance Procedures used for compliance with the ERO standards that it must distribute before the procedure becomes effective. The note will be a reminder to ensure that it distributes the procedure to the applicable entities as required by the specific ERO standard.
2017-12-28 | SERC Reliability Corporation (SERC) | South Carolina Public Service Authority (SCPSA) | NCR01312 | SERC2017017428 | COM-002-4 | R3 | On April 21, 2017, SCPSA submitted a Self-Report stating that, as a Distribution Provider (DP), it was in noncompliance with COM-002-4 R3. SCPSA did not document that it conducted initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction. On February 17, 2017, SCPSA identified that certain DP personnel should have received training to meet the requirements of COM-002-4 R3 as those personnel have authorization to perform switching on 230 kV and 115 kV facilities. A training instructor for a distribution switching class was reviewing training requirements and identified that SCPSA authorizes certain DP personnel to execute switching on a de-energized transmission line and therefore must receive training. SCPSA did not identify any instances in which the DP personnel received Operating Instructions during the period of noncompliance. However, the DP personnel have been in the position to receive an oral two-party, person to person Operating Instruction since July 1, 2016. The supervisor of applicable DP personnel provided informal training because SCPSA recognized the documented communications protocols training as a best practice their personnel already followed and provided it as awareness. The training the DP personnel received was the same training all other operating personnel received. However, SCPSA did not maintain specific records of the DP personnel training, as SCPSA did not believe this training was required at the time of the training. The primary cause of the noncompliance was that SCPSA did not consider switching associated with a facility in a de-energized state as changing the status of an Element in Real-time and therefore believed that such switching did not meet the NERC definition of an Operating Instruction. This noncompliance started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on May 17, 2017, when SCPSA completed the Operating Instruction training for its DP operating personnel. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SCPSA’s failure to provide formal training to its DP operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an Operating Instruction could limit operators’ awareness of predefined communications protocols, which could increase the possibility of miscommunication. However, this noncompliance concerned experienced operators who received the initial training prior to July 1, 2016 but SCPSA did not document training attendance. No harm is known to have occurred. SERC considered SCPSA‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SCPSA: 1) trained operating personnel that hold a "D" or "d" switching code on SCPSA's documented communications protocols; and 2) incorporated the training into the distribution switching training that SCPSA provides to personnel before they can be placed on the Authorized Switching List. Although the training by the Standard is a one-time training, SCPSA incorporated this training into the Distribution switching refresher course that it provides every three years to personnel to maintain their eligibility on the Authorized Switching List.
2017-12-28 | SERC Reliability Corporation (SERC) | South Carolina Public Service Authority (SCPSA) | NCR01312 | SERC2017017951 | MOD-026-1 | R4 | On July 14, 2017, SCPSA submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-026-1 R4. SCPSA did not provide revised model data for Winyah unit 2 and unit 3 to its Transmission Planner (TP) within 180 calendar days of making changes to the plant Automatic Voltage Regulator (AVR) control function that alter the equipment response characteristic. On June 6, 2015, the Superintendent of Electrical Maintenance at the Winyah Generating Station communicated via email to the TP department the plan to replace the unit 2 AVR during the upcoming 2015 fall outage and the unit 3 AVR during the upcoming 2016 spring outage. On November 9, 2015, SCPSA completed the low load portion of the unit 2 model validation just after startup. On May 26, 2016, SCPSA completed the full load portion of the model validation. The delay in completing the model validation for unit 2 was due to unit commitments, load demand, and vendor availability. Based on the completion date of May 26, 2016, SCPSA should have provided the revised unit 2 model data to the TP on or before November 22, 2016. On April 25, 2016, SCPSA completed the low load portion of the unit 3 model validation just after startup. On May 6, 2016, SCPSA completed the full load portion of the model validation; therefore, SCPSA should have provided the revised unit 3 model data should to the TP on or before November 2, 2016. SCPSA personnel frequently meet to discuss matters related to compliance with NERC Reliability Standards. On February 20, 2017, during a discussion between the Generation NERC Coordinator and the Manager of System Control regarding Power System Stabilizers, SCPSA discovered it had not provided the TP the validated models for the new unit 2 and unit 3 AVRs. SCPSA contacted the vendor after the discovery and requested the data. SCPSA provided the TP the validated models for Winyah unit 2 and unit 3 on February 27, 2017. SPCSA determined that the primary cause of the noncompliance was a lack of knowledge by certain personnel of the related compliance requirements. This noncompliance started on November 2, 2016, when SCPSA should have provided the revised AVR data for unit 3 to its TP, and ended on February 27, 2017, when SCPSA provided the revised AVR data for units 2 and 3 to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SCPSA’s failure to provide revised model data to its TP within 180 days of a change could result in inaccurate representations of the unit’s voltage control system in models used to assess BPS reliability. However, SCPSA conducted a detailed analysis of the difference in the models prior to the AVR upgrades with the model after the AVR upgrade and there was no significant difference between simulation results and associated conclusions. In addition, the exciter capabilities did not change, only the method of voltage control. Unit 2 and unit 3 are each 285 MVA net rated coal units with capacity factors of 18% and 15% respectively for the June 2016 to June 2017 period. No harm is known to have occurred. SERC considered SCPSA‘s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SCPSA: 1) provided the MOD-026 validated models for both Winyah 2 and Winyah 3 to the TP; 2) sent a notice to Generating Station management and supervision with a brief explanation that some maintenance affects compliance. This note also requested notification of the Generation Compliance Coordinator and the Santee Cooper Manager of NERC Compliance if any of this type of maintenance or repairs is planned or conducted; and 3) wrote and published a Generation Standard (a generation department policy) on the Generation Department intranet home page. SCPSA will promulgate to the Station Managers, Operations Superintendents, and Maintenance Superintendents. The Generation Standard provides a summary of the NERC MOD-026 Standard and what is required to maintain compliance.
2017-12-28 | Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2017018370 | COM-001-2.1 | R9 | During a Compliance Audit conducted from September 19, 2017, through September 21, 2017, SPPRE determined that LAFA, as a Balancing Authority and Transmission Operator was not compliant with COM-001-2.1 R9. LAFA utilizes a satellite telephone system as its Alternate Interpersonal Communication system. To verify testing of the satellite telephone system SPPRE requested LAFA to provide evidence of testing once each calendar month. LAFA was unable to provide evidence of a test of its satellite telephone system for two calendar months between November 2015 and July 2017. The first noncompliance occurred on March 31, 2016, the end of the calendar month in which LAFA could not provide evidence of testing of its satellite telephone system and ended on April 3, 2016, when LAFA performed a test of its satellite telephone system. The second noncompliance occurred on November 30, 2016, the end of the second calendar month in which LAFA could not provide evidence of testing of its satellite telephone system and ended on December 4, 2016, when LAFA performed a test of its satellite telephone system. The root cause of this noncompliance was human error. LAFA initially relied on the satellite phone test performed by the Midwest Independent System Operator (MISO) to verify operation of its satellite telephone system and failed to realize that because the MISO test is performed every five weeks, the test would not meet the calendar month test requirement in COM-001-2.1 R9. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to routinely test the Alternate Interpersonal Communication system creates the potential that alternative communications would be unavailable in the event of the loss of primary communications. The loss of operator communications degrades operator situational awareness and increases the risk that operators will not respond or will respond incorrectly to system emergencies. Here, LAFA’s inability to provide evidence of testing of its satellite telephone system was limited to two calendar months. LAFA attests that it did not experience a failure of its satellite telephone system. Additionally, LAFA’s primary communication systems, i.e., telephone landline and 800 MHz two-way radio, were operational during the months documentation of satellite telephone system tests was unavailable. LAFA’s primary and alternative communication systems are inherently reliable and failure of one or more of these communications systems is unlikely. No actual harm is known to have occurred. LAFA has no relevant prior violations of COM-001-2.1 or any other standards that are similar in nature. | To mitigate this noncompliance, LAFA: 1) revised its loss of communications procedure to include a satellite phone test on the first working Monday of each month (such test is in addition to the satellite test initiated by MISO every five weeks); and 2) revised the Day operator checklist to include the test of the satellite phone system by calling MISO. SPP RE has verified the completion of all mitigation activity.
2017-12-28 | Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2017018544 | PRC-005-1.1b | R2; R2.1 | On May 16, 2017, SPA submitted a Self-Report stating that, as a Transmission Owner, it had an issue of noncompliance with PRC-005-1.1b R2.1. During an internal review, SPA discovered that it did not complete testing of fiber strands within five segments of dark fiber within the 15 month interval established for communication systems in its Protection System Testing and Maintenance Program (Program). The duration of this instance of noncompliance was from October 1, 2015, the day after the dark fiber segments should have been tested, through May 12, 2017, the date the final dark fiber segment was successfully tested. The root cause of this instance of noncompliance was a combination of human error and lack of internal controls. The instances of incomplete testing were all conducted by one SPA technician in 2015. The SPA technician left shortly after the 2015 testing was completed and SPA did not assign a technician to the geographic area where the dark fibers were located. Further, there were no internal controls in place that would have detected the incomplete testing. A single point of contact was reviewing the test record summaries, however, the test results were not being reviewed for completeness. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to test associate communication systems within defined intervals has the potential to affect the reliability of the BPS by increasing the risk that the associated communications systems will not operate properly, thereby increasing the risk of potential protection system misoperations. Notwithstanding, the issue involved less than 0.1% of the fiber strands within the five dark fiber segments. The five dark fiber segments represented .25% of all SPA Protection System devices. Active fibers within the five dark fiber segments were not impacted however, if impacted, the fibers are monitored by SPA’s supervisory control and data acquisition (SCADA) system that would send an alarm if an active fiber strand had experienced a failure. SPA technicians were available 24/7 for any issues that may have arisen, however, no known major fiber failures occurred for the duration of the issue. No harm is known to have occurred. SPA has no relevant prior violations of PRC-005-1.1b R2.1 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, SPA: 1) tested the five segments of fiber; 2) implemented a quality assurance review that requires both the testing technician and a peer reviewer to sign off on protection system device testing results; 3) reinforced that protection system device testing will adhere to the SPA Program, and 4) hired a technician for the affected geographic area and approved two additional technician positions to be filled to address staffing issues. SPP RE has verified the completion of all mitigation activity.
2017-12-28 | Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (Empire) | NCR01155 | SPP2017017397 | TOP-001-3 | R13 | On April 18, 2017, Empire submitted a Self-Report stating that, as a Transmission Operator, it was in noncompliance with TOP-001-3 R13 because it failed to ensure that Real-Time Assessments were performed at least once every 30 minutes during two weekends. Empire contracts with its Reliability Coordinator (RC), the Southwest Power Pool (SPP), to perform the required Real-Time Assessments to determine if there are any contingencies that could result in instability, uncontrolled separation, or Cascading outages. Empire’s Real-Time Contingency Analysis (RTCA) application is utilized to retrieve the Real-Time Assessments from SPP every 20 minutes. In late 2016, Empire began its process of moving its RTCA application to a new platform. The testing of the new RTCA platform was completed on March 31, 2017, and the new platform was made operational on that same date. On April 10, 2017, Empire discovered that the RTCA application was configured to run only Monday through Friday. As a result, Real-Time Assessments performed by SPP had not been retrieved for two consecutive weekends. Because Empire did not retrieve the Real-Time Assessments, it lacked evidence to ensure that the assessments were performed. There were two instances of noncompliance. The first instance of noncompliance started on April 1, 2017, at 12:00 a.m., the date the RTCA application stopped running and retrieving Real-Time Assessments from SPP, and ended on April 3, 2017, at 12:00 a.m., the date the RTCA application began running and retrieving the Real-Time Assessments from SPP. The duration of the second instance of noncompliance began on April 8, 2017, at 12:00 a.m., the date the RTCA application stopped running and retrieving Real-Time Assessments from SPP, and ended on April 10, 2017, at 12:00 a.m., the date the RTCA application began running and retrieving the Real-Time Assessments from SPP. The root cause of these instances of noncompliance was the lack of an internal control to ensure adherence to the standard. The IT Department was responsible for moving the RTCA application to the new platform on behalf of the Operations Department. During the testing phase of the RTCA application, the application was configured to run only Monday through Friday, which is the default schedule that IT uses to run IT-related tasks. The IT Department’s schedule did not include a separate schedule for the Operations Department, i.e., the required 24 x 7 schedule of the RTCA application. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to ensure that Real-Time Assessments are performed at least once every 30 minutes has the potential to affect the reliability of the BPS by limiting Empire’s ability to be aware of contingencies that could result in instability, uncontrolled separation, or Cascading outages. Notwithstanding, SPP was monitoring the Empire transmission system and would have alerted Empire had there been a potential for instability, uncontrolled separation, or a Cascading outage. Additionally, SPP conducted Real-Time Assessments at least every 30 minutes during both weekends. Thus, Empire would have been able to promptly obtain the Real-Time Assessments conducted by SPP had SPP alerted Empire of an issue affecting the reliability of its transmission system. Moreover, Empire maintained situational awareness and was monitoring its system during both weekends. No harm is known to have occurred. Empire has no relevant prior violations of TOP-001-3 R13 or any other standards that are similar in nature. | To mitigate this noncompliance, Empire: 1) revised the IT Department’s schedule to include the 24 x 7 schedule of the RTCA application and included a note instructing IT personnel not to change the schedule of the RTCA application without first obtaining approval from the Operations Department; 2) reconfigured the RTCA application to run 24 x 7; and 3) verified that Real-Time Assessments are being conducted every 30 minutes seven days a week. SPP RE has verified the completion of all mitigation activity.
2017-12-28 | Southwest Power Pool Regional Entity (SPP RE) | USACE-Tulsa District (COETULSA) | NCR06038 | SPP2017017062 | PRC-005-6 | R3 | On February 24, 2017, COETULSA submitted a Self-Certification stating that, as a Generator Owner (GO), it had an issue of noncompliance with PRC-005-6 R3 because it did not maintain the Protection System Devices included in its time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within the PRC-005-6 R3 Tables. Specifically, COETULSA did not have evidence of the four-month Vented Lead-Acid (VLA) battery tests as required by Table 1-4 (a). This issue of noncompliance involved three of COETULSA’s seven hydroelectric plants. In 2016, one plant missed two VLA battery test intervals and two plants missed one VLA battery test interval. The duration of this instance of noncompliance was from September 30, 2016, four months after the last recorded test of the VLA batteries, through January 3, 2017, the date the VLA batteries were tested and testing was verified. The root cause of this instance of noncompliance was human error and a lack of internal controls because the plant operation manager did not verify that testing was being performed. COETULSA had a large number of equipment upgrades at its plants, and the routine maintenance was overlooked by its operations and maintenance personnel. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform VLA battery tests has the potential to affect the reliability of the BPS by increasing the risk that VLA batteries would fail to supply sufficient power to protection system relays and DC circuits thereby causing a misoperation of the Protection System Devices. Notwithstanding, COETULSA’s VLA batteries are continuously monitored for intentional grounds, and when COETULSA performed the required four-month tests on the batteries, the three batteries tested at acceptable levels. No harm is known to have occurred. COETULSA has no relevant prior violations of PRC-005-6 R3 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, COETULSA: 1) completed VLA battery testing and inspection in January 2017; and 2) implemented quarterly battery maintenance in its Facility Equipment System to be completed within specific timeframes to ensure the four-month interval for VLA battery testing and inspection is not exceeded. SPP RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Senate Wind, LLC (Senate) | NCR11274 | TRE2017018302 | PRC-005-2(i) | R3 | During a Compliance Audit conducted from July 25, 2017 through September 6, 2017, Texas RE determined that Senate, as a Generator Owner (GO), was in noncompliance with PRC-005-2(i) R3. In particular, Senate did not timely perform all required 4-month and 18-month maintenance and testing activities for two Vented-Lead Acid (VLA) batteries as required by PRC-005-2(i), Table 1-4(a). Pursuant to the Implementation Plan for PRC-005-2(i), Senate was required to complete initial 4-month testing on its two VLA batteries by October 1, 2015. Senate timely performed certain required maintenance and testing activities, but did not inspect for unintentional grounds as required. Senate was further required to perform specified 18-month maintenance and testing activities on the two VLA batteries by April 1, 2017. However, Senate again did not perform all required 18-month maintenance and testing activities. Specifically, Senate did not verify battery continuity, battery terminal connection resistance, battery intercell connection resistance, or measure battery cell values as required. On June 6, 2017, Senate completed all required 4-month and 18-month maintenance and testing activities for the two VLA batteries, ending the issue. The root cause of this noncompliance was that Senate did not have an adequate procedure that addressed all the required maintenance activities of the new Standard version. In particular, the checklist that Senate used as part of its procedure to document its battery testing activities did not include all required 4-month and 18-month maintenance tasks for the VLA batteries in question. This noncompliance started on October 1, 2015, the date Senate did not perform all required 4-month testing activities for the two VLA batteries, and ended on June 6, 2017, when Senate completed all required testing activities for the VLA batteries at issue. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the VLA batteries at issue only represent approximately 1.6% (2/123) of the total Protection System devices in Senate’s PSMP. Second, Senate did not identify any issues with the two VLA batteries when it performed the required 4-month and 18-month testing. Third, Senate had been performing regular monthly testing on the two VLA batteries at issue, including checking battery voltage and physical inspections, reducing the scope of the missing testing. Finally, the single Senate wind generation Facility at issue is small, with a nameplate rating of 150 MW. No harm is known to have occurred. Texas RE considered Senate’s and its affiliates' PRC-005 R3 compliance history in determining the disposition track. Senate has no relevant prior instances of noncompliance. However, two Senate affiliates have relevant prior noncompliance records involving versions of PRC-005 R3 (RFC2017017067 and WECC2017017160). Texas RE determined that these prior instances of noncompliance should not serve as an aggravating factor because the root cause of RFC2017017067 is distinguishable from the current noncompliance, and the remediation pertaining to WECC20170170160 is similar to the actions Senate has taken to prevent recurrence of TRE2017018302. RFC2017017067 for ShadyOak (NCR11247) – ShadyOak did not inspect the condition of all individual units of its VRLA type batteries by measuring battery cell/unit internal ohmic values nor did ShadyOak verify that the station battery could perform as manufactured by evaluating cell/unit measurements indicative of battery performance against the station battery baseline. The root cause of the issue stemmed from ShadyOak’s use of a third party contractor to perform battery testing and maintenance activities pursuant to its Protection System Maintenance Program. ShadyOak believed that its contractor had performed all required battery maintenance and testing, and ShadyOak liked sufficient oversight of this contractor’s testing activities. In contrast, the current circumstances involved the Senate’s failure to include all required 4-month and 18-month maintenance tasks on the checklist that Senate’s internal personnel used as part of their procedure to document all battery testing activities. WECC2017017160 for AGPS (NCR11249) – AGPS failed to perform the minimum maintenance activities within the maximum maintenance intervals for its two VLA batteries for unintentional grounds as prescribed in Table 1-4(a). AGPS’ maintenance documentation did not have instructions to inspect for unintentional grounds so that requirement was omitted from AGPS’ periodic maintenance activities. Texas RE determined that although the circumstances pertaining to this previous issue are similar to the current noncompliance, the noncompliance instances occurred around similar time frames and remediation has been taken to help prevent recurrence. | To mitigate this noncompliance, Senate: 1) performed the required maintenance testing activities; 2) updated the monthly and annual procedure checklists to include all required 4-month and 18-month maintenance activities; and 3) updated its PSMP to include all required maintenance activities for VLA batteries. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Senate Wind, LLC (Senate) | NCR11274 | TRE2017018777 | PRC-005-2(i) | R1 | During a Compliance Audit conducted from July 25, 2017 through September 6, 2017, Texas RE determined that Senate, as a Generator Owner (GO), was in noncompliance with PRC-005-2(i) R3 because it did not timely perform all required 4-month and 18-month maintenance and testing activities for two Vented-Lead Acid (VLA) batteries as required by PRC-005-2(i), Table 1-4(a). Subsequently, on December 12, 2017, Texas RE determined that Senate likewise had a noncompliance of PRC-005-2(i) R1. Specifically, Senate failed to establish a Protection System Maintenance and Testing Program (PSMP) for all of its Protection System devices. Senate's wind generation Facility has two VLA batteries. On July 1, 2015, Senate adopted a new PSMP to reflect the maintenance and testing requirements established under PRC-005-2(i). In doing so, however, Senate incorporated requirements and testing intervals for Valve Regulated Lead-Acid (VRLA) battery Protection Systems instead of the VLA batteries actually in place at its generation Facility. During a compliance review, however, Senate determined that its PSMP failed to include such VRLA battery devices. On May 24, 2017, Senate amended its PSMP to include the required testing intervals and activities for its VLA batteries, ending the issue. This noncompliance started on July 1, 2015, the date Senate established its new PSMP without including its two VLA batteries, and ended on May 24, 2017, when Senate updated its PSMP to include VLA batteries. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the VLA batteries at issue only represent approximately 1.6% (2/123) of the total Protection System devices in Senate’s PSMP. Second, Senate did not identify any issues with the two VLA batteries when it performed the required 4-month and 18-month testing. Third, Senate had been performing regular monthly testing on the two VLA batteries at issue, including checking battery voltage and physical inspections, reducing the scope of the missing testing. Finally, the single Senate wind generation Facility at issue is small, with a nameplate rating of only 150 MW. No harm is known to have occurred. Texas RE considered Senate’s and its affiliates’ PRC-005 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Senate: 1) updated its PSMP to include VLA battery device Protection System maintenance and testing activities; 2) performed all required maintenance and testing activities on the two VLA batteries at issue; and 3) developed a documented corporate wide NERC Internal Compliance Program, including a process for conducting annual internal compliance assessments. Texas RE has verified the completion of all mitigation activity.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 2 LLC (SW2) | NCR04132 | TRE2017016947 | PRC-024-2 | R1 | On February 7, 2017, SW2 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. In particular, SW2 failed to set its frequency protective relays such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW2 personnel discovered that it had not evaluated the relay settings for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW2 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW2 discovered that several of its generator frequency protective relays were set to operate within the frequency “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW2 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW2 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and will end when SW2 either sets its frequency protective relays to not trip within the “no trip zone” or documents any relays that cannot be reset due to equipment limitations and communicates that information to its Transmission Planner (TP) and Planning Coordinator (PC). | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW2 produced a relatively small amount of power, with a maximum nameplate rating of 105 MW and a 34% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the frequency trip settings for SW2’s single wind generation Facility were set such that the changes to the relays required adjusting overfrequency turbine settings by 0.8 Hz and underfrequency settings by 1.5 Hz at a 0.20 second time setting, as well as adjusting the overfrequency substation relay settings by 1.3 Hz at a 0.35 second time setting to comply with the requisite trip zone settings. Despite these required changes, however, SW2 had no operational issues from these incorrect settings. No harm is known to have occurred. Texas RE considered SW2’s and its affiliates' PRC-024-2 R1 compliance history in determining the disposition track. SW2 has no relevant prior instances of noncompliance. However, a SW2 affiliate has one relevant prior noncompliance record involving PRC-024-2 R1 (SPP2016016224). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW2 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016224 (PRC-024-2 R1) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the frequency protective relays at its wind farm were set such that its generators would not trip when system frequency was within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW2: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; and 7) retained a new director of regulatory compliance that now reports directly to SW2’s Chief Operating Officer. Furthermore, SW2 will complete the following actions by December 29, 2017: 1) document any relays that cannot be reset due to equipment limitations; 2) communicate its relay settings and any known equipment limitations to its TP and PC; and 3) reprogram its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 2 LLC (SW2) | NCR04132 | TRE2017016948 | PRC-024-2 | R2 | On February 7, 2017, SW2 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. In particular, SW2 did not set its protective relays such that its generator voltage protective relaying would not trip applicable generating units as a result of a voltage excursion within the “no trip zone” set forth in PRC-024 Attachment 2. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW2 personnel discovered that it had not evaluated the relay settings for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW2 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW2 discovered that several of its generator voltage protective relays were set to operate within the voltage “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW2 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW2 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and will end when SW2 either sets its voltage protective relays to not trip within the “no trip zone” or documents any relays that cannot be reset due to equipment limitations and communicates that information to its Transmission Planner (TP) and Planning Coordinator (PC) as required. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW2 produced a relatively small amount of power, with a maximum nameplate rating of 105 MW and a 34% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the generator voltage trip settings for SW2’s single wind generation Facility were set such that changes to the relays required increasing the turbine overvoltage settings from 110 to 117.5% and reducing the turbine undervoltage settings from 90 to 45% at a 0.20 second time delay, as well as reducing the substation overvoltage settings from 117 to 115% at a 0.27 second time delay to comply with the requisite trip zone settings. No harm is known to have occurred. Texas RE considered SW2’s and its affiliates' PRC-024-2 R2 compliance history in determining the disposition track. SW2 has no relevant prior instances of noncompliance. However, a SW2 affiliate has one relevant prior noncompliance record involving PRC-024-2 R2 (SPP2016016226). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW2 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016226 (PRC-024-2 R2) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the protective relays at its wind farm were set such that its generators would not trip when system voltage was within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW2: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; and 7) retained a new director of regulatory compliance that now reports directly to SW2’s Chief Operating Officer. Furthermore, SW2 will complete the following actions by December 29, 2017: 1) document any relays that cannot be reset due to equipment limitations; 2) communicate its relay settings and any known equipment limitations to its TP and PC; and 3) reprogram its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2017016952 | PRC-024-2 | R1 | On February 7, 2017, SW3 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. In particular, SW3 failed to set its frequency protective relays such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW3 personnel discovered that it had not evaluated the relay settings for its two generation Facilities by the July 1, 2016 deadline. Following this discovery, SW3 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW3 discovered that several of its generator frequency protective relays were set to operate within the frequency “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW3 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW3 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and ended on November 29, 2017, when SW3 completed its mitigation activities. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW3 produced a relatively small amount of power, with a maximum nameplate rating of 129 MW and a 36% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the wind generation Facilities at issue have never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the frequency trip settings for SW3’s wind generation Facilities were set such that the changes to the relays required adjusting turbine overfrequency settings by 0.8 Hz and underfrequency settings by 1.5 Hz at a 0.20 second time setting, as well as adjusting the overfrequency substation relay settings by 1.3 Hz at a 0.35 second time setting and the underfrequency substation relay settings by 0.8 Hz at a 30.1 second time setting to comply with the requisite trip zone settings. Despite these required changes, however, SW3 had no operational issues from these incorrect settings. No harm is known to have occurred. Texas RE considered SW3’s and its affiliates' PRC-024-2 R1 compliance history in determining the disposition track. SW3 has no relevant prior instances of noncompliance. However, a SW3 affiliate has one relevant prior noncompliance record involving PRC-024-2 R1 (SPP2016016224). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW3 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016224 (PRC-024-2 R1) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the frequency protective relays at its wind farm were set such that its generators would not trip when system frequency was within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW3: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; 7) retained a new director of regulatory compliance that now reports directly to SW3’s Chief Operating Officer. 8) documented any relays that could not be reset due to equipment limitations; 9) communicated its relay settings and any known equipment limitations to its TP and PC; and 10) reprogrammed its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2017016950 | PRC-024-2 | R2 | On February 7, 2017, SW3 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. In particular, SW3 did not set its protective relays such that its generator voltage protective relaying would not trip applicable generating units as a result of a voltage excursion within the “no trip zone” set forth in PRC-024 Attachment 2. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW3 personnel discovered that it had not evaluated the relay settings for its two generation Facilities by the July 1, 2016 deadline. Following this discovery, SW3 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW3 discovered that several of its generator voltage protective relays were set to operate within the voltage “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW3 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW3 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and ended on November 29, 2017, when SW3 completed its mitigation activities. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW3 produced a relatively small amount of power, with a maximum nameplate rating of 129 MW and a 36% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the wind generation Facilities at issue have never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the generator voltage trip settings for SW3’s wind generation Facilities were set such that changes to the relays required increasing the turbine overvoltage settings from 110 to 117.5% and reducing the turbine undervoltage settings from 90 to 45% at a 0.20 second time delay, as well as reducing the substation undervoltage settings from 70 to 65% at a 1.50 second time delay to comply with the requisite trip zone settings. No harm is known to have occurred. Texas RE considered SW3’s and its affiliates' PRC-024-2 R2 compliance history in determining the disposition track. SW3 has no relevant prior instances of noncompliance. However, a SW3 affiliate has one relevant prior noncompliance record involving PRC-024-2 R2 (SPP2016016226). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW3 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016226 (PRC-024-2 R2) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the protective relays at its wind farm were set such that its generators would not trip when system voltage was within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW3: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; 7) retained a new director of regulatory compliance that now reports directly to SW3’s Chief Operating Officer. 8) documented any relays that could not be reset due to equipment limitations; 9) communicated its relay settings and any known equipment limitations to its TP and PC; and 10) reprogrammed its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2017016959 | PRC-024-2 | R1 | On February 7, 2017, SW4 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. In particular, SW4 failed to set its frequency protective relays such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW4 personnel discovered that it had not evaluated the relay settings for its three generation Facilities by the July 1, 2016 deadline. Following this discovery, SW4 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW4 discovered that several of its generator frequency protective relays were set to operate within the frequency “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW4 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW4 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and will end when SW4 either sets its frequency protective relays to not trip within the “no trip zone” or documents any relays that cannot be reset due to equipment limitations and communicates that information to its Transmission Planner (TP) and Planning Coordinator (PC). | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW4 produced a relatively small amount of power, with a maximum nameplate rating of 240 MW and a 34% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the wind generation Facilities at issue have never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the frequency trip settings for SW4’s wind generation Facilities were set such that the changes to the relays required adjusting overfrequency turbine relay settings by 0.8 Hz at a 0.30 second time setting, as well as the overfrequency and underfrequency turbine relay settings by 0.1 Hz at a 3600.00 time setting to comply with the requisite trip zone settings. Despite these required changes, however, SW4 had no operational issues from these incorrect settings. No harm is known to have occurred. Texas RE considered SW4’s and its affiliates' PRC-024-2 R1 compliance history in determining the disposition track. SW4 has no relevant prior instances of noncompliance. However, a SW4 affiliate has one relevant prior noncompliance record involving PRC-024-2 R1 (SPP2016016224). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW4 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016224 (PRC-024-2 R1) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the frequency protective relays at its wind farm were set such that its generators would not trip when system frequency was within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW4: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; and 7) retained a new director of regulatory compliance that now reports directly to SW4’s Chief Operating Officer. Furthermore, SW4 will complete the following actions by December 30, 2017: 1) document any relays that cannot be reset due to equipment limitations; 2) communicate its relay settings and any known equipment limitations to its TP and PC; and 3) reprogram its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2017016961 | PRC-024-2 | R2 | On February 7, 2017, SW4 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. In particular, SW4 did not set its protective relays such that its generator voltage protective relaying would not trip applicable generating units as a result of a voltage excursion within the “no trip zone” set forth in PRC-024 Attachment 2. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW4 personnel discovered that it had not evaluated the relay settings for its three generation Facilities by the July 1, 2016 deadline. Following this discovery, SW4 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW4 discovered that several of its generator voltage protective relays were set to operate within the voltage “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW4 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW4 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and will end when SW4 either sets its voltage protective relays to not trip within the “no trip zone” or documents any relays that cannot be reset due to equipment limitations and communicates that information to its Transmission Planner (TP) and Planning Coordinator (PC) as required. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW4 produced a relatively small amount of power, with a maximum nameplate rating of 240 MW and a 34% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the wind generation Facilities at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the generator voltage trip settings for SW4’s wind generation Facilities were set such that changes to the relays required changing the turbine undervoltage settings to not trip at a 0.10 second time delay, as well as reduce turbine undervoltage settings by as much 25% at time delays between 0.15 and 0.50 seconds to comply with the requisite trip zone settings. No harm is known to have occurred. Texas RE considered SW4’s and its affiliates' PRC-024-2 R2 compliance history in determining the disposition track. SW4 has no relevant prior instances of noncompliance. However, a SW4 affiliate has one relevant prior noncompliance record involving PRC-024-2 R2 (SPP2016016226). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW4 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016226 (PRC-024-2 R2) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the protective relays at its wind farm were set such that its generators would not trip when system voltage was within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW4: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; and 7) retained a new director of regulatory compliance that now reports directly to SW4’s Chief Operating Officer. Furthermore, SW4 will complete the following actions by December 30, 2017: 1) document any relays that cannot be reset due to equipment limitations. 2) communicate its relay settings and any known equipment limitations to its TP and PC; and 3) reprogram its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 5 LLC (SW5) | NCR02715 | TRE2017016965 | PRC-024-2 | R1 | On February 7, 2017, SW5 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R1. In particular, SW5 failed to set its frequency protective relays such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW5 personnel discovered that it had not evaluated the relay settings for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW5 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW5 discovered that several of its generator frequency protective relays were set to operate within the frequency “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW5 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW5 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R1 became mandatory and enforceable, and will end when SW5 either sets its frequency protective relays to not trip within the “no trip zone” or documents any relays that cannot be reset due to equipment limitations and communicates that information to its Transmission Planner (PC) and Planning Coordinator (PC). | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW5 produced a relatively small amount of power, with a maximum nameplate rating of 79 MW and a 34% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the frequency trip settings for SW5’s single wind generation Facility were set such that the changes to the relays required adjusting underfrequency and overfrequency turbine relay settings by 0.1 Hz respectively at a 3600.00 second time delay to comply with the requisite trip zone settings. Despite these required changes, however, SW5 had no operational issues from these incorrect settings. No harm is known to have occurred. Texas RE considered SW5’s and its affiliates' PRC-024-2 R1 compliance history in determining the disposition track. SW5 has no relevant prior instances of noncompliance. However, a SW5 affiliate has one relevant prior noncompliance record involving PRC-024-2 R1 (SPP2016016224). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW5 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016224 (PRC-024-2 R1) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the frequency protective relays at its wind farm were set such that its generators would not trip when system frequency was within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW5: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; and 7) retained a new director of regulatory compliance that now reports directly to SW5’s Chief Operating Officer. Furthermore, SW5 will complete the following actions by December 30, 2017: 1) document any relays that cannot be reset due to equipment limitations; 2) communicate its relay settings and any known equipment limitations to its TP and PC; and 3) reprogram its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-12-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 5 LLC (SW5) | NCR02715 | TRE2017016966 | PRC-024-2 | R2 | On February 7, 2017, SW5 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-024-2 R2. In particular, SW5 did not set its protective relays such that its generator voltage protective relaying would not trip applicable generating units as a result of a voltage excursion within the “no trip zone” set forth in PRC-024 Attachment 2. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW5 personnel discovered that it had not evaluated the relay settings for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW5 personnel took steps to retain a third-party contractor to evaluate its generator frequency protective relays and generator voltage protective relays. In May 2017, following the conclusion of the third-party engineering firm’s assessment, SW5 discovered that several of its generator voltage protective relays were set to operate within the voltage “no trip zone.” The root cause of this noncompliance was insufficient internal controls to ensure SW5 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW5 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when PRC-024-2 R2 became mandatory and enforceable, and will end when SW5 either sets its voltage protective relays to not trip within the “no trip zone” or documents any relays that cannot be reset due to equipment limitations and communicates that information to its Transmission Planner (TP) and Planning Coordinator (PC) as required. | This noncompliance posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW5 produced a relatively small amount of power, with a maximum nameplate rating of 79 MW and a 34% capacity factor for the period from July 1, 2016 through July 1, 2017. Second, the single wind generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” In particular, the generator voltage trip settings for SW5’s single wind generation Facility were set such that changes to the relays required changing the turbine undervoltage settings to not trip at a 0.10 second time delay, as well as reduce turbine undervoltage settings from 80 to 75% at a 2.00 second time delay to comply with the requisite trip zone settings. No harm is known to have occurred. Texas RE considered SW5’s and its affiliates' PRC-024-2 R2 compliance history in determining the disposition track. SW5 has no relevant prior instances of noncompliance. However, a SW5 affiliate has one relevant prior noncompliance record involving PRC-024-2 R2 (SPP2016016226). Texas RE determined that this prior instance of noncompliance should not serve as an aggravating factor because the previous issue occurred concurrently with this noncompliance. Furthermore, the previous noncompliance involved the same root cause. As a result, Caprock Wind, LLC and SW5 have completed or will complete similar mitigating activities to help prevent recurrence. Affiliate Compliance History SPP2016016226 (PRC-024-2 R2) for Caprock Wind, LLC (NCR05059) – This prior noncompliance also related to the entity’s failure to verify that the protective relays at its wind farm were set such that its generators would not trip when system voltage was within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new NERC Reliability Standard and a lack of managerial oversight. | To mitigate this noncompliance, SW5: 1) notified its TP of its current (noncompliant) relay settings; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 3) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 4) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 5) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; 6) conducted training on the new documented internal compliance programs for all personnel with NERC compliance related duties; and 7) retained a new director of regulatory compliance that now reports directly to SW5’s Chief Operating Officer. Furthermore, SW5 will complete the following actions by December 30, 2017: 1) document any relays that cannot be reset due to equipment limitations. 2) communicate its relay settings and any known equipment limitations to its TP and PC; and 3) reprogram its generator frequency and generator voltage protective relays to adhere to the criteria established in PRC-024.
2017-11-30 | Midwest Reliability Organization (MRO) | Minnesota Municipal Power Agency (MMPA) | NCR01012 | MRO2016016115 | PRC-005-1b | R2 | On August 10, 2016, MMPA submitted a Self-Report stating that, as a Distribution Provider and Generator Owner, it had an issue with PRC-005-1b R2. As part of an internal review, MMPA discovered that it did not have five year test records for a relay at the Minnesota River Station generator (MRS). MMPA contracts with another registered entity to test some of its protection system components, including this relay. That registered entity assured MMPA that the relay had been tested within the five-year interval, but was unable to document that the testing had occurred. MMPA hired a third-party consultant to perform a comprehensive review of all test records, and that comprehensive review uncovered another device at the MRS that did not have up to date test records. Due to the need to schedule an outage, completion of testing for the remaining device at the MRS may not be performed until October 31, 2018. The cause of the noncompliance was MMPA's reliance upon the registered entity that it contracted with, and a lack of diligence to verify the testing had occurred. This issue began on June 17, 2013, five years after the last documented test of the relay, and is expected to end on or before October 31, 2018, when it completes testing on the second device at the MRS. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the noncompliance was limited to only two BES devices, which MMPA verified through a third-party consultant retained to perform a comprehensive review of all test records to detect similar noncompliance. The potential risk is also reduced as the MRS only has a 50 MVA nameplate rating and MMPA's protection systems cannot trip networked BES facilities at or above 200 kV. Finally, MMPA's transmission facilities are not part of an IROL, RAS, cranking path, nor identified as Black start units. No harm is known to have occurred. MMPA has no relevant history of noncompliance. | To mitigate this issue, MMPA: 1) tested one of the devices on May 3, 2016; 2) discussed the issue with the registered entity that performs the testing, who agreed to providing maintenance and test records to MMPA within 30 days of test completion; 3) retained a consultant who performed a comprehensive review of all relay test records; 4) added all equipment that is tested by a third party to MMPA's asset management software system; and 5) ensured that the second device is scheduled for testing; the testing cannot occur until a new substation is constructed, energized, and an outage can occur; MMPA believes that testing will be complete on or before October 31, 2018. MMPA stated that all mitigating activities will be completed by October 31, 2018.
2017-11-30 | Midwest Reliability Organization (MRO) | Rochester Public Utilities (RPU) | NCR01027 | MRO2017017919 | COM-001-2.1 | R9 | During a Compliance Audit conducted from June 20, 2016 through June 22, 2016, MRO determined that RPU, as a Transmission Operator, had an issue with COM-001-2.1 R9. The noncompliance related to RPU's failure to test its Alternative Interpersonal Communication capability. RPU designated satellite phones as its Alternative Interpersonal Communication device under the Standard and Requirement. RPU was unable to provide evidence of required monthly testing for two of the seven calendar months between the effective date of the Standard and the Compliance Audit. The Standard became mandatory and enforceable on November 13, 2015. The two months that RPU could not supply testing records for are December 2015 and April 2016. The noncompliance was caused by a lack of internal controls such as procedures and training on the testing of the satellite phones. This issue started on January 1, 2016, when RPU missed testing in December 2015, and ended on May 1, 2016, when RPU conducted a monthly test in May 2016 after missing testing in April 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RPU provided documentation of successful testing for five of the seven months, and there is no evidence that the satellite phones were not functional during the period of noncompliance. Additionally, RPU's Reliability Coordinator initiates the monthly tests, meaning that it is possible that the tests occurred, but RPU failed to document the testing. Further, RPU's potential impact to the BPS is limited. RPU has a 161 kV transmission system that primarily distributes power to the city of Rochester, and it does not have any IROLs, Blackstart Resources, or Cranking Paths, meaning that its impact to the BPS outside of its footprint is limited. No harm is known to have occurred. RPU has no relevant history of noncompliance with COM-001-2.1 R9. | To mitigate this issue, RPU: 1) trained its System Operators to enter the satellite phone tests into the System Operation's Daily Log; 2) trained its System Operators to initiate the tests with its Reliability Coordinator on or in the days immediately prior to the 15th of the month, if the Reliability Coordinator had not already initiated a test; 3) added a monthly task as an internal control that alerts on the 16th of the month, for the supervisor of the System Operators to review the Daily Log to ensure testing has been completed; and 4) provided evidence that its internal controls are functioning through successful log entries of tests for the months of October, November, and December 2016.
2017-11-30 | Midwest Reliability Organization (MRO) | Rochester Public Utilities (RPU) | NCR01027 | MRO2017017920 | EOP-005-2 | R4 | During a Compliance Audit conducted from June 20, 2016 through June 22, 2016, MRO determined that RPU, as a Transmission Operator, had an issue with EOP-005-2 R4. Specifically, RPU did not update its restoration plan prior to implementing a planned BES modification (the energization of a 161 kV Transmission Line) that changed the implementation of its restoration plan. RPU also failed to submit its revised restoration plan to its Reliability Coordinator for approval. RPU updated its restoration plan on May 24, 2016 in response to receiving an RSAW from MRO, and RPU sent its updated restoration plan to its Reliability Coordinator on June 17, 2016 in response to a pre-audit request for information from MRO. The cause of the noncompliance was a lack of controls associated with BES modifications and the updating of its restoration plan. The noncompliance began on January 25, 2016, when RPU did update its restoration plan prior the energization of the Transmission Line, and ended on June 17, 2016, when RPU sent its updated restoration plan to its Reliability Coordinator. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RPU participates annually in its Reliability Coordinator's system restoration drills, increasing the likelihood that System Operators would adequately respond to challenges during restoration. Further, RPU's 161 kV transmission system primarily distributes power to the city of Rochester, meaning that its impact to the BPS outside of its footprint is limited. Finally, none of RPU's neighboring entities rely on RPU for support during restoration activities, and RPU does not have any restoration facilities, such as Blackstart Resources, or Cranking Paths. No harm is known to have occurred. RPU has no relevant history of noncompliance with EOP-005-2 R4. | To mitigate this issue, RPU: 1) updated its restoration plan and sent the updated restoration plan to its Reliability Coordinator; and 2) provided training to its System Operators on the need to review and if necessary, update the restoration plan 90 days prior to energizing a planned BES modification.
2017-11-30 | Midwest Reliability Organization (MRO) | Rochester Public Utilities (RPU) | NCR01027 | MRO2017017921 | EOP-005-2 | R6 | During a Compliance Audit conducted from June 20, 2016 through June 22, 2016, MRO determined that RPU, as a Transmission Operator, had an issue with EOP-005-2 R6. RPU did not verify, through analysis of actual events or testing, that its restoration plan can accomplish its intended function. RPU does participate in its Reliability Coordinator's system restoration drills, but those drills do not verify all the data required by R6, such as a calculation of power flows, which is necessary to verify that the location and magnitude of RPU's loads and the capability of RPU's generation resources could control voltage and frequency within acceptable operating limits. The cause of the noncompliance was RPU's failure to understand the scope of its obligations under the Standard and Requirement, as it believed that its participation in the Reliability Coordinator's restoration drills were sufficient to meet its obligations with EOP-005-2 R6. The noncompliance began on July 1, 2013, when the Standard and Requirement became mandatory and enforceable, and will end when RPU verifies that its restoration plan can accomplish its intended function. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While the Reliability Coordinator's drills does not calculate power flows, it does calculate generation and spinning reserves, partially fulfilling the obligations of the Requirement. Additionally, RPU participates annually in its Reliability Coordinator's system restoration drills, increasing the likelihood that System Operators would be prepared to respond to challenges during restoration. Further, RPU's 161 kV transmission system primarily distributes power to the city of Rochester, meaning that its impact to the BPS outside of its footprint is limited. Finally, none of RPU's neighboring entities rely on RPU for support during restoration activities and RPU does not have any restoration facilities, such as Blackstart Resources or Cranking Paths. No harm is known to have occurred. RPU has no relevant history of noncompliance with EOP-005-2 R6. | To mitigate this violation, RPU will: 1) participate in its Reliability Coordinator's system restoration drill; 2) have its subject matter experts perform a table top exercise during that drill to evaluate its restoration plan against the results of the Reliability Coordinator's simulation. This evaluation will include an evaluation of RPU system voltages, frequency, generation resource capabilities, and whether acceptable operating limits are maintained; 3) have its System Operators sign a training log sheet establishing they participated in the table top exercise; 4) will develop a table top exercise process document and evaluation criteria that outlines a checklist of steps to be performed during its Reliability Coordinator's annual system restoration drill to evaluate RPU's restoration plan against the results of its Reliability Coordinator's simulation; and 5) have its subject matter experts determine if the Reliability Coordinator's simulation meets the requirements of EOP-005-2 R6. If it does not meet the requirements of the Standard and Requirement, RPU will run a software simulation and/or additional evaluation of its restoration plan. RPU has submitted a Mitigation Plan, that MRO accepted, with a completion date of January 17, 2018.
2017-11-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2017017745 | PRC-024-2 | R2. | On June 19, 2017, Noble Wethersfield Windpark, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R2. Specifically, the Entity failed to implement voltage relay settings that would ensure that its generator voltage protective relaying does not trip its generating facilities within the no trip zone of PRC-024-2 Attachment 2. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on April 5, 2017, when the Entity implemented required voltage relay settings for its generating assets to ensure its compliance with the standard/requirement. The root cause of this instance of noncompliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its Wethersfield Windpark facility needed to be 100% compliant with the standard and requirement by 7/1/2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 24%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 126 MW, which is less than 6.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For both devices, the change implemented to make the old settings compliant with the standard/requirement was to increase the time delay from the existing 1 second (60 cycles) to 3.5 seconds (210 cycles). The change enables both relays to trip the generating unit(s) outside of the no trip-zone (Attachment 2 of the standard). No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by implementing required voltage relay settings for its generating assets; 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-11-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Emera, Maine | NCR07013 | NPCC2017016855 | PRC-006-NPCC-1 | R4. | On January 18, 2017, Emera, Maine (the Entity) submitted a Self-Report stating that, as a Distribution Provider (DP) and Transmission Owner (TO), it was in noncompliance with PRC-006-NPCC-1 R4. Specifically, the Entity discovered that its 2017 UFLS program capability was out of compliance with the required automatic load shedding levels for Steps 2 and 4, which in turn caused the entire program to also be out-of-compliance with NERC Reliability Standard PRC-006-NPCC-1 Attachment C, UFLS Table 1. This noncompliance started on January 1, 2017, when the Entity's noncompliant 2017 UFLS program was initially implemented, and ended on April 12, 2017, when the Entity completed testing of the new relay settings for its rebalanced 2017 UFLS program. The root cause of this instance of noncompliance was the permanent retirement, in 2017, of a large industrial load (a paper mill with a peak load of 12-17 MW range) that lowered overall system peak by approximately 5% and caused the existing UFLS program's cumulative load shedding capability, in the last step, to be deficient by approximately the same percentage relative to the amount required by the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The total load shedding deficiency of the Entity's UFLS program was approximately 12 MWs, a relatively small amount compared with the Entity's annual system peak load, which ranges from 265 to 275 MW. Additionally, the Entity's RC's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. In conclusion, the Entity's UFLS program's temporary deficiency could have been rectified in real-time by operating personnel during a load shedding event. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by rebalancing its UFLS program; and 2) to prevent a recurrence of similar instances of noncompliance, re-designed its UFLS program so that it no longer includes single large loads the magnitude of the retired mill load. NPCC has verified the completion of all mitigation activity.
2017-11-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Green Mountain Power Corporation | NCR07103 | NPCC2017017082 | PRC-006-NPCC-1 | R13. | On February 21, 2017, Green Mountain Power Corporation (the Entity) submitted a Self-Certification stating that, as a Generator Owner (GO), it was in noncompliance with PRC-006-NPCC-1 R13. Specifically, the Entity discovered that the frequency relay settings for its Ascutney GT generator's single relay were not in compliance with PRC-006-NPCC-1, R13 (Figure 1). This noncompliance started on July 1, 2016, when the Entity's activities to achieve compliance with the frequency requirements of standard PRC-024-2 caused an inadvertent noncompliance with PRC-006-NPCC-1 R13, and ended on January 25, 2017, when the Entity implemented new under-frequency settings that were compliant with both aforementioned standards. The root cause of this instance of noncompliance was the Entity's failure to verify that frequency settings for its generator's single relay simultaneously satisfy the trip-curves of both PRC-006-NPCC-1 and the continent-wide standard PRC-024-2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's non-compliant asset is a 13.5 MVA Blackstart resource in ISO-NE’s System Restoration Plan and only runs on an as-needed basis, upon ISO-NE's request. During the period on noncompliance (approximately seven months), the unit had a total runtime of approximately 31 hours (strictly peak-load operation). Additionally, the Entity's RC's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. In conclusion, the Entity's temporary noncompliance could have been rectified in real-time by operating personnel during a frequency event. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by implementing new under/over-frequency settings that are compliant with both PRC-006-NPCC-1 and the continent-wide standard PRC-024-2; and 2) to prevent a recurrence of similar instances of noncompliance, with the help of an outside Engineering Consultant, will perform periodic reviews of all applicable PRC Standards that require relay settings verification/updates. NPCC has verified the completion of all mitigation activity.
2017-11-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Wallingford Energy LLC | NCR11102 | NPCC2017018529 | MOD-025-2 | R2. | On October 31, 2017, Wallington Energy, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. Specifically, while populating an internal compliance tracking tool, the Entity discovered that the facility where its generating assets are located had provided only partial information to its Transmission Planner (ISO-NE) for compliance with MOD-025-2 Attachment 2 Reactive Power testing. This noncompliance started on July 1, 2016, the enforcement date of the standard & requirement, and ended on September 6, 2017, when the Entity performed a verification of the Reactive Power Capability of its applicable generating facilities, and subsequently submitted, within the required 90 days, all testing results to its Transmission Planner, as required by the standard and requirement. The root cause of this instance of noncompliance was the Entity's failure to timely recognize that full compliance with the standard & requirement consisted in gathering a significant amount of additional data (such as Humidity, Transformer Tap Settings and Voltage Ratio) above and beyond similar, but less comprehensive, reactive power tests that the facility had completed in 2012, four years prior to the enforcement date of the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's three non-compliant assets are each rated at 45 MVA, and their capacity factors ranged from 8.7% to 12.32% in 2016, and from 6.67% to 7.46 in 2017, to date. Additionally, the Entity's RC's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. There's a corresponding amount of reactive capability associated with these (MW) reserves that is determined by individual (on-reserve) generators' capability curves. The RC has comparable summer operating reserves requirements. In conclusion, the Entity's temporary noncompliance, consisting of an incomplete verification test of its units' reactive capabilities, could have been mitigated in real-time by operating personnel during an event requiring dispatch of system reactive resources. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by performing a verification of the Reactive Power Capability of its applicable generating facilities, and submitting, within the required 90 days, all testing results to its Transmission Planner; and 2) to prevent a recurrence of similar instances of noncompliance: (i) has created a NERC Preventive Maintenance (PM) task in its computerized maintenance management system that more clearly defines the conditions under which the Real and Reactive Power tests must be performed and their frequency; and (ii) has provided supplemental training on the noncompliance to the operating staff responsible for the testing . NPCC has verified the completion of all mitigation activity.
2017-11-30 | Northeast Power Coordinating Council, Inc. (NPCC) | Waterbury Generation, LLC | NCR10339 | NPCC2017018055 | PRC-006-NPCC-1 | R13. | On July 28, 2017, Waterbury Generation, LLC (the Entity) submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-006-NPCC-1 R13. Specifically, the Entity discovered that the frequency relay settings for its Waterbury generating unit were not in compliance with under-frequency trip settings of PRC-006-NPCC-1, R13 (Figure 1). This noncompliance started on July 1, 2015, the enforcement date of the standard & requirement, and ended on September 23, 2017, when the Entity implemented new under-frequency relay settings that are compliant with the standard and requirement. The root cause of this instance of noncompliance was the Entity's reliance on GE Energy, Aero Energy Division’s Position Paper #45 Rev B (dated January 1st , 2013), which states that GE aero LM gas turbine generator protection system includes under and over frequency detection (which would result in alarm only), and that trip or shutdown of gas turbine is not required per GE design practices and is in accordance to industry standards. The Entity later confirmed with the generator OEM, Brush, that set-point adjustment required by the standard would be within the design parameters of the generator set, and proceeded to implement necessary relay settings changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Entity's non-compliant asset is a 100 MVA simple cycle plant that provides peaking energy to the New England power market. For example, this generating unit was operated at a capacity factor of 4.7% in 2016. Additionally, the Entity's RC's (ISO-NE) required winter operating reserves are approximately 2600 MWs, a value which is often exceeded by a margin of about 2000 MW above that requirement. In conclusion, the Entity's temporary noncompliance could have been rectified in real-time by operating personnel during a frequency event. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined that there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by implementing new under-frequency relay settings that are compliant with the standard and requirement; and 2) to prevent a recurrence of similar instances of noncompliance, has entered Preventative Maintenance orders (PMs) in its Computerized Maintenance Management system that automatically generate Work Orders based on appropriate implementation dates that have been entered in the PMs to ensure compliance with NERC Standards. NPCC has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Baltimore Gas and Electric Company (BGE) | NCR00689 | RFC2017017410 | PRC-005-1 | R2 | On April 6, 2017, BGE submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it was in noncompliance with PRC-005-1 R2. On February 1, 2017, as part of a review of vented lead-acid battery system quarterly test results, BGE determined that it had failed to conduct quarterly inspections for unintentional grounds on one specific battery system since March 29, 2007, when a new battery charger was installed to support the subject battery system. The old battery charger (i.e., the one in place prior to March 29, 2007) had a built-in metering function for measuring unintentional grounds. Consequently, the relevant information was readily available to the vendor responsible for performing the necessary inspections, who properly recorded the information. However, the replacement battery charger did not have this built-in metering function for measuring unintentional grounds. Therefore, when the vendor attempted to perform the inspection for unintentional grounds during the first post-installation quarterly battery inspection, he simply marked “N/A” on the results sheet because the information was not readily available. The vendor continued making this “N/A” notation on all subsequent quarterly inspection sheets through Q4 2016. The root cause of this noncompliance was the fact that the vendor did not understand that he had to obtain the measurement data by other means. Another factor contributing to the cause of this noncompliance was BGE’s failure to verify the inspection results and question why the vendor was marking “N/A.” These major contributing factors involve the management practices of verification, which involves establishing verification procedures and criteria, external interdependencies, which includes managing external entity performance, and grid maintenance, which includes monitoring maintenance performance. This noncompliance started on July 1, 2007, when BGE was required to have completed the Q2 2007 battery inspections and ended on February 1, 2017, when BGE completed the required inspections. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The subject battery system is located in a non-BPS (local distribution) station. Therefore, the only direct harm that could result from this noncompliance would be the interruption of non-BPS power flow in the presence of multiple battery grounds, causing tripping of remote BPS breakers. This risk is mitigated by the fact that the primary and backup protection systems installed to detect faults on the remote BPS terminals are supplied from independently fused DC control circuits. ReliabilityFirst also notes that BGE has not observed any actual impacts to the BPS caused by unintentional grounds on the subject battery system. Furthermore, the test results of the inspection for unintentional grounds conducted on February 1, 2017, were within acceptable thresholds for positive and negative grounding values. No harm is known to have occurred. ReliabilityFirst considered BGE's PRC-005 R2 compliance history in determining the disposition track. BGE’s relevant prior noncompliance with PRC-005 R2 includes: RFC200900123. A Settlement Agreement covering a violation of PRC-005-1 R2.1, 2.2 was filed with FERC under NP10-150-000 on July 30, 2010. On August 27, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. The prior violation is distinguishable from the instant noncompliance because the prior violation was related to BGE’s efforts to transition its Protection System Maintenance and Testing Program to accommodate ReliabilityFirst’s clarified definition of the Bulk Electric System (BES). When brining new elements into the program, BGE failed to include a total of eight protection systems. The current noncompliance, on the other hand, was not related to ReliabilityFirst’s clarified BES definition. Rather, it involved a vendor’s failure to perform one specific inspection on one particular battery system. ReliabilityFirst determined that BGE’s compliance history should not serve as a basis for applying a penalty. | To mitigate this noncompliance, BGE: 1) inspected the subject battery system for unintentional grounds; 2) provided comprehensive training and guidance to BGE’s battery testing vendor on PRC-005-6 battery system maintenance requirements and BGE’s Protection System Maintenance Program as it applies to battery system maintenance; 3) upgraded the battery test documentation form to highlight test data fields that are PRC-005-6 compliance requirements; and 4) developed a sufficient battery system compliance testing evidence review process that has achieved all required approvals. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Elgin Energy Center, LLC (Elgin) | NCR11437 | RFC2016015901 | MOD-025-2 | R1 | On July 11, 2016, Elgin submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Elgin Energy Center did not complete its Real Power testing and did not provide its Transmission Planner with the verification of Elgin’s Real Power capability of its applicable Facilities by the July 1, 2016 enforcement date for MOD-025-2 R1. While conducting a mock audit in July 2016, Elgin and its contractor conducting the mock audit discovered that Elgin misinterpreted the MOD-025-2 Standard and Requirements. Elgin incorrectly believed that because its MOD-025-2 data did not change, it did not need to submit data again to its Transmission Planner. During that same mock audit, Elgin’s contractors explained to Elgin that it needed to conduct new testing and that the results should be submitted by the enforcement date for at least two generators (40%) per the implementation plan for MOD-025-2 R1. Elgin hired an engineering firm (Kestrel) to conduct the testing on behalf of Elgin. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Elgin compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is Elgin’s failure to effectively plan for the July 1, 2016 effective date for MOD-025-2. This issue started on July 1, 2016, when Elgin was required to comply with MOD-025-2 R1 and ended on January 24, 2017, when Elgin completed its Mitigation Plan by completing the necessary testing and sending the results of the testing to its Transmission Planner. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Elgin quickly identified and corrected this noncompliance. Lastly, Elgin contributes approximately 484 MWs to the grid and operated at approximately a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Elgin’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Elgin selected Kestrel Engineering to perform its Real Power Testing to verify output. Elgin Energy Center now understands the requirements of MOD-025 and has developed a plant procedure which demonstrates the verification type and periodicity which Real and Reactive Power Capability Testing must be completed. The procedure also ensures that Elgin Energy Center completes Attachment 2 of the standard and submits the necessary data within the specified timeframe. Elgin also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Elgin Energy Center will also rely on outside mock audits and internal self-assessments to prevent the probability of this violation happening again. Bi-weekly compliance calls are held to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Elgin Energy Center, LLC (Elgin) | NCR11437 | RFC2016015902 | MOD-025-2 | R2 | On July 11, 2016, Elgin submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Elgin Energy Center did not complete its Real Power testing and did not provide its Transmission Planner with the verification of Elgin’s Real Power capability of its applicable Facilities by the July 1, 2016 enforcement date for MOD-025-2. While conducting a mock audit in July 2016, Elgin and its contractor conducting the mock audit discovered that Elgin misinterpreted the MOD-025-2 Standard and Requirements. Elgin incorrectly believed that because its MOD-025-2 data did not change, it did not need to submit data again to its Transmission Planner. During that same mock audit, Elgin’s contractors explained to Elgin that it needed to conduct new testing and that the results should be submitted by the enforcement date for at least two generators (40%) per the implementation plan for MOD-025-2. Elgin hired an engineering firm (Kestrel) to conduct the testing on behalf of Elgin. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Elgin compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is Elgin’s failure to effectively plan for the July 1, 2016 effective date for MOD-025-2. This issue started on July 1, 2016, when Elgin was required to comply with MOD-025-2 R2 and ended on January 24, 2017, when Elgin completed its Mitigation Plan by completing the necessary testing and sending the results of the testing to its Transmission Planner. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Elgin quickly identified and corrected this noncompliance. Lastly, Elgin contributes approximately 484 MWs to the grid and operated at approximately a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Elgin’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Elgin selected Kestrel Engineering to perform its Reactive Power Testing. Elgin Energy Center now understands the requirements of MOD-025 and has developed a plant procedure which demonstrates the verification type and periodicity which Real and Reactive Power Capability Testing must be completed. The procedure also ensures that Elgin Energy Center completes Attachment 2 of the standard and submits the necessary data within the specified timeframe. Elgin also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Elgin Energy Center will also rely on outside mock audits and internal self-assessments to prevent the probability of this violation happening again. Bi-weekly compliance calls are held to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Elgin Energy Center, LLC (Elgin) | NCR11437 | RFC2016016051 | PRC-019-2 | R1 | On August 19, 2016, Elgin submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Elgin did not perform the applicable coordination and did not perform the required verification of current data by a third party by the July 1, 2016 implementation date for PRC-019-2 R1. While conducting a mock audit in July 2016, Elgin and its contractor conducting the mock audit discovered that Elgin misinterpreted the PRC-019-2 Standard and Requirements. Elgin incorrectly believed that its existing documentation and data were sufficient to show compliance. After further examining the existing documentation and data, however, Elgin discovered that it needed to perform a verification. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Elgin compliance staff failed to interpret and implement PRC-019-2 correctly. A root cause of this noncompliance is Elgin’s failure to effectively plan for the July 1, 2016 effective date for PRC-019-2. This issue started on July 1, 2016, when Elgin was required to comply with PRC-019-2 R1 and ended on January 19, 2017, when Elgin completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because when Elgin performed the verification and coordination, no changes were required. Additionally, Elgin quickly identified and corrected this noncompliance. Lastly, Elgin contributes approximately 484 MWs to the grid and operated at approximately a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Elgin’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Elgin: 1) contracted an engineering firm to perform the verification of the data necessary to confirm compliance; and 2) drafted a procedure to assure ongoing compliance. Elgin will review documentation periodically as well as directing coordination of settings every five years. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Elgin Energy Center, LLC (Elgin) | NCR11437 | RFC2016016052 | PRC-019-2 | R2 | On August 19, 2016, Elgin submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R2. Elgin did not perform the applicable coordination and did not perform the required verification of current data by a third party by the July 1, 2016 implementation date for PRC-019-2 R2. While conducting a mock audit in July 2016, Elgin and its contractor conducting the mock audit discovered that Elgin misinterpreted the PRC-019-2 Standard and Requirements. Elgin incorrectly believed that its existing documentation and data were sufficient to show compliance. After further examining the existing documentation and data, however, Elgin discovered that it needed to perform a verification. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Elgin compliance staff failed to interpret and implement PRC-019-2 correctly. A root cause of this noncompliance is Elgin’s failure to effectively plan for the July 1, 2016 effective date for PRC-019-2. This issue started on July 1, 2016, when Elgin was required to comply with PRC-019-2 R2 and ended on January 24, 2017, when Elgin completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because when Elgin performed the verification and coordination, no changes were required. Additionally, Elgin quickly identified and corrected this noncompliance. Lastly, Elgin contributes approximately 484 MWs to the grid and operated at approximately a 5% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Elgin’s PRC-019 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Elgin: 1) contracted an engineering firm to perform the verification of the data necessary to confirm compliance; and 2) drafted a procedure to assure ongoing compliance. Elgin will review documentation periodically as well as directing coordination of settings every five years. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Elgin Energy Center, LLC (Elgin) | NCR11437 | RFC2017017629 | PRC-024-2 | R1 | On May 16, 2017, Elgin submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Elgin’s owner conducted a mock audit on another plant that it owns in July 2016. During this audit, the contractors running the audit identified that the other plant being audited misinterpreted PRC-024-2. Following from this discovery, Elgin’s owner evaluated Elgin’s understanding of PRC-024-2 and discovered that Elgin also misinterpreted PRC-024-2. Elgin realized that testing under MOD-025 needed to take place and coordinating documentation was needed so that verification could be completed under PRC-024. Under the MOD-025 implementation plan, at least two generators (40%) needed to be tested and the coordination studies needed to take place at Elgin. Elgin subsequently hired Kestrel Power Engineering to conduct the testing on Units 1-4 at Elgin and performed the verification under PRC-024. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Elgin compliance staff failed to interpret and implement PRC-024-2 correctly. A root cause of this noncompliance is Elgin’s failure to effectively plan for the July 1, 2016 effective date for PRC-024-2. This issue started on July 1, 2016, when Elgin was required to comply with PRC-024-2 R1 and ended on January 24, 2017, when Elgin completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because when Elgin performed the verification study, no changes were required. Lastly, Elgin contributes approximately 484 MWs to the grid and operated at approximately a 5% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Elgin’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Elgin: 1) conducted testing on all units; and 2) completed the required coordination study and submitted all relevant documentation. Elgin now understands the requirements of PRC-024 and has developed a plant procedure which demonstrates that coordination of protective relaying is crucial such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the "no trip zone" of PRC-024 Attachment 1, as well as when the coordination must take place. To prevent the probability of this violation happening again, Elgin will annually review the internal plant procedure, while also updating any standard revisions. Elgin also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Elgin will also utilize outside mock audits and internal self-assessments as a second check. Bi-weekly compliance calls are held to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Elgin Energy Center, LLC (Elgin) | NCR11437 | RFC2017017630 | PRC-024-2 | R2 | On May 16, 2017, Elgin submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Elgin’s owner conducted a mock audit on another plant that it owns in July 2016. During this audit, the contractors running the audit identified that the other plant being audited misinterpreted PRC-024-2. Following from this discovery, Elgin’s owner evaluated Elgin’s understanding of PRC-024-2 and discovered that Elgin also misinterpreted PRC-024-2. Elgin realized that testing under MOD-025 needed to take place and coordinating documentation was needed so that verification could be completed under PRC-024. Under the MOD-025 implementation plan, at least two generators (40%) needed to be tested and the coordination studies needed to take place at Elgin. Elgin subsequently hired Kestrel Power Engineering to conduct the testing on Units 1-4 at Elgin and performed the verification under PRC-024. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because Elgin compliance staff failed to interpret and implement PRC-024-2 correctly. A root cause of this noncompliance is Elgin’s failure to effectively plan for the July 1, 2016 effective date for PRC-024-2. This issue started on July 1, 2016, when Elgin was required to comply with PRC-024-2 R2 and ended on January 24, 2017, when Elgin completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is minimized because when Elgin performed the verification study, no changes were required. Lastly, Elgin contributes approximately 484 MWs to the grid and operated at approximately a 5% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Elgin’s PRC-024 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Elgin: 1) conducted testing on all units; and 2) completed the required coordination study and submitted all relevant documentation. Elgin now understands the requirements of PRC-024 and has developed a plant procedure which demonstrates that coordination of protective relaying is crucial such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the "no trip zone" of PRC-024 Attachment 1, as well as when the coordination must take place. To prevent the probability of this violation happening again, Elgin will annually review the internal plant procedure, while also updating any standard revisions. Elgin also has an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate, called Gensuite. Therefore, MOD-025/PRC-024 has been added with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies. Elgin will also utilize outside mock audits and internal self-assessments as a second check. Bi-weekly compliance calls are held to ensure plant staff are aware of upcoming deadlines and compliance obligations. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Midcontinent Independent System Operator, Inc. (MISO) | NCR00826 | RFC2017017416 | NUC-001-3 | R4 | On April 11, 2017, MISO submitted a Self-Report stating that, as a Reliability Coordinator, it was in noncompliance with NUC-001-3 R4. NUC-001-3 R4 requires MISO to incorporate Nuclear Plant Interface Requirements (NPIRs) into its operating analyses and to operate the electric system to meet those NPIRs. The Monticello Nuclear Generating Plant (The Monticello Nuclear Generating Plant is a boiling water reactor plant located on a 215-acre site 40 miles northwest of the Twin Cities in Minnesota. The Plant can generate 671 Megawatts.) is a facility in the MISO footprint that MISO has implemented NPIRs through a Nuclear Plant Operating Agreement (NPOA). Although most nuclear facilities have a set voltage limit described in the NPIRs and NPOAs, Monticello has voltage set points that vary depending on operating conditions. ( For the Monticello 115kV bus associated with this issue, adequate minimum voltage is either 115.6kV (when the plant electrical load is supplied by the preferred 345 kV source) or 116kV (when the plant electrical load is supplied by the alternate 115 kV source). Per the Monticello NPIR its 345kV minimal bus voltage is 342kV regardless which source is supplying the electrical load.) MISO’s contact with the plant is governed by the NPOA in effect, which lists roles and responsibilities among MISO, the nuclear plant generator owner, and transmission operator(s). Under normal conditions, MISO serves as the backup voltage monitor for Monticello and Northern States Power (Northern States Power is operated by Xcel Energy.) serves as the primary voltage monitor for this plant. On September 30, 2016, due to a transformer outage, operating staff at the Monticello nuclear power plant changed the plant's minimum voltage requirement from 115.6 kV to 116 kV for one 115 kV bus. There are three 345 kV lines connected to the Monticello substation and three 115 kV lines connected to the Monticello substation. Monticello operating staff returned the minimum voltage to 115.6 kV following restoration of the transformer to service on October 6, 2016. MISO, however, incorrectly implemented the October 6, 2016 minimum voltage requirement change. MISO’s incorrect implementation resulted in a monitored minimum voltage of 83 kV instead of the required 115.6 kV established by Monticello for one 115 kV bus. This incorrect condition remained in place from October 6, 2016 to October 13, 2016 when a MISO reliability engineer discovered the flawed monitoring setting while researching questions related to proposed NPOA revisions for the Monticello plant on October 13, 2016. Although MISO inputted the flawed setting on October 6, 2016, MISO was not the primary voltage monitor for Monticello per its NPOA from October 6, 2016 to October 12, 2016. (MISO’s contact with the plant is governed by the Nuclear Power Operating Agreement (NPOA) in effect, which lists roles and responsibilities among MISO, the nuclear plant generator owner, and transmission operator(s). The NPOA in effect did not require contact with the plant from MISO; instead the responsibility for communication, generally and specifically for this type of event, rests with the transmission operator, Northern States Power Company. Northern States Power Company informed Monticello of the loss of its RTCA tool pursuant to the NPOA.) Northern States Power, the primary local voltage monitor for Monticello, was the primary voltage monitor for Monticello per its NPOA from October 6, 2016 to October 12, 2016 but suffered a loss of its Real Time Contingency Analysis (RTCA) tool from October 12, 2016 to October 13, 2016. During the four hours and 38 minutes that Northern States Power’s RTCA was unavailable, MISO served as the primary voltage monitor with the incorrect monitored minimum voltage of 83 kV in place for one 115 kV bus. For those approximately four and a half hours, alarming would not occur if NPIR-defined low voltage conditions between 83.1 kV and 115.6 kV developed at Monticello on that one 115 kV bus. This noncompliance involves the management practice of verification and asset and configuration management. A MISO employee incorrectly inputted too low a voltage in the voltage monitoring tool and MISO did not have a verification process in place to check for and correct that human input error. This lack of a verification process and check is a root cause of this noncompliance. Asset and configuration management is also involved because the procedure MISO used to update voltage limits in its EMS does not specifically address the variable voltage characteristics of Monticello. The weakness of that procedure is a contributing cause of this noncompliance. This issue started on October 12, 2016, when MISO was serving as the primary local voltage monitor for Monticello while having an incorrect monitored minimum voltage for Monticello in MISO’s EMS and ended early in the morning on October 13, 2016, when MISO corrected the monitored minimum voltage for Monticello. Northern States Power also took over as the primary local voltage monitor for Monticello after restoring its RTCA later in the day on October 13, 2016. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is a failure to alarm if NPIR-defined low voltage conditions had developed at the Monticello plant during the noncompliance because of MISO’s incorrect minimum voltage setting. Because MISO's voltage monitoring tool was monitoring to a voltage set point lower than that established by the nuclear power plant in the NPIR, MISO may have been unaware of low voltage conditions at the Monticello plant. The risk is minimized because MISO was in noncompliance as the primary voltage monitor for Monticello for a short amount of time (four hours and 38 minutes). MISO only had incorrect information about one of the three 115 kV lines connected to Monticello. For the duration of the noncompliance, MISO had correct information about the three 345 kV lines connected to Monticello. Additionally, MISO’s SCADA and State Estimator tools would have shown lower voltages around the Monticello bus if a low voltage condition occurred during the noncompliance and that could notify MISO’s operators of the low voltage condition. Lastly, ReliabilityFirst notes there was no actual impact from this noncompliance because no low voltage issues occurred and MISO continued to effectively operate the electric system to meet the Monticello NPIR for the duration of the noncompliance. No harm is known to have occurred. ReliabilityFirst considered MISO's NUC-001 R4 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, MISO: 1) sent a training memo to reliability coordinators and reliability engineers regarding how to manage voltage threshold changes at Monticello and another nuclear plant that has variable voltage set points; 2) revised its operating procedure to better describe how to change NPIR values; and 3) embedded a peer check into the NPIR parameter change process, whereby the reliability engineer enters the parameter change into the relevant reference files, and the reliability coordinator validates the accuracy of that change. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Southern Indiana Gas & Electric Company d/b/a Vectren Energy Delivery of Indiana, Inc. (Vectren) | NCR00917 | RFC2017017333 | COM-001-2.1 | R10 | On March 24, 2017, Vectren submitted a Self-Report stating that, as a Balancing Authority and Transmission Operator, it was in noncompliance with COM-001-2.1 R10. On March 1, 2017, Vectren’s phone service provider experienced issues with its service due to storm damage to a number of cell towers and services in the region. Vectren also experienced phone service outage in its corporate phone system causing incoming and outgoing calls to fail. Internal calls, however, continued to function properly. On March 6, 2017, during a subsequent review of the matter, Vectren discovered that the control room operator failed to follow the established procedure for loss of primary voice communications by failing to make the required notifications to all relevant parties. The root cause of this noncompliance was the lack of a clear and simple procedure for control room operators to follow when faced with the loss of primary voice communications. This major contributing factor involves the management practice of grid operations, which includes performing incident management and control. This noncompliance started on March 1, 2017, when Vectren lost its primary voice communications for more than 30 minutes and ended approximately 10 hours later that same day, March 1, 2017, when Vectren’s primary voice communications were restored. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, during the time that the primary voice communications were down, Vectren maintained all communications necessary for reliability purposes using alternate means of communications as identified in its System Operator Event Reporting & Emergency Operations Procedures. Second, Vectren quickly identified and corrected the issue through detective and corrective controls. No harm is known to have occurred. ReliabilityFirst considered Vectren’s COM-001 R10 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, Vectren: 1) created a checklist specifically for COM-001-2 R10 that includes the list of entities to be contacted, their primary contact information, and space to record the date and time of both the contact and the failure that triggered the need for contact; 2) communicated the checklist to Operators and it is now located at the Primary and Backup Operations desks; 3) provided additional communication training, including training on the use of the checklist; and 4) provided additional human performance and error prevention training. Said training reviewed types of human errors and ways to prevent each type, including, for example, use of checklists and similar supports. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | West Deptford Energy, LLC (West Deptford) | NCR11391 | RFC2017017372 | EOP-005-2 | R17 | On April 4, 2017, West Deptford submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with EOP-005-2 R17. West Deptford did not provide training to all operating personnel regarding its system restoration plan and related procedures prior to its Blackstart Resource being put into service. West Deptford's Blackstart Resource became available for PJM use on October 9, 2015. The operating personnel were given a variety of training on the Blackstart unit at that time, but the training sign-in sheets do not specifically state the training was for the System Restoration Plan. Since West Deptford’s Blackstart unit went online, West Deptford has been participating in PJM’s Blackstart drills and sending operating personnel to PJM for System Restoration Training. At the time of the self-report, all operators had been through some form of Blackstart Training, but one operator that had not been through a PJM Restoration Drill. Additionally, one operator did not complete Blackstart Start Up procedure training until May 12, 2016. All other operators completed the training prior to that date. The root cause to this noncompliance was West Deptford’s misunderstanding of what the Standard required. More specifically, West Deptford did not know whether or not the training needed to be completed before the Blackstart Resource went into service or if it had two years to complete the training. This noncompliance involves the management practices of verification and planning because West Deptford failed to create a plan and verify that it would be compliant with EOP-005-2 R17 upon its unit becoming a Blackstart Resource. This noncompliance started on October 9, 2015, when West Deptford was required to comply with EOP-005-2 R17 and ended on October 12, 2016, when West Deptford completed its Mitigation Plan. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. At the time the Blackstart unit went into service, all operators had some form of Blackstart training, although potentially not all training as required by the Standard and Requirement. Additionally, most operators completed the required training within the first few months that the unit was put into service. Additionally, West Deptford’s practice is to provide more than the required two hours of Blackstart training to its operating personnel, including in-house training, participation in PJM drills, and other restoration drills. Accordingly, there was only minimal risk that the operators did not thoroughly understand the Blackstart procedures. No harm is known to have occurred. ReliabilityFirst considered West Deptford’s EOP-005 R17 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, West Deptford: 1) completed the required training; and 2) developed an Operator Training Matrix so it can clearly Track and see the dates the control room operators were last trained, what current training is needed and the dates Operators training needs to be completed. The training is being tracked by calendar year to ensure that no Operator can go more than two calendar years before receiving the correct EOP-005 Training - or other training. ReliabilityFirst has verified the completion of all mitigation activity.
2017-11-30 | SERC Reliability Corporation (SERC) | Bishop Hill Energy II LLC (Bishop) | NCR11309 | SERC2017017401 | MOD-025-2 | R1 | On April 17, 2017, Bishop submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Bishop did not submit a completed Attachment 2 to its Transmission Planner (TP) verifying the Real Power capability for 40% of its applicable Facilities by July 1, 2016 as required in the NERC Implementation Plan. On March 7, 2017 during its annual internal review process, Bishop identified the noncompliance. At the beginning of every year, the Wind Site Manager and the NERC Corporate support staff review each applicable NERC Reliability Standard RSAW and verify that Bishop completed all associated compliance activities and that proper documentation exists. On July 1, 2016, Bishop completed Real Power verification testing in accordance with Requirements R1. On October 7, 2016, Bishop submitted the Real Power data required in Attachment 2 to its TP. Bishop consists of 50 individual 1.6 MW wind turbines that it tested as a single facility. Bishop identified that its lack of sufficient main step-up transformer information resulting in a delay of the submittal of the information was the primary cause of the noncompliance. Part of the documentation required for MOD-025 testing involves determining the MVA losses experienced by the main step-up transformer. After consulting with company engineers, Bishop determined that it did not have sufficient documentation of the transformer to complete this determination and had to contact the transformer manufacturer for assistance. On September 26, 2016, the manufacturer provided the required information to Bishop. On October 7, 2016, Bishop completed the calculations and final documentation and submitted the data to its TP. This noncompliance started on July 1, 2016, when Bishop did not meet the implementation schedule and ended on October 7, 2016, when Bishop provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Bishop’s failure to provide Real Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Bishop operated at a 44% capacity factor for the 12-months prior to October 1, 2017. On October 7, 2016, Bishop completed testing that demonstrated Real Power capabilities for its facility and therefore all 50 1.6 MW wind turbines were in compliance by that date, as opposed to only 40% of the turbines as allowed in the implementation schedule. No harm is known to have occurred. SERC considered Bishop's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Bishop: 1) coordinated with the transformer manufacturer to identify the proper method of calculating transformer power losses; 2) completed the Real Power verification and provided the required information to its TP; and 3) created two inter-related records for NERC Reliability Standard MOD-025 in the electronic compliance management system. The first record (Parent Record) is a recurring 5-year notification to the Site Manager and a Corporate Support Staff employee for the completion of MOD-025 related testing. The Parent Record sends the reminder notification one year in advance of the due date. The second MOD-025 related record (Child Record) links to the Parent Record. Completion of the Parent Record triggers the Child Record. The Child Record has a due date of 90 days from the completion of the Parent Record. The Child Record describes the MOD-025 requirement to submit MOD-025 testing results to the TP within 90 days of completion of the testing and generates and sends a reminder email notification to the Site Manager and a Corporate Support Staff employee 30 days prior to the Child Record due date.
2017-11-30 | SERC Reliability Corporation (SERC) | Bishop Hill Energy II LLC (Bishop) | NCR11309 | SERC2017017514 | MOD-025-2 | R2 | On May 1, 2017, Bishop submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Bishop did not submit a completed Attachment 2 to its Transmission Planner (TP) verifying the Reactive Power capability for 40% of its applicable Facilities by July 1, 2016 as required in the NERC Implementation Plan. On March 7, 2017 during its annual internal review process, Bishop identified the noncompliance. At the beginning of every year, the Wind Site Manager and the NERC Corporate support staff review each applicable NERC Reliability Standard RSAW and verify that Bishop completed all associated compliance activities and that proper documentation exists. On July 1, 2016, Bishop completed Reactive Power verification testing in accordance with Requirements R2. On October 7, 2016, Bishop submitted the Reactive Power data required in Attachment 2 to its TP. Bishop consists of 50 individual 1.6 MW wind turbines that it tested as a single facility. Bishop identified that its lack of sufficient main step-up transformer information resulting in a delay of the submittal of the information was the primary cause of the noncompliance. Part of the documentation required for MOD-025 testing involves determining the MVA losses experienced by the main step-up transformer. After consulting with company engineers, Bishop determined that it did not have sufficient documentation of the transformer to complete this determination and had to contact the transformer manufacturer for assistance. On September 26, 2016, the manufacturer provided the required information to Bishop. On October 7, 2016, Bishop completed the calculations and final documentation and submitted the data to its TP. This noncompliance started on July 1, 2016, when Bishop did not meet the implementation schedule and ended on October 7, 2016, when Bishop provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Bishop’s failure to provide Reactive Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Bishop operated at a 44% capacity factor for the 12-months prior to October 1, 2017. On October 7, 2016, Bishop completed testing that demonstrated Reactive Power capabilities for its facility and therefore all 50 1.6 MW wind turbines were in compliance by that date as opposed to only 40% of the turbines as allowed in the implementation schedule. No harm is known to have occurred. SERC considered Bishop's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Bishop: 1) coordinated with the transformer manufacturer to identify the proper method of calculating transformer power losses; 2) completed the Reactive Power verification and provided the required information to its TP; and 3) created two inter-related records for NERC Reliability Standard MOD-025 in the electronic compliance management system. The first record (Parent Record) is a recurring 5-year notification to the Site Manager and a Corporate Support Staff employee for the completion of MOD-025 related testing. The Parent Record sends the reminder notification one year in advance of the due date. The second MOD-025 related record (Child Record) links to the Parent Record. Completion of the Parent Record triggers the Child Record. The Child Record has a due date of 90 days from the completion of the Parent Record. The Child Record describes the MOD-025 requirement to submit MOD-025 testing results to the TP within 90 days of completion of the testing and generates and sends a reminder email notification to the Site Manager and a Corporate Support Staff employee 30 days prior to the Child Record due date.
2017-11-30 | SERC Reliability Corporation (SERC) | California Ridge Energy LLC (CalRidge) | NCR11318 | SERC2017017672 | PRC-005-6 | R3 | On May 31, 2017, CalRidge submitted a Self-Certification stating that, as a Generator Owner (GO), it was in noncompliance with PRC-005-6 R3. CalRidge did not perform all of the required battery testing. CalRidge is a wind farm spanning parts of two counties in eastern Illinois. It consists of 134 wind turbine generators. Each turbine has a pad-mounted 690 V/34.5 kV transformer that feeds a collector bus. The chain of collector buses terminates at a 34.5 kV/138 kV substation. From there, a single 9-mile long 138 kV transmission line connects the aggregated generation to the point of interconnection with its Transmission Owner. CalRidge uses a Protection System Maintenance Program (PSMP) provided by a third-party. That PSMP includes the performance of intercell resistance testing on an 18-month cycle as required by PRC-005-6 Table 1-4. On July 21, 2015, a contractor performed periodic maintenance and testing of the 60-cell battery at the CalRidge substation. That activity included measurement of intercell resistance. On August 22, 2016, a contractor performed battery maintenance and testing, but did not perform the intercell resistance test. On May 18, 2017, CalRidge discovered the oversight while reviewing its compliance records for self-certification and contacted the contractor. On May 19, 2017, the contractor returned to the site and performed the required test, but outside of the required 18-month interval. The primary cause of the noncompliance is that CalRidge failed to account for the required testing in the contract with its contractor. Another cause was a deficient process which led to inadequate monitoring of third-party contractor performance. This noncompliance started on February 1, 2017, the day after the 18-month interval lapsed and ended on May 19, 2017, when CalRidge performed the intercell resistance tests. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Inadequate maintenance and testing of Protection System devices can lead to misoperations affecting the reliability of the Bulk Electric System (BES). However, CalRidge has a maximum output of 214 MW. The battery not tested within the required interval provides protection to a single substation that is not a network substation, so any misoperations would be limited to the generator interconnection and not to a networked substation. As a wind generator, CalRidge is an intermittent source and is not critical to BPS reliability. CalRidge performs monthly battery checks. CalRidge only lacked intercell resistance measurements from the 18 month inspection and all other battery checks were satisfactory. When CalRidge measured the intercell resistance it found no issues. No misoperations occurred at CalRidge during the approximately four months of noncompliance. No harm is known to have occurred. SERC considered CalRidge's compliance history and determined that there were no relevant instances of noncompliance | To mitigate this noncompliance, CalRidge: 1) notified the third-party contractor of the missing test data on May 18, 2017. The contractor sent out a service team the following day to the site to do the maintenance task that had not been satisfied during their previous visit; 2) required the third-party contractor to utilize the new testing equipment during the annual battery maintenance and testing activities to provide a more thorough and comprehensive dataset that includes intercell resistance; 3) performs a more thorough review of the all test data provided by third-party contractors; and 4) updated its process so that staff will use a job list description as a checklist when reviewing the test data. Also, two individuals must sign off on the review.
2017-11-30 | SERC Reliability Corporation (SERC) | Carville Energy LLC (Carville) | NCR11479 | SERC2017017961 | MOD-025-2 | R1 | On July 18, 2017, Carville submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Carville did not meet the NERC implementation schedule to provide its Transmission Planner (TP) with verification of the Real Power capability of its applicable Facilities in accordance with Attachment 1. On July 17, 2015, Carville performed the Generation Verification Test Capacity (GVTC) testing that demonstrated the facility’s maximum Real Power capabilities as required by its Transmission Operator (TOP). Carville incorrectly believed that the GVTC tests met the MOD-025-2 R1 and R2 Attachment 1 testing requirements. On May 23, 2017, Carville identified a noncompliance with MOD-025-2 R2 and submitted a Self-Report. On June 2, 2017, Carville conducted MOD-025-2 R1 and R2 testing in accordance with Attachment 1. On June 20, 2017, Carville provided the test results for R1 and R2 compliance to its TP. On July 6, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Carville determined that it misinterpreted the testing requirements listed in MOD-025-2 R1 Attachment 1 and determined that the July 17, 2015 testing did not meet the Attachment 1 requirements either. However, because Carville completed the test on June 2, 2017, Carville completed the MOD-025-2 R1 testing prior to the identification of the MOD-025-2 R1 noncompliance on July 6, 2017. The primary cause of the noncompliance was Carville’s misinterpretation of Attachment 1 testing requirements. This noncompliance started on July 1, 2016, when Carville did not meet the implementation schedule and ended on June 20, 2017, when Carville provided its TP with verification of the Real Power capability of its applicable Facilities in accordance with MOD-025-2 Attachment 1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Carville’s failure to provide Real Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, in 2015, Carville completed testing that demonstrated the facility’s Real Power capabilities as required by previous versions of the MOD Standards; therefore the TP was aware of certain unit capabilities. Carville is a 570 MW facility that operated at a 63% capacity factor for the 12-months prior to June 30, 2017. No harm is known to have occurred. SERC considered Carville's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Carville: 1) conducted the Real Power tests for its generators; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the four tests that must be performed every five years. The PM is designed to notify plant personnel six months prior to the tests due dates; 4) performed supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program to ensure staff understands the implementation of new or revised Standards or staff seeks guidance from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Carville Energy LLC (Carville) | NCR11479 | SERC2017017962 | MOD-025-2 | R2 | On July 18, 2017, Carville submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Carville failed to meet the NERC implementation schedule to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its applicable Facilities. On May 23, 2017, Carville determined that it misinterpreted the testing requirements listed in Attachment 1. Since Carville normally operates its gas turbines generators (GTG) at base load, Carville believed that testing the GTGs at the base load level met the maximum and minimum Reactive Power testing requirements. However, a third party contractor reviewed the test results and provided Carville with guidance that NERC intended that the minimum load Reactive Power test was to demonstrate the facility’s Reactive Power capabilities throughout its entire operating range. On June 2, 2017, Carville conducted the Reactive Power tests for its two GTGs and its steam turbine generator (STG). On June 20, 2017, Carville provided those test results to the TP. On July 14, 2017, Carville conducted additional Reactive Power tests on the GTGs and planned to submit the test results to the TP within 90 days of the completion of the test. The primary cause of the noncompliance was Carville’s misinterpretation of the Standard. This noncompliance started on July 1, 2016, when Carville did not meet the implementation schedule and ended on September 29, 2017, when Carville completed its mitigating activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Carville’s failure to provide correct modelling of unit Reactive Power capabilities to the TP could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the Carville facility was able to supply the Reactive Power requested by the Transmission Operator during the period of noncompliance. Carville is a 570 MW facility that operated at a 63% capacity factor for the 12-months prior to June 30, 2017. No harm is known to have occurred. SERC considered Carville's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Carville: 1) conducted the Reactive Power tests for its two GTGs and its STG; 2) provided those test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool (Maximo) that indicates the four tests that must be performed every five years. The PM is designed to notify plant personnel six months prior to the tests due dates; 4) performed supplemental training on the violation for the operating staff involved with the testing; and 5) revise its Internal Compliance Program to ensure implementation of new or revised Standards are clearly understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | City of North Little Rock Electric Department (NLRED) | NCR11091 | SERC2017017345 | MOD-025-2 | R1 | On April 5, 2017, NLRED submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. NLRED did not meet the MOD-025-2 implementation schedule to verify the Real Power capability of 40% of its applicable Facilities and provide that information to its Transmission Planner (TP) by July 1, 2016. On October 3, 2016, NLRED determined that it had insufficient data to meet the compliance requirements for MOD-025-2 R1. NLRED initially believed that the data it had prior to July 1, 2016 met the requirements. However, the NLRED compliance administrator retired and NLRED hired a new compliance administrator. The new compliance administrator contracted consultants to assist in performing a review of all the NERC Standards applicable to NLRED. During this review, NLRED determined that it did not have sufficient data to meet the requirements of MOD-025-2 R1. NLRED performs an annual review of all applicable standards. The 2016 review was part of the annual review process. The primary cause of the noncompliance was a misunderstanding of the requirements of the Standard. This noncompliance started on July 1, 2016, when NLRED did not meet the implementation schedule and ended on January 31, 2017, when NLRED provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NLRED’s incorrect modelling of unit capabilities could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the NLRED facility consists of two 20 MW run-of-the-river hydro units in the MISO area that run only when water is available. During 2016, the capacity factor was 59% for unit 1 and 33% for unit 2. While NLRED missed the July 1, 2016 deadline to verify the Real Power capability of one unit, it completed verification of the Real Power capability of both units before July 1, 2017, the deadline by which it would need to verify 100% of its units and notify the TP pursuant to the MOD-025-2 implementation schedule. Therefore, NLRED’s delay in meeting the 40% requirement resulted in minimal additional risk. No harm is known to have occurred. SERC considered NLRED's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, NLRED: 1) performed the test for verification of the Real Power capability; 2) notified its TP via email and attached the Real Power Verification reports; and 3) implemented a scheduling reminder to ensure that supporting documentation is updated as necessary. NLRED will review MOD-025 at least once every calendar year to determine if any changes have been made that would require additional testing and verification.
2017-11-30 | SERC Reliability Corporation (SERC) | City of North Little Rock Electric Department (NLRED) | NCR11091 | SERC2017017346 | MOD-025-2 | R2 | On April 5, 2017, NLRED submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. NLRED did not meet the MOD-025-2 implementation schedule to verify the Reactive Power capability of 40% of its applicable Facilities and provide that information to its Transmission Planner (TP) by July 1, 2016. On October 3, 2016, NLRED determined that it had insufficient data to meet the compliance requirements for MOD-025-2 R2. NLRED initially believed that the data it had prior to July 1, 2016 meet the requirements. However, the NLRED compliance administrator retired and NLRED hired a new compliance administrator. The new compliance administrator contracted consultants to assist in performing a review of all the NERC Standards applicable to NLRED. During this review, NLRED determined that it did not have sufficient data to meet the requirements of MOD-025-2 R2. NLRED performs an annual review of all applicable standards. The 2016 review was part of the annual review process. The primary cause of the noncompliance was a misunderstanding of the requirements of the Standard. This noncompliance started on July 1, 2016, when NLRED did not meet the implementation schedule and ended on January 31, 2017, when NLRED provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NLRED’s incorrect modelling of unit capabilities could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the NLRED Facility consists of two 20 MW run-of-the-river hydro units in the MISO area that run only when water is available. During 2016, the capacity factor was 59% for unit 1 and 33% for unit 2. While NLRED missed the July 1, 2016 deadline to verify the Reactive Power capability of one unit, it completed verification of the Reactive Power capability of both units before July 1, 2017, the deadline by which it would need to verify 100% of its units and notify the TP pursuant to the MOD-025-2 implementation schedule. Therefore, NLRED’s delay in meeting the 40% requirement resulted in minimal additional risk. No harm is known to have occurred. SERC considered NLRED's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, NLRED: 1) performed the test for verification of the Reactive Power capability; 2) notified its TP via email and attached the Reactive Power Verification reports; and 3) implemented a scheduling reminder to ensure that supporting documentation is updated as necessary. NLRED will review MOD-025 at least once every calendar year to determine if any changes have been made that would require additional testing and verification.
2017-11-30 | SERC Reliability Corporation (SERC) | City of North Little Rock Electric Department (NLRED) | NCR11091 | SERC2017017347 | PRC-019-2 | R1 | On April 5, 2017, NLRED submitted a Self-Report stating that, as a Generator Owner and Transmission Owner, it was in noncompliance with PRC-019-2 R1. NLRED did not meet the PRC-019-2 implementation schedule to coordinate the voltage regulating system controls for 40% of its applicable Facilities with the applicable equipment capabilities and settings of the applicable Protection System devices and functions by July 1, 2016. On October 3, 2016, NLRED determined that it had insufficient data to meet the compliance requirements for PRC-019-2 R1. NLRED initially believed that the data it had prior to July 1, 2016 met the requirements. However, the NLRED compliance administrator retired and NLRED hired a new compliance administrator. The new compliance administrator contracted consultants to assist in performing a review of all the NERC Standards applicable to NLRED. During this review, NLRED determined that it did not have sufficient data to meet the requirements of PRC-019-2 R1. NLRED performs an annual review of all applicable standards. The 2016 review was part of the annual review process. The primary cause of the noncompliance was a misunderstanding of the requirements of the Standard. This noncompliance started on July 1, 2016, when NLRED did not meet the implementation schedule and ended on January 9, 2017, when NLRED implemented the setting changes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NLRED’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, the NLRED facility consists of two 20 MW run-of-the-river hydro units in the MISO area that run only when water is available. During 2016, the capacity factor was 59% for unit 1 and 33% for unit 2. NLRED found during its verification efforts that the maximum deviation from acceptable control parameters was 6%. While NLRED missed the July 1, 2016 deadline to verify the settings of its protective relaying of one unit, it completed the required coordination of its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for both generation units before by July 1, 2017, the deadline by which it would need to complete coordination of 100% of its units. Therefore, NLRED’s delay in meeting the 40% requirement resulted in minimal additional risk. No harm is known to have occurred. SERC considered NLRED's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, NLRED: 1) completed the setting changes; and 2) implemented a scheduling reminder to ensure that supporting documentation is updated as necessary. NLRED will review PRC-019 at least once every calendar year to determine if any protection schemes changed and would require another validation of the coordination.
2017-11-30 | SERC Reliability Corporation (SERC) | City of North Little Rock Electric Department (NLRED) | NCR11091 | SERC2017017399 | PRC-024-2 | R1 | On April 14, 2017, NLRED submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. NLRED did not verify the settings of its protective relaying for 40% of its applicable Facilities such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1 by July 1, 2016. On October 3, 2016, NLRED determined that it had insufficient data to meet the compliance requirements for PRC-024-2 R1. NLRED initially believed that the data it had prior to July 1, 2016 met the requirements. However, the NLRED compliance administrator retired and NLRED hired a new compliance administrator. The new compliance administrator contracted consultants to assist in performing a review of all the NERC Standards applicable to NLRED. During this review, NLRED determined that it did not have sufficient data to meet the requirements of PRC-024-2 R1. NLRED performs an annual review of all applicable standards. The 2016 review was part of the annual review process. The primary cause of the noncompliance was a misunderstanding of the requirements of the Standard. This noncompliance started on July 1, 2016, when NLRED did not meet the implementation schedule, and ended on December 30, 2016, when NLRED verified its relay settings met the “no trip zone” requirement. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NLRED’s failure to verify that the generator frequency relays are set not trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, no changes to the relay settings were required as a result of the verification analysis. In addition, the NLRED Facility consists of just two 20 MW run-of-the-river hydro units in the MISO area that run only when water is available. During 2016, the capacity factor was 59% for unit 1 and 33% for unit 2. While NLRED missed the July 1, 2016 deadline set by the NERC implementation plan to verify the settings of its protective relaying of one unit, it completed verification for both generation units before July 1, 2017, the deadline by which it would need to verify 100% of its units. Therefore, NLRED’s delay in meeting the 40% requirement resulted in minimal additional risk. No harm is known to have occurred. SERC considered NLRED's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, NLRED: 1) completed the relay setting verification; and 2) implemented a scheduling reminder to ensure that supporting documentation is updated as necessary. NLRED will review PRC-024 at least once every calendar year to determine if any protection schemes changed and would require another validation of the coordination. If NLRED modifies the protection schemes for the Murray Generators, it will conduct an assessment of PRC-024 to insure the relay setting remain outside the no-trip zones. If the validation determines that the settings do not meet PRC-024, NLRED will conduct a study and change the settings to meet the needs of the Protection System and the Standard.
2017-11-30 | SERC Reliability Corporation (SERC) | City of North Little Rock Electric Department (NLRED) | NCR11091 | SERC2017017400 | PRC-024-2 | R2 | On April 14, 2017, NLRED submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. NLRED did not verify the settings of its protective relaying for 40% of its applicable Facilities such that the generator voltage protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 2 by July 1, 2016. On October 3, 2016, NLRED determined that it had insufficient data to meet the compliance requirements for PRC-024-2 R2. NLRED initially believed that the data it had prior to July 1, 2016 met the requirements. However, the NLRED compliance administrator retired and NLRED hired a new compliance administrator. The new compliance administrator contracted consultants to assist in performing a review of all the NERC Standards applicable to NLRED. During this review, NLRED determined that it did not have sufficient data to meet the requirements of PRC-024-2 R2. NLRED performs an annual review of all applicable standards. The 2016 review was part of the annual review process. The primary cause of the noncompliance was a misunderstanding of the requirements of the Standard. This noncompliance started on July 1, 2016, when NLRED did not meet the implementation schedule, and ended on December 30, 2016, when NLRED verified its relay settings met the “no trip zone” requirement. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NLRED’s failure to verify that the generator voltage relays are set not trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, no changes to the relay settings were required as a result of the verification analysis. In addition, the NLRED Facility consists of just two 20 MW run-of-the-river hydro units in the MISO area that run only when water is available. During 2016, the capacity factor was 59% for unit 1 and 33% for unit 2. While NLRED missed the July 1, 2016 deadline set by the NERC implementation plan to verify the settings of its protective relaying of one unit, it completed verification for both generation units before July 1, 2017, the deadline by which it would need to verify 100% of its units. Therefore, NLRED’s delay in meeting the 40% requirement resulted in minimal additional risk. No harm is known to have occurred. SERC considered NLRED's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, NLRED: 1) completed the relay setting verification; and 2) implemented a scheduling reminder to ensure that supporting documentation is updated as necessary. NLRED will review PRC-024 at least once every calendar year to determine if any protection schemes changed and would require another validation of the coordination. If NLRED modifies the protection schemes for the Murray Generators, it will conduct an assessment of PRC-024 to insure the relay setting remain outside the no-trip zones. If the validation determines that the settings do not meet PRC-024, NLRED will conduct a study and change the settings to meet the needs of the Protection System and the Standard.
2017-11-30 | SERC Reliability Corporation (SERC) | Columbia Energy LLC (Columbia) | NCR11480 | SERC2017017991 | MOD-025-2 | R1 | On July 21, 2017, Columbia submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Columbia did not meet the MOD-025-2 implementation schedule to verify the Real Power capability of 40% of its applicable Facilities and provide that information to its Transmission Planner (TP) by July 1, 2016. On May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Columbia discovered that it did not complete the required verification of the Real Power capability of 40% of its generating units and provide that information to its TP by July 1, 2016. On August 16, 2016 and August 17, 2016, Columbia performed tests that demonstrated the Real Power capabilities of 100% of its units. On September 12, 2016, Columbia provided the test results to the TP. Columbia attributes this noncompliance to its misinterpretation of the testing requirements contained in Attachment 1. Columbia believed it was required to provide its TP the verification of the Real Power capability by July 1, 2019. This noncompliance started on July 1, 2016, when Columbia did not meet the implementation schedule and ended on September 12, 2016, when Columbia provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Columbia’s failure to provide Real Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Columbia is a 650 MW combined cycle facility with a capacity factor of 29% for the 12-months ending June 2017. While Columbia missed the July 1, 2016 deadline to verify Real Power output of two units, it had an additional year for the verification and notification to the TP of the remaining unit. Therefore, Columbia’s delay of 73 days in completing the 40% requirement resulted in minimal additional risk and Columbia provided verification of the Real Power capability for 100% of its units on September 12, 2016, further reducing the risk. No harm is known to have occurred. SERC considered Columbia's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Columbia: 1) conducted the Real Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Real Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Columbia Energy LLC (Columbia) | NCR11480 | SERC2017017994 | MOD-025-2 | R2 | On July 21, 2017, Columbia submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Columbia did not meet the MOD-025-2 implementation schedule to verify the Reactive Power capability of 40% of its applicable Facilities and provide that information to its Transmission Planner (TP) by July 1, 2016. On May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Columbia discovered that it did not complete the required verification of the Reactive Power capability of 40% of its generating units and provide that information to its TP by July 1, 2016. On August 16, 2016 and August 17, 2016, Columbia performed tests that demonstrated the Reactive Power capabilities of 100% of its units. On September 12, 2016, Columbia provided the test results to the TP. Columbia attributes this noncompliance to its misinterpretation of the testing requirements contained in Attachment 1. Columbia believed it was required to provide its TP the verification of the Reactive Power capability by July 1, 2019. This noncompliance started on July 1, 2016, when Columbia did not meet the implementation schedule and ended on September 12, 2016, when Columbia provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Columbia’s failure to provide Reactive Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, Columbia is a 650 MW combined cycle facility with a capacity factor of 29% for the 12-months ending June 2017. While Columbia missed the July 1, 2016 deadline to verify Reactive Power output of two units, it had an additional year for the verification and notification to the TP of the remaining unit. Therefore, a delay of 73 days in completing the 40% requirement resulted in minimal additional risk. Columbia provided verification of the Reactive Power capability for 100% of its units on September 12, 2016, further reducing the risk. No harm is known to have occurred. SERC considered Columbia's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Columbia: 1) conducted the Reactive Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Reactive Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing: and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Columbia Energy LLC (Columbia) | NCR11480 | SERC2017018276 | PRC-019-2 | R1 | On August 28, 2017, Columbia submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Columbia did not meet the PRC-019-2 implementation schedule to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for 40% of its applicable Facilities. On July 14, 2017, while conducting an internal review as a result of identified noncompliance with another Standard subject to the same implementation schedule, Columbia discovered that it did not coordinate the voltage regulating system controls for 40% of its applicable Facilities by July 1, 2016. On December 15, 2016, Columbia performed the coordination study. Columbia stated that the primary cause was its lack of understanding of the phased implementation compliance dates. This noncompliance started on July 1, 2016, when Columbia did not meet the implementation schedule and ended on December 15, 2016, when it verified coordination of the voltage regulating system controls with the applicable Protection System devices and functions. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Columbia’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to a generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, Columbia found that the settings did not require changes in order to meet compliance. Columbia is a 650 MW combined cycle facility with a capacity factor of 29% for the 12-months ending June 2017. While Columbia missed the July 1, 2016 deadline to verify coordination of two units, it had an additional year for the coordination verification of the remaining unit. Therefore, Columbia’s delay of 167 days for the 40% requirement resulted in minimal additional risk and Columbia verified coordination for 100% of its units on December 15, 2016, further reducing the risk. No harm is known to have occurred. SERC considered Columbia's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Columbia: 1) performed the coordination study; 2) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the coordination of the voltage regulating system controls with Protection System devices and functions must be performed every five years. The PM will notify plant personnel six months prior to the tests due dates; 3) conducted training for Columbia personnel; and, 4) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Columbia Energy LLC (Columbia) | NCR11480 | SERC2017018277 | PRC-024-2 | R1 | On August 28, 2017, Columbia submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Columbia did not set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1 in accordance with the NERC implementation schedule. Columbia is a 650 MW combined cycle facility with two combustion turbines and one steam turbine generator. On November 21, 2016, Columbia completed the analysis for PRC-024-2 R1 compliance. Columbia identified a steam turbine generator underfrequency primary relay and steam turbine backup relay that encroached on the no-trip zone, but the trip setpoints for the two combustion turbines were in compliance. On January 18, 2017, Columbia changed the steam turbine trip settings from 61 Hz to 61.8 Hz. On July 14, 2017, while conducting an internal review as a result of identified noncompliance with another Standard subject to the same implementation schedule, Columbia discovered that it did not set its frequency protective relaying by July 1, 2016 as required by the implementation plan for PRC-024-2. Columbia stated that the primary cause was its lack of understanding of the phased implementation compliance dates. This noncompliance started on July 1, 2016, when Columbia did not set its frequency protective relaying as required and ended on January 18, 2017, when it completed the analysis and changed the relay settings for one of the three units. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Columbia’s failure to verify that the generator frequency relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, Columbia is a 650 MW combined cycle facility with a capacity factor of 29% for the 12-months ending June 2017. No setting changes were required for the two combustion turbines and the steam turbine trip setpoint required only 0.8 Hz adjustment. The NERC implementation plan allowed Columbia to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” for only two units by July 1, 2016. Columbia did not verify compliance by July 1, 2016, but did so 143 days late. The implementation plan allows an additional year for the remaining unit and Columbia set its protective relaying for 100% of its units on January 18, 2017 becoming fully compliant prior to the required date. No unplanned trips or system disturbances resulted from the single inadequate setpoint. No harm is known to have occurred. SERC considered Columbia's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Columbia: 1) completed an analysis of the generator frequency protective relay settings for compliance with PRC-024; 2) changed relay settings; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that triggers a monthly review of applicable NERC Standards, including PRC-024 and requires all changes to voltage or frequency ride-through capability or relay settings be reported to personnel with responsibilities for day to day compliance at Columbia; 4) conducted training for Columbia personnel on applicable NERC Standards. During presentation of requirements of PRC-024-2, staff discussed the failure to meet the compliance requirements as well as the steps taken to prevent a similar occurrence; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Columbia Energy LLC (Columbia) | NCR11480 | SERC2017018278 | PRC-024-2 | R2 | On August 28, 2017, Columbia submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Columbia did not set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 2 in accordance with the NERC implementation schedule. On November 21, 2016, Columbia completed the analysis for PRC-024-2 R2 compliance. Columbia identified a primary and backup relays on both combustion turbines and the steam generator that encroached on the no-trip zone. On January 18, 2017, Columbia changed the 12 relay settings to establish compliance On July 14, 2017, while conducting an internal review as a result of identified noncompliance with another Standard subject to the same implementation schedule, Columbia discovered that it did not set its voltage protective relaying by July 1, 2016. Columbia stated that the primary cause was its lack of understanding of the phased implementation compliance dates. This noncompliance started on July 1, 2016, when Columbia did not set its voltage protective relaying as required and ended on January 18, 2017, when it completed the relay setting changes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Columbia’s failure to verify that the generator voltage relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, Columbia is a 650 MW combined cycle facility with a capacity factor of 29% for the 12-months ending June 2017. The as-found relay settings would have allowed Columbia to endure an undervoltage transient of 97% of the required magnitude for at least one second, and an overvoltage disturbance of the required magnitude for approximately 50 seconds prior to tripping. The NERC implementation plan allows Columbia to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units within the “no trip zone” for only two units by July 1, 2016 and allows an additional year for the remaining unit. Columbia set its protective relaying for 100% of its units on January 18, 2017, establishing full compliance more than five months before required by the implementation plan. No unplanned trips or system disturbances resulted from the inadequate setpoints. No harm is known to have occurred. SERC considered Columbia's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Columbia: 1) completed an analysis of the generator voltage protective relay settings for compliance with PRC-024; 2) changed relay settings; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that triggers a monthly review of applicable NERC Standards, including PRC-024 and requires all changes to voltage or frequency ride-through capability or relay settings be reported to personnel with responsibilities for day to day compliance at Columbia; 4) conducted training for Columbia personnel on applicable NERC Standards. During presentation of requirements of PRC-024-2, staff discussed the failure to meet the compliance requirements as well as the steps taken to prevent a similar occurrence; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Cypress Creek Renewables (CCR) | NCR11624 | SERC2017018289 | PRC-024-2 | R1 | On August 31, 2017, Cypress Creek Renewables (CCR) submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. CCR did not verify that its frequency responsive relay settings were outside the “no trip zone”. CCR is the owner of a 90 MW solar power facility that connects to the Bulk Power System through a single inverter and at a single point at 115 kV. On December 9, 2016, it began commercial operation. On June 20, 2017, NERC issued a NERC Alert titled “Industry Recommendation – Loss of Solar Resources during Transmission Disturbances due to Inverter Settings.” On August 16, 2017, during an investigation of inverter settings, CCR discovered that the generator frequency ride-through (FRT) duration settings of the Facility’s inverters were set inside of the no-trip zone designated for the Eastern Interconnection. The generator FRT settings were programmed to provide insufficient ride through duration for frequencies outside of the region of Continuous operation of <60.5 and >59.5 Hz. The original settings allowed for continuous operation within 60.5-59.5 Hz as required by PRC-024-2 Eastern Interconnection standards, but did not meet the required durations outside of that band. In response to the NERC Alert, the Generator Owner requested that the manufacturer of the inverters reset them in accordance with PRC-024-2 R1. CCR believes that the primary cause of the noncompliance was largely a result of a software limitation that prevented the requisite length of time for FRT. This was an original and latent design error, which has since been corrected. This noncompliance started on December 9, 2016, when CCR began operation with the incorrect trip settings and ended on August 23, 2017, when CCR corrected the FRT trip settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Premature tripping of generation assets could exacerbate a frequency disturbance. However, CCR is a 90 MW solar farm with its maximum output dependent on intensity of solar radiation. Its capacity factor is approximately 26%. The original settings allowed for continuous operation within 60.5-59.5 Hz as required by PRC-024-2, however, original settings applied a time delay of 100 milliseconds to frequencies outside of that range. That time delay is substantially less than the delay required by PRC-024-2, but is 10 times longer than the brief time delay that caused the loss of generation that triggered the NERC Alert. The improper FRT settings did not cause any unnecessary tripping events. CCR operated with inadequate FRT settings for less than one year and the settings did not adversely impact grid reliability during that relatively brief operational period. No harm is known to have occurred. SERC considered CCR’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, CCR: 1) requested the manufacturer of the inverters to reset the inverters in accordance with PRC-024-2, R1. It reported that software changes restoring compliance had been completed as of 8/23/2017. 2) the asset manager will include the verification of the generator FRT settings in the required scope of work for all inverter commissioning and proof of compliance will be generated and archived at the time the applicable facility is interconnected.
2017-11-30 | SERC Reliability Corporation (SERC) | Decatur Energy Center, LLC (Decatur) | NCR11481 | SERC2017018041 | MOD-025-2 | R1 | On July 26, 2017, Decatur submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Decatur did not meet the implementation schedule verify the Real Power capability of 40% of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. In 2012, Decatur performed tests previously required under the SERC regional Generator Testing program for MOD-024-1, MOD-025-1, MOD-026-1 and MOD-027-1. Decatur initially believed that these tests also covered the MOD-025-2 requirements. However, on May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Decatur identified that the prior testing did not meet all of the MOD-025-2 R1 requirements. Decatur determined the primary cause of the noncompliance was a misinterpretation of the testing requirements contained in Attachment 1. This noncompliance started on July 1, 2016, when Decatur did not meet the implementation schedule and ended on October 11, 2017, when Decatur provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Decatur’s failure to provide Real Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, in 2012, Decatur completed testing that demonstrated the facility’s Real Power capabilities as required by previous versions of the MOD Standards, and therefore the TP was aware of certain unit capabilities. Decatur is a 795 MW 3x1 combined cycle facility that operated at an average capacity factor of 35% for the 12-month period ending June 2017. No harm is known to have occurred. SERC considered Decatur's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Decatur: 1) conducted the Real Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Real Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Decatur Energy Center, LLC (Decatur) | NCR11481 | SERC2017018042 | MOD-025-2 | R2 | On July 26, 2017, Decatur submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Decatur did not meet the implementation schedule to verify the Reactive Power capability of 40% of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. In 2012, Decatur performed tests previously required under the SERC regional Generator Testing program for MOD-024-1, MOD-025-1, MOD-026-1 and MOD-027-1. Decatur initially believed that these tests also covered the MOD-025-2 requirements. However, on May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Decatur identified that the prior testing did not meet all of the MOD-025-2 R2 requirements. Decatur determined the primary cause of the noncompliance was a misinterpretation of the testing requirements contained in Attachment 1. This noncompliance started on July 1, 2016, when Decatur did not meet the implementation schedule and ended on October 11, 2017, when Decatur provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Decatur’s failure to provide Reactive Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, in 2012, Decatur completed testing that demonstrated the facility’s Reactive Power capabilities as required by previous versions of the MOD Standards, and therefore the TP was aware of certain unit capabilities. Decatur is a 795 MW 3x1 combined cycle facility that operated at an average capacity factor of 35% for the 12-month period ending June 2017. No harm is known to have occurred. SERC considered Decatur's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Decatur: 1) conducted the Reactive Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Reactive Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Doswell Limited Partnership (Doswell) | NCR11193 | SERC2017018034 | MOD-025-2 | R1 | On July 25, 2017, Doswell submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Doswell did not meet the implementation schedule to verify the Real Power capability of 40% of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. The Doswell facility has seven units subject to the MOD-025-2 testing requirements. On October 23, 2014, Doswell performed testing required by the Transmission Operator (TOP) that demonstrated the Real Power capabilities of one of its combustion turbines and two steam turbine generators; however, these tests did not meet the requirements for MOD-025-2 Attachment 1. Doswell incorrectly believed that these tests met the MOD-025-2 R1 testing requirement and believed it was compliant on July 1, 2016. However, on May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Doswell identified that the 2014 testing did not meet all of the MOD-025-2 R1 requirements. Doswell determined the primary cause of the noncompliance was a misinterpretation of the testing requirements contained in Attachment 1. This noncompliance started on July 1, 2016, when Doswell did not meet the implementation schedule and ended on August 1, 2017, when Doswell provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Doswell’s failure to provide the required Real Power capability information to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, on October 23, 2014, Doswell completed testing that demonstrated the facility’s Real Power capabilities as required by its TOP, and therefore the TOP was aware of some unit capabilities. Doswell is an 860 MW facility consisting of two combined cycle systems and one additional peaking turbine. The Doswell facility operated at an average capacity factor of 50% for the 12-month period ending June 2017. No harm is known to have occurred. SERC considered Doswell's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Doswell: 1) conducted the Real Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Real Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Doswell Limited Partnership (Doswell) | NCR11193 | SERC2017018035 | MOD-025-2 | R2 | On July 25, 2017, Doswell submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. SREC did not meet the implementation schedule to verify the Reactive Power capability of 40% of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. The Doswell facility has seven units subject to the MOD-025-2 testing requirements. On October 23, 2014, Doswell performed testing required by the Transmission Operator (TOP) that demonstrated the Reactive Power capabilities of one of its combustion turbines and two steam turbine generators; however, these tests did not meet the requirements for MOD-025-2 Attachment 1. Doswell incorrectly believed that these tests met the MOD-025-2 R2 testing requirement and believed it was compliant on July 1, 2016. However, on May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Doswell identified that the 2014 testing did not meet all of the MOD-025-2 R2 requirements. Doswell determined the primary cause of the noncompliance was a misinterpretation of the testing requirements contained in Attachment 1. This noncompliance started on July 1, 2016, when Doswell did not meet the implementation schedule and ended on August 1, 2017, when Doswell provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Doswell’s failure to provide the required Reactive Power capability information to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, on October 23, 2014, Doswell completed testing that demonstrated the facility’s Reactive Power capabilities as required by its TOP and therefore the TOP was aware of some unit capabilities. Doswell is an 860 MW facility consisting of two combined cycle systems and one additional peaking turbine. The Doswell facility operated at an average capacity factor of 50% for the 12-month period ending June 2017. No harm is known to have occurred. SERC considered Doswell's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Doswell: 1) conducted the Reactive Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Reactive Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards is understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | E.I. du Pont de Nemours and Company (EIdP) | NCR09008 | SERC2017018096 | PRC-005-6 | R3 | On August 2, 2017, EIdP submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-005-1.1b R2. EIdP reported that it did not complete required battery maintenance. EIdP has three generating units. Each unit has a lead-acid battery associated with its generator Protection System. On April 27, 2017, EIdP performed a routine check of its maintenance records and determined that it did not have record of a scheduled quarterly battery maintenance for the first quarter of 2017. EIdP explained and provided evidence that it performed weekly, monthly and quarterly inspections as part of its Protection System Maintenance Program (PSMP). EIdP attributed the missing inspection to a programming problem in the fourth quarter of 2016 that led to the system failing to generate a work order for the first quarter of 2017. Furthermore, the routine check that detected the missing maintenance activity did not occur until after closure of the quarter, and delayed detection did not allow EIdP to schedule and complete the activity in the first quarter. EIdP believed that it needed to self-report because it had a violation of its internal PSMP. During its assessment, SERC staff noted that EIdP still maintained its battery under the self-imposed requirements of PRC-005-1.1b, however the implementation plan for PRC-005-6 required performance of short-term maintenance requirements by October 1, 2015 and required maintenance activities with intervals of one-to-two years by April 1, 2017. Therefore, EIdP should have converted all but its long-term battery maintenance program over to comply with PRC-005-2 by April 1, 2017. SERC staff requested evidence of compliance with PRC-005-6 and found EIdP’s PSMP under PRC-005-1.1b provided for all of the required maintenance activities under PRC-005-6 with the exception of an 18-month requirement to verify battery terminal resistance. Since EIdP required those maintenance activities on a shorter interval than required, the missing quarterly maintenance was not a noncompliance of PRC-005-2. However, because EIdP had not met the implementation dates for PRC-005-6 by failing to perform the terminal resistance checks, SERC concluded that EIdP had a noncompliance with PRC-005-6 rather than PRC-005-1.1b as EIdP originally self-reported. The apparent cause of this noncompliance was EIdP’s assumption that the previous PSMP activities were sufficient for compliance resulting in its failure to implement the battery maintenance requirements in accordance with the implementation plan for PRC-005-6. This noncompliance started on April 1, 2017, the date by which EIdP needed to perform terminal resistance checks and ended on October 10, 2017, when EIdP performed the required checks. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). EIdP’s failure to properly maintain the generator Protection System may result in failure of a unit to trip during fault conditions or could result in unplanned tripping, either of which may cause disturbances on the BPS and equipment damage. However, EIdP is an Independent Power Producer and a Qualifying Facility providing power and process steam to an adjacent manufacturing plant. EIdP provides only excess generation of approximately 300 MW to the BPS and operates at a 44% capacity factor. EIdP was able to show compliance with all battery maintenance requirements except terminal resistance and EIdP performed those activities on a shorter interval than required by PRC-005-2, suggesting that the batteries would be capable of performing their design function if they had been called upon to do so. EIdP verified proper operation of the battery chargers which are capable of providing Protection System functions. The failure to verify terminal resistance did not cause or prevent any Protection System functions. No harm is known to have occurred. SERC considered EIdP’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, EIdP: 1) Changed internal processes to assure EIdP’s SERC/NERC compliance coordinator audits the computer folder to verify the folder contains necessary records; 2) EIdP verified that it was performing all applicable requirements of Tables 1 through 5 of PRC-005; 3) Changed the method of generating work orders: the system was generating quarterly and monthly inspection notifications using the same equipment ID number, thus, the Planner would determine if the notification was going to be a monthly or a quarterly notification. Now there will be four quarterly maintenance plans, and 12-monthly maintenance plans. Thus, EIdP will generate a notification for each month of the year, which will include weekly events for the month along with a monthly, due to a monthly has additional inspections, on top of the weekly inspection; and 4) Procedurally, technicians will annually be physically checking post-to-post, below the connection for resistance with a Fluke model 1587. Technicians will verify that the readings are less than 1 ohms. Anything over that will require cleaning of the post and connections.
2017-11-30 | SERC Reliability Corporation (SERC) | Electric Energy, Inc. (EEI) | NCR11399 | SERC2017017666 | BAL-002-1 | R4 | On May 26, 2017, Electric Energy, Inc. (EEI) submitted a Self-Report stating that, as a Balancing Authority, it was in noncompliance with BAL-002-2 R4. EEI did not restore its Area Control Error (ACE) within 15 minutes following a Reportable Disturbance. EEI is a generation-only BA consisting of a six-unit, 1,002 net MW coal-fired facility, and a two-unit 140 net MW gas-fired facility. On May 15, 2017, a 230KV transmission line owned by an interconnected Transmission Owner (TO) tripped. By design, the line fully isolated by opening a breaker that supplies the startup transformer at the EEI facility, so loss of that line led to the loss of an interconnected EEI-owned startup transformer. The startup transformer was supplying a station auxiliary 4160 V bus. One of the loads on that bus was a spare exciter at the Joppa Power Plant. The spare exciter provides excitation to any one of the six EEI coal units at Joppa and, at the time of the loss, it was providing excitation to Unit 6. The loss of the spare exciter power caused Unit 6 to trip offline and resulted in a loss of 161 MW equivalent to the loss of 96% of EEI’s Most Severe Single Contingency (MSSC) and resulted in a Reportable Disturbance. The loss of Unit 6 caused ACE to decrease by 161 MW from -13 MW before the Disturbance to -174 MW after the Disturbance. All of the operating power plants were fully loaded and EEI could not start and load the gas-fired units within 15 minutes. EEI needed to adjust its interchange schedules to restore ACE. However, the loss of the auxiliary power also caused a loss of internet access for the EEI’s Joppa Transmission Control Center. Due to the loss of internet access, the operator was unable to adjust the EEI Interchange Schedule quickly enough to recover ACE within the required 15 minutes. The Unit 6 trip occurred at 2:32:28 p.m. It took approximately ten minutes to restore internet access allowing EEI to adjust its Interchange Schedules. EEI reached 81% recovery at the 15 minute mark and recovered ACE to the pre-Disturbance value at 2:49:00 p.m. Full recovery took 16 minutes and 32 seconds. The root cause of this noncompliance was the unexpected loss of internet occurring at the same time as the loss of generation, causing a delay in the ability to adjust Interchange Schedules. This noncompliance started at 2:47:28 p.m. on May 15, 2017, at the end of the Disturbance Recovery Period and ended at 2:49:00 on May 15, 2017, when EEI recovered its ACE to the pre-Disturbance value. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). EEI’s inability to return ACE to its pre-Disturbance value within 15 minutes could have resulted in a frequency imbalance lasting longer than necessary, thereby stressing the reliability of the BPS. Based upon 2014 data, EEI provides only 0.12% of the generation to the Eastern Interconnection. EEI recovered 81% of its ACE in 15 minutes and fully restored ACE 1 minute 32 seconds later. Frequency was normal during the entire recovery period (average of approximately 59.991 from the occurrence start till 20 minutes after the start). Unit 6 was generating only 161 MW and less than 10 MVAR at the time of the occurrence. The five remaining Joppa generators remained online and stable throughout the occurrence. EEI’s systems supervisor maintained contact with the affected the TO and its Reliability Coordinator throughout the occurrence. No harm is known to have occurred. SERC considered EEI’s compliance history and determined that there were no relevant instances of noncompliance. SERC considered the compliance history of a deregistered entity, Electric Energy, Inc. (NCR01230) in determining the disposition track. Electric Energy, Inc. (NCR01230)’s relevant prior noncompliance with BAL-002-0 R4 includes NERC Violation IDs SERC200800226 and SERC2011007386. SERC determined that Electric Energy, Inc. (NCR01230)’s BAL-002-0 R4 compliance history should not serve as a basis for a penalty because both prior instances of noncompliance were mitigated more than six years prior to the instance noncompliance, indicating that this is not a frequent or widespread problem requiring a penalty. | To mitigate this noncompliance, EEI: 1) Notified EEI systems operators that effective May 16, 2017, they should decrease EEI schedules by 250 MW for loss of a unit to provide a shorter recovery period. 2) EEI/Dynegy IT group installed a firewall and router in Systems Primary and Backup Control Centers with auto-failover to a cellular connection. This provides secure and redundant internet access for critical applications; and 3) EEI will maintain an additional 33MW (19%) of Contingency Reserves during the third quarter of 2017.
2017-11-30 | SERC Reliability Corporation (SERC) | ETEC-Hardin County Peaking Facility (ETEC-HCPF) | NCR11656 | SERC2017018272 | MOD-025-2 | R1 | On August 25, 2017, ETEC-HCPF submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. ETEC-HCPF did not meet the implementation schedule to provide its Transmission Planner (TP) with verification of the Real Power capability of 40% of its applicable Facilities by July 1, 2016. On June 30, 2016, ETEC-HCPF completed Real Power testing for unit 1. On July 2, 2016, ETEC-HCPF completed Real Power testing for unit 2. On July 29, 2016, ETEC-HCPF provided the verification results of the Real Power capability for both units to the TP. On July 6, 2017, ETEC-HCPF, as part of a review during development of an internal compliance monitoring tool and review of associated documentation, discovered that it did not provide the Real Power capability of its units to its TP by July 1, 2016 as required. ETEC-HCPF determined the primary cause of the noncompliance appears to a misunderstanding due to poor communications between different groups within the operating company. This noncompliance started on July 1, 2016, when ETEC-HCPF did not meet the implementation schedule and ended on July 29, 2016, when ETEC-HCPF provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ETEC-HCPF’s lack of information could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the ETEC-HCPF facility consists of two natural gas units with nameplate ratings of 101.8 MVA each. The 12-month facility capacity factor for the period ending June 30, 2017 was 4.56%. The NERC implementation plan allows ETEC-HCPF to verify Real Power output of only one unit by July 1, 2016 and allows an additional year for the verification and notification to the TP of the remaining generation, therefore a delay of 29 days for the 40% requirement results in minimal additional risk. ETEC-HCPF provided verification of the Real Power capability for 100% of its units on July 29, 2016, further reducing the risk. No harm is known to have occurred. SERC considered ETEC–HCPF's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETEC-HCPF: 1) completed Real Power testing for unit 1 and unit 2; 2) provided test results to the TP; and 3) created NERC Preventive Maintenance (PM) tasks in its Main Saver compliance management scheduling program to notify plant personnel the next time testing is due to be completed. This PM will notify the plant at least six months prior to the 5 year compliance anniversary.
2017-11-30 | SERC Reliability Corporation (SERC) | ETEC-Hardin County Peaking Facility (ETEC-HCPF) | NCR11656 | SERC2017018273 | MOD-025-2 | R2 | On August 25, 2017, ETEC-HCPF submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. ETEC-HCPF did not meet the implementation schedule to provide its Transmission Planner (TP) with verification of the Reactive Power capability of 40% of its applicable Facilities by July 1, 2016. On June 30, 2016, ETEC-HCPF completed Reactive Power testing for unit 1. On July 2, 2016, ETEC-HCPF completed Reactive Power testing for unit 2. On July 29, 2016, ETEC-HCPF provided the verification results of the Reactive Power capability for both units to the TP. On July 6, 2017, ETEC-HCPF, as part of a review during development of an internal compliance monitoring tool, discovered that it did not provide the Reactive Power capability of its units to its TP by July 1, 2016. ETEC-HCPF determined the primary cause of the noncompliance appears to a misunderstanding due to poor communications between different groups within the operating company. This noncompliance started on July 1, 2016, when ETEC-HCPF did not meet the implementation schedule, and ended on July 29, 2016, when ETEC-HCPF provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ETEC-HCPF’s lack of information could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the ETEC-HCPF facility consists of two natural gas units with nameplate ratings of 101.8 MVA each. The 12-month facility capacity factor for the period ending June 30, 2017 was 4.56%.The NERC implementation plan allows ETEC-HCPF to verify Reactive Power output of only one unit by July 1, 2016 and allows an additional year for the verification and notification to the TP of the remaining generation, therefore a delay of 29 days for the 40% requirement resulted in minimal additional risk. ETEC-HCPF provided verification of the Reactive Power capability for 100% of its units on July 29, 2016, further reducing the risk. No harm is known to have occurred. SERC considered ETEC–HCPF's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETEC-HCPF: 1) completed Reactive Power testing for unit 1 and unit 2; 2) provided test results to the TP; and 3) created NERC Preventive Maintenance tasks (PM) in its Main Saver compliance management scheduling program to notify plant personnel the next time testing is due to be completed. This PM will notify the plant at least six months prior to the 5 year compliance anniversary.
2017-11-30 | SERC Reliability Corporation (SERC) | ETEC-Hardin County Peaking Facility (ETEC-HCPF) | NCR11656 | SERC2017018422 | PRC-024-2 | R2 | On October 3, 2017, ETEC-HCPF submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. ETEC-HCPF did not meet the implementation schedule requirement to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units for 40% of its applicable units by July 1, 2016. On January 1, 2016, operational control of ETEC-HCPF transferred from one party to another. Prior to that date, ETEC-HCPF management was not aware of the new PRC-024-2 Standard. After January 1, 2016, the operating party informed Hardin management of the PRC-024-2 requirements. In June 2016, a consultant completed the relay settings review. The review identified that the generator voltage protective relay settings were within the no trip zone identified in the Standard. Plant management contacted the manufacturer to determine if the proposed settings were within the operating parameters of the plant or if it would put the plant at risk for damage. On June 30, 2016, the manufacturer responded that the proposed settings were acceptable. On July 12, 2016, the earliest date the contractor relay specialist was available, ETEC-HCPF made the changes to the relay settings to both units. ETEC-HCPF changed the overvoltage pick-up from 126 V (109.6% of 115V Nominal Voltage) to 127V (110.4% of 115 V Nominal Voltage). ETEC-HCPF changed the undervoltage pick-up time from 1 second to 3 seconds. On September 1, 2017, ETEC-HCPF identified the noncompliance after SERC staff asked if ETEC-HCPF was compliant with PRC-019 and PRC-024 following ETEC-HCPF’s Self-Report of MOD-025-2 The primary cause of the noncompliance was the lack of awareness by ETEC-HCPF ownership of new NERC Standards. This noncompliance started on July 1, 2016, when ETEC-HCPF did not set its voltage protective relaying and ended on July 12, 2016, when it completed the relay setting changes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ETEC-HCPF’s failure to verify that the generator voltage relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, minimal relay setting changes were required and the delay was only 12 days. The ETEC-HCPF facility consists of two natural gas units with nameplate ratings of 101.8 MVA each. The 12-month facility capacity factor for the period ending June 30, 2017 was 4.56%. The NERC implementation plan allowed ETEC-HCPF to verify that the generator voltage protective relaying does not trip within the “no trip zone” of only one unit by July 1, 2016 and allowed an additional year for the verification of the second unit. ETEC-HCPF reset the generator voltage relays for both units on July 12, 2016, further reducing the risk. No harm is known to have occurred. SERC considered ETEC–HCPF's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETEC-HCPF: 1) made relay setting changes for both units; 2) allows no employees at the ETEC-HCPF plant to make changes to a relay or to do anything with a relay beyond a self-test or reset. Therefore, the relay settings are not changed outside of a controlled process; 3) assigned NERC Compliance oversight to the operating party in January 2016. The operating party reviews new and revised standards and communicates these changes with affected ETEC-HCPF management; and 4) set-up PMs to review relay settings for compliance with PRC-019 and PRC-024 every five years.
2017-11-30 | SERC Reliability Corporation (SERC) | ETEC-San Jacinto County Peaking Facility (ETEC-SJCPF) | NCR11657 | SERC2017018274 | MOD-025-2 | R1 | On August 25, 2017, ETEC–SJCPF submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. ETEC–SJCPF did not meet the implementation schedule to provide its Transmission Planner (TP) with verification of the Real Power capability of 40% of its applicable Facilities by July 1, 2016. On July 6, 2017, ETEC–SJCPF, as part of a review during development of an internal compliance monitoring tool, discovered that it did not provide the Real Power capability of its units to its TP by July 1, 2016. On June 29, 2016, ETEC–SJCPF completed Real Power testing for unit 1 and unit 2. On July 29, 2016, ETEC–SJCPF provided the verification results of the Real Power capability for both units to the TP. ETEC–SJCPF determined the primary cause of the noncompliance appears to a misunderstanding due to poor communications between different groups within the operating company. This noncompliance started on July 1, 2016, when ETEC–SJCPF did not meet the implementation schedule and ended on July 29, 2016, when ETEC–SJCPF provide its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ETEC–SJCPF’s lack of information could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the ETEC–SJCPF facility consists of two natural gas units with nameplate ratings of 101.8 MVA each. The 12-month facility capacity factor for the period ending June 30, 2017 was 15.35%. The NERC implementation plan allows ETEC–SJCPF to verify Real Power output of only one unit by July 1, 2016 and allows an additional year for the verification and notification to the TP of the remaining generation, therefore a delay of 29 days for the 40% requirement results in minimal additional risk. ETEC–SJCPF provided verification of the Real Power capability for 100% of its units on July 29, 2016, further reducing the risk. No harm is known to have occurred. SERC considered ETEC–SJCPF's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETEC–SJCPF: 1) completed Real Power testing for unit 1 and unit 2; 2) provided test results to the TP; and 3) created NERC Preventive Maintenance (PM) tasks in its compliance management scheduling program to notify plant personnel the next time testing is due to be completed. This PM will notify the plant at least six months prior to the 5 year compliance anniversary.
2017-11-30 | SERC Reliability Corporation (SERC) | ETEC-San Jacinto County Peaking Facility (ETEC-SJCPF) | NCR11657 | SERC2017018275 | MOD-025-2 | R2 | On August 25, 2017, ETEC-SJCPF submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. ETEC-SJCPF did not meet the implementation schedule to provide its Transmission Planner (TP) with verification of the Reactive Power capability of 40% of its applicable Facilities by July 1, 2016. On July 6, 2017, ETEC-SJCPF, as part of a review during development of an internal compliance monitoring tool, discovered that it did not provide the Reactive Power capability of its units to its TP by July 1, 2016. On June 29, 2016, ETEC-SJCPF completed Reactive Power testing for unit 1 and unit 2. On July 29, 2016, ETEC-SJCPF provided the verification results of the Reactive Power capability for both units to the TP. ETEC-SJCPF determined the primary cause of the noncompliance appears to a misunderstanding due to poor communications between different groups within the operating company. This noncompliance started on July 1, 2016, when ETEC-SJCPF did not meet the implementation schedule and ended on July 29, 2016, when ETEC-SJCPF provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ETEC-SJCPF’s lack of information could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the ETEC-SJCPF facility consists of two natural gas units with nameplate ratings of 101.8 MVA each. The 12-month facility capacity factor for the period ending June 30, 2017 was 15.35%.The NERC implementation plan allows ETEC-SJCPF to verify Reactive Power output of only one unit by July 1, 2016 and allows an additional year for the verification and notification to the TP of the remaining generation, therefore a delay of 29 days for the 40% requirement results in minimal additional risk. ETEC-SJCPF provided verification of the Reactive Power capability for 100% of its units on July 29, 2016, further reducing the risk. No harm is known to have occurred. SERC considered ETEC–SJCPF's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETEC-SJCPF: 1) completed Reactive Power testing for unit 1 and unit 2; 2) provided test results to the TP; and 3) created NERC Preventive Maintenance (PM) tasks in its compliance management scheduling program to notify plant personnel the next time testing is due to be completed. This PM will notify the plant at least six months prior to the 5 year compliance anniversary.
2017-11-30 | SERC Reliability Corporation (SERC) | ETEC-San Jacinto County Peaking Facility (ETEC-SJCPF) | NCR11657 | SERC2017018423 | PRC-024-2 | R2 | On October 3, 2017, ETEC-SJCPF submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. ETEC-SJCPF did not meet the implementation schedule to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units for 40% of applicable units by July 1, 2016. On January 1, 2016, operational control of ETEC-SJCPF transferred from the owner to another party. Prior to that date, ETEC-SJCPF management was not aware of the new PRC-024-2 Standard. After January 1, 2016, the operating party informed ETEC-SJCPF management of the PRC-024-2 requirements. In June 2016, a consultant completed the relay settings review. The review identified that the generator voltage protective relay settings were within the no trip zone identified in the Standard. Plant management contacted the manufacturer to determine if the proposed settings were within the operating parameters of the plant or if it would put the plant at risk for damage. On June 30, 2016, the manufacturer responded that the proposed settings were acceptable. On July 12, 2016, the earliest date the contractor relay specialist was available, ETEC-SJCPF made the changes to the relay settings to both units. ETEC-SJCPF changed the overvoltage pick-up from 126 V (109.6% of 115V Nominal Voltage) to 127V (110.4% of 115 V Nominal Voltage). ETEC-SJCPF changed the undervoltage pick-up time from 1 second to 3 seconds, On September 1, 2017, ETEC-SJCPF identified the noncompliance after SERC staff asked if ETEC-SJCPF was compliant with PRC-019 and PRC-024 following ETEC-SJCPF’s Self-Report of MOD-025-2. The primary cause of the noncompliance was the lack of awareness by ETEC-SJCPF ownership of new NERC Standards. This noncompliance started on July 1, 2016, when ETEC-SJCPF did not set its voltage protective relaying and ended on July 12, 2016, when it completed the relay setting changes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ETEC-SJCPF’s failure to verify that the generator voltage relays are set not to trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, minimal relay setting changes were required and the delay was only 12 days. The ETEC-SJCPF facility consists of two natural gas units with nameplate ratings of 101.8 MVA each. The 12-month facility capacity factor for the period ending June 30, 2017 was 15.35%. The NERC implementation plan allows ETEC-SJCPF to verify that the generator voltage protective relaying does not trip within the “no trip zone” of only one unit by July 1, 2016 and allows an additional year for the verification of the second unit. ETEC-SJCPF reset the generator voltage relays for both units on July 12, 2016, further reducing the risk. No harm is known to have occurred. SERC considered ETEC–SJCPF's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, ETEC-SJCPF: 1) made relay setting changes for both units; 2) allows no employees at the ETEC-SJCPF plant to make changes to a relay or to do anything with a relay beyond a self-test or reset. Therefore, the relay settings are not changed outside of a controlled process; 3) assigned NERC Compliance oversight to a third party in January 2016. The operating party reviews new and revised standards and communicates these changes with affected ETEC-SJCPF management; and 4) set-up PMs to review relay settings for compliance with PRC-019 and PRC-024 every five years.
2017-11-30 | SERC Reliability Corporation (SERC) | Mobile Energy LLC (Mobile) | NCR11482 | SERC2017018004 | MOD-025-2 | R1 | On July 24, 2017, Mobile submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. Mobile failed to meet the NERC implementation schedule to provide its Transmission Planner (TP) with verification of the Real Power capability of 40% of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. On June 4, 2012, Mobile performed the SERC regional generator testing that demonstrated the facility’s Real Power capabilities as required by its Transmission Operator (TOP). Mobile incorrectly believed that the SERC regional generator tests met the MOD-025-2 R1 testing requirements. On May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, Mobile discovered that the tests that it completed in 2012 did not meet all of the testing requirements in MOD-025-2 R1 Attachment 1 and therefore it did not complete the generator Real Power tests by July 1, 2016. The primary cause of the noncompliance was Mobile’s misinterpretation of the Attachment 1 testing requirements. This noncompliance started on July 1, 2016, when Mobile did not meet the implementation schedule and ended on August 7, 2017, when Mobile provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Mobile’s failure to provide Real Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, in 2012, Mobile completed testing that demonstrated the facility’s Real Power capabilities as required by previous versions of the MOD Standards, and therefore the TP was aware of certain unit capabilities. Mobile is a 232 MW facility that operated at a 37% capacity factor for the 12-months prior to June 30, 2017. No harm is known to have occurred. SERC considered Mobile's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Mobile: 1) conducted the Real Power tests for its generators; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the four tests that Mobile must perform every five years. The PM is designed to notify plant personnel six months prior to the tests due dates; 4) performed supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure staff understands the implementation of new or revised standards or staff seeks guidance from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Mobile Energy LLC (Mobile) | NCR11482 | SERC2017018005 | MOD-025-2 | R2 | On July 24, 2017, Mobile submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. Mobile failed to meet the NERC implementation schedule to provide its Transmission Planner (TP) with verification of the Reactive Power capability of 40% of its applicable Facilities by July 1, 2016. On May 19, 2017, Mobile determined that it misinterpreted the testing requirements listed in Attachment 1. Since Mobile normally operates its gas turbines generator (GTG) at base load, Mobile believed that testing the GTG at the base load level met the maximum and minimum Reactive Power testing requirements. However, a third-party contractor reviewed the test results and provided Mobile with guidance that NERC intended that the minimum load Reactive Power test was to demonstrate the facility’s Reactive Power capabilities throughout its entire operating range. The primary cause of the noncompliance was Mobile’s misinterpretation of the Standard. This noncompliance started on July 1, 2016, when Mobile did not meet the implementation schedule and ended on August 7, 2017, when Mobile provide its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Mobile’s failure to provide correct modelling of unit capabilities could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the Mobile facility was able to supply the Reactive Power requested by the Transmission Operator during the period of noncompliance. Mobile is a 232 MW facility that operated at a 37% capacity factor for the 12-months prior to June 30, 2017. No harm is known to have occurred. SERC considered Mobile's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Mobile: 1) conducted the Reactive Power tests for its generators; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the four tests that must be performed every five years. The PM is designed to notify plant personnel six months prior to the tests due dates; 4) performed supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards are understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Santa Rosa Energy Center, LLC (SREC) | NCR11483 | SERC2017018010 | MOD-025-2 | R1 | On July 24, 2017, SREC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R1. SREC did not meet the implementation schedule to provide its Transmission Planner (TP) with verification of the Real Power capability of 40% of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. On June 6, 2012, SREC completed the testing required by its Transmission Operator (TOP) that demonstrated the facility’s Real Power capabilities however; these tests did not meet the requirements for MOD-025-2 Attachment 1. SREC incorrectly believed this testing showed compliance with MOD-025-2 R1 and as such, SREC would need to perform the next tests by July 6, 2017. However, on May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, SREC determined that the testing required by the TO did not satisfy all of the MOD-025-2 R1 requirements. SREC determined the primary cause of the noncompliance was a misinterpretation of the testing requirements contained in Attachment 1. This noncompliance started on July 1, 2016, when SREC did not meet the implementation schedule and ended on July 10, 2017, when SREC provided its TP with verification of the Real Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SREC’s failure to verify and provide Real Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, on June 6, 2012, SREC completed the testing required by its TOP that demonstrated the facility’s Real Power capabilities as required by its TOP therefore the TOP was aware of certain unit capabilities. SREC is a one gas turbine and one steam turbine generator combined cycle plant with a maximum capacity of 236 MW. SREC operated at a 51% capacity factor for the 12-month period ending June 2017. No harm is known to have occurred. SERC considered SREC's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SREC: 1) conducted the Real Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Real Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests’ due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards are clearly understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Santa Rosa Energy Center, LLC (SREC) | NCR11483 | SERC2017018013 | MOD-025-2 | R2 | On July 24, 2017, SREC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with MOD-025-2 R2. SREC did not meet the implementation schedule to provide its Transmission Planner (TP) with verification of the Reactive Power capability of 40% of its applicable Facilities in accordance with Attachment 1 by July 1, 2016. On May 19, 2017, while populating an internal compliance tracking tool and reviewing associated documentation, SREC discovered that it did not provide the required Reactive Power capability of its units to its TP by July 1, 2016. On June 6, 2012, SREC completed the testing required by its Transmission Operator (TOP) that demonstrated the facility’s Reactive Power capabilities however; these tests did not meet the requirements for MOD-025-2 Attachment 1. SREC incorrectly believed this testing showed compliance with MOD-025-2 R2 and as such, SREC would need to perform the next tests by July 6, 2017. However, after review of data and discussions while populating the tracking tool, SREC determined that this testing did not satisfy all of the MOD-025-2 R2 requirements. On June 21, 2017, SREC conducted the Reactive Power tests that demonstrated the facility’s Reactive Power capabilities as required under MOD-025-2. On July 10, 2017, SREC provided the test results to the TP. SREC determined the primary cause of the noncompliance was a misinterpretation of the testing requirements contained in Attachment 1. This noncompliance started on July 1, 2016, when SREC did not meet the implementation schedule and ended on July 10, 2017, when SREC provided its TP with verification of the Reactive Power capability of its applicable Facilities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SREC’s failure to verify and provide Reactive Power capability to the TP could result in incorrect modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, on June 6, 2012, SREC completed the testing required by its TOP that demonstrated the facility’s Reactive Power capabilities therefore the TOP was aware of certain unit capabilities. SREC is a one gas turbine and one steam turbine generator combined cycle plant with a maximum capacity of 236 MW. SREC operated at a 51% capacity factor for the 12-month period ending June 2017. No harm is known to have occurred. SERC considered SREC's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, SREC: 1) conducted the Reactive Power tests; 2) provided the test results to the TP; 3) created a NERC Preventive Maintenance (PM) task in its compliance management tool that indicates the Reactive Power tests that must be performed every five years and the PM is designed to notify plant personnel six months prior to the tests’ due dates; 4) conducted supplemental training on the violation for the operating staff involved with the testing; and 5) revised its Internal Compliance Program (ICP) to ensure implementation of new or revised standards are clearly understood or guidance is sought from NERC and/or Regional Entities via established processes.
2017-11-30 | SERC Reliability Corporation (SERC) | Shelby County Energy Center, LLC (SCEC) | NCR11629 | SERC2016016283 | PRC-024-2 | R1 | On September 29, 2016, SCEC submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. SCEC stated that it had not completed its verification of generator frequency protection setpoints for 40% of its applicable generating units by July 1, 2016. The implementation plan for PRC-024-2 requires the GO to verify its generator frequency Protection System setpoints in annual increments beginning with 40% of its generation by July 1, 2016. SCEC has eight 44 MW combustion turbines, so in order to comply with the requirement, SCEC was required to perform the verification of at least four of the units by July 1, 2016. SCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for PRC-024-2 R1 compliance, and did not understand the requirement for verification of the frequency protection setpoint. On June 29, 2016, a third-party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to SCEC on or about July 1, 2016. The root cause of the noncompliance was an incorrect understanding of compliance requirements and inadequate contract oversight. SCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The noncompliance started on July 1, 2016, when SCEC missed the implementation schedule requirements, and ended on May 1, 2017, when SCEC completed its mitigating activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCEC’s failure to properly verify the frequency protection setpoints could result in generators unnecessarily tripping off-line. SCEC contributes only 352 MW to the grid while operating and operates at approximately less than a 5% capacity factor. When SCEC has operated during the period of noncompliance, no trips occurred due to incorrect setpoints. No harm is known to have occurred. SERC considered SCEC's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate the noncompliance, SCEC: 1) scheduled all necessary verification testing to be completed; 2) developed and will annually review an internal compliance procedure while also updating upon any standard revisions; 3) implemented an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate; 4) added PRC-024 to the compliance tracker with appropriate lead-time so as to hire consultants to help with setpoint studies; 5) will continue to use third-party mock audits and internal self-assessments as a second check on the compliance tracker; and 6) begin holding bi-weekly compliance calls to ensure plant staffs are aware of upcoming deadlines and compliance obligations.
2017-11-30 | SERC Reliability Corporation (SERC) | Shelby County Energy Center, LLC (SCEC) | NCR11629 | SERC2017017254 | PRC-024-2 | R2 | On March 23, 2017, Shelby County Energy Center (SCEC) submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. SCEC stated that it had not completed its verification of generator voltage protection setpoints for 40% of its applicable generating units by July 1, 2016. The implementation plan for PRC-024-2 requires the GO to verify its generator voltage Protection System setpoints in annual increments beginning with 40% of its generation by July 1, 2016. SCEC has eight 44 MW combustion turbines, so in order to comply with the requirement, SCEC was required to perform the verification of at least four of the units by July 1, 2016. SCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for PRC-024-2 R2 compliance, and did not understand the requirement for verification of the voltage protection setpoint. On June 29, 2016, a third-party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to SCEC on or about July 1, 2016. The root cause of the noncompliance was an incorrect understanding of compliance requirements and inadequate contract oversight. SCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The noncompliance started on July 1, 2016, when SCEC missed the implementation schedule requirements, and ended on May 1, 2017, when SCEC completed its mitigating activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCEC’s failure to properly verify the voltage protection setpoints could result in generators unnecessarily tripping off-line. SCEC contributes only 352 MW to the grid while operating and operates at approximately less than a 5% capacity factor. When SCEC has operated during the period of noncompliance, no trips occurred due to incorrect setpoints. No harm is known to have occurred. SERC considered SCEC's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate the noncompliance, SCEC: 1) scheduled all necessary verification testing to be completed; 2) developed and will annually review an internal compliance procedure while also updating upon any standard revisions; 3) implemented an internal software product that allows for tracking of compliance reporting functions and internal deadlines that are deemed appropriate; 4) added PRC-024 to the compliance tracker with appropriate lead-time so as to hire consultants to help with setpoint studies; 5) will continue to use third-party mock audits and internal self-assessments as a second check on the compliance tracker; and 6) begin holding bi-weekly compliance calls to ensure plant staffs are aware of upcoming deadlines and compliance obligations.
2017-11-30 | SERC Reliability Corporation (SERC) | The Dow Chemical Company (Dow) | NCR09037 | SERC2017017801 | MOD-025-2 | R1 | On June 23, 2017, Dow submitted a Self-Report stating that, as a Generator Owner it was in noncompliance with MOD-025-2 R1. Dow did not properly notify its Transmission Planner (TP) of its Real Power verification in accordance with the MOD-025-2 implementation plan, which required Dow to verify the Real Power capability of 40% of its generating units by July 1, 2016. In March 2016, Dow personnel identified the need to perform a Real Power verification and to notify its TP, however it took no action at that time. In the week of July 1, 2016, Dow discovered the oversight when it held a discussion with a newly-hired third-party NERC compliance consultant in another Region. The cause of the noncompliance was insufficient monitoring of and response to impending dates of compliance enforcement. This noncompliance started on July 1, 2016, when Dow had not verified the Real Power capability of 40% of its generating units and provided that information to its TP, and ended on November 30, 2016, when Dow notified its TP of the Real Power capability of 80% of its applicable units. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to provide verification of real power capability may result in inaccurate planning models and inaccurate assessment of bulk power system reliability. However, Dow had already submitted some Real Power data to the TP for modeling purposes. When Dow performed the Real Power verifications, it made no changes to the data already provided to the TP. Dow is a five-unit facility with a total output of 991 MW and operated with a 50% capacity factor in 2016. Dow is a cogenerator providing power and steam to an adjacent petrochemical plant. The Balancing Authority does not dispatch it and it supplies only excess generation to the grid. Therefore, if any errors in the plant data existed, it would have presented a minor variation in planning results. Dow also completed Real Power verification tests on 80% of its generating units and provided the information to its TP by November 30, 2016, well in advance of the July 1, 2018 deadline for that level of verification, reducing the risk. No harm is known to have occurred. SERC considered Dow’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Dow: 1) completed Real Power verification tests on four out of five units and submitted the results to the TP; 2) added a compliance task to Dow's Internal Compliance Program (ICP) to prompt any future requirement activities; and 3) contracted with a third party to provide quarterly guidance on upcoming deadlines and requirements to prevent recurrence.
2017-11-30 | SERC Reliability Corporation (SERC) | The Dow Chemical Company (Dow) | NCR09037 | SERC2017017810 | MOD-025-2 | R2 | On June 26, 2017, Dow submitted a Self-Report stating that, as a Generator Owner it was in noncompliance with MOD-025-2 R2. Dow did not properly notify its Transmission Planner (TP) of its Reactive Power verification in accordance with the MOD-025-2 implementation plan, which required Dow to verify the Reactive Power capability of 40% of its generating units by July 1, 2016. In March 2016, Dow personnel identified the need to perform a Reactive Power verification and to notify its TP, however, it took no action at that time. In the week of July 1, 2016, Dow discovered the oversight when it held a discussion with a newly-hired third-party NERC compliance consultant in another Region. The cause of the noncompliance was insufficient monitoring of and response to impending dates of compliance enforcement. This noncompliance started on July 1, 2016, when Dow had not verified the Reactive Power capability of 40% of its generating units and provided that information to its TP, and ended on November 30, 2016 when Dow notified its TP of the Reactive Power capability of 80% of its applicable units. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to provide verification of Reactive Power capability may result in inaccurate planning models and inaccurate assessment of bulk power system reliability. However, Dow had already submitted some Reactive Power data to the TP for modeling purposes. When Dow performed the Reactive Power verifications, it made no changes to the data already provided to the TP. Dow is a five-unit facility with a total output of 991 MW and operated with a 50% capacity factor in 2016. Dow is a cogenerator providing power and steam to an adjacent petrochemical plant. The Balancing Authority does not dispatch it and it supplies only excess generation to the grid. Therefore, if any errors in the plant data existed, it would have presented a minor variation in planning results. Dow also completed Reactive Power verification tests on 80% of its generating units and provided the information to its TP by November 30, 2016, well in advance of the July 1, 2018 deadline for that level of verification, reducing the risk. No harm is known to have occurred. SERC considered Dow’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Dow: 1) completed Reactive Power verification tests on four out of five units and submitted the results to the TP; 2) added a compliance task to Dow's Internal Compliance Program (ICP) to prompt any future requirement activities; and 3) contracted with a third party to provide quarterly guidance on upcoming deadlines and requirements to prevent recurrence.
2017-11-30 | SERC Reliability Corporation (SERC) | The Dow Chemical Company (Dow) | NCR09037 | SERC2017017802 | PRC-019-2 | R1 | On June 23, 2017, Dow submitted a Self-Report stating that, as a Generator Owner it was in noncompliance with PRC-019-2 R1. Dow did not have proper documentation of coordination of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions in accordance with the PRC-019 implementation plan, which required Dow to verify 40% of its applicable Facilities by July 1, 2016. In March 2016, Dow personnel identified the need to perform a Real Power verification and the related verification of control system coordination, however it took no action at that time. During the week of July 1, 2016, Dow discovered the oversight when it held a discussion with a newly-hired third-party NERC compliance consultant in another Region. Dow also discovered that it did not have sufficient documentation to verify coordination of generating unit voltage regulating controls, limit functions, equipment capabilities and Protection System settings. The cause of the noncompliance was insufficient monitoring of and response to impending dates of compliance enforcement. This noncompliance started on July 1, 2016, when Dow did not verify coordination of its voltage regulating system controls with its Protection Systems as required by the PRC-019 implementation plan, and ended on June 19, 2017, when Dow performed the required coordination on four of five generating units. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Dow’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, Dow is a five-unit facility with a total output of 991 MW and operated with a 50% capacity factor in 2016. It interconnects as a cogenerator providing power and steam to an adjacent petrochemical plant and provides an average of 340 MW to the grid when it operates. Therefore, if coordination conflicts had resulted in unit problems, it would not have caused a significant loss to system operation. Dow has until July 1, 2019 to become fully compliant with the requirements and verified the required coordination of 80% of its units by July 1, 2017, a year earlier than required under the PRC-019-2 implementation plan, reducing the risk. Dow has not experienced a trip or loss of a generator unit during operation indicating there are no apparent problems with control system coordination. No harm is known to have occurred. SERC considered Dow’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Dow: 1) completed unit control verifications on four of five units; 2) added a compliance task to Dow's Internal Compliance Program (ICP) to prompt any future requirement activities; and 3) contracted with a third party to provide quarterly guidance on upcoming deadlines and requirements to prevent recurrence.
2017-11-30 | SERC Reliability Corporation (SERC) | The Dow Chemical Company (Dow) | NCR09037 | SERC2017017953 | PRC-024-2 | R1 | On July 17, 2017, Dow submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R1. Dow did not have proper documentation that its generator frequency trip setpoints were outside the no-trip zones for 40% of its applicable generating units by July 1, 2016, as required by the PRC-024-2 implementation plan. On July 7, 2017, Dow discussed earlier self-reported noncompliances with SERC staff and discovered it had a noncompliance of PRC-024-2 R1 as well. The cause of the noncompliance was insufficient monitoring of, and response to, impending dates of compliance enforcement. This noncompliance started on July 1, 2016, when Dow did not verify that its generator frequency trip setpoints were outside the no-trip zones as required by the PRC-024-2 implementation plan, and ended on July 7, 2017, when Dow verified its frequency protective relay setpoints. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Dow’s failure to verify the frequency trip setpoint could allow the unit to trip rather than ride through a frequency disturbance. However, Dow is a five-unit facility with a total output of 991 MW and operated with a 50% capacity factor. It interconnects as a cogenerator providing power and steam to an adjacent petrochemical plant and provides an average of 340 MW to the grid when it operates. Therefore, if inadequate trip setpoints resulted in a premature trip, it would not have been significant loss to system operation. Dow has until July 1, 2019 to become fully compliant with the requirements. Dow has not experienced a trip or loss of a generator unit during operation. Furthermore, Dow identified no frequency-related trip setpoints inside the no-trip zone. No harm is known to have occurred. SERC considered Dow’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Dow: 1) reviewed its frequency protective settings and documented the settings along with PRC-024 documentation; 2) added a compliance task to Dow's Internal Compliance Program (ICP) to prompt any future requirement activities; and 3) contracted with a third party to provide quarterly guidance on upcoming deadlines and requirements to prevent recurrence.
2017-11-30 | SERC Reliability Corporation (SERC) | The Dow Chemical Company (Dow) | NCR09037 | SERC2017017952 | PRC-024-2 | R2 | On July 17, 2017, Dow submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-024-2 R2. Dow did not have proper documentation that its generator voltage trip setpoints were outside the no-trip zones for 40% of its applicable generating units by July 1, 2016, as required by the PRC-024-2 implementation plan. On July 7, 2017, Dow discussed earlier self-reported issues with SERC staff and discovered it had a noncompliance of PRC-024-2 R2 as well. The cause if the noncompliance was insufficient monitoring of, and response to, impending dates of compliance enforcement. This noncompliance started on July 1, 2016, when Dow did not verify that its generator voltage trip setpoints were outside the no-trip zones as required by the PRC-024-2 implementation plan, and ended on July 14, 2017 when Dow verified its voltage trip setpoints and notified its Transmission Planner (TP) and Balancing Authority (BA) of its limitation in accordance with R3. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Dow’s failure to verify the voltage trip setpoint could allow the unit to trip rather than fide through a voltage disturbance. However, Dow is a five-unit facility with a total output of 991 MW and operated with a 50% capacity factor. It interconnects as a cogenerator providing power and steam to an adjacent petrochemical plant and provides an average of 340 MW to the grid when it operates. Therefore, if inadequate trip setpoints resulted in a premature trip, it would not have been significant loss to system operation. Dow has until July 1, 2019 to become fully compliant with the requirements. Dow has not experienced a trip or loss of a generator unit during operation. Furthermore, Dow identified that only the volts-per-hertz relay setpoints are inadequate, but the units should not trip if the automatic voltage regulators are controlling in automatic, Dow informed the TP and BA of that fact in accordance with R3. No harm is known to have occurred. SERC considered Dow’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this noncompliance, Dow: 1) verified the voltage trip setpoints for its generators and notified its TP and BA of setpoints within the no-trip zone for voltage; and 2) contracted with a third party to provide quarterly guidance on upcoming deadlines and requirements to prevent recurrence.
2017-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Red Hills Wind Project, LLC. (RHWP) | NCR10304 | SPP2017017051 | PRC-005-1.1b | R2 | On February 24, 2017, RHWP submitted a Self-Certification stating that, as a Generator Owner (GO), it had an issue of noncompliance with PRC-005-6 R3 because RHWP did not maintain its Communication Systems in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed in PRC-005-6, Table 1-2. PRC-005-6 Table 1-2 requires verification of unmonitored communication systems functionality every four calendar months. RHWP’s last record of Communication System testing was September 2014. The duration of this instance of noncompliance was from February 1, 2015, the date the communication systems inspections should have occurred, through March 24, 2017, the date RHWP’s Communications Systems were tested and verified. The root cause of this instance of noncompliance was human error and lack of internal controls. RHWP inadvertently omitted the fields documenting Communication Systems functional verification from its High Voltage Substation Maintenance and Inspection Program Monthly Checklist during a revision of the checklist in 2014. As a result, the last verification of Communication System functionality was performed in September 2014. Additionally, RHWP did not have a review process in place to verify the completion of the High Voltage Substation Maintenance and Inspection Program Monthly Checklist and ensure correction of unresolved maintenance issues. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform Communication Systems testing has the potential to affect the reliability of the BPS by increasing the risk that Communication Systems will fail, causing the misoperation of the associated Protection Systems. The risk to the BPS was mitigated because the noncompliance was limited to two of RHWP’s 44 (4.55%) Protection System Devices and the implicated Communication Systems were determined to be operating correctly during subsequent testing. Moreover, RHWP is a small intermittent wind generation resource, consisting of 82, 1.5MW Wind Turbine Generators for an aggregate capacity of 123 MW. No harm is known to have occurred. RHWP has no relevant prior violations of PRC-005-6 R3 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, RHWP: 1) completed and documented Communication Systems testing on February 25, 2017; 2) updated the HVSMIP monthly checklist to include Communication System testing; and 3) required a peer review of the HVSMIP checklist to ensure that the proper form was used, the form was complete, and that there were no unresolved maintenance issues. SPP RE has verified the completion of all mitigation activity.
2017-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Sunflower Electric Power Corporation (SECI) | NCR01148 | SPP2017017081 | PRC-005-1.1b | R2; R2.1 | On February 28, 2017, SECI submitted a Self-Certification stating that, as a Transmission Owner, it had an issue of noncompliance with PRC-005-1.1b R2.1 because it failed to test one of its 555 microprocessor Protection System relays within its defined four-year interval. The duration of this instance of noncompliance was from April 21, 2016, the date the microprocessor relay should have been tested, through March 23, 2017, the date the microprocessor relay was tested. The root cause of this instance of noncompliance was human error because a SECI employee excluded the microprocessor Protection System relay from the SECI Relay Inventory List, therefore the relay was missed during testing. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform Protection System relay testing has the potential to affect the reliability of the BPS by increasing the risk that the Protection System relay will fail, causing a misoperation of the associated Protection System. Notwithstanding, the issue of noncompliance involved one microprocessor protective relay located on a line section that has independent primary and secondary protection systems in place. Had a misoperation occurred on the relay, the secondary protection system that runs parallel to the primary protection system would have provided protection to the BPS. SECI discovered the deficiency during an internal review of its Relay Inventory list and corrected the issue promptly. No harm is known to have occurred. SECI has no relevant prior violations of PRC-005-1.1b R2.1 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, SECI: 1) completed testing of the protection system relay; 2) completed a full field inventory verification; and 3) trained engineering staff involved with maintaining SECI’s Protection System spreadsheets and quality control process. SPP RE has verified the completion of all mitigation activity.
2017-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Sunflower Electric Power Corporation (SECI) | NCR01148 | SPP2017017080 | FAC-008-3 | R6 | On February 28, 2017, SECI submitted a Self-Certification stating that, as a Transmission Owner, it had an issue of noncompliance with FAC-008-3 R6 because the Ford to North Fort Dodge line segment conductor rating was not consistent with SECI’s associated Facility Ratings methodology (FRM). Specifically, the Facility Ratings Spreadsheet (FRS) showed that the conductor for the Ford to North Fort Dodge line segment was rated at 100 °C. However, the conductor should have been rated at 86 °C. The duration of this instance of noncompliance was from March 19, 2015, the date the FRS was incorrectly updated, through April 27, 2017, the date the updated FRS was transmitted to SECI’s Reliability Coordinator. The root cause of this instance of noncompliance was human error. When the FRS was updated to include the Ford Substation and the original conductor was split into the two conductor line segments (Ford to North Fort Dodge and Ford to Shooting Star), the SECI employee updating the FRS entered the wrong conductor temperature for the Ford to North Fort Dodge line segment. Therefore, the line segment was not rated per SECI’s FRM. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SECI’s failure to document a Facility Rating consistent with its FRM could have led to equipment damage because applying a Facility Rating that is higher than the actual rating could have allowed the system operator to unknowingly overload the transmission line, causing it to overheat. Notwithstanding, the maximum load on this line segment during the noncompliance never exceeded 50% of its 86 °C facility rating. Additionally, the adjacent facility (Ford to Shooting Star) had a lower Facility Rating than the Ford to North Fort Dodge line segment; therefore, it would have been unlikely that the Ford to North Dodge line would have overheated or reached the 100 °C facility rating. Further, no other Facility Rating errors were found during mitigation and no harm is known to have occurred. A Settlement Agreement covering violation of FAC-009-1 R1 (SPP2011008130) for SECI (NCR01148) was filed with FERC under NP12-42-000 on July 31, 2013. On August 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE considered SECI’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment because the underlying conduct of the two instances was different. The prior violation was related to numerous transmission equipment Facility Rating issues across the SECI system while the instant issue was related to a facility rating change due to construction and had a minimal impact on the BES. | To mitigate this minimal risk instance of noncompliance, SECI: 1) corrected the facility rating error on the FRS and communicated the new rating internally and to its Reliability Coordinator via the Rating Submission Tool; 2) reviewed line conductor temperature ratings on all FRSs to check for similar errors; and 3) held informal training to reiterate to SECI staff that the FRS needs to reflect the information in the FRM. SPP RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Bryan Texas Utilities (BTU) | NCR04022 | TRE2017017385 | COM-001-2.1 | R9 | During a Compliance Audit conducted from January 23, 2017 through March 22, 2017, Texas RE determined that BTU, as a Transmission Operator (TOP), was in noncompliance with COM-001-2.1 R9. Specifically, BTU failed to test its designated Alternative Interpersonal Communication (AIC) capability for two adjacent TOPs at least once each calendar month. The root cause of this noncompliance was an insufficient process to remind all applicable staff members to conduct all required AIC capability testing on a monthly basis. In particular, BTU did not require the use of task notifications or other adequate reminders to ensure its personnel tested all designated AIC capabilities on a monthly basis. This noncompliance started on August 1, 2016, the day after BTU’s monthly AIC capability testing was due, and ended on August 2, 2016, when BTU successfully completed its testing of its designated AIC capability with the two adjacent TOPs at issue. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the noncompliance was short, lasting only two days. BTU further provided evidence that it successfully completed all required AIC capability testing every month in 2016, except for the July issue with the single designated method for two adjacent TOPs. Second, when BTU tested the specific AIC capability at issue, it functioned properly. Third, the issue related solely to BTU’s alternative, or backup, method of communication. As such, in the event the normal mode of communication with the two affected TOPs failed, BTU had multiple methods to communicate with the two TOPs at issue. Furthermore, BTU in practice had more than one communication capability for each adjacent TOP. As a result, even if there was a malfunction with the alternative communication at issue, BTU could reach its adjacent TOPs by utilizing other communication methods. Finally, the noncompliance did not impact AIC capability devices with BTU’s Reliability Coordinator (RC) and Balancing Authority (BA), further reducing the scope of the issue. No harm is known to have occurred. Texas RE considered BTU’s and its affiliate’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, BTU: 1) completed the required monthly AIC capability testing; 2) created a recurring task notification that reminds all System Operators to conduct all AIC capability testing on a monthly basis; 3) created a task in its maintenance tracking system that generates a monthly work order that is tracked by the Transmission Staff Assistant to verify that all required AIC capability testing is completed on a monthly basis; and 4) implemented a checklist spreadsheet that includes both Primary Interpersonal Communication and AIC methods to ensure that all of the communication devices are tested on the same day and at least once per month. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Stephens Ranch Wind Energy (SRWE) | NCR11507 | TRE2017017475 | PRC-019-2 | R1 | On April 27, 2017, SRWE submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with PRC-019-2 R1. Specifically, SRWE did not coordinate its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for its two wind generation Facilities by July 1, 2016, as required. In February 2017, SRWE determined that it had not performed the required verification of its voltage regulating system controls for its two generation Facilities by the July 1, 2016 deadline. Following this discovery, SRWE made arrangements to perform the required coordination study with a third-party contractor. SRWE completed this initial coordination study on March 27, 2017, and submitted it to Texas RE with its Self-Report. Upon review of SRWE’s initial coordination study, however, Texas RE determined that it did not include coordination of all required controls, capabilities, and settings. SRWE then re-performed its coordination study. In doing so, SRWE determined that the feeder protection systems at both generation Facilities were not properly set. On October 12, 2017, SRWE corrected the settings for these feeder Protection Systems, ending the issue. The root cause of this noncompliance was insufficient resources to ensure compliance with all newly applicable NERC Reliability Standards. SRWE contracts with a third-party asset management firm to manage its GO compliance responsibilities. SRWE did not ensure that this contractor had sufficient resources dedicated to its compliance tasks and SRWE personnel also did not adequately communicate with this contractor regarding upcoming compliance obligations. This noncompliance started on July 1, 2016, when PRC-019-2 became mandatory and enforceable, and ended on October 12, 2017, when SRWE completed the updates to its feeder Protection System settings. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the results of the verification activity indicated that only minor adjustments were necessary to properly coordinate all Protection Systems. In particular, SRWE’s feeder Protection System settings at the two generation Facilities in question were only set 0.011 PU below the appropriate setting. Second, during the period of noncompliance, SRWE’s two generation Facilities contributed a combined average of only 147.86 MW and operated at an approximately 39% capacity factor. Third, throughout the period of noncompliance, SRWE only experienced very minor deviations of its voltage profile for a very small amount of time (approximately 0.02% of the total operating time at issue). Finally, when SRWE’s Facilities operated during the period of noncompliance, neither Facility experienced any trips or misoperations as a result of inadequate coordination. No harm was known to have occurred. Texas RE considered SRWE’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SRWE: 1) completed the coordination study of its voltage regulating system controls, protection system elements, and equipment capabilities; 2) completed reprogramming of its Protection Systems to properly coordinate with its voltage regulating system controls; 3) ensured that its third-party compliance contractor retained and dedicated additional staff and resources to perform SRWE’s compliance tasks; and 4) established a coordination review process to occur one year and six months in advance of the next required testing date involving both SRWE and the third-party compliance contractor’s management to facilitate communication and oversight. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2017016955 | MOD-025-2 | R1 | On February 6, 2017, SW2 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, SW2 neither verified the Real Power capability of its single generation unit in accordance with MOD-025-2, Attachment 1 nor submitted a completed Attachment 2 form to its Transmission Planner (TP) within 90 calendar days of the date of its recorded staged test. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW2 determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline. As a result, SW2 performed the required Real Power capability verification testing for its single generation unit on October 11, 2016, but could not provide evidence that it submitted the test results to its TP within 90 days of completing testing. On February 2, 2017, SW2 submitted its Real Power capability testing results to its TP, ending the noncompliance. The root cause of this noncompliance was insufficient internal controls to ensure SW2 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW2 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on February 2, 2017, when SW2 submitted the required MOD-025-2, Attachment 2 form with its most recent Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW2 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW2 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, SW2 has a nameplate capacity of only 105 MW and operated only at approximately a 34% capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW2: 1) performed the required Real Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to SW2’s Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2017016956 | MOD-025-2 | R2 | On February 6, 2017, SW2 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with MOD-025-2 R2. In particular, SW2 neither verified the Reactive Power capability of its single generation unit in accordance with MOD-025-2, Attachment 1 nor submitted a completed Attachment 2 form to its Transmission Planner (TP) within 90 calendar days of the date of its recorded staged test. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW2 determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline. As a result, SW2 performed the required Reactive Power capability verification testing for its single generation unit on October 11, 2016, but could not provide evidence that it submitted the test results to its TP within 90 days of completing testing. On February 2, 2017, SW2 submitted its Reactive Power capability testing results to its TP, ending the noncompliance. The root cause of this noncompliance was insufficient internal controls to ensure SW2 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW2 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on February 2, 2017, when SW2 submitted the required MOD-025-2, Attachment 2 form with its most recent Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW2 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW2 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, SW2 has a nameplate capacity of only 105 MW and operated only at approximately a 34% capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW2: 1) performed the required Reactive Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to SW2’s Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2017016957 | MOD-025-2 | R1 | On February 6, 2017, SW3 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, SW3 neither verified the Real Power capability in accordance with MOD-025-2, Attachment 1 nor submitted a completed Attachment 2 form to its Transmission Planner (TP) within 90 calendar days of the date of its recorded staged test for at least 40 percent of its generation units. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW3 determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline. As a result, SW3 performed the required Real Power capability verification testing of its applicable generation units on October 11, 2016, but could not provide evidence that it submitted the test results to its TP within 90 days of completing testing. On February 2, 2017, SW3 submitted its Real Power capability testing results to its TP, ending the noncompliance. The root cause of this noncompliance was insufficient internal controls to ensure SW3 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW3 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on February 2, 2017, when SW3 submitted the required MOD-025-2, Attachment 2 form with its most recent Real Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW3 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW3 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, SW3 has a nameplate capacity of only 129 MW and operated only at approximately a 36% capacity factor during the issue period. As a result, any errors in the Facilities’ Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW3: 1) performed the required Real Power capability verification testing for its applicable generation units; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to SW3’s Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 3 LLC (SW3) | NCR04133 | TRE2017016960 | MOD-025-2 | R2 | On February 6, 2017, SW3 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with MOD-025-2 R2. In particular, SW3 neither verified the Reactive Power capability in accordance with MOD-025-2, Attachment 1 nor submitted a completed Attachment 2 form to its Transmission Planner (TP) within 90 calendar days of the date of its recorded staged test for at least 40 percent of its generation units. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW3 determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline. As a result, SW3 performed the required Reactive Power capability verification testing of its applicable generation units on October 11, 2016, but could not provide evidence that it submitted the test results to its TP within 90 days of completing testing. On February 2, 2017, SW3 submitted its Reactive Power capability testing results to its TP, ending the noncompliance. The root cause of this noncompliance was insufficient internal controls to ensure SW3 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW3 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on February 2, 2017, when SW3 submitted the required MOD-025-2, Attachment 2 form with its most recent Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW3 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW3 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, SW3 has a nameplate capacity of only 129 MW and operated only at approximately a 36% capacity factor during the issue period. As a result, any errors in the Facilities’ Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW3: 1) performed the required Reactive Power capability verification testing for its applicable generation units; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to SW3’s Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2017016962 | MOD-025-2 | R1 | On February 6, 2017, SW4 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, SW4 failed to verify the Real Power capability of at least 40 percent of its generation units in accordance with MOD-025-2, Attachment 1. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW4 determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline. As a result, SW4 performed the required Real Power capability verification testing for two of its wind generation Facilities on November 22, 2016, and submitted the results to its TP on February 2, 2017. The root cause of this noncompliance was insufficient internal controls to ensure SW4 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW4 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on November 22, 2016, when SW4 completed the required Real Power capability verification testing for at least 40 percent of its generation units in accordance with MOD-025-2, Attachment 1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW4 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW4 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. SW4’s three wind generation Facilities have a combined nameplate capacity of 239 MW and operated only at approximately a 34% capacity factor during the issue period. As a result, any errors in the Facilities’ Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW4: 1) completed the required Real Power capability verification testing of at least 40 percent of its generation units; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to Sweetwater Facilities’ Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 4 LLC (SW4) | NCR04135 | TRE2017016963 | MOD-025-2 | R2 | On February 6, 2017, SW4 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. In particular, SW4 failed to verify the Reactive Power capability of at least 40 percent of its generation units in accordance with MOD-025-2, Attachment 1. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW4 determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline for at least 40 percent of its three wind generation Facilities. As a result, SW4 performed the required Reactive Power capability verification testing for two of its wind generation Facilities on November 22, 2016, and submitted the results to its TP on February 2, 2017. The root cause of this noncompliance was insufficient internal controls to ensure SW4 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW4 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on November 22, 2016, when SW4 completed the required Reactive Power capability verification testing for at least 40 percent of its generation units in accordance with MOD-025-2, Attachment 1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW4 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW4 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, SW4’s three wind generation Facilities have a combined nameplate capacity of 239 MW and operated only at approximately a 34% capacity factor during the issue period. As a result, any errors in the Facilities’ Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW4: 1) completed the required Reactive Power capability verification testing of at least 40 percent of its generation units; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to SW4’s Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2017016951 | MOD-025-2 | R1 | On February 6, 2017, SW5 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R1. In particular, SW5 failed to verify the Real Power capability of its single generation unit in accordance with MOD-025-2, Attachment 1. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW5 determined that it had not completed the required Real Power capability verification testing by the July 1, 2016 deadline. As a result, SW5 performed the required Real Power capability verification testing of its single generation unit on January 23, 2017, and submitted the results to its TP on February 2, 2017. The root cause of this noncompliance was insufficient internal controls to ensure SW5 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW5 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R1 became mandatory and enforceable, and ended on January 23, 2017, when SW5 completed the required Real Power capability verification testing for its single generation unit in accordance with MOD-025-2, Attachment 1. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW5 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW5 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, SW5 has a nameplate capacity of 79 MW and operated only at approximately a 34% capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW5’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW5: 1) performed the required Real Power capability verification testing for its single generation unit; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; and 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to SW5’s Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2017016953 | MOD-025-2 | R2 | On February 6, 2017, SW5 submitted a Self-Report stating that, as a Generator Owner (GO), it was in noncompliance with MOD-025-2 R2. In particular, SW5 neither verified the Reactive Power capability in accordance with MOD-025-2, Attachment 1 nor submitted a completed Attachment 2 form to its Transmission Planner (TP) within 90 calendar days of the date of its recorded staged test for at least 40 percent of its generation units. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW5 determined that it had not completed the required Reactive Power capability verification testing by the July 1, 2016 deadline. As a result, SW5 performed the required Reactive Power capability verification testing on January 23, 2017. However, on February 2, 2017, SW5 inadvertently submitted inaccurate Reactive Power capability testing results to its TP. After the issue was discovered, SW5 submitted its corrected Reactive Power capability testing results to its TP on July 11, 2017, ending the noncompliance. The root cause of this noncompliance was insufficient internal controls to ensure SW5 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW5 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This noncompliance started on July 1, 2016, when MOD-025-2 R2 became mandatory and enforceable, and ended on July 11, 2017, when SW5 submitted its corrected Reactive Power capability testing results to its TP. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, SW5 provided previous Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SW5 provided information similar to the required Real and Reactive Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, SW5 has a nameplate capacity of 79 MW and operated only at approximately a 34% capacity factor during the issue period. As a result, any errors in the Facility's Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered SW5’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this noncompliance, SW5: 1) performed the required Reactive Power capability verification testing for its single generation unit; 2) submitted accurate forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion; 4) established regular meetings among NERC compliance personnel to discuss all elements of its compliance program, including ongoing projects and upcoming compliance deadlines; 5) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance and mitigation issues; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) retained a new director of regulatory compliance that now reports directly to SW5’s Chief Operating Officer. Texas RE has verified the completion of all mitigation activity.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Algonquin Power Sanger LLC (AGPS) | NCR11249 | WECC2017017160 | PRC-005-2(i) | R3 | On March 1, 2017, AGPS submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-005-2(i) R3. Specifically, while preparing for its Self-Certification, AGPS discovered that it failed to perform the minimum maintenance activities within the maximum maintenance intervals for its two Vented Lead Acid (VLA) batteries for unintentional grounds as prescribed in Table 1-4(a). AGPS’s maintenance documentation did not have instructions to inspect for unintentional grounds so that requirement was omitted from AGPS’s periodic maintenance activities. The root cause of this issue was a misunderstanding of the Standard. Specifically, AGPS misunderstood the requirement to inspect and document the periodic battery unintentional ground fault inspections. WECC determined that this issue began on August 1, 2015, when completion of the 4-month maintenance activity for the two batteries was due, and ended on March 23, 2017, when AGPS completed the maintenance activities prescribed in Table 1-4(a), for a total of 600 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AGPS failed to perform the minimum maintenance activities within the maximum maintenance intervals for two VLA batteries for unintentional grounds as prescribed in Table 1-4(a). Such failure could potentially result in degradation of equipment or the misoperation of associated Protection System devices, causing the 86.6 MVA combined cycle plant to trip. However, the likelihood of the risk occurring was reduced due to the detective and preventative controls AGPS had implemented. Specifically, the batteries in scope had ground fault alarms, so if AGPS experienced a ground fault within its Direct Current systems, its staff would have been immediately notified of the issue. Additionally, the batteries have been subject to on-going maintenance and testing activities. Specifically, AGPS conducted daily rounds to inspect its battery system, including battery charge, which may indicate if a ground fault was present. Further, AGPS’s 4-month maintenance and testing activities included checking battery float voltage, specific gravity, and a visual inspection of the electrolyte levels. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a low likelihood of causing minor harm, and therefore, posed minimal risk to the reliability of the Bulk Power System (BPS). AGPS's compliance history was reviewed and no relevant noncompliance was identified. | To mitigate this issue, AGPS: 1) completed the required 4-month maintenance for the two batteries as prescribed in Table 1-4(a); and 2) developed a new test worksheet for the 4-month battery testing that includes testing for unintentional grounds for both positive and negative voltage. WECC verified completion.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Aragonne Wind LLC (AGW) | NCR05014 | WECC2017016998 | PRC-019-2 | R1; R1.1; R1.1.1; R1.1.2 | On February 14, 2017, AGW submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, AGW reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices for its applicable Facility by the mandatory and enforceable date of the Standard. The root cause of this issue was a less than adequate compliance process. Specifically, AGW management was not aware of the new Standard and Requirement and thus, did not complete requisite testing by the mandatory and enforceable date. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for AGW’s applicable Facility, and ended on March 20, 2017, when AGW completed coordination activities for its applicable Facility, for a total of 262 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AGW failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices for its onshore wind turbine Facility by the enforcement date of the Standard. Such failure could potentially result in the loss of the generator field, system instability, and/or damage to the turbines, resulting in the loss of its 90 MW Facility. However, when AGW performed the verification, no changes were required. Additionally, the Facility in scope is an intermittent wind Facility, so in the unlikely event that AGW experienced a loss of its generator field, system reliability would not be compromised since wind generation is not typically utilized as a firm resource; therefore, the grid operates with the expectation that this generation may be unavailable at any given time. Further, the issue had a low risk of causing minor harm and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. AGW's compliance history was reviewed and no relevant noncompliance was identified. | To mitigate this issue, AGW: 1) verified coordination of its applicable Facility in accordance to the Standard; 2) implemented an action tracking system that will be maintained by a third-party NERC Consultant to monitor and track compliance with future NERC standards; 3) will conduct weekly meetings that are hosted by the NERC Consultant and attended by AGW’s Director of Regulatory Compliance, VP of Operations, and staff, to review and discuss its NERC Compliance Program; and 4) established project completion dates in advance of the enforcement dates to prevent future reoccurrence of the same or similar issues. WECC verified completion .
2017-11-30 | Western Electricity Coordinating Council (WECC) | Dominion Solar Projects III, Inc. (DOM) | NCR11633 | WECC2017017105 | PRC-005-6 | R3 | On February 27, 2017, DOM submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-005-6 R3. Specifically, DOM reported that it had multiple instances of noncompliance of PRC-006 R3 for failing to perform the minimum maintenance activities within the maximum maintenance intervals for eight Valve Regulated Lead-Acid (VRLA) batteries and 12 Vented Lead-Acid (VLA) batteries as prescribed in Table 1-4(a) and Table 1-4(b). In the first instance, DOM failed to perform the 4-month maintenance activities for eight VRLA batteries at its Enterprise and Escalante Solar Installations as prescribed in Table 1-4(b). In the second instance, DOM failed to perform the 6-month maintenance activities for the same eight VRLA batteries as prescribed in Table-1-4(b). In the third instance, DOM failed to perform the 4-month maintenance activities for 12 VLA batteries at its Granite Mountain East, Granite Mountain West, and Iron Springs Solar Installations, as well as its Granite Mountain Metering Yard as prescribed in Table-1-4(a). WECC determined that this issue began on August 1, 2016, when completion of the of the maintenance activity for the first instance of noncompliance was due, and ended on February 13, 2017, when DOM completed the testing requirements for all the batteries in scope as prescribed in Table 1-4(a) and Table 1-4(b), for a total of 196 days of noncompliance. The root cause of this issue was due to a process gap while transitioning from its construction phase to its operational phase. Specifically, DOMS’s commissioning team did not receive clear communication of compliance expectations regarding maintenance activities, so it did not perform the maintenance activities in accordance to the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, DOM failed to perform the prescribed minimum maintenance activities within the maximum maintenance intervals of Table 1-4(a) and Table 1-4(b) for eight Valve Regulated Lead-Acid (VRLA) batteries and twelve Vented Lead-Acid (VLA) batteries that provide backup power to DOM’s Protection System devices. Failure to perform battery inspections potentially could result in degradation of batteries, which could result in the misoperation of associated Protection Systems devices preventing the isolation of one or more faults. These issues of noncompliance affect 530 MW of non-synchronous generation. However, the risk was reduced due to the detective controls DOM had in place. Specifically, the batteries in scope are each in a control house that is inspected bi-weekly by DOM’s Operations and Maintenance personnel; any obvious issues would have been identified and reported. Operations personnel also complete an inspection checklist monthly, whereby they perform site checks and provide evidence, as requested. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a moderate likelihood of causing minor harm, and therefore, posed minimal risk to the reliability of the Bulk Power System (BPS). DOM's compliance history was reviewed and no relevant noncompliance was identified. | To mitigate this issue, DOM: 1) completed the required maintenance activities for the batteries in scope as prescribed in Table 1-4(a) and Table 1-4(b) 2) closed the process gap in its transition from the construction phase to the operational phase by 1) establishing expectations regarding battery testing during and post-commissioning 2) providing Preventive Maintenance Procedures early in the construction phase, and 3) providing a checklist of items required for compliance; and 3) provided the appropriate parties the Preventive Maintenance Procedure template to ensure all required maintenance activities are properly documented; quarterly Preventive Maintenance Procedures for both VRLA and VLA battery sets; and the required maintenance schedule for the remainder of 2017. WECC verified completion.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Judith Gap Energy LLC (JUGE) | NCR05503 | WECC2017017157 | PRC-024-2 | R3; R3.1 | On February 28, 2017, JUGE submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R3. Specifically, JUGE reported that it failed to communicate a documented equipment limitation to its Planning Coordinator (PC) and Transmission Planner (TP) within 30 calendar days of identification of an equipment limitation in accordance to the Standard and Requirement. The root cause of this issue was JUGE’s failure to timely identify the individual at the PC and TP with whom to communicate the equipment limitation. WECC determined that this issue began on August 1, 2016, 30 days after the Standard became mandatory and enforceable, and ended on February 28, 2017, when JUGE communicated the documented equipment limitation to its PC and TP, for a total of 212 of days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, JUGE failed to communicate the documented equipment limitation to its PC and TP within 30 calendar days of identification of an equipment limitation in accordance with the Standard and Requirement. Such failure could result in inaccurate data modeling by the PC and TP when planning for system operating conditions and addressing contingencies. Inaccurate modeling could lead to an unexpected loss of the 180 MW of generation produced by this JUGE wind facility. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 180 MW wind facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that wind generation may be unavailable at any given time, so in the unlikely event that JUGE experienced a loss of its wind facility, system reliability would not be compromised. No harm is known to have occurred. For these reasons, WECC determined that this issue had a low likelihood of causing minor harm and posed a minimal risk to the reliability of the Bulk Power System (BPS). JUGE's compliance history was reviewed and no relevant noncompliance was identified. | To mitigate this issue, JUGE: 1) determined the appropriate individual at the PC and TP to communicate the documented equipment limitation; and 2) communicated the documented equipment limitation to the PC and TP. WECC verified completion.
2017-11-30 | Western Electricity Coordinating Council (WECC) | Spring Canyon Energy LLC (SPCE) | NCR11529 | WECC2017017138 | PRC-024-2 | R3; R3.1 | On February 28, 2017, SPCE submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R3. Specifically, SPCE reported that it failed to communicate the documented equipment limitation to its Planning Coordinator (PC) and Transmission Planner (TP) within 30 calendar days of identification of an equipment limitation in accordance with the Standard and Requirement. The root cause of this issue was SPCE’s failure to timely identify the correct individual at the PC and TP with whom to communicate the equipment limitation. WECC determined that this issue began on August 1, 2016, 30 days after the Standard became mandatory and enforceable, and ended on February 28, 2017, when SPCE communicated the documented equipment limitation to its PC and TP, for a total of 212 of days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SPCE failed to communicate the documented equipment limitation to its PC and TP within 30 calendar days of identification of an equipment limitation in accordance to the Standard and Requirement. Such failure could result in inaccurate data modeling by the PC and TP when planning for system operating conditions and addressing contingencies. Inaccurate modeling could lead to an unexpected loss of the 180 MW of generation produced by this SPCE wind facility. However, the likelihood of the risk occurring was reduced because the Facility in scope is a 180 MW wind facility that is not typically utilized as a firm resource. The PC, TO and TOP plan and operate the grid with the expectation that wind generation may be unavailable at any given time, so in the unlikely event that SPCE experienced a loss of its wind facility, system reliability would not be compromised. No harm is known to have occurred. For these reasons, WECC determined that this issue had a low likelihood of causing minor harm and posed a minimal risk to the reliability of the Bulk Power System (BPS). SPCE's compliance history was reviewed and no relevant noncompliance was identified. | To mitigate this issue, SPCE: 1) determined the appropriate individual at the PC and TP to communicate the documented equipment limitation; and 2) communicated the documented equipment limitation to the PC and TP. WECC verified completion .
2017-11-30 | Western Electricity Coordinating Council (WECC) | WestRock CP, LLC (TBIO) | NCR11458 | WECC2017017135 | PRC-005-2(i) | R3 | On February 28, 2017, TBIO submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-005-2(i) R3. Specifically, during its compliance review, in preparation of its 2016 Self-Certification, TBIO discovered that it failed to perform the minimum maintenance activities within the maximum maintenance intervals for one of its four 125V Direct Current (DC) Valve Regulated Lead-Acid (VRLA) batteries as prescribed in Table 1-4(b). The testing was scheduled for the end of the calendar month, for which it was due. However, the field technicians performing the testing did not understand that the testing was to be conducted on a strict timeframe to adhere to the Standard, so it was postponed to address issues which they felt were more important for plant operations. The root cause of this issue was a lack of compliance understanding regarding the required maintenance activities for PRC-005-2(i) R3. WECC determined that this issue began on October 1, 2015, when completion of the 6-month maintenance activity for the battery was due, and ended on January 5, 2016, when TBIO completed the testing requirements prescribed in Table 1-4(b), for a total of 96 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, TBIO failed to perform the minimum maintenance activities within the maximum maintenance intervals for one 125V DC VRLA battery as prescribed in Table 1-4(b). The DC battery in scope controls generator protection relays, circuit breaker controls, and a DC lube oil pump. Failure to maintain Protection System Components could potentially result in the incorrect operation of the generator protection relays, circuit breaker controls, and/or DC lube oil pump. Had the circuit breaker failed or the relays misoperated, the plant could have lost its Alternating Current power, the turbine/generator bearings could have been damaged, potentially resulting in the loss of 64.313 MW of generation. Additionally, the generator could have tripped offline had the DC lube oil pump failed. However, the likelihood of the risk occurring was reduced due to the controls TBIO had in place. Specifically, TBIO implemented an alarm on the battery to monitor the float voltage. Additionally, the battery is monitored on a monthly basis, which includes checking and recording the charge value. Therefore, TBIO would have been able to immediately identify any issues with the battery and immediately replace it, if needed. Further, TBIO load tests the battery once per year by running the DC lube oil pump to check the condition of the battery. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal likelihood of causing minor harm, and therefore, was a minimal risk to the reliability of the Bulk Power System (BPS). TBIO's compliance history was reviewed and no relevant noncompliance was identified. | To mitigate this issue, TBIO: 1) completed the required 6-month maintenance for the battery as prescribed in Table 1-4(b); 2) changed the maintenance intervals from 6-month to 4-month intervals to allow additional time for maintenance and testing activities; and 3) sent a memo to its plant personnel informing them of the maintenance and testing activities required under PRC-005-6. The memo also reminded plant personnel of maintaining maintenance and testing documentation, and provided a list contacts for any questions regarding compliance obligations. WECC verified completion.
2017-10-31 | Florida Reliability Coordinating Council, Inc. (FRCC) | Tallahassee, City of (TAL) | NCR00073 | FRCC2017018106 | BAL-003-1.1 | R2. | On August 9, 2017, TAL submitted a Self-Report stating that, as a Balancing Authority, it had an issue of BAL-003-1.1 R2. This issue started on April 4, 2017, when TAL incorrectly entered the Frequency Bias setting into its Area Control Error (ACE) calculation during the implementation period specified by the ERO and ended on August 7, 2017, when the correct Frequency Bias setting was entered, 125 days late. During an internal review of evidence and compliance with NERC Reliability Standards as per TAL's detective internal control, TAL discovered a typographical error was made when instructing the SCADA engineers to update the Frequency Bias in the system. Per the NERC instruction dated March 4, 2017, TAL was to change its Frequency Bias setting in its ACE calculation to 4.73 MW/0.1Hz on Tuesday, April 4, 2017. TAL instructed the SCADA engineers to change the L10 value with the correct value and identified the proper date by when the changes should be implemented, but mistakenly communicated an incorrect hundredth decimal value on the Frequency Bias setting as 4.71 MW/0.1Hz. The root cause for this violation was determined to be a result of not having a preventive internal control in place for secondary verification. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The lower improper setting of the Frequency Bias setting in the ACE equation would have caused a slower increase or decrease in generation change under a frequency excursion event. This risk was reduced, however, because the variance was only .02 MW/0.1Hz, providing minimal impact on the BPS. No frequency excursions are known to have occurred during the timeframe the Frequency Bias was incorrectly set, and no harm is known to have occurred. FRCC considered TAL's BAL-003 R2 compliance history in determining the disposition track and it should not serve as a basis for applying a penalty. | To mitigate this issue, TAL: 1) corrected the Frequency Bias setting in TAL’s ACE calculation in SCADA immediately upon discovery of the error; 2) performed a root cause analysis; 3) implemented a preventive control for secondary verification by a division outside of System Operations; 4) discussed the root cause analysis determination with necessary staff and the need for the preventive internal control of secondary verification; and 5) issued written instruction to a broader staff audience of the new preventive internal control. To prevent recurrence, TAL: 1) is implementing a secondary review for all adjustments to settings affecting its ACE equation.
2017-10-31 | Midwest Reliability Organization (MRO) | Cedar Falls Utilities (CFU) | NCR00969 | MRO2017016776 | COM-002-4 | R3 | On January 11, 2017, CFU submitted a Self-Report stating that, as a Distribution Provider, it had an issue with COM-002-4 R3. Specifically, CFU did not provide initial training for its 20 operating personnel in three-part communication. The cause of the noncompliance was that CFU was unaware of the requirements of the new version of the Standard and Requirement until November 2016. This issue started on July 1, 2016, when the Standard and Requirement became mandatory and enforceable on CFU, and ended on December 31, 2016 when CFU completed initial training on three-part communication for its 20 operating personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The scope of the noncompliance is limited to CFU's function as a Distribution Provider, and as a Distribution Provider, CFU has a limited ability to impact the BPS as its 2015 peak load was only 101 MW. Further, the duration of the noncompliance was approximately six months. Finally, per CFU, oral three-part communications are not frequently necessary in its operations, as operating instructions from its Transmission Operator are infrequent, and are typically accompanied by a written switching order from its Transmission Operator that has been reviewed by both parties. No harm is known to have occurred. CFU has no relevant history of noncompliance. | To mitigate this issue, CFU: 1) completed initial training on three-part communication for its 20 operating personnel; 2) added an internal control that alerts NERC Compliance staff anytime a new employee is hired or there is a position change, so that NERC Compliance staff can conduct any necessary training; and 3) enhanced its annual training by including a section on three-part communications as a refresher for existing operating personnel. CFU stated that mitigating activities were complete as of April 27, 2017.
2017-10-31 | Midwest Reliability Organization (MRO) | Otter Tail Power Company (OTP) | NCR01023 | MRO2017017426 | VAR-002-4 | R2 | On April 20, 2017, OTP submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R2. OTP identified eight instances where BES generators did not maintain the voltage schedule provided by its Transmission Operator. Seven of the instances involved the Hoot Lake Power Plant and one instance involved the Solway Plant. There were two distinct causes of the noncompliance. The noncompliance related to the Hoot Lake Power Plant was the operators' failure to take actions to return the voltage back within the voltage schedule, although the unit was in automatic control mode and was configured to control generator voltage, the operators failed to fully adjust the regulator set point to correct the voltage at the bus. The noncompliance related to the Solway Plant was related to insufficiency in the annunciation and bandwidth of the voltage alarm, as it failed to alert the operator of the issue. This issue started on July 25, 2016, when the first instance that OTP did not maintain its voltage schedule began, and ended on December 1, 2016, when the eighth instance ended. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The facilities pose a limited risk to the BPS as Hoot Lake (152 MVA) and Solway (71 MVA) have low nameplate ratings and interconnect at 115 kV. Further, the deviations in the voltage schedules were relatively minor, as both the highest and lowest voltage readings were within OTP's Reliability Coordinator's default normal high and normal low voltage criteria. Further, per OTP it performed an extent of conditions analysis and confirmed there were no similar instances of noncompliance at its larger BES facilities. Additionally, neither facility is identified as a Blackstart Resource or associated with a Remedial Action Scheme or an IROL flowgate. Per OTP, system operators were monitoring system voltage, and no operating instructions were received to control or otherwise alter the voltage at either facility during the exceedances. No harm is known to have occurred. OTP has no relevant history of noncompliance. | To mitigate this issue, OTP: 1) returned the bus voltage to within the acceptable bandwidth; 2) stated that it performed an extent of conditions analysis and confirmed there were no similar instances of noncompliance at its larger BES facilities; 3) retrained the system operators at Hoot Lake on responding to bus voltage issues, including training on the manual control of voltage and reactive power within the applicable Facility Ratings, the logging of voltage excursions, and the requirement to notify the Transmission Operator when voltage schedules cannot be met; and 4) installed a pager alarming system at Solway for the operators to use when they are not in the control room to alert the operator when the voltage approaches the tolerance band. OTP stated that mitigating activities were complete as of April 6, 2017.
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2017018265 | PRC-024-2 | R3. | On August 25, 2017, Noble Altona Windpark, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R3. Specifically, the Entity failed to notify its Planning Coordinator/Transmission Planner of equipment limitations of its Low Voltage Ride Through (LVRT)-type wind turbines that prevent its generating units with voltage protective relays from meeting the requirement for the 0.15V to zero volts time-frame, per the setting criteria of Requirement R2. This noncompliance started on April 8, 2017, thirty days after an engineering consultant hired by the Entity documented the above equipment limitations in a report to the Entity, and ended on August 25, 2017, when the Entity formally notified its Planning Coordinator/Transmission Planner of its equipment limitations. The root cause of this instance of noncompliance was an oversight in the notification aspect of Requirement R3 of the standard. Upon consultation with an outside vendor, the Entity correctly concluded that it needed to notify its Planning Coordinator/Transmission Planner of performance limitations inherent to its facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 19.9%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 97 MW, which is less than 5.0% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal impact on the reliable operation of the BPS. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by formally notifying its Planning Coordinator/Transmission Planner of its equipment limitations; and 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Chateaugay Windpark, LLC | NCR10367 | NPCC2017018264 | PRC-024-2 | R3. | On August 25, 2017, Noble Chateaugay Windpark, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R3. Specifically, the Entity failed to notify its Planning Coordinator/Transmission Planner of equipment limitations of its Low Voltage Ride Through (LVRT)-type wind turbines that prevent its generating units with voltage protective relays from meeting the requirement for the 0.15V to zero volts time-frame, per the setting criteria of Requirement R2. This noncompliance started on April 8, 2017, thirty days after an engineering consultant hired by the Entity documented the above equipment limitations in a report to the Entity, and ended on August 25, 2017, when the Entity formally notified its Planning Coordinator/Transmission Planner of its equipment limitations. The root cause of this instance of noncompliance was an oversight in the notification aspect of Requirement R3 of the standard. Upon consultation with an outside vendor, the Entity correctly concluded that it needed to notify its Planning Coordinator/Transmission Planner of performance limitations inherent to its facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 22.4%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 106 MW, which is less than 5.4% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal impact on the reliable operation of the BPS. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by formally notifying its Planning Coordinator/Transmission Planner of its equipment limitations; and 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Clinton Windpark, LLC | NCR10272 | NPCC2017018263 | PRC-024-2 | R3. | On August 25, 2017, Noble Clinton Windpark, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R3. Specifically, the Entity failed to notify its Planning Coordinator/Transmission Planner of equipment limitations of its Low Voltage Ride Through (LVRT)-type wind turbines that prevent its generating units with voltage protective relays from meeting the requirement for the 0.15V to zero volts time-frame, per the setting criteria of Requirement R2. This noncompliance started on April 8, 2017, thirty days after an engineering consultant hired by the Entity documented the above equipment limitations in a report to the Entity, and ended on August 25, 2017, when the Entity formally notified its Planning Coordinator/Transmission Planner of its equipment limitations. The root cause of this instance of noncompliance was an oversight in the notification aspect of Requirement R3 of the standard. Upon consultation with an outside vendor, the Entity correctly concluded that it needed to notify its Planning Coordinator/Transmission Planner of performance limitations inherent to its facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 19.8%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 100.5 MW, which is less than 5.2% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal impact on the reliable operation of the BPS No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by formally notifying its Planning Coordinator/Transmission Planner of its equipment limitations; and 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Ellenburg Windpark, LLC | NCR10273 | NPCC2017018262 | PRC-024-2 | R3. | On August 25, 2017, Noble Ellenburg Windpark, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R3. Specifically, the Entity failed to notify its Planning Coordinator/Transmission Planner of equipment limitations of its Low Voltage Ride Through (LVRT)-type wind turbines that prevent its generating units with voltage protective relays from meeting the requirement for the 0.15V to zero volts time-frame, per the setting criteria of Requirement R2. This noncompliance started on April 8, 2017, thirty days after an engineering consultant hired by the Entity documented the above equipment limitations in a report to the Entity, and ended on August 25, 2017, when the Entity formally notified its Planning Coordinator/Transmission Planner of its equipment limitations. The root cause of this instance of noncompliance was an oversight in the notification aspect of Requirement R3 of the standard. Upon consultation with an outside vendor, the Entity correctly concluded that it needed to notify its Planning Coordinator/Transmission Planner of performance limitations inherent to its facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 23.7%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 81 MW, which is less than 4.2% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal impact on the reliable operation of the BPS No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by formally notifying its Planning Coordinator/Transmission Planner of its equipment limitations; and 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-10-31 | Northeast Power Coordinating Council, Inc. (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2017018267 | PRC-024-2 | R3. | On August 28, 2017, Noble Wethersfield Windpark, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R3. Specifically, the Entity failed to notify its Planning Coordinator/Transmission Planner of equipment limitations of its Low Voltage Ride Through (LVRT)-type wind turbines that prevent its generating units with voltage protective relays from meeting the requirement for the 0.15V to zero volts time-frame, per the setting criteria of Requirement R2. This noncompliance started on April 8, 2017, thirty days after an engineering consultant hired by the Entity documented the above equipment limitations in a report to the Entity, and ended on August 25, 2017, when the Entity formally notified its Planning Coordinator/Transmission Planner of its equipment limitations. The root cause of this instance of noncompliance was an oversight in the notification aspect of Requirement R3 of the standard. Upon consultation with an outside vendor, the Entity correctly concluded that it needed to notify its Planning Coordinator/Transmission Planner of performance limitations inherent to its facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 24%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. It is used to displace energy derived from fossil fuels for economic and environmental reasons, when available. The rated capability of the Entity's Wind Farm generation is 126 MW, which is less than 6.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. For all the above considerations, this instance of noncompliance represents a minimal impact on the reliable operation of the BPS. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by formally notifying its Planning Coordinator/Transmission Planner of its equipment limitations; and 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Ridge Wind Farm, LLC (ARWF) | NCR08039 | RFC2017016971 | MOD-025-2 | R1 | On February 6, 2017, ARWF submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. ARWF failed to perform the real power capability test for its facility by the July 1, 2016 deadline. ARWF did not recognize that the MOD-025-2 requirements became effective on July 1, 2016, and therefore failed to timely schedule and perform the necessary testing. Shortly after the July 1, 2016 effective date, Leeward Renewable Energy, owner and operator of Allegheny Ridge Wind Farm, made organizational changes that included the hiring of a Director of Regulatory Compliance who reports to the Chief Operating Officer. The discovery of this noncompliance is the result of the Director's review of the NERC Compliance Program. This noncompliance invovles the management practice of workforce management and planning. Workforce management and planning are both involved because ARWF compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is ARWF’s failure to effectively plan for the July 1, 2016 effective date for MOD-025-2. This issue started on July 1, 2016, when ARWF was required to comply with MOD-025-2 R1 and ended on May 11, 2017, when ARWF completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because ARWF is an intermittent generator deriving its power output from variance driven wind conditions. During the noncompliance, ARWF contributed a peak of approximately 80 MW to the grid and operated at approximately a 30% capacity factor. Lastly, ARWF implemented a new detective control, an annual review of ARWF’s NERC Compliance Program by its Director of Regulatory Compliance, and that detective control discovered this noncompliance. No harm is known to have occurred. ReliabilityFirst considered ARWF’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ARWF: 1) entered the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion; 2) performed a Real Power Capability Test (ARWF performed the test on April 6, 2017 and forwarded the test results to its Transmission Planner, PJM, on April 7, 2017.); and 3) submitted the results of the Real Power Test to its Transmission Planner, PJM. ARWF also strengthened the following preventive controls. Upon FERC approval of applicable standards, ARWF enters the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion. (Action Tracker is maintained by a third-party NERC Consultant and weekly meetings are hosted by the consultant and attended by ARWF's Director of Regulatory Compliance and VP of Operations.) ARWF establishes project completion dates sufficiently in advance of the enforcement dates to preclude future issues. Provide lessons learned review with appropriate ARWF personnel. (Training conducted by NERC consultant on October 25 2016 for Site Operations Managers and support personnel including IT, Engineering, CEO, COO, VP of Operations and Director of Regulatory Compliance.) ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Ridge Wind Farm, LLC (ARWF) | NCR08039 | RFC2017016973 | MOD-025-2 | R2 | On February 6, 2017, ARWF submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. ARWF failed to perform the real power capability test for its facility by the July 1, 2016 deadline. ARWF did not recognize that the MOD-025-2 requirements became effective on July 1, 2016, and therefore failed to timely schedule and perform the necessary testing. Shortly after the July 1, 2016 effective date, Leeward Renewable Energy, owner and operator of Allegheny Ridge Wind Farm, made organizational changes that included the hiring of a Director of Regulatory Compliance who reports to the Chief Operating Officer. The discovery of this noncompliance is the result of the Director's review of the NERC Compliance Program. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because ARWF compliance staff failed to interpret and implement MOD-025-2 correctly. A root cause of this noncompliance is ARWF’s failure to effectively plan for the July 1, 2016 effective date for MOD-025-2. This issue started on July 1, 2016, when ARWF was required to comply with MOD-025-2 R2 and ended on May 11, 2017, when ARWF completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because ARWF is an intermittent generator deriving its power output from variance driven wind conditions. During the noncompliance, ARWF contributed a peak of approximately 80 MW to the grid and operated at approximately a 30% capacity factor. Lastly, ARWF implemented a new detective control, an annual review of ARWF’s NERC Compliance Program by its Director of Regulatory Compliance, and that detective control discovered this noncompliance. No harm is known to have occurred. ReliabilityFirst considered ARWF’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ARWF: 1) entered the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion; 2) performed a Real Power Capability Test; and 3) submitted the results of the Real Power Test to its Transmission Planner, PJM. ARWF also strengthened the following preventive controls. Upon FERC approval of applicable standards, ARWF enters the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion. (Action Tracker is maintained by a third-party NERC Consultant and weekly meetings are hosted by the consultant and attended by ARWF's Director of Regulatory Compliance and VP of Operations.) ARWF establishes project completion dates sufficiently in advance of the enforcement dates to preclude future issues. Provide lessons learned review with appropriate ARWF personnel. (Training conducted by NERC consultant on October 25 2016 for Site Operations Managers and support personnel including IT, Engineering, CEO, COO, VP of Operations and Director of Regulatory Compliance.) ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Ridge Wind Farm, LLC (ARWF) | NCR08039 | RFC2017016975 | PRC-019-2 | R1 | On February 6, 2017, ARWF submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. ARWF failed to coordinate the voltage regulating system controls with the applicable equipment capabilities and protection system settings for its facility by the July 1, 2016 deadline. ARWF did not recognize that the PRC-019-2 requirements became effective on July 1, 2016, and therefore failed to timely schedule and perform the necessary testing. Shortly after the July 1, 2016 effective date, Leeward Renewable Energy, owner and operator of Allegheny Ridge Wind Farm, made organizational changes that included the hiring of a Director of Regulatory Compliance who reports to the Chief Operating Officer. The discovery of this noncompliance is the result of the Director's review of the NERC Compliance Program. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because ARWF compliance staff failed to interpret and implement PRC-019-2 correctly. A root cause of this noncompliance is ARWF’s failure to effectively plan for the July 1, 2016 effective date for PRC-019-2. This issue started on July 1, 2016, when ARWF was required to comply with PRC-019-2 R1 and ended on May 10, 2017, when ARWF completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is the discoordination of a voltage control resulting in a generator falsely tripping. The risk is minimized because the verification study that ARWF performed for PRC-019 did not require any protective relay functions/settings to be re-programmed. ARWF contributed a peak of approximately 80 MW to the grid and operated at approximately a 30% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered ARWF’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ARWF: 1) completed Voltage Regulating Systems Controls Evaluation; 2) entered the activity into an action tracking system that assigns responsibility, identifies actions, monitors status, and tracks to completion; 3) conducted a detailed evaluation of impact and actions needed based upon internal and external resource availability; and 4) provided a lessons learned review for personnel. ARWF also strengthened the following preventive controls. Upon FERC approval of applicable standards, ARWF enters the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion. (Action Tracker is maintained by a third-party NERC Consultant and weekly meetings are hosted by the consultant and attended by ARWF's Director of Regulatory Compliance and VP of Operations.) ARWF establishes project completion dates sufficiently in advance of the enforcement dates to preclude future issues. Provide lessons learned review with appropriate ARWF personnel. (Training conducted by NERC consultant on October 25 2016 for Site Operations Managers and support personnel including IT, Engineering, CEO, COO, VP of Operations and Director of Regulatory Compliance.) ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Ridge Wind Farm, LLC (ARWF) | NCR08039 | RFC2017016978 | PRC-024-2 | R1 | On February 7, 2017, ARWF submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. ARWF failed to evaluate and implement applicable generator frequency protective relay settings for its facility by the July 1, 2016 deadline. ARWF did not recognize that the PRC-024-2 requirements became effective on July 1, 2016, and therefore failed to timely schedule and perform the necessary testing. Shortly after the July 1, 2016 effective date, Leeward Renewable Energy, owner and operator of Allegheny Ridge Wind Farm, made organizational changes that included the hiring of a Director of Regulatory Compliance who reports to the Chief Operating Officer. The discovery of this noncompliance is the result of the Director's review of the NERC Compliance Program. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because ARWF compliance staff failed to interpret and implement PRC-024-2 correctly. A root cause of this noncompliance is ARWF’s failure to effectively plan for the July 1, 2016 effective date for PRC-024-2. This issue started on July 1, 2016, when ARWF was required to comply with PRC-024-2 R1 and ended on May 11, 2017, when ARWF completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is minimized because the verification study that ARWF performed for PRC-024-2 R1 did not require any protective relay functions/settings to be re-programmed. ARWF contributed a peak of approximately 80 MW to the grid and operated at approximately a 30% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered ARWF’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ARWF hired the services of an engineering firm with experience in assessing wind projects with PRC-024-2 to verify the settings. The engineering firm coordinated with stakeholders to reprogram settings. ARWF also strengthened the following preventive controls. Upon FERC approval of applicable standards, ARWF enters the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion. (Action Tracker is maintained by a third-party NERC Consultant and weekly meetings are hosted by the consultant and attended by ARWF's Director of Regulatory Compliance and VP of Operations.) ARWF establishes project completion dates sufficiently in advance of the enforcement dates to preclude future issues. Provide lessons learned review with appropriate ARWF personnel. (Training conducted by NERC consultant on October 25 2016 for Site Operations Managers and support personnel including IT, Engineering, CEO, COO, VP of Operations and Director of Regulatory Compliance.) ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Ridge Wind Farm, LLC (ARWF) | NCR08039 | RFC2017016979 | PRC-024-2 | R2 | On February 7, 2017, ARWF submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R2. ARWF failed to evaluate and implement applicable generator frequency protective relay settings for its facility by the July 1, 2016 deadline. ARWF did not recognize that the PRC-024-2 requirements became effective on July 1, 2016, and therefore failed to timely schedule and perform the necessary testing. Shortly after the July 1, 2016 effective date, Leeward Renewable Energy, owner and operator of Allegheny Ridge Wind Farm, made organizational changes that included the hiring of a Director of Regulatory Compliance who reports to the Chief Operating Officer. The discovery of this noncompliance is the result of the Director's review of the NERC Compliance Program. This noncompliance involves the management practice of workforce management and planning. Workforce management and planning are both involved because ARWF compliance staff failed to interpret and implement PRC-024-2 correctly. A root cause of this noncompliance is ARWF’s failure to effectively plan for the July 1, 2016 effective date for PRC-024-2. This issue started on July 1, 2016, when ARWF was required to comply with PRC-024-2 R2 and ended on May 11, 2017, when ARWF completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is the tripping of a generating unit within a no trip zone. The risk is minimized because the verification study that ARWF performed for PRC-024-2 R2 required only minor changes. ARWF contributed a peak of approximately 80 MW to the grid and operated at approximately a 30% capacity factor during the noncompliance. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered ARWF’s PRC-024 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ARWF hired the services of an engineering firm with experience in assessing wind projects with PRC-024-2 to verify the settings. The engineering firm coordinated with stakeholders to reprogram settings. ARWF also strengthened the following preventive controls. Upon FERC approval of applicable standards, ARWF enters the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion. (Action Tracker is maintained by a third-party NERC Consultant and weekly meetings are hosted by the consultant and attended by ARWF's Director of Regulatory Compliance and VP of Operations.) ARWF establishes project completion dates sufficiently in advance of the enforcement dates to preclude future issues. Provide lessons learned review with appropriate ARWF personnel. (Training conducted by NERC consultant on October 25 2016 for Site Operations Managers and support personnel including IT, Engineering, CEO, COO, VP of Operations and Director of Regulatory Compliance.) Allegheny requested an extension to complete the mitigation plan by November 18, 2017 because they are currently coordinating with the engineering firm on a scope of work to determine whether or not Gamesa can re-program noncompliant turbine settings. In addition, two relay settings associated with the substation will require an outage which is tentatively scheduled for mid-October.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2017017303 | EOP-001-2.1b | R5 | On March 15, 2017, AEP submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue of EOP-001-2.1b R5. On January 9, 2017, during a routine document review check, AEP discovered that it missed its 2016 annual review of its Emergency Operating Plan. The Requirement states that the TOP must annually review and update its Emergency Operating Plan and provide a copy of the same to its Reliability Coordinator and neighboring TOPs and Balancing Authorities. The Emergency Operating Plan is a comprehensive plan that requires external coordination. While portions of the Emergency Operating Plan were updated throughout 2016, final completion of the Emergency Operating Plan and official coordination with the applicable Reliability Coordinator and neighboring TOPs was not completed by December 31, 2016. AEP completed its review of the Emergency Operating Plan and sent the updated revision to its Reliability Coordinator and neighboring TOPs on January 18, 2017. Although AEP had good detective controls that resulted in AEP’s quick identification of the noncompliance, the root cause was lack of procedure controls to prevent the noncompliance by ensuring the review and coordination was timely completed. This noncompliance involves the management practice of asset and configuration management, which includes managing changes to assets, such as the Emergency Operating Plan here. This issue started on January 1, 2017, the date by which AEP was required to review, update, and coordinate its Emergency Operating Plan under EOP-001-2.1b R5, and ended on January 18, 2017, when AEP completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Although the revised Emergency Operating Plan was not issued until January, 2017, the portions of the document that required Reliability Coordinator coordination (e.g. System Restoration and GMD Procedures) occurred in 2016, thus reducing the risk of relevant entities not being aware of changes to the Emergency Operating Plan. Additionally, AEP participated in the MISO EOP Workshop in October 2016 to share AEP emergency plans with participating Reliability Coordinators and TOPs, thus further reducing the risk of relevant entities not being aware of changes to the Emergency Operating Plan. Lastly, AEP quickly identified and mitigated the noncompliance. No harm is known to have occurred. ReliabilityFirst considered AEP’s EOP-001 R5 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, AEP: 1) updated its Emergency Operating Plan (version 19); 2) continued the routine document review process; and 3) changed the coordination process to meet the new EOP-011 document review and coordination requirement. ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Aurora Generation, LLC (Aurora) | NCR11659 | RFC2016016303 | MOD-025-2 | R1 | On October 3, 2016, Aurora submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. On July 12, 2016, LS Power completed the purchase of the Aurora plant from NRG. The previous owner of Aurora had a large and diverse fleet with a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration. This compliance schedule did not include completing 40% of the applicable units for the Aurora plant by the July 1, 2016, deadline. The sale shifted the timeline requirements for the plant. The noncompliance was confirmed by the new owner (LS Power) after closing of the Aurora sale. LS Power identified this issue and notified ReliabilityFirst of this issue via an email on July 27, 2016. On September 13, 2016 ReliabilityFirst provided feedback to Aurora that it should consider making Self-Reports for MOD-025. This noncompliance involves the management practice of verification, planning, and workforce management. Verification and planning are involved because LS Power failed to verify that the Aurora plant would be compliant with MOD-025 upon its purchase of Aurora in 2016. This failure to verify that Aurora would be compliant and a failure to come up with a plan to make Aurora compliant by July 1, 2016 following the ownership transition is a root cause of this noncompliance. Workforce management is also involved because Aurora staff initially failed to identify the potential noncompliance created by the sale of the plant. This issue started on July 12, 2016, when Aurora was required to comply with MOD-025-2 R1 and ended on July 1, 2017, when Aurora completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Aurora provided all required modeling data required by MOD-023-1 and the recently retired standards of MOD-010 and MOD-012. This reduces the risk because it shows that Aurora has recently provided correct modeling data similar to the data required by MOD-025 to MISO and Aurora’s Transmission Planner (TP). LS Power also immediately identified this noncompliance after taking ownership of Aurora and contacted ReliabilityFirst to get direction on how to handle this noncompliance which evidences both strong detective controls and a strong internal compliance program. Lastly, a contributing cause is the timing of the sale of Aurora and MOD-025 becoming enforceable. The unique facts and circumstances of this noncompliance are unlikely to occur again. (Finally, it should be noted that if the previous owner had not sold the generating Facilities, from what the self-report stated, there would not have been a noncompliance during the time frame, since the previous owner would have been afforded more time to verify the Real Power capability of the applicable Facilities in accordance with the Implementation Plan.) No harm is known to have occurred. ReliabilityFirst considered Aurora’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Aurora requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activities. Aurora received four competitive cost proposals and performed a thorough technical and cost evaluation. LS Power selected Kestrel Power Engineering on September 26, 2016 to perform the required work. Even though PRC-019, PRC-024, and MOD-025 allow a staged implementation plan until July 1, 2019 for 100% completion, LS Power approved completing 100% of the activities for the four units at Aurora in 2017. These mitigating activities remediate the noncompliance and complete the required PRC-019, PRC-024, and MOD-025 activities for all plant units significantly earlier than the NERC staged implementation schedule dates allow. Aurora has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Aurora’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Aurora’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Aurora conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator reliability Standards apply and what are their responsibilities. c) Aurora conduct internal audits of their NERC program on a three-year basis. d) Aurora uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For MOD-025, a work order is generated to ensure that the Real and Reactive testing is completed on generating units every five-years and not to exceed 66 months.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Aurora Generation, LLC (Aurora) | NCR11659 | RFC2016016302 | MOD-025-2 | R2 | On October 3, 2016, Aurora submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. On July 12, 2016, LS Power completed the purchase of the Aurora plant from NRG. The previous owner of Aurora had a large and diverse fleet with a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration. This compliance schedule did not include completing 40% of the applicable units for the Aurora plant by the July 1, 2016, deadline. The sale shifted the timeline requirements for the plant. The noncompliance was confirmed by the new owner (LS Power) after closing of the Aurora sale. LS Power identified this issue and notified ReliabilityFirst of this issue via an email on July 27, 2016. On September 13, 2016 ReliabilityFirst provided feedback to Aurora that it should consider making Self-Reports for MOD-025. This noncompliance involves the management practice of verification, planning, and workforce management. Verification and planning are involved because LS Power failed to verify that the Aurora plant would be compliant with MOD-025 upon its purchase of Aurora in 2016. This failure to verify that Aurora would be compliant and a failure to come up with a plan to make Aurora compliant by July 1, 2016 following the ownership transition is a root cause of this noncompliance. Workforce management is also invovled because Aurora staff failed to identify the potential noncompliance created by the sale of the plant. This issue started on July 12, 2016, when Aurora was required to comply with MOD-025-2 R2 and ended on July 1, 2017 when Aurora completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Aurora provided all required modeling data required by MOD-023-1 and the recently retired standards of MOD-010 and MOD-012. This reduces the risk because it shows that Aurora has recently provided correct modeling data similar to the data required by MOD-025 to MISO and Aurora’s Transmission Planner (TP). LS Power also immediately identified this noncompliance after taking ownership of Aurora and contacted ReliabilityFirst to get direction on how to handle this noncompliance which evidences both strong detective controls and a strong internal compliance program. Lastly, a contributing cause is the sale of Aurora around the time that MOD-025 became enforceable and that is a onetime event that is unlikely to occur again. (Finally, it should be noted that if the previous owner had not sold the generating Facilities, from what the self-report stated, there would not have been a noncompliance during the time frame, since the previous owner would have been afforded more time to verify the Real Power capability of the applicable Facilities in accordance with the Implementation Plan.) No harm is known to have occurred. ReliabilityFirst considered Aurora’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Aurora requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activities. Aurora received four competitive cost proposals and performed a through technical and cost evaluation. LS Power selected Kestrel Power Engineering on September 26, 2016 to perform the required work. Even though PRC-019, PRC-024, and MOD-025 allow a staged implementation plan until July 1, 2019 for 100% completion, LS Power approved completing 100% of the activities for the four units at Aurora in 2017. These mitigating activities remediate the noncompliance and complete the required PRC-019, PRC-024, and MOD-025 activities for all plant units significantly earlier than the NERC staged implementation schedule dates allow. Aurora has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Aurora’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Aurora’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Aurora conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator reliability Standards apply and what are their responsibilities. c) Aurora conduct internal audits of their NERC program on a three-year basis. d) Aurora uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For MOD-025, a work order is generated to ensure that the Real and Reactive testing is completed on generating units every five-years and not to exceed 66 months.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Aurora Generation, LLC (Aurora) | NCR11659 | RFC2016016304 | PRC-019-2 | R1 | On October 3, 2016, Aurora submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. On July 12, 2016, LS Power completed the purchase of the Aurora plant from NRG. The previous owner of Aurora had a large and diverse fleet with a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration. This compliance schedule did not include completing 40% of the applicable units for the Aurora plant by the July 1, 2016, deadline. The sale shifted the timeline requirements for the plant. The noncompliance was confirmed by the new owner (LS Power) after closing of the Aurora sale. LS Power identified this issue and notified ReliabilityFirst of this issue via an email on July 27, 2016. On September 13, 2016 ReliabilityFirst provided feedback to Aurora that it should consider making Self-Reports for PRC-019 and PRC-024. This noncompliance involves the management practice of verification, planning, and workforce management. Verification and planning are involved because LS Power failed to verify that the Aurora plant would be compliant with PRC-019 upon its purchase of Aurora in 2016. This failure to verify that Aurora would be compliant and a failure to come up with a plan to make Aurora compliant by July 1, 2016 following the ownership transition is a root cause of this noncompliance. Workforce management is also involved because Aurora staff failed to identify the potential noncompliance created by the sale of the plant. This issue started on July 12, 2016, when Aurora was required to comply with PRC-019-2 R1 and ended on July 1, 2017, when Aurora completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that Aurora’s noncompliance has the potential to harm the BPS by causing a discoordination of voltage controls which can result in a generator falsely tripping. The risk is minimized because Aurora has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since Aurora started operating. When Aurora performed the verification, only minor changes were required. A contributing cause of this noncompliance is the sale of Aurora to LS Power around the time that PRC-019 became enforceable and that is a onetime event that resulted from the sale of the plant and the implementation of a new Standard and is unlikely to occur again. Further, LS Power also immediately identified this noncompliance after taking ownership of Aurora and contacted ReliabilityFirst to get direction on how to handle this noncompliance which evidences both strong detective controls and a strong internal compliance program. (Finally, it should be noted that if the previous owner had not sold the generating Facilities, from what the self-report stated, there would not have been a noncompliance during the time frame, since the previous owner would have been afforded more time to verify the Real Power capability of the applicable Facilities in accordance with the Implementation Plan.) No harm is known to have occurred. ReliabilityFirst considered Aurora’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Aurora requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activities. Aurora received four competitive cost proposals and performed a through technical and cost evaluation. LS Power selected Kestrel Power Engineering on September 26, 2016 to perform the required work. Even though PRC-019, PRC-024, and MOD-025 allow a staged implementation plan until July 1, 2019 for 100% completion, LS Power approved completing 100% of the activities for the four units at Aurora in 2017. These mitigating activities remediate the noncompliance and complete the required PRC-019, PRC-024, and MOD-025 activities for all plant units significantly earlier than the NERC staged implementation schedule dates allow. Aurora has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Aurora’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Aurora’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Aurora conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator reliability Standards apply and what are their responsibilities. c) Aurora conduct internal audits of their NERC program on a three-year basis. d) Aurora uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For PRC-019, Aurora created a work order to ensure that coordination of voltage regulating systems and protection systems is completed.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Aurora Generation, LLC (Aurora) | NCR11659 | RFC2016016305 | PRC-024-2 | R1 | On October 3, 2016, Aurora submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. On July 12, 2016, LS Power completed the purchase of the Aurora plant from NRG. The previous owner of Aurora had a large and diverse fleet with a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration. This compliance schedule did not include completing 40% of the applicable units for the Aurora plant by the July 1, 2016, deadline. The sale shifted the timeline requirements for the plant. The noncompliance was confirmed by the new owner (LS Power) after closing of the Aurora sale. LS Power identified this issue and notified ReliabilityFirst of this issue via an email on July 27, 2016. On September 13, 2016 ReliabilityFirst provided feedback to Aurora that it should consider making Self-Reports for PRC-019 and PRC-024. This noncompliance involves the management practice of verification, planning, and workforce management. Verification and planning are involved because LS Power failed to verify that the Aurora plant would be compliant with PRC-024 upon its purchase of Aurora in 2016. This failure to verify that Aurora would be compliant and a failure to come up with a plan to make Aurora compliant by July 1, 2016 following the ownership transition is a root cause of this noncompliance. Workforce management is also involved because Aurora staff failed to identify the potential noncompliance created by the sale of the plant. This issue started on July 12, 2016, when Aurora was required to comply with PRC-024-2 R1 and ended on July 1, 2017, when Aurora completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because Aurora has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since Aurora started operating. When Aurora performed the verification, only minor changes were required. A contributing cause of this noncompliance is the sale of Aurora to LS Power around the time that PRC-024 became enforceable and that is a onetime event that resulted from the sale of the plant and the implementation of a new Standard and is unlikely to occur again. Further, LS Power also immediately identified this noncompliance after taking ownership of Aurora and contacted ReliabilityFirst to get direction on how to handle this noncompliance which evidences both strong detective controls and a strong internal compliance program. (Finally, it should be noted that if the previous owner had not sold the generating Facilities, from what the self-report stated, there would not have been a noncompliance during the time frame, since the previous owner would have been afforded more time to verify the Real Power capability of the applicable Facilities in accordance with the Implementation Plan.) No harm is known to have occurred. ReliabilityFirst considered Aurora’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Aurora requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activities. Aurora received four competitive cost proposals and performed a through technical and cost evaluation. LS Power selected Kestrel Power Engineering on September 26, 2016 to perform the required work. Even though PRC-019, PRC-024, and MOD-025 allow a staged implementation plan until July 1, 2019 for 100% completion, LS Power approved completing 100% of the activities for the four units at Aurora in 2017. These mitigating activities remediate the noncompliance and complete the required PRC-019, PRC-024, and MOD-025 activities for all plant units significantly earlier than the NERC staged implementation schedule dates allow. Aurora has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Aurora’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Aurora’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Aurora conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator reliability Standards apply and what are their responsibilities. c) Aurora conduct internal audits of their NERC program on a three-year basis. d) Aurora uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Baltimore Gas and Electric Company (BGE) | NCR00689 | RFC2017017247 | FAC-008-3 | R6 | On March 9, 2017, BGE submitted a Self-Report stating that, as a Transmission Owner, it had an issue of FAC-008-3 R6. On December 21, 2016, during an annual review of transmission line work energized during the year, BGE discovered two instances where its published facility ratings were not consistent with the BGE Transmission Ratings Methodology (BGE TRM), which provides that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. In both instances, elements that were removed in the field were not removed from the rating calculation, and therefore artificially limited the overall Facility Ratings because they were the most limiting elements within the Facilities. (In the first instance, the elements involved were transmission elements that should have been removed from the calculation after a circuit was relocated from a retired transmission substation to a rebuilt one at the same location. In the second instance, an old transmission conductor was not removed from the calculation during a project to replace an existing single circuit overhead transmission tower line with a new dual circuit pole line.) Once they were removed, the Facility ratings were increased. The root cause of this noncompliance was deficient procedural controls for maintaining the ratings database. Another contributing cause was inadequate training on established procedures for contracted employees. These contributing causes involve the management practices of grid maintenance and implementation, which includes ensuring requirements from operations and maintenance have been communicated and implemented. This issue started on October 21, 2016, when BGE made the first change requiring an update to the facility ratings and ended on January 10, 2017, when BGE updated the ratings and communicated those updated ratings to PJM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, BGE identified the issue through an internal review that was designed to detect these types of issues. Second, the fact that the previous ratings were more limiting artificially limited the capacity of the new line, meaning that operations would have been more conservative than necessary. ReliabilityFirst also notes that these ratings were never exceeded during the time period in question. No harm is known to have occurred. ReliabilityFirst considered BGE's FAC-008 R6 compliance history in determining the disposition track. BGE’s relevant prior noncompliances with FAC-008 R6 include: a. RFC2014014269. A Compliance Exception addressing a noncompliance with FAC-008-3 R6 was posted on the NERC website on May 28, 2015. The prior noncompliance is distinguishable from the instant noncompliance because in the prior noncompliance BGE identified that four related BGE facilities had incorrect Facility Ratings. The Facility Ratings were incorrect and not updated on time because the engineer in charge of one project updated the Facility Ratings late and the engineer in charge of a second project incorrectly believed that Facility Ratings changes should be communicated at the end of a multi-facility project rather on a per-facility basis. The current noncompliance is distinguishable because it involves the relocation of a circuit and the failure to remove a conductor from the Facility rating. b. RFC2015015146. A Compliance Exception addressing a noncompliance with FAC-008-3 R6 was posted on the NERC website on February 29, 2016. The prior noncompliance is distinguishable from the instant noncompliance because the prior noncompliance involved the incorrect mapping of certain relays to their corresponding Bulk Electric System Facility. The current noncompliance, on the other hand, involves the relocation of a circuit and the failure to remove a conductor from the Facility rating. ReliabilityFirst determined that BGE’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, BGE: 1) conducted refresher training on NERC Facility Ratings Training and OP-BE-005010 “Energizing New Electrical Equipment” training; 2) created an on-board checklist for new hires and contracted Project Manager/Construction Manager individuals to include NERC Facility Ratings and OP-BE-005010 training; and 3) developed a formal procedure describing the process to update and review overhead and underground transmission components in the BGE Ratings Database. This new procedure will be communicated to the entire Transmission Engineering, Design and Standards team. ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Lakewood Cogeneration, LP (Lakewood) | NCR00168 | RFC2016016311 | MOD-025-2 | R1 | On October 4, 2016, Lakewood submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. Lakewood compliance staff misinterpreted MOD-025-2 which led them to believe, incorrectly, that PJM and ISO-NE had incorporated the MOD-025-2 testing requirements in its tariff procedures and that separate MOD-025 demonstration was not necessary. Lakewood did not think they needed to perform any other MOD-025 related maintenance and testing to show compliance. This noncompliance involves the management practices of planning and information management. Planning and information management are involved because Lakewood compliance staff misunderstood the requirements of MOD-025-2. Lakewood staff incorrectly believed they did not need to take any other actions to show compliance with MOD-025-2. Lakewood’s misunderstanding of the requirements of MOD-025-2 is a root cause of this noncompliance. This issue started on July 1, 2016, when Lakewood was required to comply with MOD-025-2 R1 and ended on December 29, 2016, when Lakewood submitted the required testing it performed to PJM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized here because each Lakewood unit satisfied its real and reactive power verification requirements put in place by PJM and ISO-NE for the past five-years and each unit performed its claimed real power capability testing during the summer of 2016. Finally, no unit was requested to operate at its maximum leading or lagging reactive limit from 2014 to 2016. No harm is known to have occurred. ReliabilityFirst considered Lakewood's MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Lakewood: 1) determined if the claimed capability test performed in 2016 can be utilized to satisfy the real power verification (R1.1). Lakewood confirmed that the claimed capability tests could be utilized for R1.1. Lakewood also determined that supporting data at the points specified in R1.1 were recorded during the test and could be utilized for MOD-025-2 reporting purposes; 2) scheduled and performed any real power verifications required and reactive power verifications by the end of 2016 to minimally meet the 40% threshold at each facility that was required by July 1, 2016; and 3) published a five-year MOD-025-2 performance schedule for all Essential Power facilities. This five-year schedule will help prevent recurrence because Lakewood personnel will know what tasks they need to perform to maintain compliance with MOD-025. ReliabilityFirst has verified the completion of all mitigation activity.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | PECO Energy Company (PECO) | NCR08026 | RFC2017017150 | NUC-001-3 | R6 | On February 24, 2017, PECO submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue of NUC-001-3 R6. PECO is a party to a Nuclear Plant Interface Requirement (NPIR), which requires that the nuclear plant control room supervisors be notified prior to, and upon completion of, any work in the nuclear plant switchyards. On December 2, 2016, two PECO Overhead Transmission (OHT) crews were assigned the task of inspecting lightning masts at two separate substations connected to a nuclear plant. This activity required entrance into each substation. However, both crews failed to notify the Nuclear Plan Generator Operator (NGOP) Control Room Supervisor upon entrance and exit. The root cause of this noncompliance was a lack of understanding on the part of the PECO OHT personnel performing the work. The PECO OHT department had experienced significant personnel turnover, which resulted in current personnel not being adequately familiar with plant specific NPIRs. This major contributing factor involves the management practice of workforce management, which includes managing succession plans and providing training, education, and awareness to employees. This issue started on December 2, 2016, when the PECO OHT crews performed the work and ended later that day, when the PECO OHT crews completed their work. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the fact that lightning mast inspections are non-intrusive, meaning that they do not involve any control house protection and control equipment and also do not require any operation or manipulation of any switchyard equipment that affects the BPS. Accordingly, these inspections could not have caused any kind of inadvertent operation of substation equipment. No harm is known to have occurred. PECO’s relevant prior noncompliance with NUC-001 R6 includes: RFC2015014974. A Compliance Exception addressing a noncompliance with NUC-001-2 R6 was posted on the NERC website on December 30, 2015. The prior noncompliance is distinguishable from the instant noncompliance because the prior noncompliance involved PECO’s failure to perform quarterly battery inspections in accordance with applicable NPIRs. The current noncompliance, on the other hand, involves the coordination of maintenance work at nuclear plant switchyards. ReliabilityFirst determined that PECO’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, PECO: 1) provided refresher training/brief on NUC-001-3, applicable NPIRs and associated Interface Agreements and procedures to the PECO OHT Department; 2) created entry/exit guidance document (Job aid) to include as an attachment in Job Process Procedures (JPP). Reviewed and updated Job Process document to incorporate changes; 3) updated PECO Substation Entry procedure to include notifications required at a Nuclear Switchyard/Substation; 4) developed and installed access notification signage at all PECO Nuclear Substations; 5) reviewed updated Job Process document and Substation Entry Procedure with Maintenance Manager Substations, Maintenance Supervisors and Sr. Contract Coordinator; 6) reviewed updated Job Process document and Substation Entry Procedure with PECO Transmission and Substations (T&S) Testing Department; 7) reviewed updated Job Process document and Substation Entry Procedure with PECO T&S Engineering Managers & Design Supervisor; 8) reviewed updated Job Process document and Substation Entry Procedure with PECO OHT Department; 9) reviewed updated Job Process document and Substation Entry Procedure with project managers, construction managers, and contracted substation engineers in the PECO Project Management group that could require access to a nuclear substation; 10) reviewed updated Job Process document and Substation Entry Procedure with PECO Real Estate and Facilities “required personnel” i.e. facility mechanics that perform work at a Nuclear Substation; 11) reviewed updated Job Process document and Substation Entry Procedure with PECO Customer Field Operations Electric Meter Service Technicians; 12) reviewed updated Job Process document and Substation Entry Procedure with Utility Communications “required personnel;” and 13) will develop supplemental annual refresher and New Employee training for Nuclear Switchyard/Substation Entry requirements.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Rockford Generation, LLC (Rockford) | NCR11660 | RFC2016016309 | MOD-025-2 | R1 | On October 4, 2016, Rockford submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. LS Power purchased Rockford Generation on July 12, 2016. The previous owner of the Rockford plant had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at the Rockford plant by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at the Rockford plant by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Rockford would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Rockford, LS Power discovered that Rockford was not compliant with MOD-025-2 R1 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because Rockford’s noncompliance partially arose from its transfer in ownership close in time to the effective date for MOD-025-2 R1 and LS Power’s failure to effectively plan to ensure Rockford would be compliant after the purchase. Verification is involved because LS Power staff failed to verify that Rockford would be in compliance with MOD-025-2 upon their purchase and that is a root cause of this noncompliance. This issue started on July 12, 2016, when Rockford was required to comply with MOD-025-2 R1 and ended on March 3, 2017 when Rockford completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Rockford Generation has provided all modeling data required by MOD-032 and the recently retired standards MOD-010 and MOD-012. The data required by MOD-032, MOD-010, and MOD-012 is similar to the data required by MOD-025. LS Power also exhibited strong detective controls in identifying this noncompliance as LS Power discovered that Rockford was noncompliant with MOD-025 quickly after acquiring Rockford and promptly notified ReliabilityFirst of this noncompliance. Lastly, Rockford contributes approximately 462 MW to the grid and operated at approximately a 7% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rockford’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Rockford: 1) requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activity. Rockford selected Kestrel Power Engineering on September 26, 2016, to perform the required work; and 2) approved completing 100% of all units in 2017, even though the three standards mentioned above allow a staged implementation plan until July 1, 2019 for 100% completion. Rockford has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Rockford’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Rockford’s NERC Program Team conducts training based on the ReliabilityFirst Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Rockford conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator Reliability Standards apply and what are their responsibilities. c) Rockford conducts internal audits of their NERC program on a three-year basis. d) Rockford uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For MOD-025, a work order is generated to ensure that the Real and Reactive testing is completed on generating units every five-years and not to exceed 66 months.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Rockford Generation, LLC (Rockford) | NCR11660 | RFC2016016310 | MOD-025-2 | R2 | On October 4, 2016, Rockford submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. LS Power purchased Rockford Generation after the July 1, 2016 implementation date. The previous owner of the Rockford plant had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at the Rockford plant by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at the Rockford plant by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Rockford would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Rockford, LS Power discovered that Rockford was not compliant with MOD-025-2 R2 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because Rockford’s noncompliance partially arose from its transfer in ownership close in time to the effective date for MOD-025-2 R2 and LS Power’s failure to effectively plan to ensure Rockford would be compliant after the purchase. Verification is involved because LS Power staff failed to verify that Rockford would be in compliance with MOD-025-2 upon their purchase and that is a root cause of this noncompliance. This issue started on July 12, 2016, when Rockford was required to comply with MOD-025-2 R2 and ended on March 3, 2017 when Rockford completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Rockford Generation has provided all required modeling data required by MOD-032-1 and the recently retired standards MOD-010 and MOD-012-0. The data required by MOD-032, MOD-010, and MOD-012 is similar to the data required by MOD-025. LS Power also exhibited strong detective controls in identifying this noncompliance as LS Power discovered that Rockford was noncompliant with MOD-025 quickly after acquiring Rockford and promptly notified ReliabilityFirst of this noncompliance. Lastly, Rockford contributes approximately 462 MW to the grid and operated at approximately a 7% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rockford’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Rockford: 1) requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activity. Rockford selected Kestrel Power Engineering on September 26, 2016, to perform the required work; and 2) approved completing 100% of all units in 2017, even though the three standards mentioned above allow a staged implementation plan until July 1, 2019 for 100% completion. Rockford has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Rockford’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Rockford’s NERC Program Team conducts training based on the ReliabilityFirst Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Rockford conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator Reliability Standards apply and what are their responsibilities. c) Rockford conducts internal audits of their NERC program on a three-year basis. d) Rockford uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For MOD-025, a work order is generated to ensure that the Real and Reactive testing is completed on generating units every five-years and not to exceed 66 months
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Rockford Generation, LLC (Rockford) | NCR11660 | RFC2016016307 | PRC-019-2 | R1 | On October 3, 2016, Rockford submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. LS Power purchased Rockford Generation after the July 1, 2016 implementation date. The previous owner of the Rockford plant had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at the Rockford plant by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at the Rockford plant by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Rockford would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Rockford, LS Power discovered that Rockford was not compliant with PRC-019-2 R1 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification management. External interdependencies management is involved because Rockford’s noncompliance partially arose from its transfer in ownership close in time to the effective date for PRC-019-2 R1 and LS Power’s failure to effectively plan to ensure Rockford would be compliant after the purchase. Verification is involved because LS Power staff failed to verify that Rockford would be in compliance with MOD-025-2 upon their purchase and that is a root cause of this noncompliance. This issue started on July 12, 2016, when Rockford was required to comply with PRC-019-2 R1 and ended on March 3, 2017 when Rockford completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because Rockford has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since Rockford started operating. When Rockford performed the verification, no changes were required. A contributing cause of this noncompliance is the sale of Rockford to LS Power around the time that PRC-019 became enforceable and that is a onetime event that resulted from the sale of the plant and the implementation of a new Standard and is unlikely to occur again. Further, LS Power also immediately identified this noncompliance after taking ownership of Rockford and contacted ReliabilityFirst to get direction on how to handle this noncompliance which evidences both strong detective controls and a strong internal compliance program. Lastly, Rockford contributes approximately 462 MW to the grid and operated at approximately a 7% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rockford’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Rockford: 1) requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activity. Rockford selected Kestrel Power Engineering on September 26, 2016, to perform the required work; and 2) approved completing 100% of all units in 2017, even though the three standards mentioned above allow a staged implementation plan until July 1, 2019 for 100% completion. Rockford has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Rockford’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Rockford’s NERC Program Team conducts training based on the ReliabilityFirst Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Rockford conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator Reliability Standards apply and what are their responsibilities. c) Rockford conducts internal audits of their NERC program on a three-year basis. d) Rockford uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For PRC-019, Rockford created a work order to ensure that coordination of voltage regulating systems and protection systems is completed.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Rockford Generation, LLC (Rockford) | NCR11660 | RFC2016016308 | PRC-024-2 | R1 | On October 3, 2016, Rockford submitted a Self-Report stating that, as a Generator Operator, it had an issue of PRC-024-2 R1. LS Power purchased Rockford Generation after the July 1, 2016 implementation date. The previous owner of the Rockford plant had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at the Rockford plant by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at the Rockford plant by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Rockford would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Rockford, LS Power discovered that Rockford was not compliant with PRC-024-2 R1 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because Rockford’s noncompliance partially arose from its transfer in ownership close in time to the effective date for PRC-024-2 R1 and LS Power’s failure to effectively plan to ensure Rockford would be compliant after the purchase. Verification is involved because LS Power staff failed to verify that Rockford would be in compliance with MOD-025-2 upon their purchase and that is a root cause of this noncompliance. This issue started on July 12, 2016, when Rockford was required to comply with PRC-024-2 R1 and ended on March 3, 2017 when Rockford completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because Rockford has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since Rockford started operating. When Rockford performed the verification, only minor changes were required. A contributing cause of this noncompliance is the sale of Rockford to LS Power around the time that PRC-024 became enforceable and that is a onetime event that resulted from the sale of the plant and the implementation of a new Standard and is unlikely to occur again. Further, LS Power also immediately identified this noncompliance after taking ownership of Rockford and contacted ReliabilityFirst to get direction on how to handle this noncompliance which evidences both strong detective controls and a strong internal compliance program. Lastly, Rockford contributes approximately 462 MW to the grid and operated at approximately a 7% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Rockford’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Rockford: 1) requested proposals to complete the required PRC-019, PRC-024, and MOD-025 activity. Rockford selected Kestrel Power Engineering on September 26, 2016, to perform the required work; and 2) approved completing 100% of all units in 2017, even though the three standards mentioned above allow a staged implementation plan until July 1, 2019 for 100% completion. Rockford has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance. a) Rockford’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Rockford’s NERC Program Team conducts training based on the ReliabilityFirst Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended. b) Rockford conducts annual NERC training to ensure all plant personnel understand what Generator Owner/Generator Operator Reliability Standards apply and what are their responsibilities. c) Rockford conducts internal audits of their NERC program on a three-year basis. d) Rockford uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Seneca Generation, LLC (Seneca) | NCR11446 | RFC2017017308 | MOD-025-2 | R1 | On March 18, 2017, Seneca submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. LS Power purchased Seneca after the July 1, 2016 implementation date. The previous owner of Seneca had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at Seneca by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at Seneca by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Seneca would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Seneca, LS Power discovered that Seneca was not compliant with MOD-025-2 R1 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because Seneca’s noncompliance partially arose from its transfer in ownership close in time to the effective date for MOD-025-2 R1 and LS Power’s failure to effectively plan to ensure Seneca would be compliant after the purchase. Verification is involved because LS Power staff failed to verify that Seneca would be in compliance with MOD-025-2 upon their purchase. This failure to verify is a root cause of this noncompliance. This issue started on July 1, 2016, when Seneca was required to comply with MOD-025-2 R1 and will end on February 28 2018, when Seneca committed to complete its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Seneca has provided all required modeling data required by MOD-032-1 and the recently retired standards MOD-010 and MOD-012-0. The data required by MOD-032, MOD-010, and MOD-012 is similar to the data required by MOD-025. LS Power also exhibited strong detective controls in identifying this noncompliance as LS Power discovered that Seneca was noncompliant with MOD-025 after acquiring Seneca and notified ReliabilityFirst of this noncompliance. Lastly, Seneca contributes approximately 451 MW to the grid and operated at approximately a 14% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Seneca’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Seneca: 1) obtained PRC-019, PRC-024, and MOD-025 vendor proposals, completed a cost/scope comparison, and selected the winning bid; 2) issued a purchase order to the selected vendor; 3) gathered and assembled the required equipment data for a coordination study; and 4) submitted the equipment data to the selected vendor (Kestrel Power Engineering). Seneca will complete the following mitigation activities by February 28, 2018: 1) will conduct a PRC-019/PRC-024 generator relay/limiter coordination study; and 2) will complete MOD-025 real and reactive power baseline testing for 100% of its facility units. Seneca had difficulty in finding time to schedule an outage to perform the necessary study and testing and that difficulty is the reason why the mitigation activities will not be complete until February 2018. Seneca has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance: a) Seneca’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Seneca’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended; b) Seneca conducts annual NERC training to ensure all plant personnel understand what GO/GOP Reliability Standards apply and what are their responsibilities; c) Seneca conducts internal audits of their NERC program on a three-year basis; and d) Seneca uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For MOD-025, a work order is generated to ensure that the Real and Reactive testing is completed on generating units every five-years and not to exceed 66 months.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Seneca Generation, LLC (Seneca) | NCR11446 | RFC2017017310 | MOD-025-2 | R2 | On March 18, 2017, Seneca submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. LS Power purchased Seneca after the July 1, 2016 implementation date. The previous owner of Seneca had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at Seneca by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at Seneca by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Seneca would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Seneca, LS Power discovered that Seneca was not compliant with MOD-025-2 R1 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because Seneca’s noncompliance partially arose from its transfer in ownership close in time to the effective date for MOD-025-2 R2 and LS Power’s failure to effectively plan to ensure Seneca would be compliant after the purchase. Verification is involved because LS Power staff failed to verify that Seneca would be in compliance with MOD-025-2 upon their purchase. This failure to verify is a root cause of this noncompliance. This issue started on July 1, 2016, when Seneca was required to comply with MOD-025-2 R2 and will end on February 28, 2018, when Seneca committed to complete its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Seneca has provided all required modeling data required by MOD-032-1 and the recently retired standards MOD-010 and MOD-012-0. The data required by MOD-032, MOD-010, and MOD-012 is similar to the data required by MOD-025. LS Power also exhibited strong detective controls in identifying this noncompliance as LS Power discovered that Seneca was noncompliant with MOD-025 after acquiring Seneca and notified ReliabilityFirst of this noncompliance. Lastly, Seneca contributes approximately 451 MW to the grid and operated at approximately a 14% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Seneca’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Seneca: 1) obtained PRC-019, PRC-024, and MOD-025 vendor proposals, completed a cost/scope comparison, and selected the winning bid; 2) issued a purchase order to the selected vendor; 3) gathered and assembled the required equipment data for a coordination study; and 4) submitted the equipment data to the selected vendor (Kestrel Power Engineering). Seneca will complete the following mitigation activities by February 28, 2018: 1) will conduct a PRC-019/PRC-024 generator relay/limiter coordination study; and 2) will complete MOD-025 real and reactive power baseline testing for 100% of its facility units. Seneca had difficulty in finding time to schedule an outage to perform the necessary study and testing and that difficulty is the reason why the mitigation activities will not be complete until February 2018. Seneca has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance: a) Seneca’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Seneca’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended; b) Seneca conducts annual NERC training to ensure all plant personnel understand what GO/GOP Reliability Standards apply and what are their responsibilities; c) Seneca conducts internal audits of their NERC program on a three-year basis; and d) Seneca uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For MOD-025, a work order is generated to ensure that the Real and Reactive testing is completed on generating units every five-years and not to exceed 66 months.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Seneca Generation, LLC (Seneca) | NCR11446 | RFC2017017306 | PRC-019-2 | R1 | On March 18, 2017, Seneca submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. LS Power purchased Seneca after the July 1, 2016 implementation date. The previous owner of Seneca had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at Seneca by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at Seneca by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Seneca would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Seneca, LS Power discovered that Seneca was not compliant with PRC-019-2 R1 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because Seneca’s noncompliance partially arose from its transfer in ownership close in time to the effective date for PRC-019-2 R1 and LS Power’s failure to effectively plan to ensure Seneca would be compliant after the purchase. Verification is involved because LS Power staff failed to verify that Seneca would be in compliance with PRC-019-2 upon their purchase. This failure to verify is a root cause of this noncompliance. This issue started on July 1, 2016, when Seneca was required to comply with PRC-019-2 R1 and will end on February 28, 2018, when Seneca committed to complete its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is the discoordination of voltage control which can result in a generator falsely tripping. The risk is minimized because Seneca has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since Seneca started operating. A contributing cause of this noncompliance is the sale of Seneca to LS Power around the time that PRC-019 became enforceable and that is a onetime event that resulted from the sale of the plant and the implementation of a new Standard and is unlikely to occur again. Further, LS Power also identified this noncompliance after taking ownership of Seneca and notified ReliabilityFirst of this noncompliance which evidences both strong detective controls and a strong internal compliance program. (Finally, it should be noted that if the previous owner had not sold the generating Facilities, from what the self-report stated, there would not have been a noncompliance during the time frame, since the previous owner would have been afforded more time to verify the Real Power capability of the applicable Facilities in accordance with the Implementation Plan.) Lastly, Seneca contributes approximately 451 MW to the grid and operated at approximately a 14% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Seneca’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Seneca: 1) obtained PRC-019, PRC-024, and MOD-025 vendor proposals, completed a cost/scope comparison, and selected the winning bid; 2) issued a purchase order to the selected vendor; 3) gathered and assembled the required equipment data for a coordination study; and 4) submitted the equipment data to the selected vendor (Kestrel Power Engineering). Seneca will complete the following mitigation activities by February 28, 2018: 1) will conduct a PRC-019/PRC-024 generator relay/limiter coordination study; and 2) will complete MOD-025 real and reactive power baseline testing for 100% of its facility units. Seneca had difficulty in finding time to schedule an outage to perform the necessary study and testing and that difficulty is the reason why the mitigation activities will not be complete until February 2018. Seneca has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance: a) Seneca’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Seneca’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended; b) Seneca conducts annual NERC training to ensure all plant personnel understand what GO/GOP Reliability Standards apply and what are their responsibilities; c) Seneca conducts internal audits of their NERC program on a three-year basis; and d) Seneca uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval. For PRC-019, Seneca created a work order to ensure that coordination of voltage regulating systems and protection systems is completed.
2017-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Seneca Generation, LLC (Seneca) | NCR11446 | RFC2017017307 | PRC-024-2 | R1 | On March 18, 2017, Seneca submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. LS Power purchased Seneca after the July 1, 2016 implementation date. The previous owner of Seneca had a large and diverse fleet, and implemented a compliance schedule for PRC-019, PRC-024, and MOD-025 based on their bundled NERC registration using the large fleet as the baseline for implementation. The previous owner’s implementation plan did not include completing 40% of the applicable units at Seneca by July 1, 2016. Based off of this previous owner’s implementation plan, verification was not performed at 40% of the applicable units at Seneca by July 1, 2016. During the purchase process, LS Power did not effectively plan to ensure that Seneca would be compliant with the July 1, 2016 newly enforceable Standards and Requirements. After purchasing Seneca, LS Power discovered that Seneca was not compliant with PRC-024-2 R1 and took steps to return to compliance. LS Power initially notified ReliabilityFirst of this noncompliance via an email on July 27, 2016. This noncompliance involves the management practices of external interdependencies and verification. External interdependencies management is involved because Seneca’s noncompliance partially arose from its transfer in ownership close in time to the effective date for PRC-024-2 R1 and LS Power’s failure to effectively plan to ensure Seneca would be compliant after the purchase. Verification management is involved because LS Power staff failed to verify that Seneca would be in compliance with PRC-024-2 upon their purchase. This failure to verify is a root cause of this noncompliance. This issue started on July 1, 2016, when Seneca was required to comply with PRC-024-2 R1 and will end on February 28, 2018, when Seneca committed to complete its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that if the frequency relays are set in the “no trip zone”, a generator could trip incorrectly for a system event, and thereby cause a loss of generation. The risk is minimized because Seneca has not had any generator trips caused by incorrect coordination of the voltage regulating system control and protection systems since Seneca started operating. A contributing cause of this noncompliance is the sale of Seneca to LS Power around the time that PRC-019 became enforceable and that is a onetime event that resulted from the sale of the plant and the implementation of a new Standard and is unlikely to occur again. Further, LS Power also identified this noncompliance after taking ownership of Seneca and notified ReliabilityFirst of this noncompliance which evidences both strong detective controls and a strong internal compliance program. (Finally, it should be noted that if the previous owner had not sold the generating Facilities, from what the self-report stated, there would not have been a noncompliance during the time frame, since the previous owner would have been afforded more time to verify the Real Power capability of the applicable Facilities in accordance with the Implementation Plan.) Lastly, Seneca contributes approximately 451 MW to the grid and operated at approximately a 14% capacity factor during the noncompliance. No harm is known to have occurred. ReliabilityFirst considered Seneca’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Seneca: 1) obtained PRC-019, PRC-024, and MOD-025 vendor proposals, completed a cost/scope comparison, and selected the winning bid; 2) issued a purchase order to the selected vendor; 3) gathered and assembled the required equipment data for a coordination study; and 4) submitted the equipment data to the selected vendor (Kestrel Power Engineering). Seneca will complete the following mitigation activities by February 28, 2018: 1) will conduct a PRC-019/PRC-024 generator relay/limiter coordination study; and 2) will complete MOD-025 real and reactive power baseline testing for 100% of its facility units. Seneca had difficulty in finding time to schedule an outage to perform the necessary study and testing and that difficulty is the reason why the mitigation activities will not be complete until February 2018. Seneca has also instituted and strengthened the following preventative controls to help prevent recurrence of this noncompliance: a) Seneca’s NERC team has a standing Fleetwide teleconference (2nd Thursday at 11:00 am PT) to review the plant’s data gathering, evidence, and submittal for all NERC Reliability standards. Submittals are reviewed and compliance evidence is discussed to ensure appropriate data is being collected and stored. In addition to this standing meeting, individual plant reviews are conducted as needed. NERC duties are segregated between plant personnel (who are generating the data) and corporate employees (who are reviewing the data). In addition, prior to any submittal on the webCDMS site, the reports are reviewed and approved by the Authorizing officer. During the monthly Fleetwide teleconference, Seneca’s NERC Program Team conducts training based on the RF Compliance Program Monthly Update letter, the open compliance call, and the various compliance workshops attended; b) Seneca conducts annual NERC training to ensure all plant personnel understand what GO/GOP Reliability Standards apply and what are their responsibilities; c) Seneca conducts internal audits of their NERC program on a three-year basis; and d) Seneca uses a Work Management System. Standards that include time-based intervals for compliance are entered as work orders into the Maximo System. A work order is generated to be completed before the due date of the interval.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Caprock Wind LLC (Caprock) | NCR05059 | SPP2016016226 | PRC-024-2 | R2 | On September 28, 2016, Caprock submitted a Self-Report stating that, as a Generator Owner, it was not compliant with PRC-024-2 R2. Caprock did not verify that the protective relays at its 80 MW wind farm were set such that its generators would not trip when system voltage is within the “no trip zone” of PRC-024 Attachment 2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through November 18, 2017, the date Caprock has committed to complete its mitigation plan. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new standard and requirement, and a lack of managerial oversight to ensure adherence to the standard and requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Here, the risk to the BPS is mitigated because Caprock is a small 80 MW wind farm, only capable of intermittent generation. Additionally, Caprock has not experienced any unexpected voltage trips since commissioning in 2012. No harm is known to have occurred as a consequence of Caprock’s noncompliance with PRC-024-2 R2. SPP RE reviewed Caprock’s violation history and determined that Caprock has no prior instances of noncompliance with PRC-024-2. | To mitigate this noncompliance issue, Caprock plans to complete the following mitigation activities by November 18, 2017: 1. engage an engineering firm to perform an assessment of Caprock’s voltage protection relays to ensure compliance with PRC-024-2 R2; 2. reprogram voltage protection relays that do not comply with PRC-024-2 R2; 3. conduct a "lessons learned" training session for Site Operations Managers and support personnel including IT, Engineering, CEO, COO, VP of Operations and Director of Regulatory Compliance; 4. implement an action tracking system that will assign responsibility to the appropriate party and identify an action plan to comply with FERC approved standards and monitor project status until completion; and 5. establish project completion dates well in advance of the enforcement dates, to preclude future noncompliance issues.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Caprock Wind, LLC (Caprock) | NCR05059 | SPP2016016224 | PRC-024-2 | R1 | On September 28, 2016, Caprock submitted a Self-Report stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1 because it did not verify that the frequency protective relays at its 80 MW wind farm were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through November 18, 2017, the date Caprock has committed to complete its mitigation for the noncompliance. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new standard and requirement and a lack of managerial oversight, ensuring adherence to the new standard and requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relays in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Caprock is a wind farm generating facility with 80 – one MW wind turbine generators that run intermittently and are capable of providing minimal system frequency support. In addition, Caprock has operated without experiencing any frequency, or PRC-024-2 related issues since May 29, 2012, the commissioning date of the facility. No harm is known to have occurred. SPP RE reviewed Caprock’s violation history and determined that Caprock has no prior instances of noncompliance with PRC-024-2 R1. | To mitigate this issue, Caprock commits to complete the following mitigation activities by November 18, 2017: 1) hired a consultant to assess the frequency protective relay settings; 2) conducted a “lessons learned” training session for Site Operations Managers and support personnel including IT, Engineering, Chief Executive Officer, Chief Operating Officer, Vice President of Operations and Director of Regulatory Compliance. 3) Re-program relay settings if the report from the consultant identifies non-compliant frequency relay settings; 4) develop an action tracking system that will assign responsibility to the appropriate party, identify an action plan to comply with a new standard and monitor project status until completion; and 5) host a weekly meeting between the Director of Regulatory Compliance, Vice President of Operations and the NERC consultant that maintains the standards action tracking system.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Cimarron Bend Wind Project, LLC (Cimarron) | NCR11693 | SPP2017017480 | VAR-002-4 | R1 | On April 26, 2017, Cimarron submitted a Self-Certification stating that, as a Generator Operator, it had an issue of noncompliance with VAR-002-4 R1. On March 31, 2017, at 5:00 p.m., during startup testing, the Voltage Controller, i.e., the automatic voltage regulator, for Unit II at Cimarron was disabled due to a suspected loss of power. Unit II began commercial operations at 12:00 a.m. on April 1st, 2017, with its Voltage Controller out of service and its Control Monitoring Room Operators unaware of the Voltage Controller status. On April 6, 2017, at 1:45 p.m., a Control Monitoring Room Operator discovered that the Voltage Controller was disabled and immediately notified Cimarron’s Transmission Operator (TOP). At 2:48 p.m. that same day, the Unit II Voltage Controller was restored to automatic operation and the TOP was notified. At the time the Unit II Voltage Controller became inoperable, Cimarron’s System Control and Data Acquisition system was not configured to collect generator voltage data for Unit II and the status alarm for the Unit II Voltage Controller had not been installed. Unit II is a 200 MW wind farm connected radially to a ring bus located at Cimarron Unit 1 (also a 200 MW wind farm) and both units share a common point of interconnection with the bulk electric system. For the duration of the outage of the Unit II Voltage Controller, the Unit I Voltage Controller was in automatic mode and controlling voltage within the voltage schedule established by Cimarron’s TOP. The duration of this instance of noncompliance was from March 31, 2017, the date the Unit II Voltage Controller became disabled and the Cimarron TOP was not notified, until April 6, 2017, the date the Unit II Voltage Controller was placed in automatic mode and the TOP notified. The root cause of this instance of noncompliance was lack of procedures to ensure proper operation of the Voltage Controller during startup testing and verification of its operation prior to commercial operations. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to operate a generator in the automatic voltage control mode limits the ability of the generator to respond automatically to system voltage excursions. When generators are unavailable to provide voltage support, the reliability of the BPS is negatively affected because the ability of the BPS to ride through a voltage event is diminished. Here, the outage of the Voltage Controller was for a short duration and the generator is not capable of providing significant voltage support. Additionally, for the duration of the event, Unit 1, a wind farm of equal size and sharing the same interconnection, was operating in automatic voltage control mode and capable of responding to voltage excursions. No harm is known to have resulted from the noncompliance. A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities, including the noncompliance by Cimarron’s affiliate, Smoky Hills Wind Farm, LLC (Smoky), with VAR-002-1.1b R3 (SPP2013012628) was posted on the NERC website on September 30, 2014. The 60-day review period passed on November 29, 2014. SPP RE considered the compliance history of Cimarron and determined that the instant compliance issue was appropriate for Compliance Exception treatment because: (1) the prior noncompliance involved an affiliate and is not indicative of a systemic problem; (2) the prior noncompliance was discovered during a compliance audit in 2013 but actually occurred in 2011; and the prior noncompliance involved different facts and circumstances, i.e., the failure to notify the TOP of the outage of an eight MVAR capacitor bank. | To mitigate this minimal risk instance of noncompliance, Cimarron: 1) conducted an onsite field investigation to evaluate the Power Plant Controller wiring design and integrity at Cimarron Unit II; 2) developed a standardized test procedure to confirm the functionality of the Power Plant Controller during a loss of power event and its impact on the voltage control device; 3) included the Power Plant Controller and Voltage Controller Alarms in the Engineering & Construction critical equipment scope; 4) updated the Operations and Maintenance Start Up and Shut Down Procedure to include a Commercial Operation Date check; 5) updated the Control Monitoring Room Start Up and Shut Down Procedure to include a Commercial Operation Date check; and 6) installed voltage controller status alarms at Cimarron Unit II. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | City Utilities of Springfield, MO (SPRM) | NCR01081 | SPP2017017940 | COM-001-2.1 | R11 | On July 14, 2017, SPRM submitted a Self-Log stating that, as a Distribution Provider (DP) and Generator Operator (GOP) it had an issue of noncompliance with COM-001-2.1 R11 because it detected a failure of its Interpersonal Communications and did not contact its Balancing Authority (BA) to determine a mutually agreeable action for the restoration of its Interpersonal Communications capability. On April 3, 2017, SPRM’s telecommunications system was affected by an AT&T system-wide problem related to its IP Flex product. AT&T’s problem resulted in SPRM’s inability to communicate with its external parties using its primary phone system. The communications problem was first reported at 10:29 a.m. to the SPRM Power System Control Operators, who perform DP duties for SPRM. SPRM Power System Control did not notify SPRM’s Balancing Authority (BA). Similarly, the SPRM John Twitty Energy Center (JTEC) performs GOP duties; experienced the same communications problem; and failed to notify SPRM’s BA of the communications failure. The AT&T problem was resolved and the IP Flex system was restored at approximately 2:07 p.m. and all affected entities, including SPRM’s BA, were notified that the primary phone system was operational. The duration of this instance of noncompliance was from April 3, 2017, at 10:29 a.m., when SPRM was notified that the communications system was not working and it did not notify its BA, through April 3, 2017, at 2:07 p.m., when the communication system was restored and the BA was notified. The root cause of this instance of noncompliance was a combination of human error and a lack of a process document. A SPRM Power System Control operator called the Reliability Coordinator (RC) desk and thought that was sufficient for notifying the BA because the Southwest Power Pool (SPP) serves as SPRM’s RC and BA. Additionally, the JTEC GOP duties document had not been updated to include the COM-001-2.1 requirements; therefore, the JTEC system operators did not know to contact the BA about the communication system outage. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with COM-001-2.1 R11 has the potential to affect the reliability of the BPS because the failure to follow the proper notification procedures could increase the risk to the BPS if an Operating Emergency occurred and the BA needed to be informed of an imminent threat or needed to issue an Operating Instruction to preserve the state of the Bulk Electric System (BES). Notwithstanding, the backup communications line was intact and operational throughout the duration of the noncompliance. The IP Flex line was unavailable for less than five hours. No harm is known to have occurred. SPRM has no relevant prior violations of COM-001-2.1 R11 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, SPRM: 1) revised the JTEC Operating Procedures to include the COM-001-2.1 R11 responsibility for notifying the SPP BA during telecommunications outages; 2) distributed the updated Operating Procedure to JTEC operations personnel; and, 3) provided additional training to each Power System Operator on the requirement to notify both the SPP RC and BA desks of telecommunication issues. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | City Utilities of Springfield, MO (SPRM) | NCR01081 | SPP2017017941 | COM-001-2.1 | R10 | On July 14, 2017, SPRM submitted a Self-Log stating that, as a Transmission Operator it had an issue of noncompliance with COM-001-2.1 R10 because it did not notify its Balancing Authority (BA) within 60 minutes of the detection of a failure of an Interpersonal Communication capability that lasted 30 minutes or longer. On April 3, 2017, SPRM’s telecommunications system was affected by an AT&T system wide problem related to its IP Flex product. AT&T’s problem resulted in SPRM’s inability to communicate with external parties using its primary phone system. The communications problem was first reported to SPRM Power System Operator via email at 10:29 a.m. The SPRM Power System Operator did not notify SPRM’s BA. The AT&T problem was resolved and the IP Flex system was restored at approximately 2:07 p.m., and all affected entities, including SPRM’s BA, were notified that the primary phone system was operational again. The duration of this instance of noncompliance was from April 3, 2017, at 10:29 a.m., when SPRM was required to notify its BA that the communications system was not working, through April 3, 2017, at 2:07 p.m., when the communication system was restored and the BA was notified. The root cause of this instance of noncompliance was a combination of human error and a lack of a process document. SPRM Power System Control Operator called the Reliability Coordinator (RC) desk and thought that was sufficient for notifying the BA because the Southwest Power Pool (SPP) serves as SPRM’s RC and BA. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with COM-001-2.1 R10 has the potential to affect the reliability of the BPS because the failure to notify the BA within 60 minutes could increase the risk to the BPS if an Operating Emergency occurred and the BA needed to be informed of an imminent threat or needed to issue an Operating Instruction to preserve the state of the Bulk Electric System. Notwithstanding, alternative communications were intact and operational throughout the duration of the noncompliance. The IP Flex line was unavailable for less than five hours. No harm is known to have occurred. SPRM has no relevant prior violations of COM-001-2.1 R10 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, SPRM provided additional training to each Power System Operator on the requirement to notify both the SPP desks within 60 minutes of telecommunication issues. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Eastman Cogeneration Limited Partnership (Eastman) | NCR01092 | SPP2016015923 | PRC-024-2 | R2 | On July 21, 2016, Eastman submitted a Self-Report stating that, as a Generator Owner, it had an issue of noncompliance with PRC-024-2 R2. Eastman did not verify that the protective relays for its cogenerating facility’s two 165 MW gas turbines and one 127 MW steam turbine were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024-2 R2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2017, the date Eastman committed to complete its mitigation of the noncompliance. The root cause of this instance of noncompliance was a combination of Eastman’s lack of understanding of the new standard and requirement, and a lack of managerial oversight to ensure adherence with the standard and requirement. | This noncompliance issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Here, the risk to the BPS is mitigated because approximately 50% of the cogeneration facility capacity is consumed by its host and Eastman has not experienced any unexpected voltage trips since commissioning in 2001. No harm is known to have occurred as a consequence of Eastman’s noncompliance with PRC-024-2 R2. SPP RE reviewed Eastman’s violation history and determined that Eastman has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Eastman commits to complete the following mitigation activities by December 30, 2017: 1) review the violation and corrective actions with the appropriate staff to ensure the issue will not happen again; 2) complete the necessary coordination study on the protective relays; 3) send the new relay set points to the Transmission Operator (American Electric Power) for approval before settings changes are made; and 4) perform the maintenance activity to reset the protective relays.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Sikeston Board of Municipal Utilities (Sikeston) | NCR01142 | SPP2016016285 | MOD-025-2 | R1; R1.1, R1.2 | On September 30, 2016, Sikeston submitted a Self-Certification stating that, as a Generator Operator, it had an issue of noncompliance with MOD-025-2 R1. Sikeston did not verify the Real Power capability of its Sikeston Power Station generation facility in accordance with Attachment 1 of MOD-025-2 (R1.1) and submit a completed Attachment 2 or the equivalent to its Transmission Planner (TP) in accordance with the requirements of MOD-025-2 (R1.2). The duration of this instance of noncompliance was from July 1, 2016, the date MOD-025-2 became mandatory and enforceable, through September 20, 2016, the date Sikeston completed the required capability testing and submitted the results to its TP. The root cause of this instance of noncompliance was a combination of human error and a lack of controls. Sikeston’s management failed to recognize that the implementation date for MOD-025-2 was July 1, 2016, and there were no controls in place to prevent the oversight. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate long-term decisions affecting the reliability of the BPS. Notwithstanding Sikeston’s failure to perform the real power capability test for the Sikeston Power Station in accordance with MOD-025-2 Attachment 1, it provides the summer net real power capability of the Sikeston Power Station to the Southwestern Power Administration (SWPA), its TP, pursuant to requirements in the Southwest Power Pool (SPP) Planning Criteria, Although the scope of data required by the SPP Planning Criteria differs from the verification specifications of MOD-025-2 Attachment 1, the information captured is substantially the same. Additionally, there was no substantive difference in the Sikeston Power Station real power capability reported to SWPA and SPP. No actual harm is known to have occurred as a result of this noncompliance. Sikeston has no relevant prior violations of MOD-025-2 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, Sikeston: 1) performed a real power capability test of the Sikeston Power Station; 2) reported the results of the real power capability test to the SWPA and SPP; and 3) created a Reliability Standard spreadsheet, wherein, the effective date of Reliability Standards is tracked. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Sikeston Board of Municipal Utilities (Sikeston) | NCR01142 | SPP2016016286 | MOD-025-2 | R2; R2.1, R2.2 | On September 30, 2016, Sikeston submitted a Self-Certification stating that, as a Generator Operator, it had an issue of noncompliance with MOD-025-2 R1. Sikeston did not verify the Reactive Power capability of its Sikeston Power Station generation facility in accordance with Attachment 1 of MOD-025-2 (R2.1) and submit a completed Attachment 2 or the equivalent to its Transmission Planner (TP) in accordance with the requirements of MOD-025-2 (R2.2). The duration of this instance of noncompliance was from July 1, 2016, the date MOD-025-2 became mandatory and enforceable, through September 20, 2016, the date Sikeston completed the required capability testing and submitted the results to its TP. The root cause of this instance of noncompliance was a combination of human error and a lack of controls. Sikeston’s management failed to recognize that the implementation date for MOD-025-2 was July 1, 2016, and there were no controls in place to prevent the oversight. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate long-term decisions affecting the reliability of the BPS. Notwithstanding Sikeston’s failure to verify the reactive power capability of the Sikeston Power Station in accordance with MOD-025-2 Attachment 1, it provides the reactive power capability of the Sikeston Power Station to the Southwestern Power Administration (SWPA), its TP, pursuant to requirements in the Southwest Power Pool (SPP) Planning Criteria. The reactive power capability of the Sikeston Power Station previously reported to SWPA and SPP is substantially the same as the information reported in MOD-025-2 Attachment 2. No actual harm is known to have occurred as a result of this noncompliance. Sikeston has no relevant prior violations of MOD-025-2 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, Sikeston: 1) performed the required reactive power capability tests of the Sikeston Power Station; 2) reported the results of the reactive power capability tests to the SWPA and SPP; and 3) created a Reliability Standard spreadsheet, wherein, the effective date of Reliability Standards is tracked. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE – Tulsa District (COETULSA) | NCR06038 | SPP2017017058 | PRC-005-2 | R1; R1.1, R1.2 | On February 24, 2017, COETULSA submitted a Self-Certification that, as a Generator Owner (GO), it had an issue of noncompliance with PRC-005-2 R1. COETULSA did not have maintenance activities in its Protection System Maintenance Program (PSMP) consistent with the PRC-005-2 and PRC-005-6 tables. Specifically, COETULSA did not check for unintentional grounds and perform load tests on its Vented Lead-Acid (VLA) Batteries, per Table 1-4a. In addition, COETULSA did not include sudden pressure relaying in the PSMP per PRC-005-6. Out of the 370 devices in COETULSA’s PSMP, 15 are sudden pressure relays and eight are VLA batteries representing a total of 6.2% of COETULSA’s protection system devices. The duration of this instance of noncompliance was from April 1, 2015, the effective date of PRC-005-2, through July 7, 2017, the date COETULSA completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was human error because COETULSA’s Internal Compliance Program (ICP) manager did not fully monitor the requirements of the Standards and was not aware of the changes in the intervals in the PRC-005-2 tables. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to maintain a comprehensive list of protection system devices and identify the required maintenance activities and intervals creates the risk that protection system devices will not be properly maintained, thereby increasing the potential for protection system misoperations. The risk to the BPS is mitigated because: COETULSA was maintaining its sudden pressure relays concurrently with the maintenance it was performing on other equipment; only 6.2% of COETULSA’s Protection System Devices were affected; and no failures of the involved protection system devices occurred. No harm is known to have occurred. COETULSA has no relevant prior violations of PRC-005-2 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, COETULSA: 1) produced a new PSMP that complied with PRC-005-2 and PRC-005-6 to include all maintenance and testing activities and protection system devices; and 2) changed internal compliance staffing to reemphasize focus on maintenance of NERC documentation and compliance. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP2016016515 | FAC-008-3 | R6 | During a Compliance Audit conducted from November 7, 2016 through November 10, 2016, SPP RE determined that Westar, as a Generator Owner (GO), was not compliant with FAC-008-3 R6. Westar’s facility rating documentation contained errors resulting in incorrect facility ratings for three generating facilities. Additionally, Westar’s Facility Rating Methodology (FRM) did not accurately reflect the procedures utilized by Westar to establish the ratings for conductors and rigid bus elements in its generation facilities. In determining the facility ratings for the Flat Ridge wind farm, Westar did not consider the ratings of the individual generator units in establishing the facility rating for the wind farm. As a consequence, the Step-Up (GSU) transformer (115 MVA), and not the generating units (105 MVA), was incorrectly identified as the most limiting element of the generating facility. In Westar’s Facility Rating Documentation Spreadsheets for the Central Plains Wind Farm and Lawrence Energy Center Unit 4 (LEC4), SPP RE identified documentation errors affecting the facility ratings. As to the Central Plains Wind Farm, Westar incorrectly identified the GSU (112 MVA) as the limiting element when a jumper (100 MVA), listed in the spreadsheet, should have been identified as the most limiting element under Summer Normal conditions. Also, inclusion of the generators in the facility rating for the wind farm resulted in the generators (101 MVA) becoming the most limiting element under other conditions. As to LEC4, notwithstanding the individual elements of the generation facility were correctly identified and rated, in the Facility Rating Documentation Spreadsheet, Westar failed to identify a bus (127 MVA) as a limiting element of the generation facility under Summer Normal Conditions. Finally, Westar’s FRM states that the emergency rating shall be equal to the normal rating for conductors and rigid bus elements when determining the facility rating for its generation facilities. In practice, however, Westar calculates the normal and emergency rating for conductors and rigid bus elements using different conductor temperatures, thereby establishing different ratings for normal and emergency conditions. The duration of this instance of noncompliance was from December 13, 2013, the day after the previous Compliance Audit, through February 27, 2017, the date Westar completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was a combination of misinterpretation of the FRM by a new Subject Matter Expert (SME) and lack of managerial oversight to ensure the SME correctly established facility ratings for its generating facilities. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to establish and utilize accurate generation facility ratings increases the potential for generation facilities to be operated in excess of their capacity rating, thereby creating the opportunity for equipment damage and facility outages. Here, the risk to the BPS is mitigated because: the resulting errors in the facility ratings were small, collectively less than 19 MVA; the noncompliance was limited to three small generating units, representing less than four percent of Westar’s installed generation capacity; two of the involved generation facilities were wind farms, only capable of intermittent generation; and the conductor and rigid bus issue was a documentation issue and did not affect the ratings of any generation facilities. No harm is known to have resulted from the noncompliance. A Spreadsheet Notice of Penalty addressing the noncompliance of certain registered entities including Westar’s noncompliance with FAC-009-1 R1 (SPP201000418) was filed with FERC under NP14-14-000 on December 30, 2013. On January 29, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Westar’s prior noncompliance relates to its failure to include all transmission circuit elements identified in its FRM in its transmission facility ratings. Additionally, the current carrying capacity of specific protection system relays were not considered in the facility ratings of the respective transmission facilities. Although the prior and instant noncompliance issues are different, i.e., SPP201000418 relates to transmission facilities and SPP2016016515 relates to generation facilities, both involve the omission of elements of a facility in the determination of a facility’s rating. Nevertheless, it is SPP RE’s determination that the instant violation is appropriate for compliance exception disposition. The prior noncompliance occurred in 2010, six years before the instant violation and more importantly, the instant noncompliance does not represent a systemic problem with Westar’s facility ratings. | To mitigate this minimal risk instance of noncompliance, Westar: 1) updated the Generating Equipment Ratings section of its FRM to accurately reflect the conductor and rigid bus rating methodology; 2) verified that the Facility Rating Documentation Spreadsheets correctly reflected the Westar FRM; 3) modified the Facility Rating Documentation Spreadsheets for Flat Ridge and Central Plains windfarms to include the generator ratings; and 4) trained the new SME on the FRM requirements. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Dempsey Ridge Wind Farm (DRWF) | NCR11179 | SPP2017017057 | PRC-005-6 | R3 | On February 24, 2017, DRWF submitted a Self-Certification stating that, as a Generator Owner (GO), it had an issue of noncompliance with PRC-005-6 R3 because it did not maintain the Protection System Devices that are in its time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed in the PRC-005-6 R3 Tables. Specifically, DRWF did not have evidence of the four-month Communications Systems test and the six-month Valve Regulated Lead-Acid (VRLA) battery tests as required by Table 1-2 and Table 1-4 (b) respectively. This issue of noncompliance involved six (11%) of DRWF’s 57 Protection System Devices. The duration of this instance of noncompliance was from January 1, 2016, the effective date of the Standard, through March 24, 2017, the date DRWF’s Communications Systems and VRLA batteries were tested and verified. The root cause of this instance of noncompliance was human error and a lack of internal controls. The DRWF Site Manager did not use the applicable High Voltage Substation Maintenance and Inspection Program (HVSMIP) Monthly Checklist specific to his plant as requested, to ensure that all Protection System Devices were tested. Additionally, DRWF had no internal controls to verify that the correct Monthly Checklist was used on a regular basis to verify Protection System maintenance and testing. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform Communications Systems tests and Valve Regulated Lead-Acid (VRLA) battery tests has the potential to affect the reliability of the BPS by increasing the risk of misoperations. Communication Systems not providing the proper signal to its intended location and/or the batteries not suppling sufficient power to relays and DC circuits could cause a misoperation of a Protection System Device. DRWF had satisfactory tests on these systems in 2015. Notwithstanding, when DRWF performed the required six-month tests on the batteries, the batteries tested at acceptable levels. In addition, when DRWF performed an end-to-end functional test on its communication systems the test results were successful. This issue of noncompliance only affected 11 percent of DRWF’s Protection System Devices. DRWF is an intermittent wind generation resource, consisting of 66, 2 MW wind turbine generators for an aggregate capacity of 132MW, that was commissioned in 2012. No harm is known to have occurred. DRWF has no relevant prior violations of PRC-005-6 R3 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, DRWF: 1) completed a battery test and inspection in August of 2016; 2) completed a functional end to end test of the communication systems; 3) required the Site Manager to no longer maintain a local or hard copy of the HVSMIP Monthly but upload the document to the AENA SharePoint site; 4) required the HVSMIP to be checked to ensure that the proper form was used, the content was complete and that there were no unresolved maintenance issues; and 5) created a digital calendar appointment with associated reminders for the next VRLA battery Inspection. SPP RE has verified the completion of all mitigation activity.
2017-10-31 | Texas Reliability Entity, Inc. (Texas RE) | Bryan Texas Utilities (BTU) | NCR04022 | TRE2017017384 | COM-001-2 | R4; R4.3 | During a Compliance Audit conducted from January 23, 2017 through March 22, 2017, Texas RE determined that BTU, as a Transmission Operator (TOP), had an issue with COM-001-2 R4.3. Specifically, BTU failed to properly designate an Alternative Interpersonal Communication capability with one of its adjacent synchronously connected TOPs. Texas RE subsequently determined that the duration of this issue was from October 1, 2015 until February 14, 2017. Accordingly, Texas RE determined that BTU had an issue with COM-001-2 R4.3 from October 1, 2015 until November 12, 2015. BTU then had an issue with COM-001-2.1 R4.3 from November 13, 2015 until February 14, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in BTU’s compliance obligations under the applicable versions. The root cause of this issue was that BTU mistakenly designated its Alternative Interpersonal Communication capability with an incorrect registered entity. In particular, BTU’s telecommunication process document referred to the owner of an adjacent transmission system rather than the TOP actually operating that adjacent synchronously connected transmission system. This issue began on October 1, 2015, when COM-001-2 R4 became enforceable, and ended on February 14, 2017, when BTU revised its process document to properly designate its Alternative Interpersonal Communication capability with the single adjacent synchronously connected TOP at issue. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This noncompliance was documentary in nature. BTU possessed multiple normal methods of communicating with its adjacent synchronously connected TOP and demonstrated that it regularly used those methods to communicate with the proper TOP. As such, the erroneous Alternative Interpersonal Communication designation would only have been involved had all of these normal communications methods failed. Further, BTU personnel demonstrated that its operators understood that references to the misidentified entity in fact referred to the proper adjacent synchronously connected TOP because that was the entity actually operating the transmission assets at issue. No harm is known to have occurred. Texas RE considered BTU’s and its affiliate’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BTU: 1) revised its telecommunications process document to correctly designate the Alternative Interpersonal Communication capability with the single adjacent synchronously connected TOP at issue; 2) provided its revised telecommunications process document to affected staff; and 3) conducted training regarding the revised telecommunications process to its affected staff. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Florida Reliability Coordinating Council (FRCC) | Bartow, City of (BAR) | NCR00003 | FRCC2017017912 | PRC-006-2 | R9. | On July 12, 2017, BAR submitted a Self-Report stating that, as a Distribution Provider Under Frequency Load Shedding (UFLS), it had an issue of PRC-006-2 R9. The issue started on March 1, 2017, when BAR failed to provide automatic tripping of load in accordance with the FRCC Under Frequency Load Shedding (UFLS) Program design and schedule for implementation as determined by its Planning Coordinator. This issue ended on May 11, 2017, when BAR corrected the relay settings to meet the new program requirements. BAR, with a summer peak of approximately 62 MW, changed its UFLS settings to be a combination of steps in the 2017 FRCC UFLS program. Challenges posed by the number of feeders in BAR’s system and amount of load to be dropped with the new program resulted in BAR modifying the settings from the approved 2017 UFLS program in order to protect critical loads. Instead of using Step 1a or Steps one through nine (1-9), BAR combined some of the one through nine (1-9) steps and ended up with a total of six (6) steps instead of nine (9). The root cause for this violation was BAR personnel attempting to avoid tripping critical loads and believing the settings implemented were complying with the new 2017 UFLS program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). BAR’s risk to the BPS was that 9% (2.66 MW) of their required load shed would have occurred at a frequency of 59.6 rather than the required 59.5. The remaining 91% (26.9 MW) of the load shed required would have occurred over five (5) additional steps at lower frequencies ranging from 59.4 to 58.4. This could have allowed an increased frequency decay by not shedding all the load properly at the required 59.5 frequency setting. After participating in a peer review, BAR re-evaluated its options and found a way to use Step 1a to drop its required 29.56 MW (50%) of load in accordance with the 2017 UFLS program. The risk was reduced because BAR’s UFLS load shed requirement is less than 0.06% of the entire FRCC Region. Furthermore, the six (6) feeder relays were armed to trip load, though not in accordance with the approved FRCC UFLS program. The acceptable cumulative percentage of load shed would have occurred over a series of six (6) steps although at lower frequencies. No load shed was required during the noncompliance period and no harm is known to have occurred. FRCC considered BAR’s PRC-006-2 (R9) compliance history in determining the disposition track. BAR has no relevant prior noncompliance. | To mitigate this issue, BAR: 1) corrected the relay settings to using Step 1a according to the 2017 FRCC UFLS program and submitted those settings to FRCC PC. To prevent recurrence, BAR: 1) will continue peer reviews as they are part of an effort to improve the BAR's compliance stance; 2) adopted an internal compliance program which provides for more awareness, peer reviews, and fosters a culture of compliance; and 3) will ensure the involvment of more employees in NERC compliance activities.
2017-09-28 | Midwest Reliability Organization (MRO) | Benson Power, LLC (BEN) | NCR11300 | MRO2016016407 | MOD-025-2 | R1 | On October 7, 2016, Benson Power, LLC (BEN) submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. Specifically, BEN did not verify its Real Power capability for 40% of its generator units by July 1, 2016 in accordance with the MOD-025-2 implementation plan. Because BEN only has one generator unit, it was required to test it by July 1, 2016 under the implementation plan. The cause of this noncompliance was that BEN did not know that this Standard and Requirement was becoming enforceable, and therefore, failed to understand its obligations under the Standard and Requirement. This failure to understand was caused by a lack of training for employees who have compliance responsibility and employees' not understanding materials sent by BEN's third-party compliance consultant. The noncompliance began on July 1, 2016, when the Standard and Requirement became enforceable on BEN, and ended on September 8, 2016, when BEN verified its Real Power capability and submitted a completed Attachment 2 to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BEN has a single steam generator unit with a nameplate rating of 73.3 MVA, and is rarely asked to provide grid support by its Transmission Operator (TOP). Additionally, the duration of the noncompliance was approximately 70 days. Further, the generator unit is not identified as a Blackstart Resource in the TOP's restoration plan, and is not associated with an IROL. Finally, there is no ongoing risk of noncompliance, as per BEN, the generator unit has been recently sold to another registered entity, and is slated to be decommissioned. No harm is known to have occurred. BEN has no relevant history of noncompliance. | To mitigate this issue, BEN: 1) performed Real and Reactive power capability testing, and reported those results to its Transmission Planner; 2) placed all periodic NERC requirements into a project management tool, including the MOD-025-2 five year interval; 3) conducted a gap analysis of its NERC Compliance Program; and 4) reached an agreement with its third-party compliance consultant regarding ongoing compliance responsibilities, which included its third-party compliance consultant performing a formal cause analysis of the noncompliance, its third-party compliance consultant providing additional compliance support, and its third-party compliance consultant logging BEN's compliance activities into a project management tool.
2017-09-28 | Midwest Reliability Organization (MRO) | Benson Power, LLC (BEN) | NCR11300 | MRO2016016406 | MOD-025-2 | R2 | On October 7, 2016, Benson Power, LLC (BEN) submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. Specifically, BEN did not verify its Reactive Power capability for 40% of its generator units by July 1, 2016 in accordance with the MOD-025-2 implementation plan. Because BEN only has one generator unit, it was required to test it by July 1, 2016 under the implementation plan. The cause of this noncompliance was that BEN did not know that this Standard and Requirement was becoming enforceable, and therefore, failed to understand its obligations under the Standard and Requirement. This failure to understand was caused by a lack of training for employees who have compliance responsibility and employees' not understanding materials sent by BEN's third-party compliance consultant. The noncompliance began on July 1, 2016, when the Standard and Requirement became enforceable on BEN, and ended on September 8, 2016, when BEN verified its Reactive Power capability and submitted a completed Attachment 2 to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BEN has a single steam generation with a nameplate rating of 73.3 MVA, and is rarely asked to provide grid support by its Transmission Operator (TOP). Additionally, the duration of the noncompliance was approximately 70 days. This delay did not appear to impact the Transmission Planner's annual model building. Further, the generator unit is not identified as a Blackstart Resource in the TOP's restoration plan, and is not associated with an IROL. Finally, there is no ongoing risk of noncompliance, as per BEN, the generator unit has been recently sold to another registered entity, and is slated to be decommissioned. No harm is known to have occurred. BEN has no relevant history of noncompliance. | To mitigate this issue, BEN: 1) performed Real and Reactive power capability testing, and reported those results to its Transmission Planner; 2) placed all periodic NERC requirements into a project management tool, including the MOD-025-2 five year interval; 3) conducted a gap analysis of its NERC Compliance Program; and 4) reached an agreement with its third-party compliance consultant regarding ongoing compliance responsibilities, which included its third-party compliance consultant performing a formal cause analysis of the noncompliance, its third-party compliance consultant providing additional compliance support, and its third-party compliance consultant logging BEN's compliance activities into a project management tool.
2017-09-28 | Midwest Reliability Organization (MRO) | Benson Power, LLC (BEN) | NCR11300 | MRO2016016405 | PRC-019-2 | R1 | On October 7, 2016, Benson Power, LLC (BEN) submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. BEN did not perform a coordination study of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable protection system devices and functions by July 1, 2016. The cause of this noncompliance was that BEN did not know that this Standard and Requirement was becoming enforceable, and therefore, failed to understand its obligations under the Standard and Requirement. This failure to understand was caused by a lack of training for employees who have compliance responsibility and employees' not understanding materials sent by BEN's third-party compliance consultant. The noncompliance began on July 1, 2016, when the Standard and Requirement became enforceable on BEN, and ended on September 8, 2016, when BEN completed the coordination study. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BEN has a single steam generation with a nameplate rating of 73.3 MVA, and is rarely asked to provide grid support by its Transmission Operator (TOP). Additionally, the duration of the noncompliance was relatively brief (70 days) and the study determined that the voltage regulating system controls were properly coordinated with the applicable Protection Systems. Further, the generator unit is not identified as a Blackstart Resource in the TOP's restoration plan, and is not associated with an IROL. Finally, there is no ongoing risk of noncompliance, as per BEN, the generator unit has been recently sold to another registered entity, and is slated to be decommissioned. No harm is known to have occurred. BEN has no relevant history of noncompliance. | To mitigate this issue, BEN: 1) completed the PRC-019-2 coordination study; 2) placed all periodic NERC requirements into a project management tool, including the PRC-019-2 five year interval; 3) conducted a gap analysis of its NERC Compliance Program; and 4) reached an agreement with its third-party compliance consultant regarding ongoing compliance responsibilities, which included its third-party compliance consultant performing a formal cause analysis of the noncompliance, its third-party compliance consultant providing additional compliance support, and its third-party compliance consultant logging BEN's compliance activities into a project management tool.
2017-09-28 | Midwest Reliability Organization (MRO) | Great River Energy (GRE) | NCR00092 | MRO2017016775 | EOP-005-2 | R16 | On December 27, 2016, GRE submitted a Self-Report stating that, as a Generator Operator, it had an issue with EOP-005-2 R16. Specifically, GRE missed the three-year Blackstart testing interval on the Maple Lake generator. The Maple Lake generator was last Blackstart tested in 2012. According to GRE, the cause of the noncompliance is that following training, new supervisors responsible for testing failed to understand that each Blackstart Resource required testing every three years. This issue started on January 1, 2016, when the Blackstart Resource missed its Blackstart testing interval, and ended on December 1, 2016, when the Blackstart Resource was tested. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential harm is reduced because the Maple Lake generator, while identified as a Blackstart Resource in the Power System Restoration Procedure, is not utilized in the plan to start another non-Blackstart unit. In the procedure, Maple Lake is utilized to restore local area load and to energize GRE's Control Center and Backup Control Center. Although, prior to restoration from Maple Lake, the Control Center and Backup Control Center are powered via on-site redundant UPS battery backup systems and diesel generators. Additionally, per GRE, the Maple Lake generator is tested every two months to ensure operational capability if called upon by the MISO market. Further, per GRE, the risk was reduced because successful Blackstart testing had been conducted in 2010 and 2012, the recent Blackstart testing did not identify any significant issues or necessary maintenance activities, and the Maple Lake generator was not called upon to function as a Blackstart Resource during the period of noncompliance. No harm is known to have occurred. GRE has no relevant history of noncompliance. | To mitigate this issue, GRE: 1) performed Blackstart testing of the Maple Lake generator; 2) provided revised training to the supervisors associated with this issue; and 3) developed a control for the testing operator and generation subject matter expert to ensure the correct units were tested and the test records are reviewed.
2017-09-28 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2016016200 | PRC-005-2(i) | R3 | On August 26, 2016, NSP, submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-005-2(i) R3. Two relays at a jointly-owned substation were not tested within their associated maintenance interval. Per NSP, the relays were lasted tested on December 3, 2009, and after that testing, the relays were incorrectly marked as "foreign owned" in the NSP protection system database. The foreign owned designation caused NSP not to perform further maintenance testing, as it appeared from the database that another registered entity was responsible for performing the maintenance. The relays should have been tested on or before December 31, 2015, but were not tested until June 7, 2016. The cause of the noncompliance was human error in entering information into the database. The noncompliance began on January 1, 2016, when the relays missed their testing interval, and ended on June 7, 2016, when the relays were tested. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope and duration of the noncompliance was limited. A review of relays at jointly owned substations did not identify any similar issues, and the duration of the noncompliance was less than six months on a six year testing interval. Additionally, the affected substation is not associated with any Interconnection Reliability Operating Limits (IROLs) or a Remedial Action Scheme (RAS). Further, per NSP, the testing did not identify any required follow-up maintenance activities and the relays were not called to activate during the noncompliance. Finally, the issue was self-identified, which is an indication of functioning detective controls. No harm is known to have occurred. NSP has no relevant history of noncompliance with PRC-005-2(i) R3. | To mitigate this issue, NSP: 1) completed the required testing on the two relays; 2) completed a review and comparison of information for relays at jointly owned substations not primarily owned by NSP; this was accomplished by comparing data in its Work Management System and data in its protection system database, this review found no other discrepancies; and 3) provided a lessons learned to business units that have the ability to make changes in the protection system database, to reinforce the importance of having accurate information in its databases.
2017-09-28 | Northeast Power Coordinating Council (NPCC) | Noble Altona Windpark, LLC | NCR10366 | NPCC2017017764 | PRC-019-2 | R1. | On June 21, 2017, Noble Altona Windpark, LLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, Noble Altona Windpark, LLC failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions by 7/1/2016, as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on August 31, 2017, when Noble Altona Windpark, LLC completed its coordination verification and adjusted voltage regulating system controls of relay SEL-351 for devices 67 AL1 and 67 AL2. The root cause of this instance of non-compliance was Noble Altona Windpark, LLC's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to its dispersed wind generating units. Upon consultation with an outside vendor, Noble Altona Windpark, LLC correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by 7/1/2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of Noble Altona Windpark, LLC's generation facility for the year 2016 was 19.9%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of Noble Altona Windpark, LLC's Wind Farm generation is 97 MW, which is less than 5.0% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (Noble Altona Windpark, LLC's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered Noble Altona Windpark, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, Noble Altona Windpark, LLC: 1) corrected the noncompliance by completing its coordination verification and adjusting voltage regulating system controls of relay SEL-351 for devices 67 AL1 and 67 AL2; and 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-09-28 | Northeast Power Coordinating Council (NPCC) | Noble Bliss Windpark, LLC | NCR10271 | NPCC2017018268 | PRC-024-2 | R3. | On August 28, 2017, Noble Bliss Windpark, LLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R3. Specifically, Noble Bliss Windpark, LLC failed to notify its PC/TP of equipment limitations of its Low Voltage Ride Through (LVRT)-type wind turbines that prevent its generating units with voltage protective relays from meeting the requirement for the 0.15V to zero volts time-frame, per the setting criteria of Requirement R2. This noncompliance started on April 8, 2017, thirty days after an engineering consultant hired by Noble Bliss Windpark, LLC documented the above equipment limitations in a report to Noble Bliss Windpark, LLC, and ended on September 6, 2017, when Noble Bliss Windpark, LLC formally notified its TP (National Grid) of its equipment limitations, after it had previously notified its PC (NYISO) on an earlier date. The root cause of this instance of non-compliance was an oversight in the notification aspect of Requirement R3 of the standard. Upon consultation with an outside vendor, Noble Bliss Windpark, LLC correctly concluded that it needed to notify its PC/TP of performance limitations inherent to its facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of Noble Bliss Windpark, LLC's generation facility for the year 2016 was 23.2%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of Noble Bliss Windpark, LLC's Wind Farm generation is 100.5 MW, which is less than 5.2% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (Noble Bliss Windpark, LLC's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered Noble Bliss Windpark, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, Noble Bliss Windpark, LLC: 1) corrected the noncompliance by formally notifying its TP (National Grid) and PC (NYISO) of its equipment limitations; and 2) to prevent a recurrence of similar instances of noncompliance: a) added a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) amended an existing service agreement with an outside consultant to provide for more effective documentation, procedure review, on-going education and auditability of the NERC Standards applicable to the Entity. NPCC has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Alcoa Power Generating Inc. (Alcoa) | NCR00667 | RFC2017017228 | PRC-005-6 | R3 | On March 6, 2017, Alcoa submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-6 R3. Alcoa’s general process for battery testing and maintenance is that an automated work order is generated by a software program and as soon as the work order is completed, the documentation is uploaded to a compliance folder by the electrical maintenance team leader. The particular battery bank at issue supports a line that was originally built as a backup line to power the Warwick Power Plan smelter pot lines. However, in April 2016, the Warwick smelter closed. As a result of this closing, the software license for the battery maintenance software was discontinued for the smelter assets. Consequently, automated work orders were stopped. Aware of the need to maintain the battery bank at issue, (Despite the smelter closing, the line supported by the battery bank at issue is still used as a redundant auxiliary feed to certain assets as well as an additional line out of a 15kV bus.) the electrical supervisor for the closed smelter continued the maintenance program by manually generating work orders and verifying completion. However, during Q4 2016, the electrical supervisor was out on short term disability for a health issue. While he was off, his replacement was not made aware of the requirements for the maintenance of this battery bank. As a result, the Q4 2016 tests were not completed. The root cause of this noncompliance was the fact that Alcoa was relying on a manual process to perform the periodic testing and maintenance of this battery bank. Another contributing cause was the fact that the electrical supervisor’s replacement was not adequately made aware of these maintenance requirements. These major contributing factors involve the management practices of grid maintenance and workforce management, which includes managing succession plans. This issue started on December 31, 2016, the last date on which Alcoa could have completed the Q4 battery maintenance and testing and ended on March 20, 2017, when Alcoa completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, Alcoa quickly detected the issue through its processes and procedures pursuant to which maintenance and testing records are regularly requested and reviewed for each quarter. Second, the line at issue was originally built as a redundant feed for a smelter pot that is no longer in service. Now, it is used as a redundant feed to an auxiliary bus. As such, its loss is not likely to lead to additional outages or failures elsewhere on the grid. No harm is known to have occurred. ReliabilityFirst considered Alcoa’s PRC-005 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Alcoa: 1) met with the Warrick Operations Facility Manager and Rolling Division Maintenance Superintendent and their engineering and electrical supervisor to review NERC Standards and PRC-005 battery requirements; 2) verified there is a working process for submittal of the Warrick Operations documents for battery maintenance from Warrick Operations to Warrick Power Plant Subject Matter Expert (SME); 3) verified that automated work orders are generated in the Warrick Operations and Rolling division facility Oracle maintenance management system; and 4) reviewed the documentation submitted by the rectifier supervisor and verified it meets the SME’s expectations and requirements. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | American Bituminous Power Partners, L.P. (ABPP) | NCR00680 | RFC2016016629 | PRC-024-2 | R2 | On December 1, 2016, ABPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R2. ABPP relied upon an incorrect interpretation offered by a NERC Consultant (ICF International) in determining that they had until 2019 to verify its relay settings or to change a relay setting to fall outside the “no trip zone”. On November 1, 2016, ABPP reached out to ReliabilityFirst for clarification on its compliance obligations for PRC-024-2 R2 and learned that the coordination changes were due July 1, 2016. Therefore, the root cause of this instance of noncompliance was ABPP’s misinterpretation of the timeline of PRC-024-2. This noncompliance involves the management practices of external interdependencies, information management, and planning. Information management and external interdependencies are both involved because ABPP relied on a NERC Consultant to inform ABPP when it needed to show compliance with PRC-024-2. That reliance on incorrect information from a third party NERC Consultant is a contributing cause of this noncompliance. Verification is also involved because ABPP did not verify that the information it was getting from its NERC Consultant was accurate and that failure to verify is another contributing cause of this noncompliance. This issue started on July 1, 2016, when ABPP was required to comply with PRC-024-2 R2 and ended on November 29, 2016, when ABPP completed its Mitigating Activities by verifying that the extant voltage relay settings are compliant. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that a voltage excursion could have occurred which may have resulted in a generator trip. The risk is minimized because the relay involved in this instance of noncompliance has been on the same trip setting (1 second trip timing) since 1993 without incident. All of ABPP’s existing settings, including overvoltage and under voltage settings and settings for over/under-frequency protective relays, were found to be compliant with the “no trip zone” defined in PRC-024-2 after ABPP completed the overdue verification. (ABPP did adjust the time delay setting on a Basler 27/59 relay by changing the under voltage time delay from 1 second to 3 seconds, but with that change, the setting still remained compliant with the “no trip zone.”) No harm is known to have occurred. ReliabilityFirst considered ABPP’s PRC-024 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ABPP hired a contractor to make the necessary verifications/changes to the relay setting. As a result of this incident, ABPP has a heightened awareness for interpretation to NERC Standards and will be more inclined to seek further counsel when/if an action required by a particular standard appears to be unclear. ABPP reviews communications relative to NERC Standards on a monthly basis and conducts a thorough review of its Internal Compliance Manual annually. These actions include a review of upcoming standards and changes/revisions to existing standards. In cases where the interpretation of the standard is unclear, as a secondary step, ABPP will seek guidance from ReliabilityFirst on their interpretation of the standard via email prior to updating the facility maintenance, protection system, and reporting plans to meet prevailing and upcoming NERC standards. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Big Sky Wind, LLC (Big Sky Wind) | NCR11461 | RFC2017017154 | MOD-025-2 | R1 | On February 27, 2017, Big Sky Wind submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. Big Sky Wind incorrectly determined that its generator real and reactive power capability modeling data was sufficient to comply with MOD-025-2 R1. After discussions with ReliabilityFirst, Big Sky Wind realized that its initial determination was incorrect and that Big Sky Wind needed to provide its Transmission Planer (TP) with verification of the real power capability of Big Sky Wind’s applicable facilities. This noncompliance involves the management practice of information management, planning, and verification. Information management and planning are involved because Big Sky Wind misunderstood the requirements of MOD-025-2 R1. Big Sky Wind’s misunderstanding of what it needed to show to achieve compliance with MOD-025-2 R1 is a root cause of the noncompliance. Verification is also involved because Big Sky Wind did not verify that its understanding of how to comply with MOD-025-2 R1 was correct. That failure to verify is a contributing cause of this noncompliance. This issue started on July 1, 2016, when Big Sky Wind was required to comply with MOD-025-2 R1 and ended on April 13, 2017, when Big Sky Wind completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Big Sky Wind submitted real and reactive capability data to the TP, but did not supply verification data in accordance with MOD-025-2. Big Sky Wind is also a wind farm with a nameplate rating of 239.4 MVA and wind is a variable resource. Further, no changes occurred from the generator real and reactive power capability modeling data which would require an update to the model. No harm is known to have occurred. ReliabilityFirst considered Big Sky Wind’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Big Sky Wind: 1) worked with the Balancing Authority to verify and confirm the accuracy of the current modeling; 2) worked with the Balancing Authority and Transmission Planner to schedule the testing; and 3) created a work order in Computerized Maintenance Management Software to ensure model validation testing occurs prior to the next scheduled interval. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Big Sky Wind, LLC (Big Sky Wind) | NCR11461 | RFC2017017155 | MOD-025-2 | R2 | On February 27, 2017, Big Sky Wind submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. Big Sky Wind incorrectly believed that its generator real and reactive power capability modeling data was sufficient to comply with MOD-025-2 R2. After discussions with ReliabilityFirst, Big Sky Wind realized that this belief was incorrect and that Big Sky Wind needed to provide its Transmission Planer (TP) with verification of the real power capability of Big Sky Wind’s applicable facilities. This noncompliance involves the management practice of information management, planning, and verification. Information management and planning are involved because Big Sky Wind misunderstood the requirements of MOD-025-2 R2. Big Sky Wind’s misunderstanding of what it needed to show to achieve compliance with MOD-025-2 R2 is a root cause of the noncompliance. Verification is also involved because Big Sky Wind did not verify that its understanding of how to comply with MOD-025-2 R2 was correct. That failure to verify is a contributing cause of this noncompliance. This issue started on July 1, 2016, when Big Sky Wind was required to comply with MOD-025-2 R2 and ended on April 13, 2017, when Big Sky Wind completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. The risk is minimized because Big Sky Wind submitted real and reactive capability data to the TP, but did not supply verification data in accordance with MOD-025-2. Big Sky Wind is also a wind farm with a nameplate rating of 239.4 MVA and wind is a variable resource. Further, no changes occurred from the generator real and reactive power capability modeling data which would require an update to the model. No harm is known to have occurred. ReliabilityFirst considered Big Sky Wind’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Big Sky Wind: 1) worked with the Balancing Authority to verify and confirm the accuracy of the current modeling; 2) worked with the Balancing Authority and Transmission Planner to schedule the testing; and 3) created a work order in Computerized Maintenance Management Software to ensure model validation testing occurs prior to the next scheduled interval. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | C.P. Crane LLC (CP Crane) | NCR11619 | RFC2017016983 | PRC-019-2 | R1 | On February 6, 2017, CP Crane submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. CP Crane did not verify the proper coordination of its voltage regulating system controls for its two units with the applicable equipment capabilities and settings of the applicable protection system devices and functions prior to the July 1, 2016 implementation date for PRC-019-2 R1. CP Crane failed to timely perform these verifications because CP Crane misunderstood the phased-in implementation plan for PRC-019-2 R1 and did not understand whether it should consider its small 16 MW oil-fired combustion turbine unit. CP Crane has two coal-fired generating units that are powered by cyclone steam boilers and can generate up to 385 MW of electricity. It also has a 16 MW oil-fired combustion turbine that is a blackstart unit. CP Crane did not understand if it should include its third unit, the 16 MW oil-fired combustion turbine, in scope for PRC-019-2. CP Crane incorrectly believed that it should not consider its third unit in scope and that it should use the 60% implementation date of July 1, 2017 as its first implementation deadline for a single unit of a two-unit facility. Because CP Crane has three units, one of which is less than 20 MVA but is a designated blackstart unit (the oil-fired combustion turbine unit), CP Crane needed to show compliance for two of its three units by the July 1, 2016 implementation date. This noncompliance involves the management practices of information management, planning, and verification. Information management and planning are both involved because CP Crane did not effectively plan to be compliant with PRC-019-2 R1 by the implementation date. This failure to effectively plan is a root cause of this noncompliance. Verification is also involved because CP Crane did not verify that its understanding of what it needed to do to achieve compliance with PRC-019-2 was correct. This failure to verify is another contributing cause of this noncompliance. This issue started on July 1, 2016, when CP Crane was required to comply with PRC-019-2 R1 and ended on October 21, 2016, when CP Crane completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that CP Crane’s failure to properly coordinate between generator protective relays and generator voltage regulator controls and limit functions could result in generators unnecessarily tripping off-line. (Another potential risk is the interruption of one or more of the generators’ output while online at the time of an event that might lead to a device operation based on a protective device setting that is not properly coordinated with the plant capabilities.) The risk is minimized because CP Crane has not experienced any prior improper coordination between the voltage regulating system controls and its equipment capabilities and the settings of protection system devices and functions. CP Crane contributes 385 MW to the grid while operating and operated at approximately a 10% capacity factor during the noncompliance. Lastly, the results of the coordination verification activity revealed only minor adjustments were needed for complete coordination with unit capabilities which further reduces the risk. No harm is known to have occurred. ReliabilityFirst considered CP Crane’s PRC-019-2 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CP Crane completed the required verification activities for the first two of its units in August 2016, only one month late. The verification showed that the extant settings were not compliant with PRC-019-2 R1 and CP Crane made appropriate changes as recommended by its contractor for relays activated to trip the units. CP Crane made the changes to Unit 1 (overexcitation and V/Hz) on October 12, 2016 and CP Crane made the changes to Unit 2 (overexcitation only) on October 21, 2016. Going forward, CP Crane management will track the required review to ensure proper coordination is planned and verified at least every five calendar years. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | C.P. Crane LLC (CP Crane) | NCR11619 | RFC2017016984 | PRC-024-2 | R2 | On February 6, 2017, CP Crane submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R2. For two of its three units, CP Crane did not verify that the settings of its voltage relaying were activated to not trip in the “do not trip zone” prior to the July 1, 2016 implementation date for PRC-024-2 R2. CP Crane failed to timely perform these verifications because CP Crane misunderstood the phased-in implementation plan for PRC-024-2 R2 and did not understand whether it should consider its small 16 MW oil-fired combustion turbine unit. CP Crane has two coal-fired generating units that are powered by cyclone steam boilers and can generate up to 385 MW of electricity. It also has a 16 MW oil-fired combustion turbine that is a blackstart unit. CP Crane did not understand if it should include its third unit, the 16 MW oil-fired combustion turbine, in scope for PRC-024-2. CP Crane incorrectly believed that it should not consider its third unit in scope and that it should use the 60% implementation date of July 1, 2017 as its first implementation deadline for a single unit of a two-unit facility. Because CP Crane has three units, one of which is less than 20 MVA but is a designated blackstart unit (the oil-fired combustion turbine unit), CP Crane needed to show compliance for two of its three units by the July 1, 2016 implementation date. This noncompliance involves the management practices of information management, planning, and verification. Information management and planning are both involved because CP Crane did not effectively plan to be compliant with PRC-024-2 R2 by the implementation date. This failure to effectively plan is a root cause of this noncompliance. Verification is also involved because CP Crane did not verify that its understanding of what it needed to do to achieve compliance with PRC-024-2 R2 was correct. This failure to verify is another contributing cause of this noncompliance. This issue started on July 1, 2016, when CP Crane was required to comply with PRC-024-2 R2 and ended on August 1, 2016, when CP Crane completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is negative impact to the BPS due to generating units tripping on over/under frequency while within the “no trip zone”. (Another potential risk is if the frequency protective relays are not set properly, parts of or the entire plant could be deenergized for an event that should not cause such deenergization.) The risk is minimized because CP Crane has had no unit or plant trips based on incorrect settings of frequency protective relaying. CP Crane contributes 385 MW to the grid while operating and operated at approximately a 10% capacity factor during the noncompliance. Lastly, the results of the coordination verification activity revealed only minor adjustments were needed for complete coordination with unit capabilities and that the extant frequency relay settings are compliant with PRC-024-2 R2 which further reduces the risk. No harm is known to have occurred. ReliabilityFirst considered CP Crane’s PRC-024-2 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CP Crane completed the required verification activities for the two largest units in August 2016. The verification showed the extant frequency relay settings are compliant with PRC-024-2 R2 and the contractor recommended no changes. Going forward, CP Crane will review frequency device settings to ensure proper coordination as part of its ongoing protection system maintenance program to ensure settings do not change. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Forked River Power LLC (Forked River) | NCR00376 | RFC2016016306 | PRC-019-2 | R1 | On September 30, 2016, Forked River submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. Forked River failed to verify the proper condition of its voltage regulating system controls for the first of its two units by the July 1, 2016 compliance date due to an incorrect interpretation of PRC-019-2 R1. Forked River has two units, and it erroneously determined the implementation date of July 1, 2017, was its first implementation deadline, and therefore it did not need to show compliance with PRC-019-2 R1 until July 1, 2017. After the July 1, 2016 compliance deadline for PRC-019-2 R1 passed, two Regional Entities (Although Maxim Power Corp. is not a Multi-Regional Registered Entity (MRRE), it owns and operates generating facilities in the United States in the footprints of multiple Regional Entities.) informed Forked River that the first implementation date was July 1, 2016. This noncompliance involves the management practices of information management, planning, and verification. Information management and planning are both involved because Forked River staff incorrectly identified the compliance requirements of PRC-019-2. Forked River staff’s incorrect interpretation of the enforcement date for PRC-019-2 is a root cause of this noncompliance. Verification is also involved because Forked River did not verify that its interpretation of the compliance timeline for PRC-019-2 was correct. This issue started on July 1, 2016, when Forked River was required to comply with PRC-019-2 R1 and ended on September 27, 2016, when Forked River completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that Forked River could falsely trip a generator due to discoordination of voltage control. The risk is minimized because the Forked River facility operates infrequently. During the noncompliance, Forked River contributed 59 MW to the grid while operating and operated at approximately a 5% capacity factor. Further, plant documentation demonstrates that there has never been a unit trip due to incorrect coordination for any of their devices or protective relays. Lastly, the coordination study revealed that only small adjustments needed to be made to two relays to provide full protection (v/Hz and over excitation protection) for the generator and the generator step up transformer. No harm is known to have occurred. ReliabilityFirst considered Forked River’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Forked River conducted a study (of all applicable PRC-019-2 devices and equipment capabilities) which was completed on June 30, 2016. The study identified that the in-service over excitation protection for the generator and generator step up transformer does not properly protect the transformer, as the existing settings were based on typical damage curves for both the generator and transformer. In accordance with PRC-001-1(ii) R3 on September 8, 2016 Forked River contacted First Energy, Forked River’s Transmission Owner, to coordinate these changes in the Protection System. Forked River received acknowledgement from First Energy that the over excitation limiter function setting changes are acceptable and Forked River made the changes. Forked River will also take the following prevention measures: 1) going forward, Forked River management will track the required review to ensure proper coordination is planned and verified at least every five calendar years; and 2) will schedule a Preventive Maintenance activity in its maintenance management software application to conduct an annual review of this activity as part of the annual budget planning process. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | NedPower Mount Storm, LLC (NedPower) | NCR00293 | RFC2016015890 | PRC-019-2 | R1 | On July 1, 2016, NedPower submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. NedPower failed to meet the coordination requirements found in PRC-019-2 for voltage regulating system controls (including in-service limiters and protection functions) with equipment capabilities and settings of the Protection System devices and functions because NedPower failed to effectively plan to meet the July 1, 2016 compliance date. Specifically, NedPower did not perform 40 percent of the facilities coordination activities required by PRC-019 by July 1, 2016. NedPower relied on third party contractors to complete the required coordination and did not give itself enough time to hire the contractors and find dates before July 1, 2016 where the contractors had availability to come and complete the required coordination. This noncompliance involves the management practices of information management, planning, and verification. Information management and planning are involved because NedPower staff did not effectively hire and schedule contractors to timely perform the required coordination. This failure to effectively plan is a root cause of this noncompliance. Verification is also involved because NedPower did not verify that the contractors it planned on hiring could complete the required coordination on time. This issue started on July 1, 2016, when NedPower was required to comply with PRC-019-2 R1 and ended on September 1, 2016, when NedPower completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that NedPower’s failure to properly coordinate between generator protective relays and generator voltage regulator controls and limit functions could result in generators unnecessarily tripping off-line. NedPower’s maximum contribution to the grid is 264 MWs and during the noncompliance, NedPower operated at a capacity factor of approximately 16%. The risk is minimized because NedPower’s facilities are intermittent resources and each facility had demonstrated compliance with MOD-025-2, real and reactive power capability without incident. That minimizes the risk because all information on NedPower’s real and reactive power capability was up to date and accurate as of the July 1, 2016 compliance date. Lastly, after performing the coordination requirements, no changes were required. NedPower found that all protective relay functions and settings were compliant with PRC-019-2 R1 and no relay setting changes were made. No harm is known to have occurred. ReliabilityFirst considered NedPower’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, NedPower took corrective actions upon identification of the potential noncompliance which included evaluation of potential operational impacts, identification of barriers to meeting the regulatory deadline, and establishment of a more realistic timeline to complete PRC-019-2 coordination studies that included consideration of plant and external resource availability. To prevent this type of error from occurring again, NedPower put the following preventive controls in place: 1) entered the activity into an action tracking system that assigns responsibility, identifies actions, monitors status (notifications), and tracks to completion; 2) conducted a detailed evaluation of impact and actions needed based upon internal and external (contract) resource availability; and 3) established project completion dates sufficiently in advance of the enforcement dates to preclude future issues.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2017017059 | NUC-001-2.1 | R4 | On February 16, 2017, PJM submitted a Self-Report stating that, as a Transmission Operator, it had an issue of NUC-001-2.1 R4. PJM failed to incorporate into its operating analysis the Nuclear Plant Interface Requirements (NPIR) for FirstEnergy Nuclear Generation, LLC's (FE) Davis-Besse Nuclear Power Station (the DB Power Station) that required it to monitor “on any phase.” For the DB Power Station, as with all other nuclear units, PJM used B-phase measurements in order to perform energy management system state-estimation and security analysis and thus did not monitor each individual phase. Regarding the event at issue, on September 10, 2016, the DB Power Station unit tripped offline. Following the trip, the A-phase voltages of the station’s J and K 345 kV buses dropped below the NPIR emergency low voltage requirement (i.e., 339.1 kV) for approximately two hours and thirty minutes. However, because the PJM tools used to monitor DB Power Station’s bus voltages only monitored the B-phase voltages, PJM was not aware that the A-phase voltages dropped until FE transmission notified PJM during the event. At all times, the voltages were still above the PJM baseline voltage limit (i.e., SOL) of 327.8 kV. FE transmission notified DB Power Station that it was exceeding the emergency low voltage limit per the NPIR. This notification prompted DB Power Station to initiate its Degraded Grid Procedure, which would allow DB Power Station to safely shut down the plant if necessary. In accordance with this procedure, DB Power Station started its emergency diesel generators. FE transmission also communicated a request for voltage support to PJM, and PJM initiated voltage support controls and inquired through FE transmission whether DB Power Station would authorize off-cost generation to operate to the NPIR emergency low voltage limit consistent with procedures defined in PJM Manual 03, Section 3.4. An authorization for off-cost generation was not granted by DB Power Station and PJM did not schedule additional generation for reactive control since voltages were still above PJM baseline voltage limit (i.e., SOL) of 327.8 kV. Within about two hours and thirty minutes, as a result of diminishing area loads and diminishing transfers, the A-phase voltages on the DB Power Station 345 kV buses improved until they were above the NPIR emergency low voltage limit. Although PJM did not specifically monitor the DB Power Station A-phase voltage, FE transmission and the DB Power Station were both able to, and did, monitor the A-phase voltage on an actual basis at the time of the event, consistent with requirements contained within Manual M03, Section 3.4, of PJM’s transmission operations manual and the DB Power Station NPIR, ensuring the notification requirement within the NPIR was satisfied. As a result of the event, on November 22, 2016, PJM began monitoring the individual phases, allowing PJM to alert DB Power Station if any of the phases drop below the acceptable levels in the NPIR. The root cause related to lack of verification controls to ensure that PJM operations complied with the NPIR. This issue started on June 12, 2015, the effective date of the NPIR, and ended on November 22, 2016, when PJM began monitoring individual phases for the DB Power Station. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. In a low voltage situation such as the one that occurred here, the most likely risk to the system is that the low voltage would cause generation to unexpectedly trip offline. However, that risk was not present here because the generating unit tripped offline prior to the event. And, throughout the event, at the Bulk Electric System level, there was not a low voltage situation because voltages were above the PJM baseline voltage limit. The other potential risk relates to safety concerns at the power station as a result of the low voltage. However, FE transmission and the DB Power Station were both able to, and did, monitor the A-phase voltage on an actual basis at the time of the event, ensuring the notification requirement within the NPIR was satisfied to ensure that DB Power Station initiated its Degraded Grid Procedure, which would have allowed the station to safely shut down if necessary. Additionally, DB Power Station noted that that the 345 kV voltage limits documented in the DB Power Station NPIR are a surrogate for the more restrictive 4.16 kV and 480 V internal safety bus voltage limits, which were never exceeded during the event, and never triggered more limiting conditions of operations for the plant. No harm is known to have occurred. ReliabilityFirst considered PJM’s NUC-001 R4 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PJM: 1) began monitoring all three phases, which is in line with the revised NPIR for actual voltage monitoring. PJM also monitors B-phase on a contingency basis; and 2) completed revisions to the DB Power Station NPIR that removed the “on any phase” language from the voltage limits section where it was applicable to both actual and contingency voltage limits. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Potomac Electric Power Company (Pepco) | NCR00881 | RFC2017017972 | EOP-004-2 | R3 | On February 1, 2017, Pepco submitted a self-log stating that, as a Transmission Owner, it had an issue of EOP-004-2 R3. On January 5, 2017, Pepco determined that it had a potential issue involving EOP-004-2 R3 regarding the annual validation of its operating plan contacts. The potential issue was identified while the business area was performing a review of all its system operations procedures to ensure roles and responsibilities were properly assigned. It was at this time the EOP-004-2 R1 procedure was reassigned due to a voluntary termination of the former assignee in December. Given his new role and past familiarity with the standard, the assigned individual immediately undertook efforts to validate the contacts listed in the operating plan. A review of evidence identified that the contacts were not validated in 2016 prior to the departure of the previous assignee. A validation on the contact list was initiated and completed the following day on January 6, 2017. The validation found that all numbers were active and connected with the intended contact; however, two of the numbers were changed to reflect internal changes to personnel. The contacts were immediately validated and updates were made, as necessary, to the operating plan. This noncompliance involves the management practice of validation as Pepco failed to validate the contacts listed in the operating plan. The change in personnel responsible for validating the contacts listed in the operating plan is a root cause of this noncompliance. This issue started on January 1, 2017, when Pepco failed to validate the contacts listed in the operating plan and ended on January 6, 2017 when Pepco completed validating the contacts listed in the operating plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Risk-Harm assessment determined that the risk to the BPS was minimal. Validation of operating plan contacts could have a potential impact to the restoration or communication of an event, but would not be a direct cause. Additionally, through the course of day-to-day business, most of the listed contacts were called during the 2016 calendar year. Of the 19 contacts listed in the Operating Plan, Pepco was in contact with 79% of those listed, many on a frequent basis, throughout 2016. Validation of the contact list was initiated and completed shortly after the possible non-compliance began, and the validation found that all numbers were active and connected with the intended contact; however, two of the numbers were changed to reflect internal changes of personnel. No harm is known to have occurred. | To mitigate this issue, Pepco: 1) performed a validation of its Operating Plan contacts and made the necessary updates to the contact list and 2) created a recurring evidence schedule in Pepco’s Compliance Tracking System as a control to ensure the annual requirement of contact validation will not be overlooked in the future.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PSEG Nuclear LLC (PSEG Nuclear) | NCR00895 | RFC2017017245 | MOD-025-2 | R1 | On March 9, 2017, PSEG Nuclear submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. During a PSEG Nuclear standard implementation review for MOD-025-2, PSEG Nuclear discovered that they failed to submit a MOD-025-2 Attachment 2 Real Power Testing Form or equivalent to PJM, the Transmission Planner, within 90 days of a staged test for Salem Unit 2 and Hope Creek Generation. MOD-025-2 required that PSEG Nuclear complete verification on the initial 40% of its units by July 1, 2016. PSEG Nuclear provides annual PJM Manual 21 Summer Real Power Net Capability test data to PJM every year. This information is summarized for the annual MOD-010 submittals. Neither of these data packages is equivalent to the MOD-025-2 attachment and cannot be used to show compliance with MOD-025-2. PSEG Nuclear, however, misinterpreted the MOD-025-2 requirements and attempted to report the MOD-010 packages to satisfy compliance with MOD-025-2 and the MOD-010 data packages do not satisfy MOD-025-2. Therefore, PSEG Nuclear failed to submit the proper testing information by the July 1, 2016 deadline. This noncompliance involves the management practice of information management, planning, and verification. Information management and planning are involved because PSEG Nuclear’s compliance staff misunderstood how to show compliance with MO-025-2. That misunderstanding is a root cause of the noncompliance. Verification is also involved because PSEG Nuclear did not verify that the MOD-010 data packages were sufficient to show compliance with MOD-025-2. That failure to verify is another contributing cause of the noncompliance. This issue started on July 1, 2016, when PSEG Nuclear was required to comply with MOD-025-2 R1 and ended on June 13, 2017, when PSEG Nuclear completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that failing to timely provide data regarding generating capacity could lead to inaccurate information in the generating models and that could lead to a loss of generation. The risk is minimized because Hope Creek and Salem Unit 2 both passed the equivalent annual PJM Summer Real Power Net Capability testing that PSEG Nuclear submitted to PJM in accordance with PJM Manual 21. This testing provides reasonable assurance that the units are capable of providing their rated Real Power output which makes it more likely that the existing data in the generating models for PSEG Nuclear is accurate. No harm is known to have occurred. ReliabilityFirst considered PSEG Nuclear’s MOD-025 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PSEG Nuclear: 1) submitted to PJM MOD-025-2 Attachment 2 Staged Real Power Verification form for Hope Creek and Salem Unit 2, using the plant data from the following Reactive testing dates: Hope Creek Generating Station (May 16, 2015); Salem Generating Station Unit 2 (June 22, 2016); 2) revised procedure ER-AA-510-2001, PJM Capability Demonstration, to reflect NERC Standard MOD-025-2 submittal requirements and the content of PJM Compliance Bulletin 23; and 3) revised the Hope Creek, Salem 1 and Salem 2 Periodic Maintenance tasks to schedule and perform future Real Power Tests concurrently with the next scheduled Reactive Power Tests. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Red Oak Power, LLC (Red Oak Power) | NCR00665 | RFC2017017153 | PRC-019-2 | R1 | On February 28, 2017, Red Oak Power submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. Red Oak Power contracts with the vendor Cogrentrix Energy Power Management to perform asset management and to support its NERC Compliance program. Cogentrix did not correctly calculate the 40% implementation period from the FERC approval date of PRC-019-2. The miscalculation by Cogentrix and ultimately, Red Oak Power, led Red Oak Power to incorrectly determine that the first implementation period threshold of 40% would become effective July 1, 2017 instead of July 1, 2016. Once Red Oak Power realized they had miscalculated the date, they evaluated MOD-025 data collected prior to July 1, 2016, with the assumption that the testing and physical verification of all of its generator voltage regulating equipment settings relative to its protective system settings would be sufficient to demonstrate PRC-019-2 compliance. However, Red Oak Power’s internal audit determined that this assumption was incorrect. This noncompliance involves the management practice of external interdependencies, information management, and planning. External interdependencies is involved because Red Oak Power relied on Cogentrix to verify that the Red Oak Power plant would be compliant with NERC standards. Information management and planning are involved because Red Oak Power’s compliance staff failed to identify what it needed to complete to achieve compliance with PRC-019-2 on July 1, 2016. This ineffective planning is a root cause of the noncompliance with PRC-019-2. This issue started on July 1, 2016, when Red Oak Power was required to comply with PRC-019-2 R1 and ended on June 6, 2017, when Red Oak Power completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that Red Oak Power’s failure to properly coordinate between generator protective relays and generator voltage regulator controls and limit functions could result in generators unnecessarily tripping off-line. The risk is minimized because Red Oak Power has never experienced a trip or loss of a generator unit during MOD-025 tests or as a result of system conditions. Lastly, after performing the coordination requirements, Red Oak Power found that all protective relay functions were compliant and made only minor relay setting changes. No harm is known to have occurred. ReliabilityFirst considered Red Oak Power’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Red Oak Power: 1) created a notification in the form of a recurring Preventive Maintenance work order or as an obligation that escalates until completed in the Company Obligation Tracking System or Gensuite application for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable standards incorporating the NERC initial notification of confirmation of the implementation or due date(s). In addition, Red Oak Power created a tracking spreadsheet to monitor compliance deadlines and status for responsible parties and the Corporate Reliability Standards Compliance Group will coordinate all new or modified standards with the necessary engineering groups within the Cogentrix organization, to include, but not limited to, submittal of verification to the region (RF) to ensure the understanding of all aspects of the Reliability Standard including Requirements, Implementation Plans and schedules, as necessary. The objective is to ensure a complete implementation strategy will be developed to convey acceptable approaches with clear understanding, responsibilities, and timelines; 2) created a tracking spreadsheet to monitor compliance deadlines and status for responsible parties; and 3) reviewed the Kestrel report and updated the Limiter/Protective relays as necessary. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Red Oak Power, LLC (Red Oak Power) | NCR00665 | RFC2016016312 | PRC-024-2 | R1 | On September 30, 2016, Red Oak Power submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. Red Oak Power’s power generation facility consists of three combustion turbine generators (CTG) and one steam turbine generator (STG). Each of these generators have two multi-function relays which utilize eight applicable relay functions. On each of the CTG relays, one of the eight settings was not in compliance with PRC-024-2. Specifically, the time delay setting was shorter than the calculation in the Standard for each CTG relay, and thus not in compliance with PRC-024-2 requirements as of July 1, 2016. The STG time delay setting on one relay was shorter than the calculation in the standard and the over frequency protection function for the other relay was also not in compliance. Red Oak Power did not discover that these relays were not in compliance until August 25, 2016, when Cogentrix personnel completed their evaluation of on-site protection. This noncompliance involves the management practice of external interdependencies and asset and configuration management. External interdependencies is involved because Red Oak Power relied on Cogentrix to verify that the Red Oak Power plant would be compliant with NERC standards. Asset and configuration management is involved because Red Oak Power compliance staff did not ensure that all settings on all applicable relays were in compliance with PRC-024-2. This failure to keep track of all of the settings on all of the applicable relays is a root cause of this noncompliance. This issue started on July 1, 2016, when Red Oak Power was required to comply with PRC-024-2 R1 ended on October 25, 2016, when Red Oak Power completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is negative impact to the BPS due to generating units tripping on over/under frequency while within the “no trip zone”. The risk is minimized because Red Oak Power’s generators have not tripped due to the current relay settings. The probability of the frequency being in the “no trip zone” during the duration of the noncompliance is small which helps reduce the risk. Further, Red Oak Power’s verification showed that the extant voltage relay settings are compliant with PRC-024-2 R1 and no changes were required. No harm is known to have occurred. ReliabilityFirst considered Red Oak Power’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Red Oak Power scheduled the required relay setting changes to be implemented during the next scheduled outage, targeted for October 17, 2016. Red Oak Power had a planned facility outage on October 17, 2016 and all relay settings were changed to make 100% of Red Oak Power's units compliant with PRC-024-2.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Twin Ridges Wind Farm (Twin Ridges) | NCR11280 | RFC2016016477 | MOD-025-2 | R2 | On October 27, 2016, Twin Ridges submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. Twin Ridges’ staff misinterpreted MOD-025-2 R1 to the extent that they believed that Generator Real and Reactive Power Capability modeling data would satisfy MOD-025-2. Twin Ridges later discovered that modeling data does not meet the requirements of MOD-025-2 and Twin Ridges did not make this discovery until October 3, 2016, months following the July 1, 2016 deadline. The Site Manager for Twin Ridges discovered this potential noncompliance during a periodic review of the current NERC standards. This noncompliance involves the management practices of information management, planning, and verification. Information management is involved because Twin Ridges’ staff misunderstood the requirements of MOD-025-2. Twin Ridges’ staff incorrectly believed they could use modeling data to comply with MOD-025-2. This misinterpretation is a root cause of this noncompliance. Verification is involved because Twin Ridges did not verify that the Generator Real and Reactive Power Capability modeling data would satisfy MOD-025-2. This issue started on July 1, 2016, when Twin Ridges was required to comply with MOD-025-2 R2 and ended on November 22, 2016, when Twin Ridges completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is that by providing incorrect data regarding generating capacity, the veracity of generating models and power flow analyses for planning and operations would be affected. Having incorrect data in generating models and power flow analyses would lead to faulty conclusions based off of that incorrect data. The risk is minimized because Twin Ridges is required to perform Megawatt (MW) testing as an entity within the PJM market. This MW testing helps provide a correct model of Twin Ridges’ generation capacity to PJM and other market participants. The risk is further minimized because the entity submitted Generator Real and Reactive Power Capability modeling data in December 2011, and no changes have been made since 2011 which would require an update to the model. No harm is known to have occurred. ReliabilityFirst considered Twin Ridges’ MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Twin Ridges: 1) worked with the Balancing Authority and Transmission Planner to schedule the testing; and 2) created a work order in Twin Ridges’ Computerized Maintenance Management System to ensure model validation testing occurs prior to the next scheduled interval. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Whiting Clean Energy, Inc. (Whiting) | NCR00417 | RFC2016016449 | PRC-019-2 | R1 | On October 24, 2016, Whiting submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. Whiting contracted with Kestrel Power Engineering (Kestrel) to evaluate the coordination of the protection system and excitation limit per PRC-019 requirements. Kestrel determined that the V/Hz limiter and Digital Generator Protection (DGP) relay settings did not meet PRC-019 requirements. In order to meet the requirements Whiting needed to put the V/Hz limiter on a lower setting than the generator trip scheme. Whiting received the aforementioned recommendation from Kestrel on June 25, 2016, just five days before the July 1, 2016, deadline for PRC-019. Kestrel then proceeded to consult with the generator manufacturer and an engineering firm to determine whether the change should be made to the excitation limiter or the generator protection relay. This led to a coordination study to consider the impact of changing the settings. By the time the coordination study was completed, the July 1, 2016 compliance deadline had already passed. This noncompliance involves the management practice of information management, planning, and verification. Information management and planning are involved because Whiting staff did not properly identify the coordination adjustments necessary to comply with PRC-019-2 in a timely manner. Whiting staff did not give themselves enough time to show compliance with PRC-019-2 as of July 1, 2016 and that failure to plan is a root cause of the noncompliance. Verification is also involved because Whiting staff did not verify with Kestrel that Kestrel could complete all the work that needed to be done to show compliance by July 1, 2016. This issue started on July 1, 2016, when Whiting was required to comply with PRC-019-2 R1 and ended on October 13, 2016, when Whiting completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this instance of noncompliance is that the miscoordination of the limiter settings could have caused a misoperation that could have tripped the generators whose total output exceeds 500 MW. The risk is minimized because the Whiting generating facility has not been declared an asset critical to the reliability of the BPS by NIPSCO, the Transmission Operator and MISO, the Reliability Coordinator. Whiting also contributes 525 MW to the grid while operating and operated at approximately a 56% capacity factor during the noncompliance. When Whiting performed the coordination of the protection system and excitation limit per PRC-019 requirements, the changes it made were minimal. When Whiting performed the verification, only minor changes were required. (Whiting changed the excitation limiter setting on generators GT2 and the STG to coordinate with the associated Digital Generator Protection (DGP) Relay trip setting. The excitation limit setting on these generators was changed from 110% to 109% so the excitation limit could be reached prior to reaching the DGP V/HZ trip setting of 110%.) The generators would have had to have operated near the exciter maximum limits in order for the relaying to trip the unit off‐line. Lastly, there was no actual impact to the BPS. No harm is known to have occurred. ReliabilityFirst considered Whiting’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Whiting changed the excitation limiter setting on generators GT2 and the STG to coordinate with the associated Digital Generator Protection (DGP) Relay trip setting. The excitation limit setting on these generators was changed from 110% to 109% so the excitation limit could be reached prior to reaching the DGP V/HZ trip setting of 110%. To help prevent recurrence, Whiting: 1) improved an existing internal control regarding vendor management. Whiting has a contract with a NERC Consultant and that NERC Consultant provides quarterly reports to Whiting that describe newly approved Standards and the status of new or changed Standards in the NERC development queue; 2) has established weekly conferences and quarterly face-to-face meetings between the NERC Consultant, Whiting Compliance staff, and Whiting Subject Matter Experts. This internal control is used to identify enforcement dates of new or changed Standards and to track them on a multi-year schedule to allow for early identification of implementation milestone dates. The weekly meetings will also serve as a communication bridge for any future personnel turn-over; and 3) hired a dedicated person specifically for NERC compliance, who attends RF and NERC related workshops, conference calls, training, etc. ReliabilityFirst has verified the completion of all mitigation activity.
2017-09-28 | SERC Reliability Corporation (SERC) | Effingham County Power, LLC (Effingham) | NCR11597 | SERC2016016284 | PRC-024-2 | R2 | On September 29, 2016, Effingham submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R2. Effingham did not complete trip setting verification for at least 40% of its generating units in accordance with the PRC-024-2 implementation plan by July 1, 2016. Effingham incorrectly believed that the implementation schedule required that 40% of all relay functionality be compliant, as opposed to 40% of all units. On or about August 25, 2016, Effingham identified its misinterpretation of the implementation schedule and thus its noncompliance while reviewing the PRC-024-2 Reliability Standard Audit Worksheet. Effingham consists of two combustion turbine generators and one steam turbine generator, each of which have two relays, or six total relays. Effingham did not set the undervoltage protection functions for one channel of each of the relays such that they would not trip the generating units within the “no trip zone” of PRC-024 Attachment 2 by July 1, 2016. Effingham determined that the main cause of the issue was its misinterpretation of the PRC-024-2 NERC Implementation Plan. This issue started on July 1, 2016, when Effingham did not meet the implementation schedule, and ended on September 8, 2016, when Effingham changed the relay settings to meet the “no trip zone” requirement for at least 40% of its generating units. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Effingham’s failure to verify that the voltage relays are set to not trip in the “no trip zone” could allow a generator to trip incorrectly for a system event. However, the Effingham Facility consists of three generators with total output capacity of 595 MWs in the Southern Company Balancing Area. Since the largest of the three individual units involved was 199 MWs, they should have a minimal impact if any tripped offline. At the time of noncompliance, all undervoltage relay settings were 0.90 pu with a one second delay. Effingham changed the settings to 0.89 pu with a three second delay to be compliant. Effingham reported that there were no unit trips based on incorrect voltage relay settings. Effingham operates at a 40% capacity factor. No harm is known to have occurred. SERC considered Effingham’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Effingham: 1) changed the relay settings to meet the “no trip zone” requirement for at least 40% of its generating units; 2) created a notification in the form of a recurring preventive maintenance work order or as an obligation that escalates until completed in the Effingham tracking system for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable Standards incorporating the NERC initial notification of confirmation of the implementation or due date(s); and 3) created a tracking spreadsheet to monitor compliance deadlines and status for responsible parties. The corporate reliability standards compliance group will coordinate all new or modified standards with the necessary engineering groups within the Cogentrix organization, to include, but not limited to submittal of verification to the region (SERC) to ensure the understanding of all aspects of the Reliability Standard including requirements, implementation plans, and schedules, as necessary. The objective is to ensure Effingham develops a complete implementation strategy to convey acceptable approaches with clear understanding, responsibilities, and timelines.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2016016084 | TOP-006-2 | R1; R1.1 | On September 1, 2016, AECC submitted a Self-Report stating that, as a Generator Operator, it had an issue of noncompliance with TOP-006-2 R1. On July 26, 2016, at 5:23 p.m. Unit 6 at AECC's Oswald Generating Station tripped offline. The Senior Operator on duty at the time did not notify the Balancing Authority (BA) and Transmission Operator (TOP) of the unit forced outage. AECC’s operating procedures require the Senior Operator on duty to notify the BA and TOP of unit outages. On July 27, 2016 at 5:45 a.m. the Senior Operator on duty notified the BA and TOP of the outage. The duration of this instance of noncompliance was from July 26, 2016, at 5:23 p.m. when Unit 6 tripped offline, through July 27, 2016, at 5:45 a.m., when the Senior Operator contacted the BA and TOP informing them of a change in the availability of AECC’s generation resources. The root cause of this instance of noncompliance was a combination of human error and lack of internal controls to ensure AECC operating procedures are followed. The Senior Operator on duty at the time of the outage failed to follow AECC’s operating procedures, which require operators to notify the BA and TOP when there is a plant outage or a situation which limits plant output. In addition, AECC did not have internal processes and procedures in place to confirm the BA and TOP are notified when there is a change in available generation resources. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to notify the BA and TOP of unit outages has the potential to affect the reliability of the BPS because the BA and TOP will not have situational awareness of the availability of generation resources to respond to system voltage and/or frequency events. Notwithstanding, AECC’s Oswald Plant had nine other units operating when the outage occurred. Additionally, Unit 6 at Oswald Generating Station has a capacity of less than 50MW, which has minimal impact on the BPS. No harm is known to have occurred. AECC has no relevant prior violations for TOP-006-2 R1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, AECC: 1) retrained the Senior Operator who was on duty when the outage occurred on AECC’s operating procedures; 2) required all Senior Operators to sign a Memo of Understanding about reporting outages and limitations to the BA and TOP; 3) revised its operating procedures to require Market Operators to validate that notification is given the BA and TOP when they become aware of events that alter the capability of a plant; and, 4) trained Senior Operators on the new operating procedures. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Dempsey Ridge Wind Farm, LLC (DRWF) | NCR11179 | SPP2017017485 | VAR-002-4 | R1 | On May 1, 2017, DRWF submitted a Self-Certification stating that, as a Generator Operator, it had an issue of noncompliance with VAR-002-4 R1. On February 3, 2017, at 5:32 p.m., the DRWF Master Control Board (MCB) experienced a communication trip on both Power Module Enclosures, causing the DRWF dynamic VAR compensator, i.e., automatic voltage regulator, (AVR) to fault out of service and unable to control voltage. Because the operators at DRWF’s System Operation Center (SOC) incorrectly believed one of the data points related to the DRWF voltage controller was an indication of AVR status and the AVR status had not been properly integrated into DRWF’s Supervisory Control and Data Acquisition (SCADA) system, SOC operators were unaware that the AVR was out of services and did not notify the Transmission Operator of the status change. In addition, DRWF did not have an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the TOP. As a result, DRWF exceeded its voltage schedule 3.1% of the time the AVR was out of service. On March 08, 2017, at 1:47 p.m., the SOC operators determined the voltage regulator was not in service and reset the AVR to control voltage to the voltage schedule. The duration of this instance of noncompliance was from February 03, 2017, at 5:32 p.m., when a communications trip caused the AVR to fault out of service, to March 08, 2017, at 1:47 p.m., when the AVR was placed in service. The root cause of this instance of noncompliance was human error. Because the SOC operators incorrectly assumed the voltage controller data point was an indication of AVR status and the AVR status had not been properly integrated into DRWF’s SCADA system the SOC operators were not aware the AVR was out of service and did not notify the TOP of the status change. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). DRWF is a 132 MW intermittent wind generation resource with a voltage schedule of 235.98 kV ± 1.0%. For the 33 days DRWF’s AVR was out of service, the highest voltage level was 239.6 kV, only 1.2 kV greater than the scheduled voltage. Additionally, DRWF’s TOP did not contact DRWF regarding its voltage schedule or call upon DRWF to change its voltage level. No harm is known to have occurred as a consequence of the AVR outage. DRWF has no relevant prior violations for VAR-002-4 R1 or any similar standards. | To mitigate this minimal risk instance of noncompliance, DRWF: 1) implemented an hourly shift check of the DRWF MCB status. This began on March 09, 2017 as a temporary action until a more robust mitigation could occur. 2) implemented two alarms in their asset monitoring tool as follows: a. An alarm to notify the SOC when the reactive power command to the wind turbine generator is 0kvar for more than 10 minutes. b. An alarm to notify the SOC when the Dynamic VAR Compensator’s MCB is not in the status of “RUN”. 3) integrated the dynamic VAR compensator MCB status (Run/Off) into their SCADA system for DRWF’s voltage control to make operators aware of the AVR status. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Dogwood Power Management, LLC (Dogwood) | NCR11250 | SPP2016016272 | PRC-019-2 | R1; R1.1 | On September 30, 2016, Dogwood submitted a Self-Certification stating that, as a Generator Owner, it had an issue of noncompliance with PRC-019-2 R1. In its Self-Certification, Dogwood stated that it had determined that it lacked an all-encompassing document to illustrate the coordination between its in-service limiters and protective functions at the Dogwood Energy Facility. Dogwood stated that it had relied upon the commissioning and tuning reports for the Automatic Voltage Regulators (AVR) and Power System Stabilizers (PSS) which were installed at the Dogwood Energy Facility in October 2014, to document its compliance with PRC-019-2 R1. The operation of the overexcitation, underexcitation, and volts per hertz limiters for Combustion Turbine 1 (CT1), Combustion Turbine 2 (CT2), and Steam Turbine 1 (ST1) at the Dogwood Energy Facility were verified during the AVR commissioning. The protective relays for CT1, CT2 and ST1 were last tested in February 2012. Dogwood determined the commissioning and tuning reports it provided its Transmission Planner on November 5, 2014, did not adequately verify that the in-service limiters were set to operate before the generator protection systems (R1.1.1) or that protection system devices were set to properly protect the Dogwood Energy Facility generators (R1.1.2). The duration of this instance of noncompliance was from July 1, 2016, the date the implementation plan for PRC-019-2 required verification of the coordination of the in-service limiters and protection system devices for 40 percent of applicable facilities, through October 31, 2016, the date Dogwood received from its consultant's verification of the coordination of the in-service limiters and protection system devices for CT1, CT2 and ST1. Dogwood determined the root cause of this instance of noncompliance was that its existing procedures did not incorporate a review by its NERC Compliance Manager of the evidence demonstrating compliance with new or revised NERC Standards. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly coordinate exciter limiters and generator protection relays can cause the generator AVR to impose unacceptable operating conditions on the generator. Such conditions, i.e. overexcitation and underexcitation, have the potential to affect the reliability of the BPS by decreasing the generator’s ability to withstand system voltage events and increasing the probability of generator trips due to loss of synchronism and generator field overloads. The risk of this noncompliance is mitigated because Dogwood verified the operation of its in-service limiters in October 2014 and tested its generator protection relays in February 2012. Dogwood confirmed its in-service limiters and protection system devices were set properly and no changes were required to mitigate its noncompliance with PRC-019-2 R1. No actual harm is known to have occurred as a result of this noncompliance. Dogwood has no relevant prior violation of PRC-019-2 R1 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, Dogwood: 1) verified the coordination of its in-service limiters and protection system devices, creating a report containing a graphic depiction of the coordination between the AVR/PSS settings/limiters and the generator protection relays; 2) revised procedures for compliance with PRC-019-2 to require responsible personnel to prepare (or arrange to have prepared) a graphic depiction of coordination; 3) augmented its standard review program to require that its NERC Compliance Manager review all updated procedures and testing prepared by the respective subject-matter experts to ensure that such procedures and testing programs fully satisfy the NERC standard at issue; 4) trained its subject matter experts and their supervisors on procedures to be following for the implementation of new and revised applicable NERC standards. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Eastman Cogeneration Limited Partnership (Eastman) | NCR01092 | SPP2016015922 | PRC-024-2 | R1 | On July 21, 2016, Eastman submitted a Self-Report stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Eastman is a cogenerating facility consisting of two, 170 MW gas turbines and one, 128 MW steam turbine applicable to PRC-024-2 R1. Eastman did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through August 30, 2016, the date Eastman verified its underfrequency relays were set in accordance with PRC-024-2 Attachment 1. The root cause of this instance of noncompliance was a combination of Eastman’s lack of understanding of the new standard and requirement and a lack of managerial oversight ensuring adherence to the standard and requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relays in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Eastman Chemical manufacturing facility consumes 200 MWs of the available generation from its cogeneration facility, leaving only 268 MW going to the bulk electric system. The generators are controlled by plant operators who monitor system frequency regularly. Additionally, Eastman attested that this generation facility has operated without experiencing any frequency, excitation system, or PRC-024 related issues since its 2001 commissioning date. Eastman verified that no changes were required to its protective relay settings. No harm is known to have occurred. SPP RE reviewed Eastman’s violation history and determined that Eastman has no prior instances of noncompliance with PRC-024-2. | To mitigate this issue, Eastman completed the following mitigation activities: 1) conducted a verification to determine if the relay settings currently in place were compliant with PRC-024-2 R1; and 2) revised its NERC Reliability Compliance Policy to require NERC standard implementation dates be reviewed quarterly instead of annually, and undergo at least two levels of management review. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Origin Wind Energy, LLC (ORGNWE) | NCR11496 | SPP2016015957 | VAR-002-4 | R1 | On July 28, 2016, ORGNWE submitted a Self-Certification stating that, as a Generation Operator, it had an issue of noncompliance with VAR-002-4 R1. On June 21, 2016, ORGNWE performed a routine inspection of its Supervisory Control and Data Acquisition (SCADA) system and discovered that its generation facility had not been operating in automatic voltage control mode since routine substation maintenance conducted on June 15, 2016 inadvertently caused the Automatic Voltage Regulator (AVR) to be disabled. ORGNWE reactivated the AVR and restored operation to automatic voltage control mode on June 21, 2016. Because the operators were unaware that the AVR was out of service, ORGNWE did not inform the Transmission Operator (TOP) of the status change. The duration of this instance of noncompliance was from June 15, 2016, when the AVR was disabled and the TOP was not notified, through June 21, 2016, the date ORGNWE reactivated the AVR and restored operation to automatic voltage control mode. The root cause of this instance of noncompliance was human error. Because the Uninterruptable Power Supply (UPS) for the collector substation equipment was installed incorrectly, when the substation equipment was de-energized during routine substation maintenance conducted on June 15, 2017, the AVR was disabled because there was no alternative power source. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with VAR-002-4 R1 has the potential to affect the reliability of the BPS by preventing a generating facility from responding to system voltage excursions, which could limit the TOP’s ability to respond to system voltage problems. ORGNWE’s voltage set point was maintained during the outage because the plant excitation system defaults to Power Factor Mode of operation, which maintains a Power Factor of 1.0 thus maintaining the terminal voltage equal to the system voltage even when the generators are not operating in automatic voltage control mode. Therefore, ORGNWE’s generation facility did not deviate from the voltage schedule, and no system voltage excursions occurred requiring response from either ORGNWE or its TOP. ORGNWE consists of 75 2.0 MW wind turbines with minimal impact on the BPS. No harm is known to have occurred. ORGNWE has no relevant prior violations for VAR-002-4 R1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, ORGNWE: 1) trained applicable staff on how and when to inspect the Power Plant Controller operation; 2) verified that UPS’s were installed correctly on existing and new projects; 3) connected an alternative power source to the Programmable Logic Controller to ensure backup power supply during maintenance periods; 4) issued a temporary operating memo detailing procedures for planned and unplanned outages for use during drafting of a new Standard Operating Procedure; and, 5) published a new Standard Operating Procedure for planned and unplanned outages. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Southwestern Power Administration (SPA) | NCR01144 | SPP2017017424 | MOD-026-1 | R6 | On April 17, 2017, SPA submitted a Self-Report stating that, as a Transmission Planner, it had an issue of noncompliance with MOD-026-1 R6 because it failed to provide a written response to the Generator Owner (GO) within 90 calendar days of receiving generator excitation control system or plant volt/var control function model (control system model) information that the model is usable or not usable. SPA received control system model from one GO on August 1, 2016, and from a different GO on September 30, 2016. SPA should have provided a written response to the GOs about the models by October 31, 2016, and December 29, 2016, respectively. However, SPA did not provide either GO a written response. The duration of this instance of noncompliance was from October 31, 2016, the date SPA should have provided the first GO with a written response stating if the models provided were usable, through April 27, 2017, the date SPA provided a written response to the two GOs stating whether or not the models were usable. The root cause of this instance of noncompliance was a combination of inadequate preventative or detective controls in SPA’s new Modeling, Data and Analysis process and lack of employee awareness of the newly implemented MOD-026-1 process. The model information from the GOs only went to one SPA employee and internal controls, i.e. additional reviews by other SPA employees, were not in place to ensure the employee responsible provided a written response to the GO within 90 calendar days. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to notify the GO that the models submitted are usable or not usable creates the potential that the results of dynamic simulations of generator performance would not accurately represent the response of the generator excitation control system or plant volt/var control function to system events. This could result in an inaccurate assessment of dynamic reliability issues and the development of inaccurate corrective action plans to address such issues. Notwithstanding, the actual risk was minimal. The SPA system dynamic models have been performing accurately with the previous generator model information that is based on engineering judgement and manufacturers’ data. Additionally, the model data provided did not result in a material change to the dynamic simulations performed by SPA. No harm is known to have occurred. SPA has no relevant prior violations of MOD-026-1 R6 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, SPA: 1) provided a written response to the two GOs stating whether or not the models provided were usable; 2) created an email distribution group that consists of several engineers within the SPA planning division that will receive the models provided by the GOs for review and response; and 3) implemented internal controls such as peer reviews and hiring an additional engineer to ensure models submitted by GOs are reviewed and a response is provided within 90 calendar days. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Sunflower Electric Power Corporation (SECI) | NCR01148 | SPP2017017279 | PRC-023-1 | R1; R1.1 | On March 23, 2017, SECI submitted a Self-Report stating that, as a Transmission Owner, it had an issue of noncompliance with PRC-023-1 R1.1 because SECI failed to set one transmission line relay that protects SECI’s neighboring entity’s Holcomb to Finney County 345kV transmission line so it would not operate at or below 150% of the highest seasonal Facility Rating. The duration of this instance of noncompliance was from July 1, 2010, the date the standard became mandatory and enforceable, through July 28, 2016, the date SECI reset the transmission line relay so that it did not operate at or below 150% of the highest seasonal Facility Rating. The root cause of this instance of noncompliance was human error. This noncompliance occurred because of a misunderstanding regarding the demarcation point in compliance obligations between SECI and the neighbor who owned the transmission line. SECI believed that the owner of the transmission line had compliance responsibility for the relay settings because the owner dictates the relay settings required to protect the transmission line. As a result, SECI did not include the relay on its PRC-023 list and it was not evaluated for proper settings. In July 2016, corrective settings were communicated to SECI by the owner of the transmission line after they identified the issue while performing an internal review. In March 2017, during its internal PRC-023 review process, SECI identified that is was responsible for the relay setting and that the setting was incorrect. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Setting protective relays below 150% of the transmission line Facility Ratings creates the potential for the load impedance of heavily loaded transmission lines to cause distance relays to trip when no real fault exists. Notwithstanding, SECI’s noncompliance was limited to Zone 4 of the Holcomb to Finney County 345kV transmission line relay, which was set at 125% of its highest seasonal rating or 1191 MVA. For the duration of noncompliance, the load on the Holcomb to Finney County transmission line has remained well below the 1191 MVA set point, not exceeding 804 MVA. No harm is known to have occurred. SECI has no relevant prior violations of PRC-023-1 R1.1 or any other standards that are similar in nature. | To mitigate this minimal risk instance of noncompliance, SECI: 1) added the protective relay to SECI’s PRC-023 list; 2) corrected the relay setting; 3) reviewed all SECI relays applicable to PRC-023; 4) revised SECI’s Operating Procedure to add clarity of what owner is responsible for monitoring relay settings; and, 5) provided reinforcement training to SECI staff on the Operating Procedure and the PRC-023 ratings. SPP RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 2, LLC (SW2) | NCR04132 | TRE2017016949 | PRC-019-2 | R1 | On February 7, 2017, SW2 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, SW2 did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its single generation Facility by July 1, 2016 as required. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW2 personnel discovered that SW2 had not performed the required voltage coordination verification activities for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW2 personnel took steps to retain a third-party contractor to evaluate its voltage regulating system controls and ensure that they were properly coordinated. The third-party contractor completed an initial review of SW2’s Facility on February 13, 2017. In doing so, however, the contractor did not include all required voltage regulating system controls within its initial review. The third-party contractor then performed all required voltage coordination verifications and completed a revised coordination study on August 6, 2017, ending the issue. The root cause of this issue was insufficient internal controls to ensure SW2 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW2 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This issue started on July 1, 2016, when PRC-019-2 became enforceable, and ended on August 6, 2017, when SW2 completed all required voltage coordination verifications. | This issue posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, when SW2 performed the required voltage coordination verifications, it did not identify any necessary settings changes to properly coordinate its voltage regulating system controls. Second, SW2 produces a relatively small amount of power, with a maximum nameplate rating of 105 MW and a 34% capacity factor for the period from July 1, 2016 until July 1, 2017. Finally, when SW2 operated during the non-compliance period, SW2 did not experience any unit trips related to voltage coordination issues. No harm is known to have occurred. Texas RE considered SW2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SW2: 1) completed the required voltage regulating system controls coordination verifications to demonstrate compliance with PRC-019-2 R1; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion, including compliance with upcoming voltage coordination verification deadlines; 3) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance issues; 4) retained a new Director of Regulatory Compliance that now reports directly to SW2’s Chief Operating Officer regarding NERC compliance obligations; 5) established regular meetings among NERC compliance personnel to discuss all elements of SW2’s compliance program, including ongoing projects and upcoming compliance deadlines; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance related duties. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 3, LLC (SW3) | NCR04133 | TRE2017016954 | PRC-019-2 | R1 | On February 7, 2017, SW3 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, SW3 did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its single generation Facility by July 1, 2016 as required. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW3 personnel discovered that SW3 had not performed the required voltage coordination verification activities for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW3 personnel took steps to retain a third-party contractor to evaluate its voltage regulating system controls and ensure that they were properly coordinated. The third-party contractor completed an initial review of SW3’s Facility on February 13, 2017. In doing so, however, the contractor did not include all required voltage regulating system controls within its initial review. The third-party contractor then performed all required voltage coordination verifications and completed a revised coordination study on July 25, 2017, ending the issue. The root cause of this issue was insufficient internal controls to ensure SW3 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW3 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This issue started on July 1, 2016, when PRC-019-2 became enforceable, and ended on July 25, 2017, when SW3 completed all required voltage coordination verifications. | This issue posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, when SW3 performed the required voltage coordination verifications, it did not identify any necessary settings changes to properly coordinate its voltage regulating system controls. Second, produces a relatively small amount of power, with a maximum nameplate rating of 129 MW and a 36% capacity factor for the period from July 1, 2016 until July 1, 2017. Finally, when SW3 operated during the non-compliance period, SW3 did not experience any unit trips related to voltage coordination issues. No harm is known to have occurred. Texas RE considered SW3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SW3: 1) completed the required voltage regulating system controls coordination verifications to demonstrate compliance with PRC-019-2 R1; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion, including compliance with upcoming voltage coordination verification deadlines; 3) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance issues; 4) retained a new Director of Regulatory Compliance that now reports directly to SW3’s Chief Operating Officer regarding NERC compliance obligations; 5) established regular meetings among NERC compliance personnel to discuss all elements of SW3’s compliance program, including ongoing projects and upcoming compliance deadlines; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance related duties. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 4, LLC (SW4) | NCR04135 | TRE2017016958 | PRC-019-2 | R1 | On February 7, 2017, SW4 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, SW4 did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its single generation Facility by July 1, 2016 as required. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW4 personnel discovered that SW4 had not performed the required voltage coordination verification activities for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW4 personnel took steps to retain a third-party contractor to evaluate its voltage regulating system controls and ensure that they were properly coordinated. The third-party contractor completed an initial review of SW4’s Facility on February 28, 2017. In doing so, however, the contractor did not include all required voltage regulating system controls within its initial review. The third-party contractor then performed all required voltage coordination verifications and completed a revised coordination study on July 25, 2017, ending the issue. The root cause of this issue was insufficient internal controls to ensure SW4 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW4 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This issue started on July 1, 2016, when PRC-019-2 became enforceable, and ended on July 25, 2017, when SW4 completed all required voltage coordination verifications. | This issue posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, when SW4 performed the required voltage coordination verifications, it did not identify any necessary settings changes to properly coordinate its voltage regulating system controls. Second, SW4 produces a relatively small amount of power, with a maximum nameplate rating of 239 MW and a 34% capacity factor for the period from July 1, 2016 until July 1, 2017. Finally, when SW4 operated during the non-compliance period, SW4 did not experience any unit trips related to voltage coordination issues. No harm is known to have occurred. Texas RE considered SW4’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SW4: 1) completed the required voltage regulating system controls coordination verifications to demonstrate compliance with PRC-019-2 R1; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion, including compliance with upcoming voltage coordination verification deadlines; 3) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance issues; 4) retained a new Director of Regulatory Compliance that now reports directly to SW4’s Chief Operating Officer regarding NERC compliance obligations; 5) established regular meetings among NERC compliance personnel to discuss all elements of SW4’s compliance program, including ongoing projects and upcoming compliance deadlines; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance related duties. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Sweetwater Wind 5, LLC (SW5) | NCR02715 | TRE2017016964 | PRC-019-2 | R1 | On February 7, 2017, SW5 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, SW5 did not verify the coordination of its voltage regulating system controls with the equipment capabilities and settings of applicable Protection System devices and functions for its single generation Facility by July 1, 2016 as required. During an internal review of its overall compliance with NERC Reliability Standards in the fall of 2016, SW5 personnel discovered that SW5 had not performed the required voltage coordination verification activities for its single generation Facility by the July 1, 2016 deadline. Following this discovery, SW5 personnel took steps to retain a third-party contractor to evaluate its voltage regulating system controls and ensure that they were properly coordinated. The third-party contractor completed an initial review of SW5’s Facility on February 28, 2017. In doing so, however, the contractor did not include all required voltage regulating system controls within its initial review. The third-party contractor then performed all required voltage coordination verifications and completed a revised coordination study on July 25, 2017, ending the issue. The root cause of this issue was insufficient internal controls to ensure SW5 identified and complied with all newly applicable NERC Reliability Standards. In particular, SW5 lacked sufficient compliance personnel or adequate compliance procedures to monitor new compliance obligations and take necessary steps to ensure compliance. This issue started on July 1, 2016, when PRC-019-2 became enforceable, and ended on July 25, 2017, when SW5 completed all required voltage coordination verifications. | This issue posed a minimal risk and did not pose as serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, when SW5 performed the required voltage coordination verifications, it did not identify any necessary settings changes to properly coordinate its voltage regulating system controls. Second, SW5 produces a relatively small amount of power, with a maximum nameplate rating of 79 MW and a 34% capacity factor for the period from July 1, 2016 until July 1, 2017. Finally, when SW5 operated during the non-compliance period, SW5 did not experience any unit trips related to voltage coordination issues. No harm is known to have occurred. Texas RE considered SW5’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SW5: 1) completed the required voltage regulating system controls coordination verifications to demonstrate compliance with PRC-019-2 R1; 2) instituted an action tracking system, which assigns responsibilities, identifies required actions, and monitors the status of open items until completion, including compliance with upcoming voltage coordination verification deadlines; 3) developed new internal compliance review processes and procedures that include regular meetings with senior management regarding compliance issues; 4) retained a new Director of Regulatory Compliance that now reports directly to SW5’s Chief Operating Officer regarding NERC compliance obligations; 5) established regular meetings among NERC compliance personnel to discuss all elements of SW5’s compliance program, including ongoing projects and upcoming compliance deadlines; 6) engaged a third-party contractor to create fully documented sets of compliance policies and procedures that address every applicable NERC Reliability Standard; and 7) conducted training on the new documented internal compliance program for all personnel with NERC compliance related duties. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Victoria WLE LP (VWLE) | NCR04159 | TRE2017017008 | MOD-025-2 | R1 | On February 13, 2017, VWLE submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R1. Specifically, VWLE neither verified the Real Power capability of two generating units in accordance with MOD-025-2, Attachment 1 nor submitted a completed form to its Transmission Planner (TP) containing the same information as MOD-025-2, Attachment 2 within 90 calendar days of the date of its recorded staged test. On June 1, 2016, VWLE acquired the two generating units at issue. Upon completing this acquisition, however, VWLE recognized that the previous owner had not taken steps to perform the required Real Power capability verifications by the July 1, 2016 deadline established for MOD-025-2 R1. VWLE initially scheduled the required Real Power capability testing in November 2016. However, an issue with the generation units’ combustion turbine prevented the units from providing their full rate output. VWLE subsequently addressed the issue with its combustion turbine and retained a third-party contractor to perform the required Real Power capability testing. VWLE completed its Real Power capability testing on April 25, 2017, but could not provide evidence that it submitted these test results to its TP within 90 days of completing those tests. On August 2, 2017, VWLE submitted its Real Power capability testing results to its TP, ending the issue. The root cause of this issue was that VWLE did not possess adequate processes for ensuring compliance with all applicable NERC Reliability Standards upon acquisition of the generation units at issue. In particular, VWLE did not have a process to verify that the previous owners had taken the necessary steps to comply with all MOD-025 Real Power capability testing requirements by July 1, 2016 as required, as well as processes to ensure adequate retention of compliance records. This issue started on July 1, 2016, when MOD-025-2 R1 became enforceable, and ended on August 2, 2017, when VWLE submitted a form containing the same information identified in MOD-025-2, Attachment 2 to its TP for both generating units. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following two factors. First, VWLE provided previously passing Real and Reactive Power verifications under substantially similar region-specific output conditions within two years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, VWLE provided information similar to the required Real Power capability verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, the two VWLE generating units at issue have a combined 377 MW nameplate rating and operated only at approximately a 54% capacity factor during the issue period. As a result, any errors in the Facility’s Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered VWLE’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, VWLE: 1) performed the required Real Power capability verification testing for the generation units at issue; 2) submitted forms for each generating unit containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) hired a compliance manager; 4) implemented an internal compliance program for the generation units at issue; 5) began implementing a Compliance Management System which will allow VWLE to track compliance deadlines, including upcoming Real and Reactive Power capability verification deadlines; 6) created a document repository within its compliance tracking software to retain necessary evidence to demonstrate compliance with MOD-025-2 Real and Reactive Power capability verifications; and 7) implemented a documented procedure of MOD-025-2, including procedures for tracking deadlines and retaining required compliance evidence. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Victoria WLE LP (VWLE) | NCR04159 | TRE2017018291 | MOD-025-2 | R2 | On February 13, 2017, VWLE submitted a Self-Report stating that it had an issue of MOD-025-2 R1. Specifically, VWLE stated it did not verify the Real Power capability of its generating units in accordance with Attachment 1. Subsequently, on September 5, 2017, Texas RE determined that the issue described in VWLE’s MOD-025-2 R1 Self-Report was also a noncompliance of MOD-025-2 R2 for VWLE as a Generator Owner (GO). In particular, VWLE neither verified the Reactive Power capability of its generating units in accordance with MOD-025-2, Attachment 1 nor submitted a completed form to its Transmission Planner (TP) containing the same information as MOD-025-2, Attachment 2 within 90 calendar days of the date of its recorded staged test. On June 1, 2016, VWLE acquired the two generating units at issue. Upon completing this acquisition, however, VWLE recognized that the previous owner had not taken steps to perform the required Reactive Power capability verifications by the July 1, 2016 deadline established for MOD-025-2 R1. VWLE initially scheduled the required Reactive Power capability testing in November 2016. However, an issue with the generation units’ combustion turbine prevented the units from providing their full rate output. VWLE subsequently addressed the issue with its combustion turbine and retained a third-party contractor to perform the required Reactive Power capability testing. VWLE completed its Reactive Power capability testing on April 25, 2017, but could not provide evidence that it submitted these test results to its TP within 90 days of completing those tests. On August 2, 2017, VWLE submitted its Reactive Power capability testing results to its TP, ending the issue. The root cause of this issue was that VWLE did not possess adequate processes for ensuring compliance with all applicable NERC Reliability Standards upon acquisition of the generation units at issue. In particular, VWLE did not have a process to verify that the previous owners had taken the necessary steps to comply with all MOD-025 Reactive Power capability testing requirements by July 1, 2016 as required, as well as processes to ensure adequate retention of compliance records. This issue started on July 1, 2016, when MOD-025-2 R2 became enforceable, and ended on August 2, 2017, when VWLE submitted a form containing the same information identified in MOD-025-2, Attachment 2 to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, VWLE provided previously passing Real and Reactive Power verifications under substantially similar region-specific output conditions within two years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, VWLE provided information similar to the required Reactive Power capability verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, the two VWLE generating units at issue have a combined 377 MW nameplate rating and operated only at approximately a 54% capacity factor during the issue period. As a result, any errors in the Facility’s Reactive output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered VWLE’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, VWLE: 1) performed the required Reactive Power capability verification testing for the generating units at issue; 2) submitted forms containing the same information identified in MOD-025-2, Attachment 2 to its TP; 3) hired a compliance manager; 4) implemented an internal compliance program for the Facility at issue; 5) began implementing a Compliance Management System which will allow VWLE to track compliance deadlines, including upcoming Real and Reactive Power capability verification deadlines; 6) created a document repository within its compliance tracking software to retain necessary evidence to demonstrate compliance with MOD-025-2 Real and Reactive Power capability verifications; and 7) implemented a documented procedure of MOD-025-2, including procedures for tracking deadlines and retaining required compliance evidence. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC2017017299 | PRC-019-2 | R2. | On March 24, 2017, AVGO submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2. Specifically, AVGO failed to coordinate its voltage regulating system controls with generator capabilities and protection device settings of at least 40 percent of its applicable Facilities within 90 days following the identification or implementation of systems, equipment, or setting changes that would affect the coordination described in Requirement 1 of the Standard. The cause of this noncompliance was a misunderstanding of the Standard and Requirement. Specifically, AVGO failed to understand that all changes and coordination identified in Requirement 1 must be made to at least 40 percent of its applicable Facilities within 90 days. AVGO believed that the coordination between Protection System devices and the in-service limiters was required by the Standard’s enforcement date and all other changes and coordination could be made at a later date. WECC determined that this noncompliance began on September 28, 2016, 90 days after AVGO identified the necessary Protection System changes, but failed to implement those changes and coordination defined in Requirement 1 of the Standard, through March 7, 2017, when it completed its mitigation activities. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, AVGO failed to coordinate voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of applicable Facilities within 90 days of identification or implementation of changes identified in Requirement 1 of the Standard. Failure to coordinate could result in an unnecessary device operation causing the generator to prematurely trip or damage to the turbine. This could result in the loss of 580 MW of generation at AVGO’s combined cycle combustion Facility. The facility is a combined cycle plant with one power block (3 generators), consisting of two combustion units and one steam unit with a combined capacity of 580 MW. Each generator has a primary protection relay and a backup relay. Only 2 of the 3 generators required settings changes as per the implementation plan of the standard but the entity adjusted all the three generators. The as found and as left settings of the limiter were 1.10/1.05 and 1.10/1.06 for the combustion and steam units. However, although AVGO failed to make settings changes within 90 days of identification, it contracted to have the PRC-019-2 engineering study completed prior to the implementation date of the Standard. AVGO has not experienced any unit trips due to mis-coordination between the generating units’ voltage regulating system controls and the applicable equipment capabilities. No harm is known to have occurred. For these reasons, WECC determined that this noncompliance posed a minimal risk to the reliability of the BPS. AVGO does not have any prior noncompliance with this Standard and Requirement. | To mitigate this noncompliance, AVGO: 1) completed all identified settings changes effecting the Facility’s automatic voltage regulators, protection relays settings, and equipment capabilities; 2) created Outlook calendar reminders and maintenance management system reminders for annual reviews of any completed settings or equipment changes to verify they have not impacted any coordination items outlined in Requirement 1; 3) created an Outlook calendar reminders and maintenance management system reminders on a five-year interval to perform coordination studies as required by the Standard; and 4) created maintenance management system assignments to generate notifications and reminders for the completion of PRC-019 specific compliance studies.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | WECC2017017446 | PRC-019-2 | R1 | On April 18, 2017, FEUS submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, FEUS reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. The cause of this noncompliance was insufficient time allotted to complete coordinating activities. Specifically, due to a slow response time from FEUS’ equipment manufacturers conducting the study, FEUS’ Subject Matter Experts (SME’s) were unable to complete the coordination study and to implement the recommended setting changes by the effective date of the Standard. WECC determined this noncompliance began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of FEUS’s applicable Facilities, and ended on October 13, 2016, when FEUS completed coordination activities for 40 percent of its applicable Facilities, for a total of 104 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, FEUS failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. Such failure could result in a generator trip during a system event that should not cause the generator to trip. However, the likelihood of the risk to the BPS was reduced because the combined capacity of FEUS’s two generating Facilities is 81 MW: the Bluffview Plant (63 MW) and the Animas Plant (18MW). Only 1 of the 2 generators required settings changes as per the implementation plan of the standard but the entity adjusted both generators. Additionally, the noncompliance had a low risk of causing minor harm and no harm is known to have occurred. For these reasons, WECC determined that this noncompliance posed a minimal risk to the reliability of the BPS. WECC notes that FEUS identified and Self-Reported the noncompliances described herein and does not have previous noncompliances of these Standards and Requirements. For these reasons, WECC considers FEUS’s compliance history a factor in its designation of these remediated noncompliances as a CE. | To mitigate this noncompliance, FEUS: 1) completed coordinating its voltage regulating system with its generator capabilities and Protection System devices for its Bluffview Facility (December 13, 2016) and Animas Facility (March 7, 2017). Therefore, bringing 100 percent of FEUS’ applicable Facilities into compliance with the PRC-019-2 R1; 2) modified its Compliance Monitoring and Enforcement Program to include quarterly Compliance Review meetings. These meetings will be between internal compliance staff and SME’s to discuss NERC Standards and to ensure SME's are reviewing the Standards in a timely manner; and 3) created an Internal Audit Tracking Sheet to ensure all Standards are reviewed and monitored for completion by SME’s.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | WECC2017017444 | PRC-024-2 | R1 | On April 18, 2017, FEUS submitted Self-Reports stating that, as a Generator Owner, it had possible noncompliances of noncompliance with PRC-024-2 R1 and R2. Specifically, FEUS reported that it failed to set its frequency protective relaying in accordance with Attachment 1 and its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The cause of these noncompliances was insufficient time allotted to complete coordinating activities. Specifically, due to a slow response time from FEUS’ equipment manufacturers conducting the study, FEUS’ SME’s were unable to complete the coordination study and to implement the recommended setting changes by the effective date of the Standard. WECC determined that these noncompliances began July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of FEUS’s applicable generating units, and ended December 13, 2016, when FEUS adjusted its frequency and voltage protective relaying in accordance with Attachments 1 and 2, for a total of 104 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, FEUS failed to set its frequency and voltage protective relaying such that it would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to frequency or voltage excursions within the “no trip zone”. However, the likelihood of the risk to the BPS was reduced because the combined capacity of FEUS’s two generating Facilities is 81 MW: the Bluffview Plant (63 MW) and the Animas Plant (18MW). Only 1 of the 2 generators required settings changes as per the implementation plan of the standard but the entity adjusted both generators. Additionally, the noncompliances had a low risk of causing minor harm and no harm is known to have occurred. For these reasons, WECC determined that this noncompliance posed a minimal risk to the reliability of the BPS. WECC notes that FEUS identified and Self-Reported the noncompliances described herein and does not have previous noncompliances of these Standards and Requirements. For these reasons, WECC considers FEUS’s compliance history a factor in its designation of these remediated noncompliances as a CE. | To mitigate this noncompliance, FEUS: 1) completed the required verification activities for its generating units in accordance with PRC-024-2 for all its applicable Facilities; and; 2) modified its Compliance Monitoring and Enforcement Program to include quarterly Compliance Review meetings. These meetings will be between internal compliance staff and SME’s to discuss NERC Standards and to ensure SME's are reviewing the Standards in a timely manner; and 3) created an Internal Audit Tracking Sheet to ensure all Standards are reviewed and monitored for completion by SME’s.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | WECC2017017445 | PRC-024-2 | R2 | On April 18, 2017, FEUS submitted Self-Reports stating that, as a Generator Owner, it had possible noncompliances of noncompliance with PRC-024-2 R1 and R2. Specifically, FEUS reported that it failed to set its frequency protective relaying in accordance with Attachment 1 and its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. The cause of these noncompliances was insufficient time allotted to complete coordinating activities. Specifically, due to a slow response time from FEUS’ equipment manufacturers conducting the study, FEUS’ SME’s were unable to complete the coordination study and to implement the recommended setting changes by the effective date of the Standard. WECC determined that these noncompliances began July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of FEUS’s applicable generating units, and ended December 13, 2016, when FEUS adjusted its frequency and voltage protective relaying in accordance with Attachments 1 and 2, for a total of 104 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). 14. In this instance, FEUS failed to set its frequency and voltage protective relaying such that it would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to frequency or voltage excursions within the “no trip zone”. However, the likelihood of the risk to the BPS was reduced because the combined capacity of FEUS’s two generating Facilities is 81 MW: the Bluffview Plant (63 MW) and the Animas Plant (18MW). Only 1 of the 2 generators required settings changes as per the implementation plan of the standard but the entity adjusted both generators. The Bluffview Plant required only the time delays be adjusted. For the Animass Plant, the as found/as left voltage setting change was 83.2 V/103.5V Additionally, the noncompliances had a low risk of causing minor harm and no harm is known to have occurred. For these reasons, WECC determined that this noncompliance posed a minimal risk to the reliability of the BPS. WECC notes that FEUS identified and Self-Reported the noncompliances described herein and does not have previous noncompliances of these Standards and Requirements. For these reasons, WECC considers FEUS’s compliance history a factor in its designation of these remediated noncompliances as a CE. | To mitigate this noncompliance, FEUS: 1) completed the required verification activities for its generating units in accordance with PRC-024-2 for all its applicable Facilities; and; 2) modified its Compliance Monitoring and Enforcement Program to include quarterly Compliance Review meetings. These meetings will be between internal compliance staff and SME’s to discuss NERC Standards and to ensure SME's are reviewing the Standards in a timely manner; and 3) created an Internal Audit Tracking Sheet to ensure all Standards are reviewed and monitored for completion by SME’s.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Malacha Hydro Limited Partnership GOP (MHGOP) | NCR05229 | WECC2017017127 | PRC-019-2 | R1 | On February 28, 2017, MHGOP submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, MHGOP reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its one applicable Facility by the effective date of the Standard. The root cause of this issue was MHGOP’s failure to understand the scope of the work required to meet the Standard by the effective date. WECC determined this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for MHGOP’s applicable Facility, and ended on April 11, 2017, when MHGOP completed coordination activities for its applicable Facility, for a total of 284 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, MHGOP failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its applicable Facility by the effective date of the Standard. Such failure could result in a generator trip during a system event that should not cause the generator to trip. However, when MHGOP performed the verification, no changes were required. Additionally, the likelihood of the risk to the BPS was reduced because the capacity of MHGOP’s hydro generating Facility is 30 MW. Further, the issue had a low risk of causing minor harm and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined MHGOP had no previous relevant compliance history related to this PRC-019-2 R1 issue of noncompliance. | To remediate and mitigate this issue, MHGOP: a. completed coordinating its voltage regulating system with its generator capabilities and Protection System devices; b. created a preventative maintenance task in its Maintenance Management System to trigger coordination reverification within a five-year window. WECC verified completion of the Mitigation Plan on August 17, 2017.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Rio Bravo Rocklin (RBROC) | NCR11296 | WECC2016016294 | PRC-019-2 | R1 | On September 30, 2016, RBROC submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, RBROC reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its applicable Facility by the effective date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for PRC-019-2 R1. RBROC believed that because it only had one applicable Facility, it was not required to meet the implementation deadline until July 1, 2019, when 100% of applicable Facilities are required to be compliant. WECC determined this issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for RBROC’s applicable Facility, and ended on November 28, 2016, when RBROC completed verification activities, for a total of 150 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, RBROC failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of its applicable Facility by the effective date of the Standard. Such failure could potentially result in a generator trip during a system event that should not cause the generator to trip, resulting in the loss of 24.4 MW of generation. However, the coordination study verified that no modifications were necessary. Therefore, there was a low probability that this issue would cause any impact to the reliability of the BPS. No harm was known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined RBROC had no previous relevant compliance history related to this PRC-019-2 R1 issue of noncompliance. | To remediate and mitigate this issue, RBROC: a. coordinated the voltage regulating system with its generator capabilities and Protection System devices for its applicable Facility; and b. maintains a master NERC equipment testing list that tracks upcoming equipment test dates.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Rio Bravo Rocklin (RBROC) | NCR11296 | WECC2016016296 | MOD-025-2 | R1; R1.1 | On September 30, 2016, RBROC submitted Self-Report stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 R1. Specifically, RBROC reported that it failed to verify Real Power capabilities of at least 40 percent of its applicable Facilities in accordance with Attachments 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding of the implementation plan for MOD-025-2. RBROC interpreted the "two years after regulatory approval" as being two years from the Standard’s effective date. WECC determined this issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of RBROC’s generating units, and ended on November 28, 2016, when RBROC completed testing in accordance with Attachment 1, for a total of 150 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, RBROC failed to verify Real Power capabilities of at least 40 percent of its generating units in accordance to Attachments 1 by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess BPS reliability. However, this issues would not likely have significantly affected current planning models as RBROC tested its unit in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Additionally, the Facility in scope has a total capacity of 32.9 MW. Therefore, there was a low probability that this issue would cause a minimal impact to the reliability of the BPS. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined RBROC had no previous relevant compliance history related to this MOD-025-2 R1 issue of noncompliance. | To remediate and mitigate these issues, RBROC: a. verified Real Power capabilities in accordance to the Standard and Requirements; b. submitted its Real Power verifications to its Transmission Planner; and c. maintains a master NERC equipment testing list that tracks upcoming equipment test dates.
2017-09-28 | Western Electricity Coordinating Council (WECC) | Rio Bravo Rocklin (RBROC) | NCR11296 | WECC2016016297 | MOD-025-2 | R2 | On September 30, 2016, RBROC submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, RBROC reported that it failed to verify Reactive Power capabilities of at least 40 percent of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding of the implementation plan for MOD-025-2. RBROC interpreted the "two years after regulatory approval" as being two years from the Standard’s effective date. WECC determined this issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of RBROC’s generating units, and ended on November 28, 2016, when RBROC completed testing in accordance with Attachment 1, for a total of 150 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance (BPS), RBROC failed to verify Reactive Power capabilities of at least 40 percent of its generating units in accordance to Attachments 1 by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess BPS reliability. However, this issues would not likely have significantly affected current planning models as RBROC tested its unit in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Additionally, the Facility in scope has a total capacity of 32.9 MW. Therefore, there was a low probability that this issue would cause a minimal impact to the reliability of the BPS. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined RBROC had no previous relevant compliance history related to this MOD-025-2 R2 issue of noncompliance. | To remediate and mitigate these issues, RBROC: a. verified Reactive Power capabilities in accordance to the Standard and Requirements; b. submitted its Reactive Power verifications to its Transmission Planner; and c. maintains a master NERC equipment testing list that tracks upcoming equipment test dates.
2017-09-28 | Western Electricity Coordinating Council (WECC) | US Navy, Naval Base Kitsap (USNK) | NCR05444 | WECC2017017178 | COM-002-4 | R3 | On March 1, 2017, USNK submitted a Self-Certification stating that, as a Distribution Provider, it had a possible issue of noncompliance with COM-002-4 R3. Specifically, USNK failed to conduct initial training for each of its operating personnel who can receive an oral, two-party, person-to-person Operating instruction. The root cause of this issue was the USNKs failure to realize that this Standard and Requirement applied to Distribution Providers. WECC determined that this issue began on July 1, 2016, when the Standard became mandatory and enforceable and ended April 3, 2017, when WECC determined that deregistration of the Distribution Provider function was warranted for USNK, for a total of 277 of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, USNK failed to conduct initial training for each of its operating personnel who can receive an oral, two-party, person-to-person Operating instructions. This issue could result in miscommunication while attempting to convey dispatch instructions that may lead to an unintended action or inaction of the facility. However, this facility consists of three closely-located 115 kV substations serving up to 50 MW of load. Miscommunication causing unintended action would primarily affect USNK’s own load with minimal potential impact on the interconnected BPS. Additionally, the associated 115 kV transmission line relays are owned by a neighboring Registered Entity and their operation was not the responsibility of USNK. WECC determined that this issue had a minimal likelihood of causing minor harm. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC determined USNK had no previous relevant compliance history related to this COM-002-4 R3 issue of noncompliance. | To remediate and mitigate this issue, USNK has requested and received approval to deregister as a Distribution Provider. USNK’s system serves a total peak load of 73 MW that is directly connected to the BPS, and fails to meet any of the minimal requirements of Appendix 5b, section III(b), of the NERC Rules of Procedure.
2017-08-31 | Midwest Reliability Organization (MRO) | Alliant Energy - East (ALTE) | NCR00961 | MRO2017016768 | MOD-025-2 | R1 | On October 3, 2016, ALTE submitted a Self-Log stating that, as a Generator Owner, it had an issue with MOD-025-2 R1. ALTE did not provide a verification of its Real Power capability to its Transmission Planner within 90 calendar days of the date the data was recorded during a staged test. ALTE completed the required testing on March 22, 2016, but the completed Attachment 2 form was not sent to its Transmission Planner until 116 days later. The noncompliance involved the Emery Generating Station which is owned by Alliant Energy - West (ALTW) (NCR00962). The cause of the noncompliance was a lack of a procedure or other internal control to ensure that test results were submitted to its Transmission Planner within 90 days. The issue began on July 1, 2016, when under the MOD-025-2 Implementation Plan registered entities were required to be 40% compliant with MOD-025-2 R1, and missing the Emery Generating Station caused ALTE to miss the 40% requirement, and ended on July 18, 2016, when the complete test results for the Emery Generating Station were submitted to the Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ALTE missed the 90-day reporting requirement by 26 days according to the specifications of the Standard, but due to the effective date of the Standard, and the implementation plan, the duration of the noncompliance was limited to only 18 days. This delay did not appear to impact the Transmission Planner's annual model building. Further, the data from the testing was very close to the historical data that the Transmission Planner was already in possession of. No harm is known to have occurred. ALTE has no relevant history of noncompliance. | To mitigate this issue, ALTE: 1) sent the test results to its Transmission Planner; and 2) augmented its MOD-025-2 Guidance Documents, which included required-by dates in its Attachment 2 form, having ALTE's NERC Compliance Department included on all emails for tracking, and creating a flow chart that illustrated hand offs and responsibilities between departments. ALTE stated that all mitigating activities were complete as of July 27, 2016.
2017-08-31 | Midwest Reliability Organization (MRO) | Alliant Energy - East (ALTE) | NCR00961 | MRO2017016769 | MOD-025-2 | R2 | On October 3, 2016, ALTE submitted a Self-Log stating that, as a Generator Owner, it had an issue with MOD-025-2 R2. ALTE did not provide a verification of its Reactive Power capability to its Transmission Planner within 90 calendar days of the date the data was recorded during a staged test. ALTE completed the required testing on March 22, 2016, but the completed Attachment 2 form was not sent to its Transmission Planner until 116 days later. The noncompliance involved the Emery Generating Station which is owned by Alliant Energy - West (ALTW) (NCR00962). The cause of the noncompliance was a lack of a procedure or other internal control to ensure that test results were submitted to its Transmission Planner within 90 days. The issue began on July 1, 2016, when under the MOD-025-2 Implementation Plan registered entities were required to be 40% compliant with MOD-025-2 R2 and missing the Energy Generating Station caused ALTE to miss the 40% requirement, and ended on July 18, 2016, when the complete test results for the Emery Generating Station were submitted to the Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ALTE missed the 90-day reporting requirement by 26 days according to the specifications of the Standard, but due to the effective date of the Standard, and the implementation plan, the duration of the noncompliance was limited to only 18 days. This delay did not appear to impact the Transmission Planner's annual model building. Further, the data from the testing was very close to the historical data that the Transmission Planner was already in possession of. No harm is known to have occurred. ALTE has no relevant history of noncompliance. | To mitigate this issue, ALTE: 1) sent the test results to its Transmission Planner; and 2) augmented its MOD-025-2 Guidance Documents, which included required-by dates in its Attachment 2 form, having ALTE's NERC Compliance Department included on all emails for tracking, and creating a flow chart that illustrated hand offs and responsibilities between departments. ALTE stated that all mitigating activities were complete as of July 27, 2016.
2017-08-31 | Midwest Reliability Organization (MRO) | Central Nebraska Public Power and Irrigation District, The (CNPPID) | NCR11163 | MRO2017016831 | EOP-004-2 | R3 | On January 24, 2017 CNPPID submitted a Self-Report stating that, as a Generator Owner, Generator Operator, and Transmission Owner, it had an issue with EOP-004-2 R3. Specifically, CNPPID did not perform the annual validation of its contact information for reporting events per its Operating Plan. CNPPID did not perform the annual verification in 2014 or 2015. The cause of the noncompliance was CNPPID's failure to understand its obligations under the Standard and Requirement. The noncompliance began on January 1, 2015, after CNPPID failed to perform a validation in 2014, and ended on December 21, 2016, when CNPPID validated the contact information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential risk of the noncompliance is that a registered entity, after identifying a reportable event, would not be able to successfully or quickly contact the other registered entities to efficiently implement the Operating Plan. The potential risk from the noncompliance in this case is low, as CNPPID's Transmission Operator, Balancing Authority, or Reliability Coordinator would likely identify a reportable event involving CNPPID and notify the appropriate entities. Further, the risk is reduced because the issue was self-detected, which demonstrates that the detective secondary control implemented as a mitigating activity in MRO2016016402 is functioning. Finally, the actual risk was reduced because CNPPID did not have any reportable events during the period of noncompliance, and the validation of the contract information confirmed that all the listed phone numbers were functioning. No harm is known to have occurred. CNPPID has no relevant history of noncompliance. | To mitigate this issue, CNPPID: 1) validated the contact information in its event reporting Operating Plan; and 2) committed to continuing to conduct quarterly reviews of proposed and current NERC Reliability Standards to detect areas of noncompliance. CNNPID stated that mitigating activities were complete as of December 21, 2016.
2017-08-31 | Midwest Reliability Organization (MRO) | Central Nebraska Public Power and Irrigation District, The (CNPPID) | NCR11163 | MRO2016016402 | PRC-002-2 | R1 | On September 28, 2016 CNPPID submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-002-2 R1. Specifically, CNPPID did not identify the BES buses where sequence of events recording (SER) and fault recording (FR) data is required. The cause of the noncompliance was CNPPID's failure to understand its obligations under the Standard and Requirement. Specifically, CNPPID was unaware that the Standard was applicable to a Transmission Owner, as CNPPID was deficient in monitoring and reviewing revised NERC Reliability Standards. The noncompliance began on July 1, 2016, the date the Standard and Requirement became enforceable upon CNPPID, and ended on October 13, 2016, when CNPPID completed its study to identify which BES buses required SER and FR data monitoring equipment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Under the Implementation Plan, the noncompliance only related to failing to timely identify which BES buses would require SER and FR data monitoring equipment, and the delay in this identification is not expected to impact the installation schedule for the required SER and FR equipment under the PRC-002-2 R1 implementation plan. Further the risk is further reduced because SER and FR data is used in post-fault analysis, and does not clear a fault or prevent a fault from occurring. Finally, the study indicates that CNPPID is only required to install SER and FR equipment at a single location, and CNPPID only owns four BES substations. No harm is known to have occurred. CNPPID has no relevant history of noncompliance. | To mitigate this issue, CNPPID: 1) completed its study and identified what BES buses SER and FR equipment is required; 2) notified its neighboring registered entity of the BES bus where SER and FR equipment would be installed; and 3) committed to performing quarterly reviews of proposed and current NERC Reliability Standards to detect areas of noncompliance. CNNPID stated that mitigating activities were complete as of October 13, 2016.
2017-08-31 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2016016201 | EOP-010-1 | R3 | On August 4, 2016, NSP, as a Multi-Region Registered Entity coordinated oversight program participant in a group that includes three registered entities, submitted a Self-Report stating that, as a Transmission Operator, it had an issue with EOP-010-1 R3, when it failed to fully implement its GMD Operating Procedure. NSP's GMD Operating Procedure requires it log the event, send a Major Event Notification to alert management, and send a Mission Mode Notification to generation facilities instructing them to report any abnormal activity. NSP failed to fully implement its procedure for Geomagnetic Disturbance Warnings issued on May 7, 2016, and May 8, 2016 by the National Oceanic and Atmospheric Administration (NOAA). The noncompliance occurred in the operating areas of the Public Service Company of Colorado (PSCO) (NCR05521) and Southwestern Public Service Company (SPS) (NCR01145). PSCO operators logged the first warning, but failed to log the second warning and failed to send the Major Event Notification or the Mission Mode Notification for both warnings. SPS operators logged both warnings and sent the Mission Mode Notification for both warnings, but failed to send the Major Event Notification for both warnings. The cause of the noncompliance is inadequate training and unclear procedure documentation. This issue started on May 7, 2016, when NSP failed to implement its GMD Operating Procedure after NOAA issued its first warning, and ended on May 8, 2016, when the second warning from NOAA expired. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk of noncompliance is that operators would not increase their vigilance, and not report any unusual operations caused by a GMD occurrence. PSCO had logged the event, so Control Center operators would likely have been vigilant to any issues in the generation facilities. SPS had logged the event and sent an notification to the generation facilities, so the noncompliance was limited to a failure to notify employees who would not be directly impacted by the occurrences. Additionally, both warnings from NOAA stated that the area that could be potentially impacted would be "primarily poleward of 50 degrees Geomagnetic Latitude." PSCO and SPS were not expected to see any effects of the GMD occurrence because PSCO operates at approximately 40 degrees Geomagnetic Latitude and SPS operates south of PSCO. Further, there was no reported equipment issues as a result of the GMD occurrence. No harm is known to have occurred. NSP has no relevant history of noncompliance. | To mitigate this issue, NSP: 1) PSCO and SPS-Xcel Control Center managers emphasized the importance of the GMD response procedure; 2) augmented the GMD Operating Procedure to clearly detail the Major Event Notification and Mission Mode Notification steps; and 3) trained operators on its augmented GMD Operating procedure. NSP stated that mitigating activities were complete as of June 6, 2017.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Noble Bliss Windpark, LLC (Noble Bliss) | NCR10271 | NPCC2017017746 | PRC-019-2 | R1. | On June 19, 2017, Noble Bliss submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on March 8, 2017, when the Entity completed its coordination verification and determined that voltage regulating system controls were appropriately coordinated. The cause of this instance of non-compliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 23.2%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 100.5 MW, which is less than 5.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by completing a coordination verification for its generating assets, which determined that voltage regulating system controls were appropriately coordinated 2) will prevent a recurrence of similar instances of noncompliance by: a) adding a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) hiring, by end of August 2017, a consultant to provide on-going education, awareness, and assistance in its NERC compliance program.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Noble Chateauguay Windpark, LLC (Noble Chateauguay) | NCR10367 | NPCC2017017747 | PRC-019-2 | R1. | On June 19, 2017, Noble Chateauguay submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on March 8, 2017, when the Entity completed its coordination verification and determined that voltage regulating system controls were appropriately coordinated. The cause of this instance of non-compliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 22.4%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 106 MW, which is less than 5.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by completing a coordination verification for its generating assets, which determined that voltage regulating system controls were appropriately coordinated 2) will prevent a recurrence of similar instances of noncompliance by: a) adding a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) hiring, by end of August 2017, a consultant to provide on-going education, awareness, and assistance in its NERC compliance program.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Noble Clinton Windpark, LLC (Noble Clinton) | NCR10272 | NPCC2017017748 | PRC-019-2 | R1. | On June 19, 2017, Noble Clinton submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on March 8, 2017, when the Entity completed its coordination verification and determined that voltage regulating system controls were appropriately coordinated. The cause of this instance of non-compliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 19.8%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 100.5 MW, which is less than 5.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by completing a coordination verification for its generating assets, which determined that voltage regulating system controls were appropriately coordinated 2) will prevent a recurrence of similar instances of noncompliance by: a) adding a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) hiring, by end of August 2017, a consultant to provide on-going education, awareness, and assistance in its NERC compliance program.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Noble Ellenburg Windpark, LLC (Noble Ellenburg) | NCR10273 | NPCC2017017749 | PRC-019-2 | R1. | On June 19, 2017, Noble Ellenburg submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on March 8, 2017, when the Entity completed its coordination verification and determined that voltage regulating system controls were appropriately coordinated. The cause of this instance of non-compliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 23.7%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 81 MW, which is less than 4.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by completing a coordination verification for its generating assets, which determined that voltage regulating system controls were appropriately coordinated 2) will prevent a recurrence of similar instances of noncompliance by: a) adding a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) hiring, by end of August 2017, a consultant to provide on-going education, awareness, and assistance in its NERC compliance program.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Noble Wethersfield Windpark, LLC (Noble Wethersfield) | NCR10368 | NPCC2017017743 | PRC-019-2 | R1. | On June 19, 2017, Noble Wethersfield submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, the Entity failed to verify the coordination of voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions as required by PRC-019-2 R1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on March 8, 2017, when the Entity completed its coordination verification and determined that voltage regulating system controls were appropriately coordinated. The cause of this instance of non-compliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to their dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its facilities needed to be 100% compliant with the standard and requirement by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 24%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 126 MW, which is less than 6.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of non-compliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by completing a coordination verification for its generating assets, which determined that voltage regulating system controls were appropriately coordinated 2) will prevent a recurrence of similar instances of noncompliance by: a) adding a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) hiring, by end of August 2017, a consultant to provide on-going education, awareness, and assistance in its NERC compliance program.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Delmarva Power & Light Company (DPL) | NCR00752 | RFC2017017824 | FAC-009-1 | R1 | On November 1, 2016, DPL submitted a self-log stating that, as a Distribution Provider and Transmission Owner, it had an issue of FAC-009-1 R1. On September 23, 2016, DPL Transmission Planning discovered a possible issue involving FAC-009-1. Specifically, DPL found that the calculated operating limits of a 138 kV Bulk Electric System (BES) facility were not representative of the most limiting component at that facility. A thorough investigation of the issue was initiated with the following facts and casual factors identified. DPL utilizes an Impedance Information System Access Data Base (z-table) to analyze individual facility components, identify the most limiting equipment rating, and calculate the associated facility operating limits. Upon discovering the above operating limits discrepancy, a detailed review of all BES facilities in the z-table database was performed. As a result of this review, a total of three 138kV BES facilities were discovered as having operating limits that were not representative of their most limiting components. In all three cases, the most limiting components had been internally coded in the database as “Code 17”. Code 17 is used to flag equipment that needs to be verified as a component of a facility. Until the equipment is verified and the Code 17 is removed, the z-table excludes the component from the operating limits calculation for that facility. Accordingly, because the Code 17s had not been verified and subsequently lifted on these particular pieces of equipment due to personnel oversight, the operating limits at the three identified 138kV facilities were incorrect and not representative of their most limiting components. Upon correction (i.e., verifying the equipment and removing the Code 17 designation), the following changes in operating limits were observed: 1. Two of the facilities required a reduction in their operating limits. • One required a reduction of its Summer and Winter normal, 4hr, 24hr, and load dump operation limits. The corrected variances for all four Summer operating limits are as follows: 144 MVA, 80 MVA, 80 MVA and 59 MVA. The corrected variances for all four Winter operating limits are as follows: 107 MVA, 38 MVA, 38 MVA and 11 MVA. • The other facility required only a reduction of its Summer and Winter normal operating limits by 31 MVA and 12 MVA, respectively. 2. The remaining facility did not require any changes to its operating limits due to a component replacement that took place in Fall of 2015, which shifted the most limited designation to another component entirely. As a result of the replacement, the operating limits for this facility were self-corrected in the Fall of 2015. However, prior to the replacement, the Summer and Winter normal operating limits for the facility should have been lower by 31 MVA and 21 MVA, respectively. Records indicate that the issue began on June 18, 2007, the initial FAC-009-1 enforcement date. DPL returned to compliance on October 13, 2016, after all corrected operating limits were communicated to DPL System Operations and PJM. This noncompliance involves the management practice of verification because PHI did not ensure that the Code 17s at issue were timely verified. This failure to timely verify is a root cause of this noncompliance. This issue started on June 18, 2007, when DPL was required to comply with FAC-009-1 R1 and ended on October 13, 2016, when DPL corrected the three 138 kV facilities with incorrect operating limits. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PHI’s risk-harm assessment determined the above issue to be of minimal impact to the BPS despite the long approximately eight and a half year duration. All three facilities are 138kV, representing only 2.5% of the BPS transmission circuits in the DPL region. Moreover, these facilities are part of the networked transmission system, which allows for alternate pathways and limits the potential for BPS load loss. Additionally, the facility planning limits used for system modeling (Basecase, N-1, N-1-1) were not impacted by the Code 17 issue. All planning limits were found to be accurate and appropriately aligned to the most limiting component of the facility. Thus, system planning activities were correctly performed using accurate limits for every facility. A historical review of load dating back to 2011 further revealed that (i) one of the facilities never exceeded its corrected normal operating limits; and (ii) the other two facilities did exceed their corrected normal operating limits for a duration of less than 36 minutes, but never exceeded the emergency limits. Ratings are calculated to allow flows between normal and emergency limits for up to 4 hours. No harm is known to have occurred. | To mitigate this issue, DPL performed a comprehensive review of all BES facilities in the z-table database to identify any components with a code excluding them from the operating limits calculation. All identified coded components were reviewed and operating limits verified or corrected as necessary. Corrected operating limits were submitted to System Operations for EMS application and communicated to PJM via TERM in eDART.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (EPP) | NCR11228 | RFC2016015893 | PRC-019-2 | R1 | On July 1, 2016, EPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. EPP failed to ensure coordination of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions prior to the July 1, 2016 implementation date for PRC-019-2 R1. Therefore, EPP was not compliant with PRC-019-2 R1. EPP contracted an engineering company to ensure coordination of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions prior to the July 1, 2016 implementation date for PRC-019-2 R1. EPP, however, was unable to locate all of the necessary information needed to ensure the necessary coordination prior to the July 1, 2016 standard effective date for 40% of the entity's applicable facilities. EPP had difficulty finding the necessary information for coordination because when EPP was acquired by Rockland Capital in April 2012, the previous owner did not provide all of the necessary documentation. This difficulty in finding the necessary information is a contributing cause of this noncompliance. EPP failed to coordinate the voltage regulating system controls because EPP did not prepare sufficiently to meet the July 1, 2016 implementation date. EPP’s inability to complete the coordination in a timely manner was partially due to the installation of Steam Turbine Generator #4 in June 2016. The installation of that generator allowed EPP limited time to coordinate and update the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions prior to the July 1, 2016 implementation date. This is another contributing cause of this noncompliance. This noncompliance involves the management practices of information management and asset and configuration management. Information management is involved because EPP compliance staff did not plan effectively to ensure compliance with PRC-019-2 R1 by the July 1, 2016 implementation date. EPP’s failure to plan and give itself enough time to become compliant is a root cause of this noncompliance. This issue started on July 1, 2016, when EPP was required to comply with PRC-019-2 R1 and ended on November 15, 2016, when EPP completed verification of all necessary coordination items. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that the uncoordinated voltage regulating system controls could cause a unit outage. The risk is minimized because EPP has a generating capacity of 237 MWs and during the noncompliance operated at an approximately 58% capacity factor. EPP was also promptly aware of the noncompliance, quickly worked to mitigate the noncompliance, and self-reported the issue. All three of those facts help minimize the risk. Lastly, when EPP performed the verification, no changes were required. No harm is known to have occurred. ReliabilityFirst considered EPP’s PRC-019 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPP: 1) hired contractors and accessed voltage regulating controls to obtain existing excitation limits; 2) ensured that in-service limiters are set to operate before the protection system of the facility in order to avoid disconnecting the generators unnecessarily; 3) ensured that applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits; and 4) reviewed the causes of this noncompliance and committed to become better prepared for the implementation of new Standards and Requirements by holding quarterly reliability calls with its plants that include a discussion of new Standards and Requirements coming into scope. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (EPP) | NCR11228 | RFC2016015894 | PRC-019-2 | R2 | On July 1, 2016, EPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R2. EPP failed to ensure coordination of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions prior to the July 1, 2016 implementation date for PRC-019-2 R2. Therefore, EPP was not compliant with PRC-019-2 R2. EPP contracted an engineering company to ensure coordination of the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions prior to the July 1, 2016 implementation date. EPP, however, was unable to locate all of the necessary information needed to ensure coordination prior to the July 1, 2016 standard effective date for 40% of the entity's applicable facilities. EPP had difficulty finding the necessary information because when EPP was acquired by Rockland Capital in April 2012, the previous owner did not provide all of the necessary documentation. This difficulty in finding the necessary information is a contributing cause of this noncompliance. EPP failed to coordinate the voltage regulating system controls because EPP did not prepare sufficiently to meet the July 1, 2016 implementation date. EPP’s inability to complete the coordination in a timely manner was partially due to the installation of Steam Turbine Generator #4 in June 2016. The installation of that generator allowed EPP limited time to coordinate and update the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions prior to the July 1, 2016 implementation date. This is another contributing cause of this noncompliance. Lastly, EPP could not comply with PRC-019-2 R2 until it became compliant with PRC-019-2 R1 and EPP was not compliant with PRC-019-2 R1 on the July 1, 2016 implementation date for PRC-019-2 R2. This noncompliance involves the management practices of information management and asset and configuration management. Information management is involved because EPP compliance staff did not plan effectively to ensure compliance with PRC-019-2 R2 by the July 1, 2016 implementation date. EPP’s failure to plan and give itself enough time to become compliant is a root cause of this noncompliance. This issue started on July 1, 2016, when EPP was required to comply with PRC-019-2 R2 and ended on November 15, 2016, when EPP completed all necessary coordination. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that the uncoordinated voltage regulating system controls could cause a unit outage. The risk is minimized because EPP has a generating capacity of 237 MWs and during the noncompliance operated at an approximately 58% capacity factor. EPP was also promptly aware of the noncompliance, quickly worked to mitigate the noncompliance, and self-reported the issue. All three of those facts help minimize the risk. Lastly, when EPP performed the verification, no changes were required. No harm is known to have occurred. ReliabilityFirst considered EPP’s PRC-019 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPP: 1) hired contractors to access voltage regulating controls; 2) ensured that in-service limiters are set to operate before the protection system of the facility in order to avoid disconnecting the generators unnecessarily; 3) ensured that applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, EPP performed the coordination as described in Requirement R1; and 4) reviewed the causes of this noncompliance and committed to become better prepared for the implementation of new Standards and Requirements by holding quarterly reliability calls with its plants that include a discussion of new Standards and Requirements coming into scope. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Eagle Point Power Generation, LLC (EPP) | NCR11228 | RFC2016015892 | PRC-024-2 | R1 | On July 1, 2016, EPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. EPP failed to meet the July 1, 2016, implementation date because EPP did not set the protective relaying system such that the generator frequency protective relaying does not trip the applicable generating unit within the “no trip zone” in a timely manner. EPP found that one of its generator’s under frequency trip setting was within the no trip zone. (The setting was changed from 58 Hz to the required 47.8 Hz. PRC-024-2 R1 also required EPP to change two 27 relays from 103.5V @ 5 sec. to 102.4V @ 5 sec. and 80.5 V at 2.0 sec. to 80.5 V at 2.1 sec respectively. These changes were completed on November 15th, 2016. No functions were changed.) This issue specifically resulted from a steam turbine which was commissioned in June 2016 very close to the July 1, 2016 implementation date meaning relay settings and other criteria only became recently available for EPP. This allowed EPP limited time to become compliant with PRC-024-2 R1 prior to the July 1, 2016 implementation date. This noncompliance involves the management practices of information management and asset and configuration management. Information management is involved because EPP compliance staff did not plan effectively to ensure compliance with PRC-024-2 R1 by the July 1, 2016 implementation date. EPP’s failure to plan and give itself enough time to become compliant is a root cause of this noncompliance. This issue started on July 1, 2016, when EPP was required to comply with PRC-024-2 R1 and ended on November 14, 2016, when EPP completed its Mitigation Plan by ensuring that all relevant settings are now outside of the not rip zone. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk of not having the correct settings determined and implemented is that the unit may not be able to withstand frequency and voltage excursions described in the Standard which could result in premature separation of generation which would exacerbate the transient. The risk is minimized due to the small nature of the deviation in frequency setting (58Hz vs. 57.8Hz), the risk that the 0.2Hz difference would lead to additional issues elsewhere on the system is very low. Furthermore, EPP’s 27 MW Steam Turbine 27 relay was set to “ride through” 90% of nominal voltage (which fell on the under voltage line). That was changed on November 15th, 2016 to 89% to fall outside of the line. This small change in ride through has little effect on the unit’s ability to withstand the frequency and voltage excursions described in the Standard. EPP’s remaining 210 MW of generation was not affected and would have been able to ride through the required transient of 57.8 Hz for the duration of the noncompliance. Lastly, EPP has a generating capacity of 237 MWs and during the noncompliance operated at an approximately 58% capacity factor. EPP was also promptly aware of the noncompliance, quickly worked to mitigate the noncompliance, and self-reported the issue. All three of those facts help minimize the risk. No harm is known to have occurred. ReliabilityFirst considered EPP’s PRC-024 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPP: 1) obtained an answer for whether or not any settings within the “no trip zone” for NERC standard PRC-024-2 can be changed or if the OEM recommends not changing due to equipment limitations; 2) made changes to all applicable settings; 3) reviewed the causes of this noncompliance and committed to become better prepared for the implementation of new Standards and Requirements by holding quarterly reliability calls with its plants that include a discussion of new Standards and Requirements coming into scope. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Northeast Management Company (GenOn) | NCR11137 | RFC2017016913 | VAR-002-4 | R2 | On January 31, 2017, GenOn submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-4 R2. During a regularly scheduled quarterly internal review of its voltage schedule reporting, GenOn revealed two instances in which it failed to notify its Transmission Operator (i.e., FirstEnergy) and PJM, when the 30 minute rolling average voltage exceeded the high voltage schedule. The first event occurred on January 2, 2016, when Conemaugh Unit 1 came online at 2:35 am, while Unit 2 was already online. The operator’s attention was primarily on Unit 1 because it was in startup mode. Because Unit 1 was in startup mode, it could not be counted as released to the grid to provide adequate voltage support. As a result of these conditions, the highest 30 minute average voltage level was exceeded by .156% for a total of 44 minutes. However, the review of the operator logs showed no evidence of appropriate notifications having been made. The second event occurred on December 20, 2016, when the applications which display the 30 minute rolling average were frozen for a period of 131 minutes. As a result, the control room operator and real time desk were not receiving updated information. Once the applications came back online, the cached data showed that the voltage schedule was exceeded during this time by .199%. However, the operator logs showed no evidence of appropriate notifications having been made. The root causes of these instances of noncompliance were as follows: (a) for the first instance, an inadequate startup procedure that failed to include sufficient voltage schedule verification; and, (b) for the second instance, an update error in the Trader application, which feeds the voltage information to the control room operator and real time desk. These major contributing factors involve the management practice of grid operations, which includes validating operations tools and monitoring operations performance. This issue started on January 3, 2016, when GenOn failed to make notification for the first instance of voltage exceedance, and ended on December 20, 2016, when GenOn failed to make notification for the second instance of voltage exceedance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the voltage excursions were relatively minor (i.e., .156% and .199% above the maximum voltage schedule), reducing the likelihood that any potential harm would occur. Second, this appears to have been a unique, isolated incident that is not indicative of any systemic voltage control issues. No harm is known to have occurred. ReliabilityFirst considered GenOn's VAR-002 R2 compliance history in determining the disposition track. GenOn’s relevant prior noncompliance with VAR-002 R2 includes: RFC2015014839. ReliabilityFirst has not yet resolved this matter. The prior violation is distinguishable from the instant noncompliance because the prior violation was the result of the fact that the station control room operators did not have a rolling 30 minute average value displayed on its control screens to monitor that level. In the current noncompliance, on the hand, the 30 minute rolling average was supposed to be displayed, but was not due to a technical issue with the relevant application. ReliabilityFirst determined that GenOn’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, GenOn: 1) corrected the update issue with energy management system Trader application; 2) implemented hourly voltage logs to be maintained by operators; 3) reviewed the importance of maintaining and reporting deviations from the established Voltage Schedule; 4) reviewed and updated startup procedure to include voltage schedule verification; 5) implemented an advanced alarm to alert approaching high voltage limit and email to Operations supervision; 6) trained Real Time and Conemaugh Operations personnel on NRG OCC-VAR-002 Compliance Procedure; and 7) investigated inaccuracy of voltage monitoring points and comparison with First Energy. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | GenOn Northeast Management Company (GenOn) | NCR11137 | RFC2017016914 | VAR-002-4 | R3 | On January 31, 2017, GenOn submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-4 R3. During a regularly scheduled internal review, GenOn discovered that it failed to notify its Transmission Operator, FirstEnergy, and PJM when Conemaugh Unit #2 High Pressure (HP) generator Automatic Voltage Regulator (AVR) had gone into manual mode for a period of 36 minutes. When the AVR went into manual mode, an alarm was generated and acknowledged by the operator. However, this happened during a shift change when the operator was changing load. During this time, the operator neither switched the AVR back to automatic mode nor made appropriate communication regarding this change. The root cause of this noncompliance was insufficient alarming. Although an alarm was produced, the operator was able to acknowledge it and not take action in response. This major contributing factor involves the management practice of grid operations, which includes performing incident management and control. This issue started on November 12, 2016, when GenOn was required to communicate the AVR status change to FirstEnergy and PJM, and ended on January 27, 2017, when GenOn completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, during the time when Unit #2 HP generator AVR was in manual mode, Unit #2 LP generator AVR was in automatic mode and maintaining the desired voltage. Second, Unit #1 was also operating with both AVRs functioning to hold the voltage appropriately. Third, both units interconnect to the same bus in the substation. Therefore, adequate control to maintain the voltage schedule existed even with changes in generation at the site during this event. No harm is known to have occurred. ReliabilityFirst considered GenOn’s VAR-002 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GenOn: 1) repaired the defective HP AVR to correct sporadic operation; 2) conducted refresher training on the OCC procedure governing the VAR-002 requirements to emphasis the action required; 3) added an alarm with instruction and email distribution to Operations supervision for change in AVR status to manual mode for the units; 4) reviewed the importance for prompt response and notification when AVR alarm received; and 5) reprogrammed U2 controls to include additional alarms every two minutes when the AVR in manual condition persists. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | GSG 6, LLC (ShadyOak) | NCR11247 | RFC2017017067 | PRC-005-2(i) | R3 | On December 9, 2016, ShadyOak self-identified a possible issue of PRC-005-2(i) R3 to the ReliabilityFirst Compliance Audit team. On February 21, 2017, ReliabilityFirst confirmed that ShadyOak, as a Generator Owner (GO), had an issue of PRC-005-2(i) R3 identified during a Compliance Audit conducted from February 13, 2017 through February 17, 2017. During its annual Compliance Audit, the ReliabilityFirst Audit Team confirmed that ShadyOak, as a GO, did not inspect the condition of all individual units of its VRLA type batteries by measuring battery cell/unit internal ohmic values nor did ShadyOak verify that the station battery could perform as manufactured by evaluating cell/unit measurements indicative of battery performance against the station battery baseline. In accordance with NERC’s PRC-005-6 Implementation Plan, ShadyOak should have performed these battery checks and tests by October 1, 2015 and by April 1, 2016. The tests, however, were not completed until August 24, 2016. ShadyOak uses a third party contractor to perform battery testing and maintenance activities pursuant to its Protection System Maintenance Program. ShadyOak believed that its contractor had performed all required battery maintenance and testing, but the Audit Team confirmed, after ShadyOak's self-identification, the missed tests on ShadyOak’s VRLA type batteries during the Compliance Audit. This noncompliance involves the management practices of verification and external interdependencies. Verification and external interdependencies are both involved because ShadyOak failed to verify that ShadyOak’s third-party contractor completed all battery related maintenance activity that they were hired to perform. This failure to verify is a root cause of the noncompliance. This issue started on October 1, 2015, when ShadyOak was required to perform tests and inspections on the VRLA-type batteries at issue and ended on August 24, 2016, when ShadyOak completed the overdue battery tests and inspections. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this instance of noncompliance is a failure of ShadyOak's battery bank which would cause the loss of ShadyOak's 109.5 MW nameplate wind generation capacity for a variable period of time. The risk in this instance of noncompliance is minimized because ShadyOak completed all other maintenance testing activities required by PRC-005-2(i) R3 on the VRLA-type batteries at issue including voltage verification. Further minimizing the risk, ShadyOak had a monitoring infrastructure in place that would have alerted them to a battery system failure. No harm is known to have occurred. ReliabilityFirst considered ShadyOak's PRC-005 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ShadyOak: 1) completed the necessary maintenance and testing on the VRLA-type batteries to comply with PRC-005-2(i); 2) reviewed this issue with their contractor and conducted a comprehensive review with the contractor to make sure no other tests were missed. ShadyOak also committed to work with their contractor to ensure that the proper work was being performed to review the battery system in accordance with ShadyOak's Protection System Maintenance Program, and committed to validate the work of the contractor to ensure it satisfies PRC-005-2(i). ShadyOak established an internal control to make sure that ShadyOak verifies that its contractor is performing all the work that the contractor has been hired to complete. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Lincoln Generating Facility, LLC (Lincoln Generating) | NCR10208 | RFC2017017244 | PRC-005-6 | R3 | On March 8, 2017, Lincoln Generating submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-6 R3. While compiling evidence in February 2017 as part of an annual review, a Lincoln Generating employee discovered that Lincoln Generating did not have documentation for two specific testing components on its back-up battery systems. The first testing component was the inter-cell resistance check and the second was the cell to cell resistance check. Both of these checks were previously included in the annual checks performed by a contractor that performs these tests for Lincoln Generating. The two checks were previously completed in June 2015 and the maximum allowable time between these checks is 18 months pursuant to PRC-005-6. Therefore, Lincoln Generating was required to complete these checks by the end of December 2016. Lincoln Generating, however, did not complete these checks until February 11, 2017. Lincoln Generating completed the inter-cell resistance test on February 10, 2017 and the cell to cell resistance testing on February 11, 2017. The oversight occurred during a transition to conduct the battery testing with internal plant staff, rather than outsourcing testing to a contractor. An affiliate of Lincoln Generating purchased the necessary testing equipment for use at multiple sites with the plan of shipping the testing equipment to the Lincoln Generating Facility. The equipment was purchased in early 2016 and the affiliate plant began self-performing the battery testing then. The necessary testing equipment for these two specific checks, however, was not sent to the Lincoln Generating Facility as planned and they received the equipment late. Lincoln Generating did not miss any other tests due to receiving the testing equipment late. This noncompliance involves the management practices of verification and grid maintenance. Verification is involved because Lincoln Generating failed to verify that it timely completed all necessary testing on its back-up batteries. This failure to verify that the necessary testing was timely completed is a root cause of this noncompliance. Grid maintenance is involved because Lincoln Generating failed to monitor grid maintenance performance and operations in order to confirm that the equipment necessary for testing would be delivered in a timely manner. This issue started on January 1, 2017, when Lincoln Generating was required to have completed testing on the two components of the annual back-up battery systems in accordance with the 18 month testing interval and ended on February 11, 2017, when Lincoln Generating completed the overdue testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that not timely maintaining and testing all transmission and generation Protection System devices can have a negative effect on the reliable operation of the BPS. The risk is minimized because Lincoln Generating did successfully complete the five year battery load tests on these back-up batteries in 2016 which showed the batteries were working properly. Lincoln Generating only missed tests on two components (inter-cell resistance test and cell to cell resistance) of the backup batteries. Additionally, this noncompliance has a short duration of less than two months. Once Lincoln Generating discovered the overdue tests, Lincoln Generating promptly completed the required testing and the testing showed that all battery systems were in good condition. No harm is known to have occurred. ReliabilityFirst considered Lincoln Generating’s PRC-005 R3 compliance history and determined there were no relevant instances of noncompliance | To mitigate this issue, Lincoln Generating: 1) immediately, upon realizing that tests had been missed, acquired the necessary test equipment from their affiliate site, trained its personnel on how to use the equipment, and completed the overdue intercell and cell to cell resistance testing; 2) changed the Computerized Maintenance Management Software Work order to show that it is a NERC required compliance activity that is time sensitive. This update to Lincoln Generating’s compliance documentation will help prevent recurrence because it states that plant personnel are responsible for performing these tests on an 18 month interval. The update will remind Lincoln Generating compliance personnel to make sure that they have all the equipment they need to complete NERC-required testing; and 3) trained its technicians on these compliance activities to help prevent the recurrence of this noncompliance.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | PECO Energy Company (PECO) | NCR08026 | RFC2017016810 | PRC-005-2(i) | R3 | On January 13, 2017, PECO submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-005-2(i) R3. On November 8, 2016, during regularly scheduled trip testing, PECO identified five line relays associated with a specific 220 kV transmission line that did not have a certain alarming function required by PECO’s PRC-005 program. Testers noted that the loss of communication alarms were not wired to certain relays and that the relays in question were not designed to have alarms wired. Based upon its records, PECO believed that it was continuously monitoring communication channels on this line and, consequently, that the communications needed to be tested only every 12 calendar years. (See PRC-005-2(i), Table 1-2) However, because the line was, in actuality, not being continuously monitored, PECO should have tested the communication channels no later than August 1, 2015, four months after the effective date of PRC-005-2(i). The affected 220 kV line has six line relays, including one primary and one backup line relay at three different substations. In addition, transfer trip devices communicate between these three main substations and a fourth substation that has a tapped transformer off this line. The three primary relays have no communication alarming, and the backup relays at two substations have no communication alarming. However, the backup relay at the third substation does have communication alarming. PECO performed the testing November 8, 2016, and removed the “receive” fiber from each device at all four substations as well as cataloguing which substations had alarms present. When the fiber was removed from all of the primary relays, no alarms were present. When the fiber was removed from the backup relays or the transfer trip devices, alarms were present at some substations. Consequently, because the primary and backup relays are fully redundant in terms of system protection, this line would not have fully lost communication-based protection functions without alarming. The root cause of this noncompliance was the fact that PECO incorrectly assumed that any devices identified as being capable of alarming for a loss of communication were, in fact, designed and installed to provide those alarms. This noncompliance involves the management practices of verification and grid maintenance. Verification is involved because PECO failed to verify the alarming configuration on these relays. Grid maintenance is involved because PECO failed to monitor grid maintenance performance and operations in order to confirm that the necessary alarms and trip devices were installed. This issue started on August 1, 2015, the first date that communications testing would have been required for an unmonitored relay and will end on November 18, 2016, when PECO completed the testing of the communication channels on this line. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is the potential loss of the 220 kV line in question due to improper relay operation because of an undetected communication failure. The risk is minimized based on the following factors. First, since the primary and backup relays are fully redundant in terms of system protection, and both provide instantaneous tripping during a line fault, the protection system would not be affected by a loss of communication. Second, there are working alarms on parallel fiber systems that would detect any issue that affected this line fiber, so the issue would be identified even if some of the relays on the line were not alarming. Third, these relays are equipped with backup step distances protection that trips for a fault regardless of communication status. Finally, the backup relaying would be able to trip instantaneously even if the primary relay lost communication, and any communication failure would trigger an alarm to the system. No harm is known to have occurred. ReliabilityFirst considered PECO’s PRC-005 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PECO: 1) created work orders to install communication alarms on these identified 220 kV line relays; 2) created triggers to perform preventive maintenance work orders for manually testing unmonitored communication devices, to be performed every three months. Applied this to relays on this 220 kV line with a last maintenance date of November 18, 2016; 3) updated Engineering Practice document for Transmission Line Relaying to identify the need for communication alarms on new relays; 4) updated Engineering Practice document for Relay Setting Project Checklist to include a check for alarms, including communication alarms, as needed; 5) updated Job Process for Maintaining PECO’s PRC-005 Excel Workbook (JPP-1312) to include an independent review by the Subject Matter Expert for Communications; 6) conducted training for all relay engineers and independent reviewers on verifying communication alarms and updating the PRC-005 Change Form; and 7) completed initial extent of condition review. Created a list for field verification if necessary. PECO will complete the following mitigation activities by December 22, 2017: 1) will complete field verification of communication alarms identified by Engineering Review; 2) will ensure installation of communication alarms on these identified 220kV line relays; and 3) will complete verification documentation of communication spreadsheet, based on the results of the field testing of communication equipment. This length of time is necessary due to scheduling the work to be performed on the 220 kV line.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | PSEG Nuclear LLC (PSEG Nuclear) | NCR00895 | RFC2017017246 | VAR-002-2b | R3 | On March 9, 2017, PSEG Nuclear submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue of VAR-002-2b R3. This noncompliance contains three separate instances of noncompliance. While preparing a Reliability Standard Audit Worksheet (RSAW) for VAR-002 in December 2016, PSEG Nuclear identified three instances where it did not make Power System Stabilizer (PSS) notifications within the required 30 minute notification window specified in VAR-002-4 R3. PSEG Nuclear is required to notify its Transmission Operator (TOP) within 30 minutes of any status or capability change of its PSS and the expected duration of that change. First, on August 24, 2013 at PSEG Nuclear’s Salem Unit 1 Reactor, the Salem Control Room Operator notified PSEG (its TOP) that it would be synching the Automatic Voltage Regulator (AVR) in automatic and with the PSS enabled (on) at 3:15 PM. At 4:39 PM, Salem Unit 1 synchronized to the grid. (A Salem Control Room Operator, however, called PSEG Energy Resource and Trading (ER&T) at 6:59 PM and told PSEG ER&T that the PSS is now enabled as of 6:59 PM. A ticket was put into PSEG ER&T’s system and immediately canceled because there was not a prior notification from Salem that the PSS was off.) The PSS was disabled (off) when Salem Unit 1 synchronized to the grid at 4:39 PM and Salem Unit 1 did not inform its TOP (which is PSEG) of this disabled PSS status until 6:59 PM when Salem informed PSEG (the TOP) that the PSS had been enabled. Therefore, PSEG Nuclear did not inform its TOP within 30 minutes of a change in status of the PSS. In this instance, PSEG Nuclear notified its TOP approximately two hours late of a change in the status of the PSS. Second, on December 1, 2015, at PSEG Nuclear’s Salem Unit 2 Reactor, Unit 2 was in startup testing associated with an AVR replacement and generator step up transformers replacement. During this startup testing, there were regular communications back and forth between Salem, PSEG (its TOP), and PJM that the AVR would be in manual and the PSS would be out of service for portions of the testing. (At 10:55 AM on December 2, 2015, a Salem Control Room Operator called its TOP to state that the AVR was now in automatic and the ticket previously establishing the AVR in manual was closed. Salem’s Nuclear Operator Narrative logs note the AVR in automatic and the PSS enabled on December 2, 2015 at 10:46 AM. At 4:24 PM on that same day, PSEG ER&T asked Salem Unit 2 about the status of the PSS and noted it was enabled. PSEG ER&T then closed the ticket that had previously established the PSS as off. At 5:10 PM, a second discussion between Salem Unit 2 and PSEG ER&T occurred where PSEG ER&T noted the PSS as enabled but not tuned. Following this discussion, PSEG ER&T contacted PJM and reopened the PSS disabled ticket. On December 3, 2016, at 4:38 AM, Salem Unit 2 notified PSEG ER&T that the PSS was enabled and the ticket was closed.) Salem Unit 2 did not properly communicate the PSS enabled status at 10:46 AM on December 2, 2015 to its TOP until 4:24 PM on December 2, 2015. In this instance, PSEG Nuclear notified its TOP of a change in the PSS status more than five hours late. Third, on November, 11, 2016, Hope Creek (PSEG Nuclear’s Hope Creek Generating Station is a single unit (one reactor) station which has 1,219 MW of total generating capacity.) notified PSEG (its TOP) that it would be synchronizing with the AVR in automatic and the PSS enabled at 2:30 AM. Hope Creek has a new voltage regulator that automatically enables the PSS when power reaches approximately 193.6 MW and this is automatically controlled by software. Hope Creek synchronized to the grid at 5:37 PM on that same day and did not notify PSEG (its TOP) that the PSS was enabled until 8:41 PM. In sum, Hope Creek did not properly communicate to its TOP that the PSS was off at 5:37 PM and did not notify the TOP of the status at all until Hope Creek informed the TOP that the PSS was back enabled at 8:41 PM. In this instance PSEG Nuclear notified its TOP of a change in the PSS status more than two hours late. This noncompliance involves the management practices of workforce management and work management. Workforce management is involved because PSEG Nuclear ineffectively trained its personnel on what kind of PSS related notifications needed to be made. Specifically, PSEG Nuclear provided ineffective procedural guidance and training to its personnel responsible for making PSS notifications to ensure accurate and timely communication of status changes of the PSS. Work management is also involved because PSEG Nuclear’s process for communicating PSS status changes was ineffective, which is a root cause of this noncompliance. This noncompliance contains three separate issues. The first issue began and ended on August 24, 2013. The second issue began and ended on December 2, 2015. The third issue began and ended on November 11, 2016. Following from that, the first issue in this noncompliance began on August 24, 2013, and the last issue of the noncompliance ended on November 11, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that PSEG Nuclear, as the GOP, is making status changes to equipment that provides voltage control without notifying the TOP. Making these changes without notifying the TOP puts the TOP in a position where it does not have full and accurate information about how the GOP is controlling voltage. The risk is minimized here because the design of the voltage regulators dispatched across the PSEG nuclear fleet (including the three reactors at issue here), includes automatic activation of the PSS through software configuration once minimum power levels have been achieved. This reduces the risk because the PSS, which helps stabilize voltage and provide grid stability, is automatically turned on once minimum power levels are reached meaning the PSS is turned on even if a nuclear operator does not actively enable the PSS. Further reducing the risk, two of the three issues (the issue at Salem Unit 1 and Hope Creek) involved PSEG Nuclear failing to timely inform its TOP of the PSS being enabled meaning that the PSS was already performing its grid stability function before the TOP was notified. For the third issue, at Salem Unit 2, it occurred during AVR change out and testing activities and the TOP had been notified that testing would be ongoing for the AVR and the PSS. This reduces the risk because the TOP knew that Salem Unit 2 would be turning its AVR and PSS on and off during that day. No harm is known to have occurred. ReliabilityFirst considered PSEG Nuclear's VAR-002 R3 compliance history in determining the disposition track. PSEG Nuclear’s relevant prior noncompliance with VAR-002 R3 includes: RFC2012011214. A Find, Fix and Track Report (FFT) informational posting addressing a noncompliance with VAR-002-1.1b R3 was posted on the NERC website on August 30, 2013. In the prior issue, PSEG Nuclear failed to notify its TOP within 30 minutes of a status change on its PSS on three occasions in May 2012. A primary contributing cause of this prior issue was that PSEG Nuclear’s notification procedure in effect at the time incorrectly indicated that the PSEG Nuclear Control Room Operator should notify the local system operator and load dispatcher of PSS status changes. The procedure should have instructed the operator to specifically notify the PSEG Energy Resource and Trading (ER&T) desk of these PSS changes. The prior issue is distinguishable from the instant noncompliance because the prior issue involves a different contributing cause. In the prior issue, the operator was correctly following an incorrect procedure and making PSS notifications to the wrong people. In the current noncompliance, however, the operator was not effectively trained on how to follow the correct procedure. ReliabilityFirst determined that PSEG Nuclear’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, PSEG Nuclear: 1) issued a standing order which promulgated the requirement to notify PSEG ER&T within 15 minutes of any change in the status of the Hope Creek Generator PSS; 2) issued a standing order which promulgated the requirement to notify PSEG ER&T within 15 minutes of any change in the status of Salem Unit 1 or Salem Unit 2 Generator PSS; 3) added steps to procedures that manipulate the PSS and the procedure that verifies the PSS automatically changes status to notify PSEG ER&T of the PSS status within 15 minutes of the change; and 4) added steps to procedures that manipulate the PSS and the procedure that verifies the PSS automatically changes status to notify PSEG ER&T of the PSS status within 15 minutes. PSESG Nuclear retrained all relevant personnel on these revised procedures and these revised procedures and the retraining will help prevent recurrence. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | T.E.S. Filer City Station Limited Partnership (TES) | NCR00925 | RFC2016015889 | MOD-025-2 | R2 | On July 5, 2016, TES submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R2. TES, as a GO, did not verify the reactive power capability of its generating units by the compliance implementation date of July 1, 2016. TES compliantly provided the reactive power data to its Transmission Planner (TP) within 90 days of MOD-025-2’s implementation plan. Shortly after the July 1, 2016 implementation date and while TES was planning to submit its reactive power data to its TP within 90 days of that implementation date, TES discovered that it had not performed the reactive power tests by the required July 1, 2016 implementation date. Following this discovery, TES realized that it was not in compliance with MOD-025 R2.1 and quickly submitted this Self-Report. This noncompliance involves the management practices of planning and grid maintenance. Planning is involved because TES did not sufficiently plan to ensure that it was compliant with both MOD-025-2 R2.1 and R2.2 by the required dates. As a result of this lack of planning, TES only complied with R2.2, and not 2.1, by submitting the required data to the TP on time. This failure to plan effectively is the root cause. This issue started on July 1, 2016, when TES was required to comply with MOD-025-2 R2 and ended on July 26, 2016, when TES completed the overdue generator reactive capability test. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that the Regional Transmission Organization (RTO) would not have accurate information on generator gross and net Real and Reactive Power capability and synchronous condenser Reactive Power capability to use for its planning models to assess BPS reliability. The risk is minimized here because TES provided the required test result data to its TP on time (within 90 days of the implementation date) pursuant to MOD-025-2 R2.1 and the short duration of the noncompliance (25 days). Timely providing the data to the TP and RTO and the overall short duration reduces the risk because it lessens the time that the TP and RTO would potentially not have accurate information on TES. Lastly, TES is a small (73 MVA gross nameplate rating) generating unit that has been reliably supplying generation to the BPS since 1990 and has only experienced a small reduction in its reactive capability, thus, the data the TP and RTO previously had about TES was largely correct. TES operates with approximately a 96% capacity factor and provides 60 MW to the BPS through Consumers Energy. No harm is known to have occurred. ReliabilityFirst considered TES’s MOD-025 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TES: 1) conducted the generator Reactive Capability test on July 26, 2016; and 2) implemented a compliance tracking system to define and track actions that are to be taken to implement new and modified NERC Standards and Requirements. Specifically, TES utilized the “Standards Subject to Future Enforcement” and “Standards Filed and Pending Regulatory Approval” listings published by NERC and provided a list of standards to relevant personnel biannually that are applicable to GOs and Generator Operators, and are subject to enforcement within two years for implementation planning. TES also trained relevant personnel on this new compliance tracking system. A contributing factor to this noncompliance is that TES did not understand what MOD-025-2 R2 required them to do and they did not take the time to ask questions and ensure that they understood the requirements correctly. Tracking what Standards and Requirements are subject to enforcement two years out will allow TES more time to ensure that they completely understand the upcoming Standards and Requirements. ReliabilityFirst has verified the completion of all mitigation activity.
2017-08-31 | Southwest Power Pool Regional Entity (SPP RE) | CPV Keenan II Renewable Energy Company, LLC (KREC) | NCR11081 | SPP2016016209 | PRC-024-2 | R1 | On September 28, 2016, KREC submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. KREC is a wind farm generating facility with 66 generating units applicable to PRC-024-2. Specifically, KREC did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through September 14, 2016, the date KREC corrected its generator frequency protective relay settings. The root cause of this instance of noncompliance was lack of managerial oversight ensuring compliance with version two of PRC-024 by the effective date of July 1, 2016. KREC did not contact its Transmission Planner (TP) until June 23, 2016, to confirm that the protective relay settings set in December 2010, when the facility was commissioned, were still applicable. On June 30, 2016, the TP requested that KREC make an adjustment to the 11T1 relay set point to bring the relay into PRC-024-2 specifications. KREC hired a contractor to make the changes to the protective relays; however, the contractor was not able to complete the changes by July 1, 2016, the PRC-024-2 implementation date. The correction to the 11T1 relay setting was performed on September 14, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Although the prior setting for a KREC frequency protection relay did encroach on the “no trip zone” of PRC-024-2, the encroachment was near the bottom of the “no trip zone,” i.e., pickup at 58.5 Hz with a time delay of .2 seconds. A 58.5 Hz system frequency excursion is extreme and would have initiated all three steps of the Southwest Power Pool underfrequency load shed program, potentially causing the load shed of approximately 17,000 MW. KREC is an intermittent generation wind farm with a capacity of 152 MW. The premature operation of the KREC frequency protection relay at 58.5 Hz and the loss of 152 MW would have a minor impact on the system frequency and the recovery from such an extreme frequency event. KREC has not experienced any frequency related trips or PRC-024 related issues between the commissioning date in December of 2010 and September 14, 2016 when the correction was made to the 11T1 relay setting. No harm is known to have occurred. SPP RE reviewed KREC’s violation history and determined that KREC has no prior instances of noncompliance with PRC-024. | To mitigate this issue, KREC completed the following mitigation activities: 1) set generator frequency protective relays in accordance with R1; 2) provided training to personnel on the change that was made to the relay settings per PRC-024-2; and 3) provided training on generator frequency protective relay systems.
2017-08-31 | Southwest Power Pool Regional Entity (SPP RE) | KODE Novus I, LLC (KODE) | NCR11329 | SPP2016016264 | PRC-024-2 | R1 | On September 30, 2016, KODE submitted a Self-Certification stating that, as a Generator Owner, it had an issue of noncompliance with PRC-024-2 R1 because it did not verify that its frequency protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through April 26, 2017, the date KODE completed a relay study verifying its frequency protective relays were not set to trip within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was KODE’s failure to monitor the standard development process to identify the new standards and requirements applicable to KODE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. KODE is a wind farm generating facility with 40 – two MW wind turbine generators that run intermittently and are capable of providing minimal system frequency support. Additionally, the study of KODE’s frequency protective relays indicated that the relays were not previously set to operate within the “no trip zone” of PRC-024 Attachment 1. No harm is known to have occurred as a consequence of KODE’s noncompliance with PRC-024-2 R1. SPP RE reviewed KODE’s violation history and determined that KODE has no prior instances of noncompliance with PRC-024. | To mitigate this minimal risk instance of noncompliance, KODE: 1) completed a study of its frequency protective relays; and 2) required its Compliance Manager to monitor the standards development process to identify new or changes to reliability standards and requirements. SPP RE has verified the completion of all mitigation activity.
2017-08-31 | Southwest Power Pool Regional Entity (SPP RE) | KODE Novus I, LLC (KODE) | NCR11329 | SPP2016016265 | PRC-024-2 | R2 | On September 30, 2016, KODE submitted a Self-Certification stating that, as a Generator Owner, it had an issue of noncompliance with PRC-024-2 R2 because it did not verify that its voltage protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through April 26, 2017, the date KODE completed a relay study verifying its voltage protective relays were not set to trip within the “no trip” zone of PRC-024 Attachment 1. The root cause of this instance of noncompliance was KODE’s failure to monitor the standard development process to identify the new standards and requirements applicable to KODE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relays in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. KODE is a wind farm generating facility with 40 – two MW wind turbine generators that run intermittently and are capable of providing minimal system voltage support. Additionally, the study of KODE’s voltage protective relays indicated that the relays were not previously set to operate within the “no trip zone” of PRC-024 Attachment 1. No harm is known to have occurred as a consequence of KODE’s noncompliance with PRC-024-2 R2. SPP RE reviewed KODE’s violation history and determined that KODE has no prior instances of noncompliance with PRC-024. | To mitigate this minimal risk instance of noncompliance, KODE: 1) completed a study of its voltage protective relays; and 2) required its Compliance Manager to monitor the standards development process to identify new or changes to reliability standards and requirements. SPP RE has verified the completion of all mitigation activity.
2017-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Oklahoma Municipal Power Authority (OMPA) | NCR04108 | SPP2016016254 | MOD-025-2 | R2; R2.1 | On September 30, 2016, OMPA submitted a Self-Certification stating that, as a Generator Owner (GO), it had an issue of noncompliance with MOD-025-2 R2.1 because the reactive power capability test performed for the Charles D. Lamb Energy Center, a 103 MW peaking facility, did not comply with Attachment 1 of MOD-025-2. Specifically, the reactive power capability test performed by OMPA was for 15 minutes and not for one hour as required by MOD-025-2 Attachment 1, verification specifications for applicable Facilities, p. 2.1.1. The 15 minute Reactive Power capability test was performed and the results transmitted to the OMPA Transmission Planner (TP) on April 28, 2016. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through September 16, 2016, the date OMPA transmitted the results of a one hour Reactive Power capability test performed on September 10, 2016, (MOD-025 Attachment 2) to its TP. The root cause of this instance of noncompliance was a combination of human error and insufficient oversight to ensure adherence to MOD-025-2 R2.1. OMPA staff incorrectly assumed reactive power capability testing performed to comply with Southwest Power Pool Criteria 12.1.6 would fulfill the testing requirements of MOD-025-2. Further, OMPA did not have controls in place to ensure the accuracy and completeness of information transmitted to its TP. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate long-term decisions affecting the reliability of the BPS. Notwithstanding OMPA’s failure to perform its reactive power capability test in accordance with Attachment 1, it did perform a reactive power capability test, but for a shorter test period, and provided the results of the test to its TP. Additionally, the Charles D. Lamb Energy Center is a 103 MW peaking facility that operates infrequently, having a capacity factor of .05. No actual harm is known to have occurred as a result of this noncompliance. SPP RE reviewed OMPA’s violation history and determined that it has no prior instances of noncompliance with MOD-025 or a similar standard. | To mitigate this minimal risk instance of noncompliance, OMPA: (1) completed a reactive power capacity verification test in accordance with the requirements of MOD-025-2 Attachment 1; (2) delivered the test results to its Transmission Planner in accordance with MOD-025-2 R2.2; and, (3) performed an internal review of the requirements of the MOD-025-2 standard and required its NERC consultant to review MOD-025-2 submittals for accuracy and completeness. SPP RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | American Electric Power Service Corp as agent for AEP Texas North Co, AEP Texas Central Co, and Public Service of Oklahoma (AEPSC) | NCR04006 | TRE2016016204 | PRC-005-2(i) | R3 | On September 26, 2016, AEPSC submitted a Self-Report to Texas RE after receiving notice of an upcoming Compliance Audit stating that, as a Transmission Owner, it had discovered multiple instances of noncompliance with PRC-005-2(i) R3. In particular, AEPSC did not maintain 14 communications Protection Systems in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed in PRC-005-2(i), Table 1-2. Texas RE subsequently determined the duration of this issue was from October 1, 2015 until May 2, 2017. Based upon a review of evidence, Texas RE subsequently determined that AEPSC failed to completely mitigate all of its maintenance and testing issues until May 2, 2017. Accordingly, Texas RE determined that AEPSC had an issue with PRC-005-2(i) R3 from October 1, 2015 until December 31, 2015. AEPSC then had an issue with PRC-005-6 R3 from January 1, 2016 until May 2, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in AEPSC’s compliance obligations under the applicable PRC-005 versions at issue. PRC-005-2(i), Table 1-2 requires entities to verify the functionality of unmonitored communications systems every four months. Pursuant to PRC-005-2(i)’s implementation plan, entities must perform all required four-month verifications by October 1, 2015. In December 2015, AEPSC discovered during an internal review that it had not performed the required four-month testing on 11 unmonitored communications systems. On June 3, 2016, AEPSC completed this required testing. Subsequently, in November 2016, AEPSC performed an additional assessment of its substation Protection Systems. During this second review, AEPSC identified three additional unmonitored communications systems that had not undergone the required four-month testing. On May 2, 2017, AEPSC performed the required four-month testing activities on the two additional unmonitored communications systems, ending the issue. The root cause of these noncompliance instances was an insufficient process to transition all applicable Protection Systems to the new PRC-005-2(i) maintenance and testing intervals. In particular, the unmonitored communications devices at issue were not previously subject to defined maintenance and testing intervals in AEPSC’s prior Protection System Maintenance and Testing Programs (PSMPs). As a result, AEPSC personnel did not identify these unmonitored communications systems as Protection Systems subject to periodic maintenance and testing requirements in AEPSC’s new Protection System tracking database for PRC-005-2(i). The issue started on October 1, 2015, when AEPSC failed to complete all maintenance and testing activities required under PRC-005-2(i) R3 for 14 communications systems, and ended on May 2, 2017, when AEPSC completed testing on the last communication system at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the communication devices at issue only represent approximately 2% of the communication systems and 0.06% (14/25,190) of the total Protection System devices in AEPSC’s PSMP. Second, AEPSC did not identify any issues with the communication devices when it performed the required testing. Finally, there were no misoperations at any of the locations at issue during the noncompliance period. No harm is known to have occurred. Texas RE considered AEPSC’s and its affiliates’ PRC-005 compliance history in determining the disposition track. AEPSC’s relevant prior noncompliance includes three issues with versions of PRC-005 (TRE2015015416, TRE2012010184 and TRE201100300). In addition, AEPSC’s affiliates have four relevant prior noncompliances involving versions of PRC-005 (TRE2015015414, TRE2012011136, TRE2016015435, and TRE2016015454). Texas RE determined that these prior noncompliances should not serve as an aggravating factor because the root causes of these issues are distinguishable from the current issue. AEPSC Compliance History AEPSC’s prior issue pertaining to TRE2015015416 involved the incorrect entry of “in service” dates for two new devices into AEPSC’s PSMP. In particular, AEPSC personnel used the date AEPSC energized a substation rather than the date AEPSC actually installed the batteries and battery chargers as the initial “in service” date for the new battery and battery charger devices. AEPSC’s prior issue in TRE2012010184 involved the failure to perform all required maintenance activities for instrument transformers during its scheduled maintenance interval. The root cause was misunderstanding of staff of the revised maintenance and testing activities for such devices. In other regions (RF and SPP), AEP Generation did not perform testing on batteries as required (RFC2012010261, SPP2012010129). Finally, AEPSC’s prior issue in TRE201100300 involved AEPSC’s failure to test certain relays. The root cause was that asset tracking database included incorrect testing dates, relays not being properly inventoried, and trip testing paths that were lacking sufficient data. Other regions reported similar issues (SPP201100449, RFC201000668, SPP200900137). Affiliate Compliance History TRE2016015453 for TRENT (NCR04148) – This previous issue involved contractors failing to perform semi-annual required battery inspections in a timely manner. The root cause of this issue was that TRENT did not clearly articulate to the facility's new operations managers the resources and time needed to perform required maintenance and testing activities. As a result, the new operations managers did not adequately account for the length of time required to complete the requisite inspections, including the amount of time required to procure contractors to perform them. This issue was mitigated by providing outreach sessions and training regarding the importance of planning for completing protection system testing in appropriate timeframes, including manpower and availability issues. TRE2016015454 for Desert Sky (NCR04050) – This previous issue involved contractors failing to perform semi-annual required battery inspections in a timely manner. The root cause of this issue was that Desert Sky did not clearly articulate to the facility's new operations managers the resources and time needed to perform required maintenance and testing activities. As a result, the new operations managers did not adequately account for the length of time required to complete the requisite inspections, including the amount of time required to procure contractors to perform them. This issue was mitigated by providing outreach sessions and training regarding the importance of planning for completing protection system testing in appropriate timeframes, including manpower and availability issues. TRE2015015414 for ETT (NCR10211) - This previous issue also involved ETT’s incorrect entry of “in service” dates for two new devices into ETT’s PSMP. In particular, ETT personnel used the date ETT energized a substation rather than the date ETT actually installed the batteries and battery chargers as the initial “in service” date for the new battery and battery charger devices. TRE2012011136 for ETT (NCR10211) - This previous issue involved the failure to perform all required maintenance activities for instrument transformers during its scheduled maintenance interval. The root cause was misunderstanding of staff of the revised maintenance and testing activities for such devices. In contrast to these prior issues, AEPSC’s current issue involves the failure to identify Protection System devices that were not previously subject to defined maintenance and testing intervals and ensure that they were tested according to the new maximum maintenance intervals set forth in PRC-005-2(i). In addition, AEPSC identified the current maintenance and testing issues during the process of instituting mitigating activities in connection with TRE2015015416 and TRE2015015414 associated with enhancing its processes for reviewing assets in its new PRC-005-2(i) Protection System tracking database. | To mitigate this issue, AEPSC: 1) performed all required maintenance and testing activities on the communication devices at issue; 2) entered the communication devices in the new PRC-005 maintenance and testing database; 3) cross-checked the communication systems listed in its PRC-005 database with the list of circuits, associated drawings and device settings to ensure all database information accurately reflected field conditions; 4) developed an internal spot check data review procedure for new assets; 5) developed and began using a checklist to ensure that new devices are appropriately entered into its PRC-005 maintenance and testing database; and 6) created a new database report and import process to ensure all current assets in the database are populated with the appropriate PRC-005 attributes. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Electric Transmission Texas, LLC (ETT) | NCR10211 | TRE2016016205 | PRC-005-2(i) | R3 | On September 26, 2016, American Electric Power Service Corp as agent for ETT submitted a Self-Report stating that, as a Transmission Owner (TO), it had discovered multiple instances of noncompliance with PRC-005-2(i) R3. In particular, ETT did not maintain ten communications Protection Systems in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed in PRC-005-2(i), Table 1-2. Texas RE subsequently determined the duration of this issue was from October 1, 2015 until February 10, 2017. Accordingly, Texas RE determined that ETT had an issue with PRC-005-2(i) R3 from October 1, 2015 until December 31, 2015. ETT then had an issue with PRC-005-6 R3 from January 1, 2016 until February 10, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in ETT’s compliance obligations under the applicable PRC-005 versions at issue. PRC-005-2(i), Table 1-2 requires entities to verify the functionality of unmonitored communications systems every four months. Pursuant to PRC-005-2(i)’s implementation plan, entities must perform all required four-month verifications by October 1, 2015. In December 2015, ETT discovered during an internal review that it had not performed the required four-month testing on eight unmonitored communications systems. On May 18, 2016, ETT completed this required testing. Subsequently, in November 2016, ETT performed an additional assessment of its substation Protection Systems. During this second review, ETT identified two additional unmonitored communications systems that had not undergone the required four-month testing. On February 10, 2017, ETT performed the required four-month testing activities on the two additional unmonitored communications systems, ending the issue. The root cause of these noncompliance instances was an insufficient process to transition all applicable Protection Systems to the new PRC-005-2(i) maintenance and testing intervals. In particular, the unmonitored communications devices at issue were not previously subject to defined maintenance and testing intervals in ETT’s prior Protection System Maintenance and Testing Programs (PSMPs). As a result, ETT personnel did not identify these unmonitored communications systems as Protection Systems subject to periodic maintenance and testing requirements in ETT’s new Protection System tracking database for PRC-005-2(i). The issue started on October 1, 2015, when ETT failed to complete all maintenance and testing activities required under PRC-005-2(i) R3 for ten communication systems, and ended on February 10, 2017, when ETT completed testing on the last communication system at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the communication devices at issue only represent approximately 5% of the communication systems and 0.12% (10//7748) of the total Protection System devices in ETT’s PSMP. Second, ETT did not identify any issues with the communication devices when it performed the required testing. Finally, there were no misoperations involving the devices at issue during the noncompliance period. No harm is known to have occurred. Texas RE considered ETT’s and its affiliates’ PRC-005 compliance history in determining the disposition track. ETT’s relevant prior noncompliance includes two issues with versions of PRC-005 (TRE2015015414 and TRE2012011136). In addition, ETT’s affiliates have five relevant prior noncompliances involving versions of PRC-005 (TRE2016015435, TRE2016015454, TRE2015015416, TRE2012010184, and TRE201100300). Texas RE determined that these prior noncompliances should not serve as an aggravating factor because the root causes of these issues are distinguishable from the current issue. ETT Compliance History ETT’s prior issue pertaining to TRE2015015414 involved the incorrect entry of “in service” dates for two new devices into ETT’s PSMP. In particular, ETT personnel used the date ETT energized a substation rather than the date ETT actually installed the batteries and battery chargers as the initial “in service” date for the new battery and battery charger devices. ETT’s prior issue in TRE2012011136 involved the failure to perform all required maintenance activities for instrument transformers during its scheduled maintenance interval. The root cause was misunderstanding of staff of the revised maintenance and testing activities for such devices. Affiliate Compliance History TRE2016015453 for TRENT (NCR04148) – This previous issue involved contractors failing to perform semi-annual required battery inspections in a timely manner. The root cause of this issue was that TRENT did not clearly articulate to the facility's new operations managers the resources and time needed to perform required maintenance and testing activities. As a result, the new operations managers did not adequately account for the length of time required to complete the requisite inspections, including the amount of time required to procure contractors to perform them. This issue was mitigated by providing outreach sessions and training regarding the importance of planning for completing protection system testing in appropriate timeframes, including manpower and availability issues. TRE2016015454 for Desert Sky (NCR04050) – This previous issue involved contractors failing to perform semi-annual required battery inspections in a timely manner. The root cause of this issue was that Desert Sky did not clearly articulate to the facility's new operations managers the resources and time needed to perform required maintenance and testing activities. As a result, the new operations managers did not adequately account for the length of time required to complete the requisite inspections, including the amount of time required to procure contractors to perform them. This issue was mitigated by providing outreach sessions and training regarding the importance of planning for completing protection system testing in appropriate timeframes, including manpower and availability issues. TRE2015015416 for AEPSC (NCR04006) – This previous issue involved the incorrect entry of “in service” dates for two new devices into AEPSC’s PSMP. In particular, AEPSC personnel used the date AEPSC energized a substation rather than the date AEPSC actually installed the batteries and battery chargers as the initial “in service” date for the new battery and battery charger devices. TRE2012010184, RFC2012010261, SPP2012010129 for AEPSC (NCR04006, NCR00682, NCR01056) – This previous issue involved the failure to perform all required maintenance activities for instrument transformers during its scheduled maintenance interval. The root cause was misunderstanding of staff of the revised maintenance and testing activities for such devices. In other regions (RF and SPP), AEP Generation did not perform testing on batteries as required. TRE201100300, SPP201100449, RFC201000668, SPP200900137 for AEPSC (NCR04006, NCR00682, NCR01056) - This previous violation was that AEPSC did not test some of its relays. The root cause was that asset tracking database included incorrect testing dates, relays not being properly inventoried, and trip testing paths that were lacking sufficient data. In contrast to these prior issues, ETT’s current issue involves the failure to identify Protection System devices that were not previously subject to defined maintenance and testing intervals and ensure that they were tested according to the new maximum maintenance intervals set forth in PRC-005-2(i). In addition, ETT identified the current maintenance and testing issues during the process of instituting mitigating activities in connection with TRE2015015414 and TRE2015015416 associated with enhancing its processes for reviewing assets in its new PRC-005-2(i) Protection System tracking database. | To mitigate this issue, ETT: 1) performed all required maintenance and testing activities on the communication devices at issue; 2) entered the communication devices in the new PRC-005 maintenance and testing database; 3) cross-checked the communication systems listed in its PRC-005 database with the list of circuits, associated drawings and device settings to ensure all database information accurately reflected field conditions; 4) developed an internal spot check data review procedure for new assets; 5) developed and began using a checklist to ensure that new devices are appropriately entered into its PRC-005 maintenance and testing database; and 6) created a new database report and import process to ensure all current assets in the database are populated with the appropriate PRC-005 attributes. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Keechi Wind, LLC (KWLLC) | NCR11497 | TRE2017017009 | PRC-019-2 | R1 | On February 12, 2017, KWLLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, KWLLC did not coordinate its voltage regulating system controls with applicable equipment capabilities and settings of the applicable Protection System devices and functions for its single generation Facility by July 1, 2016, as required. Following discussions with other registered entities in August 2016, KWLLC determined that as a GO with a single generation Facility, it was required to verify the coordination of its voltage regulating system controls with applicable equipment capabilities and settings of the applicable Protection System devices and functions by July 1, 2016. Following this recognition, KWLLC began the process of identifying and retaining a third-party contractor to perform the necessary verifications. On February 14, 2017, KWLLC secured a third-party contractor to perform the required verification work. This contract then completed the requisite verifications for KWLLC’s single generation Facility on June 16, 2017, ending the issue. The root cause of this issue was a misunderstanding of the required date for KWLLC to complete the initial voltage coordination verifications specified under PRC-019-2. In particular, KWLLC mistakenly believed that because it only owned a single generation Facility, it did not need to perform the required verifications until July 1, 2019, the date entities are required to be 100% compliant with the PRC-019-2 Standard requirements. The issue started on July 1, 2016, when PRC-019-2 became enforceable, and ended on June 16, 2017, when KWLLC verified the coordination of its voltage and generation protection settings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following four reasons. First, when KWLLC performed the required voltage and generation protection verifications through a coordination study, the study confirmed that no changes were required to the single generation Facility’s voltage controls and generation protection settings. Second, during the period of noncompliance, KWLLC contributed an average of only 52 MW to the grid and operated at approximately a 47% capacity factor. Third, KWLLC experienced frequency excursions less than one percent of the time during the period of noncompliance. Fourth, when KWLLC operated during the period of noncompliance, no trips occurred due to inadequate coordination. No harm was known to have occurred. Texas RE considered KWLLC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, KWLLC: 1) verified the coordination of its voltage controls and generation protection devices; 2) created a series of automated PRC-019 compliance reminders to notify the appropriate staff members of the next PRC-019 deadline at least one year in advance of the required verification date; and 3) notified affected personnel of this new PRC-019-2 compliance process. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | TRE2017017526 | PRC-005-1 | R2; R2.1 | On May 5, 2017, Oncor submitted a Self-Report stating that, as a Distribution Provider (DP) and Transmission Owner (TO), it had discovered multiple instances of noncompliance with PRC-005-1 R2.1. In particular, Oncor failed to provide evidence that certain Protection System devices were maintained and tested within the defined intervals included in its Protection System Maintenance Program (PSMP). Based upon a review of evidence, Texas RE subsequently determined that Oncor failed to completely mitigate all of its maintenance and testing issues until November 22, 2016. Accordingly, Oncor likewise was in noncompliance with PRC-005-1a R2.1, PRC-005-1b R2.1, and PRC-005-1.1b R2.1. Texas RE further determined that, for purposes of this matter, there was no substantive change in Oncor’s compliance obligations under all applicable PRC-005 versions. Oncor organizes a number of its Protection System maintenance and testing activities by panel. Specifically, Oncor’s panels typically include four types of Protection System components: relays, communications systems, voltage and current sensing devices, and dc control circuitry. Prior to adopting its current PSMP, Oncor performed the required maintenance and testing on these Protection System components by classifying each panel based upon its voltage level and technology type. In March 2016, Oncor discovered an issued with its panel classifications and corresponding testing intervals for the Protection Systems associated with those panels while performing upgrades at one of its substations. Specifically, Oncor determined that its personnel had incorrectly classified two 345 kV solid state panels containing eight total Protection System devices as 345 kV microprocessor panels. Oncor’s then-current PSMP established a 60-month testing interval for 345 kV solid state panels. Oncor previously tested the two panels at issue on February 6, 2008. As such, Oncor should have performed the next maintenance and testing activity on the Protections Systems associated with those two panels on February 6, 2013. However, Oncor determined that because of the panel misclassification, it did not in fact perform all required testing activities on the two panels at issue until April 11, 2014. Following the discovery of this panel classification issue, Oncor performed an extent of condition review in conjunction with its ongoing activities to transition its PSMP to PRC-005-6. During this process, Oncor determined that it had also misclassified an additional nine panels containing 51 total Protection System components at various substations. The earliest testing date at issue was for a 138 kV solid state panel. Oncor’s then-current PSMP established a 48-month testing interval for 138 kV solid state panel types. Oncor previously tested the particular 138 kV panel at issue on September 18, 2006. As such, Oncor should have performed the next maintenance and testing activity on the Protections Systems associated with this panel on September 18, 2010. However, Oncor determined that because of the panel misclassification, it did not in fact perform all required testing activities on this particular 138 kV solid state panel until January 19, 2012. Oncor discovered similar testing issues with the other panels, completing all required maintenance and testing activities on the last panel at issue on November 22, 2016. The root cause of this issue was that Oncor lacked a process to ensure that all devices/panels were correctly classified in its internal tracking system. In particular, Oncor lacked a process to verify that the panel classification information entered into its maintenance and testing tracking system matched the actual panel type in the field. The issue began on September 18, 2010, the first date Oncor missed a maintenance interval, and ended on November 22, 2016, the date Oncor performed the required maintenance and testing in accordance with the applicable version of its PSMP on the Protection System devices associated with the panels at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, this issue involved only 0.9% (59/6819) of Oncor’s Protection System devices. Second, Oncor did not identify any issues with the Protection System devices in question when it performed the required testing. Third, there were no misoperations involving the devices at issue during the noncompliance period. Finally, Oncor performed monthly station inspections and routine patrols at each of the substations at issue, which could have detected Protection System issues through observations of monitoring lights, annunciators, and circuit breaker and air switch inspections. No harm is known to have occurred. Texas RE considered Oncor’s and its affiliates’ PRC-005 R2.1 compliance history in determining the disposition track. Oncor’s relevant compliance history includes three prior issues with versions of PRC-005 (TRE2015015045, TRE201100459, and TRE201000280) Texas RE determined that these prior noncompliances should not serve as an aggravating factor because the root causes of the previous instance are distinguishable from the current issue. The prior issue pertaining to TRE2015015045 involved several root causes, including Oncor’s failure to properly enter prior testing dates in its maintenance and testing tracking tool, using outdated reports to track its maintenance due dates, issues with clearly identifying device locations, and incorrectly identifying an autotransformer as a distribution transformer in the system that issues work orders for BPS maintenance. The prior noncompliance pertaining to TRE201100459 involved the improper closure of a work order prior to testing the applicable Protection Systems and creating new work orders with incorrect maintenance due dates, as well as erroneously identifying a single battery as a non-Oncor asset and therefore not subject to Oncor's maintenance and testing program. Finally, TRE201000280 pertained to 23 relay systems that were not tested within the appropriate intervals because Oncor personnel entered incorrect benchmark dates for initial testing. Since the benchmark date establishes the starting point for maintenance intervals, the work-order triggers were inappropriately extended beyond the required date. In the current issue, Oncor improperly classified panels and their associated Protection System devices. As such, although Oncor personnel correctly entered prior testing dates and device locations, Oncor did not establish correct testing intervals for the specific devices at issue because of the panel classification issue. Further, the current issue does not involve the use of outdating tracking programs addressed in previous mitigating activities. Affiliate Compliance History TRE201000272, TRE201000273, and TRE201000274 for Big Brown (NCR10217), LGC (NCR10219), and Tradinghouse (NCR10220) – In the previous instance, the affiliates failed to test all relays and instrument transformers in their Protection System Maintenance and Testing Program because the TO had been previously responsible for protection system maintenance in the switchyard. Additionally, the affiliates operated under separate compliance responsibilities than Oncor. | To mitigate this issue, Oncor: 1) performed all required maintenance and testing activities on the devices at issue; 2) updated its internal databases to reflect the correct panel classifications for the devices at issue; 3) reviewed all protection system panels by querying and cross-referencing its internal database with relay drawings of all BES panel locations to ensure the proper classification of all panel types; 4) ensured that the correct maintenance plan was identified for devices still under PRC-005-1b by performing a query on the internal database; 5) implemented a process that requires technicians to verify and document that the panel asset information is correct when performing maintenance on all required devices; and 6) implemented a new PSMP consistent with PRC-005-6 that will eliminate panel classifications as a basis for maintenance intervals and instead test all panels on a fixed six-year cycle upon full implementation. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Stephens Ranch Wind Energy (SRWE) | NCR11507 | TRE2017017474 | MOD-025-2 | R1 | On April 27, 2017, SRWE submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R1. Specifically, SRWE failed to verify the Real Power capability of 40 percent of its applicable Facilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. In February 2017, SRWE determined that it had not completed the required Real Power capability verifications for 40 percent of its applicable Facilities by the July 1, 2016 deadline. SRWE then made arrangements to perform the required Real Power capability verifications, completing this testing on February 28, 2017. On April 25, 2017, SRWE then submitted the completed Real Power capability verifications for its two generating Facilities to its TP as required, ending the issue. The root cause was an inadequate process to ensure compliance with all aspects of newly applicable NERC Reliability Standards. In particular, SRWE lacked a dedicated compliance manager at the time of the issue and, as a result, did not properly identify the need to submit additional Real and Reactive Power capability verifications beyond what had previously been required under existing region-specific requirements. The issue started on July 1, 2016, the effective date of MOD-025-2, and ended on April 25, 2017, when SRWE submitted its completed Real Power capability verification for 40 percent of its generation Facilities in accordance with MOD-025-2, Attachment 1 to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, SRWE provided previously passing Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SRWE provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator in June 2016, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, the two SRWE wind Facilities at issue have a combined name capacity of 376 MW and each Facility operated only at approximately a 39% capacity factor during the issue period. As a result, any errors in the Facilities’ Real output data would only have a minor impact on planning results. No harm was known to have occurred. Texas RE considered SRWE’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SRWE: 1) performed the verification testing of its Real Power capability for both of its generation units; 2) submitted its Real Power capability verification results to its TP; 3) hired a new Director of NERC Compliance, tasked with responsibility for ensuring compliance with NERC Reliability Standards, including the Real and Reactive Power capability tests associated with MOD-025-2; 4) retained additional staff to aid in the implementation of SRWE’s ICP; and 5) established meeting reminders to perform Real and Reactive Power capability testing at both 1-year and 6 months in advance of the next required testing date. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Stephens Ranch Wind Energy (SRWE) | NCR11507 | TRE2017017575 | MOD-025-2 | R2 | On May 17, 2017, SRWE submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R2. Specifically, SRWE failed to verify the Reactive Power capability of 40 percent of its applicable Facilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. In February 2017, SRWE determined that it had not completed the required Reactive Power capability verifications for 40 percent of its applicable Facilities by the July 1, 2016 deadline. SRWE then made arrangements to perform the required Reactive Power capability verifications, completing this testing on February 28, 2017. On April 25, 2017, SRWE then submitted the completed Reactive Power capability verifications for its two generating Facilities to its TP as required, ending the issue. The root cause was an inadequate process to ensure compliance with all aspects of newly applicable NERC Reliability Standards. In particular, SRWE lacked a dedicated compliance manager at the time of the issue and, as a result, did not properly identify the need to submit additional Real and Reactive Power capability verifications beyond what had previously been required under existing region-specific requirements. The issue started on July 1, 2016, the effective date of MOD-025-2, and ended on April 25, 2017, when SRWE submitted its completed Reactive Power capability verification for 40 percent of its generation Facilities in accordance with MOD-025-2, Attachment 1 to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, SRWE provided previously passing Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, SRWE provided information similar to the required Reactive Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, the two SRWE wind Facilities at issue have a combined name capacity of 376 MW and each Facility operated only at approximately a 39% capacity factor during the issue period. As a result, any errors in the Facilities’ Reactive output data would only have a minor impact on planning results. No harm was known to have occurred. Texas RE considered SRWE’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SRWE: 1) performed the verification testing of its Reactive Power capability for both of its generation units; 2) submitted its Reactive Power verification testing results to its TP; 3) hired a new Director of NERC Compliance, tasked with responsibility for ensuring compliance with NERC Reliability Standards, including the Real and Reactive Power capability tests associated with MOD-025-2; 4) retained additional staff to aid in the implementation of SRWE’s ICP; and 5) established meeting reminders to perform Real and Reactive Power capability testing at both 1-year and 6 months in advance of the next required testing date. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Texas Reliability Entity (Texas RE) | Victoria WLE LP (VWLE) | NCR04159 | TRE2017017007 | PRC-019-2 | R1 | On February 13, 2017, VWLE submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. Specifically, VWLE did not coordinate its voltage regulating system controls with the applicable equipment capabilities and settings of Protection System devices and functions by July 1, 2016 as required. On June 1, 2016, VWLE acquired a single generation Facility. Upon completing this acquisition, however, VWLE recognized that the previous owner had not taken steps to perform the coordination of its voltage controls and generation protection devices by the July 1, 2016 deadline established for PRC-019-2. Over the next few months, VWLE took steps to retain a third-party contractor to perform the necessary coordination verification study. On November 16, 2016, VWLE completed the required voltage coordination and generation protection coordination, ending the issue. The root cause of this noncompliance was that VWLE did not possess adequate processes for ensuring compliance with all applicable NERC Reliability Standards upon acquisition of the Facility at issue. In particular, VWLE did not have a process to verify that the previous owners had taken the necessary steps to comply with PRC-019’s voltage and generation protection coordination requirements by the July 1, 2016 deadline. The issue started on July 1, 2016, when PRC-019-2 became enforceable, and ended on November 16, 2016, when VWLE verified the coordination of its voltage and generation protection settings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following five reasons. First, when VWLE performed the required voltage and generation protection verifications through a coordination study, the study confirmed that no changes were required to the single generation Facility’s voltage controls and generation protection settings. Second, during the period of noncompliance, VWLE contributed an average of 150 MWs and operated at a 51% capacity factory. Third, VWLE experienced frequency excursions less than one percent of the time during the period of noncompliance. Fourth, when VWLE operated during the period of noncompliance, no trips occurred due to inadequate coordination. Finally, the duration of the issue was relatively short, lasting approximately 4.5 months. No harm is known to have occurred. Texas RE considered VWLE’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, VWLE: 1) verified the coordination of its voltage controls and generation protection devices; 2) hired a compliance manager for the Facility at issue; 3) implemented an internal compliance program for the Facility at issue; 4) began implementing a Compliance Management System which will allow VWLE to track compliance deadlines, including upcoming voltage and generation protection device coordination verifications; and 5) implemented a documented procedure addressing all PRC-019-2 verification requirements. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Malaga Power, LLC (MLGP) | NCR11542 | WECC2017017001 | PRC-019-2 | R1; R1.1; R1.1.1; R1.1.2 | On February 14, 2017, MLGP submitted a Self-Report stating that, as a Generator Owner, it was in noncompliance with PRC-019-2 R1. Specifically, MLGP reported that it failed to verify coordination of voltage regulating system controls with the equipment capabilities and settings for the applicable Protection System devices and functions for at least 40 percent of its applicable Facilities by the enforcement date of the Standard. The cause of this noncompliance was an error in calculating the enforcement date of the Standard. Specifically, MLGP incorrectly calculated the enforcement date as the first day of the first calendar quarter, two years following applicable regulatory approval of Version 2 of the Standard. This calculation should have been made from the applicable regulatory approval date of version 1. WECC determined that this noncompliance began on July 1, 2016, when PRC-019-2 became mandatory and enforceable for 40 percent of MLGP’s applicable Facilities, and is currently ongoing. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, MLGP failed to verify coordination of at least 40 percent of its applicable Facilities in accordance with Requirement 1 by the effective date of the Standard. Such failure could result in the loss of the generator field, system instability, slipping poles, and/or damage to the turbines. However, MLGP’s Facilities have not experienced a trip or loss while operating live or during automatic voltage regulator testing. This noncompliance concerns two 60.5MW units and no harm is known to have occurred. For these reasons, WECC determined that this noncompliance posed a minimal risk to the reliability of the BPS. MLGP does not have any prior noncompliance with this Standard and Requirement. | To remediate and mitigate this noncompliance, MLGP will by September 29, 2017: 1) Complete the PRC-019 Limiter/Protection Coordination Study and make and coordination related changes if necessary; 2) create a tracking spreadsheet to monitor compliance deadlines and the status for responsible parties; 3) create automated Preventative Maintenance work orders that escalate tasks until they are completed in MLGP’s Company Obligation Tracking System; and 4) create automated Gensuite notifications that will prompt Plant Management to conduct quarterly reviews of future NERC Reliability Standards and Implementation Plans to ensure compliance prior to their enforcement dates.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Valley Electric Association, Inc (VEA) | NCR05447 | WECC2016016648 | PER-003-1 | R2; R2.2 | On December 9, 2016, VEA submitted a Self-Report stating that, as a Transmission Operator, it was in noncompliance with PER-003-1 R2. Specifically, VEA reported that one of its System Operators failed to renew their NERC Reliability Operator Certificate before it expired and continued to perform Real-time Transmission Operator reliability-related tasks. The cause of this noncompliance was human error. The Operator failed to ensure that they successfully renewed their certificate prior to exiting NERC’s System Operator Certification and Continuing Education Database. WECC determined that this noncompliance began on November 11, 2016, when the System Operator’s NERC certificate expired, through March 23, 2017, when it completed its mitigation activity. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, VEA failed to continuously staff each of its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have maintained a valid NERC certificate. A System Operator’s failure to demonstrate competency in transmission operations, emergency preparedness and operations, system operations, protection and control, and voltage and reactive power control by maintaining a valid NERC certificate could result in the inability for VEA to ensure that its System Operators are competent to perform Real-Time, BES reliability-related tasks. However, the System Operator completed all of their required Continuing Education Hours for the year and has held their NERC certification since 2011. Additionally, they attempted to renew their certificate prior to its expiration date but were unsuccessful due to an expired credit card. No harm is known to have occurred. For these reasons, WECC determined that this noncompliance posed a minimal risk to the reliability of the BPS. VEA does not have any prior noncompliance with this Standard and Requirement. | To remediate and mitigate this noncompliance, VEA: 1) renewed the System Operators NERC Reliability Operators Certificate; and 2) sent a reminder email to all VEA System Operators to renew their NERC Certificates early and verify that the renewal has been processed prior to the expiration date.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Cowlitz County PUD No. 1 (COWPD) | NCR05123 | WECC2016016708 | PRC-005-2(i) | R3 | On December 22, 2016, COWPD submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it was in noncompliance with PRC-005-2(i) R3. Specifically, COWPD reported that on December 8, 2016, during an inspection of its Protection System Maintenance Program (PSMP), COWPD discovered that it failed to perform the minimum maintenance activities within the maximum maintenance intervals for two communication assisted relays as prescribed in Table 1-2. The causes of this noncompliance were 1) a less than adequate process to ensure maintenance activities for newly commissioned relays are entered into its maintenance tracking software correctly; and 2) a less than adequate process to ensure the communication LED light was properly set up to test and verify communication. WECC determined that this noncompliance began on July 1, 2016, when completion of the 4-month maintenance activity for the two relays was due, and ended on December 13, 2016, when COWPD completed the maintenance activities prescribed in Table 1-2, for a total of 165 days of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, COWPD failed to perform the minimum maintenance activities within the maximum maintenance intervals for two communication assisted relays as prescribed in Table 1-2. Such failure could potentially result in degradation of equipment, the misoperation of the associated Protection System devices, resulting in the loss of one 115 kV line. However, the likelihood of the risk occurring was reduced by the controls COWPD had implemented. Specifically, both relays are programmed to noncompliance a Supervisory Control and Data Acquisition (SCADA) alarm in the event of a loss of communication. COWPD monitors its SCADA alarms, 24 hours a day, 7 days a week. Additionally, if a fault occurred, COWPD’s bus scheme would allow the bus and transformer to separate in order to protect the equipment. Further, the line in scope is not a WECC Major Transfer Path, does not contain Bulk Electric System generation, and is not associated with any minor scheduled transfer path. No harm is known to have occurred. For these reasons, WECC determined that this noncompliance posed a low likelihood of causing minor harm, and therefore, was a minimal risk to the reliability of the BPS. WECC reviewed COWPD’s compliance history and determined that COWPD does not have relevant prior noncompliance with PRC-005. COWPD took voluntary corrective action to remediate and mitigate this noncompliance. WECC considered these factors in its designation of this remediated noncompliance as a CE. | To mitigate this noncompliance, COWPD: 1) completed the required 4-month maintenance activities for the two relays as prescribed in Table 1-2; 2) corrected the programming noncompliance in its device maintenance tracking software to properly list the communication channel functional verification on future 4-month interval maintenance work orders; 3) programmed and tested front-panel custom LED and labeled both SEL 311C relays to indicate communication failures; 4) created a master list of all COWPD’s BES components, including a list of required maintenance, as outlined in COWPD’s PSMP; and 5) performed a thorough audit of all compliance documentation to verify all test and maintenance dates of its Protection System components as required by PRC-005.
2017-08-31 | Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2017017202 | VAR-002-4 | R3 | On March 6, 2017, PGE submitted a Self-Report stating that, as a Generator Operator, it was in noncompliance with VAR-002-4 R3. Specifically, PGE reported that on October 20, 2016, while performing testing and tuning studies of its Carty Generating Station (Carty) the Plant's power system stabilizers (PSS) were placed into service. That same day, during a review of the Carty Generating Station’s SharePoint compliance-related database, PGE discovered that it failed to notify its Transmission Operator (TOP) within 30 minutes of one power system stabilizer (PSS) status change. The cause of this noncompliance was PGE’s plant operation personnel’s failure to follow its documented procedures, in turn, missing the step requiring them to notify the System Control Center (SCC) staff of the PSS status change. SCC staff is responsible for notifying the TOP of any PSS status changes. WECC determined that this noncompliance began on October 20, 2016 at 5:00 a.m., 30 minutes after PGE implemented the PSS status change without notifying its TOP, and ended at 3:53 p.m., when PGE notified its TOP of the status change of the PSS, for approximately 11 hours of noncompliance. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, PGE failed to notify its Transmission Operator of one PSS status change within 30 minutes of that change. Such failure could result in the TOP not including the PSS status for the generating Facility in its Operating Plan and Real-Time Assessment, potentially delaying scheduled outages, running other generation out of economics, or cause other excessive pre-contingent actions to be taken. However, PGE’s SCC staff was aware that testing was being conducted during the three days preceding the noncompliance period and on heightened alert to detect any changes in the generator output. PGE’s failure to provide timely notification of the new PSS going into service did not significantly reduce situational awareness by the TOP. Additionally, PGE had a detective control, its compliance related database, that allowed its personnel to identify and correct the noncompliance in a timely manner. Carty is a 559MW gas-fired, combined cycle power plant. No harm is known to have occurred. For these reasons, WECC determined that this noncompliance had a low likelihood of causing minor harm, and posed a minimal risk to the reliability of the BPS. WECC notes that PGE has identified and Self-Reported this noncompliance described herein, took voluntary corrective action to remediate and mitigate this noncompliance, and has provided WECC documentation of its internal compliance program. For these reasons, WECC considers PGE’s compliance history a factor in its designation of this remediated noncompliance as a CE. WECC also considered PGE’s VAR-002 compliance history in determining the disposition track. PGE’s prior noncompliance with VAR-002 R3 includes NERC noncompliance ID WECC2014013851. The prior noncompliance does not have the same or similar cause as the current noncompliance. The cause of the prior noncompliance was due to a configuration error that caused PGE’s audio and visual alarm to malfunction. Thus, the operator was not notified when the PSS had not been activated. For these reasons, WECC determined that PGE’s VAR-002 compliance history should not serve as an aggravating factor in its disposition determination. | To mitigate this noncompliance, PGE: 1) informed the TOP of the PSS status change; and 2) developed a Supplemental PSS Notifications Training and trained all Carty plant operations personnel on the plant-specific procedure for reporting AVR and PSS status changes.
2017-07-31 | Florida Reliability Coordinating Council (FRCC) | Beaches Energy Services (BES) | NCR00004 | FRCC2017017488 | PRC-002-2 | R1 (Part 1.2) | On May 1, 2017, BES submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-002-2, R1 Part 1.2. The issue began on September 30, 2016, when BES failed to notify Florida Power and Light (FPL) within 90-calendar days that the Sampson substation 230 kV bus had been identified as requiring Sequence of Events Recording data and/or Fault Recording data as required by the Standard. This data is required for long-term stability studies. The violation ended on January 19, 2017, when BES made the appropriate notification to Florida Power and Light (112 days late). The root cause for this violation was a failure to insert the 90-day notification alert into BES' internal control, the BES Work Plan Calendar. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BES' failure to notify other owners connected to the identified 230kV buses could have caused FPL installation delays; thus, impacting future reliability and/or stability in the area. The risk was reduced because the actual installation is not due for another six years (per the Standard Implementation Plan), and no events occurred during the 112 day noncompliance period. No harm is known to have occurred. FRCC considered BES' PRC-002-2 R1 compliance history in determining the disposition track and it should not serve as a basis for applying a penalty. | To mitigate this issue, BES: notified FPL upon discovery To prevent recurrence, BES: updated their internal controls by adding implementation requirements associated with PRC-002-2 to the Work Plan Calendar and review them during its internal compliance meetings which are held every two weeks/twice a month.
2017-07-31 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2017016773 | VAR-002-4 | R3 | On December 16, 2016, NSP submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R3. Specifically, NSP did not report a change in a generation unit's Automatic Voltage Regulator (AVR) to its Transmission Operator (TOP) in a timely fashion. On October 19, 2016, at 10:10 a.m., there was an issue with the Arc Net system and the AVR switched to manual mode. A communication fault alarm activated at the same time that the AVR manual alarm activated. The generation operator acknowledged both alarms, but did not recognize that the AVR status had changed, and did not notify the TOP that the AVR was in manual mode. Approximately 25 minutes later, the generation operator adjusted the voltage to maintain the assigned voltage schedule. Immediately thereafter, the generation operator requested support from a technician. The technician quickly recognized that the AVR was in manual mode, then the generation operator returned the AVR to automatic, and then the generation operator notified the TOP at 10:51 a.m. Operation personnel promptly reported the issue to the Xcel Energy NERC Compliance staff who determined that the AVR was in manual mode for 41 minutes. The cause of this issue was a lack of awareness that caused the incorrect identification and clearing of the AVR manual alarm. The generation operator had reduced awareness regarding this issue as result of infrequent AVR status alarm activations, coupled with a history of more frequent communication fault alarm activations that have been previously cleared without incident. The issue began on October 19, 2016, at 10:41 a.m., when the TOP was not notified within 30 minutes, and ended 10 minutes later when the TOP was notified. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The generation operator was actively monitoring the voltage and maintained the proper voltage schedule by making manual adjustments. Further, the duration of the noncompliance was only 11 minutes. Additionally, the generation unit only has a nameplate rating of 195.6 MVA, is not a blackstart unit, and its associated substation is not part of an IROL. Finally, the issue was immediately recognized by operations staff and promptly reported to compliance staff, which is indicative of a strong culture of compliance. No harm is known to have occurred. | To mitigate this issue, NSP: 1) returned the AVR to automatic and notified its TOP; 2) identified the three other generating units with the Arc Net system and conducted additional training for those generation operators; and 3) shared the lessons learned from this noncompliance with all other generation facilities. NSP stated that mitigating activities were complete as of December 9, 2016.
2017-07-31 | Northeast Power Coordinating Council (NPCC) | Noble Bliss Windpark, LLC | NCR10271 | NPCC2017017751 | PRC-024-2 | R2. | On June 19, 2017, Noble Bliss Windpark, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R2. Specifically, the Entity failed to implement voltage relay settings that would ensure that its generator voltage protective relaying does not trip its generating facilities within the "no trip zone" of PRC-024-2 Attachment 2. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on April 5, 2017, when the Entity implemented required voltage relay settings for its generating assets to ensure its compliance with the standard/requirement. The root cause of this instance of noncompliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to its dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its Bliss Windpark facility needed to be 100% compliant with the standard and requirement by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 23.2%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 100.5 MW, which is less than 5.2% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system voltage event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by implementing required voltage relay settings for its generating assets 2) will prevent a recurrence of similar instances of noncompliance by: a) adding a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) hiring, by end of August 2017, a consultant to provide on-going education, awareness, and assistance in its NERC compliance program.
2017-07-31 | Northeast Power Coordinating Council (NPCC) | Noble Wethersfield Windpark, LLC | NCR10368 | NPCC2017017731 | PRC-024-2 | R1. | On June 14, 2017, Noble Wethersfield Windpark, LLC ("the Entity") submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R1. Specifically, the Entity failed to implement frequency relay settings that would ensure that its generator frequency protective relaying does not trip its generating facilities within the "no trip zone" of PRC-024-2 Attachment 1. This noncompliance started on July 1, 2016, when the standard and requirement became enforceable, and ended on April 5, 2017, when the Entity implemented required frequency relay settings for its generating assets to ensure its compliance with the standard/requirement. The root cause of this instance of noncompliance was the Entity's lack of clear understanding of how the phased-in implementation plan for the Standards and Requirement would apply to its dispersed wind generating units. Upon consultation with an outside vendor, the Entity correctly concluded that its Wethersfield Windpark facility needed to be 100% compliant with the standard and requirement by July 1, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The capacity factor of the Entity's generation facility for the year 2016 was 24%, which is a direct result of the fact that wind-generated energy is often intermittent, as it relies on wind speed, air density and turbine characteristics, and cannot be easily dispatched. The rated capability of the Entity's Wind Farm generation is 126 MW, which is less than 6.5% of the NYISO's required Operating Reserve (approximately 1965 MW). Therefore, if this instance of noncompliance had caused the entire generating facility to trip unnecessarily during a system frequency event, the NYISO (the Entity's Planning Coordinator) would have been able to replace the lost capacity. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered the Entity's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, the Entity: 1) corrected the noncompliance by implementing required frequency relay settings for its generating assets 2) will prevent a recurrence of similar instances of noncompliance by: a) adding a calendar reminder to its V-Comply platform (a due-date tracking software) to review all applicable standards' effective dates and implementation plans on an annual basis, and b) hiring, by end of August 2017, a consultant to provide on-going education, awareness, and assistance in its NERC compliance program.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017016724 | COM-002-4 | R1 | On December 21, 2016, Consumers submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue of COM-002-4 R1. Consumers received BA responsibilities when those BA responsibilities were added to the JRO-00001 for COM-002-4 beginning in 2009. Following this addition of responsibilities, Consumers drafted a new Energy Supply Compliance Program (ESCP) procedure. This new procedure was approved, but only included compliance instructions for Generator Operators (GOPs) for COM-002-4 because the previous version of COM-002 in effect only applied to Consumers as a Transmission Operator (TOP) (At Consumers, a different business unit handles the TOP responsibilities and that business unit (Transmission & Regulatory Strategies) had its procedure accurately reflect that the COM-002-4 requirements now apply to Consumers as a TOP and as a BA. Both the TOP and GOP business units, however, did not update its procedures to specifically reflect that Consumers needed to maintain compliance for the BA portions of COM-002-4, R1 (specifically R1.5 and R1.6).) and GOP. This new procedure was inaccurate because it should have included compliance instructions for Consumers’ new BA responsibilities. To satisfy compliance with COM-002-4 which became effective July 1, 2016, Consumers’ procedure needed to state that as a BA, Consumers would develop documented communications protocols for its operating personnel that issue and receive Operating Instructions in accordance with COM-002-4 R1. Consumers’ procedures, however, did not have this component and did not reference Consumers’ BA obligations. This noncompliance involves the management practice of information management because Consumers did not have an effective process of ensuring new responsibilities were updated in its procedures. This lack of a process is a root cause of this noncompliance. Consumers’ personnel were also not aware that they needed to update Consumers’ procedures to include the new BA obligations. This issue started on July 1, 2016, when Consumers was required to comply with COM-002-4 R1 and ended on December 21, 2016, when Consumers revised its ESCP procedure to include Consumers new BA responsibilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that not following predefined communications protocols increases the possibility of miscommunication that could lead to action or inaction harmful to the reliability of the BPS because affected entities may be unaware of conditions that could threaten the reliability of their area. That risk is minimized here because Consumers has other longstanding policies and procedures in place that train and require operating personnel to follow documented communications protocols and to utilize three way communication when issuing & receiving operating instructions. These policies and procedures and the use of three way communication minimize the risk of miscommunications. Therefore, this is primarily a documentation issue as Consumers failed to timely update its procedure to include Consumers new BA communications responsibilities which are similar to the communication responsibilities Consumers already follows as a GOP and TOP. Additionally ReliabilityFirst notes at no time since COM-002-4 became enforceable on July 1, 2016 has Consumers acted in a BA capacity. Since 2009, MISO has functioned as Consumer’s BA and shares the BA activities with Consumers under JRO00001 for COM-002-4 R1.5 and R1.6. No harm is known to have occurred. ReliabilityFirst considered Consumers' COM-002 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Consumers: 1) updated its ESCP communications procedure to reflect the new BA responsibilities to end the noncompliance; 2) delivered training on the new procedure to all relevant personnel; 3) updated NERC Compliance Responsibilities to include steps for validating assignments and to evaluate readiness for new standards prior to the enforcement date of the new standards. This step will help prevent recurrence of this noncompliance as it will ensure Consumers is more prepared to comply with new standards prior to the enforcement date of the new standards; and 4) provided an awareness notification to all relevant compliance personnel of the revised ESCP communications procedure. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2017016725 | COM-002-4 | R2 | On December 21, 2016, Consumers submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue of COM-002-4 R2. Consumers received BA responsibilities when those BA responsibilities were added to the JRO-00001 for COM-002-4 beginning in 2009. Following this addition of responsibilities, Consumers drafted a new Energy Supply Compliance Program (ESCP) procedure. This new procedure was approved, but only included compliance instructions for Generator Operators (GOPs) for COM-002-4 because the previous version of COM-002 in effect only applied to Consumers as a Transmission Operator (TOP) (At Consumers, a different business unit handles the TOP responsibilities and that business unit (Transmission & Regulatory Strategies) had its procedure accurately reflect that the COM-002-4 requirements now apply to Consumers as a TOP and as a BA. Both the TOP and GOP business units, however, did not update its procedures to specifically reflect that Consumers needed to maintain compliance for the BA portions of COM-002-4, R1 (specifically R1.5 and R1.6).) and GOP. This new procedure was inaccurate because it should have included compliance instructions for Consumers’ new BA responsibilities. To satisfy compliance with COM-002-4 R2 which became effective July 1, 2016, Consumers’ needed to train its operating personnel on the communications protocols developed in COM-002-4 R1. Consumers’ procedures, however, did not reference Consumers’ BA obligations and did not conduct this training. This noncompliance involves the management practice of workforce management and information management because Consumers did not have an effective process of ensuring new responsibilities were updated in its procedures. This lack of a process is a root cause of this noncompliance. Consumers’ personnel were also not aware that they needed to update Consumers’ procedures to include the new BA obligations. This issue started on July 1 2016, when Consumers was required to comply with COM-002-4 R2 and ended on December 21, 2016, when Consumers revised its ESCP procedure to include Consumers new BA responsibilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that not following predefined communications protocols increases the possibility of miscommunication that could lead to action or inaction harmful to the reliability of the BPS because affected entities may be unaware of conditions that could threaten the reliability of their area. That risk is minimized here because Consumers has other longstanding policies and procedures in place that train and require operating personnel to follow documented communications protocols and to utilize three way communication when issuing & receiving operating instructions. These policies and procedures and the use of three way communication minimize the risk of miscommunications. Therefore, this is primarily a documentation issue as Consumers failed to timely update its procedure to include Consumers new BA communications responsibilities which are similar to the communication responsibilities Consumers already follows as a GOP and TOP. Additionally ReliabilityFirst notes, at no time since COM-002-4 became enforceable on July 1, 2016 has Consumers acted in a BA capacity. Since 2009, MISO has functioned as Consumer’s BA and shares the BA activities with Consumers under JRO00001 for COM-002-4 R1.5 and R1.6. No harm is known to have occurred. ReliabilityFirst considered Consumers' COM-002 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Consumers: 1) updated its ESCP communications procedure to reflect the new BA responsibilities to end the noncompliance and bring Consumers back into compliance; 2) delivered training on the new procedure to all relevant personnel; 3) updated NERC Compliance Responsibilities to include steps for validating assignments and to evaluate readiness for new standards prior to the enforcement date of the new standards. This step will help prevent recurrence of this noncompliance as it will ensure Consumers is more prepared to comply with new standards prior to the enforcement date of the new standards; and 4) provided an awareness notification to all relevant compliance personnel of the revised ESCP communications procedure. ReliabilityFirst has verified the completion of all mitigation activity.
2017-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016016352 | PRC-001-1.1(ii) | R3 | On October 6, 2016, PJM submitted a Self-Report stating that, as a Transmission Operator, it had an issue of PRC-001-1.1(ii) R3. The nature of the violation is that a relay settings change was not coordinated on a 345 kV transmission line between two member Transmission Owners within the PJM footprint: AEP and Duquesne Light Company (Duquesne). More specifically, as the result of an increase to the Winter Emergency rating of the Tidd-Collier 345 kV line, AEP performed a relay loadability evaluation and determined that the load-encroachment setting for this line should be changed to accommodate the new rating. This line is the point of interconnection with Duquesne. However, AEP failed to contact Duquesne regarding the change as required by PRC-001-1.1(ii) R3.2. On November 6, 2015, AEP applied the revised relay settings. AEP discovered the error in June 2016 during a subsequent relay loadability review on the line. As a result of this subsequent review, AEP again increased the load-encroachment setting, but, this time, coordinated the change with Duquesne. The root cause was lack of clear procedures regarding the need to coordinate load-encroachment settings. This cause involves the management practice of external interdependencies, which include mitigating risks associated with external interdependencies. This issue started on November 6, 2015, when the revised relay settings were applied and ended on June 14, 2016, when AEP coordinated a subsequent relay change with Duquesne. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Uncoordinated relay changes can create issues where facilities trip in unexpected ways or at unexpected times. Here, the original setting (prior to the violation occurring) would have constrained loadability and tripped sooner than what the line was rated, and thus the revised settings actually corrected the issue. And here, Duquesne was not required to make any changes to its system based on AEP’s revised setting, and thus the lack of coordination did not result in any increased risk to the BPS. Additionally, the Protection System coordination is based on the distance elements settings of the relay. The increased load-encroachment setting does not affect the distance element during fault conditions, and therefore did not impact the Protection System's ability to operate as intended during fault conditions. No harm is known to have occurred. ReliabilityFirst considered PJM's PRC-001 R3 compliance history in determining the disposition track. PJM’s relevant prior noncompliances with PRC-001 R3 include: a. RFC2013011659. A Settlement Agreement covering a violation of PRC-001-1 R3 was filed with FERC under NP14-28-000 on January 30, 2014. On February 28, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In the prior violation, in early 2012, AEP issued revised relay settings for a line that was an interconnection with FirstEnergy. The AEP engineer revising the settings failed to recognize the interconnection with FirstEnergy and thus did not notify FirstEnergy of the revised settings. The prior violation is distinguishable in that here, the engineer failed to follow the process to make proper notifications, whereas in the prior violation, the engineer failed to recognize an interconnection. b. RFC2016015941. A Compliance Exception addressing a noncompliance with PRC-001-1.1(ii) R3 was posted on the NERC website on February 28, 2017. The prior noncompliance is distinguishable from the current noncompliance. In the prior noncompliance, a newly integrated member TO failed to coordinate an increase to a relay setting without notifying PJM or neighboring entities. PJM discovered the noncompliance one week later. The prior noncompliance is distinguishable in that it involves conduct by different member TOs than the current noncompliance; the conduct is not recurring. ReliabilityFirst determined that PJM’s compliance history should not serve as a basis for applying a penalty | To mitigate this issue, PJM will ensure AEP completes the following mitigation activities by December 15, 2017: 1) revise AEP's protection system coordination guide to clarify the need to coordinate load-encroachment settings; 2) train AEP's protection engineers on revisions to the relay coordination; 3) execute a project to add functionality to AEP's asset database to ensure coordination of settings on interconnections; and 4) train AEP's protection engineers on the workflow changes within the asset tracking database. The proposed completion date will allow AEP time to train its engineers following completion of the database project.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Borger Energy Associates, LP (BOEA) | NCR01062 | SPP2016016287 | PRC-024-2 | R1 | On September 30, 2016, BOEA submitted a Self-Certification stating that, as a Generator Owner, it had an issue of noncompliance with PRC-024-2 R1. BOEA is a gas fired cogeneration power plant with two gas turbine generating units applicable to PRC-024-2. BOEA did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The duration of this instance of noncompliance was from July 1, 2016, the effective date of PRC-024-2, through January 23, 2017, the date BOEA completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new standard and requirement, and a lack of managerial oversight, ensuring adherence to the standard and requirement. BOEA site staff erroneously believed that the generation facility was in compliance with PRC-024-2 R2 after completing the Model Validation and Reactive Capability Testing for MOD-025, MOD-026, and MOD-027 during the fourth quarter of 2015 and 2016. Additionally, BOEA did not exercise corporate oversight of plant compliance activities. Onsite staff exclusively were responsible for compliance with all NERC standards, associated policies, and procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relays in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, BOEA is a gas-fired cogeneration power plant that contributes only 200 MW to the grid while operating, and is continuously controlled by plant operators who monitor system frequency. Additionally, BOEA attested that this generation facility has operated without experiencing any frequency, excitation system, or PRC-024 related issues since May 31, 2007, the commissioning date of the facility. Furthermore, BOEA verified that no changes were required to its protective relay settings. No harm is known to have occurred. SPP RE reviewed BOEA’s violation history and determined that BOEA has no prior instances of noncompliance with PRC-024. | To mitigate this minimal risk instance of noncompliance, BOEA: 1) completed its Relay/Limiter Coordination Study and verified that no changes were required to the generator frequency protective relay settings to meet the standard and requirement; and 2) hired a Director of Compliance to oversee compliance activities. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Borger Energy Associates, LP (BOEA) | NCR01062 | SPP2016016288 | PRC-024-2 | R2 | On September 30, 2016, BOEA submitted a Self-Certification stating that, as a Generator Owner, it had an issue of noncompliance with PRC-024-2 R2. BOEA is a gas fired cogeneration power plant with two gas turbine generating units applicable to PRC-024-2. BOEA did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of PRC-024-2, through January 30, 2017, the date BOEA completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was a combination of a lack of understanding of the new standard and requirement and a lack of managerial oversight, ensuring adherence to the standard and requirement. BOEA site staff erroneously believed that the generation facility was in compliance with PRC-024-2 R2 after completing the Model Validation and Reactive Capability Testing for MOD-025, MOD-026, and MOD-027 during the fourth quarter of 2015 and 2016. Additionally, BOEA did not exercise corporate oversight of plant compliance activities. Onsite staff exclusively were responsible for compliance with all NERC standards, associated policies, and procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, BOEA contributes only 200 MW to the grid while operating, and is continuously controlled by plant operators who monitor system voltage. Additionally, BOEA attested that this generation facility has operated without experiencing any voltage control, excitation system, or PRC-024 related issues since May 31, 2007, the commissioning date of the facility. Furthermore, BOEA verified that no changes were required to its protective relay settings. No harm is known to have occurred. SPP RE reviewed BOEA’s violation history and determined that BOEA has no prior instances of noncompliance with PRC-024. | To mitigate this minimal risk instance of noncompliance, BOEA: 1) conducted a Relay/Limiter Coordination Study and verified that no changes were required to the protective relay settings to meet the standard and requirement; 2) obtained approval from the Transmission Planner to continue operating with current voltage settings; and 3) hired a Director of Compliance to oversee compliance activities. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Tex-La Electric Cooperative of Texas, Inc (TEXLA) | NCR01342 | SPP2015015227 | PRC-006-1 | R9 | During a Compliance Audit conducted September 9 - 10, 2015, the SPP RE Audit Team determined that TEXLA, as a Transmission Owner and Distribution Provider, was in violation of PRC-006-1 R9 because it did not provide for the automatic tripping of load in accordance with the Underfrequency Load Shed (UFLS) Plan established by the Southwest Power Pool Planning Coordinator (SPP PC). Section 5.0 – UFLS Program > 100MW of the SPP PC UFLS Plan states: Each UFLS entity that has a total forecasted peak Load greater than or equal to 100 MW will develop and implement an automatic UFLS program that meets the following requirements: • A minimum of 10% will be shed at each UFLS step in accordance with the data as follows: UFLS Step 1 - Frequency (hertz): 59.3, Minimum accumulated load relief as percentage of forecasted peak Load: 10%, Maximum accumulated load relief as percentage of forecasted peak Load: 25% UFLS Step 2 - Frequency (hertz): 59.0, Minimum accumulated load relief as percentage of forecasted peak Load: 20%, Maximum accumulated load relief as percentage of forecasted peak Load: 35% UFLS Step 3 - Frequency (hertz): 58.7, Minimum accumulated load relief as percentage of forecasted peak Load: 30%, Maximum accumulated load relief as percentage of forecasted peak Load: 45% • The intentional relay time delay for UFLS will be less than or equal to 30 cycles. • There is no minimum total clearing time (relay operating time + breaker trip time). • Undervoltage inhibit setting will be less than or equal to 85% of nominal voltage. UFLS entities may implement an aggregated UFLS program with other UFLS entities. The 100 MW limit refers to the aggregated plan, if one exists. During the audit, TEXLA provided the Audit Team with the UFLS inventory that was submitted to the SPP PC on January 8, 2015 (2014 UFLS Inventory) in compliance with the SPP PC UFLS Plan. The Audit Team observed that the total UFLS inventory identified by TEXLA was 26.88% of its total load and did not meet the 20% and 30% minimum accumulated load relief required by steps 2 and 3 of the SPP UFLS Plan. Upon further investigation it was discovered that the total UFLS inventory identified by TEXLA in 2015 was 25.97% of its total load and did not meet the 20% and 30% minimum accumulated load relief required by step 2 and 3 of the SPP UFLS Plan. SPP RE determined that TEXLA failed to provide automatic tripping of load in accordance with the UFLS program design and schedule for application as determined by the SPP PC. The violation began on October 1, 2013, the date PRC-006-1 became mandatory and enforceable, and ended on February 16, 2017, the date TEXLA completed verification of the load shed by its UFLS relays. The root cause of TEXLA’s violation of PRC-006-1 R9 was failure to inform its member cooperatives of the requirements to maintain a UFLS program and a lack of internal controls to ensure its member cooperatives were following the UFLS guidelines established in the SPP PC UFLS Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failure to comply with the minimum requirements of the regional PC’s UFLS program increases the potential risk that the regional response to an underfrequency event will be insufficient to halt the collapse of the bulk electric system following the loss of generation resources. Although TEXLA was not complying with the SPP PC’s UFLS Program, the TEXLA system is small (less than 130 MW), with a total UFLS load shed of approximately 38 MW or less than 1% of the SPP regional UFLS load shed inventory. The TEXLA UFLS 2015 inventory included 33.3 MW or 86% of the total requirement and the load dispersion across the SPP PC UFLS Plan steps was 13.4 MW for step 1, 8 MW for step 2, and 11.9 MW for step 3. Only 4.28 MW and 5.2 MW of additional load shed for steps 2 and 3, respectively, would have been required to comply with the SPP PC UFLS Program. No actual harm is known to have occurred as a result of this noncompliance. No previously filed violations of the same or similar reliability standards or requirements were identified. | To mitigate this minimal risk instance of noncompliance, TEXLA: 1) redesigned its UFLS program based upon load data collected from its member cooperatives; 2) installed new UFLS relays or modified existing UFLS relays to comply with the SPP PC UFLS Plan; 3) conducted a Fall and Winter test of the UFLS relays; 4) implemented an agenda item for discussion of the UFLS program at its annual member meeting to increase program awareness; 5) implemented an annual review of member cooperative load data to ensure compliance with the SPP PC UFLS Plan; and, 6) implemented an annual UFLS test to be performed before the SPP PC UFLS data request to validated program compliance. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE - Kansas City District (COEKS) | NCR01357 | SPP2016016251 | MOD-025-2 | R1; R1.1, R1.2 | On September 30, 2016, COEKS submitted a Self-Certification stating that, as a Generator Owner (GO), it had an issue of noncompliance with MOD-025-2 R1.1. The Implementation Plan for MOD-025-2 states that 40% of applicable units must be tested and verified by July 1, 2016. COEKS has six applicable generating units at the Harry S. Truman hydroelectric plant and one applicable generating unit at the Stockton hydroelectric generating plant. COEKS did not verify the Real Power capability of 40% 4/7) of the units by the implementation date and as a result, COEKS was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of the applicable generating units at the Truman and Stockton plants. The root cause of this instance of noncompliance was COEKS’ error in calculating the effective date of MOD-025-2. The NERC website shows July 1, 2016 as the effective date for MOD-025-2. The Implementation Plan for MOD-25-2 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” COEKS erroneously used July 1, 2016 as the “regulatory approval” date and calculated two years forward (July 1, 2018) as the effective date for MOD-25-2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of MOD-025-2 through September 29, 2016, the date COEKS completed mitigation activities for this issue of noncompliance. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate decisions affecting the reliability of the BPS. Notwithstanding, the Real Power capability of the COEKS’s generators has historically been provided to its TOP, BA and Planning Coordinator to support development of the planning models. Truman has six 27 MW generating units, and Stockton has one 52 MW generating unit which have minimal impact on the BPS. No harm is known to have occurred. COEKS has no relevant prior violations for MOD-025-2 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, COEKS: 1) verified the Real Power capability of 40% of the applicable generating units at the Harry S. Truman and Stockton plants and provided verification thereof to its TP; and 2) included a schedule in the maintenance management program that will initiate review and verification of the Real Power capability on a four year cycle, to be completed by the five year interval. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE - Kansas City District (COEKS) | NCR01357 | SPP2016016252 | MOD-025-2 | R2; R2.1, R2.2 | On September 30, 2016, COEKS submitted a Self-Certification stating that, as a Generator Owner (GO), it had an issue of noncompliance with MOD-025-2 R2.1. The Implementation Plan for MOD-025-2 states that 40% of applicable units must be tested and verified by July 1, 2016. COEKS did not verify the Reactive Power capability of six generating units at the Harry S. Truman hydroelectric generating plant (Truman), and one generating unit/synchronous condenser at the Stockton hydroelectric generating plant (Stockton) in accordance with MOD-025-2 Attachment 1. As a result, COEKS was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of the applicable generating units at the Truman and Stockton plants. The root cause of this instance of noncompliance was COEKS’s error in calculating the effective date of MOD-25-2. The NERC website shows July 1, 2016 as the effective date for MOD-25-2. The Implementation Plan for MOD-25-2 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” COEKS erroneously used July 1, 2016 as the “regulatory approval” date and calculated two years forward (July 1, 2018) as the effective date for MOD-25-2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of MOD-025-2, through September 29, 2016, the date COEKS completed mitigation activities for this issue of noncompliance. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Noncompliance with MOD-025-2 creates the potential for the Transmission Planner (TP) to have inaccurate or incomplete information regarding the capabilities of the generating units and synchronous condensers in its planning area. Notwithstanding, the Reactive Power capability of COEKS's generators and synchronous condenser has historically been provided to its Transmission Operator, Balancing Authority, and Planning Coordinator to support development of the planning models. COEKS states that its hydroelectric facilities are rarely called upon to provide Reactive Power and when called upon, the demand does not approach the machine limits. Truman has six 27 MW generating units capable of generating approximately 15 MVAR each, Stockton has one 52 MW generator/synchronous condenser capable of producing approximately 22 MVAR; all of which have minimal impact on the BPS. No harm is known to have occurred. COEKS has no relevant prior violations for MOD-025-2 or any other standards that are similar in nature to this instance of noncompliance | To mitigate this minimal risk instance of noncompliance, COEKS: 1) verified Reactive Power capability of applicable generating units at the Harry S. Truman and Stockton plants and provided verification thereof to its TP; and 2) included a schedule in the maintenance management program that will initiate review and verification of the settings on a four year cycle, to be completed by the five year interval. SPP RE has verified the completion of all mitigation activity.
2017-07-31 | Texas Reliability Entity (Texas RE) | Bobcat Bluff Wind Project, LLC (BBWP) | NCR11320 | TRE2016016522 | IRO-010-1a | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that BBWP, as a Generator Operator (GOP), had an issue with IRO-010-1a R3. BBWP did not provide data and information, as specified, to its Reliability Coordinator (RC) with which it had a reliability relationship. Specifically, BBWP did not provide the status of its Automatic Voltage Regulator (AVR) for a single generation unit via telemetry as specified by its RC. Electric Reliability Council of Texas (ERCOT) Nodal Protocol § 3.15.3(4) requires certain generators in the ERCOT interconnection, including BBWP, to provide their AVR status to its RC via telemetry on a continuous basis. Beginning on February 7, 2013, BBWP telemetered an offline AVR status to its RC even though the AVR was online and operational. Upon discovering the issue during the Compliance Audit, BBWP determined that an issue with its telemetry logic caused its AVR status to occasionally become inverted. On September 13, 2016, BBWP corrected its AVR telemetry coding, ending the issue. The root cause of the issue was that BBWP did not have a sufficient process to ensure its AVR status was being correctly telemetered to its RC. Specifically, BBWP did not have a process in place to review telemetered data provided by the entity responsible for submitting such information to its RC, as well as checks to validate that data against its generating unit’s actual operating status. This issue began on February 7, 2013, when BBWP provided the first incorrect AVR status to its RC, and ended on September 13, 2016, when BBWP corrected the AVR status telemetry it sent to its RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, throughout the duration of the issue, BBWP’s generation unit’s AVR remained in service and would have likely operated to mitigate any voltage excursions that could impact the Bulk Electric System (BES) from generator disturbances. Second, the single generation unit at issue was small, with a nameplate rating of 150 MW and only an average output of 45 MW in 2016. As a result, the single wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. Third, BBWP did not experience any trips or other issues related to voltage excursions during the noncompliance periods. Finally, BBWP’s telemetry issues were limited in scope. In particular, BBWP is required to telemeter 36 data points under its applicable RC data specifications and the single AVR data point only represents 2.77% of BBWP’s overall telemetry obligations. No harm is known to have occurred. Texas RE considered BBWP’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BBWP: 1) corrected the AVR status telemetry it sent to its RC. Furthermore, BBWP will complete the following actions by September 29, 2017: 1) amend its service agreement to provide BBWP personnel with access to ICCP data provided to its RC by its third-party scheduling entity; 2) create a process to actively monitor its plant AVR status and ensure that status is accurately telemetered; and 3) institute alarms to notify operating personnel if the plant’s AVR status differs from the AVR status being telemetered to its RC.
2017-07-31 | Texas Reliability Entity (Texas RE) | Bobcat Bluff Wind Project, LLC (BBWP) | NCR11320 | TRE2016016521 | VAR-002-3 | R2; R2.3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that Bobcat Bluff Wind Project, LLC (BBWP), as a Generator Operator (GOP), had an issue with VAR-002-3 R2.3. In particular, BBWP neither monitored its voltage at the location specified in its voltage schedule nor possessed a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point it actually monitored. Texas RE subsequently determined that the duration of this issue was from October 1, 2014 until June 1, 2016. Accordingly, Texas RE determined that BBWP had an issue with VAR-002-3 R2.3 from October 1, 2014 until May 28, 2015. BBWP then had an issue with VAR-002-4 R2.3 from May 29, 2015 until June 1, 2016. Texas RE further determined that, for purposes of this issue, there was no substantive change in BBWP’s compliance obligations under the applicable versions. BBWP’s previous voltage schedule specified that BBWP will monitor voltage at its Point of Interconnection (POI). During the issue in question, however, BBWP instead monitored its voltage output at the high side of its step-up transformer. BBWP further lacked a methodology for converting the scheduled voltage to the point actually being monitored. The root cause of this issue was an inadequate process to ensure compliance with all applicable requirements in VAR-002 R2. Specifically, BBWP personnel did not sufficiently understand the requirement to monitor voltage at its designated voltage point or develop a conversion methodology. This issue started on October 1, 2014, when VAR-002-3 R2.3 became enforceable, and ended on June 1, 2016, when the TOP issued a new voltage schedule for BBWP that provided that BBWP may also monitor voltage at the high side of its step-up transformer, as well as at the POI. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, BBWP did not deviate from its voltage schedule during the duration of the voltage monitoring issues in question. Second, Texas RE did not identify any unintended voltage controlling actions by the TOP that were related to BBWP not monitoring its voltage at the designated point in its voltage schedule or any trips or outages caused by BBWP’s failure to maintain its voltage output. Third, BBWP provided examples demonstrating instances when it was instructed by its local TOP to modify voltage. In these instances, BBWP was either able to successfully meet its local TOP’s request or was able to provide adequate notification that it could not modify its voltage. Finally, the generation Facility at issue is small, with a nameplate rating of 150 MW and only an average output of approximately 45 MW in 2016. As a result, the single wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These four elements further serve to reduce the risk to reliability while BBWP completes all required mitigation activities. No harm is known to have occurred. Texas RE considered BBWP’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BBWP: 1) received a new voltage schedule from its TOP specifying the high-side of its step-up transformer as a valid point of monitoring; 2) reconfigured its Energy Management System (EMS) to monitor voltage status at the POI in real time in addition to other designated voltage monitoring points; 3) created alarms to automatically alert its operating personnel of any voltage excursions in real time to further enhance awareness of voltage monitoring issues and responsibilities; 4) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel have adequate training regarding voltage control and monitoring issues; 5) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 6) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities, including monitoring voltage at the designated voltage points.
2017-07-31 | Texas Reliability Entity (Texas RE) | Cameron Wind I, LLC (CWI) | NCR11591 | TRE2017017697 | PRC-005-2(i) | R1 | On March 13, 2017, CWI submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3 relating to its failure to timely perform certain maintenance and testing activities for its single Valve Regulated Lead-Acid (VRLA) battery device. Subsequently, on June 2, 2017, Texas RE determined that the issue described in CWI's PRC-005-2(i) R3 Self-Report was also a noncompliance of PRC-005-2(i) R1. Specifically, CWI failed to establish a Protection System Maintenance and Testing Program (PSMP) for all of its Protection System devices. CWI's generation Facility has a single Valve Regulated Lead-Acid (VRLA) battery Protection System. During a compliance review, however, CWI determined that its PSMP failed to include such VRLA battery devices. CWI then amended its PSMP to include the required testing intervals and activities for VRLA batteries on November 6, 2016. The root cause of the issue was that CWI did not have adequate internal controls to ensure it properly included all applicable categories of Protection System devices within its PSMP. Specifically, CWI failed to include VRLA batteries in its PSMP because it mistakenly classified a single VRLA battery device as a Vented Lead-Acid (VLA) battery device. This issue started on November 6, 2015, when CWI registered as a GO and did not include VRLA batteries in its PSMP, and ended on November 2, 2016, when CWI updated its PSMP to include VRLA batteries. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following six factors. First, the issue involved only a single battery, which itself represents only 4% (1/25) of CWI’s total devices within its PSMP. Second, when CWI performed the required 4-month, 6-month, and 18-month testing activities for the single battery device in question, there were no issues found with the condition of the device. Third, CWI had been performing regular monthly testing on the single VRLA battery at issue since January 21, 2016. Fourth, throughout the period of noncompliance, the battery device was within the first year of use. Therefore, there was little risk of loss of capacity in the battery itself. Fifth, CWI’s battery system is partially monitored. Particularly, CWI’s control center receives alarms in response to issues with the DC control system. Finally, over the entire period of noncompliance, CWI produced an average of only 55.9 MW. No harm is known to have occurred. Texas RE considered CWI’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CWI: 1) updated its PSMP to include VRLA battery device Protection System maintenance and testing activities; 2) performed all required maintenance and testing activities on the single VRLA battery at issue; and 3) instituted regular, bi-monthly meetings with site operations staff to review ongoing compliance responsibilities, including a review of CWI’s PRC-005 PSMP and any associated maintenance/testing activities. Texas RE has verified the completion of all mitigation activity.
2017-07-31 | Texas Reliability Entity (Texas RE) | Cameron Wind I, LLC (CWI) | NCR11591 | TRE2017017222 | PRC-005-2(i) | R3 | On March 13, 2017, CWI submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3. In particular, CWI did not timely perform the required 4-month, 6-month, and 18-month maintenance and testing activities for a single Valve Regulated Lead-Acid (VRLA) battery device as required by PRC-005-2(i) R3, Table 1-4(b). CWI failed to perform the required testing for its VRLA battery device prior to registering as a GO on November 6, 2015. Specifically, CWI did not complete its initial 4-month testing requirements until January 21, 2016. Additionally, CWI failed to perform required 6-month and 18-month testing activities until November 30, 2016. The root cause of the issue was that CWI did not have adequate internal controls to ensure it properly identified all Protection System devices and then timely performed all required maintenance and testing on those devices. Specifically, CWI failed to include VRLA batteries in its PSMP because it mistakenly classified a single VRLA battery device as a VLA battery device. In addition, CWI failed to perform all initial required maintenance activities on the single VRLA battery device at issue. This issue started on November 6, 2015, when CWI registered as a GO and failed to perform prior testing of its VRLA battery device, and ended on November 30, 2016, when CWI completed all required VRLA battery testing activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following six factors. First, the issue involved only a single battery device, which itself represents only 4% (1/25) of CWI’s total devices within its PSMP. Second, when CWI performed the required 4-month, 6-month, and 18-month testing activities for the battery device in question, there were no issues found with the condition of the device. Third, CWI had been performing regular monthly testing on the single VRLA battery at issue since January 21, 2016. Fourth, throughout the period of noncompliance, the battery device was within the first year of use. Therefore, there was little risk of loss of capacity in the battery itself. Fifth, CWI’s battery system is partially monitored. Particularly, CWI’s control center receives alarms in response to issues with the DC control system. Finally, over the entire period of noncompliance, CWI produced an average of only 55.9 MW. No harm is known to have occurred. Texas RE considered CWI’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CWI: 1) updated its PSMP to include VRLA battery device Protection System maintenance and testing activities; 2) performed all required maintenance and testing activities on the single VRLA battery device at issue; 3) reviewed all other Protection System devices to confirm it possessed initial maintenance and testing records for those devices; and 4) instituted regular, bi-monthly meetings with site operations staff to review its ongoing compliance responsibilities, including a review of CWI’s PRC-005 PSMP and any associated maintenance and testing activities. Texas RE has verified the completion of all mitigation activity.
2017-07-31 | Texas Reliability Entity (Texas RE) | Longhorn Wind Project, LLC (LWPLLC) | NCR11503 | TRE2016016524 | IRO-010-1a | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that LWPLLC, as a Generator Operator (GOP), had an issue with IRO-010-1a R3. LWPLLC did not provide data and information, as specified, to its Reliability Coordinator (RC) with which it had a reliability relationship. Specifically, LWPLLC did not correctly provide the status of its Automatic Voltage Regulator (AVR) for a single generation unit via telemetry as specified by its RC. Electric Reliability Council of Texas (ERCOT) Nodal Protocol § 3.15.3(4) requires certain generators in the ERCOT interconnection, including LWPLLC to provide their AVR status to its RC via telemetry on a continuous basis. Beginning on September 18, 2015, LWPLLC telemetered an offline AVR status to its RC even though the AVR was online and operational. LWPLLC subsequently determined that in establishing the initial telemetry data points in preparation for bringing the single generation unit at issue into commercial operation, the initial AVR telemetry data point linked to a backup AVR unit rather than the generation unit’s primary AVR. Because LWPLLC’s was set to operate in manual mode, LWPLLC telemetered an offline AVR data point to its RC even though its primary AVR remained operational. The third-party entity responsible for submitting telemetered information to LWPLLC’s RC identified LWPLLC’s offline AVR status and requested LWPLLC investigate the issue. On October 8, 2015, LWPLLC identified the incorrect link to the backup AVR and corrected the issue, ending its AVR telemetry issues. The root cause of the issue was that LWPLLC did not have a sufficient process to ensure its AVR status was being correctly telemetered to its RC. Specifically, LWPLLC did not have a process in place to review telemetered data provided to its RC, as well as checks to validate that data against its generating unit’s actual operating status. This issue started on September 18, 2015, when LWPLLC provided the first incorrect AVR status to its RC, and ended on October 8, 2015, when LWPLLC corrected the AVR status telemetry it sent to its RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, throughout the duration of the issue, LWPLLC’s generation unit’s AVR remained in service and would have likely operated to mitigate any voltage excursions that could impact the Bulk Electric System (BES) from generator disturbances. Second, the single generation unit at issue was small, with a nameplate rating of 200 MW and only an average output of 87 MW in 2016. As a result, the single wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. Third, LWPLLC did not experience any trips or other issues related to voltage excursions during the noncompliance periods. Finally, LWPLLC’s telemetry issues were limited in scope. In particular, LWPLLC is required to telemeter 36 data points under its applicable RC data specifications and the single AVR data point only represents 2.77% of LWPLLC’s overall telemetry obligations. No harm is known to have occurred. Texas RE considered LWPLLC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LWPLLC: 1) corrected the AVR status telemetry it sent to its RC. Furthermore, LWPLLC will complete the following actions by September 29, 2017: 1) amend its service agreement to provide LWPLLC personnel with access to ICCP data provided to its RC by its third-party scheduling entity; 2) create a process to actively monitor its plant AVR status and ensure that status is accurately telemetered; and 3) institute alarms to notify operating personnel if the plant’s AVR status differs from the AVR status being telemetered to its RC.
2017-07-31 | Texas Reliability Entity (Texas RE) | Longhorn Wind Project, LLC (LWPLLC) | NCR11503 | TRE2016016523 | VAR-002-3 | R2; R2.3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that LWPLLC, as a Generator Operator (GOP), had an issue with VAR-002-3 R2.3. In particular, LWPLLC neither monitored its voltage at the location specified in its voltage schedule nor possessed a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point it actually monitored. Texas RE subsequently determined that the duration of this issue was from December 13, 2014 until June 1, 2016. Accordingly, Texas RE determined that LWPLLC had an issue with VAR-002-3 R2.3 from December 13, 2014 until May 28, 2015. LWPLLC then had an issue with VAR-002-4 R2.3 from May 29, 2015 until June 1, 2016. Texas RE further determined that, for purposes of this issue, there was no substantive change in LWPLLC’s compliance obligations under the applicable versions. LWPLLC’s previous voltage schedule specified that LWPLLC will monitor voltage at its Point of Interconnection (POI). During the issue in question, however, LWPLLC instead monitored its voltage output at the high side of its step-up transformer. LWPLLC further lacked a methodology for converting the scheduled voltage to the point actually being monitored. The root cause of this issue was an inadequate process to ensure compliance with all applicable requirements in VAR-002 R2. Specifically, LWPLLC personnel did not sufficiently understand the requirement to monitor voltage at its designated voltage point or develop a conversion methodology. This issue started on December 13, 2014, when LWPLLC registered as a GOP, and ended on June 1, 2016, when the TOP issued a new voltage schedule for LWPLLC that provided that LWPLLC may also monitor voltage at the high side of its step-up transformer, as well as at the POI. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, LWPLLC did not deviate from its voltage schedule during the duration of the voltage monitoring issues in question. Second, Texas RE did not identify any unintended voltage controlling actions by the TOP that were related to LWPLLC not monitoring its voltage at the designated point in its voltage schedule or any trips or outages caused by LWPLLC’s failure to maintain its voltage output. Third, there were no instances in which the TOP instructed LWPLLC to modify its voltage output. Finally, the generation Facility at issue was small, with a nameplate rating of 200 MW and only an average output of 87 MW in 2016. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These four elements further serve to reduce the risk to reliability while LWPLLC completes all required mitigation activities. No harm is known to have occurred. Texas RE considered LWPLLC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LWPLLC: 1) received a new voltage schedule from its TOP specifying the high-side of its step-up transformer as a valid point of monitoring; 2) reconfigured its Energy Management System (EMS) to monitor voltage status at the POI in real time in addition to other designated voltage monitoring points; 3) created alarms to automatically alert its operating personnel of any voltage excursions in real time to further enhance awareness of voltage monitoring issues and responsibilities; 4) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel have adequate training regarding voltage control and monitoring issues; 5) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 6) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities, including monitoring voltage at the designated voltage points.
2017-07-31 | Texas Reliability Entity (Texas RE) | Longhorn Wind Project, LLC (LWPLLC) | NCR11503 | TRE2017017937 | VAR-002-3 | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that certain LWPLLC affiliates, as Generator Operators (GOP), had issues with VAR-002-3 R3. Subsequently, on July 10, 2017, Texas RE Enforcement determined that LWPLLC, as a GOP, likewise had an issue with VAR-002-3 R3. Specifically, LWPLLC failed to notify its associated Transmission Operator (TOP) of status changes on its Automatic Voltage Regulators (AVR) within 30 minutes of each change. Texas RE further determined that the duration of this issue was from December 15, 2014 until November 24, 2015. Accordingly, Texas RE concluded that LWPLLC had an issue with VAR-002-3 R3 from December 15, 2014 until May 28, 2015. LWPLLC then had an issue with VAR-002-4 R3 from May 29, 2015 until November 24, 2015. Texas RE further determined that, for purposes of this issue, there was no substantive change in LWPLLC’s compliance obligations under the applicable versions. On December 15, 2014, LWPLLC returned its generation units to service with their AVRs offline. However, LWPLLC failed to inform its TOP of this AVR status change within 30 minutes as required. LWPLLC’s two AVRs remained offline until December 18 and December 19, 2014, respectively. Over the following months, LWPLLC experienced several other instances of AVR status changes but likewise failed to provide the required notifications to its TOP. Instead, LWPLLC continued to indicate that both its AVRs were online and operational at all relevant times. On November 24, 2015, LWPLLC returned its AVRs to online mode for the final time, ending the issue. The root cause of this issue was related to LWPLLC’s failure to establish adequate processes to identify AVR status changes and provide the required notifications to its TOP within 30 minutes of any such changes. Specifically, LWPLLC relied solely on its operating personnel to manually identify AVR status changes. Moreover, LWPLLC’s existing procedures did not provide clear instructions for identifying such status changes and providing the required notifications to its TOP. The issue started on December 15, 2014, the date of LWPLLC’s first failure to provide a notification to its TOP of an AVR status change, and ended on November 24, 2015, when LWPLLC restored its AVRs to service to match the AVR statuses provided to its TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, LWPLLC did not deviate from its voltage schedule during the duration of the AVR issues in question. Second, Texas RE did not identify any unintended voltage controlling actions by the TOP that were related to LWPLLC not providing timely AVR status information or any trips or outages caused by LWPLLC’s failure to maintain its voltage output. Third, there were no instances in which the TOP instructed LWPLLC to modify its voltage output. Finally, the generation Facility at issue was small, with a nameplate rating of 200 MW and only an average output of 87 MW in 2016. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These four elements further serve to reduce the risk to reliability while LWPLLC completes all required mitigation activities. No harm is known to have occurred. Texas RE considered LWPLLC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LWPLLC: 1) reconfigured its Energy Management System (EMS) to monitor AVR status in real time; 2) created alarms to automatically alert its operating personnel of any AVR status changes; 3) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel had adequate training regarding communications protocols and voltage control issues; 4) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 5) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities.
2017-07-31 | Texas Reliability Entity (Texas RE) | Spinning Spur Wind Three, LCC (SSW3) | NCR11575 | TRE2016016527 | IRO-010-1a | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that SSW3, as a Generator Operator (GOP), had an issue with IRO-010-1a R3. In particular, SSW3 did not provide data and information, as specified, to its Reliability Coordinator (RC) with which it had a reliability relationship. Specifically, SSW3 did not correctly provide the status of two Automatic Voltage Regulators (AVR) via telemetry as specified by its RC. Electric Reliability Council of Texas (ERCOT) Nodal Protocol § 3.15.3(4) requires certain generators in the ERCOT interconnection, including SSW3, to provide their AVR status to its RC via telemetry on a continuous basis. Beginning on October 30, 2015, and continuing on several occasions throughout 2015 and 2016, SSW3 telemetered an incorrect AVR statuses to its RC for two generation units. Upon discovering the issue during the Compliance Audit, SSW3 determined that an issue with its telemetry logic caused its AVR status to occasionally become inverted. This would, for instance, result in SSW3 telemetering an offline AVR status when the AVR was in fact online and operational. On September 13, 2016, SSW3 corrected its AVR telemetry coding, ending the issue. The root cause of the issue was that SSW3 did not have a sufficient process to ensure its AVR status was being correctly telemetered to its RC. Specifically, SSW3 did not have a process in place to review telemetered data provided by the entity responsible for submitting such information to its RC, as well as checks to validate that data against its generating unit’s actual operating status. This issue started on October 30, 2015, when SSW3 provided the first incorrect AVR status to its RC, and ended on September 13, 2016, when SSW3 corrected the AVR status telemetry it sent to its RC at both generation units at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the single generation unit at issue was small, with a nameplate rating of 194 MW and only an average output of 92 MW in 2016. As a result, the single wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. Second, SSW3 did not experience any trips or other issues related to voltage excursions during the noncompliance periods. Finally, SSW3’s telemetry issues were limited in scope. In particular, SSW3 is required to telemeter 36 data points under its applicable RC data specifications for each of the two generation units at issue. As such, the single AVR data point only represents 2.77% of SSW3’s overall telemetry obligations. No harm is known to have occurred. Texas RE considered SSW3’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SSW3: 1) corrected the AVR status telemetry it sent to its RC. Furthermore, SSW3 will complete the following actions by September 29, 2017: 1) amend its service agreement to provide SSW3 personnel with access to ICCP data provided to its RC by its third-party scheduling entity; 2) create a process to actively monitor its plant AVR status and ensure that status is accurately telemetered; and 3) institute alarms to notify operating personnel if the plant’s AVR status differs from the AVR status being telemetered to its RC.
2017-07-31 | Texas Reliability Entity (Texas RE) | Spinning Spur Wind Three, LCC (SSW3) | NCR11575 | TRE2016016525 | VAR-002-4 | R2; R2.3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that SSW3, as a Generator Operator (GOP), had an issue with VAR-002-4 R2.3. In particular, SSW3 neither monitored its voltage at the location specified in its voltage schedule nor possessed a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point it actually monitored. SSW3’s previous voltage schedule specified that SSW3 will monitor voltage at its Point of Interconnection (POI). During the issue in question, however, SSW3 instead monitored its voltage output at the high side of its step-up transformer. SSW3 further lacked a methodology for converting the scheduled voltage to the point actually being monitored. The root cause of this issue was an inadequate process to ensure compliance with all applicable requirements in VAR-002 R2. Specifically, SSW3 personnel did not sufficiently understand the requirement to monitor voltage at its designated voltage point or develop a conversion methodology. This issue started on September 3, 2015, when SSW3 registered as a GOP, and ended on June 1, 2016, when the TOP issued a new voltage schedule for SSW3 that provided that SSW3 may also monitor voltage at the high side of its step-up transformer, as well as at the POI. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, SSW3 did not deviate from its voltage schedule during the duration of the voltage monitoring issues in question. Second, Texas RE did not identify any unintended voltage controlling actions by the TOP that were related to SSW3 not monitoring its voltage at the designated point in its voltage schedule or any trips or outages caused by SSW3’s failure to maintain its voltage output. Third, SSW3 provided examples demonstrating instances when it was instructed by its local TOP to modify voltage. In these instances, SSW3 was either able to successfully meet its local TOP’s request or was able to provide adequate notification that it could not modify its voltage. Finally, the generation Facility at issue is small, with a nameplate rating of 194 MW and only an average output of 92 MW in 2016. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These four elements further serve to reduce the risk to reliability while SSW3 completes all required mitigation activities. No harm is known to have occurred. Texas RE considered SSW3’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SSW3: 1) received a new voltage schedule from its TOP specifying the high-side of its step-up transformer as a valid point of monitoring; 2) reconfigured its Energy Management System (EMS) to monitor voltage status at the POI in real time in addition to other designated voltage monitoring points; 3) created alarms to automatically alert its operating personnel of any voltage excursions in real time to further enhance awareness of voltage monitoring issues and responsibilities; 4) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel have adequate training regarding voltage control and monitoring issues; 5) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 6) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities, including monitoring voltage at the designated voltage points.
2017-07-31 | Texas Reliability Entity (Texas RE) | Spinning Spur Wind Three, LCC (SSW3) | NCR11575 | TRE2016016526 | VAR-002-4 | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that SSW3, as a Generator Operator (GOP), had an issue with VAR-002-4 R3. Specifically, SSW3 failed to notify its associated Transmission Operator (TOP) of status changes on its Automatic Voltage Regulators (AVR) within 30 minutes of each change. On September 10, 2015, SSW3 returned a single generation unit to service with its AVR offline. However, SSW3 failed to inform its TOP of this AVR status change within 30 minutes as required. Over the following months, SSW3 experienced several other instances of AVR status changes for both its AVRs but likewise failed to provide the required notifications to its TOP. Instead, SSW3 continued to indicate that both its AVRs were online and operational at all relevant times. On August 10, 2016, SSW3 returned its AVRs to online mode for the final time, ending the issue. The root cause of this issue was related to SSW3’s failure to establish adequate processes to identify AVR status changes and provide the required notifications to its TOP within 30 minutes of any such changes. Specifically, SSW3 relied solely on its operating personnel to manually identify AVR status changes. Moreover, SSW3’s existing procedures did not provide clear instructions for identifying such status changes and providing the required notifications to its TOP. This issue started on September 10, 2015, when SSW3 failed to inform its TOP of an AVR status change in the first instance, and ended on August 10, 2016, when SSW3 restored its AVRs to service in the last instance to match the AVR statuses provided to its TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, SSW3 did not deviate from its voltage schedule during the duration of the AVR issues in question. Second, Texas RE did not identify any unintended voltage controlling actions by the TOP that were related to SSW3 not providing timely AVR status information or any trips or outages caused by SSW3’s failure to maintain its voltage output. Third, SSW3 provided examples demonstrating instances when it was instructed by its local TOP to modify voltage. In these instances, SSW3 was either able to successfully meet its local TOP’s request or was able to provide adequate notification that it could not modify its voltage. Finally, the generation Facility at issue is small, with a nameplate rating of 194 MW and only an average output of 92 MW in 2016. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These four elements further serve to reduce the risk to reliability while SSW3 completes all required mitigation activities. No harm is known to have occurred. Texas RE considered SSW3’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SSW3: 1) reconfigured its Energy Management System (EMS) to monitor AVR status in real time; 2) created alarms to automatically alert its operating personnel of any AVR status changes; 3) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel had adequate training regarding communications protocols and voltage control issues; 4) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 5) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities.
2017-07-31 | Texas Reliability Entity (Texas RE) | Spinning Spur Wind Two (SSWT) | NCR11464 | TRE2016016530 | IRO-010-1a | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that SSWT, as a Generator Operator (GOP), had an issue with IRO-010-1a R3. In particular, SSWT did not provide data and information, as specified, to its Reliability Coordinator (RC) with which it had a reliability relationship. Specifically, SSWT did not provide the status of its Automatic Voltage Regulator (AVR) for a single generation unit via telemetry as specified by its RC. Electric Reliability Council of Texas (ERCOT) Nodal Protocol § 3.15.3(4) requires certain generators in the ERCOT interconnection, including SSWT, to provide their AVR status to its RC via telemetry on a continuous basis. Beginning on June 30, 2014, SSWT telemetered an incorrect AVR status to its RC for a single generation unit. In April 2016, SSWT identified issues with the AVR telemetry at its single generation Facility and changed the method with which it telemetered its AVR status, ending the violation on April 9, 2016. During the Compliance Audit, SSWT subsequently identified additional issues with its telemetry logic, which had also caused SSWT’s generation Facility to occasionally telemeter an inverted AVR status. In the current circumstances, this resulted in SSWT telemetering that its AVR was online and operational when it was in fact offline. On September 13, 2016, SSWT corrected its AVR telemetry coding to address these root cause issues. The root cause of the issue was that SSWT did not have a sufficient process to ensure its AVR status was being correctly telemetered to its RC. Specifically, SSWT did not have a process in place to review telemetered data provided by the entity responsible for submitting such information to its RC, as well as checks to validate that data against its generating unit’s actual operating status. This issue started on June 30, 2014, when SSWT provided the first incorrect AVR status to its RC, and ended on April 9, 2016, when SSWT corrected the AVR status telemetry it sent to its RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the single generation unit at issue was small, with a nameplate rating of 161 MW and only an average output of 69 MW in 2016. As a result, the single wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. Second, SSWT did not experience any trips or other issues related to voltage excursions during the noncompliance periods. Finally, SSWT’s telemetry issues were limited in scope. In particular, SSWT is required to telemeter 36 data points under its applicable RC data specifications and the single AVR data point only represents 2.77% of SSWT’s overall telemetry obligations. Texas RE considered SSWT’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SSWT: 1) corrected the AVR status telemetry it sent to its RC. Furthermore, SSWT will complete the following actions by September 29, 2017: 1) amended its service agreement to provide SSWT personnel with access to ICCP data provided to its RC by its third-party scheduling entity; 2) create a process to actively monitor its plant AVR status and ensure that status is accurately telemetered; and 3) institute alarms to notify operating personnel if the plant’s AVR status differs from the AVR status being telemetered to its RC.
2017-07-31 | Texas Reliability Entity (Texas RE) | Spinning Spur Wind Two (SSWT) | NCR11464 | TRE2016016528 | VAR-002-3 | R2; R2.3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that SSWT, as a Generator Operator (GOP), had an issue with VAR-002-3 R2 and R2.3. Specifically, SSWT did not maintain the generator voltage schedule provided by the Transmission Operator (TOP), or otherwise meet the conditions of notification for deviations from the voltage schedule provided by the TOP. In addition, SSWT neither monitored its voltage at the location specified in its voltage schedule nor possessed a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point it actually monitored. Texas RE subsequently determined that the duration of this issue was from October 1, 2014 until February 17, 2017. Accordingly, Texas RE determined that SSWT had an issue with VAR-002-3 R2 from October 1, 2014 until May 28, 2015. SSWT then had an issue with VAR-002-4 R2 from May 29, 2015 until February 17, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in SSWT’s compliance obligations under the applicable versions. Pursuant to Electric Reliability Council of Texas (ERCOT) Operating Guide 2.7.4.1(4), generators are required to maintain transmission system voltage within +/- 2.0% of their designated voltage profile while operating at less than their maximum reactive capabilities. Beginning on April 10, 2015, and continuing on several occasions from 2015 through 2017, SSWT’s voltage exceeded this +/- 2% voltage deviation tolerance. During the issue period, Texas RE determined that SSWT exceeded the required voltage deviation tolerance for 4.01% of its total operating time with the largest deviation of -4.10% occurring on May 6, 2015. Regarding SSWT’s issue with VAR-002-3 R2.3, Texas RE reviewed SSWT’s previous voltage schedule. This voltage schedule specified that SSWT will monitor voltage at its Point of Interconnection (POI). Beginning on October 1, 2014, however, SSWT instead monitored its voltage output at the high side of its step-up transformer. SSWT further lacked a methodology for converting the scheduled voltage to the point actually being monitored. On June 1, 2016, SSWT’s TOP issued a new voltage schedule designating that SSWT may also monitor voltage at the high side of its step-up transformer. The root cause of this issue was SSWT’s failure to establish adequate processes and controls in order to ensure compliance with VAR-002 R2. Specifically, SSWT relied solely on its operating personnel to manually identify voltage deviations, and the SSWT control room was not configured to actively monitor its voltage at its Point of Interconnection (POI) or produce an alarm on a voltage excursion. Moreover, SSWT’s existing procedures did not provide clear instructions for sufficiently understanding the requirement to monitor voltage at its designated voltage point or develop a conversion methodology, identifying voltage deviations, and taking appropriate responsive actions. This issue started on October 1, 2014, when VAR-002-3 R2.3 became enforceable, and ended on February 17, 2017, when the last recorded instance of SSWT exceeding its voltage schedule occurred. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, there were no instances in which the TOP instructed SSWT to modify its voltage output. Second, Texas RE did not identify any trips or outages caused by SSWT’s failure to maintain its voltage output or notify its TOP when it could not meet its voltage schedule. Third, the generation Facility at issue is small, with a nameplate rating of 161 MW and only an average output of 69 MW in 2016. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These three elements further serve to reduce the risk to reliability while SSWT completes all required mitigation activities. No harm is known to have occurred. Texas RE considered SSWT’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SSWT: 1) ceased voltage deviations beyond the +/-2.0% tolerance; 2) reconfigured its Energy Management System (EMS) to monitor voltage status at the POI in real time in addition to other designated voltage monitoring points; 3) created alarms to automatically alert its operating personnel of any voltage excursions in real time to further enhance awareness of voltage monitoring issues and responsibilities; 4) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel had adequate training regarding voltage control and monitoring issues; 5) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 6) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities, including maintaining SSWT’s voltage profile and monitoring voltage at the designated voltage points.
2017-07-31 | Texas Reliability Entity (Texas RE) | Spinning Spur Wind Two (SSWT) | NCR11464 | TRE2016016529 | VAR-002-3 | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that SSWT, as a Generator Operator (GOP), had an issue with VAR-002-3 R3. Specifically, SSWT failed to notify its associated Transmission Operator (TOP) of a status change on its Automatic Voltage Regulator (AVR) within 30 minutes of the change. Texas RE subsequently determined that the duration of this issue was from April 30, 2015 until September 6, 2015. Accordingly, Texas RE determined that SSWT had an issue with VAR-002-3 R3 from April 30, 2015 until May 28, 2015. SSWT then had an issue with VAR-002-4 R3 from May 29, 2015 until September 6, 2015. Texas RE further determined that, for purposes of this issue, there was no substantive change in SSWT’s compliance obligations under the applicable versions. On April 30, 2015, SSWT’s AVR status changed from online to offline. However, SSWT failed to notify its TOP of the AVR status change within 30 minutes of this AVR status change. SSWT’s AVR remained offline until September 6, 2015, when it returned to online and normal operating mode. The root cause of this issue was related to SSWT’s failure to establish adequate processes to identify AVR status changes and provide the required notifications to its TOP within 30 minutes of any such changes. Specifically, SSWT relied solely on its operating personnel to manually identify AVR status changes. Moreover, SSWT’s existing procedures did not provide clear instructions for identifying such status changes and providing the required notifications to its TOP. The issue started on April 30, 2015, the date of SSWT’s first failure to provide a notification to its TOP within 30 minutes of an AVR status change, and ended on September 6, 2015, when SSWT restored its AVR to service to match the AVR status provided to its TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, Texas RE did not identify any unintended voltage controlling actions by the TOP that were related to SSWT not providing timely AVR status information or any trips or outages caused by SSWT’s failure to maintain its voltage output. Second, there were no instances in which the TOP instructed SSWT to modify its voltage output. Finally, the single generation unit at issue was small, with a nameplate rating of 161 MW and only an average output of 69 MW in 2016. As a result, the single wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These three elements further serve to reduce the risk to reliability while SSWT completes all required mitigation activities. No harm is known to have occurred. Texas RE considered SSWT’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SSWT: 1) reconfigured its Energy Management System (EMS) to monitor AVR status in real time; 2) created alarms to automatically alert its operating personnel of any AVR status changes; 3) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel had adequate training regarding communications protocols and voltage control issues; 4) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 5) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities.
2017-07-31 | Texas Reliability Entity (Texas RE) | TX Hereford Wind, LLC (TXHWLLC) | NCR11495 | TRE2016016533 | IRO-010-1a | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that TXHWLLC, as a Generator Operator (GOP), had an issue with IRO-010-1a R3. TXHWLLC did not provide data and information, as specified, to its Reliability Coordinator (RC) with which it had a reliability relationship. Specifically, TXHWLLC did not correctly provide the status of its Automatic Voltage Regulator (AVR) for a single generation unit via telemetry as specified by its RC. Electric Reliability Council of Texas (ERCOT) Nodal Protocol § 3.15.3(4) requires certain generators in the ERCOT interconnection, including TXHWLLC, to provide their AVR status to its RC via telemetry on a continuous basis. Beginning on February 2, 2015, and continuing on several occasions throughout 2015 and 2016, TXHWLLC telemetered an incorrect AVR status to its RC for a single generation unit. Upon discovering the issue during the Compliance Audit, TXHWLLC determined that an issue with its telemetry logic caused its AVR status to occasionally become inverted. This would, for instance, result in TXHWLLC telemetering an “offline” AVR status when the AVR was in fact “online” and operational. On September 13, 2016, TXHWLLC corrected its AVR telemetry coding, ending the issue. The root cause of the issue was that TXHWLLC did not have a sufficient process to ensure its AVR status was being correctly telemetered to its RC. Specifically, TXHWLLC did not have a process in place to review telemetered data provided by the entity responsible for submitting such information to its RC, as well as checks to validate that data against its generating unit’s actual operating status. This issue started on February 2, 2015, when TXHWLLC provided the first incorrect AVR status to its RC, and ended on September 13, 2016, when TXHWLLC corrected the AVR status telemetry it sent to its RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the single generation unit at issue was small, with a nameplate rating of 200 MW and only an average output of 84 MW in 2016. As a result, the single wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. Second, TXHWLLC did not experience any trips or other issues related to voltage excursions during the noncompliance periods. Finally, TXHWLLC’s telemetry issues were limited in scope. In particular, TXHWLLC is required to telemeter 36 data points under its applicable RC data specifications and the single AVR data point only represents 2.77% of TXHWLLC’s overall telemetry obligations. No harm is known to have occurred. Texas RE considered TXHWLLC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TXHWLLC: 1) corrected the AVR status telemetry it sent to its RC. Furthermore, TXHWLLC will complete the following actions by September 29, 2017: 1) amend its service agreement to provide TXHWLLC personnel with access to ICCP data provided to its RC by its third-party scheduling entity; 2) create a process to actively monitor its plant AVR status and ensure that status is accurately telemetered; and 3) institute alarms to notify operating personnel if the plant’s AVR status differs from the AVR status being telemetered to its RC.
2017-07-31 | Texas Reliability Entity (Texas RE) | TX Hereford Wind, LLC (TXHWLLC) | NCR11495 | TRE2016016531 | VAR-002-3 | R2; R2.3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that TXHWLLC, as a Generator Operator (GOP), had an issue with VAR-002-3 R2 and R2.3. Specifically, TXHWLLC did not maintain the generator voltage schedule provided by the Transmission Operator (TOP), or otherwise meet the conditions of notification for deviations from the voltage schedule provided by the TOP. In addition, TXHWLLC neither monitored its voltage at the location specified in its voltage schedule nor possessed a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point it actually monitored. Texas RE subsequently determined that the duration of this issue was from October 29, 2014 until October 6, 2016. Accordingly, Texas RE determined that TXHWLLC had an issue with VAR-002-3 R2 from October 29, 2014 until May 28, 2015. TXHWLLC then had an issue with VAR-002-4 R2 from May 29, 2015 until October 6, 2016. Texas RE further determined that, for purposes of this issue, there was no substantive change in TXHWLLC’s compliance obligations under the applicable versions. Pursuant to Electric Reliability Council of Texas (ERCOT) Operating Guide 2.7.4.1(4), generators are required to maintain transmission system voltage within +/- 2.0% of their designated voltage profile while operating at less than their maximum reactive capabilities. Beginning on December 2, 2014, and continuing on several occasions in 2015 and 2016, TXHWLLC’s voltage exceeded this +/- 2% voltage deviation tolerance. During the issue periods, Texas RE determined that TXHWLLC exceeded the required voltage deviation tolerance for 55.16% of its total operating time with the largest deviation of -4.81% occurring on July 1, 2015. Regarding TXHWLLC’s issue with VAR-002-3 R2.3, Texas RE reviewed TXHWLLC’s previous voltage schedule. This voltage schedule specified that TXHWLLC will monitor voltage at its Point of Interconnection (POI). Beginning on October 29, 2014, however, TXHWLLC instead monitored its voltage output at the high side of its step-up transformer. TXHWLLC further lacked a methodology for converting the scheduled voltage to the point actually being monitored. On June 1, 2016, TXHWLLC’s TOP issued a new voltage schedule designating that TXHWLLC may also monitor voltage at the high side of its step-up transformer. The root cause of this issue was TXHWLLC’s failure to establish adequate processes and controls in order to ensure compliance with VAR-002 R2. Specifically, TXHWLLC relied solely on its operating personnel to manually identify voltage deviations, and the TXHWLLC control room was not configured to actively monitor its voltage at its Point of Interconnection (POI) or produce an alarm on a voltage excursion. Moreover, TXHWLLC’s existing procedures did not provide clear instructions for sufficiently understanding the requirement to monitor voltage at its designated voltage point or develop a conversion methodology, identifying voltage deviations, and taking appropriate responsive actions. This issue started on October 29, 2014, when TXHWLLC registered as a GOP, and ended on October 6, 2016, when the last recorded instance of TXHWLLC exceeding its voltage schedule occurred. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, there were no instances in which the TOP instructed TXHWLLC to modify its voltage output. Second, Texas RE did not identify any trips or outages caused by TXHWLLC’s failure to maintain its voltage output or notify its TOP when it could not meet its voltage schedule. Third, the generation Facility at issue is small, with a nameplate rating of 200 MW and only an average output of 84 MW in 2016. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. Finally, the distance between the high side of the TXHWLLC step-up transformer and its POI is only 0.31 miles, limiting the amount of line losses that would need to be accounted for using a conversion methodology. These four elements further serve to reduce the risk to reliability while TXHWLLC completes all required mitigation activities. No harm is known to have occurred. Texas RE considered TXHWLLC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TXHWLLC: 1) ceased voltage deviations beyond the +/-2.0% tolerance; 2) reconfigured its Energy Management System (EMS) to monitor voltage status at the POI in real time in addition to other designated voltage monitoring points; 3) created alarms to automatically alert its operating personnel of any voltage excursions in real time to further enhance awareness of voltage monitoring issues and responsibilities; 4) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel had adequate training regarding voltage control and monitoring issues; 5) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 6) updated its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities, including maintaining TXHWLLC’s voltage profile and monitoring voltage at the designated voltage points.
2017-07-31 | Texas Reliability Entity (Texas RE) | TX Hereford Wind, LLC (TXHWLLC) | NCR11495 | TRE2016016532 | VAR-002-3 | R3 | During a Compliance Audit conducted from October 10, 2016 through November 11, 2016, Texas RE determined that TXHWLLC, as a Generator Operator (GOP), had an issue with VAR-002-3 R3. Specifically, TXHWLLC failed to notify its associated Transmission Operator (TOP) of status changes on its Automatic Voltage Regulators (AVR) within 30 minutes of each change. Texas RE subsequently determined that the duration of this issue was from November 10, 2014 until July 19, 2016. Accordingly, Texas RE determined that TXHWLLC had an issue with VAR-002-3 R3 from November 10, 2014 until May 28, 2015. TXHWLLC then had an issue with VAR-002-4 R3 from May 29, 2015 until July 19, 2016. Texas RE further determined that, for purposes of this issue, there was no substantive change in TXHWLLC’s compliance obligations under the applicable versions. On November 10, 2014, one of TXHWLLC’s two AVRs switched from online to offline. However, TXWHLLC failed to notify its TOP of the AVR status change within 30 minutes of the change. Over the following months, TXHWLLC experienced several other instances of AVR status changes but likewise failed to provide the required notifications to its TOP. Instead, TXHWLLC continued to indicate that both its AVRs were online and operational at all relevant times. On July 19, 2016, both TXHWLLC AVRs returned to online mode for the final time, ending the issue. The root cause of this issue was related to TXHWLLC’s failure to establish adequate processes to identify AVR status changes and provide the required notifications to its TOP within 30 minutes of any such changes. Specifically, TXHWLLC relied solely on its operating personnel to manually identify AVR status changes. Moreover, TXHWLLC’s existing procedures did not provide clear instructions for identifying such status changes and providing the required notifications to its TOP. The issue started on November 10, 2014, the date of TXHWLLC’s first failure to provide a notification to its TOP within 30 minutes of an AVR status change, and ended on July 19, 2016, when TXHWLLC restored its AVRs to service to match the AVR statuses provided to its TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, Texas RE did not identify any unintended voltage controlling actions by the TOP that were related to TXHWLLC not providing timely AVR status information or any trips or outages caused by TXHWLLC’s failure to maintain its voltage output. Second, there were no instances in which the TOP instructed TXHWLLC to modify its voltage output. Finally, the generation Facility at issue is small, with a nameplate rating of 200 MW and only an average output of 84 MW in 2016. As a result, the wind generation Facility in question would have had only a negligible impact on the system’s ability to respond to voltage deviations. These three elements further serve to reduce the risk to reliability while TXHWLLC completes all required mitigation activities. No harm is known to have occurred. Texas RE considered TXHWLLC’s and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TXHWLLC: 1) reconfigured its Energy Management System (EMS) to monitor AVR status in real time; 2) created alarms to automatically alert its operating personnel of any AVR status changes; 3) restructured its fleet of operating personnel to include operators who are either NERC-certified or in the process of becoming NERC-certified in order to ensure that such personnel had adequate training regarding communications protocols and voltage control issues; 4) installed compliance tracking software to assist with tracking its ongoing compliance responsibilities, as well as tracking any upcoming or revised NERC Reliability Standards; and 5) update its VAR-002 procedures to include more detailed instructions that will assist its operators in performing all designated VAR-002 responsibilities, including providing notice of any AVR status changes to its TOP within 30 minutes.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Plains End II, LLC (PEII) | NCR00082 | WECC2017016895 | PRC-005-2(i) | R3 | On January 31, 2017, PEII submitted a Self-Report stating that, as a as a Generator Owner, it had a possible issue of noncompliance with PRC-005-2(i) R3. Specifically, during a review of its Internal Compliance Program, PEII discovered that it failed to perform the minimum maintenance activities within the maximum maintenance intervals for one 120VDC Valve Regulated Lead-Acid battery as prescribed in Table 1-4(b). The root cause of this issue was a misunderstanding of the Standard. Specifically, PEII misinterpreted the Standard as having a semi-annual maintenance interval when the actual interval is six calendar months. WECC determined that this issue began on December 1, 2016, when completion of the 6-month maintenance activity for the battery was due, and ended on December 20, 2016, when PEII completed the testing requirements prescribed in Table 1-4(b), for a total of 19 days of noncompliance. PEII identified and self-reported the issue described herein and does not have prior noncompliance with this Standard and Requirement. WECC considered these factors in its designation of this issue as a CE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PEII failed to perform the minimum maintenance activities within the maximum maintenance intervals for one battery as prescribed in Table 1-4(b). The battery in scope provides back-up power to PEII’s Protection System in the event the Plant loses back-feed or experiences failure of multiple rectifiers that normally supply Direct Current (DC) power to its system. Failure to maintain Protection System Components could potentially result in degradation of equipment, loss of this back-up power resource, resulting in the misoperation of associated Protection System devices, causing the 144 MW combustion generator to trip. However, the likelihood of the risk occurring was reduced because the battery in scope is only used to ensure the protection system remains functional in the event the generator is not online. PEII utilizes a preventative maintenance scheduler to ensure required maintenance activities are completed, however, because the maintenance interval was incorrect in its system, the testing was not completed on time. Additionally, during the period in scope, PEII did not require back-up power, the primary and back-up DC supplies were active, and the Facility only operated twice with a total operating time of 3.7 hours. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). | To mitigate this issue, PEII: 1) completed the required 6-month maintenance for the battery as prescribed in Table 1-4(b); 2) re-trained its operating personnel on the testing intervals for PRC-005; 3) added notes to its Preventative Maintenance scheduler to test every 6 months; and 4) updated its compliance calendar/outlook calendar and Preventative Maintenance Plan to include testing every 6 months.
2017-07-31 | Western Electricity Coordinating Council (WECC) | Plains End, LLC (PEL) | NCR05320 | WECC2017016894 | PRC-005-2(i) | R3 | On January 31, 2017, PEL submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-005-2(i) R3. Specifically, during a review of its Internal Compliance Program, PEL discovered that it failed to perform the minimum maintenance activities within the maximum maintenance intervals for four 120VDC Valve Regulated Lead-Acid batteries as prescribed in Table 1-4(b). The root cause of this issue was a misunderstanding of the Standard. Specifically, PEII misinterpreted the Standard as having a semi-annual maintenance interval when the actual interval is six calendar months. WECC determined that this issue began on December 1, 2016, when completion of the 6-month maintenance activity for the four batteries was due, and ended on December 20, 2016, when PEL completed the testing requirements prescribed in Table 1-4(b), for a total of 19 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PEL failed to perform the minimum maintenance activities within the maximum maintenance intervals for four batteries as prescribed in Table 1-4(b). The batteries in scope provide back-up power to PEL’s Protection System in the event the Facility loses back-feed or experiences failure of multiple rectifiers that normally supply Direct Current (DC) power to its system. Failure to maintain Protection System Components could potentially result in degradation of equipment, loss of this back-up power resource, resulting in the misoperation of associated Protection System devices, causing the 144 MW combustion generator to trip. However, the likelihood of the risk occurring was reduced because the batteries in scope are only utilized during start-up and/or power-down in the event the Facility loses its DC power. The generator would not solely operate on battery power. Additionally, during the period in scope, PEL did not require back-up power, the primary and back-up DC supplies were active, and the Facility only operated twice with a total operating time of 3.7 hours. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). WECC considered PEL’s PRC-005 compliance history in determining the disposition track. PEL’s prior noncompliance with PRC-005 include: NERC Violation ID: WECC2014013715. In the prior issue of noncompliance, PEL tested and maintained 44 of its auxiliary potential transformers (PT’s), but failed to document the auxiliary PT’s in its Protection System Maintenance and Testing Program as required in PRC-005-1 R1. The prior conduct differs from PEL’s current issue, which is the reason WECC determined that PEL's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, PEL: 1) completed the required 6-month maintenance for the four batteries as prescribed in Table 1-4(b); 2) re-trained its operating personnel on the testing intervals for PRC-005; 3) added notes to its Preventative Maintenance scheduler to test every 6 months; and 4) updated its compliance calendar/outlook calendar and Preventative Maintenance Plan to include testing every 6 months.
2017-07-31 | Western Electricity Coordinating Council (WECC) | PUD No. 1 of Douglas County (DOPD) | NCR05343 | WECC2017016843 | BAL-004-WECC-02 | R3 | On January 19, 2017, DOPD submitted a Self-Report stating that, as a Balancing Authority, it had a possible issue of noncompliance with BAL-004-WECC-02 R3. Specifically, DOPD reported that on December 15, 2016, its System Operators noticed that its accumulated On-Peak and Off-Peak Primary Inadvertent Interchange was steadily increasing outside of DOPD’s normal range, prompting a same-day investigation. DOPD discovered that its Automatic Time Error Correction (ATEC) was not in service and immediately enabled the ATEC; in turn, exceeding the allowable exception period of less than or equal to an accumulated 24 hours per calendar quarter. The root cause of this issue was DOPD’s failure to have an adequate process in place to identify changes to the ATEC mode. WECC determined that this issue began on November 23, 2016, when DOPD’s ATEC was not in service for a timeframe that exceeded the 24-hour quarterly exception period for Quarter 4 of 2016, and ended on January 1, 2017, when the allowable exception period reset for Quarter 1 of 2017, for approximately 39 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, DOPD kept its ATEC out of service for a timeframe that exceeded its 24-hour quarterly exception period. Such failure could have resulted in excessive accumulation of Primary Inadvertent Interchange, which would have required frequent manual time error corrections and increased the likelihood of frequency deviations. However, the likelihood of the risk occurring was reduced by the controls DOPD had implemented. DOPD has experienced System Operators that monitor the system and noticed that the accumulated On-peak and Off-peak Primary Inadvertent Interchange was steadily increasing outside of DOPD’s normal range, prompting a same-day investigation. Additionally, during the period in scope the total accumulated primary inadvertent interchange during Heavy Load Hours and Light Load Hours were only slightly outside DOPD’s normal range. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). WECC notes that DOPD has identified and self-reported the issues described herein, and does not have previous violations of these Standards and Requirements. WECC considered these factors in its designation of these remediated issues as a CE. | To mitigate this issue, DOPD: 1) re-enabled the ATEC and created an alarm to inform the operator when the ATEC is disabled in the future; and 2) the alarm will persist, and cannot be dismissed, until the AGC is put back into ATEC mode. WECC has verified the completion of all mitigation activity.
2017-07-31 | Western Electricity Coordinating Council (WECC) | PUD No. 1 of Douglas County (DOPD) | NCR05343 | WECC2017016730 | EOP-005-2 | R17 | On December 29, 2016, DOPD submitted a Self-Report stating that, as a Generator Operator, it had a possible issue of noncompliance with EOP-005-2 R17. Specifically, during an internal compliance review, DOPD discovered that it failed to provide a minimum of two hours of training every two calendar years for 12 of its 14 generation operating personnel responsible for the startup of its Blackstart Resource generating units and energizing a bus in accordance with the Standard. The root cause of this issue was a misinterpretation of the Standard. DOPD Subject Matter Experts believed that this Standard was only applicable to its System Operators and not for its generation operating personnel. WECC determined that this issue began on January 1, 2015, when DOPD failed to provide a minimum of two hours of training every two calendar years for 12 of its 14 generation operating personnel responsible for the startup of its Blackstart Resource generating units and energizing a bus, and ended on December 21, 2016, when DOPD provided the requisite training to the generation operating personnel in scope, for a total of 720 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, DOPD failed to provide two hours of system restoration training for 12 generation operating personnel responsible for tasks related to the startup of its Blackstart Resources. Such failure could have delayed implementation of DOPD’s System restoration procedure during an event. However, the likelihood of the risk occurring was reduced by the controls DOPD had implemented. Per DOPD’s operating protocol, the Blackstart operation of this Facility is no different than the normal operation of this Facility. Although the generation operating personnel in scope had not completed formal training, two of DOPD’s 14 generation operating personnel have experience operating the hydroelectric generating units because the units are started up and shut down on a regular basis. The Facility is in regular use and not used solely for Blackstart purposes. These generators are used for baseload as well as peaking generation. The combined capacity of DOPD’s hydroelectric generating units is 937 MVA. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC notes that DOPD has identified and self-reported the issues described herein, and does not have previous violations of these Standards and Requirements. WECC considered these factors in its designation of these remediated issues as a CE. | To mitigate this issue, DOPD: 1) completed the requisite training for all its generation operating personnel subject to this Standard and Requirement; and 2) created a task in its Sharepoint compliance tracking list that will remind a primary and secondary assignee to complete tasks on a recurring basis. WECC has verified the completion of all mitigation activity.
2017-06-29 | Midwest Reliability Organization (MRO) | Western Area Power Administration - Upper Great Plains East (WAPA) | NCR01036 | MRO2016016396 | PER-003-1 | R3.2 | On September 15, 2016, WAPA submitted a Self-Report stating that, as a Balancing Authority, it had an issue of PER-003-1 R3.2. Specifically, a System Operator performed Balancing Authority reliability-related tasks within the Western Area Power Administration - Upper Great Plains West, NCR05467 system, after his NERC certification expired on September 5, 2016. The System Operator continued to perform Balancing Authority reliability-related tasks until the System Operator and WAPA became aware of the issue on September 6, 2016. The System Operator's NERC certification was returned to active status on September 8, 2016. The System Operator had all the required qualifications and had completed all required training necessary to keep his NERC certification active, but had forgotten to pay the renewal fee. The cause of this noncompliance was the System Operator's inattention to the expiration date of his NERC certification, and the fact that WAPA had no system in place to provide an alert or warning to System Operators regarding expiring NERC certifications. This issue started on September 5, 2016, when the System Operator performed Balancing Authority reliability-related tasks with an expired certification, and ended on September 6, 2016, when WAPA removed the System Operator from those tasks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance can be accurately categorized as administrative, as the System Operator had all the required training and qualifications, but missed the renewal payment. Additionally, the duration of the noncompliance was very brief. No harm is known to have occurred. WAPA has no relevant history of noncompliance with PER-003-1. | To mitigate this issue, WAPA: 1) took steps to restore the System Operator's certification; 2) issued a memorandum to System Operators reminding them to check the renewal date of their NERC Certifications; 3) addressed this incident during the 2017 Spring Dispatcher Training; and 4) implemented a feature in its training database to alert System Operators of certifications set to expire within six months. WAPA stated that mitigating activities were complete as of March 13, 2017.
2017-06-29 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC) | NCR00824 | MRO2016016400 | PRC-005-2(i) | R3 | On September 23, 2016 and October 7, 2016, MEC submitted self-logs stating that, as a Transmission Owner, it had an issue with PRC-005-2(i) R3. Specifically, on September 6, 2016, MEC discovered eight Valve Regulated Lead Acid (VRLA) batteries missed their six-month August 31, 2016 testing deadline. On September 27, 2016, MEC discovered an additional VRLA battery, that had been tested the day before, had also missed its August 31, 2016 testing deadline. The causes of this noncompliance were human error and inadequate labeling of the test packets. The group of eight batteries missed the deadline because the testing crew took the wrong test packet and tested a different set of batteries. The other battery missed its deadline because the required testing deadline was entered into the database incorrectly. This issue began on September 1, 2016 when the batteries missed their testing interval, and ended on September 26, 2016, when the last battery was tested. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the noncompliance was brief and the noncompliance was detected by MEC's functioning detective controls. Additionally, none of the tested batteries required any follow-up maintenance. No harm is known to have occurred. | To mitigate this issue, MEC: 1) tested the nine batteries; 2) improved the test packet labels by adding the test period to help identify what batteries should be tested; and 3) created a VRLA control report that includes the next, last, and previous to last test dates. MEC stated that mitigating activities were completed as of September 27, 2016.
2017-06-29 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC) | NCR00824 | MRO2017016946 | PRC-008-0 | R2 | On January 12, 2017, MEC submitted a self-log stating that, as a Transmission Owner, it had an issue with PRC-008-0 R2. Specifically, on September 20, 2016, MEC discovered an Under Frequency Load Shedding (UFLS) relay that was not tested within the eight-year test interval. MEC's standard procedure is to replace all relays in a substation at one time. In this case, MEC replaced some, but not all of the relays at the substation. After the partial relay replacement, this relay was incorrectly removed from the UFLS relay testing list. A 2013 compliance review did not catch this issue because it did not reconcile the new and existing relays to circuits at the substation. The 2016 compliance review discovered this interval test issue. The cause of this noncompliance was that MEC deviated from its standard relay replacement process, and did not have any process in place related to that deviation, to track the necessary maintenance related to the relay that was not replaced. The exact date that the relay missed its eight-year testing interval is unknown. The relay was installed sometime in 2005, so while the exact date that noncompliance began cannot be identified, the testing interval was missed sometime in 2013. The noncompliance could have begun as early as January 1, 2013, and the noncompliance ended on September 22, 2016, when the relay was tested. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MEC had SCADA alarming on this relay for DC power failure and loss of the Power Transformer Input. Additionally, MEC reviewed more than 275 UFLS relays and this was the only relay that had a testing issue, which represents only 0.3% of all MEC UFLS relays, and only 1.3% of its UFLS MW load shed obligation. Finally, the relay passed the 2016 UFLS test. No harm is known to have occurred. | To mitigate this issue, MEC: 1) tested the UFLS relay; 2) conducted a review of all UFLS relays and verified this was the only UFLS relay that required testing; and 3) added PRC-008 data to its automated inventory system to enhance UFLS relay test management. MEC stated that mitigating activities were completed as of December 8, 2016.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Cleveland, Dept. of Public Utilities, Division of Cleveland Public Power (CPP) | NCR00712 | RFC2016016540 | PRC-005-2(i) | R5 | On November 11, 2016, ReliabilityFirst determined that City of Cleveland Public Power (CPP), as a Transmission Owner, had an issue of PRC-005-2(i) R5 as a result of a Compliance Audit conducted from September 15, 2016 through September 21, 2016. As of the time of the audit notification, CPP had not taken any efforts to address or correct any of the four valid Unresolved Maintenance Issues that were on the Unresolved Maintenance List CPP had provided to the Audit Team. The only action CPP took was to put the issues on its Unresolved Maintenance List. The four Unresolved Maintenance Issues on the list CPP provided to the Audit Team are as follows: a. CPP had a cracked portion of a battery string serving generator equipment at the transmission line designated Lake Road #1. b. CPP had not verified the condition of the fiber optic cable between the Northeast and Medco substations. c. CPP electricians had not finished troubleshooting a communications issues on the Lake Road – East Industrial transmission line. d. CPP had identified but not yet addressed rusty trip/close coils and a faulty cabinet latch at one of its substations. CPP had an ineffective procedure in place to track Unresolved Maintenance Issues that CPP employees were not consistently following. CPP followed its procedure in terms of updating items on the Unresolved Maintenance List, but did not have an effective procedure in place to ensure that it undertook efforts to actually correct the identified Unresolved Maintenance Issues. (CPP electricians perform a number of inspections at CPP substations on a monthly basis. Several reports are generated including reports on general maintenance and one focused specifically on battery condition. CPP has two resources for the repair and maintenance tasks, CPP's electricians and CPP's substation maintenance contractor.) Two of the four actual Unresolved Maintenance Issues were more than one year old. This noncompliance involves the management practices of verification and work management. CPP did not have a process or any controls in place to ensure that CPP undertook efforts to correct Unresolved Maintenance Issues which is a root cause of this noncompliance. CPP also did not have any personnel responsible for tracking the progress on addressing the Unresolved Maintenance Issues which involves work management and is another contributing cause of this noncompliance. This issue started on May 29, 2015, when PRC-005-2(i) R5 went into effect and CPP could not demonstrate that it had taken efforts to correct its identified Unresolved Maintenance Issues, and ended on August 5, 2016, when CPP began its efforts to correct its identified Unresolved Maintenance Issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. These Unresolved Maintenance Issues could lead to damage of equipment or the tripping of additional transmission lines which could lead to loss of power for customers. That potential risk is minimized in this instance because all four of the actual Unresolved Maintenance Issues were minor issues that posed minimal risk to the BPS. CPP’s protection system is built with redundancy to serve as a backup. Following from that, unless the primary and the backup would malfunction and misoperate, the probability of an actual loss of equipment and possible loss of load is minimal. ReliabilityFirst also notes that CPP is a small Transmission Owner, as all of its transmission lines are less than 200 kV, meaning the tripping of CPP’s transmission lines would have a reduced impact on the BPS. No harm is known to have occurred. ReliabilityFirst considered CPP’s PRC-005-2 R5 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CPP: 1) undertook efforts to correct each of the identified Unresolved Maintenance Issues which brought CPP back into compliance. (First, CPP obtained a quote for replacing the battery with cracked battery cells at the Division Substation Bus 3 from its contractor and will replace the battery in 2017. Second, CPP repaired the fiber optic cable between the Northeast and Medco substations by replacing the bad jumper that was causing the problem. Third, CPP re-established communications through an alternative fiber channel on August 5, 2016 to resolve the communication issue on the Lake Road – East Industrial transmission line that was caused by a break in the cable. Fourth, CPP had its substation maintenance contractor address the rusty trip/close coils at one of its substations. The rusty appearance was caused by a faulty cabinet latch that allowed moisture seepage and CPP’s contractor replaced the faulty cabinet latch to prevent future moisture seepage.); and 2) completed a process review, led by CPP’s NERC Compliance Section members, to determine how CPP could improve its existing procedures to more timely address Unresolved Maintenance Issues and to better track the progress of repairs to completion. As a result of this process review, CPP developed a method to prioritize and expedite the repair of critical transmission components, particularly those related to the protection system. This new method is reflected in CPP’s new Protection System Maintenance Procedure (The new Protection System Maintenance Procedure was formally issued by the Commissioner of Cleveland Public Power on December 28, 2016.) which addresses three main areas: a. Reporting of Maintenance Issues (CPP developed a process to ensure that such issues are promptly communicated upon discovery.) b. Analysis and Assignment of Maintenance Tasks (The intake for all maintenance reports involving the transmission system is now performed by the Compliance Engineer to ensure that protection system issues are quickly flagged and tracked for compliance purposes.) c. Status Review (The Transmission Engineer will now keep a log of all protection system related maintenance work and will meet periodically, initially twice per month, with the Compliance Engineer, the Warehouse Manager and the Assistant Commissioner of Operations to address any open issues and to evaluate the effectiveness of the new procedure). The protection system-related work orders will now be specifically coded for more effective tracking of individual maintenance items and the overall effectiveness of the maintenance program.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Generation and Marketing as agent for FirstEnergy Generation; FirstEnergy Solutions Corp. (FEGM) | NCR11317 | RFC2016016538 | VAR-002-4 | R2 | On November 15, 2016, FEGM submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue of VAR-002-4 R2. This noncompliance contains three separate instances of noncompliance. The first occurred on April 8, 2016 and the second and third both occurred on October 22, 2016. A weekly detective control report completed by FEGM corporate staff identified all three instances where the Sammis and Bay Shore plants deviated from their voltage schedules and did not make proper notifications to the Transmission Load Control Center (LCC) following the deviations. On April 7, 2016, at 11:20 PM, FEGM’s operator received a Distributed Control System (DCS) alarm indicating that the Sammis plant exceeded the upper voltage schedule band for more than thirty minutes. To address the alarm, FEGM’s operator notified the transmission LCC that the Sammis plant was within its voltage schedule, and the operator indicated in the DCS that he notified the LCC. Entering this notification information in the DCS locked out any further DCS alarms until the alarms were automatically reset by the DCS. The DCS automatically resets the alarms when the thirty-minute rolling average is within the DCS voltage schedule band. Because the DCS alarms were locked out, the operator did not receive a DCS alarm at 12:29 AM on April 8, 2017 when the voltage at the Sammis plant actually exceeded the upper voltage schedule band. As a result of not receiving this alarm, the operator did not notify the LCC within the thirty-minute notification requirement. (Per PJM Manual 3, section 3.3.3, Generator Operators are expected to maintain their assigned voltage schedule and notify the LCC when a generator is outside of the specified voltage schedule limits continuously for thirty minutes unless otherwise specified by the Transmission Owner.) Upon further investigation, FEGM determined that when the operator received the first alarm, the Sammis plant was actually meeting its voltage schedule and the alarm triggered due to a DCS alarm logic issue. A FEGM investigation identified a DCS alarm logic issue that contributed to the problem. The DCS alarm logic was alarming at a tighter bandwidth than the actual voltage schedule bandwidth, which generated a false alarm. Further alarms were locked out when the operator responded to the false alarm. After receiving the alarm and observing that the voltage was still within the voltage bandwidth, the operator correctly followed the plant procedure. (The plant procedure is: SA00-EL-138/345KV-001, 138 kV/345 kV Switch Yard Voltage Schedule Monitoring.) The DCS alarm logic issue has been addressed by aligning the DCS alarm bandwidth with the required voltage schedule bandwidth. The additional two instances are as follows. On October 22, 2016 at 3:45 AM and 5:56 PM separately, FEGM’s Bay Shore Generating Plant experienced a slightly different issue where the operator received the proper alarms indicating that the thirty-minute rolling average voltage value exceeded the upper voltage schedule band but the operator failed to follow FEGM’s procedure by failing to notify the LCC. The operator did not understand that he had to communicate with the LCC directly to meet the notification requirement. These instances of noncompliance involve the management practices of asset and configuration management and workforce management. Asset and configuration management is involved for the Sammis issue because the DCS alarms were incorrectly configured to lock out until the DCS alarms reset and that prevented an alarm from reaching the operator when the Sammis plant exceeded its voltage schedule. Additionally, the DCS alarm logic was incorrectly alarming at a tighter bandwidth than the actual voltage schedule bandwidth. That poor DCS configuration is a root cause of this noncompliance. Workforce management is involved for the Bay Shore issue as the operator in that instance did not understand that he had to communicate with the LCC directly to meet the notification requirement. The operator was not effectively trained on what notifications to make and that ineffective training is a contributing cause of this noncompliance. This issue started on April 8, 2016 when FEGM’s Sammis generating plant deviated from its voltage schedule and did not notify its LCC, and ended on October 22, 2016 when FEGM’s Bay Shore generating plant returned to its voltage schedule and notified its LCC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that the plant operator would not be aware of voltage schedule exceedances caused by sudden momentary spikes or dips in system voltage since the 30 minute rolling average alarm was disabled and thus, not notify the Transmission Operator that the 30 minute rolling average line voltage was out of schedule for FEGM’s Sammis and Bay Shore Yards generation plants. That risk is minimized here because FEGM's detective controls are working effectively as weekly detective control reports completed by FEGM's corporate staff identified each of the three instances in this noncompliance within two weeks of each instance occurring. Further minimizing the risk is the relatively small size of the voltage deviations at Sammis and Bay Shore. At the Sammis generating plant, the deviation from the voltage schedule limit on average was less than .03% for 4 hours and 17 minutes, at Bay Shore the voltage deviation was less than 1% for 2 hours and 13 minutes during the morning of October 22, 2016 and for 43 minutes during the afternoon of October 22, 2016. The small size of the voltage deviations reduces the chance that the deviation could lead to voltage instability in the area. (PJM and the LCC monitor for wide-spread abnormal voltage conditions on the transmission system and would direct the plants to take appropriate actions.) No harm is known to have occurred. ReliabilityFirst considered FEGM’s VAR-002 R2 compliance history in determining the disposition track. FEGM’s relevant prior noncompliance with VAR-002 R2 includes: RFC2013012500. A Settlement Agreement covering a violation of VAR-002-1.1b R2 was filed with FERC under NP15-30-000 on June 30, 2015. On July 30, 2015, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In the prior violation, FEGM’s generating plants had three instances at three different plants where the plant’s deviated from the voltage schedule that was issued by its Transmission Local Control Center (“LCC”) on behalf of the Transmission Operator (PJM) and did not communicate their inability to maintain voltage to the LCC. FEGM discovered this issue in April 2013 when reviewing compliance with VAR-002. FEGM conducted a formal root cause analysis and determined the violation was caused by: (i.) lack of recognition of voltage schedule deviations; (ii.) lack of a formal documented process for monitoring voltage schedules; and (iii.) inadequate shift turnover in which the expiration of temporary voltage schedules are not always communicated to oncoming shifts. The prior violation is distinguishable from the instant noncompliance because the prior violation has a different root cause. For the instant noncompliance, the root cause was a DCS alarm logic issue at Sammis and ineffective training at Bay Shore. The DCS alarm logic was alarming at a tighter bandwidth than the actual voltage schedule bandwidth, which generated a false alarm. Further alarms were locked out when the operator responded to the false alarm and the operator did not receive the next legitimate alarm that came through when voltage spiked at the Sammis plant. In contrast, the root cause of the prior violation was a lack of a formal documented process for monitoring voltage schedule deviations. ReliabilityFirst determined that FEGM's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, FEGM: 1) aligned the DCS Alarm bandwidth to meet the required voltage bandwidth. This activity ensures that the GOP personnel can identify and correctly react to alarms related to voltage schedule monitoring; 2) reviewed BS00-H11-005, Voltage Control Monitoring procedure, with all applicable GOP personnel. This activity reinforces the operator’s obligations for voltage schedule monitoring; 3) implemented step-discipline to the individual operator involved in the noncompliance. This included counseling and training on BS00-H11-005, Voltage Control Monitoring procedure. This activity reinforces the operator’s accountability and obligations for voltage schedule monitoring; and 4) implemented a bi-annual detective control at Sammis to verify alarm logic. This activity will verify that compliance alarm logic is working as expected.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Utilities as agent for Allegheny Energy Supply Company, L.L.C., American Transmission Systems, Incorporated; The Cleveland Electric Illuminating Company; Jersey Central Power & Light Company; Metropolitan Edison Company; Mid-Atlantic Interstate Transmission; Monongahela Power Company; Ohio Edison Company; Pennsylvania Electric Company; Pennsylvania Power Company; The Potomac Edison Company; The Toledo Edison Company; Trans-Allegheny Interstate Line Company; and West Penn Power Company (FEU) | NCR11315 | RFC2016016537 | VAR-002-4 | R2 | On November 15, 2016, FEU submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-4 R2. On July 30, 2016 at 5pm, FEU did not receive the Generation Management System (GMS) alarms that were alarming because FEU’s Yards Creek generation plant 30-minute rolling average line voltage was outside of its voltage schedule. Therefore, FEU did not notify the Transmission Operator that the 30-minute rolling average line voltage was out of schedule for FEU’s Yards Creek generation plant. FEU discovered this issue on August 11, 2016 through a weekly detective control report compiled by FEU corporate staff. While preparing this report, FEU corporate staff identified the instances where the Yards Creek plant deviated from their voltage schedule for thirty minutes or more and where proper notification to the transmission Load Control Center (LCC) and then to the Transmission Operator was not made for the referenced deviations. After discovering this issue, FEU generation conducted an investigation to determine the cause of this issue. FEU discovered that the GMS alarms were enabled as intended at the time of the event at FEU’s Yards Creek generation plant. FEU’s Regulated Generation Dispatch (RGD) unit has the primary responsibility for voltage monitoring at the Yards Creek plant and provides back-up voltage monitoring to the local plant control room for the remaining FEU generating plants. RGD management had the GMS alarming at Yards Creek modified to alarm for instantaneous voltage schedule deviations rather than a thirty-minute rolling average deviation. The desired effect of this change was to get earlier operator responses to voltage issues. However, the modification unintentionally disabled the 30-minute rolling average alarm, as well as subsequent alarms, intended for operator awareness when a deviation required action to correct or to contact the LCC. Although the operators were receiving the new alarms for instantaneous voltage schedule deviations, because the operators were not receiving the 30-minute rolling average alarms, the operators were not taking steps to bring the voltage back into the voltage schedule and not notifying the Transmission LCC of these deviations. The operators were not taking these actions because they had been trained to rely on the 30 minute rolling average alarm before taking any of these actions. Per PJM Manual 3, section 3.3.3, Generator Operators are expected to maintain their assigned voltage schedule and notify the Transmission LCC when a generator is outside of the specified voltage schedule limits continuously for thirty minutes unless otherwise specified by the Transmission Owner. This noncompliance involves the management practice of verification because FEU did not verify that when RGD management had the GMS alarming at Yards Creek modified to alarm for instantaneous voltage schedule deviations rather than a thirty-minute rolling average deviation, that this modification in alarming would not disable the 30 minute rolling average alarm. This failure to verify that no adverse effects would come from the alarming modification is a root cause of this noncompliance. This noncompliance also involves workforce management because the operators were not trained on how to respond when they were only receiving instantaneous voltage schedule deviation alarms. This issue started on July 30, 2016, when FEU did not notify the LCC and the Transmission Operator that the 30 minute rolling average line voltage was out of schedule, and ended on August 24, 2016, when FEU re-enabled GMS Alarms using the 30 minute rolling average. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that the plant operator would not respond to voltage schedule exceedances caused by sudden momentary spikes or dips in system voltage since the 30-minute rolling average alarm was disabled and the operator had been trained to rely on the 30-minute rolling average alarm. By not responding to these short voltage schedule exceedances, the operator would also fail to notify the Transmission Operator of these sudden momentary spikes or dips in system voltage. That risk is minimized here because of the relatively small size of the voltage deviations at Yards Creek. The thirty minute running average for Yards Creek (232 kV nominal voltage) beginning at 1700 deviated slightly from the schedule limit on average by 0.3 kV (0.13%) for 1 hour and 21 minutes. The maximum deviation from the schedule limit was 0.4 kV (< 0.2%). The small size of the voltage deviations reduces the chance that the deviation could lead to voltage instability in the area. (PJM and the LCC monitor for wide-spread abnormal voltage conditions on the transmission system and would direct the plant to take appropriate actions.) FEU’s detective controls are also working effectively as a weekly detective control report completed by FEU corporate staff identified the noncompliance within two weeks after the noncompliance began. No harm is known to have occurred. ReliabilityFirst considered FEU’s VAR-002 R2 compliance history in determining the disposition track. FEU’s relevant prior noncompliance with VAR-002 R2 includes: RFC2014014256. A Settlement Agreement covering a violation of VAR-002-2b R2 was filed with FERC under NP15-30-000 on June 30, 2015. On July 30, 2015, FERC issued an order stating it would not engage in further review of the Notice of Penalty. FE Utilities reported that three of its generating plants deviated from the voltage schedule that was issued by the LCC on behalf of the Transmission Operator (PJM) and did not communicate the inability to maintain voltage to the LCC. These incidents took place during the months of September 2013 and January 2014 and were discovered during a review of compliance with VAR-002. FEU identified human performance issues as the root cause. FEU conducted a formal root cause analysis and determined the violation was caused by: (i.) lack of recognition of voltage schedule deviations; (ii.) lack of a formal documented process for monitoring voltage schedules; and (iii.) inadequate shift turnover in which the expiration of temporary voltage schedules are not always communicated to oncoming shifts. The prior violation is distinguishable from the instant noncompliance because the prior violation has a different root cause. For the instant noncompliance, the root cause was FEU modified the GMS alarming at Yards Creek to alarm for instantaneous voltage schedule deviations rather than a thirty-minute rolling average deviation. The desired effect of this change was to get earlier operator responses to voltage issues. However, the modification unintentionally disabled the 30-minute rolling average alarm, as well as subsequent alarms, intended for operator awareness when a deviation required action to correct or to contact the LCC. In contrast, the root cause of the prior violation was caused by a lack of a formal documented process for monitoring voltage schedule deviations. ReliabilityFirst determined that FEU's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, FEU: 1) re-enabled the GMS alarms using the 30-minute rolling average. This activity ensures that the GOP personnel can identify and correctly react to GMS alarms related to voltage schedule monitoring; 2) reviewed the Voltage Schedule Monitoring Procedure (RGD Reporting Process) with applicable GOP personnel. This activity reinforced the proper actions that should be taken when a voltage deviation occurs; and 3) made applicable FEU Staff approvers for GMS Application Changes. This activity will prevent future GMS changes in “compliance alarm logic” without applicable FEU Staff approval. ReliabilityFirst has verified the completion of all mitigation activity
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW1) | NCR03006 | RFC2016016589 | VAR-002-4 | R2 | On November 21, 2016, Arbuckle Mountain Wind Farm LLC (Arbuckle) submitted a Self-Report through MLW1, under an existing multi-region registered entity agreement stating that, as a Generator Operator, it had an issue of VAR-002-4 R2. As part of EDP Renewables' (EDPR) 2016 Internal Audit Review of VAR-002-4, EDPR discovered two possible issues with VAR-002-4 at Arbuckle that occurred on June 12, 2016. On June 12, 2016 at 12:30 PM, Arbuckle’s voltage exceeded the voltage schedule established by Arbuckle’s Transmission Operator (TOP). Arbuckle’s voltage schedule varies based upon the day of the week and the hour. In this instance, beginning at 12:30 PM, Arbuckle exceeded its voltage schedule for approximately 165 minutes (At 1:14 PM, Arbuckle’s voltage was within its bandwidth and voltage schedule for one minute.) and during that 165 minutes, Arbuckle’s largest deviation was .8 kV outside of the voltage schedule. From 3:15 PM to 3:38 PM, Arbuckle’s voltage stayed within its voltage schedule. Beginning at 3:38 PM, Arbuckle’s voltage rose to 140.2 kV, which is .1 kV outside of Arbuckle’s voltage schedule, and Arbuckle continued to exceed its voltage schedule for the next 30 minutes. In that 30 minute span, the largest deviation was .9 kV outside of the voltage schedule. During all of these voltage schedule deviations, Arbuckle was neither exempt nor operating at the limit of its facility’s capabilities thereby violating VAR-002-4 R2. EDPR investigated these voltage issues at Arbuckle and determined that they did not result from a status or capability change of Arbuckle’s reactive power resources. EDPR determined that these voltage issues resulted from Arbuckle not modifying voltage parameters in an accurate or timely manner. EDPR conducted a root cause analysis of this event and determined that the root cause was that EDPR’s alarms were not properly configured for Arbuckle’s voltage schedule which varies based upon the day of the week and the hour. In this instance, EDPR’s voltage control system did not account for daylight savings time. This noncompliance involves the management practice of asset and configuration management because EDPR did not modify its voltage parameters to ensure that Arbuckle would comply with its voltages schedules that vary based upon the day of the week and the hour. EDPR was not receiving accurate alarms because it had set up its voltage alarming parameters incorrectly and this is a contributing cause of the noncompliance. This issue started on June 12, 2016, when Arbuckle first deviated from its assigned voltage schedule and ended on June 12, 2016, when Arbuckle returned to compliance with its voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that the wind farm may have been contributing to a high system voltage and since the TOP was not notified, the TOP was unaware what was causing the high voltage. That risk is minimized here because of the relatively small size of the voltage deviations at Arbuckle. On June 12, 2016, Arbuckle’s largest voltage schedule deviation was .9 kV outside of its voltage schedule. The small size of the voltage deviations reduce the chance that the deviation could lead to voltage instability in the area. Arbuckle is a dispersed generation resource that has a total generating capacity of approximately 100 MW. Wind generation is an intermittent generation source that is not regularly relied upon to provide significant voltage control and a 100 MW wind facility has limited capability to provide voltage control. As part of EDPR’s 2016 Internal Audit Review of VAR-002-4, EDPR confirmed that this issue on June 12, 2016 was Arbuckle’s only violation of VAR-002-4 all year. Lastly, there was no unintended loss of BES equipment, load, or generation. No harm is known to have occurred. ReliabilityFirst considered Arbuckle’s VAR-002 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Arbuckle: 1) reviewed with Remote Operations Control Center (ROCC) Specialists the proper protocols for handling of VAR-002 notifications during a ROCC meeting; 2) modified the function of the voltage control system to accommodate the complexity of the multiple day/date values of the issued voltage schedule from Arbuckle's Transmission Owner. EDPR modified its voltage controls system to properly alarm and conform to Arbuckle’s voltage schedule which varies based upon the day of the week and the hour. Arbuckle’s voltage control system will now account for daylight savings time; and 3) upgraded the ROCC Voltage Schedule related notification system to optimize the number of alarms to ensure ROCC Specialists receive accurate alarms when notification is required. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW1) | NCR03006 | RFC2016016590 | VAR-002-4 | R2 | On November 21, 2016, Timber Road II, also known as Paudling Wind Farm II, submitted a Self-Report through MLW1, under an existing multi-region registered entity agreement stating that, as a Generator Operator, it had an issue of VAR-002-4 R2. As part of EDP Renewables' (EDPR) 2016 Internal Audit Review of VAR-002-4, EDPR discovered a possible issue with VAR-002-4 at its Timber Road II Wind Farm. On March 4, 2016, at 3:17 AM, the voltage at the interconnection point for Timber Road II had fallen below the voltage schedule range set by Timber Road II’s Transmission Owner (TO). Timber Road II is scheduled to maintain voltage between 138.5 kV and 141.3 kV. Timber Road II’s voltage deviation lasted for 118 minutes and its largest deviation from this voltage schedule was when its voltage hit 137.72 kV, .78 kV outside of its voltage schedule. EDPR’s Remote Operations Control Center (ROCC) received an HMI alarm at 3:41 AM on March 4, 2016. After receiving the alarm, instantaneous voltage observed by the ROCC Specialist indicated that the voltage was at 138.5 kV, inside the Timber Road II voltage schedule. Due to this observation, the ROCC Specialist did not notify PJM, Timber Road II’s Transmission Operator (TOP), or AEP, Timber Road II’s TO, of a voltage schedule deviation at Timber Road II. The ROCC Specialist also did not internally record a voltage deviation by Timber Road II because he did not observe one. The thirty-minute average of the voltage data, however, was below the voltage schedule at 138.46kV, a .04kV deviation. Because the thirty-minute average of the voltage data was below the voltage schedule, Timber Road II did not maintain its generator voltage within the voltage schedule issued by its TO thereby violating VAR-002-4 R2. Later in the day on March 4, 2016, Timber Road II deviated from its voltage schedule three other times because of low wind conditions in the surrounding area. (At 5:15 AM on March 4, 2016, the plant generation went below the start-up exemption of 10 MW with the voltage at the Point of Interconnection still outside of the required range. Due to the exemption outlined within the voltage schedule issued by AEP, notification was not required at this time. This occurred for 124 minutes. Following this, Timber Road II went below the voltage schedule again for 86 minutes with the largest deviation from this voltage schedule being 137.62 kV, .88 kV outside of its voltage schedule. During this occurrence, EDPR NA's ROCC did not notify PJM, Timber Road II's Transmission Operator, or AEP, Timber Road II's Transmission Owner. The plant generation went below the start-up exemption of 10 MW with the Point of Interconnection still outside the required range on March 4, 2016 at 0845. Due to the exemption outlined within the voltage schedule issued by AEP, notification was not required at this time.) These deviations, however, were exempted within the voltage schedule that Timber Road II’s TO issued to Timber Road II. EDPR investigated these voltage issues at Timber Road II and determined that they did not result from a status or capability change of Timber Road II’s reactive power resources. EDPR determined that these voltage issues resulted from low wind conditions and respectively low reactive power capabilities of the type II turbines that are part of the Timber Road II facility. This noncompliance involves the management practice of asset and configuration management because EDPR’s HMI alarm did not notify the ROCC Specialist when Timber Road II deviated from its voltage schedule and this is a root cause of the noncompliance. The alarms were not correctly configured to get the ROCC Specialist the necessary voltage information when Timber Road II deviated from its voltage schedule. This issue started on March 4, 2016, when Timber Road II first deviated from its assigned voltage schedule, and ended on March, 4 2016, when Timber Road II returned to compliance with its voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this noncompliance is that the wind farm may have been contributing to a high system voltage and since the TOP was not notified, the TOP was unaware what was causing the high voltage. That risk is minimized here because of the relatively small size of the voltage deviations at Timber Road II. On March 4, 2016, Timber Road II’s largest voltage schedule deviation was approximately .04 kV. The small size of the voltage deviations reduce the chance that the deviation could lead to voltage instability in the area. Timber Road II is a dispersed generation resource that has a total generating capacity of approximately 99 MW. Wind generation is an intermittent generation source that is not regularly relied upon to provide significant voltage control and a 99 MW wind facility has limited capability to provide voltage control. Lastly, there was no unintended loss of BES equipment, load, or generation. No harm is known to have occurred. ReliabilityFirst considered Timber Road II’s VAR-002 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Timber Road II: 1) reviewed with Remote Operations Control Center (ROCC) Specialists proper protocols for handling of VAR-002 notifications during a ROCC meeting; and 2) upgraded the ROCC’s Voltage Schedule related notification system to optimize the number of alarms to ensure ROCC Specialist receive accurate alarms when notification is required. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company (NIPSCO) | NCR02611 | RFC2016016663 | PRC-005-2(i) | R3 | On December 16, 2016, NIPSCO submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-005-2(i) R3. NIPSCO determined that two microwave digital radios (NIPSCO #71077 Tower Road and NIPSCO #70516 Ainsworth.) were not maintained within their four calendar month maximum maintenance intervals as prescribed in PRC-005-2(i) Table 1-2, Row 1. The four calendar month maintenance interval for these two radios ended on November 1, 2016. NIPSCO discovered the late maintenance on November 8, 2016 as part of a periodic review. Upon discovering the missed maintenance for these microwave digital radios, NIPSCO immediately performed the maintenance inspections and discovered no abnormalities on November 8, 2016. NIPSCO performed the maintenance seven days late. After NISPCO discovered this issue, NIPSCO conducted an investigation and determined that new technicians assigned to the maintenance inspections missed these two due dates in NIPSCO’s Cascade database. (NIPSCO uses the Cascade database to track and schedule NIPSCO’s protection system maintenance testing and activity.) Although NIPSCO has maintenance triggers (NIPSCO’s maintenance triggers are similar to alerts.) enabled in Cascade for protective relays, when this noncompliance occurred, NISPCO had not yet enabled maintenance triggers for microwave digital radios. This noncompliance involves the management practices of information management and asset and configuration management. Information management and asset and configuration management are both involved because NIPSCO did not yet have maintenance triggers enabled in its Cascade database for maintaining microwave digital radios. The failure to enable maintenance triggers for these radios is a root cause of this noncompliance. The maintenance triggers serve as a reminder to the technicians to make sure the necessary maintenance is completed timely. This issue started on November 1, 2016, when NIPSCO was required to complete maintenance on two microwave digital radios, and ended on November 8, 2016, when NIPSCO completed the maintenance on those two microwave digital radios. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by not maintaining microwave digital radios is that if the radios would fail, NIPSCO would need to implement another form of communication to ensure that timely and accurate information continued to be exchanged with the required parties. This risk, however, is minimized because these two microwave digital radios are continuously monitored and alarmed. If either of these radios had failed, an alarm would be sent to the Transmission System Supervisor, which is NIPSCO’s Transmission Operator (TOP), and the TOP would take immediate remedial action after receiving the alarm. Additionally, these radios would qualify for a longer maintenance interval, but NIPSCO voluntarily chose a more aggressive interval for reliability purposes for these radios based on monitoring per PRC-005-2(i) R1.2. NIPSCO identified, assessed, and corrected this noncompliance quickly as the noncompliance was identified seven days after it began, assessed and corrected on that same day, and NIPSCO completed all mitigating activities ten days after the noncompliance began. Lastly, the noncompliance had a short duration of only seven days. No harm is known to have occurred. ReliabilityFirst considered NIPSCO’s PRC-005-2(i) R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, NIPSCO performed the late maintenance on these two microwave digital radios. To prevent recurrence, NIPSCO enabled a trigger in Cascade which provides notification of approaching maintenance due dates. This warning is set up to go out ninety days after the previous maintenance was completed and that allows NIPSCO at least a month to complete the inspection within the required interval. The warning is sent via email to the Supervising Engineer Communication & Control and to the Engineer/Specialist assigned to the maintenance job. The warning is sent to both individuals to ensure that the warning is addressed even if one individual misses the warning. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas, LLC. (Duke) | NCR01219 | SERC2016015664 | BAL-005-0 | R17. | On April 14, 2016, Duke submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue of BAL-005-0.2b R17. Duke did not annually check or calibrate its time error and frequency monitors against a common reference. SERC later determined that the issue extended back to Version 0 of the Standard and Requirement. On February 1, 2016, while performing an extent of condition review because of a Self-Report submitted by an affiliate, Duke discovered it did not annually check or calibrate its time error and frequency monitors against a common reference. Since BAL-005-0 became mandatory and enforceable, Duke used four frequency devices that could not be calibrated and Duke was unaware of the need to annually check the devices against a common reference. Therefore, Duke could not provide evidence that it checked and calibrated the four frequency devices against a common reference. The root cause was Duke’s misunderstanding of the Standard and Requirement. The issue lasted from June 18, 2007, when the Standard became mandatory and enforceable, and ended on March 18, 2016, when Duke performed the crosscheck of the frequency devices against a common reference. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Duke’s failure to annually check its frequency instrumentation against a common reference could affect the accuracy of the Area Control Error calculation and result in improper generation control and unnecessary inadvertent interchange. However, the Duke BA reconciles inadvertent interchange with adjacent BAs hourly using meters that are not affected by frequency measurements. Although Duke did not annually check the devices against a common reference, it did synchronize the devices with a satellite clock. Duke rotated the use of the four devices such that, if one device had incurred an error, the error would have existed for no more than six hours per day. No harm is known to have occurred. SERC considered Duke’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Duke: 1) performed a cross-check on each of its frequency devices using a common reference; 2) documented a process for performing the annual cross-check of all frequency devices against a common reference; 3) provided process orientation for individuals responsible for periodic checks; and 4) added an item to the Duke Energy compliance tool, to notify the appropriate personnel to perform the annual cross check for all Duke primary and back-up frequency devices used for ACE.
2017-06-29 | SERC Reliability Corporation (SERC) | Duke Energy Progress, LLC. (DEP) | NCR01298 | SERC2015015408 | BAL-005-0 | R17. | On December 14, 2015, DEP, on behalf of Duke Energy Florida (DEF) submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue of BAL-005-0.2b R17. DEP submitted the Self-Report to SERC under an existing multi-region registered entity agreement. DEF did not annually check its frequency devices against a common reference. SERC later determined that the issue extended back to Version 0 of the Standard and Requirement. On November 15, 2015, during an internal compliance assessment, the DEF lead system operations analyst conducted a review of the Reliability Standard audit worksheet for BAL-005-0. The analyst could not locate frequency transducer calibration or cross-checking with a known source. Since BAL-005-0 became mandatory and enforceable, DEF has used four total frequency devices at two locations, two at the energy control center and two at the backup control center. The type of frequency devices DEF employed at these locations could not be calibrated and the DEF energy management system group did not annually check the devices against a common reference. The root cause was DEF's misunderstanding of the Standard and Requirement. The issue started on June 18, 2007, when the Standard became mandatory and enforceable, and ended August 31, 2016, when DEF performed the crosscheck of the frequency devices against a common reference. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEF’s failure to annually check its frequency devices against a common reference could affect the accuracy of the Area Control Error calculation and result in improper generation control and unnecessary inadvertent interchange. However, the BA reconciles inadvertent interchange with adjacent BAs hourly using meters that are not affected by frequency measurements. Although DEF did not annually check the devices against a common reference, it did synchronize the devices with a satellite clock. DEF rotated the use of the four devices such that, if one device had incurred an error, the error would have existed for no more than six hours per day. No harm is known to have occurred. SERC considered DEF and its affiliates’ BAL-005 R17 compliance history in determining the disposition track. DEF’s affiliate, DEP, had relevant prior noncompliance with BAL-005 R17 that includes NERC Violation ID SERC2012009742. SERC determined that the compliance history of DEF’s affiliate, DEP, should not serve as a basis for applying a penalty. The DEP issue occurred in a different Balancing Authority area in a different Regional Entity footprint and DEP mitigated the issue in 2012. DEF identified the instant issue during an internal compliance assessment in November 15, 2015 and promptly mitigated it by conducting a check of its frequency devices against a common reference by January 21, 2016. | To mitigate this issue, DEF: 1) performed a cross-check on all frequency devices using a common reference. Specifically for DEF this would be for the four frequency devices at two locations on the DEF system: Energy Control Center (2), and Back-Up Control Center(2); 2) added an item to the Duke Energy’s Compliance Tool to notify the appropriate personnel to perform the annual cross check for all primary and back-up frequency devices at DEF used for ACE; 3) documented a process for performing the annual cross check of all DEF frequency devices (primary and back-up) against a common reference; 4) provided process orientation for individuals responsible for the periodic checks; and 5) communicated its finding to all affiliates to assist in assuring compliance with the requirement across the Duke enterprise. SERC has verified the completion of all mitigation activity.
2017-06-29 | SERC Reliability Corporation (SERC) | Shelby County Energy Center, LLC (SCEC) | NCR11629 | SERC2016016162 | MOD-025-2 | R1. | On September 15, 2016, SCEC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R1. SCEC stated that it had not completed its verification testing by July 1, 2016. The implementation plan for MOD-025-2 R2 requires the GO to verify its generator reactive output in annual increments beginning with 40% of its generation by July 1, 2016 and 100% by July 1, 2019. SCEC has eight identical 44 MW combustion turbines. In order to comply with the implementation plan, SCEC needed to perform the verification on four of the units by July 1, 2016. SCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for MOD-025-2 R1 compliance and did not understand the requirement for verification during unit testing. On June 29, 2016, a third party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to SCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and inadequate contract oversight. SCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, through May 1, 2017, when SCEC completed the required real power testing and reported the results to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCEC’s failure to provide verification of real and reactive power capability may result in inaccurate planning models and inaccurate assessment of BPS reliability. However, the implementation plan for MOD-025-2 allows five years for full implementation of the requirements. SCEC contributes a maximum of 352 MW to the grid while operating and operates at less than a 5% capacity factor. Therefore, any errors in the plant data would present a minor variation in planning results. No harm is known to have occurred. SERC considered SCEC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SCEC: 1) conducted the required MOD-025 verifications; 2) submitted the necessary data to the Transmission Planner; 3) developed and annually reviews an internal compliance procedure while also updating upon any standard revisions; 4) implemented an internal software product that allows for tracking of compliance reporting functions and internal deadlines that SCEC deemed appropriate; 5) added MOD-025 to the compliance tracker with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies; 6) utilizes third-party mock audits and internal self-assessments as a second check on the compliance tracker; and 7) conducts bi-weekly compliance calls among site managers to ensure plant staffs are aware of upcoming deadlines and compliance obligations.
2017-06-29 | SERC Reliability Corporation (SERC) | Shelby County Energy Center, LLC (SCEC) | NCR11629 | SERC2016016163 | MOD-025-2 | R2. | On September 15, 2016, SCEC submitted a Self-Report stating that, as a Generator Owner (GO) it had an issue of MOD-025-2 R2. SCEC stated that it had not completed its verification testing by July 1, 2016. The implementation plan for MOD-025-2 R2 requires the GO to verify its generator reactive power output in annual increments beginning with 40% of its generation by July 1, 2016 and 100% by July 1, 2019. SCEC has eight 44 MW combustion turbines. In order to comply with the implementation plan, SCEC needed to perform the verification on four of the units by July 1, 2016. SCEC utilizes a consultant to manage its operations and maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for MOD-025-2 R2 compliance and did not understand the requirement for verification during unit testing. On June 29, 2016, a third party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to SCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and inadequate contract oversight. SCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, through May 1, 2017, when SCEC completed the required reactive power verification and reported it to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to provide verification of real and reactive power capability may result in inaccurate planning models and inaccurate assessment of BPS reliability. However, the implementation plan for MOD-025-2 allows five years for full implementation of the requirements. SCEC contributes only 352 MW to the grid while operating and operates at less than a 5% capacity factor. Therefore, any errors in the plant data would present a minor variation in planning results. SCEC completed verification of both units within the first quarter following the enforcement date resulting in a minimal risk to the BPS. No harm is known to have occurred. SERC considered SCEC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SCEC: 1) conducted the required MOD-025 verifications; 2) submitted the necessary data to the Transmission Planner; 3) developed and annually reviews an internal compliance procedure while also updating upon any standard revisions; 4) implemented an internal software product that allows for tracking of compliance reporting functions and internal deadlines that SCEC deemed appropriate; 5) added MOD-025 to the compliance tracker with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies; 6) utilizes third-party mock audits and internal self-assessments as a second check on the compliance tracker; and 7) conducts bi-weekly compliance calls among site managers to ensure plant staffs are aware of upcoming deadlines and compliance obligations
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | City Utilities of Springfield, MO (SPRM) | NCR01081 | SPP2016015750 | TOP-004-2 | R4 | On May 16, 2016, SPRM submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue of noncompliance with TOP-004-2 R4 because SPRM entered an unknown operating state and did not restore operations to respect proven reliable power system limits within 30 minutes. Specifically, on April 19, 2016, at 1:00 a.m. SPRM exceeded the system operating limit (SOL) on the Brookline 345 kV bus by .37 kV and did not return to normal operating limits for 45 minutes. On March 14, 2016, SPRM, the Southwest Power Pool (SPP), the Tennessee Valley Authority (TVA), American Electric Power, and Associated Electric Cooperative, Inc. (AECI) developed a Temporary Operating Guide (Guide) to address short-term high voltage that occurs in the Flint Creek – Brookline – Morgan 345kV area under light load conditions. The Guide calls for the SPP Reliability Coordinator (SPP RC) and TVA Reliability Coordinator (TVA RC) to evaluate the high voltage condition when it occurs and to coordinate the planned mitigation with the affected Transmission Operators (TOPs). On April 29, 2016, at 1:00:26 a.m., the SPP RC called SPRM because of high voltage in the Brookline area. The SPP RC informed SPRM that AECI was experiencing similar high voltage and that opening the Brookline to Morgan line, as identified in the Guide, would cause AECI’s high voltage condition to worsen. At this time, the voltage on SPRM’s system in the Brookline area was beginning to exceed the 362.25 kV SOL. The SPP RC said he would talk to AECI’s RC, TVA RC, to see if the TVA RC could open the Brookline to Morgan line, a second mitigation option in the Guide. At 1:30:52 a.m., the SPP RC informed SPRM that the TVA RC had requested SPP to study opening the Morgan to Huben line, a mitigation option not previously identified in the Guide. At 1:33:20 a.m. the SPP RC informed SPRM that opening the Morgan to Huben line would lower the voltage at Brookline by 2.7 kV and that he would ask the TVA RC to have AECI open the Morgan to Huben line. At 1:37:44 a.m. the SPP RC informed SPRM that AECI was opening the Morgan to Huben line. At 1:46:24 a.m., the SPP RC informed SPRM that the Morgan to Huben line was opened at 1:45 a.m. and voltage was below the SOL. As a result of the time required to implement the Guide, SPRM was in an unknown operating state for approximately 45 minutes. The duration of this instance of noncompliance was from April 19, 2016, at 1:31 a.m., 31 minutes after SPRM went into an unknown operating state, through April 19, 2016, at 1:45 a.m., when SPRM restored operations within its defined SOLs. The root cause of this instance of noncompliance was a combination of the delays caused by the SPP RC and TVA RC in developing an action plan not identified in the Guide and SPRM’s reluctance to take unilateral action before the high voltage condition exceeded the 30-minute time limit. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to restore system voltage to normal operating conditions within 30 minutes has the potential to affect the reliability of the BPS by causing damage to the equipment (i.e. breakers, transformers, surge arresters) necessary to maintain reliable operation of the BPS. Notwithstanding, the maximum voltage was 362.62 kV, which only exceeded the SOL by .37 kV. Additionally, the instance of non-compliance was short in duration (14 minutes) and both RCs were diligently trying to find the best solution for the reliability of the BPS. No actual harm is known to have occurred. SPRM has no relevant prior violations for TOP-004-2 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPRM: 1) reprimanded, in accordance with SPRM’s progressive disciplinary process, the Power System Operator involved for not taking unilateral action to comply with the 30-minute requirement; 2) updated the Brookline 345kV Voltage Control Operating Guide to include the 30-minute time limit for mitigation and identification of the Morgan to Huben line as a viable mitigation option; 3) verified the SPRM and SPP Operators are monitoring the same voltage point(s) at the Brookline bus; and, 4) created a new reliability task specific to high voltage mitigation and confirmed all Power System Operators are competent in implementing SOL mitigating actions and provided additional training as needed.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Sunflower Electric Power Corporation (SECI) | NCR01148 | SPP2017016741 | TOP-002-2.1b | R11 | On January 4, 2017, SECI submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue of noncompliance with TOP-002-2.1b R11. SECI did not timely perform nor coordinate with its Reliability Coordinator (RC), Balancing Authority (BA), or neighboring TOPs, five seasonal Bulk Electric System (BES) studies (Winter 2015 through Winter 2016) that determine System Operating Limits (SOLs). The duration of this instance of noncompliance was from December 1, 2015, the date SECI’s Winter Season 2015 study should have been performed and provided to SECI’s RC, BA, and neighboring TOPs, through December 22, 2016, the date SECI provided its Winter 2016 seasonal study to SECI’s RC, BA, and neighboring TOPs. The root cause of this instance of noncompliance was a combination of SECI’s failure to adequately scope the work required for contractors to meet compliance of TOP-002-2.1b R11 after the SECI employee responsible for coordinating operational planning studies resigned; and lack of training provided to new SECI personnel assigned to perform the operational studies, including seasonal studies. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform seasonal BES studies and provide such stidies to its RC, BA, and neighboring TOPs with the results has the potential to affect the reliability of the BPS by denying SECI's RC, BA, and neighboring TOPs with BES information necessary to identify potential SOL’s and plan how to manage transmission flows and voltage during forecasted seasonal conditions. Notwithstanding, SECI consistently performed current-day, next-day, week-ahead, and future studies and provided the results of the studies to its RC, BA, and neighboring TOPs. The current-day, next-day, week-ahead, and future studies assess real-time system outages, current generation levels, system loading, and changes in system topology. Additionally, the future studies that were performed included any significant outages that would have been included in SECI’s seasonal studies. No harm is known to have occurred. SECI has no relevant prior violations for TOP-002-2.1b R11 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SECI: 1) completed and coordinated the 2016 Winter seasonal study; and 2) required SECI subject matters experts to review SECI’s internal Operating Procedure and Normal Operations Planning. SPP RE has verified the completion of all mitigation activity.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | USACE - Kansas City District | NCR01357 | SPP2016016253 | MOD-025-2 | R3; R3.1, R3.2 | On September 30, 2016, COEKS submitted a Self-Certification stating that, as a Transmission Owner (TO), it had an issue of noncompliance with MOD-025-2 R3.1 and R3.2. Specifically, COEKS did not verify the Reactive Power capability of the synchronous condenser unit at the Stockton Dam hydroelectric generating plant in accordance with Attachment 1. As a result, COEKS was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of the applicable synchronous condenser unit at the Stockton plant. The root cause of this instance of noncompliance was COEKS’s error in calculating the effective date of MOD-025-2. The NERC website shows July 1, 2016 as the effective date for MOD-025-2. The Implementation Plan for MOD-025-2 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” COEKS erroneously used July 1, 2016 as the “regulatory approval” date and calculated two years forward (July 1, 2018) as the effective date for MOD-025-2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of MOD-025-2 through March 1, 2017, the date COEK completed all mitigation activity. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Noncompliance with MOD-025-2 R3 has the potential to affect the reliability of the BPS by increasing the risk of not being able to provide the reactive power anticipated by the Transmission Operator during a system voltage event. Notwithstanding, Stockton is a 22 MVAR synchronous condenser that is rarely called upon to provide reactive power. No harm is known to have occurred. COEK has no relevant prior violations for MOD-025-2 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, COEK: 1) verified Reactive Power capability of the synchronous condenser unit at the Stockton plant and provided verification thereof to its TP; and 2) included a schedule in the maintenance management program that will initiate review and verification of the settings on a four-year cycle, to be completed by the five-year interval. SPP RE has verified the completion of all mitigation activity.
2017-06-29 | Texas Reliability Entity (Texas RE) | Avangrid Renewables (AGR) | NCR10259 | TRE2017016820 | MOD-025-2 | R2; R2.1 | On January 23, 2017, AGR submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with MOD-025-2 R2.1. Specifically, AGR failed to verify the Reactive Power capability of at least 40 percent of its applicable Facilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Beginning in 2015, AGR assigned the completion of the required MOD-025 verifications to its engineering group. On at least one occasion in 2015, AGR’s compliance group met with the engineering group to review the MOD-025 verification requirements. However, the compliance group lacked an adequate process to actually track the timely completion of the MOD-025 verifications. AGR’s engineering group then assigned a low priority to the MOD-025 verifications. As a result, AGR failed to complete the required testing by the July 1, 2016 deadline. Subsequently, AGR attempted to schedule the Reactive Power capability verifications, but had to further delay the required testing because of unfavorable wind conditions. AGR finally completed the MOD-025 Reactive Power capability verifications on March 22, 2017, and submitted the results to its TP. The root cause of this noncompliance was an inadequate process to ensure compliance with all applicable requirements in MOD-025-2 R2. In particular, AGR lacked a sufficient process to make sure that its engineering group properly prioritized and timely performed the required MOD-025 verifications by the July 1, 2016 deadline. This issue started on July 1, 2016, when implementation of MOD-025-2 R2 became mandatory and enforceable for 40 percent of AGR’s applicable Facilities, and ended on March 22, 2017, when AGR completed the verification required by MOD-025-2 R2.1 for 40 percent of its Facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, AGR provided previously passing Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Reactive Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, AGR provided information similar to the required Reactive Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. Third, AGR’s subsequent Reactive Power capability verifications indicated that the Reactive Power capability at the two wind Facilities at issue was either consistent with or greater than the previous Reactive Power capability data provided through the regional process. Finally, the two AGR wind Facilities at issue have a combined name capacity of 402 MW and operate only at approximately a 26% and 28.5% capacity factor, respectively. As a result, any errors in the Facilities’ Real Reactive Power capability data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered AGR’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, AGR: 1) completed the Reactive Power capability verification for the two wind Facilities at issue; 2) elevated MOD-025 testing to a high-priority status within the AGR engineering group and dedicated additional resources to the timely performance of the required verifications; 3) enhanced the compliance group’s oversight of the engineering group’s progress on MOD-025 verification activities by updating the existing MOD-025 tracking spreadsheet; and 4) established a process in AGR’s task management program to track the 5-year compliance deadlines for MOD-025, including providing reminders to the AGR engineering group 12 months and 6 months before any applicable MOD-025 verification deadlines. Texas RE has verified the completion of all mitigation activity.
2017-06-29 | Texas Reliability Entity (Texas RE) | Avangrid Renewables (AGR) | NCR10259 | TRE2017016819 | MOD-025-2 | R1; R1.1 | On January 23, 2017, AGR submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with MOD-025-2 R1.1. Specifically, AGR failed to verify the Real Power capability of at least 40 percent of its applicable Facilities in accordance with MOD-025-2, Attachment 1 by July 1, 2016. Beginning in 2015, AGR assigned the completion of the required MOD-025 verifications to its engineering group. On at least one occasion in 2015, AGR’s compliance group met with the engineering group to review the MOD-025 verification requirements. However, the compliance group lacked an adequate process to actually track the timely completion of the MOD-025 verifications. AGR’s engineering group then assigned a low priority to the MOD-025 verifications. As a result, AGR failed to complete the required testing by the July 1, 2016 deadline. Subsequently, AGR attempted to schedule these verifications, but had to further delay the required testing because of unfavorable wind conditions. AGR finally completed the MOD-025 Real Power capability verifications on March 22, 2017, and submitted the results to its TP. The root cause of this noncompliance was an inadequate process to ensure compliance with all applicable requirements in MOD-025-2 R1. In particular, AGR lacked a sufficient process to make sure that its engineering group properly prioritized and timely performed the required MOD-025 verifications by the July 1, 2016 deadline. This issue started on July 1, 2016, when implementation of MOD-025-2 R1 became mandatory and enforceable for 40 percent of AGR’s applicable Facilities, and ended on March 22, 2017, when AGR completed the verification required by MOD-025-2 R1.1 for 40 percent of its Facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, AGR provided previously passing Real and Reactive Power verifications under substantially similar region-specific output conditions within the five years of performing its MOD-025 Real Power capability verifications, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, AGR provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. Finally, the two AGR wind Facilities at issue have a combined name capacity of 402 MW and operate only at approximately a 26% and 28.5% capacity factor, respectively. As a result, any errors in the Facilities’ Real output data would only have a minor impact on planning results. No harm is known to have occurred. Texas RE considered AGR’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, AGR: 1) completed the Real Power verification for the two wind Facilities at issue; 2) elevated MOD-025 testing to a high-priority status within the AGR engineering group and dedicated additional resources to the timely performance of the required verifications; 3) enhanced the compliance group’s oversight of the engineering group’s progress on MOD-025 verification activities by updating the existing MOD-025 tracking spreadsheet; and 4) established a process in AGR’s task management program to track the 5-year compliance deadlines for MOD-025, including providing reminders to the AGR engineering group 12 months and 6 months before any applicable MOD-025 verification deadlines. Texas RE has verified the completion of all mitigation activity.
2017-06-29 | Texas Reliability Entity (Texas RE) | EIF Channelview Cogeneration (EIFCVC) | NCR11430 | TRE2017017053 | BAL-001-TRE-1 | R6; R6.1 | On February 23, 2017, EIFCVC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with BAL-001-TRE-1 R6.1. In particular, EIFCVC discovered that it incorrectly set the maximum deadband setting for a single steam turbine combined-cycle unit. Pursuant to the Governor deadband settings set forth in BAL-001-TRE-1 R6.1, steam turbines with mechanical governors should be set with a maximum deadband of +/- 0.034 Hz. In turn, all other Generating Units/Generating Facilities should be set with a maximum deadband of +/- 0.017 Hz. In this instance, EIFCVC mistakenly assumed that the single generating unit’s Governor was a mechanical Governor and applied a +/- 0.034 Hz deadband setting. Subsequently, EIFCVC determined that this unit’s Governor was in fact an electronic Governor and not a mechanical one. As such, it should have been set with a maximum of +/- 0.017 Hz. Accordingly, on January 13, 2017, EIFCVC changed the deadband settings to the proper +/- 0.017 Hz settings. The root cause of this issue was an insufficient process to evaluate and determine all generating unit Governor types and their corresponding deadband settings. In particular, EIFCVC’s existing processes did not include sufficient checks to ensure that EIFCVC personnel properly identified the types of Governors at all generating units. This issue started on October 1, 2015, when EIFCVC’s turbine units were required to be 100% compliant with BAL-001-TRE-1 R6, and ended on January 13, 2017, when EIFCVC changed the logic set-point for the single generating unit Governor at issue from +/- 0.034 Hz to +/-0.017 Hz. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, throughout the duration of the Governor issue, EIFCVC continued to provide adequate Primary Frequency Response (PFR) performance. In particular, EIFCVC’s rolling 12-month average PFR remained above the required 0.75 performance level. Second, the maximum droop setting for the steam turbine combined-cycle unit was correct. Third, the other four EIFCVC units were compliant with BAL-001-TRE-1 R6, further limiting the impact of the incorrect Governor deadband settings at the single generating unit at issue. No harm is known to have occurred. Texas RE considered EIFCVC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EIFCVC: 1) changed the logic set-point for single generating unit’s deadband from +/- 0.034 Hz to +/-0.017 Hz; 2) revised its PFR procedure to clarify the types of Governors at its Generating Facility and provide clear instructions on appropriate deadband configurations for each Governor type; and 3) developed a new checklist to monitor PFR performance to ensure the PFR at each generating unit is adequate. Texas RE has verified the completion of all mitigation activity.
2017-06-29 | Texas Reliability Entity (Texas RE) | TX Jumbo Road Wind, LLC (Jumbo Road) | NCR11519 | TRE2017017288 | PRC-005-2(i) | R3 | On March 23, 2017, Jumbo Road submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3. In particular, Jumbo Road did not timely perform the required 4-month maintenance and testing activities for two of its Vented Lead-Acid (VLA) battery devices as required by PRC-005-2(i) R3, Table 1-4(a) on two separate occasions. On June 26, 2015, Jumbo Road performed testing on two of its VLA batteries. According to the maintenance intervals set forth in PRC-005-2(i), Table 1-4(a), Jumbo Road should have performed the next round of 4-month maintenance activities by October 31, 2015. However, Jumbo Road did not actually perform these required maintenance activities until November 19, 2015. Subsequently, Jumbo Road performed the next required 4-month maintenance activities on the two VLA batteries at issue on March 23, 2016. As such, Jumbo Road should have performed the next set of 4-month maintenance activities by July 31, 2016. However, Jumbo Road did not actually perform these required maintenance activities until August 26, 2016. The root cause of these noncompliance instances is an insufficient process to ensure the timely completion of all required maintenance and testing activities. In particular, Jumbo Road’s existing process did not contain sufficient checks to ensure personnel accurately tracked all upcoming maintenance and testing dates and provided sufficient lead time for third-party contractors to perform all maintenance and testing activities. This issue started on November 1, 2015, the day after the 4-month battery testing was due in the first instance, and ended on August 26, 2016, when Jumbo Road completed all required testing on the two batteries at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following five factors. First, the issue only involved approximately 1.96% (2/102) of Jumbo Road’s Protection System devices. Second, when Jumbo Road performed the required 4-month testing activities for the battery devices in question, the devices were found to be functioning properly. Third, each individual instance of noncompliance lasted a relatively short amount of time. In particular, battery testing was performed only 18 days late in the first instance and 25 days late in the second instance. Fourth, over the entire period of noncompliance, Jumbo Road produced an average of only 114.4 MW at the two affected wind generation Facilities. Finally, there were no misoperations during the noncompliance period. No harm is known to have occurred. Texas RE considered Jumbo Road’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Jumbo Road: 1) performed all required maintenance and testing activities on the two VLA batteries at issue; 2) reconfigured its compliance tracking software to send out reminder notifications 2 months in advance to provide additional lead time for maintenance and testing scheduling; 3) contracted with a second testing contractor who is available for situations where the first contractor cannot complete its testing responsibilities; and 4) developed a new documented maintenance and testing records review procedure, which includes monthly checks of all maintenance and testing dates to ensure accuracy. Texas RE has verified the completion of all mitigation activity.
2017-06-29 | Western Electricity Coordinating Council (WECC) | ProEnergy Services (PRSV) | NCR11550 | WECC2016016034 | PRC-019-2 | R1 | On August 19, 2016, PRSV submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, PRSV reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. The root cause of this issue was a misunderstanding of the implementation plan for the Standard and Requirement. PRSV interpreted the "two years after regulatory approval" as being two years from the standard effective date. WECC determined this issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of PRSV’s applicable Facilities, and ended on January 9, 2017, when PRSV completed verification activities of least 40 percent of its applicable Facilities. PRSV was in noncompliance for a total of 192 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PRSV failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. Such failure could result in loss of its generator field, instability, slipping poles, and/or damage to its turbines. However, this issue did not result in loss of its generator field, instability, slipping poles, and/or damage to its turbines. PRSV implemented a detective control by retaining a consultant to conduct a mock audit, which is how the issue was discovered. Additionally, upon discovery of the issue, PRSV immediately hired an engineering firm to verify the coordination of the voltage regulating system with its generator capabilities and Protection System devices; PRSV did not identify any changes to its coordination of the voltage regulating system. Further, the combined capacity for all of PRSV’s generating resources is approximately 69 MVA. No harm was known to have occurred. PRSV does not have any prior noncompliance with this Standard and requirement. | To remediate and mitigate this issue, PRSV: a. Completed verification activities of least 40 percent of its applicable Facilities; b. Developed a plant procedure to ensure the coordination of voltage regulating system controls and protection systems devices are completed, as well as when the coordination must take place; and c. Will continue conducting outside mock audits and internal self-assessments to prevent future reoccurrence of this issue.
2017-05-31 | Midwest Reliability Organization (MRO) | American Transmission Company, LLC (ATC) | NCR00685 | MRO2016016199 | TOP-007-0 | R1 | On July 15, 2016, ATC submitted a Self-Log stating that, as a Transmission Operator, it had an issue of TOP-007-0 R1. Specifically, ATC initiated an internal self-assessment to evaluate compliance with TOP-007-0. During that assessment, ATC was unable to locate evidence that established that ATC communicated two System Operating Limit (SOL) violations to its Reliability Coordinator. ATC initiated a broader review and discovered three additional occurrences. Four SOL violations were related to high voltage and one SOL violation was related to low voltage. The cause of this issue was a lack of training and awareness on the part of ATC operators, who believed that only thermal SOL violations were required to be reported to its Reliability Coordinator. This issue started on March 17, 2014, when the first SOL violation was not communicated, and ended on November 16, 2015, when the fifth SOL violation ended. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The SOL violations were brief, one high voltage SOL violation was seven and a half minutes, one high voltage SOL violation was less than two and a half minutes, and the remaining SOL violations lasted approximately 30 seconds. Additionally, none of the SOL violations were associated with an Interconnection Reliability Operating Limit (IROL). Further, the SOL violations were discovered during a self-assessment which indicates that ATC has functioning detective controls. No harm is known to have occurred. | To mitigate this issue, ATC: 1) completed an extent of condition review for all SOL exceedance situations from 2014 to June 2016; 2) immediately sent an email reminder to System Control Operators explaining SOL exceedance events, reinforcing the definition of an SOL violation, and the communication requirements associated with an SOL violation; 3) added more information to the System Control Operator action book regarding SOL exceedance events, reinforcing the definition of an SOL violation, and the communication requirements associated with an SOL violation, then required all System Control Operators to acknowledge that they had reviewed the action book update; and 4) conducted in-person meetings with System Control Operators to reinforce the information that was added to the action book. ATC stated that mitigating activities were complete as of December 31, 2016.
2017-05-31 | Northeast Power Coordinating Council (NPCC) | NSTAR Electric Company, (NSTAR) | NCR07180 | NPCC2017016883 | PRC-006-NPCC-1 | R4 | During a Compliance Spot Check conducted from September 21, 2016 to November 7, 2016, NPCC determined that NSTAR, as a Transmission Owner (TO), had an issue of PRC-006-NPCC-1 R4. NSTAR follows its Planning Coordinator (ISO-NE) in using Attachment C, UFLS Table 1, of the Standard for implementation of its UFLS program. NSTAR uses a load shed percentage at the 4th step of 7.78%, which was 0.28% above the defined range limits of 6.5% to 7.5%. Furthermore, the resulting cumulative load shed, expressed as a percentage of the TO load, was approximately 31.8%, which also exceeded by approximately 3% the defined range limits of 29.5% to 31.5%. This issue started on January 1, 2016, when the standard became enforceable, and ended on January 27, 2017, when NSTAR corrected the noncompliance by bringing its Stage 4 load shed percentage to 7.41% and its cumulative load shed percentage to 31.4%, both of which are now compliant with the standard's defined range limits. The root cause of this instance of noncompliance was human error, in that, during the review of the annual UFLS survey provided to ISO-NE in August of 2016, the threshold requirement exceedance was misinterpreted as acceptable due to the fact that the Reliability Coordinator was still within regional tolerances. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The cumulative load shedding overage of NSTAR's UFLS program was approximately 13 MW, a relatively small amount when compared with NSTAR's peak load for 2015 (approximately 4426 MW). Additionally, the ISO-NE's required winter operating reserves are approximately 2600 MW, a value which is often exceeded by a significant margin above that requirement. In conclusion, NSTAR's UFLS program's temporary exceedance could have been rectified in real-time by operating personnel. For all the above considerations, this instance of non-compliance poses a minimal risk on the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered NSTAR's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, NSTAR: 1) corrected the noncompliance by de-activating from its program one UFLS scheme, thus bringing its Stage 4 load shed percentage to 7.41% and its cumulative load shed percentage to 31.4%, within defined range limits. 2) Corrected the misinterpretation of the standard's requirements through resolution of this instance of noncompliance with appropriate personnel, which will prevent future recurrences of similar issues. NPCC has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Wisconsin Electric Power Company (WEPCO) | NCR00951 | RFC2016016478 | VAR-002-4 | R1 | On October 26, 2016, Wisconsin Public Service Corporation (WPS) submitted a Self-Report through WEPCO stating that, as a Generator Operator, it had an issue of VAR-002-4 R1. The GE Wind Farm Management System (WFMS) monitors voltage at the interconnection point for WPS. For WPS’s Crane Creek Wind Farm, this interconnection point is the 161 kV bus at the Jade Avenue substation. The WFMS sends VAR control signals to the individual turbines at the Crane Creek Wind Farm in order to maintain voltage at the interconnection point at 165 kV plus or minus 4 kV, per the voltage schedule issued from WPS’s Transmission Operator. At approximately 10:23 PM on September 22, 2016, the WFMS lost power due to a failure in the uninterruptible power supply serving the WFMS cabinet. This failure was unexpected and equipment-related. As part of its mitigation, WPS replaced the failed uninterruptible power supply. Upon this loss of power, some of the informational WFMS data points being monitored by WPS’s energy management system (such as number of turbines connected and number of turbines on line) indicated incorrect numbers. Other data points, such as the status or function of WFMS, indicated correct numbers. WPS did not receive any alarms or notifications regarding voltage regulation because the WFMS lost power. Following the loss of power to the WFMS, voltage at the interconnection point at the Jade Avenue substation increased and triggered a high voltage alarm at 11:02 PM on September 22, 2016 when the voltage exceeded 168 kV. Following receipt of this high voltage alarm, a WPS system operator contacted WPS’s Transmission Operator two minutes later at 11:04 PM to inform the Transmission Operator of the high voltage condition. Voltage gradually trended downward throughout the night of September 22 and the early morning of September 23, however the voltage occasionally spiked above 168 kV while the voltage began trending downward. At approximately 6:30 AM on September 23, 2016, WPS’s power generation manager noticed an error in the number of turbines on line for the Crane Creek Wind Farm during a routine check of the output from WFMS and determined that there was likely a communication issue. After further investigation, WPS contacted the onsite contractor at the Crane Creek Wind Farm at 9:28 AM to see if the SCADA screen related to WFMS could be refreshed. The contractor confirmed that he could not reestablish communication with the WFMS. After this, the contractor traveled to the substation to investigate more and discovered that there was no power to the WFMS cabinet. After reviewing the voltage levels from the night before, WPS determined that the Automatic Voltage Regulator (AVR) at Crane Creek had been out of service since the power failure began. WPS notified its Transmission Operator at 10:13 AM on September 23, 2016 that its AVR was out of service and had been out of service since the power failure. WPS made this notification to the Transmission Operator 11 hours and 50 minutes after the WFMS lost power and the AVR went out of service. Per VAR-002-4 R1, WPS has 30 minutes to notify its Transmission Operator of a change in status on its AVR. Resultantly, WPS violated VAR-002-4 R1. WPS reenergized the WFMS at noon on September 23, 2016 and at 12:45 PM WPS notified the Transmission Operator that the wind turbines were responding to voltage set point commands and that voltage regulation had returned to normal operations as the AVR had been turned back on and was properly functioning again. This noncompliance involves the management practices of grid maintenance and planning. Grid maintenance is involved because the uninterruptible power supply serving the WFMS cabinet failed and that failure is a root cause of this noncompliance. Poor planning is involved because WPS did not have a plan in place to timely receive alarms in the event of a power failure to the WFMS cabinet, which is also a root cause of this noncompliance. This issue started on September 22, 2016, when WPS failed to notify its Transmission Operator within 30 minutes after the AVR at its Crane Creek Wind Farm went out of service, and ended on September 23, 2016, when WPS put the AVR back into service and notified the Transmission Operator that the AVR was functioning again. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk posed by this noncompliance is that with the AVR out of service, voltage could spike or dip below the generator’s voltage schedule which may contribute to abnormal system voltages or voltage instability in the area. That risk is minimized here because during the time that the WFMS was out of service, voltage on the 161 kV bus at Jade Avenue fluctuated from a low of 164.1 kV to a high of 168.5 kV. This is within the Transmission Operator’s allowable voltage schedule range of 165.0 kV ± 4 kV. Once voltage exceeded 168 kV following the power supply failure, a high voltage alarm was triggered and WPS provided notification to its Transmission Operator regarding the high voltage. This notification occurred 41 minutes after the power failure that removed the AVR from service. This reduces the risk because although WPS did not timely notify its Transmission Operator of the change in status on its AVR, WPS notified its Transmission Operator of the high voltage event allowing the Transmission Operator to adjust the system voltage if needed. If the wind farm’s generation capacity was lost during this noncompliance, its impact on the BPS would be minimal because its generation fluctuated between only 9.5 MW and 36.7 MW from the time the WFMS lost power until notification was made to the Transmission Operator. Lastly, the voltage schedule is only to be followed any time generation is above 10 MW. No harm is known to have occurred. ReliabilityFirst considered WPS's VAR-002 R1 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, WPS: 1) restored power to the WFMS and the AVR was returned to service on September 23, 2016. WPS also notified its Transmission Operator that the AVR was returned to service on September 23, 2016; 2) established an alarm in its energy management system on October 6, 2016 using the Echo Setpoint signal from the WFMS. On October 18, 2016 the alarm was successfully tested to verify that the alarm would be received in the event of a power failure to the WFMS cabinet; 3) replaced the failed uninterruptible power supply on October 18, 2016; and 4) will install a hardwired alarm circuit between the WFMS and the Jade Avenue substation remote terminal unit to alarm for loss of power to the AVR, change in AVR status, and Echo Setpoint deviation. These alarms will be transmitted directly to WPS’s System Operating Center via the remote terminal unit.
2017-05-31 | SERC Reliability Corporation (SERC) | Florida Reliability Coordinating Council, Inc. (FRCC RC) | NCR00026 | SERC2016016045 | COM-002-2 | R2. | During a Compliance Audit conducted from May 10, 2016 to August 25, 2016, SERC determined that FRCC RC, as a Reliability Coordinator (RC), had an issue of COM-002-2 R2. FRCC RC did not issue a directive in a clear, concise, and definitive manner; did not ensure the recipient of the directive repeated the information back correctly; did not acknowledge the response as correct; and, did not repeat the original statement to resolve any misunderstandings. During the audit period, FRCC RC issued four directives. The SERC Audit team reviewed each and discovered that FRCC RC did not meet the directive communication requirements on one of the four directives. On September 10, 2015, the FRCC RC operator issued a directive to restore a 115 kV circuit due to an additional circuit outage, but the directive was unclear. In addition, the operator interrupted the individual receiving the directive when the individual requested clarification, and did not require the personnel receiving the directive to repeat the information back. This issue started and ended on September 10, 2015, when the FRCC RC operator did not meet the directive communication requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC RC’s failure to issue directives in a clear, concise, and definitive manner, ensure the recipient of the directive repeats the information back correctly, and acknowledge the response as correct or repeat the original statement to resolve any misunderstandings could increase the reliability risk of manual actions due to human error such as switching mistakes. However, FRCC RC issued the directive based on a Real-Time Contingency Analysis program output. The impact in this situation would have been limited to the delay of restoration of approximately 20 MW of load to avoid a SOL exceedance of the 115kV transmission line if the identified contingency had occurred real time. The SERC audit team determined that the FRCC RC operating group did not have a systemic problem implementing COM-002-2 and this was an isolated incident involving one system operator. No actual Bulk Electric System overloads occurred during the event. No harm is known to have occurred. SERC considered FRCC RC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, FRCC RC provided additional training on the FRCC Communications and Coordination procedure to the FRCC RC System Operators.
2017-05-31 | SERC Reliability Corporation (SERC) | Gibson City Energy Center, LLC (GCEC) | NCR11434 | SERC2016015909 | MOD-025-2 | R1. | On July 11, 2016, GCEC submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. GCEC stated that it had not completed its generator real power output verification testing by July 1, 2016. The implementation plan for MOD-025-2 requires the GO to verify its generator real power output in annual increments beginning with 40% of its generation by July 1, 2016 and 100% by July 1, 2019. GCEC has two 114 MW combustion turbines, so in order to comply with the requirement, GCEC was required to perform the real power verification of at least one of the units by July 1, 2016. GCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for MOD-025-2 R1 compliance, and did not understand the requirement for verification during unit testing. On June 29, 2016, a third-party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to GCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and inadequate contract oversight. GCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, and ended February 21, 2017 when GCEC completes the required real power testing and reports the results to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to provide verification of real power capability may result in inaccurate planning models and inaccurate assessment of Bulk Power System reliability. However, GCEC had already submitted real power data to the Transmission Planner. GCEC contributes only 228 MW to the grid while operating and operates at approximately a 5% capacity factor. Therefore, any errors in the plant data would present a minor variation in planning results. SERC considered GCEC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GCEC: 1) conducted the required verification at Unit 1; 2) submitted the necessary data to the Transmission Planner; 3) developed and annually reviews an internal compliance procedure while also updating upon any standard revisions; 4) implemented an internal software product that allows for tracking of compliance reporting functions and internal deadlines that GCEC deemed appropriate; 5) added MOD-025 to the compliance tracker with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies; 6) utilizes third party mock audits and internal self-assessments as a second check on the compliance tracker; and 7) conducts bi-weekly compliance calls among site managers to ensure plant staffs are aware of upcoming deadlines and compliance obligations
2017-05-31 | SERC Reliability Corporation (SERC) | Gibson City Energy Center, LLC (GCEC) | NCR11434 | SERC2016015910 | MOD-025-2 | R2. | On July 11, 2016, GCEC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R1. GCEC stated that it had not completed its verification testing by July 1, 2016. The implementation plan for MOD-025-2 R2 requires the GO to verify its generator reactive output in annual increments beginning with 40% of its generation by July 1, 2016 and 100% by July 1, 2019. GCEC has two identical 114 MW combustion turbines. In order to comply with the implementation plan, GCEC needed to perform the verification on one of the units by July 1, 2016. GCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for MOD-025-2 R2 compliance, and did not understand the requirement for verification during unit testing. On June 29, 2016, a third-party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to GCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and lack of contract oversight. GCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, and ended February 21, 2017, when GCEC completed the required reactive power testing and reported the results to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to provide verification of real and reactive power capability may result in inaccurate planning models and inaccurate assessment of BPS reliability. However, GCEC contributes only 228 MW to the grid while operating and operates at approximately a 5% capacity factor. Therefore, any errors in the plant data would present a minor variation in planning results. The implementation plan for MOD-025-2 allows five years for full implementation of the requirements. GCEC completed verification of both units within the first quarter following the enforcement date resulting in a minimal risk to the BPS. No harm is known to have occurred. SERC considered GCEC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GCEC: 1) conducted the required verification at Unit 1; 2) submitted the necessary data to the Transmission Planner; 3) developed and annually reviews an internal compliance procedure while also updating upon any standard revisions; 4) implemented an internal software product that allows for tracking of compliance reporting functions and internal deadlines that GCEC deemed appropriate; 5) added MOD-025 to the compliance tracker with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies; 6) utilizes third party mock audits and internal self-assessments as a second check on the compliance tracker; and 7) conducts bi-weekly compliance calls among site managers to ensure plant staffs are aware of upcoming deadlines and compliance obligations.
2017-05-31 | SERC Reliability Corporation (SERC) | Gibson City Energy Center, LLC (GCEC) | NCR11434 | SERC2016016457 | PRC-024-2 | R1 | On October 28, 2016, GCEC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R1. GCEC did not complete its verification of generator frequency protection set points by July 1, 2016. The implementation plan for PRC-024-2 requires the GO to verify its generator frequency Protection System set points in annual increments beginning with 40% of its generation by July 1, 2016. GCEC has two 114 MW combustion turbines, so in order to comply with the requirement, GCEC was required to perform the verification of at least one of the units by July 1, 2016. GCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for PRC-024-2 R1 compliance and did not understand the requirement for verification of the frequency protection set point. On June 29, 2016, a third-party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to GCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and contract oversight. GCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, and ended September 30, 2016 when GCEC completed the required verification the frequency protection set point on one of its units. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GCEC’s failure to verify the frequency protection set points could result in generators unnecessarily tripping off-line. However, GCEC contributes only 228 MW to the grid while operating and operates at approximately a 5% capacity factor. When GCEC operated, no trips occurred due to incorrect set points and when GCEC performed the verification, no changes were required. Also, GCEC completed the required 40% verification just three months late. No harm is known to have occurred. SERC considered GCEC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, GCEC: 1) contracted with a different Engineering firm to perform the verification of the data necessary to confirm compliance; 2) developed a plant procedure which demonstrates that coordination of protective relaying is crucial such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, as well as when the coordination must take place; and 3) added the PRC-024 requirements to the GCEC internal compliance tracking software to ensure the tasks are completed annually as required.
2017-05-31 | SERC Reliability Corporation (SERC) | Gibson City Energy Center, LLC (GCEC) | NCR11434 | SERC2016016456 | PRC-024-2 | R2 | On October 28, 2016, GCEC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R2. GCEC did not complete its verification generator voltage protection set points by July 1, 2016. The implementation plan for PRC-024-2 requires the GO to verify its generator voltage Protection System set points in annual increments beginning with 40% of its generation by July 1, 2016. GCEC has two 114 MW combustion turbines, so in order to comply with the requirement, GCEC was required to perform the verification of at least one of the units by July 1, 2016. GCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for PRC-024-2 R2 compliance and did not understand the requirement for verification of the voltage protection set point. On June 29, 2016, a third-party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to GCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and contract oversight. GCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, and ended September 30, 2016 when GCEC completed the required verification the voltage protection set point on one unit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GCEC’s failure to verify the voltage protection set points could result in generators unnecessarily tripping off-line. However, GCEC contributes only 228 MW to the grid while operating and operates at approximately a 5% capacity factor. When GCEC operated, no trips occurred due to incorrect set points and when GCEC performed the verification, no changes were required. GCEC completed the required 40% verification just three months late. No harm is known to have occurred. SERC considered GCEC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, GCEC: 1) contracted with a different Engineering firm to perform the verification of the data necessary to confirm compliance; 2) developed a plant procedure which demonstrates that coordination of protective relaying is crucial such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, as well as when the coordination must take place; and 3) added the PRC-024 requirements to the GCEC internal compliance tracking software to ensure the tasks are completed annually as required.
2017-05-31 | SERC Reliability Corporation (SERC) | James River Genco, LLC (JamesRv) | NCR01262 | SERC2017016763 | PRC-019-2 | R1. | On January 10, 2017, JamesRv submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. JamesRv did not meet the NERC implementation schedule for verifying the proper coordination of its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for 40% of its Facilities by July 1, 2016. JamesRv incorrectly believed that 40% coordination was required by July 1, 2017 as opposed to July 1, 2016 based on the approval date of PRC-019-2 instead of PRC-019-1; therefore, JamesRv did not verify the voltage regulating system controls coordination by July 1, 2016. On December 6, 2016, JamesRv identified this issue during its scope assessment review of Standards and Requirements with implementation schedules after identifying and self-reporting a similar PRC-024 issue. JamesRv determined that the main cause of the issue was its misunderstanding of the implementation schedule. This issue started on July 1, 2016, when JamesRv did not meet the implementation schedule through March 22, 2017, when JamesRv completed the required verification. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. JamesRv’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, the JamesRv Facility consists of two steam turbine generators with output capacity of 57 MW per unit in the PJM region that has more than 176,500 MW of installed generation; therefore, the two 57 MW units that were noncompliant would have a minimal impact if they tripped offline. JamesRv reported that there have been no unit trips based on incorrect coordination. No harm is known to have occurred. SERC considered JamesRv's compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, JamesRv: 1) verified coordination of the voltage regulator controls and generator protection devices; and 2) created a notification in the form of a recurring preventive maintenance work order or as an obligation that escalates until completed in the JamesRv tracking system for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable standards incorporating the NERC initial notification of confirmation of the implementation or due date(s); To mitigate this issue, JamesRv will complete the following mitigation activities by June 30, 2017: 1) create a tracking spreadsheet to monitor compliance deadlines and status for responsible parties. The Corporate Reliability Standards Compliance Group will coordinate all new or modified standards with the necessary engineering groups within the vendors organization, to include, but not limited to submittal of verification to the region (SERC) to ensure the understanding of all aspects of the Reliability Standard including Requirements, implementation plans, and schedules, as necessary. The objective is to ensure JamesRv develops a complete implementation strategy to convey acceptable approaches with clear understanding, responsibilities, and timelines.
2017-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Dogwood Power Management, LLC (Dogwood) | NCR11250 | SPP2016016215 | MOD-025-2 | R1; R1.1, R1.2 | On September 28, 2016, Dogwood submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of noncompliance with MOD-025-2 R1 because the real power capability determined for the two combustion turbine generators (CTGs) at the Dogwood Energy Facility was not determined in accordance with MOD-025-2. Specifically, the real power capability test Dogwood performed was run for 15 minutes and not for one hour as required by Section 2.1.1 of MOD-025-2 Attachment 1 (R1.1). Additionally, Dogwood provided the test data to the Southwest Power Pool (SPP) and not directly to its Transmission Planner (TP), Kansas City Power and Light (KCPL) (R1.2). The two CTGs at the Dogwood Energy Facility represent 66% of Dogwood’s generating capacity. Accordingly, Dogwood failed to verify the real power capability for at least 40 percent of its generation facilities by July 1, 2016. The duration of this instance of noncompliance was from July 1, 2016, the effective date for completion of verification of the real power capability for 40% of Dogwood’s generation facilities, through December 15, 2016, the date Dogwood provided its TP with the real power capability of its two CTGs or 66% of its generation facilities. The root cause of this instance of noncompliance was a combination of human error and insufficient oversight to ensure adherence to MOD-025-2 R1. Dogwood staff incorrectly assumed the real power capability established in the testing performed to comply with SPP Criteria 12.1.6, would fulfill the testing requirements of MOD-025-2 R1. Further, Dogwood’s NERC standards review program did not require its NERC Compliance Manager to review all updated procedures and testing prepared by its subject-matter experts to ensure compliance with the NERC standard at issue. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate decisions affecting the reliability of the BPS. Notwithstanding Dogwood’s failure to perform its real power capability tests in accordance with MOD-025-1 Attachment 1, it has provided the Southwest Power Pool (SPP) with test results indicative of the real power capability of its CTGs. Such test results are required by the SPP Criteria and are updated annually as part of the SPP Model Development Process. The SPP Model Development Working Group (MDWG) develops the planning models utilized by SPP members such as KCPL, Dogwood’s TP. Additionally, Dogwood’s TP, KCPL is a member of the SPP MDWG. The SPP Model Development Process makes it highly unlikely that Dogwood’s TP, KCPL is utilizing incorrect real power capability data for its CTGs in its planning models. The two CTG’s that are at issue are small, i.e., significantly less than 200 MW and are connected to the BES at 161 kV. No actual harm is known to have occurred as a result of this noncompliance. SPP RE reviewed Dogwood’s violation history and determined that it has no prior instances of noncompliance with MOD-025 or a similar standard. | To mitigate this minimal risk instance of noncompliance, Dogwood proposes to complete the following mitigation activities by July 1, 2017: 1) complete real power capacity verification testing in accordance with the requirements of MOD-025-2; 2) deliver test results to the TP in accordance with MOD-025-2 R1.2; 3) update internal NERC compliance procedures with respect to MOD-025-2 to require compliance with the testing criteria for all requirements of MOD-025-2; 4) to ensure future testing relies on currently effective NERC requirements, Dogwood supplemented its NERC standard review program to require that the NERC Compliance Manager review all updated procedures and testing prepared by the respective subject-matter experts to ensure that such procedures and testing programs fully satisfy the NERC standard at issue; and 5) require subject matter experts and their supervisors to participate in a refresher training program with respect to the procedures required to be followed in the implementation of new and revised NERC standards and the importance of review of upcoming new or revised standards early on to ensure compliance on the date that compliance is required.
2017-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Dogwood Power Management, LLC (Dogwood) | NCR11250 | SPP2016016216 | MOD-025-2 | R2; R2.1, R2.2 | On September 28, 2016, Dogwood submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of noncompliance with MOD-025-2 R2 because the lagging reactive power capability determined for the two combustion turbine generators (CTGs) at the Dogwood Energy Facility was not determined in accordance with MOD-025-2. Specifically, the lagging reactive power capability test Dogwood performed was run for 15 minutes and not for one hour as required by Section 2.1.1 MOD-025-2 Attachment 1 (R2.1). Additionally, Dogwood provided the test data to the Southwest Power Pool (SPP) and not directly to its Transmission Planner (TP), Kansas City Power and Light (KCPL) (R2.2). The two CTGs at the Dogwood Energy Facility represent 66% of Dogwood’s generating capacity. Accordingly, Dogwood failed to verify the lagging reactive power capability for at least 40 percent of its generation facilities by July 1, 2016. The duration of this instance of noncompliance was from July 1, 2016, the effective date for completion of verification of the reactive power capability for 40% of Dogwood’s generation facilities, through December 15, 2016, the date Dogwood provided its TP with the real power capability of its two CTGs or 66% of its generation facilities. The root cause of this instance of noncompliance was a combination of human error and insufficient oversight to ensure adherence to MOD-025-2 R2. Dogwood staff incorrectly assumed reactive power capability testing performed to comply with SPP Criteria 12.1.6, would fulfill the testing requirements of MOD-025-2 R2. Further, Dogwood’s NERC standards review program did not require its NERC Compliance Manager to review all updated procedures and testing prepared by its subject-matter experts to ensure compliance with the NERC standard at issue. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the Transmission Planner (TP) to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate decisions affecting the reliability of the BPS. Notwithstanding Dogwood’s failure to perform its reactive power capability test in accordance with Attachment 1, it did perform a reactive power capability test, but for a shorter test period, and provided the results of the test to the Southwest Power Pool (SPP). Such test results are required by the SPP Criteria and are updated annually as part of the SPP Model Development Process. The SPP Model Development Working Group (MDWG) develops the planning models utilized by SPP members such as KCPL, Dogwood’s TP. Additionally, Dogwood’s TP, KCPL is a member of the SPP MDWG. The SPP Model Development Process makes it highly unlikely that Dogwood’s TP, KCPL is utilizing incorrect reactive power capability data in its planning models. The two CTG’s that are at issue are small, i.e., significantly less than 200 MW and are connected to the BES at 161 kV. No actual harm is known to have occurred as a result of this noncompliance. SPP RE reviewed Dogwood’s violation history and determined that it has no prior instances of noncompliance with MOD-025-2 or a similar standard. | To mitigate this minimal risk instance of noncompliance, Dogwood proposes to complete the following mitigation activities by July 1, 2017: 1) complete reactive power capacity verification testing in accordance with the requirements of MOD-025-2; 2) deliver test results to the TP in accordance with MOD-025-2 R2.2; 3) update internal NERC compliance procedures with respect to MOD-025-2 to require compliance with the testing criteria for all requirements of MOD-025-2; 4) to ensure future testing relies on currently effective NERC requirements, Dogwood supplemented its NERC standard review program to require that the NERC Compliance Manager review all updated procedures and testing prepared by the respective subject-matter experts to ensure that such procedures and testing programs fully satisfy the NERC standard at issue; and 5) require subject matter experts and their supervisors to participate in a refresher training program with respect to the procedures required to be followed in the implementation of new and revised NERC standards and the importance of review of upcoming new or revised standards early on to ensure compliance on the date that compliance is required.
2017-05-31 | Southwest Power Pool Regional Entity (SPP RE) | Lea Power Partners, LLC (LEAPP) | NCR10301 | SPP2016016133 | PRC-019-2 | R1; R1.1, 1.1.1, 1.1.2 | On September 8, 2016, LEAPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of noncompliance with PRC-019-2 R1, R1.1, R1.1.1, and R1.1.2 because it failed to verify the coordination of the voltage regulating system controls, (including in-service limiters and protection functions) with the equipment capabilities and settings of the Protection System devices at its Hobbs generation station. Specifically, during a PRC-019 program assessment in August 2016, LEAPP discovered that: (1) the V/Hz exciter limiters for Combustion Turbine Generator 1 (CTG1) and Combustion Turbine Generator 2 (CTG 2) were not set to operate prior to the generator V/Hz protection relays in the range of 0 – 2 seconds; and (2) the Steam Turbine Generator (STG) V/Hz exciter limiter was not set to operate before a generator V/Hz inverse time relay in the range above 60 seconds. The duration of this instance of noncompliance was from July 1, 2016, the effective date of PRC-019-2 R1, through November 16, 2016, the date LEAPP completed the coordination studies for the Hobbs Generation Station. The root cause of this instance of noncompliance was a combination of human error and ineffective controls. Hobbs plant personnel incorrectly assumed that the MOD-025, MOD-026 and MOD-027 Model Validation and Reactive Capability Testing performed in 2015 fulfilled the requirements of PRC-019. Further, LEAPP scheduled its PRC-019 program assessment after the PRC-019 July 1, 2016, effective date thereby discovering the noncompliance after the date compliance with PRC-019 was required. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly coordinate exciter limiters and generator protection relays can cause the generator Automatic Voltage Regulator to impose unacceptable operating conditions on the generator. Such conditions, i.e. overexcitation and underexcitation, have the potential to affect the reliability of the BPS by decreasing the generators ability to withstand system voltage events and increasing the probability of generator trips due to loss of synchronism and generator field overloads. As to the STG, the risk is mitigated because the V/Hz limiter would have operated consistent with the requirements of PRC-019-2 by limiting overexcitation to 1.08 V/Hz (per unit) for events lasting less than 60 seconds. As to the CTG units, the risk is mitigated because the V/Hz protection relays were set at 1.15 V/Hz in the 0 to 2 second range, substantially above the 1.05 V/Hz (per unit) set point for the V/Hz limiter and in the range greater than two seconds the V/Hz protection relays were set consistent with the requirements of PRC-019-2. The CTG generators are connected to the BES at 115 kV, a low transmission voltage, and individually are less than 200 MW. The other overexcitation protection relays at the Hobbs generating station were set consistent with the requirements of PRC-019-2. The Hobbs generating station provides wholesale power to a single wholesale customer and does not provide reactive support to the BES. The noncompliance was identified by LEAPP during an internal review and was limited in duration. No actual harm is known to have occurred as a result of this noncompliance. LEAPP has no relevant prior violations for PRC-019-2 R1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, LEAPP: 1) performed a root cause analysis of its noncompliance; 2) performed coordination studies for CTG 1, CTG 2, and the STG; 3) performed a Protection Device coordination study for CTG 1, CTG 2, and the STG; 4) implemented the relay settings recommended in the studies; and 5) added additional staff to bolster its oversight of NERC compliance. SPP RE has verified the completion of all mitigation activity.
2017-05-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE – Kansas City District (COEKS) | NCR01357 | SPP2016016256 | PRC-019-2 | R1; R1.1, 1.1.1, 1.1.2 | On September 30, 2016, COEKS submitted a Self-Certification stating that, as a Generator Owner and Transmission Owner, it had an issue of noncompliance with PRC-019-2 R1, R1.1, R1.1.1, and R1.1.2. COEKS failed to verify coordination of all voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions, specifically, in-service limiters and protection functions. COEKS is a 214 MW hydroelectric generating facility. The root cause of this instance of noncompliance was COEKS’s error in calculating the effective date of PRC-019-2. The Implementation Plan for PRC-019-2 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” PRC-019-2 was approved by FERC on March 20, 2014 and the rule became effective on May 27, 2014. Consequently, the implementation date for PRC-019-2 was July 1, 2016. COEKS erroneously used July 1, 2016 as the “regulatory approval” date and calculated two years forward (July 1, 2018) as the implementation date for PRC-019-2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of PRC-019-2 R1, through February 23, 2017, the date COEKS completed all mitigation activity. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly set the in-service limiters can cause the generator Automatic Voltage Regulator to impose unacceptable operating conditions on the generator. Such conditions have the potential to affect the reliability of the BPS by decreasing the generators ability to withstand system voltage events and increasing the probability of generator trips due to loss of synchronism and generator field overloads. Notwithstanding, COEKS is a 214 MW hydroelectric generating facility with minimal impact on the BPS. Accordingly, during the review and verification, COEKS discovered that its original, existing settings were properly coordinated and no changes were necessary. Therefore, all were appropriately set at the time the standard became effective. No harm occurred as a result of this noncompliance. COEKS has no relevant prior violations for PRC-019-2 R1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, COEKS: 1) verified that voltage regulating system controls were coordinated with the equipment capabilities and settings of the applicable Protection System devices and functions; and 2) included a schedule in the maintenance management program that will initiate review and verification of the settings on a four year cycle, to be completed by the five year interval. SPP RE has verified the completion of all mitigation activity.
2017-05-31 | Texas Reliability Entity (Texas RE) | Formosa Utility Venture, Ltd. (FUV) | NCR04059 | TRE2017016751 | IRO-010-1a | R3 | During a Compliance Audit conducted from October 18, 2016 through January 4, 2017, Texas RE determined that FUV, as a Generator Owner (GO) and Generator Operator (GOP), had an issue with IRO-010-1a R3. FUV failed to provide data and information, as specified, to its Reliability Coordinator (RC) with which it has a reliability relationship. Specifically, FUV did not correctly provide the gross MW value of one of its generation units via telemetry as specified by its RC. Texas RE subsequently determined that the duration of this issue was from December 14, 2015 until February 21, 2017. Accordingly, Texas RE determined that FUV had an issue with IRO-010-1a R3 from December 14, 2015 until December 31, 2016. FUV then had an issue with IRO-010-2 R3 from January 1, 2017 until February 21, 2017. Texas RE further determined that, for purposes of this issue, there was no substantive change in FUV’s compliance obligations under the applicable versions. Electric Reliability Council of Texas (ERCOT) Nodal Protocol 6.5.5.2(2)(b) requires generators in the ERCOT interconnection to provide their gross real power in MW to its RC via telemetry. The RC data specification issued on January 1, 2017 pursuant to IRO-010-2 reiterates the requirement in ERCOT Nodal Protocol 6.5.5.2(2)(b) to provide gross real power to the RC and provides that entities must provide gross real power in MWs through telemetry every two seconds on a continuous basis. On December 14, 2015, FUV shutdown one of its generation units. During the shutdown, FUV determined that the data point telemetering the unit’s gross MW value was stuck, resulting in some MW output continuing to be telemetered to the RC despite the unit in question being offline. As a result of this stuck data point, FUV did not telemeter accurate gross MW values to its RC as required under ERCOT Nodal Protocol 6.5.5.2(2)(b). Throughout 2016, FUV experienced four additional issues with its gross MW value data point for the same generation unit. These occurred both following planned unit outages, as well as during normal operations. As these issues occurred, FUV performed maintenance on the computer systems associated with the gross MW data point in question and also made arrangements with a contractor to investigate and correct the ongoing issues with its gross MW value telemetry. In December 2016, the contractor in question identified an issue with the algorithm used to calculate the gross MW value data point and corrected it. Nevertheless, FUV experienced an additional issue with the gross MW data point in February 2017, which resulted in FUV again not telemetering accurate gross MW values as now required under the RC IRO-010-2 data specification. FUV performed an additional investigation and determined that this new issue related to faulty wiring. FUV replaced the wiring in question on February 21, 2017, ending the issue. Texas RE determined that the root cause of this noncompliance was a combination of technical issues in telemetering a single generating unit’s gross MW value. In particular, FUV experienced issues involving both an incorrect calculation algorithm and hardware failures resulting in it telemetering inaccurate gross MW values to its RC. This issue occurred from December 14, 2015, the earliest date of incorrect gross MW value telemetry for the single generating unit at issue, until February 21, 2017, the date FUV corrected all gross MW value telemetry issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, FUV’s generation unit operates on a Private Use Network (PUN), only intermittently exports generation to the grid, and did not export any power to the grid during this issue. Second, throughout the duration of this issue, FUV continued to accurately telemeter the net MW value from the generating unit at issue to its RC. As such, FUV’s RC continued to have accurate information regarding the actual generation FUV’s generating unit provided to the Bulk Electric System (BES) at all times. Third, the generation unit at issue is small, with a maximum capability of only 155 MW, and typically produces significantly less power than its maximum capability, even for use within FUV’s PUN. Finally, the telemetry issue only affected a single data point for relatively short periods of time. In particular, over the entire period of noncompliance, the gross MW value was only incorrect for approximately 13.42% of the time. No harm is known to have occurred. Texas RE considered FUV’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FUV: 1) corrected hardware issues and the malfunctioning algorithm causing the issues with the single generating unit’s gross MW telemetry; 2) implemented a simulated shut-down of the applicable generation unit to ensure that the gross MW value would display 0 MW; 3) replaced the wiring associated with the gross MW telemetry data point; 4) modified its operating procedures to include special instructions for its operating personnel to verify that the gross MW value displays 0 MW on its SCADA system following a shut-down of the unit; and 5) created a process to actively monitor the gross MW value, checking it regularly with each shift change to ensure it is accurately telemetered. Texas RE has verified the completion of all mitigation activity.
2017-05-31 | Texas Reliability Entity (Texas RE) | Formosa Utility Venture, Ltd. (FUV) | NCR04059 | TRE2017016753 | TOP-003-1 | R1 | During a Compliance Audit conducted from October 18, 2016 through January 4, 2017, Texas RE determined that FUV, as a Generator Operator (GOP), had an issue with TOP-003-1 R1. Specifically, FUV failed to provide outage information daily to its Transmission Operator (TOP) for scheduled generator outages planned for the next day. Prior to a planned outage of an FUV generation unit, FUV properly submitted a planned outage notification to its TOP. In that outage notification, FUV specified that the outage would be from December 16, 2015 until December 28, 2015. Due to delays in maintenance on the unit in question, however, FUV extended the outage past the December 28, 2015 date provided in the original outage schedule information. Nevertheless, the FUV personnel tasked with updating the outage information to reflect this outage extension did not do so until January 6, 2016. The root cause of the issue was that FUV did not have adequate controls in place to ensure that it properly updated the scheduled outage information provided to its TOP with any changes. In particular, FUV relied primarily on a single individual to perform the outage update task and this individual was on vacation when the outage extension occurred. This issue started on December 28, 2015, when FUV failed to notify its TOP about its continued outage, and ended on January 6, 2016, when FUV provided updated outage information to its TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, FUV’s generation unit operates on a Private Use Network (PUN) and only intermittently exports generation to the grid. As a result, FUV’s TOP would not have anticipated FUV exporting power onto the grid at the end of the originally scheduled outage period. Second, the generation unit at issue is small, with a maximum capability of only 155 MW, and typically produces significantly less power than its maximum capability, even for use within FUV’s PUN. Third, throughout the duration of the issue, the physical responsive reserves throughout the ERCOT interconnection exceeded the FUV generation unit’s maximum power capability. Finally, over the entire period of noncompliance, FUV continued to provide its TOP with other data points, including FUV’s Net MW values, that the TOP could use in its real-time operations. No harm is known to have occurred. Texas RE considered FUV’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FUV: 1) provided updated outage information to its TOP; 2) updated its outage scheduling process by assigning responsibility for updating outage schedules to a new third-party energy manager with additional resources and controls; and 3) transitioned responsibility for coordinating forced outages to the designated third-party energy manager with additional staff and 24/7 resources. Texas RE has verified the completion of all mitigation activity.
2017-05-31 | Texas Reliability Entity (Texas RE) | Keechi Wind, LLC (KWLLC) | NCR11497 | TRE2017017029 | MOD-025-2 | R1; R1.1 | On February 17, 2017, KWLLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R1. Specifically, KWLLC failed to verify the Real Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. In mid-August 2016, KWLLC determined that its single wind Facility had not completed the required Real Power verification by the July 1, 2016 deadline. KWLLC made arrangements with several contractors to perform the required Real Power verifications in conjunction with other required testing activities. KWLLC then submitted its completed Real Power capability verification on January 23, 2017 to its Transmission Planner (TP) as required. The root cause of this issue was that KWLLC misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, KWLLC mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This issue started on July 1, 2016, when implementation of MOD-025-2 R1 became mandatory and enforceable, and ended on January 23, 2017, when KWLLC submitted its completed Real Power capability verification for its single generation Facility in accordance with MOD-025-2, Attachment 1 to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following two factors. First, KWLLC previously provided passing Real and Reactive Power verifications under substantially similar region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, KWLLC provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. No harm is known to have occurred. Texas RE considered KWLLC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, KWLLC: 1) completed the required Real Power verification for its single generation Facility; 2) established a process to provide its personnel with a series of reminders regarding future MOD-025-2 verification deadlines; and 3) provided notice to affected employees of this new MOD-025-2 reminder process. Texas RE has verified the completion of all mitigation activity.
2017-05-31 | Texas Reliability Entity (Texas RE) | Keechi Wind, LLC (KWLLC) | NCR11497 | TRE2017017030 | MOD-025-2 | R2; R2.1 | On February 17, 2017, KWLLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R2. Specifically, KWLLC failed to verify the Reactive Power capability of its single generation Facility in accordance with MOD-025-2, Attachment 1 by July 1, 2016. In mid-August 2016, KWLLC determined that its single wind Facility had not completed the required Reactive Power verification by the July 1, 2016 deadline. KWLCC made arrangements with several contractors to perform the required Reactive Power verifications in conjunction with other required testing activities. On January 23, 2017, KWLLC submitted its completed Reactive Power capability verification to its Transmission Planner (TP) as required. The root cause of this issue was that KWLLC misinterpreted the enforceable dates specified in the MOD-025-2 implementation plan for single generation unit Facilities. In particular, KWLLC mistakenly believed that because it only owned a single generation Facility, it did not need to meet the July 1, 2016 40 percent implementation deadline. This issue started on July 1, 2016, when implementation of MOD-025-2 R1 became mandatory and enforceable, and ended on January 23, 2017, when KWLLC submitted its completed Reactive Power capability verification for its single generation Facility in accordance with MOD-025-2, Attachment 1 to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, KWLLC previously provided passing Real and Reactive Power verifications under substantially similar region-specific output conditions in 2015, limiting the scope of the missing verification data that would be incorporated into transmission planning models. Second, KWLLC provided information similar to the required Reactive Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. Third, the single KWLLC generation Facility has not experienced any Reactive Power capability changes since it was commissioned in 2015. Finally, KWLLC did not receive any requests to provide Reactive Power support during the issue duration. No harm is known to have occurred. Texas RE considered KWLLC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, KWLLC: 1) completed the required Reactive Power verification for its single generation Facility; 2) established a process to provide its personnel with a series of reminders regarding future MOD-025-2 verification deadlines; and 3) provided notice to affected employees of this new MOD-025-2 reminder process. Texas RE has verified the completion of all mitigation activity.
2017-05-31 | Texas Reliability Entity (Texas RE) | Brazos Electric Power Co Op, Inc. (BEPC) | NCR04015 | TRE2017017237 | COM-002-4 | R1; R1.5; R1.6 | During a Compliance Audit conducted from February 20, 2017 to March 16, 2017, Texas RE determined that BEPC, as a Transmission Operator (TOP), had an issue with COM-002-4 R1. Specifically, BEPC’s documented communications protocols did not explicitly identify instances requiring time identification when issuing and receiving Operating Instructions and the format for that time identification as required under COM-002-4 R1.5. In addition, BEPC’s documented communications protocols did not specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing Operating Instructions as required under COM-002-4 R1.6. The root cause of this issue was that BEPC’s documentation did not fully address all requirements in COM-002-4 R1. In particular, BEPC’s documented communications protocols only included general references to regional operating protocols to address compliance with COM-002-4 R1.5 and 1.6 and did not contain specific instructions regarding how to perform these two communications tasks as required. This issue started on July 1, 2016, when COM-002-4 R1 became enforceable, and ended on March 1, 2017, when BEPC updated it communications protocol document to include specific language regarding time identification and format, as well as the required nomenclature for Transmission interface Elements and Facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue in question related solely to BEPC’s documented communications protocols. Texas RE verified that BEPC personnel used appropriate time identification and Transmission Element and Facility nomenclature in its applicable communications. Additionally, BEPC possesses a number of other controls to ensure the proper implementation of required communications protocols, including clocks displaying the required 24-hour format in its control room, a wall map board with correct Transmission Element and Facility designations, and System Operator control software containing correct time and Transmission Element and Facility information and formats. Texas RE further determined that BEPC provided training to all System Operators regarding the use of proper nomenclature and appropriate 24-hour time clock usage. Finally, although BEPC excluded requirements 1.5 and 1.6 from its process document, BEPC had adequately documented communications protocols for all other required aspects of Operating Instruction communications. No harm is known to have occurred. Texas RE considered BEPC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BEPC: 1) updated its existing process document to include specifications pertaining to COM-002-4 R1.5 and R1.6; 2) uploaded the updated process document to an internal location that is viewable to all BEPC employees; and 3) notified all applicable personnel regarding the communications protocol documentation changes, highlighting the required use of a 24-hour clock and appropriate Transmission Element and Facility nomenclature. Texas RE has verified the completion of all mitigation activity.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Aragonne Wind, LLC. (AGW) | NCR05014 | WECC2017016994 | MOD-025-2 | R1: R1.1 | On February 14, 2017, AGW submitted a Self-Certification stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 R1.1 Specifically, AGW certified that it failed to verify, and provide to its Transmission Planner, the Real Power capability of its applicable Facility in accordance with MOD-025-2 Attachment 1 by the effective date of the Standard. The root cause of this issue was AGW management’s failure to identify MOD-025-2 as applicable to its Facility and complete requisite verification by the enforcement date. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for AGW’s Facility and ended February 1, 2017, when AGW completed the Real Power capability testing of its Facility. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AGW failed to verify Real Power capability by the MOD-025-2 enforcement date. Without accurate Real Power capability, the Transmission Planner may not have accurate gross and net system capability data to produce accurate planning models used to assess Bulk Electric System (BES) reliability. However, AGW discovered this issue during an internal compliance audit. Additionally, AGW is a wind farm rated at 90 MW that relies solely on wind conditions for its Real Power capabilities. Actual Real Power capability is 53.9 MW. Based on the controls in place and nature and size of generation, WECC determined that the issue had a minimal likelihood of affecting the transmission planning models or reliability of the BES. No harm is known to have occurred. AGW does not have previous noncompliances of this Standard and Requirement. | To mitigate this issue, AGW: 1) performed Real Power capability tests and provided results to the Transmission Planner; 2) hired a Director of NERC Compliance to increase internal oversight and proactively provide continuous monitoring of its internal compliance program; and 3) implemented weekly meetings with a consultant that include: upcoming Self-Certifications, data submittals, procedure reviews and sampling, compliance training, procedure revisions, FERC/NERC Standards, Requirements, or criteria changes and any regulatory changes impacting the plant. WECC verified completion of AGW's mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Aragonne Wind, LLC. (AGW) | NCR05014 | WECC2017016995 | MOD-025-2 | R2: R2.1 | On February 14, 2017, AGW submitted a Self-Certification stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 R2.1 Specifically, AGW certified that it failed to verify, and provide to its Transmission Planner, the Reactive Power capability of its applicable Facility in accordance with MOD-025-2 Attachment 1 by the effective date of the Standard. The root cause of this issue was AGW management’s failure to identify MOD-025-2 as applicable to its Facility and complete requisite verification by the enforcement date. WECC determined that this issue began on July 1, 2016, when MOD-025-2 became mandatory and enforceable for AGW’s Facility and ended February 1, 2017, when AGW completed the Reactive Power capability testing of its Facility. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AGW failed to verify Reactive Power capability by the MOD-025-2 enforcement date. Without accurate Reactive Power capability, the Transmission Planner may not have accurate gross and net system capability data to produce accurate planning models used to assess Bulk Electric System (BES) reliability. However, AGW discovered this issue during an internal compliance audit. Additionally, AGW is a wind farm rated at 90 MW that relies solely on wind conditions for its Reactive Power capabilities. Actual Reactive Power capability is -5.8 Mvar. Based on the controls in place and nature and size of generation, WECC determined that the issue had a minimal likelihood of affecting the transmission planning models or reliability of the BES. No harm is known to have occurred. AGW does not have previous noncompliances of this Standard and Requirement. | To mitigate this issue, AGW: 1) performed Real Power capability tests and provided results to the Transmission Planner; 2) hired a Director of NERC Compliance to increase internal oversight and proactively provide continuous monitoring of its internal compliance program; and 3) implemented weekly meetings with a consultant that include: upcoming Self-Certifications, data submittals, procedure reviews and sampling, compliance training, procedure revisions, FERC/NERC Standards, Requirements, or criteria changes and any regulatory changes impacting the plant. WECC verified completion of AGW's mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC2016016544 | PRC-024-2 | R1 | On November 17, 2016, AVGO submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1 and R2. Specifically, AVGO reported that it failed to set its frequency protective relaying in accordance with Attachment 1 by the effective date of PRC-024-2. This issue began July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of AVGO’s applicable generating units, and ended March 8, 2017, when AVGO adjusted its frequency protective relaying in accordance with Attachment 1. The root cause of this issue was AVGO’s misunderstanding regarding the effective date of the Standard. AVGO completed the verification analyses on its three applicable Facilities on June 30, 2016, and believed such verification was sufficient to meet the implementation deadline for PRC-024-2. | In this instance, AVGO failed to set its frequency protective relaying for two if its three applicable Facilities such that it would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to frequency excursions within the “no trip zone”. However, the two over-frequency relays had been set correctly to trip outside the no trip zone. So if the units had experienced a frequency excursion, its current settings for three of the four under-frequency relays for each unit would have caused them to trip inside the no trip zone. The three under frequency relays would have operated up to 58.8 Hz for 110 seconds, 58.4Hz for 22 seconds and 57.8 Hz for 2 seconds before tripping inside the no trip zone. The settings were later adjusted to operate up to 58.8 Hz for 180 seconds, 58.4Hz for 30 seconds and 57.8 Hz for 7.5 seconds before tripping outside the no trip zone. Additionally, AVGO completed verification studies and scheduled setting changes prior to the implementation deadline; however, such changes were scheduled for AVGO’s next planned outage in Spring 2017. This issue concerned one under-voltage time delay setting on each unit. The settings in scope have never caused any of the units to trip, and no harm is known to have occurred. Based on this information, WECC determined that these issues posed minimal risk to the reliability of the BPS. WECC considered AVGO's compliance history and determined there were no relevant instances of prior noncompliance. | To mitigate this issue, AVGO: 1) adjusted settings to meet the Requirement; and 2) established periodic notifications and reminders to ensure tracking and completion of annual and five-year reviews for PRC-024 compliance tasks. WECC verified completion of AVGO’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC2016016545 | PRC-024-2 | R2 | On November 17, 2016, AVGO submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1 and R2. Specifically, AVGO reported that it failed to set its voltage protective relaying in accordance with Attachment 2 by the effective date of PRC-024-2. This issue began July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of AVGO’s applicable generating units, and ended March 8, 2017, when AVGO adjusted its voltage protective relaying in accordance with Attachment 2. The root cause of this issue was AVGO’s misunderstanding regarding the effective date of the Standard. AVGO completed the verification analyses on its three applicable Facilities on June 30, 2016, and believed such verification was sufficient to meet the implementation deadline for PRC-024-2. | In this instance, AVGO failed to set its voltage protective relaying for two if its three applicable Facilities such that it would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to voltage excursions within the “no trip zone”. However, the over-voltage relay settings had been set correctly to trip outside the no trip zone. If the units had experienced a voltage excursion, its current settings for the under-voltage relay for each unit would have caused them to operate up to 0.9 pu voltage for 1 second before tripping inside the no trip zone. The under-voltage relay setting was later adjusted to operate up to 0.9 pu for 5 seconds which would enable it to trip outside the no trip zone. Additionally, AVGO completed verification studies and scheduled setting changes prior to the implementation deadline; however, such changes were scheduled for AVGO’s next planned outage in Spring 2017. This issue concerned one under-voltage time delay setting on each unit. The settings in scope have never caused any of the units to trip, and no harm is known to have occurred. Based on this information, WECC determined that these issues posed minimal risk to the reliability of the BPS. WECC considered AVGO's compliance history and determined there were no relevant instances of prior noncompliance. | To mitigate this issue, AVGO: 1) adjusted settings to meet the Requirement; and 2) established periodic notifications and reminders to ensure tracking and completion of annual and five-year reviews for PRC-024 compliance tasks. WECC verified completion of AVGO’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Balancing Authority of Northern California (BANC) | NCR11118 | WECC2017017230 | INT-006-4 | R1 | On January 31, 2017, BANC submitted a Self-Log stating that, as a Balancing Authority (BA), it had a possible issue of noncompliance with INT-006-4 R1.2. Specifically, BANC reported that on September 12, 2016, BANC’s scheduling software automatically approved a 5 MW Arranged Interchange request (eTag) that did not have a valid scheduling path between BANC and the Adjacent Balancing Authority. The root cause of this issue was a programming error in BANC’s scheduling software. WECC determined that this issue began at 6:00 a.m. on September 12, 2016, when BANC approved an eTag after it failed adjacency validation, and ended at 7:00 a.m., when the eTag completed its full duration of the Request for Interchange; for a total of one hour of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BANC failed to deny an eTag with an invalid Scheduling Path as prescribed in R1.2. Such failure could result in adverse impacts on unscheduled parallel energy flow, Inadvertent Energy between BAs, and possible unplanned overload of transmission systems. However, this issue concerned a single, 5 MW eTag, did not affect adjacent entities, and BANC resolved the programming error that caused the issue the following day. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. | To mitigate this issue, BANC: a) Fixed the programming error in its scheduling software; and b) Implemented process enhancements to its scheduling software to ensure that future eTags and schedules for delivery to the bus in scope have designated the correct adjacent BA for delivery of energy, otherwise they will be automatically denied. WECC verified completion of the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | CalPeak Power Panoche LLC (CPPA) | NCR05053 | WECC2017016999 | PRC-019-2 | R1 | On February 14, 2017, CPPA submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, CPPA reported that it failed to coordinate its voltage regulating system controls with its generator capabilities and Protection System devices for its applicable Facility by the enforcement date of the Standard. The root cause of this issue was less than adequate planning. CPPA management underestimated the amount of time and resources it needed to complete coordination before the enforcement date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of CPPA’s applicable Facilities, and is currently ongoing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CPPA failed to coordinate its voltage regulating system controls with its generator capabilities and Protection System devices for at least 40% of its applicable Facilities by the enforcement date of the Standard. Such failure could result in lack of situational awareness. However, CPPA was in the process of performing the coordination and verification study prior to the enforcement date. Additionally, this issue concerned a single 71 MVA Facility and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System. CPPA identified and self-reported the issue described herein and does not have previous noncompliances of the Standard and Requirement. WECC considered these factors in its designation of this issue as a CE. | To remediate and mitigate this issue, CPPA will: 1) Complete the PRC-019-2 coordination and verification study of its generating unit in accordance to the Standard and submit the verification results to its Transmission Planner; 2) Created automated Preventive Maintenance work orders that escalate tasks until they are completed in CPPA’s Company Obligation Tracking System; 3) Created notifications that will prompt Plant Management to review future Reliability Standards; 4) Developed a more robust oversight program to verify proper enforcement and effective dates of future Reliability Standards and implementation plans; and 5) Created a tracking spreadsheet to monitor compliance deadlines and the status for each responsible party. CPPA’s Corporate Reliability Standards Compliance Group will coordinate all new or modified Standards with the necessary engineering groups.
2017-05-31 | Western Electricity Coordinating Council (WECC) | CalPeak Power Vaca-Dixon LLC (CPVD) | NCR05054 | WECC2017017000 | PRC-019-2 | R1 | On February 14, 2017, CPVD submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, CPVD reported that it failed to coordinate its voltage regulating system controls with its generator capabilities and Protection System devices for its applicable Facility by the enforcement date of the Standard. The root cause of this issue was less than adequate planning. CPVD underestimated the amount of time and resources it needed to complete coordination before the enforcement date of the Standard. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of CPVD’s applicable Facilities, and is currently ongoing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CPVD failed to coordinate its voltage regulating system controls with its generator capabilities and Protection System devices for at least 40% of its applicable Facilities by the enforcement date of the Standard. Such failure could result in lack of situational awareness. However, CPVD was in the process of performing the coordination and verification study prior to the enforcement date. Additionally, this issue concerned a single 60.5 MW Facility and no harm is known to have occurred. In addition, CPVD has never experienced a trip during an operational or testing of its AVR. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System. CPVD identified and self-reported the issue described herein and does not have previous noncompliances of the Standard and Requirement. WECC considered these factors in its designation of this issue as a CE. | To mitigate this issue, CPVD will complete the following mitigation activities by September 29, 2017: 1) Complete the PRC-019-2 coordination and verification study of its generating unit in accordance to the Standard and submit the verification results to its Transmission Planner; 2) Created automated Preventive Maintenance work orders that escalate tasks until they are completed in CPVD’s Company Obligation Tracking System; 3) Created notifications that will prompt Plant Management to review future Reliability Standards and Implementation Plans to ensure future compliance with the same and similar Standards; 4) Developed a more robust oversight program to verify proper enforcement and effective dates of future Reliability Standards and implementation plans; and 5) Created a tracking spreadsheet to monitor compliance deadlines and the status for each responsible party. CPVD’s Corporate Reliability Standards Compliance Group will coordinate all new or modified Standards with the necessary engineering groups.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Catalina Solar 2, LLC (CSII) | NCR11680 | WECC2016016511 | VAR-002-4 | R1 | On November 10, 2016, CSII submitted a Self-Report stating that, as a Generator Operator (GOP), it had a possible issue of noncompliance with VAR-002-4 R1. Specifically, on September 29, 2016, during a checklist review, CSII discovered that the automatic voltage regulator (AVR) on its generator was not in service. The root cause of this issue was failure to follow documented procedure; CSII had a checklist process, but failed to ensure the AVR was in service during commercial operation. WECC determined that this issue began on September 29, 2016 at 12:00 a.m., the operating hour during which CSII’s NERC registration became effective, and ended at 5:35 p.m., when the AVR was placed in service, for approximately of 17 hours of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CSII failed to operate its generator in AVR control mode. Such failure could potentially result on the loss of 18 MW of non-synchronous generation if a voltage excursion occurred. However, CSII maintained the voltage schedule while the AVR was out of service, the unit did not trip, and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). WECC notes that CSII has identified and self-reported this issue described herein and took voluntary corrective action to remediate and mitigate this issue. For these reasons, WECC considers CSII’s compliance history a factor in its designation of this remediated issue as a CE. | To remediate and mitigate this issue, CSII: 1) Placed the AVR in service; 2) Notified relevant personnel of the possible noncompliance and reiterated expectations of NERC compliance and adherence to established procedures/processes; 3) Reviewed its program and guidance documents for VAR-002-4 and provided these documents to relevant personnel; 4) Conducted a training presentation for operating personnel; and 5) Performed an “extent of condition assessment” to ensure compliance in all areas as of the NERC registration date.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Cedar Creek Wind Energy, LLC (CCWE) | NCR10165 | WECC2017016986 | MOD-025-2 | R1 | On February 10, 2017, CCWE submitted Self-Certifications stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirement 1 and 2. Specifically, CCWE reported that it failed to verify Real and Reactive Power capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard and Requirements. The root cause of these issues was a less than adequate compliance process. Specifically, CCWE management was not aware of the new Standard and Requirements and thus, did not complete requisite testing by the enforcement date. WECC determined that these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of CCWE’s applicable Facilities, and ended on December 7, 2016, when CCWE tested its applicable Facilities, for a total of 159 of days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, CCWE failed to verify the Real and Reactive Power capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 of the Standard and Requirements. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, these issues were discovered during an internal compliance review, which was conducted following organizational changes and expansion of CCWE’s compliance staff. The combined capacity of CCWE’s applicable Facilities is approximately 300 MW of wind generation, and no harm is known to have occurred. CCWE’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the Bulk Power System. WECC notes that CCWE has identified and self-certified the issues described herein, and does not have previous noncompliances of this Standard and Requirements. WECC considered these factors in its designation of these remediated issues as CEs. | To remediate and mitigate these issues, CCWE: 1) Completed verification testing and submitted completed Attachment 2 forms to the Transmission Planner; 2) Hired a contractor to assist with its NERC Compliance Program by implementing a tracking system; and c) Will conduct weekly meetings to review and discuss its NERC Compliance Program. WECC verified that CCWE completed the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Cedar Creek Wind Energy, LLC (CCWE) | NCR10165 | WECC2017016987 | MOD-025-2 | R2 | On February 10, 2017, CCWE submitted Self-Certifications stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirement 1 and 2. Specifically, CCWE reported that it failed to verify Real and Reactive Power capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard and Requirements. The root cause of these issues was a less than adequate compliance process. Specifically, CCWE management was not aware of the new Standard and Requirements and thus, did not complete requisite testing by the enforcement date. WECC determined that these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of CCWE’s applicable Facilities, and ended on December 7, 2016, when CCWE tested its applicable Facilities, for a total of 159 of days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, CCWE failed to verify the Real and Reactive Power capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 of the Standard and Requirements. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, these issues were discovered during an internal compliance review, which was conducted following organizational changes and expansion of CCWE’s compliance staff. The combined capacity of CCWE’s applicable Facilities is approximately 300 MW of wind generation, and no harm is known to have occurred. CCWE’s Balancing Authority, Transmission Planner, and Transmission Operator, plan and operate the grid with the expectation that the generation may be unavailable at any given time. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the Bulk Power System. WECC notes that CCWE has identified and self-certified the issues described herein, and does not have previous noncompliances of this Standard and Requirements. WECC considered these factors in its designation of these remediated issues as CEs. | To remediate and mitigate these issues, CCWE: 1) Completed verification testing and submitted completed Attachment 2 forms to the Transmission Planner; 2) Hired a contractor to assist with its NERC Compliance Program by implementing a tracking system; and 3) Will conduct weekly meetings to review and discuss its NERC Compliance Program. WECC verified that CCWE completed the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Cedar Creek Wind Energy, LLC (CCWE) | NCR10165 | WECC2017016990 | PRC-019-2 | R1; R1.1; R1.1.1.; R1.1.2. | On February 10, 2017, CCWE submitted a Self-Certification stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, CCWE reported that it failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices for its applicable Facility by the enforcement date of the Standard. The root cause of this issue was a less than adequate compliance process. Specifically, CCWE management was not aware of the new Standard and Requirement and thus, did not complete requisite testing by the enforcement date. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for CCWE’s applicable Facility, and is currently ongoing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CCWE failed to verify coordination of its voltage regulating system controls with the equipment capabilities and settings of its applicable Protection System devices for its applicable Facility by the enforcement date of the Standard. Such failure could potentially result in the loss of the generator field, system instability, slipping poles, and/or damage to the turbines. However, the Facility in scope is an intermittent wind Facility, so in the unlikely event that CCWE experienced a loss of its generator field, system reliability would not be compromised since wind generation is not typically utilized as a firm resource; therefore, CCWE plans and operates the grid with the expectation that the generation may be unavailable at any given time. Further, this issue was discovered during an internal compliance review, which was conducted following organizational changes and expansion of CCWE’s compliance staff. Additionally, CCWE’s applicable on-shore wind Facility’s capacity is approximately 300 MW of generation, and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). WECC notes that CCWE has identified and self-certified this issue described herein, and does not have previous noncompliances of this Standard and Requirement. WECC considered these factors in its designation of this issue as a CE. | To mitigate this issue, CCWE will complete the following mitigation activities by July 14, 2017: 1) complete verifying coordination of its applicable Facility in accordance to the Standard and make changes to its settings, if needed; 2) implement an action tracking system that will be maintained by a third-party NERC Consultant to monitor and track compliance with future NERC standards. 3) will conduct weekly meetings that are hosted by the NERC Consultant and attended by CCWE’s the Director of regulatory Compliance, VP of Operations, and staff, to review and discuss its NERC Compliance Program; and 4) establish project completion dates in advance of the enforcement dates to prevent future reoccurrence of the same or similar issues.
2017-05-31 | Western Electricity Coordinating Council (WECC) | City of St George (CYSG) | NCR05096 | WECC2016016625 | MOD-025-2 | R1 | On December 5, 2016, CYSG submitted Self-Reports stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirements 1 and 2. Specifically, CYSG reported that it failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. The root cause of these issues was a misunderstanding of the phased-in Implementation Plan for MOD-025-2. WECC determined these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of CYSG’s generating units, and ended on November 9, 2016, when CYSG tested 40 percent of its generation units, for a total of 131 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CYSG failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as CYSG tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Therefore, if a real-time contingency occurred, requiring the generating unit to respond, the current data would be satisfactory for mitigating that contingency. Additionally, the combined capacity of both units is approximately 40 MW. No harm is known to have occurred. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the Bulk Power System (BPS). WECC notes that CYSG identified and self-reported the issues described herein and does not have previous noncompliances of these Standards and Requirements. For these reasons, WECC considers CYSG’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, CYSG: 1) Completed Real and Reactive Power testing of at least 40 percent of its generating units, per Attachment 1; 2) Provided its Transmission Planner with verification of the Real and Reactive Power capability for at least 40 percent of its applicable generating units, per Attachment 2; 3) Developed a process for tracking and storing NERC compliance data. This document serves as a process to provide an accurate source of information for its Subject Matter Experts, timeline for reviews, changes to Standards, and document controls in storage; 4) Hired an outside contractor to consult CYSG on new Standards.
2017-05-31 | Western Electricity Coordinating Council (WECC) | City of St George (CYSG) | NCR05096 | WECC2016016626 | MOD-025-2 | R2 | On December 5, 2016, CYSG submitted Self-Reports stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirements 1 and 2. Specifically, CYSG reported that it failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. The root cause of these issues was a misunderstanding of the phased-in Implementation Plan for MOD-025-2. WECC determined these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of CYSG’s generating units, and ended on November 9, 2016, when CYSG tested 40 percent of its generation units, for a total of 131 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CYSG failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as CYSG tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Therefore, if a real-time contingency occurred, requiring the generating unit to respond, the current data would be satisfactory for mitigating that contingency. Additionally, the combined capacity of both units is approximately 40 MW. No harm is known to have occurred. For these reasons, WECC determined that these issues posed a minimal risk to the reliability of the Bulk Power System (BPS). WECC notes that CYSG identified and self-reported the issues described herein and does not have previous noncompliances of these Standards and Requirements. For these reasons, WECC considers CYSG’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, CYSG: 1. Completed Real and Reactive Power testing of at least 40 percent of its generating units, per Attachment 1; 2. Provided its Transmission Planner with verification of the Real and Reactive Power capability for at least 40 percent of its applicable generating units, per Attachment 2; 3. Developed a process for tracking and storing NERC compliance data. This document serves as a process to provide an accurate source of information for its Subject Matter Experts, timeline for reviews, changes to Standards, and document controls in storage; 4. Hired an outside contractor to consult CYSG on new Standards.
2017-05-31 | Western Electricity Coordinating Council (WECC) | City of St George (CYSG) | NCR05096 | WECC2016016641 | PRC-019-2 | R1 | On December 5, 2016, CYSG submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 Requirement 1. Specifically, CYSG reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings for at least 40 percent of its applicable Facilities by the effective date of the Standard. The root cause of this issue was a misunderstanding of the phased-in Implementation Plan for PRC-019-2. WECC determined this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of CYSG’s applicable Facilities, and ended on November 9, 2016, when CYSG completed the required verification activities for both of its units, for a total of 131 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CYSG failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. Such failure could result in loss of its generator field, instability, slipping poles, and/or damage to its turbines. However, CYSG did not experience any loss of its generator field, instability, slipping poles, and/or damage to its turbines due to miscoordination. Additionally, this issue did not affect coordination because verification did not identify any changes to CYSG’s controls or protection settings. The combined capacity of both units is approximately 80 MW. No harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the BPS. WECC notes that CYSG identified and self-reported the issues described herein and does not have previous noncompliances of these Standards and Requirements. For these reasons, WECC considers CYSG’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, CYSG: 1) Completed verification activities of least 40 percent of its applicable Facilities; 2) Developed a process for tracking and storing NERC compliance data. This document will serve as a process to provide an accurate source of information for its Subject Matter Experts, timeline for reviews, changes to Standards, and document controls in storage; and 3) Hired an outside contractor to consult CYSG on new Standards.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Colorado Springs Utilities (CSU) | NCR05106 | WECC2016016466 | MOD-027-1 | R5 | On November 2, 2016, CSU submitted a Self-Report stating that, as a Transmission Planner (TP), it had a possible issue of noncompliance with MOD-027-1 R5. Specifically, CSU reported that its TP department did not provide a written response to its Generator Owner (GO) department indicating whether a revised generator model validation report was usable within the timeframe required by MOD-027-1 R5. The root cause of this issue was human error; CSU’s GO department notified its TP department of the revised generator model validation report, but its TP department missed the communication and failed to process and verify the model revision. WECC determined that this issue began on February 4, 2016, the day after the response was due, and ended October 12, 2016, when CSU provided the response, for a total of 251 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CSU’s TP department failed to provide a response to its GO department regarding a revised governor model validation report within 90 days. Such failure could potentially result in an inaccurate representation of the power response of a 208 MW unit to system frequency variations in the planning model of the TP department. However, revisions to the model were non-material and would not have affected the outcome of the Transmission Planning study, the issue was limited to a single 208 MW generator, and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System. WECC notes that CSU has identified and self-reported this issue described herein, does not have previous noncompliances of this Standard and Requirement, and has provided WECC with documentation of its internal compliance program. WECC considered these factors in its designation of this remediated issue as a CE. | To remediate and mitigate this issue, CSU: 1) Ran system models, in its TP department, using the revisions to the unit governor model to determine the extent of any differences between the updated model and the previous model to determine whether the model is usable, per requirement R5; 2) Provided notification from its TP department to its GO department that the revised model was usable; 3) Implemented a new programmatic process to review deadlines that are triggered by activity-based events, such as MOD-027-1 R5, on at least a quarterly basis; and 4) Implemented a process to ensure communications between the GO and TP department are not missed. CSU’s Compliance staff is responsible for contacting its GO and the TP departments to ensure necessary communications take place in accordance to the Standards. WECC verified that CSU completed the above-listed mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Energy Keepers Incorporated (EKI) | NCR11568 | WECC2016016123 | MOD-025-2 | R1; R1.1 | On September 8, 2016, EKI submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, EKI reported it failed to verify Real Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding of the implementation plan for the Standard and Requirement. EKI was under the impression that because all of its generating units underwent model validation in July of 2012 and received WECC Generator Testing and Validation Certificates, that this testing would be sufficient for demonstrating compliance with MOD-025-2. WECC determined this issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of EKI’s generating units, and is ongoing. EKI is scheduled to complete testing of at least 40 percent of its generating units in accordance with Attachment 1 by July 26, 2017. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, EKI failed to verify the Real Power capability of at least 40 percent of its generating units in accordance with Attachment 1 of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as EKI tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Further, no changes have been made that would require EKI to expedite model revalidation; and the results of the model validation were provided to the appropriate entities. Additionally, upon discovery of the issue, EKI immediately scheduled a vendor to test and collect the necessary data. The combined capacity of these generating resources is approximately 235 MVA. All units underwent model validation in July of 2012 and received WECC Generator Testing and Validation Certificates, which do not expire until 2018. Confirmation from the TO/TP/TOP has also been received stating no further modeling information is needed prior to the previously planned model revalidation in 2017 as per WECC regional 5 year requirement. No changes have been made which would require expedited model revalidation. No harm was known to have occurred. For these reasons, WECC determined these issues posed minimal risk to the reliability of the Bulk Power System. WECC notes that EKI has identified and self-reported this issue described herein and does not have previous noncompliances of this Standard and its Requirements. For these reasons, WECC considers EKI’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, RBFR will complete the following mitigation activities by October 10, 2017: 1) perform Real and Reactive Power capability testing; 2) integrate its MOD-025-2 periodic testing into one system; 3) submit test reports within 90 days of testing completion; 4) completed a MOD-025-2 gap analysis to identify deficiencies; and 5) completed a root cause analysis;
2017-05-31 | Western Electricity Coordinating Council (WECC) | Energy Keepers Incorporated (EKI) | NCR11568 | WECC2016016324 | MOD-025-2 | R2; R2.1 | On October 7, 2016, EKI submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, EKI reported it failed to verify Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding of the implementation plan for the Standard and Requirement. EKI was under the impression that because all of its generating units underwent model validation in July of 2012 and received WECC Generator Testing and Validation Certificates, that this testing would be sufficient for demonstrating compliance with MOD-025-2. WECC determined this issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of EKI’s generating units, and is ongoing. EKI is scheduled to complete testing of at least 40 percent of its generating units in accordance with Attachment 1 by July 26, 2017. | his issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, EKI failed to verify the Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as EKI tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Further, no changes have been made that would require EKI to expedite model revalidation; and the results of the model validation were provided to the appropriate entities. Additionally, upon discovery of the issue, EKI immediately scheduled a vendor to test and collect the necessary data. The combined capacity of these generating resources is approximately 235 MVA. No harm was known to have occurred. For these reasons, WECC determined these issues posed minimal risk to the reliability of the Bulk Power System. WECC notes that EKI has identified and self-reported this issue described herein and does not have previous noncompliances of this Standard and its Requirements. For these reasons, WECC considers EKI’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, RBFR will complete the following mitigation activities by October 10, 2017: 1) Perform Real and Reactive Power capability testing; 2) Conduct a MOD-025-2 gap analysis to identify deficiencies; 3) Perform a root cause analysis; 4) Integrate its MOD-025-2 periodic testing into one system; and 5) Submit test reports within 90 days of testing completion.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2016016706 | PRC-005-2(i) | R3 | During a Compliance Audit conducted from December 5, 2016 through December 8, 2016, WECC determined that IID, as a Generator Owner, had possible issue of noncompliance with PRC-005-2(i) R3. Specifically, WECC auditors discovered that IID had not performed the minimum maintenance activities within the maximum maintenance intervals for two batteries as prescribed in Table 1-4(b). The root cause of this issue was human error. IID mistakenly categorized and maintained the two batteries as vented lead acid batteries, which are subject to Table 1-4(a), rather than valve-regulated lead-acid batteries, which are subject to Table 1-4(b). WECC determined that this issue began on July 1, 2016, when completion of the 6-month maintenance activity for the two batteries was due, and ended on January 19, 2017, when IID completed the testing requirements prescribed in Table1-4(b), for a total of 202 of days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, IID failed to perform minimum maintenance activities within the maximum maintenance intervals for two batteries as prescribed in Table 1-4(b). Such failure could potentially result in degradation of equipment or the Misoperation of associated Protection System devices. However, IID continuously monitored the voltage and current for the batteries by using a battery charger monitoring system. Had any issues occurred, an alarm would have notified an operator immediately. Additionally, IID performed battery maintenance per the manufacturer specifications and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System. WECC reviewed IID’s compliance history and determined that IID does not have relevant prior noncompliance with PRC-005. IID took voluntary corrective action to remediate and mitigate this issue, and has provided WECC documentation of its internal compliance program. WECC considered these factors in its designation of this remediated issue as a CE. | To mitigate this issue, IID: 1) Completed the required 6-month and 18-month maintenance for the two batteries as prescribed in Table 1-4(b); 2) Created and distributed a flow chart that clearly defines maintenance responsibilities; 3) Provided a refresher training course on its current Protection System Maintenance Plan to all applicable employees. This included a refresher on how to identify different types of substation batteries to ensure they are put on the correct maintenance sheets, and maintained appropriately; 4) Installed a monitoring device that complies with the 6-month maintenance activities to measure the battery cell/unit internal ohmic values; and 5) Will complete the required 18-month maintenance activity during its annual Generation scheduled maintenance outages.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Malacha Hydro Limited Partnership GOP (MHGOP) | NCR05229 | WECC2017017123 | FAC-008-3 | R2 | On February 28, 2017, MHGOP submitted a Self-Certification stating that as a Generator Owner, it had a possible issue of noncompliance with FAC-008-3 R2. Specifically, when MHGOP revised its documentation for Facility Ratings methodology in preparation for Version 3 of the Standard, it failed to transfer all requisite information into the revised documentation. This issue began January 1, 2013, when the current version of the Standard became mandatory and enforceable to MHGOP, and ended March 1, 2017, when MHGOP revised its documented Facility Ratings methodology. The root cause of this issue was less than adequate documentation due to an editorial mistake. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, MHGOP failed to documents its Facility Ratings methodology as prescribed by R2. Such failure could result in determination and designation of inaccurate Facility Ratings. However, this issue only concerned documentation. Although MHGOP failed to document Facility Ratings methodology, it actually implemented acceptable methodology to establish Facility Ratings. Additionally, this issue concerned a single location with Facilities corresponding to 30 MW of generation; had this issue resulted in determination and designation of inaccurate Facility Ratings, the risk to the BPS would still have been limited. No harm is known to have occurred. MHGOP does not have previous noncompliances of this Standard and Requirement. | To mitigate this issue, MHGOP revised its documented Facility Ratings methodology. WECC verified completion of MHGOP’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Merced Irrigation District (MEID) | NCR05234 | WECC2016016559 | PRC-019-2 | R1 | On November 22, 2016, MEID submitted a Self-Report stating that as a Generator Owner and Transmission Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, MEID reported that it failed to verify coordination of voltage regulating system controls with equipment capabilities and Protection System device settings for its applicable Facility by the effective date of the Standard. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for MEID’s applicable Facility, and is ongoing. The root cause of this issue was a misunderstanding regarding the effective date of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MEID failed to verify coordination items prescribed by R1.1.1 and R1.1.2 for its applicable Facility by the effective date of the Standard. Such failure limits MEID’s awareness of the coordination of its applicable Facility, and could result in over-voltage damage to MEID’s applicable Facility, or an unnecessary trip during a system event that should not cause a trip. However, this issue concerned a single 94 MW Facility, which has not had any significant changes or upgrades since MEID’s last verification, and no harm is known to have occurred. MEID does not have previous noncompliances of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, MEID: 1) will verify coordination items and execute any identified setting adjustments; and 2) will hire additional staff and a third-party contractor to assist in interpretation of existing and future applicable Standards, and to ensure enforcement deadlines are understood and met. The proposed completion date for the above-listed activities is July 14, 2017.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Merced Irrigation District (MEID) | NCR05234 | WECC2016016564 | MOD-025-2 | R1 | On November 22, 2016, MEID submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, MEID reported that it failed to verify the Real Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MEID’s applicable Facility, and is ongoing. The root cause of this issue was a misunderstanding regarding the effective date of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MEID failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single 94 MW Facility, and no harm is known to have occurred. MEID tested the Facility in accordance with the WECC Model Validation Policy prior to the effective date of the Standard, and it is unlikely that untimely verification will significantly affect current planning models. MEID does not have previous noncompliances of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, MEID: 1) will complete testing in accordance with Attachment 1; and 2) will hire additional staff and a third-party contractor to assist in interpretation of existing and future applicable Standards, and to ensure enforcement deadlines are understood and met. The proposed completion date for the above-listed activities is June 23, 2017.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Merced Irrigation District (MEID) | NCR05234 | WECC2016016565 | MOD-025-2 | R2 | On November 22, 2016, MEID submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, MEID reported that it failed to verify the Reactive Power capability of its applicable Facility in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MEID’s applicable Facility, and is ongoing. The root cause of this issue was a misunderstanding regarding the effective date of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MEID failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single 94 MW Facility, and no harm is known to have occurred. MEID tested the Facility in accordance with the WECC Model Validation Policy prior to the effective date of the Standard, and it is unlikely that untimely verification will significantly affect current planning models. MEID does not have previous noncompliances of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, MEID: 1) will complete testing in accordance with Attachment 1; and 2) will hire additional staff and a third-party contractor to assist in interpretation of existing and future applicable Standards, and to ensure enforcement deadlines are understood and met. The proposed completion date for the above-listed activities is June 23, 2017.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Mesquite Solar 1, LLC (MSOL) | NCR11273 | WECC2017017088 | MOD-025-2 | R1 | On February 24, 2017, MSOL submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, MSOL reported that, following unexpected complications during initial verification testing, MSOL failed to verify the Real Power capability of its single applicable Facility in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MSOL’s applicable Facility, and ended July 15, 2016, when MSOL tested the Facility. The root cause of this issue was less than adequate consideration of potential delays; MSOL scheduled testing too close to the implementation deadline to ensure completion despite unexpected complications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MSOL failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was the result of unexpected delays, was of minimal duration (14 days), concerned a single 170 MVA unit, and no harm is known to have occurred. MSOL does not have previous noncompliances of this Standard and Requirement. | To mitigate this issue, MSOL: 1) tested its single applicable Facility, and submitted completed Attachment 2 information to its Transmission Planner; 2) addressed the issues in its procedures; 3) documented the issue as “lessons learned”; 4) automated future notifications and task management for MOD-025 in its work management system WECC verified completion of MSOL’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Mesquite Solar 1, LLC (MSOL) | NCR11273 | WECC2017017089 | MOD-025-2 | R2 | On February 24, 2017, MSOL submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, MSOL reported that, following unexpected complications during initial verification testing, MSOL failed to verify the Reactive Power capability of its single applicable Facility in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for MSOL’s applicable Facility, and ended July 15, 2016, when MSOL tested the Facility. The root cause of this issue was less than adequate consideration of potential delays; MSOL scheduled testing too close to the implementation deadline to ensure completion despite unexpected complications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MSOL failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was the result of unexpected delays, was of minimal duration (14 days), concerned a single 170 MVA unit, and no harm is known to have occurred. MSOL does not have previous noncompliances of this Standard and Requirement. | To mitigate this issue, MSOL: 1) tested its single applicable Facility, and submitted completed Attachment 2 information to its Transmission Planner; 2) addressed the issues in its procedures; 3) documented the issue as “lessons learned”; 4) automated future notifications and task management for MOD-025 in its work management system WECC verified completion of MSOL’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Nevada Power Company (NEVP) | NCR05261 | WECC2016016507 | PRC-005-2 | R3 | On November 7, 2016, NEVP submitted a Self-Report stating that as a Transmission Owner, Generator Owner and Distribution Provider, it had a possible issue of noncompliance with PRC-005-2 R3. Specifically, NEVP reported that ten battery banks at four of its substations were not tested within the intervals prescribed in Table 1-4(a) or Table 1-4(b). This issue began May 1, 2015, the earliest date by which devices in scope were due for maintenance, and ended January 20, 2017, when NEVP performed maintenance on all devices identified during NEVP’s review of this issue, and comprised a collective 203 days of noncompliance. The root cause of this issue was less than adequate training concerning management of NEVP’s automated scheduling tool. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NEVP failed to perform maintenance on Protection System Components within the intervals prescribed by PRC-005-2. Such failure could limit NEVP’s awareness of the working order of the devices, and could result in undetected degradation and/or malfunction of the devices. However, the scope of this issue concerned ten out of 195 batteries, which represented roughly five percent NEVP’s applicable devices for this Component Type. The devices in scope were continuously monitored and alarmed during the period in question, and no harm is known to have occurred. NEVP does not have relevant previous noncompliances of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, NEVP: 1) completed maintenance on all devices in scope; 2) performed a comprehensive review to identify the root cause and determine the extent of condition for this issue; 3) corrected the maintenance triggers for the devices in scope in its automated scheduling tool, and disconnected joint triggers to generate separate work orders for inspections and maintenance in the future; 4) created supplemental alerts and escalation triggers to ensure time-sensitive tasks are completed as required; 5) provided additional training to relevant staff regarding mandated timeframes in its Protection System Maintenance Program; and 6) revised its Compliance Monitoring Program to include technical assessments for this Standard. WECC verified completion of NEVP’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC2016016169 | VAR-002-4 | R3 | On September 19, 2016, PGAE submitted a Self-Report stating that, as a Generator Operator, it had a possible issue of noncompliance with VAR-002-4 R3. Specifically, PGAE reported that on June 16, 2016, it experienced system disturbances that caused the Automatic Voltage Regulator (AVR) at Balch Powerhouse 1 Unit 1 to change from automatic control to manual control. PGAE’s Fresno Operating Control Center (FOC) received an alarm at 3:56 p.m. and immediately dispatched an operator to verify the status of the AVR. The operator was not able to determine the control mode, so a second investigation was performed the next day. PGAE discovered that the AVR was in manual control mode and returned it back to automatic control mode at 11:03 a.m. PGAE notified its Transmission Operator (TOP) of the AVR change that same day at 2:34 p.m. The root cause of this issue was PGAE’s less than adequate training of its operators regarding this Standard and Requirement. WECC determined that this issue began on June 16, 2016, at 4:27 p.m., 30 minutes after PGAE failed to notify its TOP of the status change of the AVR, and ended on June 17, 2016, 2:34 p.m. when PGAE notified its TOP of the status change of the AVR, for approximately 22 hours of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PGAE failed to notify its TOP within 30 minutes of a status change of its AVR. Failure to do so could potentially lead the generator to trip if a system event occurred, and the loss of 33 MVA of generation. However, the operator at the FOC continued to maintain the voltage schedule while the AVR was in manual mode. Additionally, the unit did not trip and no harm is known to have occurred. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). WECC notes that PGAE has identified and self-reported this issue described herein, took voluntary corrective action to remediate and mitigate this issue, and has provided WECC documentation of its internal compliance program. For these reasons, WECC considers PGAE’s compliance history a factor in its designation of this remediated issue as a CE. WECC also considered PGAE’s VAR-002 compliance history in determining the disposition track. PGAE’s prior noncompliance with VAR-002 R3 includes NERC noncompliance ID WECC2014013771. The prior noncompliance does not have the same or similar root cause as the current issue. The root cause of the prior noncompliance was due to an operator error. Specifically, an outage caused a total of 27 alarms to trigger, including an alarm notifying the operator that the AVR switched to manual mode due to the outage. The generator operator acknowledged all of the alarms but was not aware of the AVR status because they acknowledged all the alarms simultaneously. This led to the operator failing to notify the TOP within 30 minutes of the change. For these reasons, WECC determined that PGAE’s VAR-002 compliance history should not serve as an aggravating factor in its disposition determination. | To mitigate this issue, PGAE: 1) Returned the AVR to automatic control 2) Communicated the incident to both of its TOP’s 3) Required its FOC operators to review the company standards, which cover notification requirements for AVR status changes 4) Developed a new smart alarm software and an automated notification will be sent to the Grid Control Center and PGAE’s Energy Procurement when a unit is online and the control mode of the AVR changes. Similarly, an automatic notification will be generated when there is a change in status to the Power System Stabilizer during appropriate operating conditions.
2017-05-31 | Western Electricity Coordinating Council (WECC) | PacifiCorp (PAC) | NCR05304 | WECC2017016981 | PER-003-1 | R2 | On February 10, 2017, PAC submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with PER-003-1 R2. Specifically, PAC reported that during a quarterly review, it discovered that the NERC certification of one of its System Operators had expired the previous quarter. This issue began November 3, 2016, when the certification expired, and ended January 30, 2017, when NERC renewed the certification. The root cause of this issue was human error; the operator completed and reported all required training hours to NERC, and believed the certification would automatically renew. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PAC failed to ensure one individual on its Real-time operating staff maintained a valid NERC certificate while performing Transmission Operator reliability-related tasks. Such failure could limit PAC’s ability to ensure that the individual in question was competent to perform Real-time reliability-related tasks. However, this issue was limited to one previously-certified individual, who had completed sufficient training hours to renew certification prior to the certification’s expiration. PAC discovered this issue following an internal compliance review, and no harm is known to have occurred. PAC does not have previous noncompliances of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PAC: 1) completed the certification renewal process and re-certified the individual in scope; 2) distributed reminders to requisite staff regarding individual and collective responsibilities for tracking and maintaining NERC certifications; and 3) revised its procedures to increase frequency of internal reviews from quarterly to monthly; 4) revised its procedures to require management to ensure certifications are current and valid prior to including operators on the work schedule; and 5) revised its procedures to require operators to renew certifications at least 30 days prior to expiration. WECC verified completion of PAC’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Pacific-Ultrapower Chinese Station (PUPCS) | NCR11279 | WECC2016016166 | PRC-024-2 | R1 | On September 14, 2016, PUPCS submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, PUPCS reported that, by the effective date of the Standard, it failed to set its protective relays in accordance with Attachment 1 of PRC-024-1. This issue began July 1, 2016, when implementation of PRC-024-1 became mandatory and enforceable for PUPCS’s applicable Facility, and ended November 7, 2016, when PUPCS reset a relay in accordance with Attachment 1 of PRC-024-1. The root cause of this issue was a misunderstanding regarding the effective dates of PRC-024-1 for single unit Facilities. The Standard does not require implementation for 100% of applicable Facilities until July 1, 2019. PUPCS believed that because it owns a single applicable generator, it was not required to meet the 40% implementation deadline, as it could not set relaying for only 40% of its generator. PUPCS pursued clarification regarding this issue prior to the July 1, 2016 implementation deadline, but did not receive confirmation until after the deadline had passed. | In this instance, PUPCS failed to set its generator frequency protective relaying to avoid tripping PUPCS’s generator unnecessarily. Such failure could result in a premature trip of the generator due to frequency excursions within the “no trip zone”. However, verification showed that the voltage relay settings are compliant with the Standard and no changes were recommended by the contractor. Additional this issue concerned a single, 25 MW generator, and no harm was known to have occurred. Based on this information, these issues posed minimal risk to the reliability of the BPS. PUPCS does not have previous noncompliance with this Standard and Requirement | To mitigate this issue, PUPCS: 1) reset a relay in accordance with Attachment 1 of PRC-024-1; and 2) created automated reminders to ensure timely completion of future compliance-related tasks associated with this Standard. WECC verified completion of PUPCS’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2016016704 | MOD-025-2 | R2 | On December 20, 2016, PSE submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, PSE reported that it failed to verify the Reactive Power capability of at least 40 percent of its generating Facilities in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of PSE’s applicable Facilities, and ended November 3, 2016, when PSE completed testing in accordance with Attachment 1. The root cause of this issue was a misunderstanding regarding the Standard implementation deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PSE failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as PSE tested its units using the WECC Model Validation Policy prior to the effective date of MOD-025-2. No harm is known to have occurred. PSE does not have previous noncompliances of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) tested at least 40 percent of its applicable Facilities; 2) verified and updated deadlines in its work management system to ensure future tasks will be completed per the implementation schedule in the Standard; and 3) revised its process for tracking and clarifying potential ambiguity concerning upcoming Standards. WECC verified completion of PSE’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Rio Bravo Fresno (RBFR) | NCR11277 | WECC2016016676 | PRC-019-2 | R1 | On December 14, 2016, RBFR submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, RBFR reported that it failed to verify coordination of its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. The root cause of this issue was a misunderstanding of the effective date of PRC-019-2 for single unit Facilities. The Standard does not require implementation for 100 percent of applicable units until July 1, 2019. RBFR believed that because it owns one small biomass power plant with a single generator, it was not required to meet the 40 percent implementation deadline until July 1, 2019. RBFR pursued clarification regarding this issue prior to the July 1, 2016 implementation deadline, but did not receive confirmation until after the deadline had passed. WECC determined this issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of RBFR’s applicable Facilities, and ended on November 11, 2016, when RBFR completed the PRC-019 coordination study of least 40 percent of its applicable Facilities, for a total of 133 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, RBFR failed to verify coordination of its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. Such failure could result in lack of situational awareness. However, this issue did not result in lack of situational awareness because verification did not identify any changes to RBFR’s control or protection settings. The combined capacity for RBFR’s single generator is approximately 25 MW and no harm was known to have occurred. WECC notes that RBFR identified and self-reported the issues described herein and does not have previous noncompliances of the Standards and Requirements. For these reasons, WECC considers RBFR’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, RBFR: 1) Completed the PRC-019-2 coordination study of its generating unit in accordance to the Standard and submitted the verification results to its Transmission Planner. 2) Implemented a preventative maintenance work order into its maintenance management system to ensure future generator testing is performed. WECC verified completion of the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Rio Bravo Fresno (RBFR) | NCR11277 | WECC2016016678 | MOD-025-2 | R1 | On December 14, 2016, RBFR submitted Self-Reports stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirements 1 and 2. Specifically, RBFR reported that it failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1, by the effective date of the Standard. The root cause of these issues was a misunderstanding of the effective date of MOD-025-2 for single unit Facilities. The Standard does not require implementation for 100 percent of applicable units until July 1, 2019. RBFR believed that because it owns one small biomass power plant with a single generator, it was not required to meet the 40 percent implementation deadline until July 1, 2019. RBFR pursued clarification regarding this issue prior to the July 1, 2016 implementation deadline, but did not receive confirmation until after the deadline had passed. These issues began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for RBFR’s single generator, and ended November 11, 2016, when RBFR tested the generator, for a total of 133 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, RBFR failed to perform testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, RBFR has provided all required modeling data required by recently retired Standards MOD-010 and MOD-012-0 to WECC and the North America Electric Reliability Corporation. The capacity of this generating resource is approximately 25 MW and no harm is known to have occurred. WECC notes that RBFR identified and self-reported the issues described herein and does not have previous noncompliances of the Standards and Requirements. For these reasons, WECC considers RBFR’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, RBFR: 1) Completed testing of its generating unit in accordance to the Standard 2) Submitted the verification results to its Transmission Planner 3) Implemented a preventative maintenance work order into its maintenance management system to ensure future generator testing is performed. WECC verified completion of the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Rio Bravo Fresno (RBFR) | NCR11277 | WECC2016016679 | MOD-025-2 | R2 | On December 14, 2016, RBFR submitted Self-Reports stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirements 1 and 2. Specifically, RBFR reported that it failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1, by the effective date of the Standard. The root cause of these issues was a misunderstanding of the effective date of MOD-025-2 for single unit Facilities. The Standard does not require implementation for 100 percent of applicable units until July 1, 2019. RBFR believed that because it owns one small biomass power plant with a single generator, it was not required to meet the 40 percent implementation deadline until July 1, 2019. RBFR pursued clarification regarding this issue prior to the July 1, 2016 implementation deadline, but did not receive confirmation until after the deadline had passed. These issues began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for RBFR’s single generator, and ended November 11, 2016, when RBFR tested the generator, for a total of 133 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, RBFR failed to perform testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, RBFR has provided all required modeling data required by recently retired Standards MOD-010 and MOD-012-0 to WECC and the North America Electric Reliability Corporation. The capacity of this generating resource is approximately 25 MW and no harm is known to have occurred. WECC notes that RBFR identified and self-reported the issues described herein and does not have previous noncompliances of the Standards and Requirements. For these reasons, WECC considers RBFR’s compliance history a factor in its designation of these remediated issues as CEs. | To mitigate this issue, RBFR: 1) Completed testing of its generating unit in accordance to the Standard 2) Submitted the verification results to its Transmission Planner 3) Implemented a preventative maintenance work order into its maintenance management system to ensure future generator testing is performed. WECC verified completion of the mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Utah Red Hills Renewable Park, LLC (UTRH) | NCR11610 | WECC2016016716 | PRC-024-2 | R1 | On December 29, 2016, UTRH submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. During an internal review, UTRH discovered that the original inverter settings at its Facility did not meet the frequency ride through requirements prescribed in Attachment 1. This issue began July 1, 2016, when implementation of PRC-024-1 became mandatory and enforceable for UTRH’s applicable Facility, and ended January 10, 2017, when UTRH adjusted the inverter settings in accordance with Attachment 1. The root cause of this issue was human error; UTRH reviewed the settings prior to the effective date of PRC-024-2 and believed the settings met the Requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, UTRH failed to set its frequency protective relaying so that it would not trip its Facility unnecessarily. Such failure could result in premature trip of the Facility due to frequency excursions within the “no trip zone”. However, the Facility in scope is a variable energy resource solar power generation Facility, which is operated with the understanding that real-power output could be at or near zero at any time. Therefore, there is a low probability that this issue would cause more than a minimal impact to the reliability of the BES. Solar generation is not typically utilized as a firm resource, therefore, UTRH plans and operates the grid with the expectation that the generation may be unavailable at any given time. Further, the capacity of this generating Facility is approximately 80 MW, the Facility did not trip during the period in question, and no harm is known to have occurred. UTRH does not have previous noncompliances of this Standard and Requirement. | To mitigate this issue, UTRH: 1) adjusted the inverter settings on all of the devices at its Facility to meet Attachment 1 requirements; and 2) will perform an annual compliance assessment, which includes a thorough review of evidence associated with all currently-applicable Standards. This assessment will also ensure UTRH tracks and performs compliance-related tasks for Standards as they become effective. WECC verified completion of UTRH’s mitigating activities.
2017-05-31 | Western Electricity Coordinating Council (WECC) | Windstar Energy, LLC (WSTAR) | NCR11292 | WECC2017017115 | FAC-008-3 | R2 | On February 28, 2017, WSTAR submitted a Self-Certification stating that as a Generator Owner, it had a possible issue of noncompliance with FAC-008-3 R2. Specifically, when WSTAR revised its documentation for Facility Ratings methodology in preparation for Version 3 of the Standard, it failed to transfer all requisite information into the revised documentation. This issue began January 1, 2013, when the current version of the Standard became mandatory and enforceable to WSTAR, and ended March 1, 2017, when WSTAR revised its documented Facility Ratings methodology. The root cause of this issue was less than adequate documentation due to an editorial mistake. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, WSTAR failed to documents its Facility Ratings methodology as prescribed by R2. Such failure could result in determination and designation of inaccurate Facility Ratings. However, this issue only concerned documentation. Although WSTAR failed to document Facility Ratings methodology, it actually implemented acceptable methodology to establish Facility Ratings. Additionally, this issue concerned a single location with Facilities corresponding to 120 MW of generation; had this issue resulted in determination and designation of inaccurate Facility Ratings, the risk to the BPS would still have been limited. No harm is known to have occurred. WSTAR does not have previous noncompliances of this Standard and Requirement. | To mitigate this issue, WSTAR revised its documented Facility Ratings methodology. WECC verified completion of WSTAR’s mitigating activities.
2017-04-27 | Florida Reliability Coordinating Council (FRCC) | Reedy Creek Improvement District (RCI) | NCR00065 | FRCC2017016851 | PRC-006-2 | R9 | On January 25, 2017, RCI submitted a Self-Report stating that, as a Distribution Provider, it had an issue of PRC-006-2 R9. From October 31, 2016 to November 8, 2016, RCI failed to provide automatic tripping of Load in accordance with the FRCC Under Frequency Load Shedding (UFLS) Program design and schedule for implementation as determined by its Planning Coordinator. RCI did not update one (1) UFLS relay to the proper frequency within the required timeframe identified in the UFLS Program. The UFLS Program, Revision No. 3, which became effective November 1, 2014, required all DPs with greater than 100MW of load meet the Appendix A Implementation Schedule by October 31, 2016. This program required the RCI to reprogram thirty-seven (37) UFLS relays. Thirty-six (36) of these relays subject to reprogramming were reprogrammed prior to October 31, 2016. The one (1) remaining 5kV UFLS relay was not programmed with the new set-point frequency (58.5 to 58.7) until November 8, 2016, eight (8) days after the required implementation date. The root cause for this noncompliance was an inadvertent omission of an update to the RCI NERC compliance program database. The historical RCI UFLS program is an annual program where the scheduled 5kV systems are tested by the end of the calendar year through scheduled outages outside of the hottest weather months. RCI missed the FRCC program date of the new set point programming steps as it was different from the typical RCI UFLS Program completion schedule. RCI normally tracks these dates in the RCI NERC compliance program database. This unique FRCC UFLS Program date, October 31, 2016, was inadvertently omitted from the RCI NERC compliance program database updates and thus the root cause of the issue. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because had an UFLS event occurred, this relay would have tripped later than required. The relay would have actuated once the frequency decayed below 58.5 Hz instead of tripping at 58.7 per the program. The UFLS relay not reprogrammed represented only 1.55MW. Which represents 2.7% (1 of 37) of RCI's UFLS devices or .01% of the FRCC armed UFLS load. FRCC determined that RCI's compliance history should not serve as a basis for applying a penalty as RCI has no prior issues with this Standard/Requirement. No harm is known to have occurred. | To mitigate this issue, RCI: 1) completed programming of the relay to the new setting and tested; and 2) updated the RCI NERC compliance program database with all future RCI maintenance program dates from 2017 through 2020, to ensure continued compliance. The compliance program database is updated annually and will always be looking forward at least four years into the future. To mitigate the issue, RCI will: 1) develop a self-assessment and monitoring program whereby the requirements of PRC-006-2 applicable to RCI will be closely supervised. This self-assessment and monitoring program will also be peer reviewed in the monthly RCES NERC Compliance Committee meetings through at least February of 2018, to ensure continued ongoing compliance with the Standard. The results of the monthly peer reviews will also be shared with the RCI Executive Compliance Committee on a quarterly basis through the first calendar quarter of 2018.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2016015458 | PRC-001-1.1 | R2 | On January 12, 2016, AEP submitted a Self-Report to ReliabilityFirst stating that, as a Generator Operator (GO), it was in noncompliance of PRC-001-1.1 R2. On February 1, 2014, AEP removed Tanners Creek Unit 2 from service on a scheduled maintenance outage. During the shutdown process, AEP performed multiple tests, and determined that the reverse power relays were not operating as intended. These relays are designed to sense a generator motoring event (which can cause extensive damage to the generator) and to trip the generator by opening the unit breakers. AEP then performed work on the relays and determined the relays were operational. On February 8, 2014, when AEP returned the unit to service, AEP performed a functional test on the relays, but again determined that the relays did not operate as intended. The operators took the unit out of parallel and contacted the Electrical Engineering Services group, who confirmed the unit could be operated with the reverse power relays in an inoperative state as long as the operator was aware the turbines would have to be manually tripped (hydraulic oil tripped) in the event of a motoring occurrence. Electrical Engineering Services then notified the operator that the procedure for reporting PRC-001 R2.1 needed to be executed because the unit would not trip automatically for an event as designed, but would instead require operator recognition and manual intervention. The unit was paralleled and returned to service. However, the operator failed to notify PJM (the Transmission Operator (TOP) and Balancing Authority (BA)) that the unit would not trip automatically as intended. The root cause was the operator’s error in not following the procedure to contact the TOP and BA even though he was aware of the procedure and the need to follow the procedure in this instance. This cause involves the management practices of workforce management, which includes training, and external interdependencies, which includes managing interdependencies to reduce risk. The duration of the issue is from February 1, 2014, the date AEP failed to contact the TOP and BA, through March 11, 2014, the date AEP fixed the underlying issue that caused the equipment failure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk of not notifying the TOP and BA of protection system failures that reduce reliability is that the TOP and BA would not coordinate their systems to address the potential protection system failure. However, here, this risk was mitigated due to the following factors. First, the operators were aware of the abnormal operating condition of the relays, and in the unlikely occurrence of a motoring event, the operators had a method by which they could manually trip the unit. Thus, it was unlikely that the protection system condition would actually reduce system reliability. Because of this, it was unlikely that PJM would have taken action had it received proper notice of the condition. It should also be noted that AEP has since retired the unit at issue. No harm is known to have occurred. ReliabilityFirst considered AEP's PRC-001 R2 compliance history in determining the disposition track. AEP’s relevant prior noncompliance with PRC-001 R2 includes: RFC2014014024. A Compliance Exception addressing a noncompliance with PRC-001-1.1 R2, R2.2 was posted on the NERC website on May 28, 2015. The noncompliance is distinguishable from the current issue. In the prior noncompliance, AEP did not immediately recognize a relay failure as inadequate protection due to the rare protection design of the relay at issue. Upon determining that the relay reduced system reliability, AEP made the proper notification. Conversely, here, AEP’s engineering department determined that the relay failure reduced system reliability, and told the operator to make the proper notification. However, the operator failed to make the notification. ReliabilityFirst determined that AEP’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, AEP: 1) corrected the issue by fixing the equipment failure; 2) sent a memorandum to all plants to reinforce the instructions regarding reporting PRC-001 events; 3) enhanced its GO notification process for plants to send an email to “Gen NERC Protection Systems” to document PRC-001 events; and 4) committed to enhance its GOP notification process by March 31, 2017 to include additional internal notifications regarding protection system outages or abnormal conditions.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE) | NCR00753 | RFC2016016290 | FAC-008-3 | R6 | On September 26, 2016, DTE submitted a Self-Report stating that, as a Generator Owner, it had an issue of FAC-008-3 R6. As a result of a change in the Bulk Electric System (BES) definition to include Black Start Resources, two of DTE’s generating units were required to have Facility Ratings by July 1, 2016. More specifically, this issue involved the peaking units at Slocum Substation, which have a name plate rating of approximately 13 MVA and are connected at 24 kV. These units were not previously subject to FAC-008-3 because of their size, but because of the revised BES definition, were required to have a Facility Rating by July 1, 2016. The Slocum peaking units supplied power to TC7A as the target unit. However, pursuant to MISO Attachment Y, which was circulated internally at DTE, TCA7A was set to retire in April 2016. As a result, the Slocum peaking units would no longer be considered Black Start Resources (since there was not a unit for the Slocum peaking units to black start). However, with this retirement, DTE had a concern about meeting system restoration requirements for a nearby nuclear plant. To address this concern long term, DTE was in the process of installing and testing a new Black Start Resource to supply the nuclear plant with power. But, because the modifications and tests were occurring around the same time as the Slocum units were set to retire, DTE and ITC determined that ITC would temporarily keep the Slocum peaking units in its System Restoration Plan as backup Black Start Resources in case the modifications or tests were not successful or completed on time. This decision to temporarily keep the Slocum peaking units as backup Black Start Resources was not communicated to all necessary individuals within DTE. As a result, the individuals responsible for setting the Facility Rating for the Slocum peaking units incorrectly believed the Slocum units were retiring in April 2016 and thus did not set a Facility Rating by the July 1, 2016 deadline. Ultimately, the modifications and tests at Delray were completed on April 9, 2016 and the ITC System Restoration Plan was updated to use Delray as the Black Start Resources. However, the ITC System Restoration still included the Slocum units and TC7A as a backup resource. The root cause was a lack of communication within DTE once DTE and ITC determined that the units should remain Black Start Resources. This involves the management practice of asset and configuration, which includes managing changes (or, in this case, cancelling a planned change) to assets that can affect the BES. To successfully manage changes, entities must establish and follow communication protocols to ensure that the custodians of the asset or configuration item are aware of the change. This issue started on July 1, 2016, when DTE was required to comply with FAC-008-3 R6, and ended on October 21, 2016, when the Slocum units were removed from the ITC System Restoration Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The Slocum units were designated in the System Restoration Plan only as backup units. Thus, if a system restoration event were to occur, the Delray units, which were successfully tested, would have been used to restore the system and the Slocum units would not be required. Additionally, DTE self-identified the issue almost immediately after the enforcement date, thus reducing the duration of risk to the BPS. No harm is known to have occurred. ReliabilityFirst considered DTE’s FAC-008 R6 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, DTE requested ITC to revise the System Restoration Plan removing all reference to TC7A as well as the Slocum Peakers as a result of DTE determining the units are not necessary for system restoration. In addition, DTE requested the addition of a different unit as a backup unit (since TC7A and Slocum are no longer backup). For additional preventative mitigation steps, see mitigation for RFC2016016340. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE) | NCR00753 | RFC2016016340 | PRC-005-6 | R3 | On October 6, 2016, DTE submitted a Self-Report stating that, as a Generator Owner and Distribution Provider, it had an issue of PRC-005-6 R3. As a result of a change in the Bulk Electric System (BES) definition to include Black Start Resources, two of DTE’s generating units were required to have maintenance by July 1, 2016. More specifically, this issue involved the peaking units at Slocum Substation, which have a name plate rating of approximately 13 MVA and are connected at 24 kV. These units were not previously subject to PRC-005-6 because of their size, but because of the revised BES definition, were required to have maintenance activities by July 1, 2016. The Slocum peaking units supplied power to TC7A as the target unit. However, pursuant to MISO Attachment Y, which was circulated internally at DTE, TCA7A was set to retire in April 2016. As a result, the Slocum peaking units would no longer be considered Black Start Resources (since there wasn’t a unit for the Slocum peaking units to black start). However, with this retirement, DTE had a concern about meeting system restoration requirements for a nearby nuclear plant. To address this concern long term, DTE was in the process installing and testing a new Black Start Resource to supply the nuclear plant with power. But, because the modifications and tests were occurring around the same time as the Slocum units were set to retire, DTE and ITC determined that ITC would temporarily keep the Slocum peaking units in its System Restoration Plan as backup Black Start Resources in case the modifications or tests were not successful or completed on time. This decision to temporarily keep the Slocum peaking units as backup Black Start Resources was not communicated to all necessary individuals within DTE. As a result, the individuals responsible for setting the Facility Rating for the Slocum peaking units incorrectly believed the Slocum units were retiring in April 2016 and thus did not perform maintenance activities by the July 1, 2016 deadline. Ultimately, the modifications and tests at Delray were completed on April 9, 2016 and the ITC System Restoration Plan was updated to use Delray as the Black Start Resources. However, the ITC System Restoration still included the Slocum units and TC7A as a backup solution. The root cause was a lack of communication within DTE once DTE and ITC determined that the units should remain Black Start Resources. This involves the management practice of asset and configuration, which includes managing changes (or, in this case, cancelling a planned change) to assets that can affect the BES. To successfully manage changes, entities must establish and follow communication protocols to ensure that the custodians of the asset or configuration item are aware of the change. This issue started on July 1, 2016, when DTE was required to comply with PRC-005-6 R3, and ended on October 21, 2016, when the Slocum units were removed from the ITC System Restoration Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The Slocum units were designated in the System Restoration Plan only as backup units. Thus, if a system restoration event were to occur, the Delray units, which were successfully tested, would have been used to restore the system and the Slocum units would not be required. Additionally, DTE self-identified the issue almost immediately after the enforcement date, thus reducing the duration of risk to the BPS. No harm is known to have occurred. ReliabilityFirst considered DTE’s PRC-005 R3 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, DTE: 1) confirmed the ITC System Restoration Plan has been revised to remove all reference to Slocum peakers being a Black Start Resource as well as all reference to TC7A being a target unit for the Slocum peakers as a result of DTE determining that these units are not necessary for system restoration; and 2) created a unit retirement notification form to be submitted to DTE business units confirming the relevant generating unit’s last day of operation. The MISO Attachment Y is the normal unit retirement notification. In this case, the MISO Attachment Y did not provide the business unit the proper direction. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2016016218 | EOP-005-2 | R17 | On September 22, 2016, ReliabilityFirst determined that IPL, as a Generator Operator, had an issue with EOP-005-2 R17 identified during a Compliance Audit conducted from September 13, 2016 through September 15, 2016. ReliabilityFirst sampled IPL’s documentation of training records for the training period ending in 2015 and discovered that 6 plant operators in the sample completed their training on January 4, 2016, or four days later than required. The root cause of this noncompliance was IPL’s failure to clearly define roles and responsibilities for training and ineffective process for ensuring that the training was timely completed. This major contributing factor involves the management practices of workforce management, which includes delivering training, education, and awareness to employees and establishing training, education, and awareness records, as well as verification. This issue started on January 1, 2016, the date by which IPL was required to have delivered the training, and ended on January 4, 2016, when IPL delivered the training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the personnel at issue had already received the relevant training, albeit during the previous two year cycle. Second, IPL provided the training only 4 days late. As a result, the personnel would most likely not be appreciably less prepared than they would have been had the training been provided by the deadline. No harm is known to have occurred. ReliabilityFirst considered IPL’s EOP-005 R17 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, IPL will complete the following mitigation activities by September 25, 2017: 1) delivered the required training to the personnel in question; 2) committed to analyze the list of operators identified to receive black start training to ensure that all operating personnel responsible for the startup of the IPL Blackstart Resource generation units and energizing a bus are included; 3) committed to track training completion via a learning management system (LMS). To more clearly define roles and responsibilities for training, IPL’s LMS will be monitored by a training coordinator, who issues weekly training status reports to each operator and monthly reports to management. Timely completion of required training is the responsibility of each applicable operator and will be added as an identified goal for 2017 and beyond, as appropriate; 4) committed to evaluate current training approach and enhance as needed to ensure training objectives are identified and achieved; and 5) committed to compile and submit evidence package to support certification of completion. The length of time required to complete these mitigation activities is necessary because they include process changes and a holistic review of the company's training approach, both of which will take several months to complete.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW1) | NCR03006 | RFC2016016079 | VAR-002-4 | R3 | On August 29, 2016, Mesquite Wind, LLC (Mesquite Wind) submitted a Self-Report through MLW1, under an existing multi-region registered entity agreement, stating that, as a Generator Operator, it had an issue of VAR-002-4 R3. On May 24, 2016, EDP Renewables' (EDPR’s) Remote Operations Control Center (ROCC) identified a possible noncompliance of VAR-002-4 R3. On May 24, 2016, at 12:39 CPT, EDP Renewables North America’s high voltage technician at Mesquite Wind called the ROCC to request that Capacitor Bank C2/Z12 be disabled in order to remove a bee hive. At 12:48 CPT, a ROCC employee disabled the capacitor bank controls using the substation human machine interface. At 12:52 CPT, the ROCC employee notified Oncor, Mesquite Wind’s Transmission Owner, that Mesquite Wind had been derated by 13.5 MVAR. Mesquite Wind’s high voltage technician called at 1:31 CPT to have the ROCC re-enable the capacitor bank controls. The ROCC re-enabled the capacitor bank controls at 13:37 CPT and again notified Oncor of the change also at 13:37 CPT. Mesquite Wind is required to notify its Transmission Operator (ERCOT) of these changes within 30 minutes. Although the ROCC employee on shift notified Oncor of the disabled capacitor bank at 12:52 CPT, the ROCC employee did not notify ERCOT of the derate until 1:37 CPT, 49 minutes after disabling the capacitor bank. 49 minutes is longer than the 30 minutes allowed for such notification under VAR-002-4 R3. Although the ROCC employee was aware of the requirement to notify ERCOT of the derate, the employee got distracted and that caused his failure to timely notify ERCOT within 30 minutes of the derate. The ROCC employee notified ERCOT at 1:37 CPT and Oncor at 1:39 CPT that the capacitor banks had been re-enabled. The ROCC employee timely made all other required communications to ERCOT and Oncor. This noncompliance involves the management practices of workforce management and work management. The ROCC employee failed to timely notify ERCOT of the derate due to the employee getting distracted. A root cause of this noncompliance is ineffective training because the employee failed to timely make the notification. Upon further investigation, Mesquite Wind determined that its ROCC employee reference material could be improved to clarify their procedure to require Mesquite Wind to contact ERCOT within thirty minutes of a change being made and to highlight the time sensitive notification requirements. This issue started on May 24, 2016, when Mesquite Wind did not notify ERCOT within 30 minutes of disabling its capacitor banks, and ended on May 24, 2016, when Mesquite Wind completed its notification to ERCOT about disabling its capacitor banks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Mesquite Wind’s timely notification to Oncor made the broader grid in the Texas Reliability Entity (TRE) region aware of the change of status, therefore the broader grid could plan accordingly for the reduction in available static reactive power from Mesquite Wind. Furthermore, Mesquite Wind’s capability is 200 MW of active power and 81 MVAR of static reactive power resources. The 200 MW of active power were not affected by this noncompliance. Although Mesquite Wind disabled some of its capacitor banks, five capacitor banks with 67.5 MVAR of static reactive power remained enabled in automatic control mode during the period of the noncompliance. Mesquite Wind’s facility MVAR capability was only reduced 13.5 MVAR. Such a small reduction in available static reactive power reduces the potential risk of voltage instability because Mesquite Wind was still providing more than 80% of its expected voltage support to the grid. Additionally, the other 20% (13.5 MVAR) that were not available could have been made available quickly due to the type of maintenance activity at issue (removing a beehive). Lastly, ERCOT was unaware of Mesquite Wind's reduction in facility MVAR capabilities for a short amount of time (19 minutes). No harm is known to have occurred. ReliabilityFirst considered MLW1’s VAR-002 R3 compliance history in determining the disposition track. MLW1’s relevant prior noncompliance with VAR-002 R3 includes: TRE2015014652. A Compliance Exception addressing a noncompliance with VAR-002-3 R3 was posted on NERC’s website on June 30, 2015. In the prior noncompliance, Mesquite Wind failed to notify its Transmission Operator within 30 minutes of the Master VAR Controller (“MVC”) being returned to automatic control. The ROCC Operator notified the Transmission Operator of the change from manual to automatic 68 minutes after the required 30 minute notification window. The root cause was determined to be a gap in communication regarding the VAR status change post maintenance between Power Engineers and EDPR NA’s ROCC, which resulted in a delayed status change notification to the Transmission Operator. The instant noncompliance is distinguishable from the prior noncompliance. In the instant noncompliance, Mesquite Wind did not timely notify ERCOT within 30 minutes of changing the status on its AVR. In the current noncompliance, Mesquite Wind timely notified its Transmission Owner, Oncor, but did not timely notify ERCOT because Mesquite Wind’s reference materials did not make clear that ROCC operators must contact ERCOT, the Transmission Operator, when changing the status of the AVR. Rather than a gap in procedure, as was the case for the prior issue, the root cause of the current noncompliance is an insufficiently clear procedure. ReliabilityFirst determined that Mesquite Wind's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Mesquite Wind: 1) revised the ROCC Reference material to depict the relationship between Oncor (Transmission Owner) and ERCOT (Transmission Operator) in a clearer format to ensure ROCC personnel know who to contact for events of a similar nature. This revision reduces the likelihood of recurrence of this noncompliance because it makes it clearer that ROCC personnel need to contact both Oncor and ERCOT within 30 minutes of a change in status; and 2) reviewed the self-reported issue during its ROCC meeting and training on August 24, 2016 with all ROCC personnel. During this review of the self-reported issue, Mesquite Wind reinforced with all ROCC employees the notification requirements. Mesquite Wind also specifically met with and retrained the ROCC employee at issue. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW1) | NCR03006 | RFC2016016080 | TOP-002-2.1b | R14 | On August 29, 2016, Blue Canyon Windpower I, LLC (Blue Canyon I) submitted a Self-Report through MLW1, under an existing multi-region registered entity agreement, stating that, as a Generator Operator, it had an issue of TOP-002-2.1b R14. On March 1, 2014, Southwest Power Pool’s (SPP) Integrated Marketplace became effective. Part of this market change included SPP becoming the Consolidated Balancing Authority (CBA) for its region. This change included deregistering legacy Balancing Authorities (BAs) within the SPP footprint. Although EDP Renewables North America (EDPR NA) was aware of the new market structure, it was unaware of and not notified that Blue Canyon I’s BA, Western Farmers Electric Cooperative, had been deregistered as Blue Canyon I’s BA. Western Famers Electric Cooperative also never notified Blue Canyon I or EDPR NA that it had been deregistered as Blue Canyon I’s BA in any way. Blue Canyon I also never received notification from its new BA, SPP, that it should now be notifying SPP instead of Western Farmers Electric Cooperative of changes in the wind farm’s real output capabilities. Due to this lack of notification, Blue Canyon I continued to notify the legacy BA, Western Farmers Electric Cooperative, instead of the new BA, SPP, of changes in the wind farm’s real output capabilities. (During the duration of the noncompliance, Blue Canyon I notified its legacy BA, Western Farmers Electric Cooperative, and its Transmission Operator of any changes in the wind farm’s real output capabilities.) Despite this lack of notification, Blue Canyon I is still responsible under TOP-002-2.1b R14 to notify its current BA of any relevant changes. Blue Canyon I had reason to know SPP was its active BA because information stating that SPP was now the BA for all Registered Entities in SPP’s footprint effective March 1, 2014 was readily available on SPP’s website and widely known throughout the SPP footprint thanks to the work of the SPP Consolidated Balancing Authority Steering Committee. It took Blue Canyon I more than two years to discover that SPP was their active BA as Blue Canyon I had been erroneously sending notifications to the incorrect BA. Blue Canyon I discovered SPP was their active BA after EDPR found out Blue Canyon I’s existing BA had deregistered during an internal information sharing meeting. This noncompliance involves the management practice of verification. After SPP’s Integrated Marketplace became effective on March 1, 2014, Blue Canyon I never verified the identity of its BA and did not have a process in place to verify that it was sending its information to the correct BA. This lack of verification is the root cause of the noncompliance. This issue started on May 15, 2014, when Blue Canyon I was required to notify its new BA, SPP, of any changes in the wind farm’s real output capabilities, and ended on December 5, 2016, when Blue Canyon I began notifying its new BA, SPP, of any changes in the wind farm’s real output capabilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm of the SPP being unaware of changes in Blue Canyon I’s real output capabilities is SPP making plans and predictions to maintain grid stability based off of inaccurate information. Throughout the noncompliance Blue Canyon I made timely notifications to its Transmission Operator. These notifications minimize the chance of any actual harm because other Reliability Entities in SPP were made aware of any changes in the wind farm’s real output capabilities. Blue Canyon I also offers a total capacity of 74.5 MW to the BES at the Washita Substation which is minimal in comparison to SPP’s total load. Blue Canyon I’s small size lessens the impact that changes to its real output capabilities would have on the rest of the grid. No harm is known to have occurred. ReliabilityFirst considered Blue Canyon I's TOP-002 R14 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, Blue Canyon I changed its reporting policies and procedure to reflect that SPP should be notified of all changes to the wind farm’s real output capabilities. To ensure that events of a similar nature will not occur, Blue Canyon I will annually confirm not only the contact information of all connected Reliability Entities in accordance with EOP-004-2 R3, but will also confirm the reliability function for which the entity is serving. By conducting these annual confirmations, it will ensure that proper reliability functions, such as the current BA, are notified when required. Blue Canyon I will also check with SPP on a quarterly basis and monitor SPP’s website to confirm that SPP is still serving as Blue Canyon I’s active BA. If Blue Canyon I discovers that SPP is no longer its BA, Blue Canyon I will take all necessary action to find out who its new BA is and then will make all proper notifications to that new BA.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW1) | NCR03006 | RFC2016016081 | TOP-002-2.1b | R14 | On August 29, 2016, Blue Canyon Windpower II, LLC (Blue Canyon II) submitted a Self-Report through MLW1, under an existing multi-region registered entity agreement, stating that, as a Generator Operator, it had an issue of TOP-002-2.1b R14. On March 1, 2014, Southwest Power Pool’s (SPP) Integrated Marketplace became effective. Part of this market change included SPP becoming the Consolidated Balancing Authority (CBA) for its region. This change included deregistering legacy Balancing Authorities (BAs) within the SPP footprint. Although EDP Renewables North America (EDPR NA) was aware of the new market structure, it was unaware of and not notified that Blue Canyon II’s BA, Western Farmers Electric Cooperative, had been deregistered as Blue Canyon II’s BA. Western Famers Electric Cooperative also never notified Blue Canyon II or EDPR NA that it had been deregistered as Blue Canyon II’s BA in any way. Blue Canyon II also never received notification from its new BA, SPP, that it should now be notifying SPP instead of Western Farmers Electric Cooperative of changes in the wind farm’s real output capabilities. Due to this lack of notification, Blue Canyon II continued to notify the legacy BA, Western Farmers Electric Cooperative, instead of the new BA, SPP, of changes in the wind farm’s real output capabilities. (During the duration of the noncompliance, Blue Canyon II notified its legacy BA, Western Farmers Electric Cooperative, and its Transmission Operator of any changes in the wind farm’s real output capabilities.) Despite this lack of notification, Blue Canyon II is still responsible under TOP-002-2.1b R14 to notify its current BA of any relevant changes. Blue Canyon II had sufficient reason to know that SPP was its active BA because information stating that SPP was now the BA for all Registered Entities in SPP’s footprint effective March 1, 2014 was readily available on SPP’s website and widely known throughout the SPP footprint thanks to the work of the SPP Consolidated Balancing Authority Steering Committee. It took Blue Canyon II more than two years to realize that SPP was their active BA. Blue Canyon II discovered this issue when they inadvertently learned that SPP was their active BA after EDPR found out Blue Canyon II’s existing BA had deregistered during an internal information sharing meeting. This noncompliance involves the management practice of verification. After SPP’s Integrated Marketplace became effective on March 1, 2014, Blue Canyon II never verified the identity of its BA and did not have a process in place to verify that it was sending its information to the correct BA. This lack of verification is the root cause of the noncompliance. This issue started on May 15, 2014, when Blue Canyon II was required to notify its new BA, SPP, of any changes in the wind farm’s real output capabilities, and ended on December 5, 2016, when Blue Canyon II began notifying its new BA, SPP, of any changes in the wind farm’s real output capabilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm from this noncompliance is that the BA is unaware of changes in Blue Canyon II’s real output capabilities and the BA is making plans and predictions to maintain grid stability based off of inaccurate information. Throughout the noncompliance Blue Canyon II made timely notifications to its Transmission Operator and its legacy BA: Western Farmers Electric Cooperative. These notifications minimize the chance of any actual harm because other Reliability Entities in SPP were made aware of any changes in the wind farm’s real output capabilities. Although SPP, as the BA, was not notified, the broader grid was aware of the changes being made because of Blue Canyon II’s notifications to its Transmission Operator. Blue Canyon II also offers a total capacity of 151.2 MW to the BES at the Washita Substation which is minimal in comparison to SPP’s total load. Blue Canyon II’s small size lessens the impact that changes to its real output capabilities would have on the rest of the grid. No harm is known to have occurred. ReliabilityFirst considered Blue Canyon II's TOP-002 R14 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, Blue Canyon II changed its reporting policies and procedure to reflect that SPP should be notified of all changes to the wind farm’s real output capabilities. To ensure that events of a similar nature will not occur, Blue Canyon II will annually confirm not only the contact information of all connected Reliability Entities in accordance with EOP-004-2 R3, but will also confirm the reliability function for which the entity is serving. By conducting these annual confirmations, it will ensure that proper reliability functions, such as the current BA, are notified when required. Blue Canyon II will also check with SPP on a quarterly basis and monitor SPP’s website to confirm that SPP is still serving as Blue Canyon II’s active BA. If Blue Canyon II discovers that SPP is no longer its BA, Blue Canyon II will take all necessary action to find out who its new BA is and then will make all proper notifications to that new BA.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW1) | NCR03006 | RFC2016016082 | TOP-002-2.1b | R14 | On August 29, 2016, Cloud County Wind Farm, LLC (Cloud County) submitted a Self-Report through MLW1, under an existing multi-region registered entity agreement, stating that, as a Generator Operator, it had an issue of TOP-002-2.1b R14. On March 1, 2014, Southwest Power Pool’s (SPP) Integrated Marketplace became effective. Part of this market change included SPP becoming the Consolidated Balancing Authority (CBA) for its region. This change included deregistering legacy Balancing Authorities (BAs) within the SPP footprint. Although EDP Renewables North America (EDPR NA) was aware of the new market structure, it was unaware of and not notified that Cloud County’s BAs, Empire District (for phase 1 of the Cloud County Wind Farm) and Westar (for phase 2 of the Cloud County Wind Farm), had been deregistered as Cloud County’s BAs. These Legacy BAs (Empire District and Westar) never notified Cloud County or EDPR NA that it had been deregistered as Cloud County’s BAs in any way. Cloud County also never received notification from its new BA, SPP, that it should now be notifying SPP instead of Empire District and Westar of changes in the wind farm’s real output capabilities. Due to this lack of notification, Cloud County continued to notify the legacy BAs instead of the new BA, SPP, of changes in the wind farm’s real output capabilities. (During the duration of the noncompliance, Cloud County notified its legacy BAs and its Transmission Operator of any changes in the wind farm’s real output capabilities.) Despite this lack of notification, Cloud County is still responsible under TOP-002-2.1b R14 to notify its current BA of any relevant changes. Cloud County should have known that SPP was its active BA because information stating that SPP was now the BA for all Registered Entities in SPP’s footprint effective March 1, 2014 was readily available on SPP’s website and widely known throughout the SPP footprint thanks to the work of the SPP Consolidated Balancing Authority Steering Committee. It took Cloud County more than two years to realize that SPP was their active BA. Cloud County discovered that SPP was their active BA after EDPR found out Cloud County’s existing BAs had deregistered during an internal information sharing meeting. This noncompliance involves the management practice of verification. After SPP’s Integrated Marketplace became effective on March 1, 2014, Cloud County never verified the identity of its new BA and did not have a process in place to verify that it was sending its information to the correct BA. This lack of verification is the root cause of the noncompliance. This issue started on May 15, 2014, when Cloud County was required to notify its new BA, SPP, of any changes in the wind farm’s real output capabilities, and ended on December 5, 2016, when Cloud County began notifying its new BA, SPP, of any changes in the wind farm’s real output capabilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm from this noncompliance is that the BA is unaware of changes in Cloud County’s real output capabilities and the BA is making plans and predictions to maintain grid stability based off of inaccurate information. Throughout the noncompliance Cloud County made timely notifications to its Transmission Operator. These notifications minimize the chance of any actual harm because other Reliability Entities in SPP were made aware of any changes in the wind farm’s real output capabilities. Cloud County also offers a total capacity of 201 MW to the BES at its Elm Creek Substation which is minimal in comparison to SPP’s total load. Cloud County’s small size lessens the impact that changes to its real output capabilities would have on the rest of the grid. No harm is known to have occurred. ReliabilityFirst considered Cloud County's TOP-002 R14 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, Cloud County changed its reporting policies and procedure to reflect that SPP should be notified of all changes to the wind farm’s real output capabilities. To ensure that events of a similar nature will not occur, Cloud County will annually confirm not only the contact information of all connected Reliability Entities in accordance with EOP-004-2 R3, but will also confirm the reliability function for which the entity is serving. By conducting these annual confirmations, it will ensure that proper reliability functions, such as the current BA, are notified when required. Cloud County will also check with SPP on a quarterly basis and monitor SPP’s website to confirm that SPP is still serving as Cloud County’s active BA. If Cloud County discovers that SPP is no longer its BA, Cloud County will take all necessary action to find out who its new BA is and then will make all proper notifications to that new BA.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW1) | NCR03006 | RFC2016016083 | TOP-002-2.1b | R14 | On August 29, 2016, Blue Canyon Windpower V, LLC (Blue Canyon V) submitted a Self-Report through MLW1, under an existing multi-region registered entity agreement, stating that, as a Generator Operator, it had an issue of TOP-002-2.1b R14. On March 1, 2014, Southwest Power Pool’s (SPP) Integrated Marketplace became effective. Part of this market change included SPP becoming the Consolidated Balancing Authority (CBA) for its region. This change included deregistering legacy Balancing Authorities (BAs) within the SPP footprint. Although EDP Renewables North American (EDPR NA) was aware of the new market structure, it was unaware of and not notified that Blue Canyon V’s BA, Western Farmers Electric Cooperative, had been deregistered as Blue Canyon V’s BA. Western Famers Electric Cooperative also never notified Blue Canyon V or EDPR NA that it had been deregistered as Blue Canyon V’s BA in any way. Blue Canyon V also never received notification from its new BA, SPP, that it should now be notifying SPP instead of Western Farmers Electric Cooperative of changes in the wind farm’s real output capabilities. Due to this lack of notification, Blue Canyon V continued to notify the legacy BA, Western Farmers Electric Cooperative, instead of the new BA, SPP, of changes in the wind farm’s real output capabilities. During the duration of the noncompliance, Blue Canyon V notified its legacy BA, Western Farmers Electric Cooperative, and its Transmission Operator of any changes in the wind farm’s real output capabilities.) Despite this lack of notification, Blue Canyon V is still responsible under TOP-002-2.1b R14 to notify its current BA of any relevant changes. Blue Canyon V should have known that SPP was its active BA because information stating that SPP was now the BA for all Registered Entities in SPP’s footprint effective March 1, 2014 was readily available on SPP’s website and widely known throughout the SPP footprint thanks to the work of the SPP Consolidated Balancing Authority Steering Committee. It took Blue Canyon V more than two years to realize that SPP was their active BA. Blue Canyon V discovered that SPP was their active BA after EDPR found out Blue Canyon V’s existing BA had deregistered during an internal information sharing meeting. This noncompliance involves the management practice of verification. After SPP’s Integrated Marketplace became effective on March 1, 2014, Blue Canyon V never verified the identity of its BA and did not have a process in place to verify that it was sending its information to the correct BA. This lack of verification is the root cause of the noncompliance. This issue started on May 15, 2014, when Blue Canyon V was required to notify its new BA, SPP, of any changes in the wind farm’s real output capabilities, and ended on December 5, 2016, when Blue Canyon V began notifying its new BA, SPP, of any changes in the wind farm’s real output capabilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm from this noncompliance is that the BA is unaware of changes in Blue Canyon V’s real output capabilities and the BA is making plans and predictions to maintain grid stability based off of inaccurate information. Throughout the noncompliance Blue Canyon V made timely notifications to its Transmission Operator. These notifications minimize the chance of any actual harm because other Reliability Entities in SPP were made aware of any changes in the wind farm’s real output capabilities. Blue Canyon V also offers a total capacity of 105.6 MW to the BES at the Cherry Road Substation which is minimal in comparison to SPP’s total load. Blue Canyon V’s small size lessens the impact that changes to its real output capabilities would have on the rest of the grid. No harm is known to have occurred. ReliabilityFirst considered Blue Canyon V's TOP-002 R14 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, Blue Canyon V changed its reporting policies and procedure to reflect that SPP should be notified of all changes to the wind farm’s real output capabilities. To ensure that events of a similar nature will not occur, Blue Canyon V will annually confirm not only the contact information of all connected Reliability Entities in accordance with EOP-004-2 R3, but will also confirm the reliability function for which the entity is serving. By conducting these annual confirmations, it will ensure that proper reliability functions, such as the current BA, are notified when required. Blue Canyon V will also check with SPP on a quarterly basis and monitor SPP’s website to confirm that SPP is still serving as Blue Canyon V’s active BA. If Blue Canyon V discovers that SPP is no longer its BA, Blue Canyon V will take all necessary action to find out who its new BA is and then will make all proper notifications to that new BA.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | PPL Electric Utilities Corporation (PPLEU) | NCR00884 | RFC2016016350 | PRC-023-3 | R1 | On October 5, 2016, PPLEU submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue of PRC-023-3 R1. Due to organizational changes and concerns over the completeness of prior relay loadability calculations related to PRC-023, PPLEU’s Relay Engineering group undertook a comprehensive review of all PRC-023 applicable relay settings in 2016. During this review, PPLEU discovered three separate instances that involve a total of four issues. First, PPLEU’s Relay Engineering group discovered that relays on two different transmission lines were set with inactive voltage supervision for switch-on-to-fault (SOTF). PPLEU had previously thought that relays on those two different transmission lines had voltage supervision active for SOTF because most other similarly situated transmission lines had voltage supervision active for SOTF. Because voltage supervision was not active, the relay settings did not meet PRC-023-3 R1 Criterion 1 as documented. Second, PPLEU determined that a separate circuit did not meet PRC-023-3 R1 Criterion 1 as documented because PPLEU used an incorrect limiting factor in a previous calculation. Using the correct limiting factor, PPLEU determined that the line met Criterion 2 without any changes to the relay settings. In sum, PPLEU had informed PJM it was using Criterion 1 for this particular circuit. PPLEU had not provided accurate information to PJM about which Criterion this circuit was using, which causes the noncompliance. Third, PPLEU determined that another separate circuit did not meet PRC-023-3 R1 Criterion 1 as documented because PPLEU used an incorrect limiting factor in a previous calculation. Using the correct limiting factor, PPLEU determined that the relay settings did meet PRC-023-3 R1 Criterion 1. This noncompliance involves the management practices of verification and workforce management through ineffective training. PPLEU determined that the prior engineering review it had conducted during preparation for its 2015 audit did not verify all the data inputs. The prior engineering review occurred shortly after the group responsible for performing the review changed from the Transmission & Substation Asset Management Operations Analysis group to the Relay Engineering group. Instead, the preparation focused on the accuracy of the PRC-023 reporting tool, incorporation of human performance alerts within the reporting tool, and the interpretation of the results from the reporting tool. This failure to verify all the data is a root cause of this noncompliance. Ineffective training is also involved because PPLEU personnel twice used the same wrong limiting factor on two separate circuits. This issue started on December 12, 2014, when PPLEU set relays on two different transmission lines with inactive voltage supervision for SOTF (the start date of the first of PPLEU’s PRC-023 issues), and ended on October 15, 2016, when PPLEU reset all of the relays to meet PRC-023 Criterion 1 and 2 and notified PJM accordingly. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm from this noncompliance is having a transmission line trip before its actual limits are met or having a transmission line not trip when needed to preserve reliability because of an incorrectly calculated rating that is then shared with and relied upon by PJM. In this case, the potential harm is minimized because SOTF elements are active for a short period of time after a breaker closes typically to protect equipment and workers in instances where protective grounds may have been left after maintenance tasks have been completed. PPLEU has checks in place to ensure those protective grounds are removed per the lock out/tag out policy, the SOTF elements would trip if a worker were to leave protective grounds in place. For the relay setting that did not meet Criterion 1, but did meet Criterion 2, the relay setting did not meet Criterion 1 by 3%. For the relay settings that did not meet Criterion 1 for loadability, PPLEU Transmission Planning completed a study of the removal of the transmission line at issue and did not identify any cascading outages. Additionally, ReliabilityFirst notes that PPLEU’s Transmission Real Time Operations and Day-Ahead Operations Planning were not adversely impacted due to these PRC-023 issues. No harm is known to have occurred. ReliabilityFirst considered PPLEU's PRC-023 R1 compliance history in determining the disposition track. PPLEU’s relevant prior noncompliance with PRC-023 R1 includes: RFC2015015272. A Compliance Exception addressing a noncompliance with PRC-023-3 R1 was posted on the NERC website on April 28, 2016. The prior noncompliance is distinguishable from the current noncompliance. In the prior noncompliance, PPLEU incorrectly classified two 230 kV transmission lines as Criterion 1 that were below the minimum relay setting for Criterion 1. A contributing cause of the prior noncompliance was that PPLEU had the Transmission & Substation Asset Management Operations Analysis group reviewing the PRC-023-3 spreadsheet when the Relay Engineering group was more appropriate to review the spreadsheet. The prior noncompliance is distinguishable because the issue was that the wrong group was reviewing the relay settings while in the current noncompliance, the correct group (Relay Engineering) was performing the review, but that group did not verify all the data inputs while preparing for PPLEU’s 2015 audit. The Relay Engineering group had just taken over responsibility for reviewing the PRC-023-3 spreadsheet when the data inputs at issue in this noncompliance were not validated prior to PPLEU’s 2015 audit. That lack of verification, which partially occurred due to the transition in groups responsible for reviewing the spreadsheet, caused the current noncompliance. ReliabilityFirst determined that PPLEU’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, PPLEU: 1) applied the correct settings to all of the involved relays in order to enable voltage supervision for SOTF; 2) notified PJM of the use of Criterion 2 for the circuit that did not meet PRC-023 R1 Criterion 1 and notified PJM of the other relay settings updates; 3) set the relay to meet PRC-023 Criterion 1; 4) reviewed the results of the comprehensive review of all PRC-023 applicable relay settings; and 5) met with staff to review and reinforce the procedure and to discuss all recent updates made to the procedure. This meeting retrained staff on the importance of having correct relay settings and on all steps they need to take while updating relay settings.
2017-04-27 | SERC Reliability Corporation (SERC) | AL Sandersville, LLC (Sandersvl) | NCR11050 | SERC2017017035 | PRC-019-2 | R1 | On February 15, 2017, Sandersvl submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. Sandersvl did not have appropriate evidence to demonstrate completion of coordination for 40% of its Applicable Facilities as required by the PRC-019-2 enforcement date as of July 1, 2016. An asset manager assists Sandersvl in its NERC Compliance program under contract. The contractor incorrectly calculated the enforcement date of PRC-019-2 as two years from the FERC approval date of PRC-019-2. However, the implementation plan for PRC-019-2 states that enforcement is based the implementation plan for PRC-019-1. This miscalculation resulted in anticipating that the first implementation period threshold of 40% would become effective July 1, 2017, instead of July 1, 2016. On December 6, 2016, a compliance committee composed of contractor representatives identified the error and reported it to Sandersvl. The primary cause of this issue is the misunderstanding of the implementation schedule resulting from inadequate compliance oversight. This issue started on July 1, 2016, when Sandersvl did not meet the implementation schedule, through March 31, 2017, when Sandersvl completed the coordination study. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Sandersvl’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, during the MOD-025 tests conducted prior to July 1, 2016 and Real and Reactive Capability tests performed in previous years, Sandersvl has not experienced a trip or loss of a generator unit during these tests indicating there are no problems with control system coordination. Sandersvl is an eight-unit peaking facility with a total output of 640 MW and operated with a 0.0% capacity factor in 2016. It interconnects with Georgia Power Company that dispatches over 15,900 MW through the Southern Company Balancing Authority. Loss of the Sandersvl output would have a minor effect on Bulk Electric System reliability. No harm is known to have occurred. SERC considered Sandersvl’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Sandersvl: 1) verified coordination of the Voltage Regulator Controls and generator protection devices; and 2) created a notification in the form of a recurring preventive maintenance work order or as an obligation that escalates until completed in the Effingham tracking system for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable Standards incorporating the NERC initial notification of confirmation of the implementation or due date(s). To mitigate this issue, Sandersvl will complete the following mitigation activity by June 30, 2017: 1) work with the asset manager who has restructured its Reliability Standards Compliance Group (RSCG) to provide increased oversight and resources to assist plants to prevent further compliance issues. In particular response to the misunderstanding of implementation dates the restructured RSCG undertook an examination and improvement of its processes for determining implementation periods to bolster the scrutiny of such dates in the future.
2017-04-27 | SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2016015978 | PRC-001-1.1(ii) | R3; R3.2 | During a Compliance Audit conducted from April 19, 2016 to August 4, 2016, SERC determined that BREC, as a Transmission Operator (TOP), had an issue of PRC-001-1.1(ii) R3.2. BREC did not provide evidence of protective system change coordination with one interconnected TOP. The audit team discovered one instance where BREC did not coordinate a zone 3 distance relay setting change with one interconnected TOP. On July 9, 2015, BREC changed a zone 3 relay setting on one 161kV line, but failed to coordinate the relay setting change with the interconnecting TOP. During the assessment, SERC verified that BREC made no other protection system changes affecting interconnected transmission systems. The primary cause of the issue is that BREC incorrectly concluded that it was not required to coordinate the zone 3 distance relay change with the TOP. This issue started on July 9, 2015, when BREC changed the zone 3 relay set point without coordination, and ended on July 21, 2016, when BREC coordinated the zone 3 set point with the interconnected TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). BREC’s failure to coordinate protection system relay settings could result in inadequate protection or unnecessary protection system actions in the event of an electrical fault. In this issue, BREC reduced the reach of a zone 3 relay, which could leave a portion of a transmission line without backup protection. However, the zone 1 and zone 2 relaying remained in effect as primary protection and the reach of the zone 3 relay was reduced only 5.5%. The issue was limited to a single relay, so any risk was limited to a confined area of the BPS. BREC did not experience any unprotected faults or unnecessary operations during the duration of the issue. No harm is known to have occurred. SERC considered BREC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, BREC: 1) updated its existing Protection System Maintenance and Testing Program document to include the following coordination requirements: a) Protection system changes impacting existing interconnections; b) Protection system additions and modifications necessary for new interconnections; and c) Other protections system changes that can reasonably be expected to have an effect on the operation of the protection system(s) of other transmission or generator operators; and 2) provided PRC-001 training to those involved in protection system modifications.
2017-04-27 | SERC Reliability Corporation (SERC) | Citizens Electric Corporation (CEC) | NCR01192 | SERC2016016403 | PRC-002-2 | R1; R1.2 | On October 24, 2016, CEC submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of PRC-002-2 R1.2. CEC did not notify another owner of Bulk Electric System (BES) Elements connected to identified BES buses within 90-calendar days of completion that the BES Elements require sequence of events recording data and/or fault recording data. On July 1, 2016, CEC identified one BES bus on CEC’s system for which sequence of events recording and fault-recording data is required. On July 6, 2016, during CEC’s quarterly compliance team meeting, the team discussed CEC’s compliance with the PRC-002-2. The team discussed the notification requirement and concluded that it could communicate the required notification at the annual transmission-planning meeting with the TO, which had a tentative meeting date set for October 6, 2016. The team acknowledged that it would need to reschedule this tentative date to an earlier date in order for CEC to meet the 90-day notification requirement for PRC-002-2 R1.2. However, CEC failed to reschedule the meeting to an earlier date and failed to notify the TO by September 29, 2016. On October 11, 2016, during a quarterly compliance review meeting, CEC discovered that it did not notify the TO of the BES bus that connects to the TO's system within 90-calendar days of the date CEC identified the bus. CEC notified the TO on October 13, 2016. CEC was 15 days late in notifying the TO. The primary cause of the issue was CEC’s failure to follow through with the meeting reschedule and notification to the TO. This issue started on September 29, 2016, when CEC did not notify the TO within 90 days after enforceable date, and ended on October 13, 2016, when CEC notified the TO. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). CEC’s failure to notify a TO of its sequence of events recording data and fault recording data requirements could result in insufficient data to fully analyze a disturbance on the BPS. However, sequence of events recording data and fault recording data are used for forensic analyses following a disturbance and do not affect real-time operation, long-term or short-term planning of the BPS. According to the implementation plan for PRC-002-2, a significant amount of sequence of events recording data and/or fault recording data capability already exists on the BPS, and fault data is readily obtainable. CEC has identified only one BES bus to become compliant to this new Standard and CEC has never received any request from the TO connected to this bus for such data. No harm is known to have occurred. SERC considered Citizens Electric Corporation’s (CEC) compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, CEC: 1) notified the TO of CEC’s one BES bus that connects to the TO's system; and 2) implemented a calendar system to track all necessary SERC and NERC deadlines with advance reminders sent to all team members of the pending due dates.
2017-04-27 | SERC Reliability Corporation (SERC) | City of Springfield, IL (CWLP) | NCR01328 | SERC2016016028 | EOP-001-2.1b | R5 | On August 17, 2016, CWLP submitted a Self-Report stating that, as a Balancing Authority (BA) and Transmission Operator (TOP), it had an issue of EOP-001-2.1b R5. CWLP did not annually review and update one emergency plan and thus it did not provide a copy of the updated emergency plan to its Reliability Coordinator (RC) and to neighboring TOPs and BAs. On July 8, 2016, CWLP discovered that it did not complete the 2015 annual review and update of one emergency plan. The purpose of the one emergency plan is to ensure that CWLP maintains adequate fuel deliveries to the generating unit facilities during normal operating conditions, delayed delivery conditions, and emergency conditions. This document addresses fuel supply and inventory as required in EOP-001-2.1b R4. CWLP discovered this issue when the operations superintendent was looking for the current version to complete a data request and identified that CWLP did not have a 2015 version of the document. CWLP determined several causes of this issue. One cause was that the responsible subject matter expert (SME) retired during the 2015 annual review and update process. The subsequent responsible SME quickly changed roles again due to a promotion and did not complete a thorough turnover of the compliance duties with the new SME. In addition, CWLP delayed the normal review and update process because the final solution was under review to replace a fuel oil storage tank at a generation black start unit. As a result, CWLP did not complete the document review and update for the CWLP Fuel Supply Policy by the end of calendar year for 2015. A CWLP internal control initiated the annual review and update event, but CWLP did not complete the review and update. This issue started on January 1, 2016, when CWLP did not complete the 2015 review of the emergency plan, and ended on August 19, 2016, when CWLP approved the revised emergency plan and provided a copy to its RC and to neighboring TOPs and BAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). CWLP’s failure to timely review and update the emergency plan could have delayed coordinated efforts to mitigate an operating emergency. However, CWLP communicates daily with the fuel suppliers, the unit operators continuously monitor the fuel oil levels, and alarms sound if the fuel oil levels decline to predetermined levels. CWLP operations remain in daily contact with the natural gas supplier as it makes nominations for the current and next day unit operations. In addition, CWLP includes and reviews the black start unit fuel reserve levels in the CWLP Restoration Plan. No harm is known to have occurred. SERC considered CWLP’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, CWLP: 1) completed the 2016 review and update of the CWLP Fuel Supply Policy; 2) provided a copy of the updated emergency plan to its RC and neighboring TOPs and BAs; and 3) implemented an additional internal control for an additional SME to annually review the emergency plan. The responsible Generation Owner (GO) SME remains the primary responsible SME, a second (TOP) and (BA) SME shall now review the document and revision date at the time of the review of CWLP Restoration Plan prior to the required document coordination with the Reliability Coordinator and neighboring TOP and (BA.
2017-04-27 | SERC Reliability Corporation (SERC) | Effingham County Power, LLC (Effingham) | NCR11597 | SERC2017016974 | PRC-019-2 | R1 | On February 10, 2017, Effingham submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. Effingham did not meet the NERC implementation schedule for verifying the proper coordination of its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for 40% of its Facilities by July 1, 2016. An asset manager assists Effingham in its NERC Compliance program under contract. The contractor incorrectly calculated the enforcement date of PRC-019-2 as two years from the FERC approval date of PRC-019-2. However, the implementation plan for PRC-019-2 states that enforcement is based on the implementation plan for PRC-019-1. This miscalculation resulted in anticipating that the first implementation period threshold of 40% would become effective July 1, 2017 instead of July 1, 2016. On December 6, 2016, a compliance committee composed of contractor representatives identified the error and reported it to Effingham. The primary cause of this issue is the misunderstanding of the implementation schedule resulting from inadequate compliance oversight. This issue started on July 1, 2016, when Effingham did not meet the implementation schedule, and ended on February 3, 2017, when Effingham completed the coordination study. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Effingham’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, the Effingham Facility consists of three generators with total output capacity of 595 MWs in the Southern Company Balancing Area, therefore the three individual units, the largest being 199 MWs, that were noncompliant should have a minimal impact if any tripped offline. Effingham reported that during the MOD-025 tests conducted prior to July 1, 2016, and the Real and Reactive Capability tests performed in previous years, Effingham did not experience a trip or loss of a generator unit during these tests because of system conditions. In addition, the coordination study identified no needed relay setting changes. No harm is known to have occurred. SERC considered Effingham’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Effingham: 1) verified the proper coordination of the voltage regulator controls and the generator protection devices; and 2) created a notification in the form of a recurring preventive maintenance work order or as an obligation that escalates until completed in the Effingham tracking system for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable Standards incorporating the NERC initial notification of confirmation of the implementation or due date(s). To mitigate this issue, Effingham will complete the following mitigation activities by June 30, 2017: 1) create a tracking spreadsheet to monitor compliance deadlines and status for responsible parties. The Corporate Reliability Standards Compliance Group will coordinate all new or modified standards with the necessary engineering groups within the asset manager organization, to include, but not limited to submittal of verification to the region (SERC) to ensure the understanding of all aspects of the Reliability Standard including requirements, implementation plans, and schedules, as necessary.
2017-04-27 | SERC Reliability Corporation (SERC) | Gibson City Energy Center, LLC (GCEC) | NCR11434 | SERC2016016036 | PRC-019-2 | R1 | On August 19, 2016, GCEC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. GCEC stated that it had not completed its verification of generator control and Protection System coordination by July 1, 2016. The implementation plan for PRC-019-2 R1 requires the GO to verify its generator control and Protection System coordination in annual increments beginning with 40% of its generation by July 1, 2016. GCEC has two 114 MW combustion turbines, so in order to comply with the requirement, GCEC was required to perform the control system coordination verification of at least one of the units by July 1, 2016. GCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for PRC-019-2 R1 compliance, and did not understand the verification requirement. On June 29, 2016, a third party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to GCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and insufficient contract or oversight. GCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, and ended September 30, 2016 when GCEC completed the required verification of system coordination on Unit 1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GCEC’s failure to properly coordinate between generator protective relays and generator voltage regulator controls and limit functions could result in generators unnecessarily tripping off-line. However, GCEC contributes only 228 MW to the grid while operating and operates at approximately a 5% capacity factor. When GCEC operated, no trips occurred due to inadequate coordination and when GCEC performed the verification, no changes were required. Also, GCEC completed the required 40% coordination three months after the required date. No harm is known to have occurred. SERC considered GCEC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GCEC: 1) conducted the required verification at Unit 1; 2) developed and will annually review an internal compliance procedure while also updating any standard revisions; 3) implemented an internal software product that allows for tracking of compliance reporting functions and internal deadlines that GCEC deemed appropriate; 4) added PRC-019 to the compliance tracker with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies; 5) continued to use third-party mock audits and internal self-assessments as a second check on the compliance tracker; and 6) scheduled bi-weekly compliance calls among site managers to ensure plant staffs are aware of upcoming deadlines and compliance obligations
2017-04-27 | SERC Reliability Corporation (SERC) | Mid Georgia Cogen L.P. (MidGa) | NCR00167 | SERC2017017031 | PRC-019-2 | R1 | On February 14, 2017, MidGa submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. MidGa did not have appropriate evidence to demonstrate completion of coordination for 40% of its Applicable Facilities as required by the PRC-019-2 enforcement date as of July 1, 2016. An asset manager assists MidGa in its NERC Compliance program under contract. The contractor incorrectly calculated the enforcement date of PRC-019-2 as two years from the FERC approval date of PRC-019-2. However, the implementation plan for PRC-019-2 states that enforcement is based on the implementation plan for PRC-019-1. This miscalculation resulted in anticipating that the first implementation period threshold of 40% would become effective July 1, 2017 instead of July 1, 2016. On December 6, 2016, a compliance committee composed of contractor representatives identified the error and reported it to MidGa. The primary cause of this issue is the misunderstanding of the implementation schedule resulting from inadequate compliance oversight. This issue started on July 1, 2016 when MidGa did not meet the implementation schedule, and will end when MidGa completes the coordination study. (Expected April 30, 2017) | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MidGa’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, during the MOD-025 tests conducted prior to July 1, 2016 and Real and Reactive Capability tests performed in previous years, MidGa has not experienced a trip or loss of a generator unit during these tests indicating there are no problems with control system coordination. MidGa is a 300 MW two-into-one cogeneration power plant that operated with an 18% capacity factor in 2016. It interconnects with Georgia Power Company that dispatches over 15,900 MW through the Southern Company Balancing Authority. Loss of the MidGa output would have a minor effect on Bulk Electric System operation. No harm is known to have occurred SERC considered MidGa’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, MidGa will complete the following mitigation activities by June 30, 2017: 1) verify coordination of the Voltage Regulator Controls and generator protection devices; 2) create a notification in the form of a recurring Preventive Maintenance work order or as an obligation that escalates until completed in the Company Obligation Tracking System for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable standards incorporating the NERC initial notification of confirmation of the implementation or due date(s); 3) review of Kestrel report once it’s been submitted to Mid Georgia and update Limiter/Protective relays as necessary; and 4) create a tracking spreadsheet to monitor compliance deadlines and status for responsible parties.
2017-04-27 | SERC Reliability Corporation (SERC) | MPC Generating, LLC (MPCGen) | NCR11596 | SERC2017017034 | PRC-019-2 | R1 | On February 15, 2017, MPCGen submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. MPCGen did not have appropriate evidence to demonstrate completion of coordination for 40% of its Applicable Facilities as required by the PRC-019-2 enforcement date as of July 1, 2016. An asset manager assists MPCGen in its NERC Compliance program under contract. The contractor incorrectly calculated the enforcement date of PRC-019-2 as two years from the FERC approval date of PRC-019-2. However, the implementation plan for PRC-019-2 states that enforcement is based on the implementation plan for PRC-019-1. This miscalculation resulted in anticipating that the first implementation period threshold of 40% would become effective July 1, 2017 instead of July 1, 2016. On December 6, 2016, a compliance committee composed of contractor representatives identified the error and reported it to MPCGen. The primary cause of this issue is the misunderstanding of the implementation schedule resulting from inadequate compliance oversight. This issue started on July 1, 2016, when MPCGen did not meet the implementation schedule, through March 31, 2017, when MPCGen completed the coordination study. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MPCGen’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, during the MOD-025 tests conducted prior to July 1, 2016 and Real and Reactive Capability tests performed in previous years, MPCGen has not experienced a trip or loss of a generator unit during these tests indicating there are no problems with control system coordination. MPCGen is a two-unit peaking facility with a total output of 309 MW and operated with a 0.5% capacity factor in 2016. It interconnects with Georgia Power Company that dispatches over 15,900 MW through the Southern Company Balancing Authority. Loss of the MPCGen output would have a minor effect on Bulk Electric System reliability. No harm is known to have occurred. SERC considered MPCGen’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, MPCGen: 1) verified coordination of the Voltage Regulator Controls and generator protection devices; and 2) created a notification in the form of a recurring Preventive Maintenance work order or as an obligation that escalates until completed in the Company Obligation Tracking System for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable standards incorporating the NERC initial notification of confirmation of the implementation or due date(s). To mitigate this issue, MPCGen will complete the following mitigation activity by June 30, 2017: 1) create a tracking spreadsheet to monitor compliance deadlines and status for responsible parties.
2017-04-27 | SERC Reliability Corporation (SERC) | Oglethorpe Power Corporation (OPC) | NCR01287 | SERC2016016191 | PRC-019-2 | R1 | On September 22, 2016, OPC submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. OPC did not meet the NERC implementation schedule for verifying the proper coordination of its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for 40% of its Facilities by July 1, 2016. OPC misunderstood the implementation plan regarding coordination studies and required setting changes. OPC mistakenly interpreted the implementation plan as requiring studies for 40% of the Facilities by July 1, 2016 and implementing necessary setting changes within 90 days of July 1, 2016. OPC completed the coordination studies for four of its nine facilities by July 1, 2016; however, based on its incorrect interpretation, OPC deferred implementing the necessary setting changes until the next maintenance outage of each unit, which was after July 1, 2016. On July 21, 2016, OPC submitted a request to SERC inquiring how to approach compliance for a must-run unit that is subject to PRC-019-2 R1. On September 6, 2016, based on SERC’s response, OPC determined that its interpretation of the implementation plan to allow 90 days from July 1, 2016 for setting changes was incorrect. This issue started on July 1, 2016, when OPC did not meet the implementation schedule, and ended on October 1, 2016, when OPC completed the setting changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. OPC’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, the instant issue includes 15 units representing approximately 1,795 MWs of OPC’s 7,972 MWs in the Southern Company Services area. The largest generator in the instant issue is 167.5 MWs; therefore, any single OPC unit should have a minimal impact if it tripped offline. No harm is known to have occurred. SERC considered Oglethorpe Power Corporation’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, OPC: 1) implemented the setting changes; 2) reviewed schedules for the additional phases of implementation of PRC-019 to ensure both the studies and the settings changes for the designated percentage of facilities are completed in the increments due; and 3) implemented a process to ensure all key parties to Standards compliance and implementation of compliance with new standards fully understand and agree regarding what action is required and when by discussion of applicable standards: a. when filed with FERC approval, with follow-up to confirm mutual understanding of required activities, milestones, and documentation; and b. upon the issuance of FERC Order approving a new or revised Reliability Standard.
2017-04-27 | SERC Reliability Corporation (SERC) | Prairie State Generating Company (PrairieSt) | NCR11175 | SERC2017016785 | VAR-002-4 | R3 | On January 13, 2017, PrairieSt submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-4 R3. PrairieSt did not notify its Transmission Operator (TOP) of a status change of the power system stabilizer (PSS) within 30 minutes of the change. On November 29, 2016, PrairieSt returned a generator unit to service following an outage. The outage work required PrairieSt to cycle off both the primary and redundant power. The power cycle placed the automatic voltage regulator (AVR) in manual and the PSS in the off state. Prior to the unit going online, the operator identified that the AVR was in manual and placed the AVR in automatic controlling voltage. On December 12, 2016 at 7:09 a.m., the shift supervisor noticed that the unit’s PSS was off and instructed the control room operator to turn the PSS on. The control room operator turned the PSS on but did not notify the TOP of the change in status of the PSS. PrairieSt determined the primary cause to be human error, as the operator did not understand the communication requirements when placing the PSS in service. This issue occurred on December 12, 2016 at 7:40 a.m., when PrairieSt changed the status of the PSS and did not notify the TOP within 30 minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PrairieSt’s failure to notify the TOP of the change of state of reactive devices may lead to inappropriate voltage-controlling action by the TOP. However, PrairieSt maintained output voltage according to the assigned Voltage Schedule throughout the period. PrairieSt consists of two coal-fired units; unit 1 operating capacity is 873 MWs, and unit 2 operating capacity is 875 MW. Unit 1 was online and operating with the AVR in automatic controlling voltage and with the PSS on for the duration of the instant issue; therefore, one of the two units had PSS capability. No harm is known to have occurred. SERC considered Prairie State Generating Company’s (PrairieSt) compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, PrairieSt: 1) revised the start-up and shut-down procedure to include verifying the PSS is in service and notifying the TOP within 30 minutes of the PSS being in service; 2) trained all of the Control Room Operators (CRO) and Shift Supervisor on the revised start-up/shut-down procedure; 3) retrained all CROs and Shift Supervisors to notify the TOP within 30 minutes of when the PSS is turned on/off; and 4) identified DCS logic revisions to implement. To mitigate this issue, PrairieSt will complete the following mitigation activities by November 1, 2017: 1) implement the following DCS logic changes: a. The PSS automatically turn on at 150 MWg on each unit via the excitation system. b. When the PSS changes state, the CRO will receive an alarm to notify Ameren within 30 minutes of the status change. c. If the PSS does not come on automatically at 150 MWg from the exciter, the new DCS logic will place the PSS in service at 160 MWg via the DCS. When the PSS changes state, the CRO will receive an alarm to notify Ameren within 30 minutes. d. If the PSS is still not in service at 175 MWg, a priority 1 alarm will notify the CRO to turn on the PSS and notify Ameren within 30 minutes that the PSS is in service. e. On a controlled shutdown or trip, the PSS will turn off automatically at 150 MWg on each unit via the excitation system. f. When the Unit is coming off line in a controlled manner and the PSS changes state, a priority 1 alarm will come in to tell the CRO to notify Ameren that the PSS is out of service within 30 minutes of the status change. g. If the unit trips off, PrairieSt will notify Ameren that the AVR is not controlling voltage and the PSS is out of service. h. PrairieSt will implement Unit 1 DCS logic changes at the next opportunity (unit outage) but no later than 5/31/17 when the unit comes out of the planned spring outage. i. PrairieSt will implement Unit 2 DCS logic changes at the next opportunity (unit outage) but no later than 11/1/17 when the unit comes out of the planned fall outage.
2017-04-27 | SERC Reliability Corporation (SERC) | Shelby County Energy Center, LLC (SCEC) | NCR11629 | SERC2016016038 | PRC-019-2 | R1 | On August, 19, 2016, SCEC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-019-2 R1. SCEC stated that it had not completed its verification of generator control and Protection System coordination by July 1, 2016. The implementation plan for PRC-019-2 requires the GO to verify its generator control and Protection System coordination in annual increments beginning with 40% of its generation by July 1, 2016. SCEC has eight combustion turbines, so in order to comply with the requirement; SCEC was required to perform the controls verification of at least four of the units by July 1, 2016. SCEC utilizes a consultant to manage its Operations and Maintenance responsibilities. The consultant believed that data recorded during commissioning was sufficient for PRC-019-2 R1 compliance, and did not understand the verification requirement. On June 29, 2016, a third party engineering consultant completed a mock audit at another managed site and discovered the misunderstanding which it reported to SCEC on or about July 1, 2016. The root cause of the issue was an incorrect understanding of compliance requirements and contract oversight. SCEC failed to perform adequate oversight to ensure compliance obligations were satisfied. The issue started on July 1, 2016, when the Standard became mandatory and enforceable, and ended August 31, 2016 when SCEC completed the required verification of system coordination on four units. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCEC’s failure to properly coordinate between generator protective relays and generator voltage regulator controls and limit functions could result in generators unnecessarily tripping off-line. However, SCEC contributes only 352 MW to the grid while operating and operates at a less than 5% capacity factor. When SCEC operated, no trips occurred due to inadequate coordination and when SCEC performed the verification, no changes were required. In addition, SCEC completed the required 40% coordination two months after the required date. No harm is known to have occurred. SERC considered SCEC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SCEC will complete the following mitigation activities by May 1, 2017: 1) conduct the required verification; 2) develop and annually review an internal compliance procedure while also updating any standard revisions; 3) implement an internal software product that allows for tracking of compliance reporting functions and internal deadlines that SCEC deemed appropriate; 4) add PRC-019 to the compliance tracker with appropriate lead-time so as to hire consultants to help with modeling and the coordination studies; 5) continue to use third party mock audits and internal self-assessments as a second check on the compliance tracker; and 6) schedule bi-weekly compliance calls among site managers to ensure plant staffs are aware of upcoming deadlines and compliance obligations.
2017-04-27 | SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, TO) (VEP-Trans) | NCR01214 | SERC2016016046 | PRC-023-3 | R1 | On August 25, 2016, VEP-Trans submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-023-3 R1. VEP-Trans discovered that two redundant digital relays at one location did not meet the transmission loadability limit requirements. VEP-Trans, per its procedure, sets the phase protective relays at each applicable circuit terminal to meet Requirement R1 using either Criteria 1 or Criteria 2 if possible. However, if VEP-Trans cannot satisfy Requirement 1 for a given circuit terminal using either Criteria 1 or Criteria 2, then System Protection Engineering (SPE) identifies other Criteria to prevent its phase protective relay settings from limiting transmission system load ability while maintaining reliable protection of the Bulk Electric System for all fault conditions. In the instant issue, during the engineering design phase of a 230kV line project, the SPE engineer developed relay settings that resulted in settings that did not satisfy Criteria 1 and Criteria 2. When submitting the request for review, the SPE design engineer communicated an issue regarding loadability. Although the reviewer suggested minor setting enhancements, the reviewer did not identify or address the loadability concern. By not addressing the loadability concern, VEP-Trans deployed non-compliant relay settings. On June 10, 2016, VEP-Trans returned the line to service with the relay settings on two redundant digital relays that did not meet the transmission loadability limit requirements. On June 14, 2016, a SPE engineer was reviewing the “Test & Energize” notification for the line and noticed that the relay settings for one terminal did not meet PRC-023-3 requirements and notified the Subject Matter Expert (SME). The SME initiated an assessment and confirmed the incorrect relay setting. The primary cause of this issue is the lack of a thorough review to include compliance requirements. In order to verify that there were no additional possible issues, VEP-Trans reviewed all applicable relay settings using existing “back from field” relay setting files to calculate the relay trip values. VEP-Trans compared the calculations to the facility rating to validate load ability compliance to PRC-023-3. VEP-Trans did not identify any additional issues. This issue started on June 10, 2016, when VEP-Trans returned the line to service with the relay settings that did not meet the transmission loadability limit requirements, and ended on June 15, 2016, when VEP-Trans developed, reviewed, and implemented correct relay settings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. VEP-Trans failure to identify relay settings that are lower than what the Standard allows could have caused the relays to trip prematurely or could limit the transmission operators’ ability to take action while protecting transmission equipment. However, the highest peak load recorded on the line during the time was 185 MVA (464 Amps at 230kV). The highest seasonal Facility Rating of the line for the available defined loading duration nearest four hours is 2440 Amps thus the highest recorded load on the line never exceeded more than 19% of the highest seasonal Facility Rating for the available defined loading duration nearest four hours. Also, the relay trip value incorrectly designed and installed in the field was 3068 Amps, resulting in a loadability of 126% of the Facility Rating applying Criteria 1 (>150%) and 106% of the Facility Rating applying Criteria 2 (>115%). Although the relay setting did not meet the compliance requirement, actual load during the period only reached 15% of the relay trip value. In addition, there were no events on the line during the period of June 10, 2016 to June 15, 2016, and the issue lasted only five days. No harm is known to have occurred. SERC considered VEP-Trans’ PRC-023-3 R1 compliance history in determining the disposition track. VEP-Trans’ relevant prior noncompliance with PRC-023-3 R1 includes: NERC Violation ID SERC2014014177. SERC2014014177 involved VEP-Trans not changing relay settings by the scheduled work order completion date. The MP for this issue did not address the cause of the instant issue. | To mitigate this issue, VEP-Trans: 1) conducted a “Compliance Stand-down” to refocus on compliance with PRC-023-3 and communicate the known factors surrounding the possible violation; 2) developed, reviewed, and implemented new relay settings on the line in question; 3) performed an extent of condition review of all applicable relay settings; 4) developed and implemented additional human performance enhancements to improve compliance visibility a. added a Compliance Tab highlighting; i. PRC-023-3 program summary; and ii. PRC-023-3 loadability calculation summary b. enhanced loadability summary section; i. automated loadability calculation cell background color for improved visibility (green/good and red/bad); and ii. added PRC-023-3 verbiage adjacent to percent loadability calculation for increased awareness; c. automated PRC-023-3 compliance verification prior to creation of relay setting file i. in the event settings are not in compliance with PRC-023-3, a pop-up warning is displayed prior to generating the relay setting file; and 5) provided additional training for the SPE group, to include the reviewers, around the human performance enhancements as well as review responsibilities.
2017-04-27 | SERC Reliability Corporation (SERC) | Walton County Power, LLC (WCP) | NCR11598 | SERC2017017032 | PRC-019-2 | R1 | On February 15, 2017, WCP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. WCP did not have appropriate evidence to demonstrate completion of coordination for 40% of its Applicable Facilities as required by the PRC-019-2 enforcement date as of July 1, 2016. An asset manager assists WCP in its NERC Compliance program under contract. The contractor incorrectly calculated the enforcement date of PRC-019-2 as two years from the FERC approval date of PRC-019-2. However, the implementation plan for PRC-019-2 states that enforcement is based on the implementation plan for PRC-019-1. This miscalculation resulted in anticipating that the first implementation period threshold of 40% would become effective July 1, 2017 instead of July 1, 2016. On December 6, 2016, a compliance committee composed of contractor representatives identified the error and reported it to WCP. The primary cause of this issue is the misunderstanding of the implementation schedule resulting from inadequate compliance oversight. This issue started on July 1, 2016, when WCP did not meet the implementation schedule, through March 31, 2017, when WCP completed the coordination study. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WCP’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, during the MOD-025 tests conducted prior to July 1, 2016 and Real and Reactive Capability tests performed in previous years, WCP has not experienced a trip or loss of a generator unit during these tests indicating there are no problems with control system coordination. WCP is a three-unit peaking facility with a total output of 450 MW and operated with an 8.0% capacity factor in 2016. It interconnects with Georgia Power Company that dispatches over 15,900 MW through the Southern Company Balancing Authority. Loss of the WCP output would have a minor effect on Bulk Electric System reliability. No harm is known to have occurred. SERC considered WCP’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, WCP: 1) verified coordination of the Voltage Regulator Controls and generator protection devices; and 2) created a notification in the form of a recurring Preventive Maintenance work order or as an obligation that escalates until completed in the Company Obligation Tracking System for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable standards incorporating the NERC initial notification of confirmation of the implementation or due date(s). To mitigate this issue, WCP will complete the following mitigation activity by June 30, 2017: 1) create a tracking spreadsheet to monitor compliance deadlines and status for responsible parties. The Corporate Reliability Standards Compliance Group will coordinate all new or modified standards with the necessary engineering groups within the Cogentrix organization, to include, but not limited to submittal of verification to the region (SERC) to ensure the understanding of all aspects of the Reliability Standard including Requirements, implementation plans, and schedules, as necessary. The objective is to ensure WCP develops a complete implementation strategy to convey acceptable approaches with clear understanding, responsibilities, and timelines.
2017-04-27 | SERC Reliability Corporation (SERC) | Washington County Power, LLC (WashCP) | NCR11599 | SERC2017017033 | PRC-019-2 | R1 | On February 15, 2017, WashCP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. WashCP did not have appropriate evidence to demonstrate completion of coordination for 40% of its Applicable Facilities as required by the PRC-019-2 enforcement date as of July 1, 2016. An asset manager assists WashCP in its NERC Compliance program under contract. The contractor incorrectly calculated the enforcement date of PRC-019-2 as two years from the FERC approval date of PRC-019-2. However, the implementation plan for PRC-019-2 states that enforcement is based on the implementation plan for PRC-019-1. This miscalculation resulted in anticipating that the first implementation period threshold of 40% would become effective July 1, 2017 instead of July 1, 2016. On December 6, 2016, a compliance committee composed of contractor representatives identified the error and reported it to WashCP. The primary cause of this issue is the misunderstanding of the implementation schedule resulting from inadequate compliance oversight. This issue started on July 1, 2016, when WashCP did not meet the implementation schedule, through March 31, 2017, when WashCP completed the coordination study. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WashCP’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, during the MOD-025 tests conducted prior to July 1, 2016 and Real and Reactive Capability tests performed in previous years, WashCP has not experienced a trip or loss of a generator unit during these tests indicating there are no problems with control system coordination. WashCP is a four-unit peaking facility with a total output of 600 MW and operated with a 2.1% capacity factor in 2016. It interconnects with Georgia Power Company that dispatches over 15,900 MW through the Southern Company Balancing Authority. Loss of the WashCP output would have a minor effect on Bulk Electric System reliability. No harm is known to have occurred. SERC considered WashCP’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, WashCP: 1) verified coordination of the Voltage Regulator Controls and generator protection devices; and 2) created a notification in the form of a recurring Preventive Maintenance work order or as an obligation that escalates until completed in the Company Obligation Tracking System for plant management to review future Reliability Standards via NERC’s Reliability Standards website for future enforceable standards incorporating the NERC initial notification of confirmation of the implementation or due date(s). To mitigate this issue, WashCP will complete the following mitigation activity by June 30, 2017: 1) create a tracking spreadsheet to monitor compliance deadlines and status for responsible parties. The Corporate Reliability Standards Compliance Group will coordinate all new or modified standards with the necessary engineering groups within the Cogentrix organization, to include, but not limited to submittal of verification to the region (SERC) to ensure the understanding of all aspects of the Reliability Standard including Requirements, implementation plans, and schedules, as necessary. The objective is to ensure WashCP develops a complete implementation strategy to convey acceptable approaches with clear understanding, responsibilities, and timelines.
2017-04-27 | Southwest Power Pool Regional Entity (SPP RE) | Buckeye Wind Energy, LLC (BEWE) | NCR11563 | SPP2016015962 | TOP-002-2.1b | R14.1 | On August 1, 2016, Buckeye Wind Energy (BEWE) submitted a Self-Certification stating that, as a Generator Operator, it had an issue of noncompliance with TOP-002-2.1b R14.1. On May 13, 2016, BEWE failed to timely notify its Transmission Operator (TOP) of changes in real output capabilities after the restoration of the real output capabilities of its generating facility, following a 17 hour forced outage on May 13, 2016 of 32 MWs of generation capacity. BEWE notified its TOP about the forced outage but did not notify its TOP of the capacity restoration until September 23, 2016, 132 days after the real output capacity of its generating facility was restored. The duration of this instance of noncompliance was from May 13, 2016, the date the feeder was restored to service and the plant was back to its full capacity, through September 23, 2016, the date the TOP was notified of the capacity restoration. The root cause of this instance of noncompliance was human error because the Operator responsible for notifying the TOP failed to adhere to BEWE’s documented notification protocols. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to timely notify the TOP of changes in capabilities and characteristics of the generating facility has the potential to affect the reliability of the BPS by causing the TOP to not have situational awareness of the system capability. Notwithstanding, BEWE is a 200 MW variable generation wind farm, which is generally not callable by system operators to support system generation, voltage, or frequency. Only one collector feeder, out of eight located on the BEWE 34.5 kV bus, was affected. This collector feeder has a capacity of 32 MW and was loaded at 19 MW when it was returned to service. BEWE did notify its BA when the collector feeder was returned to service. Because the TOP has monitoring telemetry of BEWE’s generating facility, it was aware that the real output capacity had been restored. No harm is known to have occurred. BEWE has no relevant prior violations for TOP-002-2.1b or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, BEWE: 1) investigated the noncompliance and completed a Root Cause Analysis; 2) distributed an email to all control room operators and power scheduling staff to reinforce the TOP-002.2.1, R14 communication protocols and the importance of following the process; and 3) held a mandatory meeting for Control Center Staff and discussed “Off Taker Notification Management” and the lessons learned from the untimely notification. SPP RE has verified the completion of all mitigation activity.
2017-04-27 | Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (EDE) | NCR01155 | SPP2016016185 | PRC-005-1.1b | R2.1 | On September 23, 2016, EDE submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of noncompliance with PRC-005-1.1b R2.1 because EDE did not properly maintain and test their Protection System devices. While investigating a misoperation on the 161 kV line from EDE Riverton Ram Substation 452 to EDE Oronogo Substation 110 that occurred on September 6, 2016, EDE discovered that the misoperation was the result of an incorrect CT ratio on one phase of the input to the backup protection system relay at the Oronogo Substation. Upon further investigation of the misoperation, EDE discovered that its relay maintenance technician had failed to verify the correct CT input values during the CT commissioning on June 23, 2014 and again during routine testing in July of 2015. EDE’s Protection System Maintenance Program (PSMP) requires that “Current and Voltage signals will be verified at the inputs of the protective relay during routine relay maintenance and testing interval.” However, the verification of values between the phase currents were not correctly verified thus violating PRC-005-1.1b R2.1. EDE conducted a thorough review of the technician’s maintenance activities. The review consisted of 257 tests performed by this technician. An additional 6 CT’s required resetting. EDE has approximately 4,800 devices in their PSMP and only 8 CTs were identified as having issues. The duration of this instance of noncompliance was from June 23, 2014, the date the substation was commissioned, through January 20, 2017, the date EDE completed its mitigation of the noncompliance by properly setting the CTs. The root cause of this instance of noncompliance was a combination of human error due to the failure of a relay technician to perform proper current transformer input value verification during relay commissioning and routine testing, and EDE’s failure to adequately train the technicians on these requirements and their specific responsibilities. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to verify the correct current transformer input values has the potential to affect the reliability of the BPS by allowing a relay not to operate as intended, potentially leading to false trips, remote clearing, delayed clearing, and/or the overreach of protective relays which can result in a loss of load. Notwithstanding, during this misoperation there was no load lost. As a compensating measure, EDE implemented a complete review of the technician's past maintenance activities to ensure compliance both to the Standard and EDE’s PSMP. EDE has approximately 4,800 devices in their PSMP. Only eight CTs (less than 1% of EDE’s total devices), needed resetting. No harm is known to have occurred. EDE has no relevant prior violations for PRC-005-1.1b R2 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, EDE: 1) correctly set and verified the CT input values; 2) updated its relay commissioning check-list document to include the use of a CPC (High Current Injection Test) on all commissioning; 3) conducted commissioning training; 4) conducted routine relay test training; and 5) reviewed other maintenance activities by the offending individual, and found and corrected similar issues to those reported in the self-report. SPP RE has verified the completion of all mitigation activity.
2017-04-27 | Texas Reliability Entity (Texas RE) | Barney M Davis LP (BMDLP) | NCR04009 | TRE2016016520 | MOD-025-2 | R1; R1.2 | On November 15, 2016, BMDLP submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R1. Specifically, BMDLP did not submit a completed Attachment 2 or equivalent information to its Transmission Planner (TP) within 90 calendar days of recording its Real Power capability verification during a staged test. On December 13, 2015, BMDLP conducted a Real Power verification for one of its applicable units. On February 25, 2016, BMDLP performed additional Real Power capability verifications on two other units. Although BMDLP completed its Real Power capability verifications for its three units as required by MOD-025-2 R1.1, BMDLP did not provide those verification results to its TP. BMDLP subsequently discovered that it did not submit its Real Power capability verifications while addressing issues related to its timely completion of its Reactive Power capability verifications. On February 27, 2017, BMDLP then provided the required Real Power capability verification information to its TP. The root cause of the issue was an insufficient process to ensure compliance with all applicable requirements in MOD-025-2 R1, including the applicable verification submission requirements. In particular, BMDLP personnel were not aware of the requirement to provide Real Power verification results to their TP within 90 days. This issue started on July 1, 2016, when implementation of MOD-025-2 R1 became mandatory and enforceable, and ended on February 27, 2017, when BMDLP submitted a completed Attachment 2 to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, BMDLP completed its Real Power testing as prescribed in Attachment 1 by July 1, 2016. Second, BMDLP also previously provided passing Real and Reactive Power verifications under region-specific output conditions, further limiting the scope of the missing verification data that would be incorporated into transmission planning models. Finally, BMDLP provided information similar to the required Real Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models. No harm is known to have occurred. Texas RE considered BMDLP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BMDLP: 1) submitted its Real Power verification testing results to its TP; 2) created a work order for MOD-025-2 Testing Requirements in its maintenance tracking system to ensure testing is performed prior to the required deadline; 3) conducted MOD-025-2 training for all BMDLP personnel and senior management, including training regarding the requirement to submit Real Power capability verifications to its TP within 90 days; and 4) issued a new procedure document detailing the process for completing MOD-025-2 testing and submitting the required verification information to its TP, including a requirement to submit all testing information within 60 days of completion. Texas RE has verified the completion of all mitigation activity.
2017-04-27 | Texas Reliability Entity (Texas RE) | Barney M Davis LP (BMDLP) | NCR04009 | TRE2017017361 | MOD-025-2 | R2; R2.1; R2.2 | On November 15, 2016, BMDLP submitted a Self-Report stating that, as a Generation Owner (GO), it had a possible noncompliance with MOD-025-2 R1 relating to the verification of Real Power capability. Subsequently, Texas RE determined that the issues described in BMDLP's MOD-025-2 R1 Self-Report also applied to BMDLP’s Reactive Power capability verifications. In particular, BMDLP failed to complete the required Reactive Power capability verifications as specified in MOD-025-2, Attachment 1 by July 1, 2016, as well as provide the results of those Reactive Power capability verifications to its Transmission Planner (TP) within 90 days of performing them. In early June 2016, BMDLP scheduled its required Reactive Power testing on its three generation units. However, several equipment issues required BMDLP to extend a previously planned outage through the end of June. As a result, BMDLP was not able to complete the required Reactive Power testing until July 27, 2017. Subsequently, BDMLP provided the results of its Reactive Power capability verification to its TP on November 10, 2017, approximately 106 days after it recorded the data for its Reactive Power capability verification. The root cause of the issue was an insufficient process to ensure compliance with all applicable requirements in MOD-025-2 R2. Specifically, BMDLP did not provide sufficient lead-time to ensure it could perform the required verifications in the event of an unplanned outage or other circumstance. Additionally, BMDLP was not aware of the requirement to provide Real Power verification results to their TP within 90 days. This issue started on July 1, 2016, when implementation of MOD-025-2 R2 became mandatory and enforceable, and ended on November 10, 2016, when BMDLP submitted all required Reactive Power capability verification information to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the duration of this issue was relatively short in the context of the transmission planning time horizon at issue here, with BMDLP submitting the required verification to its TP within 133 days of the date it was required to complete its Reactive Power capability verification. Second, BMDLP also previously provided passing Real and Reactive Power verifications under region-specific output conditions, further limiting the scope of the missing verification data that would be incorporated into transmission planning models. Finally, BMDLP provided information similar to the required Reactive Power verification data through other submissions to its Planning Coordinator, which then uses that information to coordinate the development of transmission planning models with region TPs. No harm is known to have occurred. Texas RE considered BMDLP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BMDLP: 1) performed all required Reactive Power testing; 2) submitted its Reactive Power verification testing results to its TP; 3) created a work order for MOD-025-2 testing requirements in its maintenance tracking system that establishes that testing will be performed on a four-year cycle to ensure there is adequate time to complete all required verifications within the five-year verification window; 4) conducted MOD-025-2 training for all BMDLP personnel and senior management regarding MOD-025-2 R2 testing requirements, including training regarding the requirement to submit Reactive Power capability verifications to its TP within 90 days; and 5) issued a new procedure document detailing the process for completing MOD-025-2 testing and submitting the required verification information to its TP, including a requirement that all testing information be submitted to its TP within 60 days of completion. Texas RE has verified the completion of all mitigation activity.
2017-04-27 | Texas Reliability Entity (Texas RE) | EC&R Panther Creek Wind Farm III, LLC (PC3) | NCR10334 | TRE2017017011 | PRC-005-2(i) | R3 | On February 10, 2017, PC3 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3. Specifically, PC3 discovered that it did not timely perform the required 18-month maintenance and testing activities for one Vented Lead-Acid (VLA) battery as set forth in PRC-005-2(i) R3, Table 1-4(a). On May 9, 2015, PC3 performed testing on a single VLA battery device. According to the maintenance intervals set forth in PRC-005-2(i), Table 1-4(a), PC3 should have performed the next round of 18-month maintenance activities by November 30, 2016. However, PC3 did not actually perform these required maintenance activities until January 20, 2017. The root cause of this issue was that PC3 did not have adequate internal controls to ensure that all required maintenance activities were completed. Specifically, PC3 personnel did not adequately track the single battery at issue and therefore failed to timely schedule the requisite maintenance activities with its contractor. This issue started on December 1, 2016, the day after the 18-calendar-month testing was due on its VLA battery, and ended on January 20, 2017, when PC3 completed the 18-month VLA battery testing activities at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the battery is monitored and PC3’s control center receives alarm notices if the battery has any issues. Second, when PC3 performed the required maintenance, the battery was operating within normal limits. Third, the issue only involved approximately 3.2% (1/31) of PC3’s Protection System devices. Finally, there were no misoperations during the duration period. No harm is known to have occurred. Texas RE considered PC3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PC3: 1) inspected the battery at issue; 2) completed an inventory on its Facility and confirmed completed maintenance for all other Protection System devices in its Protection System Maintenance and Testing Program (PSMP); and 3) created a responsibility matrix that requires multiple personnel to monitor and track maintenance activities, as well as confirm that all maintenance activities are scheduled and completed as required. Furthermore, PC3 will provide training on the PSMP requirements and the responsibility matrix.
2017-04-27 | Texas Reliability Entity (Texas RE) | Grandview Wind Farm, LLC (GV1) | NCR11491 | TRE2017017010 | PRC-005-2(i) | R3 | On February 10, 2017, GV1 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3. Specifically, GV1 discovered that it did not timely perform the required 18-month maintenance and testing activities for one Vented Lead-Acid (VLA) battery as set forth in PRC-005-2(i) R3, Table 1-4(a). On May 10, 2015, GV1 performed testing on a single VLA battery device. According to the maintenance intervals set forth in PRC-005-2(i), Table 1-4(a), GV1 should have performed the next round of 18-month maintenance activities by November 30, 2016. However, GV1 did not actually perform these required maintenance activities until January 25, 2017. The root cause of this issue was that GV1 did not have adequate internal controls to ensure that all required maintenance activities were completed. Specifically, GV1 personnel did not adequately track the single battery at issue and therefore failed to timely schedule the requisite maintenance activities with its contractor. This issue started on December 1, 2016, the day after the 18-calendar-month testing was due on its VLA battery, and ended on January 25, 2017, when GV1 completed the 18-month VLA battery testing activities at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the battery is monitored and GV1’s control center receives alarm notices if the battery has any issues. Second, when GV1 performed the required maintenance, the battery was operating within normal limits. Third, the issue only involved approximately 3.8% (1/26) of GV1’s Protection System devices. Finally, there were no misoperations during the duration period. No harm is known to have occurred. Texas RE considered GV1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GV1: 1) inspected the battery at issue; 2) completed an inventory on its Facility and confirmed completed maintenance for all other Protection System devices in its Protection System Maintenance and Testing Program (PSMP); and 3) created a responsibility matrix that requires multiple personnel to monitor and track maintenance activities, as well as confirm that all maintenance activities are scheduled and completed as required. Furthermore, GV1 will provide training on the PSMP requirements and the responsibility matrix.
2017-04-27 | Texas Reliability Entity (Texas RE) | Papalote Creek I, LLC (PAP1) | NCR10335 | TRE2017017012 | PRC-005-2(i) | R3 | On February 10, 2017, PAP1 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3. Specifically, PAP1 discovered that it did not timely perform the required 18-month maintenance and testing activities for two Vented Lead-Acid (VLA) batteries as set forth in PRC-005-2(i) R3, Table 1-4(a). On May 13, 2015, PAP1 performed testing on two VLA battery devices. According to the maintenance intervals set forth in PRC-005-2(i), Table 1-4(a), PAP1 should have performed the next round of 18-month maintenance activities by November 30, 2016. However, PAP1 did not actually perform these required maintenance activities until January 15, 2017. The root cause of this issue was that PAP1 did not have adequate internal controls to ensure that all required maintenance activities were completed. Specifically, PAP1 personnel did not adequately track the two VLA batteries at issue and therefore failed to timely schedule the requisite maintenance activities with its contractor. This issue started on December 1, 2016, the day after the 18-month testing was due on PAP1’s VLA batteries, and ended on January 15, 2017, when PAP1 completed the 18-month VLA battery testing activities at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the batteries at issue are monitored and PAP1’s control center receives alarm notices if its batteries have any issues. Second, when PAP1 performed the required maintenance, the two VLA batteries were operating within normal limits. Third, the issue only involved approximately 2.4% (2/83) of PAP1’s Protection System devices. Finally, there were no misoperations during the duration period. No harm is known to have occurred. Texas RE considered PAP1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PAP: 1) inspected the two batteries at issue; 2) completed an inventory on its Facility and confirmed completed maintenance for all other Protection System devices in its Protection System Maintenance and Testing Program (PSMP); and 3) created a responsibility matrix that requires multiple personnel to monitor and track maintenance activities, as well as confirm that all maintenance activities are scheduled and completed as required. Furthermore, PAP will provide training on the PSMP requirements and the responsibility matrix.
2017-04-27 | Texas Reliability Entity (Texas RE) | Papalote Creek II, LLC (PAP2) | NCR11033 | TRE2017017013 | PRC-005-2(i) | R3 | On February 10, 2017, PAP2 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3. Specifically, PAP2 stated that it did not timely perform the required 6-month and 18-month maintenance and testing activities for two Valve –Regulated Lead-Acid (VRLA) batteries as required by PRC-005-2(i) R3, Table 1-4(b). On May 14, 2015, PAP2 performed testing on the two VRLA battery devices at issue. According to the maintenance intervals set forth in PRC-005-2(i), Table 1-4(b), PAP2 should have performed the next round of six-month maintenance on the two VRLA batteries at issue by November 30, 2015. Further, PAP2 should have performed additional 18-month maintenance activities by November 30, 2016. However, PAP2 did not actually perform both the required 6-month and 18-month maintenance activities until January 16, 2017. The root cause of these instances of noncompliance was that PAP2 did not have adequate internal controls to ensure it included all Protection System devices within its Protection System Maintenance and Testing Program (PSMP). Specifically, PAP2 personnel omitted the two batteries at issue from the Facility’s Protection System device inventories and therefore did not recognize that maintenance and testing activities were required for these devices. This issue started on December 1, 2015, the day after the 6-month testing was due on its VRLA batteries, and ended on January 16, 2017, when PAP2 completed the required testing on two VRLA batteries at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the batteries are monitored and PAP2’s control center receives alarm notices if the devices have any issues. Second, when PAP2 performed the required maintenance, the batteries were operating within normal limits. Finally, the issue only involved approximately 2.8% (2/71) of PAP2’s Protection System devices. Texas RE considered PAP2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PAP2: 1) inspected the batteries at issue; 2) completed an inventory on its Facility and confirmed completed maintenance for all other Protection System devices in its PSMP; and 3) created a responsibility matrix that requires multiple personnel to monitor and track maintenance activities, as well as confirm that all maintenance activities are scheduled and completed as required. Furthermore, PAP2 will provide training on the PSMP requirements and the responsibility matrix.
2017-04-27 | Texas Reliability Entity (Texas RE) | Papalote Creek II, LLC (PAP2) | NCR11033 | TRE2017017378 | PRC-005-2 | R1 | On February 10, 2017, PAP2 submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3 relating to its failure to timely perform certain maintenance and testing activities for various batteries. Subsequently, Texas RE determined that the issue described in PAP2's PRC-005-2(i) R3 Self-Report was also a noncompliance of PRC-005-2 R1. Specifically, PAP2 failed to establish a Protection System Maintenance and Testing Program (PSMP) for all of its Protection System devices. On March 31, 2015, PAP2 adopted a new Protection System Maintenance and Testing Program (PSMP) reflecting the newly effective PRC-005-2 testing requirements. In doing so, however, PAP2 failed to include two Valve Regulated Lead-Acid (VRLA) battery devices in its new PSMP. PAP2 discovered the issue during an internal review of its Protection System devices and testing records. Following the review on March 29, 2017, PAP2 revised its PSMP to include the two VRLA batteries in its PSMP. The root cause of this issue was that PAP2 did not have adequate internal controls to ensure all applicable Protection System devices were included in its PSMP. Specifically, PAP2 personnel mistakenly believed that all VRLA batteries had been removed from PAP2 and other affiliated wind farms and did not have a sufficient process to review Protection System inventories to ensure that all existing Protection Systems were reflected in its revised PSMP documentation. This issue started on April 1, 2015, when PRC-005-2 R1 became enforceable, and ended on March 29, 2017, when PAP2 updated its PSMP to reflect the two VRLA batteries and their associated monitoring attributes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the two VRLA batteries are monitored and PAP2’s control center receives alarm notices if the devices have any issues. Second, when PAP2 performed the required maintenance, the batteries were operating within normal limits. Finally, the issue only involved approximately 2.8% (2/71) of PAP2’s Protection System devices. Texas RE considered PAP2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PAP2: 1) revised the PSMP to include VRLA battery activities and the documentation of monitoring attributes; 2) inspected the batteries at issue; 3) completed an inventory of its Facility and confirmed completed maintenance for all other devices in the PSMP; and 4) created a responsibility matrix that requires multiple personnel to monitor and track maintenance activities, review inventories, as well as confirm that all maintenance activities are scheduled and completed as required. Furthermore, PAP2 will provide training on the PSMP requirements and the responsibility matrix.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2016016624 | COM-002-4 | R2 | On December 2, 2016, AZPS submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with COM-002-4 R2. Specifically, AZPS reported that during an internal review, it discovered that one of its operators did not complete initial training for one of AZPS’s documented communications protocols prior to issuing an Operating Instruction. This issue began July 1, 2016, when COM-002-4 became mandatory and enforceable for AZPS, and ended August 26, 2016 when the operator completed the training. The root cause of this issue was an insufficient process to reconcile expected and actual training attendance to ensure all requisite personnel met the requirement timely. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, AZPS failed to ensure all applicable operating personnel completed initial training for AZPS’s communications protocols before such personnel issued Operating Instructions. Such failure could limit the operators’ awareness of communication protocols, which could increase the possibility of miscommunication. However, this issue concerned a single, experienced operator who completed alternative training for AZPS’s communication protocols prior to implementation of COM-002-4, and performed Operating Instructions correctly during the period in question. The operator did not issue any Operating Instructions during an emergency, and no harm is known to have occurred. AZPS does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, AZPS: 1) conducted initial training for the operator in scope, and verified that all other applicable personnel completed the training; and 2) revised its training attendance tracking, reconciliation, and make-up processes to ensure all requisite staff completes training timely. WECC verified completion of AZPS’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC2016016510 | PRC-019-2 | R1 | On November 10, 2016, AVGO submitted a Self-Report stating that as a Generator Owner, it had a potential issue on noncompliance with PRC-019-2 R1. Specifically, AVGO reported that it failed to coordinate voltage regulating system controls with equipment capabilities and Protection System device settings for at least 40 percent of its applicable Facilities by the effective date of PRC-019-2. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of AVGO’s applicable Facilities, and ended March 7, 2017, when AVGO adjusted settings to meet requisite coordination. The root cause of this issue was AVGO’s misunderstanding regarding the effective date of the Standard; AVGO completed an analysis of existing coordination of its applicable Facilities on June 30, 2016, and believed such verification was sufficient to meet the implementation deadline for PRC-019-2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, AVGO failed to coordinate at least 40 percent of its applicable Facilities in accordance with R1 by the effective date of the Standard. Such failure could result in over-voltage damage to AVGO’s applicable Facilities, or an unnecessary generator trip. However, although AVGO failed to adjust settings to ensure timely coordination, it completed an analysis of PRC-019-2 R1.1 coordination items prior to the implementation deadline. The current settings on AVGO’s applicable units have never caused the units to trip unnecessarily, and no harm is known to have occurred. AVGO does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, AVGO: 1) adjusted settings to meet requisite coordination; and 2) established periodic notifications and reminders to ensure tracking and completion of annual and five-year reviews for PRC-019-2 compliance tasks. WECC verified completion of AVGO’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | City of Tacoma, Department of Public Utilities, Light Division (TPWR) | NCR05097 | WECC2016016681 | MOD-001-1a | R4; R4.4 | On December 14, 2016, TPWR submitted a Self-Report stating that as a Transmission Service Provider, it had a possible issue of noncompliance with MOD-001-1a R4.4. Specifically, TPWR reported that it failed to notify adjacent Planning Coordinators before implementing revisions to its Available Transfer Capability Implementation Document (ATCID). This issue began February 1, 2016, when TPWR implemented the revised ATCID, and ended October 4, 2016, when it distributed the revised ATCID to adjacent Planning Coordinators. The root cause of this issue was human error and less than adequate written instructions; the individual responsible for distributing the revised ATCID referred to a distribution list rather than TPWR’s documented procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, TPWR failed to notify adjacent Planning Coordinators prior to implementing revisions to its ATCID. Such failure could limit the awareness of neighboring entities regarding changes that could affect their transmission systems. However, this issue concerned a minor change which did not affect operating limits. TPWR distributed its revised ATCID within days of discovering the oversight, and no harm is known to have occurred. TPWR does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, TPWR: 1) distributed the revised ATCID to the adjacent Planning Coordinators; and 2) updated its distribution list to include Planning Coordinators. WECC verified completion of TPWR’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | La Paloma Generating Company LLC (LPGC) | NCR05210 | WECC2017017090 | MOD-025-2 | R1; R1.2 | On February 24, 2017, LPGC submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1.2. Specifically, LPGC reported that it failed to submit the information for Real Power capability identified in MOD-025-2 Attachment 2 to its Transmission Planner within 90 calendar days of recording such data. This issue began July 20, 2016, 90 days after LPGC recorded the data, and ended August 29, 2016, when LPGC submitted the data to its Transmission Planner. The root cause of this issue was less than adequate follow up to ensure that MOD-025-2 testing reports were submitted timely. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, LPGC failed to submit Attachment 2 information to its Transmission Planner within the 90-day timeframe required by R1.2. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, LPGC verified Real capability of its applicable Facilities in accordance with MOD-025-2 prior to the implementation deadline, and submitted its Attachment 2 information as soon as the information was made available. No harm is known to have occurred. LPGC does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, LPGC: 1) distributed completed Attachment 2 forms and test reports to its Transmission Planner; 2) completed and distributed Attachment 2 information for its remaining Facilities to its Transmission Planner, eliminating risk of recurrent failure to implement MOD-025-2 in accordance with upcoming percentage-based implementation deadlines; and 3) added automated reminders for MOD-025-2 compliance tasks to its work management system to ensure submission windows are met in the future. WECC verified completion of LPGC’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | La Paloma Generating Company LLC (LPGC) | NCR05210 | WECC2017017091 | MOD-025-2 | R2; R2.2 | On February 24, 2017, LPGC submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2.2. Specifically, LPGC reported that it failed to submit the information for Reactive Power capability identified in MOD-025-2 Attachment 2 to its Transmission Planner within 90 calendar days of recording such data. This issue began July 20, 2016, 90 days after LPGC recorded the data, and ended August 29, 2016, when LPGC submitted the data to its Transmission Planner. The root cause of this issue was less than adequate follow up to ensure that MOD-025-2 testing reports were submitted timely. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, LPGC failed to submit Attachment 2 information to its Transmission Planner within the 90-day timeframe required by R2.2. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, LPGC verified Reactive capability of its applicable Facilities in accordance with MOD-025-2 prior to the implementation deadline, and submitted its Attachment 2 information as soon as the information was made available. No harm is known to have occurred. LPGC does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, LPGC: 1) distributed completed Attachment 2 forms and test reports to its Transmission Planner; 2) completed and distributed Attachment 2 information for its remaining Facilities to its Transmission Planner, eliminating risk of recurrent failure to implement MOD-025-2 in accordance with upcoming percentage-based implementation deadlines; and 3) added automated reminders for MOD-025-2 compliance tasks to its work management system to ensure submission windows are met in the future. WECC verified completion of LPGC’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Mt. Poso Cogeneration Co. (MTPO) | NCR05254 | WECC2017017216 | EOP-004-2 | R1 | On March 9, 2017, MTPO submitted a Self-Report stating that as a Generator Owner and Generator Operator, it had a possible issue of noncompliance with EOP-004-2 R1. Specifically, MTPO reported that during an internal review on November 28, 2016, it discovered its event reporting Operating Plan did not include WECC’s contact information. This issue began January 1, 2014, when EOP-004-2 became mandatory and enforceable for MTPO, and ended December 7, 2016, when MTPO discovered and corrected the omission. The root cause of this issue was human error and less than adequate documentation; MTPO did not realize that the WECC contact information was required in the initial draft of its Operating Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MTPO failed to include WECC’s contact information with the event reporting protocol(s) in its event reporting Operating Plan. Such failure could result in MTPO overlooking the requirement to notify its Regional Entity following a reportable event, which could limit situational awareness during the event. However, this issue concerned documented protocols for a single, 62 MW biomass facility. Had this issue resulted in MTPO’s failure to notify WECC directly during a reportable event, it is very likely that MTPO’s Transmission Operator would have compensated for the oversight. MTPO submitted timely responses to quarterly data requests for this Standard, did not experience any reportable events during the period in question, and no harm is known to have occurred. MTPO does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, MTPO: 1) revised its Operating Plan to include WECC’s current contact information, and require annual verification of WECC’s contact information; and 2) created automated reminders to ensure this requirement will not be overlooked in future annual reviews. WECC verified completion of MTPO’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | NAES Corporation - Pio Pico Energy Center (NAES-PP) | NCR11651 | WECC2017016844 | VAR-002-4 | R3 | On January 23, 2017, NAES-PP submitted a Self-Report stating that as a Generator Operator, it had a possible issue of noncompliance with VAR-002-4 R3. Specifically, NAES-PP reported that it inadvertently failed to enable the Power System Stabilizer (PSS) on one of its units during start-up, and did not notify its Transmission Operator (TOP) of the PSS status within 30 minutes. This issue began January 3, 2017, 30 minutes after NAES-PP started the unit without enabling the PSS, and ended the same day when NAES-PP noticed the oversight, enabled the PSS, and notified the TOP of the PSS status, for roughly one hour of noncompliance. The root cause of this issue was less than adequate training; at the time of this issue, the facility had been in commercial operation for less than two months, and the operator did not verify PSS status during start-up. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NAES-PP failed to notify its TOP of a status change on its PSS within 30 minutes. Such failure limited NAES-PP’s and its TOP’s situational awareness of the unit’s PSS capability. However, this issue was limited to a single 100 MW unit, over the course of roughly one hour. Although the PSS was disabled, the unit’s Automatic Voltage Regulator (AVR) was in service during the period in question. This issue did not cause the unit to trip, and no harm is known to have occurred. NAES-PP does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, NAES-PP: 1) enabled the unit’s PSS and notified the TOP of the PSS status; 2) implemented changes to its control system, which will alarm whenever the PSS is disabled while a generator is in service; and 3) revised its start-up checklist to include PSS status verification and retrained its operating staff on its start-up procedures. WECC verified completion of NAES-PP’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC2017016754 | MOD-025-2 | R1 | On January 6, 2017, NCPA submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, NCPA reported that it failed to submit the information for Real Power capability identified in MOD-025-2 Attachment 2 to its Transmission Planner within 90 calendar days of recording such data. This issue began July 1, 2016, when MOD-025-2 became mandatory and enforceable for 40 percent of NCPA’s applicable Facilities, and ended October 31, 2016, when NCPA discovered the oversight and distributed Attachment 2 information to its Transmission Planner. The root cause of this issue was less than adequate follow up to ensure MOD-25-2 verification tasks were completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NCPA failed to distribute Attachment 2 information to its Transmission Planner by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was unlikely to significantly affect current planning models as NCPA tested all of its generators in accordance with the WECC Model Validation Policy, and distributed those test reports to its Transmission Planner prior to development and implementation of MOD-025-2. Additionally, NCPA verified the Real Power capability of 40 percent of its applicable Facilities in accordance with MOD-025-2 well in advance of the implementation deadline. No harm is known to have occurred. NCPA does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, NCPA: 1) distributed completed Attachment 2 forms and test reports to its Transmission Planner; and 2) created automated reminders for future MOD-025-2 compliance-related tasks which emphasize the Attachment 2 submission window. WECC verified completion of NCPA’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC2017016755 | MOD-025-2 | R3 | On January 6, 2017, NCPA submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, NCPA reported that it failed to submit the information for Reactive Power capability identified in MOD-025-2 Attachment 2 to its Transmission Planner within 90 calendar days of recording such data. This issue began July 1, 2016, when MOD-025-2 became mandatory and enforceable for 40 percent of NCPA’s applicable Facilities, and ended October 31, 2016, when NCPA discovered the oversight and distributed Attachment 2 information to its Transmission Planner. The root cause of this issue was less than adequate follow up to ensure MOD-25-2 verification tasks were completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, NCPA failed to distribute Attachment 2 information to its Transmission Planner by the effective date of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was unlikely to significantly affect current planning models as NCPA tested all of its generators in accordance with the WECC Model Validation Policy, and distributed those test reports to its Transmission Planner prior to development and implementation of MOD-025-2. Additionally, NCPA verified the Reactive Power capability of 40 percent of its applicable Facilities in accordance with MOD-025-2 well in advance of the implementation deadline. No harm is known to have occurred. NCPA does not have previou noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, NCPA: 1) distributed completed Attachment 2 forms and test reports to its Transmission Planner; and 2) created automated reminders for future MOD-025-2 compliance-related tasks which emphasize the Attachment 2 submission window. WECC verified completion of NCPA’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Pacific-Ultrapower Chinese Station (PUPCS) | NCR11279 | WECC2016016165 | PRC-019-2 | R1 | On September 14, 2016, PUPCS submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, PUPCS reported that, by the effective date of the Standard, it failed to verify coordination of voltage regulating system controls with equipment capabilities and Protection System device settings for its applicable Facility. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for PUPCS’s applicable Facility, and ended September 6, 2016, when PUPCS verified requisite coordination for the Facility. The root cause of this issue was a misunderstanding regarding the effective dates of PRC-019-2 for single unit Facilities. The Standard does not require implementation for 100% of applicable Facilities until July 1, 2019. PUPCS believed that because it owns a single applicable generator, it was not required to meet the 40% implementation deadline, as it could not verify coordination of, or adjust settings for only 40% of its generator. PUPCS pursued clarification regarding this issue prior to the July 1, 2016 implementation deadline, but did not receive confirmation until after the deadline had passed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PUPCS failed to verify coordination items prescribed by PRC-019-2 R1.1.1 and R1.1.2. Such failure could result in over-current damage to PUPCS’s generator. However, this issue concerned a single, 25 MW generator, and no harm was known to have occurred. PUPCS does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, PUPCS: 1) completed the verification items prescribed by R1.1.1 and R1.1.2; and 2) created automated reminders to ensure timely completion of future compliance-related tasks associated with this Standard. WECC verified completion of PUPCS’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Platte River Power Authority (PRPA) | NCR05321 | WECC2017016896 | MOD-026-1 | R6 | On January 31, 2017, PRPA submitted a Self-Report stating that as a Transmission Planner (TP), it had a possible issue of noncompliance with MOD-026-1 R6. Specifically, PRPA reported that its TP department did not provide a written response to the Generator Owner (GO) indicating whether a generator model was usable within the timeframe required by MOD-026-1 R6. This issue began November 20, 2016, the day after the response was due, and ended December 26, 2016, when PRPA provided the response. The root cause of this issue was human error; the engineer responsible for reviewing the model information delayed the review to coincide with PRPA’s annual transmission planning assessment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PRPA failed to provide a response to its GO regarding verified model information for plant volt/var control function within 90 days. Such failure could result in use of inaccurate information in planning models used to assess Bulk Electric System reliability. However, as concerns this issue, PRPA functioned as both the TP and GO; there was continuous communication between departments serving both functions throughout the duration of this issue. The model information in scope was not significant and no harm is known to have occurred. PRPA does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PRPA: 1) provided a written response regarding the model information to the GO; 2) revised its procedures to include management and compliance staff in distribution of all TP-GO communication; and 3) established automatic tracking and reminders to ensure timely completion of compliance-related tasks. WECC verified completion of PRPA’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Platte River Power Authority (PRPA) | NCR05321 | WECC2017016897 | MOD-027-1 | R5 | On January 31, 2017, PRPA submitted a Self-Report stating that as a Transmission Planner (TP), it had a possible issue of noncompliance with MOD-027-1 R5. Specifically, PRPA reported that its TP department did not provide a written response to the Generator Owner (GO) indicating whether a generator model was usable within the timeframe required by MOD-027-1 R5. This issue began November 20, 2016, the day after the response was due, and ended December 26, 2016, when PRPA provided the response. The root cause of this issue was human error; the engineer responsible for reviewing the model information delayed the review to coincide with PRPA’s annual transmission planning assessment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PRPA failed to provide a response to its GO regarding verified model information for turbine/governor and load control within 90 days. Such failure could result in use of inaccurate information in planning models used to assess Bulk Electric System reliability. However, as concerns this issue, PRPA functioned as both the TP and GO; there was continuous communication between departments serving both functions throughout the duration of this issue. The model information in scope was not significant and no harm is known to have occurred. PRPA does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PRPA: 1) provided a written response regarding the model information to the GO; 2) revised its procedures to include management and compliance staff in distribution of all TP-GO communication; and 3) established automatic tracking and reminders to ensure timely completion of compliance-related tasks. WECC verified completion of PRPA’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | ProEnergy Services (PRSV) | NCR11550 | WECC2016015913 | MOD-025-2 | R1 | On July 11, 2016, PRSV submitted Self-Reports stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirements 1 and 2. Specifically, PRSV failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1, by the effective date of the Standard. The root cause of these issues was a misunderstanding of the implementation plan for the Standard and Requirements. PRSV interpreted the "two years after regulatory approval" as being two years from the Standard effective date. WECC determined these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of PRSV’s generating units and ended on October 12, 2016, when PRSV completed testing of at least 40 percent of its generating units in accordance with Attachment 1. PRSV was in noncompliance for a total of 103 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PRSV failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, these issues would not likely have significantly affected current planning models as PRSV tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2, and the combined capacity for all of PRSV’s generating resources is approximately 69 MVA. PRSV retained a consultant to conduct a mock audit, which is how the issues were discovered. Additionally, upon discovery of the issue, PRSV immediately hired an engineering firm to conduct testing. No harm was known to have occurred. PRSV does not have previous noncompliance with this Standard and Requirement. | To remediate and mitigate these issues, PRSV: 1) Completed Real and Reactive Power testing of at least 40 percent of its generating units, per Attachment 1; 2) Developed a plant procedure to ensure future testing of Real and Reactive Power are completed. The procedure also ensures that PRSV completes Attachment 2 of the Standard and submits the necessary data within the specified timeframe; and 3) Will continue conducting outside mock audits and internal self-assessments to prevent future reoccurrence of these issues.
2017-04-27 | Western Electricity Coordinating Council (WECC) | ProEnergy Services (PRSV) | NCR11550 | WECC2016015914 | MOD-025-2 | R2 | On July 11, 2016, PRSV submitted Self-Reports stating that, as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 Requirements 1 and 2. Specifically, PRSV failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1, by the effective date of the Standard. The root cause of these issues was a misunderstanding of the implementation plan for the Standard and Requirements. PRSV interpreted the "two years after regulatory approval" as being two years from the Standard effective date. WECC determined these issues began on July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of PRSV’s generating units and ended on October 12, 2016, when PRSV completed testing of at least 40 percent of its generating units in accordance with Attachment 1. PRSV was in noncompliance for a total of 103 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PRSV failed to verify the Real and Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 of the Standard. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, these issues would not likely have significantly affected current planning models as PRSV tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2, and the combined capacity for all of PRSV’s generating resources is approximately 69 MVA. PRSV retained a consultant to conduct a mock audit, which is how the issues were discovered. Additionally, upon discovery of the issue, PRSV immediately hired an engineering firm to conduct testing. No harm was known to have occurred. PRSV does not have previous noncompliance with this Standard and Requirement. | To remediate and mitigate these issues, PRSV: 1) Completed Real and Reactive Power testing of at least 40 percent of its generating units, per Attachment 1; 2) Developed a plant procedure to ensure future testing of Real and Reactive Power are completed. The procedure also ensures that PRSV completes Attachment 2 of the Standard and submits the necessary data within the specified timeframe; and 3) Will continue conducting outside mock audits and internal self-assessments to prevent future reoccurrence of these issues.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2017016739 | COM-002-4 | R3 | On January 3, 2017, PSE submitted a Self-Report stating that as a Distribution Provider and Generator Operator, it had a possible issue of noncompliance with COM-002-4 R3. Specifically, PSE reported that during an internal review, it discovered that operating personnel at two of its plants did not complete initial training for oral two-party, person-to-person Operating Instructions. This issue began July 1, 2016, when COM-002-4 became mandatory and enforceable for PSE, and ended November 1, 2016, when PSE trained the operators in scope. The root cause of this issue was lack of follow-up regarding the formal training deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PSE failed to conduct initial training regarding oral two-party, person-to-person Operating Instruction for each of its operating personnel. Such failure could limit operators’ awareness of predefined communications protocols, which could increase the possibility of miscommunication. However, this issue was limited to six operators, each of whom completed instructions correctly during the period in question. None of the instances identified by PSE concerned Operating Instructions issued during an emergency, and no harm is known to have occurred. PSE does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) conducted training for all operating personnel; and 2) established automated reminders, tracking tools, and training modules related to this Standard in its work management system. WECC verified completion of PSE’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | RE Astoria 2 LLC (REAII) | NCR11678 | WECC2017016781 | PRC-025-1 | R1 | On January 11, 2017, REAII submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-025-1 R1. Specifically, REAII reported that it failed to set a load-responsive protective relay greater than 130% of the maximum calculated current on the feeder protection relay, as prescribed in PRC-025-1 Attachment 1. This issue began September 29, 2016, when REAII registered as a Generation Owner, and ended January 17, 2017, when REAII adjusted the setting. The root cause of this issue was human error; the technician established an incorrect setting due to a rounding error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, REAII failed to set a load-responsive protective relay so that it would not trip an applicable generating unit unnecessarily. Such failure could result in premature trip of the unit during a system disturbance for conditions which do not pose risk of damage to the associated equipment. However, this issue concerned a single relay on a 75 MW unit, and no harm is known to have occurred. REAII does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, REAII: 1) adjusted the setting; 2) will require contractors to complete compliance-related checklists prior to commissioning Facilities; and 3) will require operations staff to complete monthly compliance reports; and 4) will continue to track compliance-related tasks electronically to ensure compliance documentation is reviewed and approved appropriately. WECC verified completion of REAII’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | RE Mustang Holdings LLC (REMH) | NCR11637 | WECC2017016782 | PRC-024-2 | R1 | On January 11, 2017, REMH submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. Specifically, REMH reported that the default inverter settings on its frequency protective relaying did not meet the criteria in PRC-024-2 Attachment 1. This issue began July 1, 2016, when PRC-024-2 became mandatory and enforceable for REMH, and ended January 12, 2017, when REMH adjusted the setting. The root cause of this issue was failure to identify and adjust settings by the implementation deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, REMH failed to set its frequency protective relaying so that it would not trip its generating units unnecessarily. Such failure could result in premature trip of one or more units offline due to frequency excursions within the “no trip zone”. However, the combined capacity of REMH’s units is 100 MW. The setting in scope did not cause any of the units to trip during the period in question, and no harm is known to have occurred. REMH's does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, REMH: 1) adjusted the setting; 2) will require contractors to complete compliance-related checklists prior to commissioning Facilities; 3) will require operations staff to complete monthly compliance reports; and 4) will continue to track compliance-related tasks electronically to ensure compliance documentation is reviewed and approved appropriately. WECC verified completion of REMH’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Sierra Pacific Power Company (SPPC) | NCR05390 | WECC2016016408 | FAC-003-3 | R6 | On October 24, 2016, SPPC submitted a Self-Report stating that as a Transmission Owner and Generator Owner, it had a possible issue of noncompliance with FAC-003-3 R6. Specifically, SPPC reported that it failed to perform a Vegetation Inspection of a single, 345kV line during the 2015 calendar year. This issue began January 1, 2016, when inspection for the line became past due, and ended September 12, 2016, when SPPC performed an inspection on the line. The root cause of this issue was a misunderstanding regarding the Requirement. SPPC’s Transmission Vegetation Management Program (TVMP) allowed for more flexible inspection scheduling for areas which posed lower risk of vegetation encroachment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, SPPC failed to perform a Vegetation Inspection of 100% of its applicable transmission lines within the 2015 calendar year. Such failure could have limited SPPC’s awareness of risk to the line due to vegetative conditions. However, this issue was limited to a single, 36-mile line, and comprised roughly three percent of SPPC’s applicable transmission. The line in question is not part of a WECC Major Transfer Path or Remedial Action Scheme. SPPC’s did not identify any vegetation hazards on line during its 2016 inspection, and no harm is known to have occurred. SPPC does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, SPPC: 1) inspected the line; 2) revised its TVMP to ensure inspection frequency meets the Requirement; and 3) discussed the facts and circumstances of this issue, the results of an internal root cause analysis, with relevant staff. WECC verified completion of SPPC’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Tucson Electric Power (TEPC) | NCR05434 | WECC2017016891 | MOD-026-1 | R4 | On January 27, 2017, TEPC submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-026-1 R4. Specifically, TEPC reported that on May 20, 2016, TEPC adjusted a setting on a Power System Stabilizer (PSS) device, and failed to notify its Transmission Planner of this adjustment within the 180-day timeframe required by MOD-026-1 R4. This issue began November 17, 2016, 181 days after TEPC adjusted the setting, and ended December 8, 2016, when TEPC discovered the oversight and formally notified the Transmission Planner. The root cause of this issue was human error; TEPC assumed that informal communication during the setting adjustment and associated testing served as formal notification. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, TEPC failed to provide revised model data for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system. Such failure could result in inaccurate representations of the unit’s excitation control system in models used to assess BES reliability. However, this issue was limited to a single unit and was identified, remediated, and reported within a relatively brief window. No harm is known to have occurred. TEPC does not have previous noncompliance with this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, TEPC: 1) formally notified the Transmission Planner of the setting adjustment; and 2) distributed a training advisory regarding this Requirement to relevant staff. WECC verified completion of TEPC’s mitigating activities.
2017-04-27 | Western Electricity Coordinating Council (WECC) | Woodland Biomass Power Ltd. (WDBM) | NCR10047 | WECC2017017217 | EOP-004-2 | R1 | On March 10, 2017, WDBM submitted a Self-Report stating that as a Generator Owner and Generator Operator, it had a possible issue of noncompliance with EOP-004-2 R1. Specifically, WDBM reported that during an internal review on November 14, 2016, it discovered its event reporting Operating Plan did not include WECC’s contact information. This issue began January 1, 2014, when EOP-004-2 became mandatory and enforceable for WDBM, and ended November 15, 2016, when WDBM discovered and corrected the omission. The root cause of this issue was human error and less than adequate documentation; WDBM did not realize that WECC’s contact information was required in the initial draft of its Operating Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WDBM failed to include WECC’s contact information with the event reporting protocol(s) in its event reporting Operating Plan. Such failure could result in WDBM overlooking the requirement to notify its Regional Entity following a reportable event, which could limit situational awareness during the event. However, this issue concerned documented protocols for a single, 24 MW biomass facility. Had this issue resulted in WDBM’s failure to notify WECC directly during a reportable event, it is very likely that WDBM’s Transmission Operator would have compensated for the oversight. WDBM submitted timely responses to quarterly data requests for this Standard, did not experience any reportable events during the period in question, and no harm is known to have occurred. WDBM does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, WDBM: 1) revised its Operating Plan to include WECC’s current contact information, and require annual verification of WECC’s contact information; and 2) created automated reminders to ensure this requirement will not be overlooked in future annual reviews. WECC verified completion of WDBM’s mitigating activities.
2017-03-30 | Florida Reliability Coordinating Council (FRCC) | Gainesville Regional Utilities (GRU) | NCR00032 | FRCC2016016420 | BAL-001-2 | R2 | On October 28, 2016, Gainesville Regional Utilities (GRU) submitted a Self-Report stating that, as a BA, it was in violation of BAL-001-2 (R2). On September 2, 2016, GRU's clock-minute average of Reporting ACE exceeded its clock-minute Balancing Authority ACE Limit (BAAL) for 37 consecutive clock-minutes between 03:26 and 04:03. This event occurred on the night of Hurricane Hermine. GRU’s internal generation consisted of two generating units on-line when a tie-line (Deerhaven to Hampton 138kV line) with FPL was lost. Both generating units were at minimum load. When the tie-line opened, GRU’s load was also dropping due to the hurricane, causing ACE to rise because of over-generation. The operator's only option to reduce ACE would have been to bring a generator offline. Although this action would have prevented the exceedance, the operator made an operational choice to support reliability by keeping all generation online for GRU's system to remain stable during the hurricane. The Reliability Coordinator issued no directives or Operating Instructions during the event. GRU did not benfit monetarily by over-generating. The root cause for this noncompliance was an operational decision to support reliability during a hurricane by keeping all generation assets online. This action allowed GRU to be prepared for the potential loss of additional facilities during the hurricane. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In the event GRU lost its other 230 kV to 138 kV interconnection at the Duke Energy Florida Archer Substation, it would only have been connected to the BPS through a single 69 kV tie-line at the Idylwild substation. The Archer substation was closer to the projected path of the hurricane than the Deerhaven to Hampton 138 kV tie-line which had already been lost. The potential risk of losing the interconnection at the Archer substation would cause a strain on the remaining 69 kV tie-line which would increase the probability of becoming islanded from the BPS for the loss of the single remaining 69 kV interconnection. By having only a single unit generating, GRU would likely not have been able to withstand the next single contingency resulting in a localize blackout in the GRU load pocket. FRCC determined that the issue posed a minimal risk to the BPS due to the fact that GRU's peak load represents approximately 0.89% of the total load in the FRCC region. A seven (7) minute exceedance of the BAAL for a utility of GRU's size (less than 500 MW peak system load) does not have an appreciable effect on the BPS. No harm is known to have occurred. FRCC considered GRU’s BAL-001-2 (R2) compliance history in determining the disposition track. GRU’s had no relevant prior noncompliance. | To mitigate this issue, GRU: 1) Returned to its BAAL following the hurricane.
2017-03-30 | Northeast Power Coordinating Council (NPCC) | Capitol District Energy Center Cogeneration Associates, JV (CDECCA) | NCR07026 | NPCC2016016197 | PRC-024-2 | R2. | On September 7, 2016, CDECCA submitted a Self-Report stating that as a Generator Owner, it had an issue of PRC-024-2 R2. CDECCA did not verify the proper coordination of its voltage regulating system controls for the first of two units with the applicable equipment capabilities and settings of the applicable Protection System devices and functions due to its interpretation of the phased–in implementation plan. The expectation by the Region is that a two-unit Facility such as CDECCA would be compliant for one of its units by the first date of July 1, 2016. CDECCA conducted a study of all applicable PRC-024-2 relays which was completed on June 30, 2016. The study identified three relays required setting adjustments for compliance with PRC-024-2. On August 29, 2016 CDECCA contacted its Transmission Operator and Transmission Owner to coordinate these changes in the Protection System. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The CDECCA power plant is a 62.1 MW natural gas-fired, dual fuel capable, combined-cycle cogeneration plant that provides peaking energy to the New England power market. The CDECCA facility has operated at less than 20% of its capacity in the past five years. Additionally, the facility has operated less than 3 months every year. It has never experienced a trip due to incorrect under voltage or over voltage (the settings that required change). No harm is known to have occurred. NPCC considered CDECCA's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, CDECCA: 1) changed the required relay settings to conform to PRC-024-2; and 2) verified actual in-service settings each time the protective device is maintained according to the CDECCA Protection System Maintenance Program. NPCC has verified the completion of all mitigation activity.
2017-03-30 | Northeast Power Coordinating Council (NPCC) | Consolidated Edison Co of NY, Inc. (Con Ed) | NCR07046 | NPCC2017016985 | PRC-005-2 | R1. | On February 9, 2017, Con Ed, submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-2 R1. Con Ed's procedure, COP 6-2-1, addressed valve-regulated lead-acid (VRLA) battery testing at Con Ed's East River Generating Station. COP 6-2-1 was part of Con Ed's Protection System Maintenance Plan (PSMP) for PRC-005-2 compliance when the standard became enforceable. COP 6-2-1 required impedance testing for VRLA batteries on an annual basis, which was not in compliance with Table 1-4(b) of PRC-005-2. Table 1-4(b) requires impedance testing of VRLA batteries every six months. The COP was revised on September 8, 2016 to require quarterly impedance testing of VRLA batteries, which exceeds the requirement of Table 1-4(b). COP 6-2-1 was renamed StOP 6-2-1. The issue started on April 1, 2015, when PRC-005-2 became enforceable and ended on September 8, 2016, when Con Ed updated its procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Battery performance at East River Unit 1 was fully satisfactory throughout the period. All applicable batteries were replaced between December 2015 and April 2016. No harm is known to have occurred. NPCC considered Con Ed's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, Con Ed: 1) revised the battery test procedure, COP 6-2-1, to require VRLA battery impedance test be conducted quarterly. The COP was renamed StOP 6-2-1 and now requires that all test data be digitized and electronically archived in the work management system; and 2) established future work orders controls in the Con Ed work management system. These controls are in place to schedule the impedance tests quarterly. NPCC has verified the completion of all mitigation activity.
2017-03-30 | Northeast Power Coordinating Council (NPCC) | Consolidated Edison Co of NY, Inc. (Con Ed) | NCR07046 | NPCC2016016370 | PRC-005-2(i) | R3. | During a Compliance Audit conducted from July 1, 2016 to September 16, 2016, NPCC determined that Con Ed as a Generator Owner, had an issue of PRC-005-2(i) R3. Con Ed self-identified an issue associated with the battery testing at the East River Generating Station. There are three sets of batteries that are subject to compliance. Each of these batteries are the Valve Regulated Lead Acid (VRLA) design. PRC-005-2(i) requires battery impedance testing to be performed on a six month cycle for VRLA batteries. The required impedance testing of all three batteries should have been performed no later than October 1, 2015. For Battery 1, certain tests were performed on September 30, 2015 but the required impedance testing could not be conducted based on an inoperable impedance measuring instrument. This battery bank was replaced on March 24, 2016 and impedance tests were conducted on April 13, 2016 and July 27, 2016. Battery Banks 1-1 and 2-1 had tests performed on October 28, 2015 but the 1-1 battery bank did not have a record of the required impedance test. The 2-1 battery bank has a record of the required impedance test. Both Battery Banks 1-1 and 2-1 attempted tests that were conducted 27 days behind the maximum test interval. Con Ed's procedure, COP 6-2-1, had not been revised when version 2 of PRC-005 went into effect. COP 6-2-1 (now renamed StOP 6-2-1) required impedance testing for VRLA batteries on an annual basis. The COP has since been revised to require the VRLA battery impedance test to be conducted quarterly. StOP 6-2-1 now requires that all test data be digitized and electronically archived in the work management system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The batteries involved did not exhibit any loss of capability during the period of the noncompliance. This was confirmed by other testing that demonstrated the readiness of all three battery banks to provide an adequate DC supply at the East River Generating Station. East River Generating Station has a 317 MW output. No harm is known to have occurred. NPCC considered Con Ed’s PRC-005 R2 compliance history in determining the disposition track. Con Ed’s relevant prior noncompliance with PRC-005 R2 include(s): NERC Violation ID NPCC2012010875. NPCC determined that Con Ed's compliance history should not serve as a basis for applying a penalty. The underlying facts and circumstances of the prior violation do not relate to the instant issue. Con Ed was in violation for its prior PRC-005 R2 issue due to several missed monthly intervals regarding their telecommunications system. The instant issue relates to missed battery testing due to a non updated procedure. | To mitigate this issue, Con Ed: 1) revised the battery test procedure, COP 6-2-1, to require VRLA battery impedance test be conducted quarterly. The COP was renamed StOP 6-2-1 and now requires that all test data be digitized and electronically archived in the work management system; and 2) established future work orders controls in the Con Ed work management system. These controls are in place to schedule the impedance tests quarterly. NPCC has verified the completion of all mitigation activity.
2017-03-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Baltimore Gas and Electric Company (BGE) | NCR00689 | RFC2016016019 | FAC-008-3 | R8 | On August 12, 2016, BGE submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of FAC-008-3 R8. On May 24, 2016, BGE, as part of a periodic review, discovered two instances where BGE did not provide (in accordance with BGE’s Transmission Ratings methodology) Facility Rating change information to PJM within PJM’s requested timeframe. BGE is required to provide requests for changes to Facility Ratings to PJM through the Transmission Equipment Ratings Monitor (TERM) system five business days prior to the expected implementation date. BGE, as the TO is responsible for verifying that all data it submits to PJM is correct. BGE’s Transmission Ratings Methodology requires BGE’s Operations Computer Support (OCS) to communicate ratings to PJM per PJM’s established schedule. As part of BGE’s 2016-01776 Relay Replacement Program, relays were scheduled to be upgraded for two BGE substations in May 2016. BGE’s relay upgrade work resulted in changes to Bulk Electric System (BES) Facility Ratings for two BES facilities, both of which are on the same BES transmission circuit. BGE, however, did not communicate those modified Facility Ratings to its team or to PJM before the new relays were energized. BGE completed the relay upgrade work and re-energized the lines on May 20, 2016. Because the thermal ratings of the new relays were less restrictive than those of the old relays, the overall Facility Ratings increased for both affected BES Transmission Facilities. BGE should have communicated the increased Facility Ratings to PJM by May 13, 2016 (five business days before May 20). BGE, however, did not submit the modified Facility Ratings to PJM until May 26, 2016, thus violating FAC-008-3 R8. After BGE energized the new relays, the Protection and Control Engineer for the relay upgrade project sent an email to the Ratings Engineer on May 24, 2016 requesting the removal of the old relays for the two facilities, as the upgrade work was complete and the lines had been re-energized on May 20, 2016. The Ratings Engineer updated and reviewed the modified Facility Ratings, and sent the new Facility Ratings to OCS on May 25, 2016. OCS implemented the new Facility Ratings in the BGE Energy Control System (ECS) and submitted them to PJM through TERM tickets on May 26, 2016. This noncompliance involves the management practice of workforce management through ineffective training and a lack of effective communication. The root cause of this noncompliance was BGE’s failure to adhere to BGE’s Transmission Ratings Methodology. The BGE program manager responsible for the work did not adequately identify the work to the Ratings Engineer using the established process for energizing new electrical equipment. The Ratings Engineer is the proper individual responsible for processing review and submission of the Facility Ratings for work that may impact BES Facility Ratings. This occurred due to confusion over whether OPBE-005010 - Energizing New Electrical Equipment applied to the program level work with the relay replacement program. This procedure is generally used for larger capital project work, but it is intended to also apply to program level work that may have a more significant impact and requires greater engagement within BGE to execute. Had the OP-BE-005010 process been followed, the Ratings Engineer would have been provided proper notice of the planned work to facilitate the Facility Ratings updates. This issue started on May 13, 2016, when BGE was required to comply with FAC-008-3 R8 by notifying PJM of the increased Facility Ratings five business days before BGE re-energized the lines on May 20, 2016, and ended on May 26, 2016, when BGE actually notified PJM of the increased Facility Ratings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential risk from not having accurate Facility Ratings is that equipment may be operated above its maximum ratings without the operators being aware and this may cause equipment degradation and potential failure. Operating below the correct rating in emergencies can also cause undo load shedding and result in incorrect post contingency planning. That potential risk is minimized here because the Facility Ratings at issue were increased after the relay upgrade work. Furthermore, ReliabilityFirst notes that the maximum loading on the line during the time of the noncompliance was considerably below the rating. The risk is also minimized due to BGE’s prompt detection of the issue which resulted in the lines only being re-energized for six days before BGE informed PJM of the new and accurate Facility Ratings. BGE quickly identified and corrected this issue as a result of an effective periodic review, which indicates that BGE’s detective and corrective controls are functioning well. Lastly, there was no actual impact to the BPS as a result of this issue. (There were no mega volt-amperes (MVA) alarms received in the BGE ECS during the period from May 20, 2016, when the new relays were energized, to May 26, 2016, when the modified Facility Ratings were implemented and communicated to PJM. Moreover, the maximum load on the circuit between May 20, 2016 and May 26, 2016 was approximately 130 MVA, which was well below the minimum rating of 216 MVA in the legacy rating set.) No harm is known to have occurred. ReliabilityFirst considered BGE’s FAC-008 R8 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BGE: 1) met with Program Managers to discuss the process to ensure the timely submission of rating changes to PJM; 2) revised OP-BE-005010-Energizing New Electrical Equipment to ensure appropriate project and program work that could impact BES Facility Ratings are included in the scope, and communicated to the appropriate project and program personnel. This revision and communication will eliminate any future confusion concerning the application of OP-BE-005010-Energizing New Electrical Equipment; and 3) reviewed communication processes that included equipment in-service dates that would provide data to the Ratings Engineer on potentially impacted BES Facility Ratings to see if any additional improvements could be made. ReliabilityFirst has verified the completion of all mitigation activity.
2017-03-30 | SERC Reliability Corporation (SERC) | AL Sandersville, LLC (Sandersville) | NCR11050 | SERC2016016534 | PRC-024-2 | R2 | On November 17, 2016, Sandersville submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R2. Sandersville did not complete trip setting verification for at least 40% of its generation units in accordance with the PRC-024-2 implementation plan by July 1, 2016. Prior to July 1, 2016, Sandersville contracted with a company to perform an assessment of the relay set points on all of Sandersville’s generation units. The contractor discovered that the undervoltage protective relay function in 15 out of 16 multifunction digital relays (MDRs) did not comply with the requirements of PRC-024-2. Each Sandersville generator unit has two MDRs, a primary and a backup, resulting in eight installed at the generation site. Each of the MDRs had four protective relay functions (overfrequency, underfrequency, overvoltage, and undervoltage) enabled and active that are subject to PRC-024-2. The contractor interpreted the PRC-024-2 implementation plan to require 40% of all protective relay functions at the facility be compliant at the time of review, as opposed to 40% of all generation units. The initial review of relay functions indicated that more than 40% of all relay functions (49 out of 64, or 77%) were compliant and the contractor erroneously stated Sandersville was PRC-024-2 compliant. On August 25, 2016, the contractor’s compliance group was performing a routine review of the PRC-024-2 Reliability Standard Audit Worksheet and it provided Sandersville additional PRC-024-2 implementation clarification. As a result, Sandersville determined that it did not complete trip setting verification for at least 40% of its generation units. The root cause of this issue was Sandersville’s lack of independent contractor oversight. This issue started on July 1, 2016, when Sandersville should have verified trip settings at least 40% of its generation units, and ended on December 2, 2016, when Sandersville reset the undervoltage trip setpoints. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Sandersville’s failure to set generator protective relays such that generating units remain connected during defined voltage excursions could result in premature separation of generation which would exacerbate the transient. However, Sandersville is not critical to the stability of the Bulk Electric System and the units did not operate in 2016. If Sandersville had operated during a voltage transient it would have been able to ride through a transient of one second rather than the required three-seconds. The other protective relay functions were set correctly and should have operated as required. No voltage transients occurred and Sandersville did not operate during the period of the issue. No harm is known to have occurred. SERC considered AL Sandersville, LLC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Sandersville: 1) received updated undervoltage settings from engineering and shared those setting with the Transmission Planner for review and approval; 2) updated the protective relays with the Transmission Planner approved settings; 3) consulted with the contractor to review its interpretation, assessments, and processes for determining implementation periods and effective dates; and 4) had the contractor restructure its compliance group to provide additional oversight and resources to assist plants to prevent further possible compliance issues.
2017-03-30 | SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2016015689 | PRC-005-1 | R2 | On April 28, 2016, Entergy submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-005-1 R2. Entergy did not have evidence of prior testing of four DC Control Circuits. On October 1, 2008, Entergy acquired the Ouachita power plant, including the switchyard, and assumed responsibilities for the assets. Entergy Fossil Generation assumed responsibility for the generating unit’s assets, and Entergy Transmission assumed responsibility for the switchyard assets. Upon acquiring the power plant and switchyard, Entergy did not verify the previous owner’s Protection System maintenance and testing records, nor did Entergy initiate or perform any Protection System testing. In 2010, Entergy updated its maintenance database to include the Ouachita equipment. The update included the four DC Control Circuits with a four-year maintenance cycle to comply with Entergy’s maintenance and testing program. Entergy entered the devices as “new devices.” Therefore, the maintenance interval started in 2010 instead of being retroactive to 2008. Based on the database entry and the four-year interval, Entergy would have performed the required testing no later than 2014. However, in 2012, as part of a Mitigation Plan for a previous violation of PRC-005-1, Entergy overhauled its Protection System maintenance program and assigned DC Control Circuits a 5-year maintenance interval. Entergy updated its maintenance database and Entergy would have performed the required testing on the four DC Control Circuits no later than December 31, 2015. On October 31, 2015, during scheduled relay calibration and DC control circuitry testing of equipment at the Ouachita 500kV switchyard, Entergy’s Transmission team discovered that prior testing evidence was not available for four DC control circuits related to breaker failure schemes. Entergy reviewed records dating back to the 2008 acquisition and was unable to locate the previous test records. Entergy Transmission pursued an extent of condition and did not locate documentation of prior testing for 19 relays, 18 DC control circuits, 3 potential transformers, and 9 current transformers. In addition, one station DC power system did not have records prior to acquisition, but did have records of monthly, annual, and 5-year testing since 2011. Entergy’s Fossil Generation Department performed a similar extent of condition review and determined that it did not have a similar issue with generator Protection System records. Entergy determined the cause of the issue to be inadequate policies and procedures during asset acquisition. Entergy did not have an adequate policy to address PRC-005 compliance and did not perform a thorough compliance review during the asset acquisition process. In addition, Entergy prolonged the issue by delaying the Protection System equipment entry into the maintenance database. Entergy has not determined the cause of the delay between the asset acquisition and database entry. This issue started on October 1, 2008, when Entergy acquired the facility without maintenance and testing records, and ended on October 30, 2016 when Entergy completed mitigation. Basis for VSL Assignment: SERC assessed a Violation Severity Level (VSL) of “Lower” in accordance with the January 6, 2017 VSL Matrix because Evidence Protection System devices were maintained and tested within the defined intervals (R2.1 and R2.2) was missing for 5% or less of the applicable devices. (49 devices of more than 54,000 devices) | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Entergy’s failure to perform maintenance and testing of the Protection System could result in misoperations and inadequate response to electrical faults on BPS Facilities. In addition, a misoperation could reduce or eliminate the output of approximately 780 MW through a single connection to the BPS. However, this issue is limited to one generation switchyard location. Ouachita operates with a capacity factor of approximately 25 percent and its operation is not critical to the reliability of the BPS. The Protection System at Ouachita uses multiple layers of protection and it is unlikely that all layers would fail at the same time. The battery did receive normal maintenance and testing during the violation period and should have functioned as required during normal plant operations. Entergy reported no misoperations at Ouachita. No harm is known to have occurred. SERC considered Entergy’s PRC-005-1 R2 compliance history in determining the disposition track. Entergy’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID SERC2016015481, SERC2013013258, and SERC2012011079. In the instant issue, Entergy failed to identify and retain maintenance and testing data when acquiring a new facility. Furthermore, it delayed entering the switchyard devices into its maintenance database effectively deferring maintenance and testing for two years. In SERC2016015481 an extended nuclear station operating schedule caused the maintenance interval to exceed the required interval certain substation activities. Mitigation required rescheduling of those activities and was completed March 18, 2016. In SERC2013013258 Entergy identified 15 relays that should have been included in the maintenance and testing program, but were not. During the scope assessment, Entergy did verify that the devices included in the instant issue were included in the database but did not verify availability of previous testing data. Mitigation included adding the devices and performing the required maintenance and testing. Entergy completed mitigation July 21, 2016. In SERC2012011079 nine communication systems were incorrectly identified resulting in the application of the incorrect test interval. Mitigation included reclassifying and testing the devices. Entergy completed mitigation September 24, 2013. The facts and circumstances of the prior issues are different than the instant issue and mitigation for these issues would not have prevented the instant issue. Therefore, SERC determined that Entergy’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Entergy: 1) completed testing of the devices and adequately documented the test; 2) performed an extent of conditions on other PRC-005 devices at this substation; 3) identified all substations acquired from a third party from 2008 forward; 4) reviewed maintenance records for all PRC-005 devices in the substations acquired since 2008 and confirmed proper documentation and intervals were met; 5) updated the Transmission Configuration Management Program procedure to include requirements for a PRC-005 compliance assessment when acquiring new assets from a third party; and 6) verified the inclusion of due diligence for new Transmission acquisitions is adequate for maintaining PRC-005 compliance following asset acquisition.
2017-03-30 | SERC Reliability Corporation (SERC) | MPC Generating, LLC (MPCGen) | NCR11596 | SERC2016016536 | PRC-024-2 | R1 | On November 17, 2016, MPCGen submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. MPCGen did not complete trip setting verification for at least 40% of its generation units in accordance with the PRC-024-2 implementation plan by July 1, 2016. Prior to July 1, 2016, MPCGen contracted with a company to perform an assessment of the relay set points on all of MPCGen’s generation units. The contractor discovered that the underfrequency protective relay function in the four multifunction digital relays (MDRs) did not comply with the requirements of PRC-024-2. Each MPCGen generator unit has two MDRs, a primary and a backup, resulting in four installed at the generation site. Each of the MDRs had four protective relay functions (overfrequency, underfrequency, overvoltage, and undervoltage) enabled and active that are subject to PRC-024-2. The contractor interpreted the PRC-024-2 implementation plan to require 40% of all protective relay functions at the facility be compliant at the time of review, as opposed to 40% of all generation units. The initial review of relay functions indicated that more than 40% of all relay functions (12 out of 16, or 75%) were compliant and the contractor erroneously stated MPCGen was PRC-024-2 compliant. On August 25, 2016, the contractor’s compliance group was performing a routine review of the PRC-024-2 Reliability Standard Audit Worksheet and it provided MPCGen additional PRC-024-2 implementation clarification. As a result, MPCGen determined that it did not complete trip setting verification for at least 40% of its generation units. The root cause of this issue was MPCGen’s lack of independent contractor oversight. This issue started on July 1, 2016, when MPCGen should have verified trip settings at least 40% of its generation units, and ended on October 7, 2016, when MPCGen reset the underfrequency trip setpoints. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MPCGen’s failure to set generator protective relays such that generating units remain connected during defined frequency excursions could result in premature separation of generation which would exacerbate the transient. However, MPCGen is not critical to the stability of the Bulk Electric System and operates with a capacity factor of about 0.5%. If MPCGen had operated during a frequency transient, it would have been able to ride through a transient to 57.9 Hz rather than the required 57.8 Hz. The other protective relay functions were set correctly and should have operated as required. No frequency transients of that magnitude occurred during the period of noncompliance. No harm is known to have occurred. SERC considered MPCGen’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate the issue, MPCGen: 1) corrected the relevant protective relay functions on its two CTGs, representing 100% of its units; 2) consulted with the contractor to review its interpretation, assessments and processes for determining implementation periods and effective dates; and 3) had the contractor restructure its compliance group to provide additional oversight and resources to assist plants to prevent further possible compliance issues.
2017-03-30 | SERC Reliability Corporation (SERC) | Washington County Power, LLC (WashCP) | NCR11599 | SERC2016016535 | PRC-024-2 | R2 | On November 17, 2016, WashCP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R2. WashCP did not complete trip setting verification for at least 40% of its generation units in accordance with the PRC-024-2 implementation plan by July 1, 2016. Prior to July 1, 2016, WashCP contracted with a company to perform an assessment of the relay set points on all of WashCP’s generation units. The contractor discovered that the undervoltage protective relay function in the eight multifunction digital relays (MDRs) did not comply with the requirements of PRC-024-2. Each WashCP generator unit has two MDRs, a primary and a backup, resulting in eight installed at the generation site. Each of the MDRs had four protective relay functions (overfrequency, underfrequency, overvoltage, and undervoltage) enabled and active that are subject to PRC-024-2. The contractor interpreted the PRC-024-2 implementation plan to require 40% of all protective relay functions at the facility be compliant at the time of review, as opposed to 40% of all generation units. The initial review of relay functions indicated that more than 40% of all relay functions (24 out of 32, or 75%) were compliant and the contractor erroneously stated WashCP was PRC-024-2 compliant. On August 25, 2016, the contractor’s compliance group was performing a routine review of the PRC-024-2 Reliability Standard Audit Worksheet and it provided WashCP additional PRC-024-2 implementation clarification. As a result, WashCP determined that it did not complete trip setting verification for at least 40% of its generation units. The root cause of this issue was WashCP’s lack of independent contractor oversight. This issue started on July 1, 2016, when WashCP should have verified trip settings at least 40% of its generation units, and ended on December 2, 2016, when WashCP reset the undervoltage trip setpoints. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WashCP’s failure to set generator protective relays such that generating units remain connected during defined voltage excursions could result in premature separation of generation which would exacerbate the transient. However, WashCP is not critical to the stability of the Bulk Electric System and operated with a capacity factor of only 2.09%. If WashCP had operated during a voltage transient it would have been able to ride through a transient of 0.90 pu (207 kV) rather than 0.88 pu (202.4 kV) as required. The other protective relay functions were set correctly and should have operated as required. No such voltage transients occurred while WashCP was operational. No harm is known to have occurred. SERC considered WashCP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate the issue, WashCP: 1) received updated undervoltage settings from engineering and shared those setting with the Transmission Planner for review and approval; 2) updated the protective relays with the Transmission Planner approved settings; 3) consulted with the contractor to review its interpretation, assessments and processes for determining implementation periods and effective dates; and 4) had the contractor restructure its compliance group to provide additional oversight and resources to assist plants to prevent further possible compliance issues.
2017-03-30 | SERC Reliability Corporation (SERC) | Entergy - Nuclear (EntergyNUC) | NCR11166 | SERC2016016357 | MOD-025-2 | R2 | On October 12, 2016, EntergyNUC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of MOD-025-2 R2. EntergyNUC submitted the Self-Report under an existing multi-regional registered entity (MRRE) agreement. EntergyNUC did not meet the NERC implementation schedule for verifying Reactive Power capabilities at 40% of its Facilities by July 1, 2016. EntergyNUC did not complete Reactive Power capability verification for 40% of its units by the July 1, 2016 implementation date. The MOD-025-2 implementation plan requires GOs to complete testing of at least 40% of applicable units by July 1, 2016 to verify Real and Reactive Power capability, but the plan is silent regarding the compliance implementation if the GO owns a single applicable unit. In March 2015, SERC provided EntergyNUC guidance that a GO with a single applicable unit did not have to be compliant until July 1, 2019. On June 30, 2016, after discussions with the ERO enterprise, SERC revised the guidance stating that a GO with a single applicable unit was required to be compliant by July 1, 2016. On October 12, 2016, EntergyNUC also submitted four additional Self-Reports for each of the additional MRREs that have one applicable unit and did not complete the required Reactive Power capabilities verification. EntergyNUC submitted Self-Reports for Indian Point 2, Indian Point 3, Fitzpatrick and Pilgrim Nuclear Stations registered in the NPCC region and Palisades Nuclear Station registered in Reliability First. EntergyNUC registers each entity as a separate GO with a single generating unit, and each entity self-reported the same issue. The cause of the issue was a change in the implementation guidance. EntergyNUC received the guidance shortly before the compliance date causing it to be noncompliant. This issue started on July 1, 2016, when EntergyNUC did not verify generator Reactive output, and will end upon Mitigation Plan completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EntergyNUC’s failure to verify its Reactive Power capacity could result in inaccurate modelling of unit capabilities and could affect the proper identification of adverse reliability impacts in the planning horizons. However, in the fourth quarter of 2015, EntergyNUC conducted similar testing of its generation units and transmitted that data to the planners for use in models and reliability studies. No harm is known to have occurred. SERC considered EntergyNUC’s, and its affiliates, compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EntergyNUC will complete the following mitigation activities by June 30, 2017: 1) update existing procedures to incorporate MOD-025 requirements with other similar required testing; 2) create an action in the Entergy Corrective Active Program to track the required testing; 3) schedule the reactive power capability testing in the Entergy work management system; and 4) perform real and reactive power verification testing.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Board of Public Utilities, Kansas City, KS (BPU) | NCR01061 | SPP2016015696 | PRC-006-2 | R8 | On May 2, 2016, BPU submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue of noncompliance with PRC-006-2 R8. BPU failed to provide Under Frequency Load Shedding (UFLS) data to its Planning Coordinator (PC) between October 6, 2015 and November 4, 2015, the PC’s annual UFLS information collection period. The PC required BPU to either update its UFLS data or attest that the data from the previous year had not changed, neither of which BPU did. The duration of this instance of noncompliance was from November 5, 2015, the day after UFLS data was due to the PC, through May 6, 2016, the date BPU provided the 2015 UFLS data to the PC. The root cause of this instance of noncompliance was human error. BPU staff failed to identify that the data request email received from the PC required action. There was also a reminder email from the PC that was ignored. BPU understood that UFLS data must be provided to the PC annually but failed to create internal controls to ensure that the data is submitted to the PC during the collection period; rather, it relied on email reminders from the PC, which were subsequently ignored. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to report UFLS data could cause the PC to rely on incomplete or inaccurate data for use in its event analysis and UFLS program assessments. Notwithstanding, BPU provided the updated UFLS data to the PC on May 6, 2016. Additionally, BPU is a small entity with a peak load of 495 MW and a total amount of UFLS capability of 227 MW. No harm is known to have occurred. BPU has no relevant prior violations for PRC-006-2 R8 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, BPU: 1) provided the updated UFLS data to the Planning Coordinator; 2) designated a specific staff member to be responsible for UFLS submittals; 3) implemented a multi-level review process for all data submittals; 4) input all periodic data submittal requirements into the BPU SharePoint Compliance Calendar; and 5) implemented DocMinder software to create, update, and send reminder notices to assigned staff in preparation of upcoming data submittal requirements. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Board of Public Utilities, Kansas City, KS (BPU) | NCR01061 | SPP2016015695 | EOP-004-2 | R1 | On May 2, 2016, BPU submitted a Self-Report stating that, as a Distribution Provider, Generator Owner, Generator Operator, Transmission Owner, and Transmission Operator, it had an issue of noncompliance with EOP-004-2 R1. During an internal review, BPU discovered that it had failed to include Electric Reliability Organization (ERO) reporting protocols of multiple event types in its Event Reporting Plan as required by EOP-004-2 R1 Attachment 1. The omitted event types were: damage or destruction of a facility; physical threats to a BES control center; BES emergency requiring public appeal for load reduction; and BES emergency requiring manual firm load shedding. Although these reportable event types were not explicitly identified per Attachment 1, the Event Reporting Plan did address appropriate actions to be taken if such events were to occur. The duration of this instance of noncompliance was from January 1, 2014, the effective date of EOP-004-2, through December 31, 2015, the effective date of BPU’s revised Event Reporting Plan, which explicitly identifies all reportable event types per the standard. The root cause of this instance of noncompliance was BPU’s failure to properly staff its compliance department to ensure that the changes to EOP-004 were implemented. BPU did not staff the vacant Compliance Officer position from October 2013 to June 2014. In June 2014, BPU added compliance oversight to the responsibilities of an Energy Control Center employee until the permanent replacement was filled in September 2015. However, the employee was unable to adequately assure all compliance functions were being performed, which resulted in the instant noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to include all applicable Reportable Event types in BPU’s Operating Plan has the potential to affect the reliability of the BPS by potentially aggravating damage or load loss by not responding appropriately to Reportable Events. Notwithstanding, BPU’s Event Reporting Plan indirectly addressed all Reportable Event types. No harm is known to have occurred. BPU has no relevant prior violations for EOP-004-2 R1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, BPU: 1) updated its Event Reporting Plan to explicitly list every type of reportable event type applicable in EOP-004-2 R1 Attachment 1; 2) expanded the Roles and Responsibilities descriptions on the Event Reporting Plan to clarify the expected actions and activities of each affected employee; and 3) hired a permanent replacement for the Compliance Officer position. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Buffalo Dunes Wind Project, LLC (Buffalo) | NCR11407 | SPP2016016208 | MOD-025-2 | R2; R2.1 | On September 28, 2016, Buffalo submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Buffalo is a wind farm generating facility with 135 generating units applicable to MOD-025-2. Buffalo did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Buffalo was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Buffalo underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through June 30, 2017, the date Buffalo has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Buffalo is a 249.75 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Buffalo’s violation history and determined that Buffalo has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Buffalo will complete the following mitigation activities by June 30, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Caney River Wind Project, LLC (Caney) | NCR11230 | SPP2016016248 | MOD-025-2 | R2; R2.1 | On September 29, 2016, Caney submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Caney is a wind farm generating facility with 111 generating units applicable to MOD-025-2. Caney did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Caney was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Caney underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through July 7, 2017, the date Caney has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Caney is a 199.8 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Caney’s violation history and determined that Caney has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Caney will complete the following mitigation activities by July 7, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (Chisholm) | NCR11291 | SPP2016016214 | MOD-025-2 | R2; R2.1 | On September 28, 2016, Chisholm submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Chisholm is a wind farm generating facility with 140 generating units applicable to MOD-025-2. Chisholm did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Chisholm was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Chisholm underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through May 5, 2017, the date Chisholm has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Chisholm is a 235.2 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Chisholm’s violation history and determined that Chisholm has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Chisholm will complete the following mitigation activities by May 5, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | City Utilities of Springfield, MO (SPRM) | NCR01081 | SPP2016015452 | PRC-005-1.1b | R2; R2.1 | On January 8, 2016, SPRM submitted a Self-Report stating that, as a Generator Owner and Transmission Owner, it had four instances of noncompliance with PRC-005-1.1b R2 and R2.1. SPRM has a documented Protection System maintenance and testing program (PSMTP), but was not adhering to the maintenance and testing intervals set forth in the program (R2, R2.1). Specifically, during an internal spot-check of battery maintenance activities, SPRM discovered that the valve lead-acid (VLA) batteries at the Junction Substation had not been maintained and tested within the established four month interval, and the valve regulated lead-acid (VRLA) batteries at the John Twitty Energy Center (JTEC) and the McCartney gas turbines had not been maintained and tested within the established six month interval. Additionally, the ICON communication node at the Junction Substation had not been maintained and tested within the established four month interval. SPRM uses Cascade, an asset management software, to generate an inspection list for the four month maintenance activities for VLA batteries. An upgrade to the Cascade software resulted in the Junction Substation being dropped from the inspection list. The inspection prior to the software update was performed on March 9, 2015. SPRM became aware of the oversight and performed an inspection on October 19, 2015, missing the four month interval by three months. The maintenance activities for VLRA batteries at the JTEC and McCartney generating facilities are performed at six month intervals by Substation personnel on behalf of Power Generation in accordance with SPRM’s Generation Protection System Program. SPRM Substation personnel failed to correctly configure work orders in Cascade, causing the maintenance of the VLRA batteries at JTEC and McCartney to be approximately nine months late. After discovering that the update to the Cascade software caused components to drop from its inspection lists, SPRM verified records for all other components of its Protection Systems. SPRM subsequently discovered an instance where one four-month interval for the ICON communication node at the Junction Substation was missed. The duration of this instance of noncompliance was from January 23, 2015, the first date SPRM missed a maintenance interval, through October 19, 2015, the date SPRM performed the maintenance and testing in accordance with its PSMTP. The root cause of this instance of noncompliance was a combination of human error by failing to correctly configure work orders and a lack of internal controls for relying solely on software for maintenance inspection lists to ensure adherence to maintenance intervals. Regarding the VLA batteries and the ICON communications node, SPRM uses Cascade, an asset management software, to generate an inspection list for the maintenance and testing activities. An upgrade to the Cascade software resulted in the Junction Substation being dropped from the inspection list. Regarding the VLRA batteries, personnel failed to correctly configure work orders in Cascade, resulting in one interval being missed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform timely battery maintenance and testing has the potential to affect the reliability of the BPS by increasing the risk that a battery may fail to provide power when needed. Here, the devices at issue represent less than one percent of all devices in SPRM’s PSMTP. The deficiencies were timely identified, self-reported, and mitigated by SPRM. In each instance, the maintenance and testing was missed by only one interval. Additionally, SPRM performed its scheduled monthly VLA and VRLA battery inspections during the noncompliance, which ensured the general condition of the batteries. As to the ICON communication node, it is continuously monitored and under the current standard does not require maintenance and testing but every 12 years. Accordingly, the four-month maintenance and testing interval for this communications device in SPRM's PSMTP greatly exceeds the maintenance and testing requirement for communications devices in the current standard. No harm is known to have occurred. SPRM has no relevant prior violations for PRC-005-1.1b R2 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPRM: 1) performed the maintenance and testing in accordance with it PSMTP; 2) verified that the configuration of Cascade was accurate according to all other maintenance activities and intervals performed by Substation personnel and listed in the PSMTP; 3) configured Cascade to generate work orders for the six month activities sixty days prior to the due date; 4) configured Cascade to create a notification to alert the supervisor (Electric T&D) when a work order is created; and 5) implemented a verification process, to be performed annually or after a software upgrade, to ensure the configuration of Cascade work orders is accurate according to the maintenance activities and intervals performed by Substation personnel and listed in the PSMTP. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Goodwell Wind Project, LLC (Goodwell) | NCR11574 | SPP2016016244 | MOD-025-2 | R2; R2.1 | On September 30, 2016, Goodwell submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Goodwell is a wind farm generating facility with 100 generating units applicable to MOD-025-2. Goodwell did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Goodwell was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Goodwell underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through June 9, 2017, the date Goodwell has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Goodwell is a 200 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Goodwell’s violation history and determined that Goodwell has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Goodwell will complete the following mitigation activities by June 9, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2016016103 | PRC-019-2 | R1; R1.1, 1.1.1, 1.1.2 | On September 2, 2016, LAFA submitted a Self-Report stating that, as a Generator Owner, it had an issue of noncompliance with PRC-019-2 R1, R1.1, R1.1.1, and R1.1.2 because it failed to coordinate all voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. Specifically, in-service limiters and protection functions. During a compliance review conducted in preparation for a Self-Certification requested by Southwest Power Pool Regional Entity (SPP RE), LAFA discovered that the final report, prepared by a third-party consultant, on the coordination study was incomplete. LAFA hired the third-party consultant to assist with gathering the necessary data required to prepare the verification report for PRC-019-2. The consultant found discrepancies in the parameter nomenclature critical to performing modeling and calculations needed to meet the standard requirements. LAFA attempted to contact the generator vendor in Shinagawa-Ku, Tokyo, Japan to acquire the vital information, but experienced several obstacles due to language and time zone differences. Consequently, LAFA was unable to obtain the information needed to complete the report for several weeks. Once LAFA received the data and validated all pertinent information, the third-party consultant was able to finalize the necessary models and calculate critical parameters for the report. Due to the delay in obtaining the necessary information from the vendor, LAFA missed verifying its two units by the standard’s effective date of July 1, 2016. The duration of this instance of noncompliance was from July 1, 2016, the effective date of PRC-019-2 R1, through September 29, 2016, the date LAFA completed the verification study on its two units. The root cause of this instance of noncompliance was a combination of LAFA’s inability to get timely information from the vendor due to language barriers and time zone differences, and LAFA not scheduling extra time to allow for unforeseen delays. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to properly set the in-service limiters can cause the generator Automatic Voltage Regulator to impose unacceptable operating conditions on the generator. Such conditions, i.e. overexcitation and underexcitation, have the potential to affect the reliability of the BPS by decreasing the generators ability to withstand system voltage events and increasing the probability of generator trips due to loss of synchronism and generator field overloads. Notwithstanding, this noncompliance was limited to two 61 MW units which have minimal impact on the BPS. In addition, the units have been in operation many years and have never experienced a protective relay operation as a result of operation of the excitation system controls. No harm occurred as a result of this noncompliance. LAFA has no relevant prior violations for PRC-019-2 R1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, LAFA: 1) verified the parameters and study for accuracy; and 2) completed and issued the final report. To prevent reoccurrence of this minimal risk instance of noncompliance, LAFA included this requirement on their tracking spreadsheet and on the NERC Calendar for testing to be flagged every 5 years, enabling LAFA to begin the review 6 months prior to the due date. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2016016090 | MOD-025-2 | R1.2 | On September 2, 2016, LAFA submitted a Self-Report stating that, as a Generation Owner (GO), it had an issue of noncompliance with MOD-025-2 R1.2 because it did not provide its internal Transmission Planner (TP) with verification of the Real Power capability of its single generating facility. The FERC-approved implementation plan for MOD-025-2 requires that each GO shall provide its TP with verification of the Real Power capability of 40% of its applicable facilities by July 1, 2016. LAFA verified the Real Power capability of its two 61.2 MW generating units at the T.J. Labbe Electric Generating Station per MOD-025-2 R1.1; submitted the test data to its Planning Coordinator (PC), Midcontinent Independent System Operator (MISO); but inadvertently failed to send the test data to its internal TP by July 1, 2016, as required by R1.2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through September 2, 2016, the date LAFA submitted MOD-025-2 Attachment 2 to its internal TP. The root cause of this instance of noncompliance was lack of internal controls to ensure adherence to MOD-025-2 R1.2. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate long-term decisions affecting the reliability of the BPS. Notwithstanding, this noncompliance was limited to two 61.2 MW generating units, which have minimal impact on the BPS. LAFA is registered as a GO/GOP and TP, and the personnel performing these functions are at the same location. Because they interact frequently, the personnel performing the TP function had knowledge of the reactive and real capabilities of the T.J. Labbe Electric Generating Units. LAFA did verify the Real Power capability of its generating units in accordance with Attachment 1 per MOD-025-2 R1.1 and provided this information to its PC. No harm is known to have occurred. SPP RE reviewed LAFA’s violation history and determined that it has no prior instances of noncompliance with MOD-025. | To mitigate this minimal risk instance of noncompliance, LAFA: 1) submitted Attachment 2 to its TP. To prevent this minimal risk instance of noncompliance from reoccurring, LAFA Generation updated its Management Control and “Generating Unit Regulatory Testing” spreadsheet to ensure Attachment 2 is submitted to LAFA’s internal TP within 90 days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Lafayette Utilities System (LAFA) | NCR01114 | SPP2016016097 | MOD-025-2 | R2.1 | On September 2, 2016, LAFA submitted a Self-Report stating that, as a Generation Owner, it had an issue of noncompliance with MOD-025-2 R2.1. LAFA has one generating facility applicable to MOD-025-2, specifically, the T.J. Labbe Electric Generating Station, which consists of two 61.2 MW generating units. LAFA did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per MOD-025-2 R2.1. As a result, LAFA was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its generating units. The root cause of this instance of noncompliance was a lack of internal processes to allow for unexpected delays of third parties who are needed to conduct necessary verification tests. LAFA was unable to schedule the generator manufacturer in time to complete the tests prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 8, 2016, the date LAFA verified the reactive capability of its units and forwarded the information to its TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 creates the potential for the TP to have inaccurate or incomplete information regarding the capabilities of the generating units in its planning area. Incorrect information in planning models introduces errors in the various studies performed by the TP and can result in inappropriate long-term decisions affecting the reliability of the BPS. Notwithstanding, this noncompliance was limited to two 61.2 MW generating units, which have minimal impact on the BPS. Additionally, the units did not exceed Reactive Power capability during the time of noncompliance. No harm is known to have occurred. SPP RE reviewed LAFA’s violation history and determined that it has no prior instances of noncompliance with MOD-025-2. | To mitigate this minimal risk instance of noncompliance, LAFA: 1) performed testing of Reactive Power capability of its generating units; 2) analysed testing data and finalized the test report; 3) completed and submitted Attachment 2 per R2.2 to its TP; and 4) included this requirement on its tracking spreadsheet and on the NERC calendar for testing to be flagged every five years. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Lea Power Partners, LLC (LEAPP) | NCR10301 | SPP2016016280 | PRC-024-2 | R1 | On September 30, 2016, LEAPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of noncompliance with PRC-024-2 R1. LEAPP is a gas fired cogeneration power plant with three generating units applicable to PRC-024-2. LEAPP did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The duration of this instance of noncompliance was from July 1, 2016, the effective date of PRC-024-2, through November 16, 2016, the date LEAPP completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was LEAPP’s lack of compliance oversight due to its vacant Director of NERC/FERC Compliance position and failure to provide an adequate substitute. Proper oversight would have ensured coordination of protective relay settings changes with the Transmission Operator and implementation of the approved changes were complete prior to the effective date of PRC-024-2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to ensure generator frequency protective relays are set in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, LEAPP is a 604 MW gas fired cogeneration power plant that is continuously monitored by plant operators who are able to analyze and respond to any changes in system frequency. Additionally, LEAPP attested that this generation facility has operated without experiencing any PRC-024 related issues since May 24, 2012, the commissioning date of the facility. No harm is known to have occurred. SPP RE reviewed LEAPP’s violation history and determined that LEAPP has no prior instances of noncompliance with PRC-024. | To mitigate this minimal risk instance of noncompliance, LEAPP: 1) commissioned Kestrel Engineering to produce a protection coordination study and report applicable to PRC-024 R1; 2) received approval from Mitsubishi Electric Company, the gas turbine generators manufacturer, for the recommended setting changes; 3) received approval from Mitsubishi, the steam turbine generators long-term service provider, for the recommended setting changes; 4) received confirmation from the Transmission Operator that the new settings and coordination is adequate; 5) made all recommended relay setting changes; 6) received the completed modeling and calculations from Kestrel Engineering to document compliance with PRC-024 R1; and 7) hired a Director of NERC/FERC Compliance. SPP RE has verified the completion of all mitigation activity.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Origin Wind Energy, LLC (Origin) | NCR11496 | SPP2016016246 | MOD-025-2 | R2; R2.1 | On September 30, 2016, Origin submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Origin is a wind farm generating facility with 75 generating units applicable to MOD-025-2. Origin did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Origin was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Origin underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through June 9, 2017, the date Origin has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Origin is a 150 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Origin’s violation history and determined that Origin has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Origin will complete the following mitigation activities by June 9, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Rocky Ridge Wind Project, LLC (Rocky) | NCR11234 | SPP2016016262 | MOD-025-2 | R2; R2.1 | On September 30, 2016, Rocky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Rocky is a wind farm generating facility with 93 generating units applicable to MOD-025-2. Rocky did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Rocky was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Rocky underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through April 28, 2017, the date Rocky has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Rocky is a 148.8 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Rocky’s violation history and determined that Rocky has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Rocky will complete the following mitigation activities by April 28, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Farm, LLC (Smoky) | NCR11049 | SPP2016016278 | MOD-025-2 | R2; R2.1 | On September 30, 2016, Smoky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Smoky is a wind farm generating facility with 56 generating units applicable to MOD-025-2. Smoky did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Smoky was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Smoky underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through July 7, 2017, the date Smoky has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Smoky is a 100.8 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Smoky’s violation history and determined that Smoky has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Smoky will complete the following mitigation activities by July 7, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Project II, LLC (Smoky II) | NCR10316 | SPP2016016279 | MOD-025-2 | R2; R2.1 | On September 30, 2016, Smoky II submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R2 and R2.1. Smoky II is a wind farm generating facility with 99 generating units applicable to MOD-025-2. Smoky II did not verify the Reactive Power capability of its generating units in accordance with Attachment 1 per R2.1. As a result, Smoky II was unable to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its wind facility per R2. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Smoky II underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through May 5, 2017, the date Smoky II has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Smoky II is a 148.5 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Smoky II’s violation history and determined that Smoky II has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Smoky II will complete the following mitigation activities by May 5, 2017: 1) complete preparations for testing and verifying the Reactive Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Reactive Power capability of its generating units; and 3) submit a verification of the Reactive Power capability of its generating units to the TP within 90 days from the test date.
2017-03-30 | Texas Reliability Entity (Texas RE) | Duke Energy Renewables Services, LLC (DERS) | NCR11032 | TRE2016016320 | TOP-002-2.1b | R13 | On October 6, 2016, DERS submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with TOP-002-2.1b R13. Specifically, DERS did not perform generating reactive capability verifications including, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, as requested by its Balancing Authority (BA). At the time of the issue in question, DERS’ BA specified that GOPs should perform required reactive capability verifications at a minimum of once every two years. DERS completed previous reactive capability testing on February 13, 2013. As such, DERS should have completed its next reactive capability verification by February 13, 2015. However, DERS did not actually complete the requisite reactive capability verification until June 11, 2015. The root cause of this issue was an insufficient process for ensuring accurate entry and tracking of reactive capability verification dates. In particular, DERS misunderstood the required periodicity under its BA’s reactive capability verification specifications. That is, DERS mistakenly believed that the two-year requirement in the relevant BA verification request was a requirement to provide specified reactive verifications to the BA every two calendar years rather than two years from the last date tested. This issue started on February 14, 2015, which is two years and one day following the date of the first qualification test performed, and ended on June 11, 2015, when DERS completed the required leading and lagging reactive capability tests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following four factors. First, the single generation Facility at issue produces a relatively small amount of generation, only approximately 200 MW. Second, DERS did not receive any requests for reactive power during the duration of the issue. Third, there were no misoperations or Bulk Electric System (BES) emergencies stemming from the issue for its duration. Finally, following this issue, DERS’ BA revised its real and reactive verification request specification to match the five-year verification interval set forth in MOD-025-2, and DERS performed all the testing at issue here within these revised intervals. No harm is known to have occurred. Texas RE considered DERS’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DERS: 1) completed all reactive capability verifications requested by its BA for 2015; 2) instituted a new Real and Reactive Verification Procedure that addresses relevant testing intervals, as well as testing procedures and appropriate testing submittal templates; 3) created a Compliance Task Schedule that includes recurring tasks and deadlines for all BA verification and test submittals and corresponding MOD-025 test data submittals; 4) modified its workflow form to include Compliance Program Manager approval for changes that may impact reactive capability and require testing or other verification; 5) created a Preventative Maintenance (PM) item in Maximo for TOP-002-2.1b R13 and MOD-025 to assist with scheduling deadlines for real and reactive verifications; 6) conducted a review of BA requests, BA data specifications, and NERC requirements to identify any periodic requirements and determine where additional guidance might be needed; and 7) conducted a training session for operations staff and management regarding all applicable real and reactive verification requirements. Texas RE verified completion of DERS' mitigating activities.
2017-03-30 | Texas Reliability Entity (Texas RE) | Quail Run Energy Partners, LP (QREP) | NCR11525 | TRE2017016859 | PRC-024-2 | R2 | On January 25, 2017, QREP submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-024-2 R2. Specifically, QREP did not set its protective relays such that its generator voltage protective relaying would not trip applicable generating units as a result of a voltage excursion within the “no trip zone” set forth in PRC-024 Attachment 2. In April 2016, QREP contracted with an engineering firm to perform a review of its frequency and voltage trip set points for its single generation Facility. However, due to a miscommunication, the contractor only provided information regarding QREP’s frequency settings in its preliminary report and omitted information corresponding to QREP’s voltage protective relaying settings. On November 10, 2016, the contractor in question properly included information concerning QREP’s voltage trip settings in its final report. QREP personnel then reviewed the final report and discovered the issue with their generating unit’s voltage settings. On December 3, 2016, QREP revised the applicable voltage settings so that they would not trip QREP’s applicable generating units within the designated “no trip zone.” The root cause of this issue was QREP did not have adequate processes in place to monitor contractor activities and track deliverables to ensure the complete performance of all required compliance tasks. In particular, QREP did not ensure that the contractors in question were fully aware of the specific services that needed to be performed. The issue started on July 1, 2016, when PRC-024-2 R2 became enforceable, and ended on December 3, 2016, when QREP reset the voltage trip settings so that they would not trip QREP’s applicable generating units within the designated “no trip zone.” | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, QREP produced a small amount of power during the issue duration, an average of approximately 100 MW. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves well in excess of the QREP Facility’s corresponding generation output. As such, even if a unit trip had occurred, the ERCOT interconnection possessed adequate reserves to respond to any issues. Third, the single generation Facility at issue has never experienced any normal operational unit trips as a result of its voltage protective relay settings being set within the “no trip zone.” No known harm is known to have occurred. Texas RE considered QREP's compliance history in determining the disposition track. QREP's relevant compliance history includes an issue with PRC-024-2 R1 (TRE2016016219). Texas RE determined that QREP's previous instance of noncompliance should not serve as an aggravating factor because the root cause of the previous instance is distinguishable from the current issue. In the previous instance related to PRC-024-2 R1, QREP failed to set its protective relaying such that the generator frequency protective relaying did not trip the applicable generating unit within the “no trip zone” of PRC-024 Attachment 1 because QREP did not provide sufficient lead time to complete the required protective relay settings changes before PRC-024-2’s July 1, 2016 enforceable date. In the current instance pertaining to PRC-024-2 R2, QREP failed to ensure that the contractor performed a review of QREP’s voltage settings as requested. Furthermore, QREP did not have adequate processes in place to monitor contractor activities and track deliverables. Finally, QREP implemented several measures in its prior mitigation activities that detected the current issue and are designed to prevent recurrence of these issues. | To mitigate this issue, QREP: 1) implemented the required settings to be compliant with PRC-024 Attachment 2; 2) provided revised voltage settings to its Planning Coordinator; 3) established a process to require that requests for quotes and purchase orders for services will be fully detailed to ensure each compliance measurement and requirement specification has been included; 4) established a process to require that senior QREP leadership participate in monthly conference calls concerning all NERC compliance activities; and 5) upgraded its Facility Issues and Actions List to include each individual requirement in compliance matters with any open issues tracked. Texas RE verified completion of QREP's mitigating activities.
2017-03-30 | Texas Reliability Entity (Texas RE) | Sandy Creek Services, LLC (SCS) | NCR11182 | TRE2016016190 | PRC-019-2 | R1 | On September 23, 2016, SCS submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-019-2 R1. In particular, SCS did not verify the coordination of its voltage regulating system controls, including in-service limiters and protection functions, with equipment capabilities and settings of the Protection System devices and functions for its single generation Facility by July 1, 2016. In February 2016, SCS hired a contractor to perform a voltage coordination study to verify that its voltage regulating system controls were properly coordinated with the applicable Protection System capabilities and settings at its sole generation Facility. In June 2016, the contractor provided screenshots of its verification results. SCS then engaged a second contractor in July 2016 to review this information and ultimately requested a full written report from the initial contractor. When the initial contractor provided a full written report in September 2016, SCS determined that the first contractor did not include all relay set points in the verification study. As a result, SCS requested that the second contractor complete an additional voltage coordination study in October 2016. On December 5, 2016, the second contractor provided a revised voltage verification study that included all required set points and devices, as well as confirmed that all such devices were properly coordinated. The root cause of this issue was insufficient planning to timely implement compliance with the voltage control coordination requirements set forth in PRC-019-2 R1. In particular, SCS did not provide sufficient lead-time for the initial contractor to properly complete the voltage verification study and for SCS to perform a review of that verification study to ensure all required in-service limiters were properly verified. The issue started on July 1, 2016, when PRC-019-2 R1 became enforceable, and ended on December 5, 2016, when SCS completed its revised PRC-019-2 study to include the voltage coordination verifications for all required devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because of the following factors. First, the December 5, 2016 coordination study ultimately verified that all SCS voltage regulating system controls were properly coordinated with the applicable equipment capabilities and settings of the applicable Protection System devices and functions of its Facility as required by PRC-019-2 R1. Second, SCS stated that there have been no unit trips related to the coordination of the voltage regulating system controls and protections systems since July 1, 2016. No harm is known to have occurred. Texas RE considered SCS' compliance history and determined there were no relevant instances of noncompliance related to PRC-019 R1. | To mitigate this issue, SCS: 1) completed a revised voltage coordination study to demonstrate compliance with PRC-019-2 R1; 2) created a recurring task reminder in its compliance management tool (Maximo) to ensure that appropriate staff members are notified of the next PRC-019-2 deadline one year in advance of the deadline; and 3) provided training that covered PRC-019-2 requirements to appropriate personnel. Texas RE verified completion of SCS' mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016015855 | MOD-001-1a | R2 | On June 22, 2016, BPA submitted a Self-Report stating that as a Transmission Service Provider, it had a possible issue of noncompliance with MOD-001-1a R2. Specifically, BPA identified instances in which the Available Transfer Capability (ATC) on certain designated ATC Paths was not calculated as specified in R2. This issue specifically concerned BA-BA interconnections that BPA designated as ATC Paths in 2014. Following supplemental guidance from WECC in 2016, BPA removed designation of these interconnections as ATC Paths from its Available Transfer Capability Implementation Document (ATCID). This issue began October 5, 2015, the earliest identified instance in which BPA failed to calculate ATC as specified in R2, and ended November 1, 2016, when BPA removed all references to the retired Paths from its ATCID and associated documentation, for a total of 393 days of noncompliance. This issue involved multiple root causes related to the automated system BPA used to calculate ATC on the Paths in scope, including: accidental disabling of calculation jobs, expiration of application data-based login, unintended disabling of calculation jobs during installation of a server patch, failure to re-enable calculations following transfer to another server, memory issues with the server, and causes BPA was unable to identify. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, BPA failed to calculate hourly and daily ATC values as prescribed by R2 for BA-BA interconnections designated as ATC Paths in BPA’s ATCID. Such failure could reduce BPA’s awareness of ATC and future flows on its system. However, this issue was limited to BA-BA interconnections that BPA 1) designated as ATC Paths solely to address documentation-related requirements in MOD-029, and 2) subjected to a separate calculation process specific and unique to the Paths in scope. This issue and its associated causes did not affect BPA’s management of any other ATC Paths, and no harm is known to have occurred. BPA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, BPA: 1) retired designation of BA-BA interconnections as ATC Paths from its systems and processes; 2) discontinued ATC calculation for the retired Paths; and 3) removed all references to the retired Paths from its ATCID and associated documentation. WECC verified completion of BPA’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016015856 | MOD-001-1a | R8 | On June 22, 2016, BPA submitted a Self-Report stating that as a Transmission Service Provider, it had a possible issue of noncompliance with MOD-001-1a R8. Specifically, BPA identified instances in which the Available Transfer Capability (ATC) on certain designated ATC Paths collectively exceeded the annual allotment of hourly values exempted by R8.1, and was not recalculated per the minimum frequency prescribed by R8.2. This issue specifically concerned BA-BA interconnections that BPA designated as ATC Paths in 2014. Following supplemental guidance from WECC in 2016, BPA removed designation of these interconnections as ATC Paths from its Available Transfer Capability Implementation Document (ATCID). This issue began October 5, 2015, the earliest identified instance in which BPA failed to calculate ATC as specified in R8, and ended November 1, 2016, when BPA removed all references to the retired Paths from its ATCID and associated documentation, for a total of 393 days of noncompliance. This issue involved multiple root causes related to the automated system BPA used to calculate ATC on the Paths in scope, including: accidental disabling of calculation jobs, expiration of application data-based login, unintended disabling of calculation jobs during installation of a server patch, failure to re-enable calculations following transfer to another server, memory issues with the server, and causes BPA was unable to identify. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, BPA failed to calculate hourly and daily ATC values as prescribed by R8 for BA-BA interconnections designated as ATC Paths in BPA’s ATCID. Such failure could reduce BPA’s awareness of ATC and future flows on its system. However, this issue was limited to BA-BA interconnections that BPA 1) designated as ATC Paths solely to address documentation-related requirements in MOD-029, and 2) subjected to a separate calculation process specific and unique to the Paths in scope. This issue and its associated causes did not affect BPA’s management of any other ATC Paths, and no harm is known to have occurred. BPA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, BPA: 1) retired designation of BA-BA interconnections as ATC Paths from its systems and processes; 2) discontinued ATC calculation for the retired Paths; and 3) removed all references to the retired Paths from its ATCID and associated documentation. WECC verified completion of BPA’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Harbor Cogeneration Company, LLC (HCC) | NCR05177 | WECC2016016128 | MOD-025-2 | R1 | On September 9, 2016, HCC submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, HCC reported that it failed to verify the Real Power capability of its single applicable Facility in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for HCC’s applicable Facility, and is ongoing. HCC tested its Facility on March 2, 2017 and will provide the report to its Transmission Planner by April 28, 2017. The root cause of this issue was a misunderstanding regarding the effective date of MOD-025-2 for single unit Facilities. HCC believed that because it owns a single applicable Facility, it was not required to meet the 40% implementation deadline, as it could not test only 40% of its Facility. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, HCC failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single 107.4 MVA Facility, and no harm is known to have occurred. Additionally, it is unlikely this issue would have significantly affected current planning models because HCC tested its units in accordance with the WECC Model Validation Policy, which yielded most of the required data, prior to the effective date of MOD-025-2. HCC does not have previous violations of this Standard and Requirement. | To mitigate this issue, HCC will complete testing of its applicable Facility and report on the results. Because this issue concerned a single Facility, there is no risk of recurrent failure to implement this Standard in accordance with future percentage-based implementation deadlines. HCC will complete its mitigation by April 28, 2017.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Harbor Cogeneration Company, LLC (HCC) | NCR05177 | WECC2016016129 | MOD-025-2 | R2 | On September 9, 2016, HCC submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, HCC reported that it failed to verify the Reactive Power capability of its single applicable Facility in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for HCC’s applicable Facility, and is ongoing. HCC tested its Facility on March 2, 2017 and will provide the report to its Transmission Planner by April 28, 2017. The root cause of this issue was a misunderstanding regarding the effective date of MOD-025-2 for single unit Facilities. HCC believed that because it owns a single applicable Facility, it was not required to meet the 40% implementation deadline, as it could not test only 40% of its Facility. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, HCC failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single 107.4 MVA Facility, and no harm is known to have occurred. Additionally, it is unlikely this issue would have significantly affected current planning models because HCC tested its units in accordance with the WECC Model Validation Policy, which yielded most of the required data, prior to the effective date of MOD-025-2. HCC does not have previous violations of this Standard and Requirement. | To mitigate this issue, HCC will complete testing of its applicable Facility and report on the results. Because this issue concerned a single Facility, there is no risk of recurrent failure to implement this Standard in accordance with future percentage-based implementation deadlines. HCC will complete its mitigation by April 28, 2017.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Hetch Hetchy Water and Power (HHWP) | NCR05182 | WECC2016016206 | FAC-003-3 | R7 | On September 20, 2016, HHWP submitted a Self-Report stating that as a Transmission Owner and Generator Owner, it had a possible issue of noncompliance with FAC-003-3 R7. Specifically, HHWP reported that it did not perform chemical vegetation control on roughly three miles of two 230 kV lines as required by its 2015 annual vegetation work plan. Although HHWP prepared and approved a work order for the lines, HHWP failed to schedule and complete the work. This issue began January 1, 2016, when any incomplete work identified in HHWP’s 2015 work plan became past due, and ended January 1, 2017, when HHWP revised its TVMP and annual vegetation work plan to remove chemical vegetation control as a requirement and replace with mechanical vegetation removal. The root cause of this issue was the lack of an internal process to track work orders via HHWP’s work management system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, HHWP failed to complete 100% of its 2015 annual vegetation work plan. Such failure could have limited HHWP’s ability to ensure prevention of vegetation encroachments into the Minimum Vegetation Clearance Distance (MVCD) of the lines in scope. However, despite the oversight behind this issue, HHWP had preventive controls in place when the issue occurred. HHWP utilizes a work management system to facilitate implementation of its Transmission Vegetation Management Program (TVMP). This system automates many of HHWP’s TVMP-related tasks, and provides visibility of overdue work. The system accurately identified the overdue work; however, the individual responsible for ensuring completion overlooked the overdue work order. Additionally, this issue concerned less than 5% of HHWP’s 2015 annual vegetation work plan. HHWP performed mechanical vegetation removal over several spans of the lines in question, and additional spans of the lines were selected as test sites for the chemical treatment included in the 2015 plan. Inspections performed by HHWP in 2016 did not identify any areas at risk from vegetation encroachment on the lines. No harm was known to have occurred. HHWP does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, HHWP: 1) amended its 2015 work plan to note that the work order in scope was moved to 2016; 2) revised its TVMP and 2016 annual vegetation work plan to replace chemical vegetation control with mechanical vegetation removal; and 3) provided training to requisite personnel regarding tracking and management of work orders related to its TMVP. WECC verified completion of HHWP’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Merced Irrigation District (MEID) | NCR05234 | WECC2016016558 | PRC-002-2 | R1 | On November 22, 2016, MEID submitted a Self-Report stating that as a Transmission Owner, it had a possible issue of noncompliance with PRC-002-2 R1. Specifically, MEID reported that it did not identify which Bulk Electric System (BES) buses required sequence of events recording (SER) and fault recording (FR) data to analyze system disturbances by the implementation deadline for PRC-002-2. This issue began July 1, 2016, when PRC-002-2 became mandatory and enforceable for MEID, and ended December 6, 2016, when MEID identified a single applicable bus in accordance with the Attachment 1 methodology, and notified owners of associated BES Elements of such identification, for a total of 158 days of noncompliance. The root cause of this issue was a misunderstanding regarding the effective date of the Standard; MEID believed it was not required to meet this Requirement until July 1, 2018. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MEID failed to identify which BES buses required SER and FR data to analyze system disturbances, which could have limited MEID’s ability to record and properly analyze system disturbance data. However, this issue concerned a single bus at a 115 kV substation, which had SER and FR capability during the period in question. MEID uses an automated work management system to schedule and perform compliance-related tasks, and would likely have met this Requirement absent the misunderstanding regarding the implementation deadline. No harm is known to have occurred. MEID does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, MEID: 1) applied the Attachment 1 methodology to identify its applicable bus; 2) notified owners of associated BES Elements of this identification; and 3) revised its compliance tracking materials in include implementation deadlines for each applicable Standard, with a specific emphasis on recent and soon-to-be enforceable Standards. WECC verified completion of MEID’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Mesquite Power LLC (MPL) | NCR05235 | WECC2016016462 | PRC-019-2 | R1 | On October 31, 2016, MPL submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, MPL reported that it failed to coordinate voltage regulating system controls with equipment capabilities and Protection System device settings for at least 40 percent of its applicable Facilities by the effective date of the Standard. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of MPL’s applicable Facilities, and ended March 7, 2017, when MPL adjusted settings to meet requisite coordination, for a total of 249 days of noncompliance. The root cause of this issue was a misunderstanding of the verification specifications of PRC-019-2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MPL failed to coordinate at least 40 percent of its applicable Facilities in accordance with R1. Such failure could result in over-voltage damage to MPL’s applicable Facilities, or unnecessary trip of a generator during a system event that should not cause a generator to trip. However, this issue concerned a single set point, which has never caused any of MPL’s units to trip unnecessarily, and has since been remediated. The collective capacity of MPL’s applicable Facilities is 813 MVA, and no harm is known to have occurred. MPL does not have previous violations of this Standard and Requirement. | To mitigate this issue, MPL: 1) adjusted settings to meet coordination requirements; and 2) established automatic periodic notifications for future tests and tasks related to this Standard. WECC verified completion of MPL’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Mt. Poso Cogeneration Co. (MTPO) | NCR05254 | WECC2016016645 | COM-002-4 | R3 | On December 8, 2016, MTPO submitted a Self-Report stating that as a Generator Operator, it had a possible issue of noncompliance with COM-002-4 R3. Specifically, MTPO reported that during an internal review, it discovered it had never conducted initial training regarding oral, two-party, person-to-person Operating Instructions. This issue began July 1, 2016, when COM-002-4 R3 became mandatory and enforceable for MTPO, and ended December 4, 2016, when all of MTPO’s operators completed the training, for a total of 156 days of noncompliance. The root cause of this issue was MTPO’s failure to identify and include such training in its training procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MTPO failed to conduct initial training regarding oral two-party, person-to-person Operating Instruction to all operating personnel. Such failure could limit operators’ awareness of predefined communications protocols, which could increase the possibility of miscommunication. However, this issue concerned experienced operators who were subject to informal on-the-job training concerning two-part communication prior to the effective date of the Standard. No harm is known to have occurred. MTPO does not have previous violations of this Standard and Requirement. | To mitigate this issue, MTPO: 1) conducted training for all operating personnel; and 2) revised its training procedure to include initial training in accordance with the Standard. WECC verified completion of MTPO’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Woodland Biomass Power Ltd. (WDBM) | NCR10047 | WECC2016016642 | COM-002-4 | R3 | On December 6, 2016, WDBM submitted a Self-Report stating that as a Generator Operator, it had a possible issue of noncompliance with COM-002-4 R3. Specifically, WDBM reported that during an internal review, it discovered it had never conducted initial training regarding oral, two-party, person-to-person Operating Instructions. This issue began July 1, 2016, when COM-002-4 R3 became mandatory and enforceable for WDBM, and ended November 21, 2016, when all of WDBM’s operators completed the training, for a total of 143 days of noncompliance. The root cause of this issue was WDBM’s failure to identify and include such training in its training procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WDBM failed to conduct initial training regarding oral two-party, person-to-person Operating Instruction to all operating personnel. Such failure could limit operators’ awareness of predefined communications protocols, which could increase the possibility of miscommunication. However, this issue concerned experienced operators whom were subject to informal on-the-job training concerning two-part communication prior to the effective date of the Standard. No harm is known to have occurred. WDBM does not have previous violations of this Standard and Requirement. | To mitigate this issue, WDBM: 1) conducted training for all operating personnel; and 2) revised its training procedure to include training in accordance with the Standard. WECC verified completion of WDBM’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Griffith Energy, LLC (GRGO) | NCR03052 | WECC2016016410 | PRC-019-2 | R1 | On October 25, 2016, GRGO submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, GRGO reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings for at least 40 percent of its applicable Facilities by the effective date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for the Standard and Requirement. WECC determined that this issue began on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of GRGO’s applicable Facilities, and ended on August 31, 2016, when GRGO completed the required verification activities for all three of its units, for a total of 61 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, GRGO failed to verify coordination items prescribed by R1.1.1 and R1.1.2 in accordance with the Standard’s implementation deadline. Such failure limited GRGO’s awareness of coordination of its applicable Facilities. However, GRGO discovered the issue and immediately made arrangements to verify the appropriate relay settings and correct as necessary. In addition, GRGO maintained coordinated voltage regulating system controls for each of its generating units at its Facility that met the requirements of PRC-019-2 R1. Further, GRGO did not experience any unit trips based on a miscoordination between the units’ voltage regulating system controls and the applicable equipment capabilities. No harm is known to have occurred. GRGO does not have previous violations of these Standards and Requirements. | To remediate and mitigate this issue, GRGO: a. Completed the required verification activities for all three of its units as required by the Standard; and b. Added the requirements of PRC-019-2 R1 within its relay tracking system to ensure proper coordination of the relay settings are verified per regulation requirements. WECC verified completion of GRGO’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Griffith Energy, LLC (GRGO) | NCR03052 | WECC2016016411 | PRC-024-2 | R1 | On October 25, 2016, GRGO submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. Specifically, GRGO reported that it failed to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for the Standard and Requirement. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of GRGO’s protective relaying, and ended August 31, 2016, when GRGO verified the settings of its protective relaying, per Attachment 1, bringing it into compliance with the current implementation schedule, for a total of 61 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, GRGO failed to set 40 percent of its protective relaying such that generator voltage protective relaying would not trip applicable generating units unnecessarily. Such failure could result in the unnecessary trip of one or more generating units offline due to frequency excursions within the “no trip zone”. However, the generating units did not trip offline due to frequency excursions within the “no trip zone”. The verification showed that the extant frequency relay settings are compliant with the standard for all of GRGO’s generators, no changes were recommended by the contractor, and no harm is known to have occurred. GRGO does not have previous violations of these Standards and Requirements. | To remediate and mitigate this issue, GRGO: a. Completed the required verification activities for all three of its units in accordance with PRC-024-2 Attachment 1; and b. Implemented a process to review frequency device settings to ensure proper coordination as part of its ongoing protection system maintenance program to ensure settings do not change. WECC verified completion of GRGO’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Griffith Energy, LLC (GRGO) | NCR03052 | WECC2016016412 | PRC-024-2 | R2 | On October 25, 2016, GRGO submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R2. Specifically, GRGO reported that it failed to set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 2 by the effective date of the Standard. The root cause of this issue was a misunderstanding of the phased-in implementation plan for the Standard and Requirement. WECC determined that this issue began on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of GRGO’s protective relaying, and ended August 31, 2016, when GRGO verified the settings of its protective relaying, per Attachment 2, bringing it into compliance with the current implementation schedule, for a total of 61 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In instance, GRGO failed to set its protective relaying such that generator voltage protective relaying would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to voltage excursions within the “no trip zone”. However, verification showed that the extant voltage relay settings are compliant with the Standard for all of GRGO’s generators, no changes were recommended by the contractor, and no harm is known to have occurred. GRGO does not have previous violations of these Standards and Requirements. | To remediate and mitigate this issue, GRGO: a. Completed the required verification activities for all three of its units in accordance with PRC-024-2 Attachment 1; and b. Implemented a process to review voltage device settings to ensure proper coordination as part of its ongoing protection system maintenance program to ensure settings do not change. WECC verified completion of GRGO’s mitigating activities.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2017017026 | TOP-007-WECC-1 | R2 | On January 30, 2017, IPCO submitted a Self-Log stating that, as a Transmission Operator (TOP), it had a possible issue of noncompliance with TOP-007-WECC R2. Specifically, IPCO reported it identified two instances during which it failed to have Net Scheduled Interchange (NSI) for power flow under the SOL rating of a WECC Major Transfer Path when it implemented real-time schedules for the next hour. In the first instance, IPCO reported that at 08:24 on August 11, 2016, the SOL decreased from 2,557 MW to 800 MW due to fires around the power lines. At 08:34, IPCO operators notified Pacificorp (PAC) regarding this issue, and informed PAC of its new share on the de-rated Path. Although curtailments of PAC schedules were required, PAC was not able to cut their schedules to their new share of the Path until 09:13. This issue began at 09:00 on August 11, 2016, when the scheduled interchange for the Path was not correct at the start of the following hour, and ended at 09:13 on August 11, 2016, when IPCO’s NSI was brought under the SOL for the following hour; for a total of 13 minutes of noncompliance. In the second instance, IPCO reported that on October 7, 2016, Path schedules exceeded the SOL from 06:24 to 07:14. Initially, there was a planned outage reducing the Total Transfer Capability (TTC) on the Path from its normal 2,557 MW to 1,987 MW. Then the Path was further reduced to 1,515 MW due to switch work. At 06:24 the Path experienced an unplanned event, which caused the TTC to drop from 1,515 MW to 850 MW, because of a transformer differential at Midpoint Substation. At 06:27, IPCO's Interchange Operator called PAC to inform them that their share on the Path would be reduced from 646 MW to 362 MW, because of the transformer differential. At 06:49, IPCO’s Interchange Operations called PAC to notify them that the appropriate curtailments had not been made; PAC replied that they were working on it. At 07:11, IPCO’s Interchange Operations called PAC again notifying them that their allocation would remain at 362 MW for the next hour as well. At 07:15 IPCO’s planning study raised the SOL up to 1124 MW. The root cause of both issues was a lack of a formalized operating procedure for IPCO’s System Operators to cover schedule reductions following the asset swap with PAC and associated changes in operating procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, IPCO failed to have NSI for power flow under transmission the Path SOL rating when the Transmission Operator implemented its real-time scheduled for the next hour. Such failure could result in voltage instability, overloaded transmission lines, and damage to equipment. However, in the first instance, actual flows on the Path were reduced to below the new limits within 30 minutes, as required. In the first instance, schedules were below the new limits three minutes after the end of the schedule ramp (09:10) for Hour Ending (HE) 10:00. Therefore, for the majority (47 minutes) of HE 10:00, schedules were under the stated limit of 800 MW. In the second instance, although the NSI flow was scheduled above limit, the Real-Time actual flows on the Path never exceeded the limit. Additionally, by contacting PAC, IPCO took appropriate measures to reduce the scheduled flows. In each instance, the duration of this issue was short, the exceedance was based on scheduled flows, and no Real-Time exceedance occurred. No harm was known to have occurred. | To remediate and mitigate this issue, IPCO: a. Brought the NSI under the SOL for the following hour for both instances; b. Documented a formal operating procedure to cover curtailments on the Path; and c. Trained its operators on the new procedure.
2017-02-28 | Northeast Power Coordinating Council (NPCC) | Danskammer Energy, LLC (DE) | NCR11487 | NPCC2017016765 | MOD-025-2 | R2 | On January 12, 2017, DE submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-1 R2. A new director of NERC compliance was hired by DE after the July 1, 2016 implementation date of MOD-025-2. The new director reviewed the facility's compliance program and noted that a gap existed between the Reactive Power capabilities that were being reported by DE to the New York Independent System Operator (NYISO), and the capabilities required by MOD-025-2 Attachment 1. Specifically, DE had been reporting Lagging vars at maximum load and Leading vars at minimum load. It had not been reporting Lagging vars at minimum load and Leading vars at maximum load. The duration of the noncompliance was from July 1, 2016, the enforceable date of MOD-025-2, to October 11, 2016, when the Reactive Power capability testing was completed on both of DE's generating units. The cause of this noncompliance was DE believing that by completing the NYISO testing requirements, it was meeting all of the requirements of MOD-025-2. When the new NERC compliance director was hired, he noticed the gap between the testing requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DE submitted the correct Reactive Power capability of its two generating units to the NYISO within 120 days of the enforceable date of the MOD-025-2 standard. The DE generating site consists of two units with a combined capability of 134 MW and has no blackstart capability. The noncompliance had no actual effect on the BPS, as the data collected is used for modeling purposes by the Transmission Operator. DE had previously been performing and reporting Reactive Power capability testing for the NYISO twice a year in the Winter and the Summer and had believed that this testing had met the requirements of MOD-025-2. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered DE's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, DE: 1) Performed all of the required Reactive Power capability testing on both generating units and reported the information to the NYISO; and 2) Will verify that all future Reactive Power capability testing to be reported to the NYISO meets the requirements of MOD-025-2. NPCC has verified the completion of all mitigation activity.
2017-02-28 | Northeast Power Coordinating Council (NPCC) | CMEEC - Alfred L. Pierce Power Station (CMEEC) | NCR10357 | NPCC2016016301 | PRC-005-2(i) | R3. | During a Compliance Audit conducted from July 15, 2016 through September 20, 2016, NPCC determined that CMEEC, as a Generator Owner, had an issue of PRC-005-2(i) R3. CMEEC did not perform the measurement of internal resistances within six months. The test was to be completed by October 1, 2015 but the test was performed on April 1, 2016. CMEEC had mistakenly identified the batteries to have internal resistance monitoring. CMEEC had continued to perform its normal maintenance of the PRC-005 Protection System maintenance plan (PSMP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Other tests that were performed, including individual cell voltages measurements and monitoring of the charger float voltages, would have indicated a failure of an individual cell in a similar way to the measurement of internal ohmic cell values. The CMEEC Power Station has a nominal winter rating of 95 MW and a nominal summer rating of 80 MW. The high side voltage is 115 kV and the low side voltage is 13.8 kV. No harm is known to have occurred as a result of this instance of non-compliance. NPCC considered CMEEC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, CMEEC: 1) performed battery testing; 2) updated work orders for periodic battery maintenance; 3) updated the PSMP detailing last and future battery testing dates; and 4) performed one interval of battery testing using the updated PSMP. NPCC has verified the completion of all mitigation activity.
2017-02-28 | Northeast Power Coordinating Council (NPCC) | Public Service Company of New Hampshire (PSNH) | NCR07203 | NPCC2016015916 | PRC-023-3 | R1 | During an On-Site Audit conducted from June 21, 2016 through June 22, 2016, NPCC determined that PSNH, as a Transmission Owner, had an issue related to standard PRC-023-3 R1. PSNH had self-identified this potential issue to NPCC after being notified of the impending Audit. This issue started on November 21, 2014, when the protection relay for a 230 kV circuit was commissioned into service with the load encroachment function incorrectly left disabled, and ended on April 5, 2016, when PSNH's Test Department enabled the load encroachment setting for the above relay (in observance of Criterion 1), thus establishing compliance with Requirement 1 of the standard. The root cause of this instance of noncompliance was human error, as both the engineer who developed the relay protection setting and the engineer who conducted a subsequent review of the installation failed to enable the required load encroachment function. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Upon discovery, PSNH informed ISO New England of the situation and discussed with them the potential impact on system reliability of this instance of noncompliance. Although the protection relay for the 230 kV circuit was incorrectly set to limit loadability of this line, two studies, independently conducted, one by ESCC (the Electric System Control Center, which is the Eversource transmission control center responsible for New Hampshire - a NERC-registered TOP function) and the other by PSNH's Protection Control & Engineering Department, concluded that this issue would have had a minor impact on system performance without causing uncontrolled cascading overloads under peak load conditions and N-1-1 contingency events. Therefore, this instance of noncompliance represents a minimal risk to the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered PSNH's compliance history and determined there are no relevant instances of noncompliance. | To mitigate this issue, PSNH: 1) enabled the load encroachment function in observance of Criterion 1, per R1 of the standard; 2) completed a Lesson Learned document documenting the cause of noncompliance; and 3) raised awareness of the issue by distributing the above document to appropriate Eversource personnel and non-Eversource P&C Vendors. NPCC has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Constellation Maryland Peaker Fleet (Constellation) | NCR11216 | RFC2016016318 | PRC-001-1.1(ii) | R1 | On October 4, 2016, ReliabilityFirst determined that Constellation, as a Generator Operator, had an issue of PRC-001-1.1(ii) R1 as a result of a Compliance Audit conducted from April 19, 2016 through May 2, 2016. Constellation failed to demonstrate that its operators are familiar with the purpose and limitations of Protection System schemes as applied to its generating facilities. During the Compliance Audit, Constellation provided the Audit Team a copy of the training on Protection System schemes that Constellation uses to train its operators. The latest training records for Constellation’s operators were dated from the summer of 2012. The Audit Team reviewed the training and found that the training did not address many of the relay schemes associated with generators. The Audit Team decided to interview one of the system operators based on the quality of the training and the date of the last training. The Audit Team prepared a series of questions and expected responses to use to determine the operator's familiarity with the purpose and limitations of Protection System schemes. Constellation provided one operator out of the eight operators for the Audit Team to interview. The Audit Team used the prepared questions and based on the operator’s responses, the Audit Team determined that the operator did not present a good understanding of the purposes and limitations of Protection System schemes as they relate to Constellation’s generators. For the relay schemes that he was questioned about, the operator did not know the purpose of several relay schemes that are used for generators and did not identify any limitations to any of the relay schemes. This lack of familiarity violates PRC-001-1.1(ii) R1. This noncompliance involves the management practice of workforce management because the Constellation operator that was interviewed to determine Constellation’s compliance with PRC-001-1.1(ii) R1 did not demonstrate that he was familiar with the purpose and limitations of Protection System schemes as applied to Constellation’s generating facilities. The root cause of this noncompliance is ineffective training because Constellation failed to properly train its operator on the purpose and limitations of Protection System schemes. Constellation determined that its training module did not fully cover common relay schemes associated with generators. Constellation also determined that it should conduct the training with its operators more frequently so they can better retain familiarity with the purpose and limitations of Protection System schemes. This issue started on May 29, 2015, when Constellation was required to comply with PRC-001-1.1(ii) R1, and will end on April 7, 2017, when Constellation committed to complete its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk that comes from this noncompliance is an unexpected loss of generation and potential damage to generating equipment because Constellation operators are not familiar with the purposes and limitations of Protection System schemes as they relate to Constellation’s generators. That risk is minimized because the facilities that Constellation operates are peaking units and do not represent a large amount of generation capacity. The units for which the operators are responsible are small peaking plants ranging from 21 to 135 MVA. Constellation operating personnel are also required to engage engineering when a significant issue arises at the generating unit. The inclusion of an additional situational review after making the area safe and before restoration reduces the risk of damage to the generating unit. The additional support provided by engineering further reduces the risk posed by any lack of knowledge by operating personnel regarding the Protection Systems in use. No harm is known to have occurred. ReliabilityFirst considered Constellation’s PRC-001 R1 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, Constellation: 1) obtained feedback from the plant technical and operations managers to get an understanding of where or if there are any specific protection systems at the Exelon Power generating stations; 2) reviewed the current Learning management system (LMS) web-based training module with Corporate Engineering Subject Matter Experts for updates and recommendations; 3) revised the LMS web-based training module; 4) set a due date for initial completion within 30 days of training upload for Constellation generating plan personnel and 3 months for all Exelon generating fleet personnel; and 5) updated the training frequency from one time to annually. Constellation will complete the following mitigation activities by April 7, 2017: 1) will confirm Constellation generating plan personnel have completed the initial training within the first 30 business days of 2017; and 2) will confirm all Exelon Power-Generation plant personnel have completed the initial training by the end of the first quarter of 2017 A significant amount of time is needed to complete this Mitigation Plan because Constellation is retraining all Exelon Power-Generation personnel and there are a lot of personnel in that group. Constellation was also unable to start retraining individuals until the training was properly revised and that further explains the length of time needed to complete this Mitigation Plan.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Handsome Lake Energy, LLC (Handsome Lake) | NCR00793 | RFC2016016317 | VAR-002-4 | R2 | On October 3, 2016, Handsome Lake submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue of VAR-002-4 R2. On May 25, 2016, after reviewing Process Book Information for Handsome Lake, Exelon Generation identified a potential voltage schedule issue at Handsome Lake. The issue occurred on May 22, 2016 with Handsome Lake Unit 4 during off-peak hours. Beginning at 11:10 PM on May 21, 2016 and continuing through 03:00 AM on May 22, 2016, the voltage at the switchyard bus for Handsome Lake Unit 4 was 4 kV higher than the voltage schedule set by Handsome Lake’s Transmission Owner (FirstEnergy). This is a small deviation above the 355 kV upper bound of Handsome Lake’s voltage schedule and is still within the default voltage values set by PJM in PJM Manual 3. At the time the issue occurred, PJM was in a High System Voltage Event, meaning voltage was high across the entire PJM System. For the duration of the issue, Handsome Lake Unit 4 was operating as a Tier 2 Synchronized Reserve Resource in PJM, meaning it was operating in standby mode and ready to be called on to generate megawatts (MWs) if needed. During the noncompliance, Handsome Lake Unit 4 was not called on as a reactive resource or asked to generate MWs. For approximately 4 hours, Handsome Lake deviated from its voltage schedule and did not notify FirstEnergy of its deviation. Handsome Lake personnel were not aware that they needed to notify FirstEnergy of this deviation while Handsome Lake Unit 4 was operating as a Tier 2 Synchronized Reserve Resource and were not continuously monitoring Unit 4’s voltage. This noncompliance involves the management practice of workforce management because Handsome Lake personnel were not aware that they needed to notify FirstEnergy of a voltage schedule deviation while Unit 4 was operating as a Tier 2 Synchronized Reserve Resource. Handsome Lake personnel were also not continuously monitoring Unit 4’s voltage during the noncompliance. The root cause of this noncompliance is ineffective training because Handsome Lake personnel were not properly trained on when and how to make the proper notifications. This issue started on May 21, 2016, when the voltage at the switchyard bus for Handsome Lake Unit 4 was 4 kV higher than the voltage schedule set by FirstEnergy, and ended on May 22, 2016, when the voltage at the switchyard bus for Handsome Lake Unit 4 dropped back down into compliance with its voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential harm that comes from a GOP letting its voltage run too high above its voltage schedule is equipment failure (such as the breakdown of insulation) that comes from prolonged periods of high voltage. In this instance, it is very unlikely that this potential harm would be realized because the observed deviation was only 4 kV beyond the voltage schedule, and at 359 kV was still within the default voltage values set by PJM in PJM Manual 3. The deviation also occurred for a short amount of time, approximately 4 hours, and only impacted one of the five units at Handsome Lake. Furthermore, Handsome Lake’s Automatic Voltage Regulator (AVR) remained in service. Unit 4 was operating as a Tier 2 Synchronized Reserve Resource and serving as a reactive resource and absorbing -6 VARS from PJM’s system to try to help lower the high voltage across the PJM system. PJM was already in a High System Voltage Event for the duration of this noncompliance, which shows that all necessary parties, including PJM, were aware of the increased voltage on the system. Handsome Lake also detected this issue within four days of its occurrence which shows that its detective controls are functioning properly. Lastly, Handsome Lake Unit 4 was taken offline at 03:00 AM, and the voltage remained slightly above the schedule at the switchyard but did not adversely impact the operation of Handsome Lake or other Bulk Power System operations. No harm is known to have occurred ReliabilityFirst considered Handsome Lake's VAR-002 R2 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, Handsome Lake: 1) reviewed with Operating personnel during Plan of the Day (POD) meetings, the requirement to notify the Transmission Operator when Handsome Lake is operating outside the voltage schedule regardless of how a unit is being dispatched (generation, Synchronous Condenser, or Tier 2 spinning Reserve); 2) mirrored the 345 KV high side voltage monitoring to a 24-hour manned monitoring station. Handsome Lake will now be continuously monitoring all of its unit’s voltage schedules even when a unit is operating as a Tier 2 Synchronized Reserve Resource; and 3) developed an alarming system using the Plant Process Information System (PI) that will alarm at the 24-hour manned monitoring station with the potential to send an email notification to a designated party for reporting. The alarm will notify the personnel at the station when any of the Handsome Lake units deviate from their voltage schedule.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | ITC Transmission (ITCT) | NCR00803 | RFC2016015712 | PRC-023-3 | R1 | On April 28, 2016, ITCT submitted a Self-Report to ReliabilityFirst stating that as a Transmission Owner, it had an issue with PRC-023-3 R1. When creating the relay settings for a new three-terminal 345 kV transmission line, an engineer correctly documented the relay “A” settings (including enabling load encroachment) in a spreadsheet later used to apply the settings. However, when copying the settings for relay “B,” the engineer incorrectly did not enable load encroachment as he should have done. ITCT then applied the settings, thus resulting in the B relay trip setting being lower than A (when they should have been identical). When the engineer later calculated the relay trip settings for relays A and B pursuant to PRC-023-3, the engineer did so using the information for A, assuming it was identical to B. Thus, the trip limit for relay B was incorrect, and, consequently, the Facility Rating was incorrect as well. ITCT put the line into service on December 8, 2015 and issued the new Facility Rating on December 16, 2015. On April 6, 2016, ITCT identified the issue while preparing evidence for its PRC-023 self-certification. Upon identification on April 6, 2016, ITCT fixed the issue. The root causes were an error in manually copying the relay settings from relay A to relay B and lack of verification management practices in that ITCT did not have a control to ensure the settings were entered correctly. Since the time of the noncompliance, ITCT has implemented, in addition to other mitigation steps, a peer review of relay settings, including a specific step to identify differences between A and B relays. ITCT has since reviewed all relay settings to ensure compliance and did not find additional similar instances. This issue started on December 8, 2015, when ITCT implemented an incorrect relay trip limit, and ended on April 6, 2016, when ITCT corrected the relay trip limit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk from a PRC-023-2 R1 violation is that the relay could trip too early and thus interfere with the system operator’s ability to take remedial action to protect system reliability. However, this risk was mitigated by the following factors. This issue was limited to a single transmission line as opposed to impacting multiple transmission lines. Additionally, because the issue occurred on a three-terminal line, even if the relay tripped too early as a result of not having load encroachment enabled, only one end of the line would trip (e.g. loss of one 345 kV facility). (Three-terminal lines are used to supply loads from three power sources — Terminals A, B, and C. See The Complexity of Protecting Three-Terminal Transmission Lines, North American Electric Reliability Counsel, page 24, for an illustration of a three-terminal line. Because of the unique configuration of three-terminal lines, a line fault will immediately result in tripping of all three terminal breakers, initiate automatic sectionalizing of the faulted line, and then restore the un-faulted line sections by reclosing the associated terminal breakers.) And, ITCT’s planning studies have not identified this contingency to cause any system issues. It is also noteworthy that throughout the duration of the noncompliance, loading never exceeded 387.5 amps, which was only 16.3 percent of the relay’s tripping limit, and thus there was no potential for loss of the facility as a result of the incorrect trip setting and Facility Rating. No harm in known to have occurred. ReliabilityFirst considered ITCT's PRC-023 R1 compliance history in determining the disposition track. ITCT’s relevant prior noncompliances with PRC-023 R1 include: a. RFC2014013450 (METC). A Compliance Exception addressing a noncompliance with PRC-023-2 R1 was posted on the NERC website on October 29, 2015. In the prior noncompliance, there were incorrect relay settings as a result of the sampling method METC used to ensure its relays were compliant when PRC-023 R1 initially became effective. The noncompliance is distinguishable from the current violation, which involves an error in manually copying the relay settings from relay A to relay B in relation to construction of a new transmission line. b. RFC2015014788 (METC). A Compliance Exception addressing a noncompliance with PRC-023-3 R1 was posted on the NERC website on October 29, 2015. In the prior noncompliance, METC raised the Facility Rating of a line as a result of construction work that increased the line’s sag limit, but METC failed to increase the relay trip setting, resulting in a relay trip setting that was two percent under the limit set forth in PRC-023-3 R1. The noncompliance occurred as a result of an employee manually bypassing a control that notifies METC if a rating is about to be published not in compliance with PRC-023. This is distinguishable from the current noncompliance because, unlike the prior noncompliance, the employee in the current noncompliance intended to revise the relay setting, but made an error in completing that task. ReliabilityFirst determined that the compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, ITCT: 1) implemented a peer review step for all relay setting changes; 2) fixed the relay setting at issue; 3) included a peer review with respect to Facility Ratings; 4) implemented technical controls in the Excel relay setting tool to visibly identify missing Facility Rating or non-compliant settings; 5) defined the scope and began development of a tool to identify differences between A and B relays, auto-generate permissible relay loadability data, and verify compliance with PRC-023; and 6) implemented the tool to identify differences between A and B relays, auto-generate permissible relay loadability data, and verify compliance with PRC-023.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | ITC Transmission (ITCT) | NCR00803 | RFC2016015935 | FAC-008-3 | R6 | On July 18, 2016, ITCT submitted a Self-Report to ReliabilityFirst stating that as a Transmission Owner, it had an issue with FAC-008-3 R6. When creating the relay settings for a new three terminal 345 kV transmission line, an engineer correctly documented the relay “A” settings (including enabling load encroachment) in a spreadsheet later used to apply the settings. However, when copying the settings for relay “B,” the engineer incorrectly did not enable load encroachment as he should have done. ITCT then applied the settings, thus resulting in the B relay trip setting being lower than A (when they should have been identical). When the engineer later calculated the relay trip settings for relays A and B pursuant to PRC-023-3, the engineer did so using the information for A, assuming it was identical to B. Thus, the trip limit for relay B was incorrect, and, consequently, the Facility Rating was incorrect as well. ITCT put the line into service on December 8, 2015 and issued the new Facility Rating on December 16, 2015. On April 6, 2016, ITCT identified the issue while preparing evidence for its PRC-023 self-certification. Upon identification on April 6, 2016, ITCT fixed the issue. The root causes were an error in manually copying the relay settings from relay A to relay B and lack of verification management practices in that ITCT did not have a control to ensure the settings were entered correctly. Since the time of the noncompliance, ITCT has implemented, in addition to other mitigation steps, a peer review of relay settings, including a specific step to identify differences between A and B relays. ITCT has since reviewed all relay settings to ensure compliance and did not find additional similar instances. This issue started on December 16, 2015, when ITCT issued the incorrect Facility Rating, and ended on April 6, 2016, when the Facility Rating was corrected. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The potential risk of applying a Facility Rating that is more conservative than necessary is that the system operator would have less time than they otherwise would to take remedial action to protect system reliability. This issue was limited to a single transmission line as opposed to impacting multiple transmission lines. Additionally, because the issue occurred on a three-terminal line, even if the relay tripped too early as a result of not having load encroachment enabled, only one end of the line would trip (e.g. loss of one 345 kV facility). And, ITCT’s planning studies have not identified this contingency to cause any system issues. It is also noteworthy that throughout the duration of the noncompliance, loading never exceeded 387.5 amps, which was only 16.3 percent of the relay’s tripping limit, and thus there was no potential for loss of the facility as a result of the incorrect trip setting and Facility Rating. No harm is known to have occurred. ReliabilityFirst considered ITCT's FAC-008 R6 compliance history in determining the disposition track. ITCT’s relevant prior noncompliances with FAC-008 R6 include: a. RFC2011001174 (METC). A Find, Fix and Track Report (FFT) informational posting addressing a noncompliance with FAC-009-1 R1 was posted on the NERC website on September 28, 2012. In the prior issue, ITCT and METC failed to revise its Facility Ratings for three transformers. The Facility Ratings were consistent with the prior Facility Ratings Methodology, but ITCT and METC failed to revise the Facility Ratings pursuant to a revised methodology effective in March, 2010. The current noncompliance is distinguishable from the prior issue in that the current noncompliance does not relate to a failure to apply a revised Facility Ratings Methodology. Rather, the current noncompliance involves an error in manually copying the relay settings from relay A to relay B in relation to construction of a new transmission line. b. RFC2011001324 (ITCT). A Find, Fix and Track Report (FFT) informational posting addressing a noncompliance with FAC-009-1 R1 was posted on the NERC website on September 28, 2012. RFC2011001324 involves the same facts as RFC2011001174, which is discussed in the previous paragraph, and is thus likewise distinguishable from the current noncompliance. ReliabilityFirst determined that the compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, ITCT: 1) implemented a peer review step for all relay setting changes; 2) fixed the setting in Milan CQB_REL; 3) implemented technical controls in the Excel relay setting tool to visibly identify missing Facility Rating or non-compliant settings which triggers a review of the limiting element; 4) defined the scope and began development of CAPE macro to identify differences between A and B relays and auto-generate permissible relay loadability data; 5) implemented CAPE macro to identify differences between A and B relays and auto-generate permissible relay loadability data. ReliabilityFirst has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | MEG Generating Company, LLC (MEG Genco) | NCR00838 | RFC2016016355 | PRC-005-1.1b | R2 | On October 6, 2016, MEG Genco submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. Shortly after MEG Genco became part of Talen Energy in 2015, several PRC-005 violations related to missed component test intervals were identified at the MEG Genco facilities. Those violations were self-reported to ReliabilityFirst in August 2015 and a mitigation plan was later submitted and completed. Following completion of the 2015 PRC-005 Mitigation Plan, MEG Genco discovered that its Newark Bay facility did not clearly document the division of responsibility between PSEG (the neighboring Transmission Owner (TO)) and Newark Bay for PRC-005 compliance testing of the various devices related to the facility's electrical interconnection. This ambiguity existed for a number of reasons, including: (1) legacy interconnection maintenance practices between the plant and PSEG for PRC-005 devices dating back to when Newark Bay was a PURPA Qualifying Cogeneration Facility; (2) lack of clarity and specificity in information shared between PSEG and the facility related to PRC-005 devices; and (3) personnel turnover at Newark Bay among facility management and NERC compliance personnel. To address this situation, MEG Genco personnel began working with PSEG personnel to resolve the ambiguities and ensure that testing records were in order for PRC-005 devices that are part of Newark Bay's electrical interconnection. While work with PSEG was ongoing, the following two PRC-005 compliance deficiencies were identified. First, MEG Genco did not test seven relays at the required four-year interval at the Newark Bay Facility. The relays were last tested in March, 2010 and were scheduled to be tested again in 2014. The seven relays were not tested again in 2014. Second, MEG Genco did not test its associated communications channel at its Newark Bay Facility at the required four-month interval. MEG Genco did not perform a baseline test in June, 2015 for the associated communications channel. MEG Genco then missed required tests for that associated communications channel in September, 2015 and January, 2016. MEG Genco completed the required test in May, 2016. This noncompliance involves the management practice of verification. MEG Genco personnel did not confirm and document that testing was completed for all applicable relays and the associated communications channel. MEG Genco personnel did not implement a testing schedule upon receiving the proper notification from PSEG and did not understand which personnel were responsible for completing the testing. The root cause of this noncompliance was the lack of an implemented process to ensure that personnel knew what equipment needed to be tested and when after the transition of ownership. This issue started on March 10, 2014, the date MEG Genco missed its first required test, and ended on August 9, 2016, when MEG Genco completed all overdue tests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The potential harm from missing these tests is that a relay misoperates when it should not operate, therefore causing generation to trip off-line or that a relay fails to operate when it should operate thereby exposing the BPS to fault conditions and requiring secondary protection systems and isolation devices to function properly. The potential harm is minimized for four reasons. First, the unit at issue, Newark Bay, only has an installed generating capacity of approximately 120.2 MW which accounts for only 0.3% of the area’s summer peak load. Second, MEG Genco also tested the back-up relays and breakers at Newark Bay that would open if the relays failed to clear the fault, and all were tested successfully. Third, the eight issues involved in this noncompliance equate to 0.7% of the 1,111 total count of devices requiring testing for MEG Genco as a whole. Fourth, the entity has not experienced any protection system misoperations. No harm is known to have occurred. ReliabilityFirst considered MEG Genco's PRC-005 R2 compliance history in determining the disposition track. MEG Genco’s relevant prior noncompliance with PRC-005 R2 includes: RFC2015015155. A Compliance Exception addressing a noncompliance with PRC-005-1 R2 was posted on the NERC website on February 29, 2016. This noncompliance is not distinguishable from the current noncompliance. In the prior noncompliance, MEG Genco did not test certain Protection System components (relays, DC Circuits, and current transformers) in accordance with PRC-005 and MEG Genco’s compliance program because of an error in compiling the lists of protection system devices subject to PRC-005 testing in 2007 that was not discovered until 2015. A total of 79 protection components were not tested across the four MEG Genco facilities in the RF region including: 17 relays, 39 CTs, and 23 DC Circuits. At the time of the prior noncompliance, MEG Genco had a total of 1,077 components and devices that required testing in the RF region. In the current noncompliance, MEG Genco failed to test seven relays and an associated communications channel at the required intervals because MEG Genco did not understand that it was responsible for performing maintenance and testing on those seven relays and the associated communications channel. Although the current noncompliance involves conduct that is arguably similar to the previous noncompliance, the current noncompliance continues to qualify for compliance exception treatment as it involves high-frequency conduct, testing Protection System components, for which MEG Genco has demonstrated an ability to identify, assess, and correct noncompliances. ReliabilityFirst also commends Talen Energy for its rigorous review of MEG Genco’s PRC-005 program after acquiring MEG Genco. ReliabilityFirst determined that MEG Genco’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, MEG Genco: 1) confirmed with PSEG what had been tested and what had not been tested. MEG Genco then tested the seven overdue relays and the associated communications channel at its Newark Bay facility; 2) reviewed all spreadsheets for all interconnection switchyard relays to ensure that the testing was recorded, with reports in hand, and for the proper intervals; 3) met with its TO, PSEG, to review their understanding of what switchyard devices are MEG Genco’s compliance responsibility to ensure both parties have the same understanding; 4) provided PSEG with written documentation of MEG Genco’s understanding regarding its responsibility for such testing and requested that PSEG respond in writing to either confirm MEG Genco’s understanding or identify what changes should be made to the list; 5) reviewed the PRC-005 program Electrical Device spreadsheet for all interconnection switchyard relays to ensure that the testing was recorded, with reports in hand, and for proper intervals; 6) reviewed interconnection agreements and technical drawings for boundary issues and potential missing devices that may be subject to PRC-005; 7) developed, for each plant, a list of components related to the plant’s interconnections/switchyards for which MEG Genco believes the plant is responsible for the PRC-005 testing. MEG Genco provided the applicable TO with written documentation of MEG Genco’s understanding regarding its responsibility for such testing and requested that the TO respond in writing to either confirm MEG Genco’s understanding or identify what changes should be made to the list; and 8) updated tracking spreadsheets to indicate correct ownership of maintenance and testing obligations.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016015940 | BAL-004-0 | R2 | On July 15, 2016, PJM submitted a Self-Report stating that, as an Reliability Coordinator (RC), it had an issue of BAL-004-0 R2. BAL-004-0 incorporates the NAESB Standard WEQ-006-4 by reference, which requires that “notice shall be given at least one hour before the Time Error Correction is to start or stop.” (As background, Interconnection frequency is normally scheduled at 60.00 Hz and controlled to that value. The control is imperfect and over time the frequency will average slightly above or below 60.00 Hz, resulting in mechanical electric clocks developing an error relative to true time. The NAESB Time Error Correction Procedure specifies the procedure to be used for reducing the error to within acceptable limits of true time. During the time error correction, the dispatcher inputs frequency schedule into the EMS system using 59.98 Hz to correct for fast time error or 60.02 Hz to correct for slow time error. The dispatcher resets the frequency to 60.00 Hz at the end of the time error correction.) On April 17, 2016, at 1102 hours, PJM, as the Eastern Interconnection Time Monitor, notified the other Eastern Interconnection RCs that a time error correction was to start at 1200 hours (approximately 58 minutes prior to the commencement of the correction and thus two minutes later than required). Additionally, the time error correction was to end at 2100 hours, but PJM provided such notice at 2009 (approximately 51 minutes prior to the end of the correction and thus nine minutes later than required). The root cause was a lack of workforce management practices in that additional training regarding timing of notices could have prevented the noncompliance from occurring. This issue started and ended on April 17, 2016, when PJM was late in giving notice that a time error correction was to start and stop. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The purpose of the notice is to allow other RCs to make minor adjustments (if any) in their operations in light of the time error correction. Here, PJM notified the other Eastern Interconnection RCs 58 minutes prior to the commencement of the correction (as opposed to the required 60 minutes) and 51 minutes prior to the end of the correction (as opposed to the required 60 minutes). Thus, it was unlikely that these slight delays in notification would have caused neighboring RCs to not have enough time to make the necessary adjustments. No harm is known to have occurred. ReliabilityFirst considered PJM’s BAL-004 R2 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, PJM verbally coached shift supervisors over the period of June 28, 2016 to July 15, 2016 to ensure they understood the need to give at least one hour notice. Additionally, the time requirements are included in PJM’s time error correction procedure and checklist. ReliabilityFirst has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016015936 | BAL-006-2 | R5 | On July 15, 2016, PJM submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue of BAL-006-2 R5. Pursuant to BAL-006-2 R5, for each month that PJM and one or more Adjacent BAs disagree on their Net Actual Interchange or Net Scheduled Interchange quantities by the fifteenth calendar day of the following month, PJM sends ReliabilityFirst a report (in the form of an email) for purposes of dispute resolution. Irrespective of the report, PJM continues to work with its Adjacent BAs to resolve the dispute without ReliabilityFirst’s involvement. Then, once PJM and BAs reach an agreement on the Net Actual and Net Scheduled Interchange numbers, PJM submits the associated information to NERC as required by BAL-006. On May 27, 2016, PJM discovered that it failed to send ReliabilityFirst a report pursuant to BAL-006-2 R5 for disputed information that should have been reported in April 2013. Upon further investigation, PJM identified six additional similar instances from September 2013 through April 2015 where it failed to send the reports to ReliabilityFirst. The root cause was a lack of verification controls to ensure all steps were taken as required when PJM and one or more BAs disagreed on Net Actual Interchange or Net Scheduled Interchange quantities. This issue started on April 15, 2013, the date of the first instance when PJM failed to send a report to ReliabilityFirst under BAL-006-2 R5 and ended on September 16, 2016, when PJM completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The reports required by BAL-006-2 R5 are submitted after a dispute for the purpose of assisting in dispute resolution. The initial report is for notice purposes and the region would only get involved if the BAs were unable to resolve the dispute on their own. Regardless of whether or not the BAs send the initial report, the BAs continue to work together to resolve the dispute and thus not sending the report does not delay a resolution. And, in all cases, PJM worked with the BAs to resolve the disputed numbers and submitted the final agreed numbers via a NERC developed process. PJM's not sending the reports to ReliabilityFirst did not impact the resolution of the disagreements. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. ReliabilityFirst considered PJM’s BAL-006 R5 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, PJM set up a monthly outlook calendar reminder to send ReliabilityFirst an email if there were outstanding disagreements as to respective Net Actual Interchange or Net Scheduled Interchange quantities. PJM also indicated that it provided coaching to staff and shift supervisors to avoid a similar occurrence. ReliabilityFirst has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016015937 | COM-001-2.1 | R4 | On July 15, 2016, PJM submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue of COM-001-2.1 R4. PJM assigns and shares certain TOP tasks with its Member Transmission Owners (TOs). PJM oversees and ensures the completion of these tasks by its Member TOs through certain established controls. For example, PJM has established its PJM TO/TOP Matrix, a document that provides a delineation of responsibility for each assigned or shared TOP task. COM-001-2.1 R4.1 requires PJM, as the TOP, to designate an Alternative Interpersonal Communication capability with its Reliability Coordinator. As the registered TOP in the PJM Region, PJM delegated a portion of this task to its Member TOs. As referenced in PJM Manual 1: Control Center and Data Exchange Requirements, Section 4.2.1, PJM designated satellite phones as its Alternative Interpersonal Communication capability for voice communications. And, PJM Manual 1 requires Member TOs to have satellite phone capabilities at both their primary and back-up facilities. PJM also requires its TOs to designate an Alternative Interpersonal Communication capability for voice communications with PJM as documented in the PJM TO/TOP Matrix, V9.1, assigned task for R4.1. However, PJM, along with one of its TOs, determined that communications via satellite phone was not the most reliable option for that TO. As such, the affected TO, in its COM-001 policy (effective September 30, 2015), designated its cell phone as the Alternative Interpersonal Communication capability for voice communications with PJM. PJM had this policy in its possession and thus had the cell phone number. However, the TO failed to separately communicate to PJM that it designated the cell phone number as the Alternative Interpersonal Communication capability for voice communications with PJM. As a result, PJM failed to specifically designate the cell phone as the Alternative Interpersonal Communication capability for that TO. The root cause was a lack of controls relating to tracking changes to designations for Alternative Interpersonal Communication capabilities. This contributing factor involves the management practice of implementation with respect to having processes in place to ensure that changes are completed. This issue started on April 1, 2016, when PJM should have designated the cell phone as the Alternative Interpersonal Communication capability, and ended on October 8, 2016, when PJM designated the cell phone as the Alternative Interpersonal Communication capability. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The noncompliance was a documentation issue. COM-001-2.1 R4 relates only to an alternative, or backup, method of communication in the event normal communication methods fail. And, PJM’s normal communications methods include multiple methods of communication (and thus PJM already has backups within the normal communications). Here, in the unlikely event the normal mode of communications failed, PJM had the TO’s cell phone number and thus could have communicated with the TO. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. ReliabilityFirst considered PJM’s COM-001 R4 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, PJM obtained the cellular telephone number for the subject TO and amended its telephone testing procedures to include the new telephone number. ReliabilityFirst has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016015938 | EOP-004-2 | R2 | On July 15, 2016, PJM submitted a Self-Report stating that, as a Balancing Authority, Reliability Coordinator, and Transmission Operator (TO), it had an issue of EOP-004-2 R2. PJM's Operating Plan for EOP-004-2 requires Members to provide event information to PJM, who, in turn, reports the events pursuant to EOP-004 R2. On October 7, 2014, at 16:45, a PJM Member TO conducted a walk-through of its substation and determined that there was a hole cut in the fence. The TO contacted local law enforcement and on October 8, 2014, at 14:04, submitted an event report to PJM. PJM determined this to be a reportable event under EOP-004-2 because the event involved suspected/actual intentional human damage. PJM determined that the event was due to be reported no later than October 9, 2014 at 14:04. PJM submitted a report to ReliabilityFirst, NERC, and the Department of Energy on October 9, 2014 at 20:52, several hours beyond the 24 hour window. The root cause was insufficient controls regarding timing of notifications. This contributing factor involves the management practice of external interdependencies, which includes managing communications, such as the reports required by EOP-004-2, with external stakeholders. This issue started and ended on October 9, 2014, when PJM was several hours late in submitting the report pursuant to EOP-004-2 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. PJM was only approximately seven hours late in submitting the report, thus reducing the likelihood that any harm would occur as a result of the slight delay. Second, both PJM and its Member TOs have reporting obligations under EOP-004-2. Thus, here, PJM’s Member TO timely submitted the event report to ReliabilityFirst, NERC, and the Department of Energy. PJM then submitted the same report, albeit several hours late, in an abundance of caution. Thus, the appropriate agencies had awareness of the event. Accordingly, the noncompliance posed only minimal risk to the reliability of the BPS. No harm is known to have occurred. ReliabilityFirst considered PJM’s EOP-004 R2 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue, PJM added a new task to the Dispatch CO-OP manual as a secondary check to ensure PJM submits EOP-004-2 reporting forms as required. ReliabilityFirst has verified the completion of all mitigation activity.
2017-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016015941 | PRC-001-1.1(ii) | R3 | On July 15, 2016, PJM submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue of PRC-001-1.1(ii) R3. On August 1, 2015, Rochelle Municipal Utilities (RMU) integrated into the PJM system as a Member Transmission Owner (TO). At that time, relay settings on one of RMU’s 138 kV lines were set to open the circuit breakers at 47 MVA. During a relay settings review, RMU determined that the relay settings were too conservative. On July 5, 2016, RMU changed the relay settings to 95.6 MVA without notifying PJM or neighboring entities. PJM discovered the issue approximately one week later during its TO/TOP Matrix audit of RMU and immediately resolved the issue by ensuring the new settings were coordinated with neighboring facilities. The root cause was an error by the RMU staff in not following the process. PJM conducted training on this subject at the time RMU integrated, but PJM acknowledged that it would enhance training for these types of tasks as a result of this noncompliance, thus implicating the management practice of workforce management. This issue started on July 5, 2016, when RMU revised the relay setting, and ended on July 13, 2016, when PJM coordinated the revisions with appropriate parties. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Uncoordinated relay changes can create issues where facilities trip in unexpected ways or at unexpected times. Here, the original setting was too conservative and thus the revised setting would result in the line tripping later than the original setting. This is less of a risk than if the relay was changed to trip sooner than expected, which would give the operators less time than expected to react if the line was overloading. Additionally, the line at issue was a 138 kV radial line and thus was less likely to have a negative impact on the coordination of relay protection systems of other facilities. No harm is known to have occurred. ReliabilityFirst determined that PJM’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, PJM: 1) trained RMU protection staff on the PJM Relay Subcommittee procedure on the Coordination of Protection on Shared Facilities; and 2) reviewed the Compliance bulletin on PRC-001.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Buffalo Dunes Wind Project, LLC (Buffalo) | NCR11407 | SPP2016016207 | MOD-025-2 | R1; R1.1 | On September 28, 2016, Buffalo submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Buffalo is a wind farm generating facility with 135 generating units applicable to MOD-025-2. Buffalo did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Buffalo was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Buffalo underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through April 7, 2017, the date Buffalo has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Buffalo is a 249.75 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Buffalo’s violation history and determined that Buffalo has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Buffalo will complete the following mitigation activities by April 7, 2017: 1) complete preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Real Power capability of its generating units; and 3) submit a verification of the Real Power capability of its generating units to the TP within 90 days from the test date.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Caney River Wind Project, LLC (Caney) | NCR11230 | SPP2016016250 | MOD-025-2 | R1; R1.1 | On September 29, 2016, Caney submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Caney is a wind farm generating facility with 111 generating units applicable to MOD-025-2. Caney did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Caney was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Caney underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through July 7, 2017, the date Caney has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Caney is a 199.8 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Caney’s violation history and determined that Origin has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Caney will complete the following mitigation activities by July 7, 2017: 1) complete preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Real Power capability of its generating units; and 3) submit a verification of the Real Power capability of its generating units to the TP within 90 days from the test date.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (Chisholm) | NCR11291 | SPP2016016213 | MOD-025-2 | R1; R1.1 | On September 28, 2016, Chisholm submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Chisholm is a wind farm generating facility with 140 generating units applicable to MOD-025-2. Chisholm did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Chisholm was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Chisholm underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through May 5, 2017, the date Chisholm has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Chisholm is a 235.2 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Chisholm’s violation history and determined that Chisholm has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Chisholm will complete the following mitigation activities by May 5, 2017: 1) complete preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Real Power capability of its generating units; and 3) submit a verification of the Real Power capability of its generating units to the TP within 90 days from the test date.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Goodwell Wind Project, LLC (Goodwell) | NCR11574 | SPP2016016395 | VAR-002-4 | R1 | On October 26, 2016,Goodwell submitted a Self-Certification stating that, as a Generator Operator, it had an issue of noncompliance with VAR-002-4 R1. Specifically, on September 13, 2016, Goodwell performed a routine inspection of its Supervisory Control and Data Acquisition (SCADA) system and discovered that its generators had not been operating in automatic voltage control mode since the last substation maintenance on September 6, 2016. Prior to the maintenance, Goodwell’s maintenance team changed the operation of its generators from automatic voltage control mode to manual mode by disabling the voltage controller. The maintenance team, however, did not return the voltage controller to an enabled state after the inspection was completed. Goodwell restored operation to the automatic voltage control mode on September 13, 2016, but did not inform the Transmission Operator (TOP) that its generators had not been operating in automatic voltage control mode. The duration of this instance of noncompliance was from September 6, 2016, the date the generators ceased operating in an automatic voltage control mode, through September 13, 2016, the date automatic voltage control mode was restored. The root cause of this instance of noncompliance was a combination of Goodwell staff not following Goodwell’s Voltage Verification Procedure and lack of internal controls to ensure the return of automatic voltage control mode after the inspection occurred. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with VAR-002-4 R1 has the potential to affect the reliability of the BPS by preventing a generating facility from responding to system voltage excursions, which could limit the facility’s Transmission Operator's (TOP) ability to respond to system voltage problems. However, in this instance, Goodwell’s voltage set point was maintained during the outage because the plant excitation system defaults to Power Factor Mode of operation, which maintains a Power Factor of 1.0, thus maintaining the terminal voltage equal to the system voltage even when the generators are not operating in automatic voltage control mode. Therefore, Goodwell’s generators did not deviate from the voltage schedule, and no system voltage excursions occurred requiring response from either Goodwell or its TOP. Also, Goodwell is a 200 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. Goodwell has no relevant prior violations for VAR-002-4 R1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, Goodwell: 1) developed new Standard Operating Procedures for voltage control restoration verification after maintenance activities have been performed, specifically for site personnel and Control Room Operators; and 2) trained all affected personnel on the newly developed Standard Operating Procedures. SPP RE has verified the completion of all mitigation activity.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Goodwell Wind Project, LLC (Goodwell) | NCR11574 | SPP2016016241 | MOD-025-2 | R1; R1.1 | On September 29, 2016, Goodwell submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Goodwell is a wind farm generating facility with 100 generating units applicable to MOD-025-2. Goodwell did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Goodwell was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Goodwell underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through June 9, 2017, the date Goodwell has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Goodwell is a 200 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Goodwell’s violation history and determined that Goodwell has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Goodwell will complete the following mitigation activities by June 9, 2017: 1) complete preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Real Power capability of its generating units; and 3) submit a verification of the Real Power capability of its generating units to the TP within 90 days from the test date.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Lea Power Partners, LLC (LEAPP) | NCR10301 | SPP2016016134 | PRC-024-2 | R2 | On September 8, 2016, LEAPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of noncompliance with PRC-024-2 R2. LEAPP is a gas-fired cogeneration power plant with two generating units applicable to PRC-024-2. LEAPP did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the PRC-024-2, through November 16, 2016, the date LEAPP completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was LEAPP’s lack of compliance oversight due to its vacant Director of NERC/FERC Compliance position and failure to provide an adequate substitute. Proper oversight would have ensured coordination of protective relay settings changes with the Transmission Operator and that implementation of the approved changes were complete prior to the effective date of PRC-024-2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, LEAPP is a 604 MW gas-fired cogeneration power plant that is continuously controlled by system operators who monitor system voltage. Additionally, LEAPP attested that this generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024-related issues since May 24, 2012, the commissioning date of the facility. No harm is known to have occurred. SPP RE reviewed LEAPP’s violation history and determined that LEAPP has no prior instances of noncompliance with PRC-024. | To mitigate this minimal risk instance of noncompliance, LEAPP: 1) commissioned a contractor to produce a coordination study and report applicable to PRC-024 R2; 2) commissioned a second contractor to provide an overcurrent protective device coordination analysis/ARC flash mitigation using the suggested changes from the coordination study and report; 3) received approval from the gas turbine generator's manufacturer for the recommended setting changes; 4) received approval from the steam turbine generator's long-term service provider for the recommended setting changes; 5) received confirmation from the Transmission Operator, SPS, that the new settings and coordination are adequate; 6) made all recommended relay setting changes; and 7) received the completed modeling and calculations from its contractor to document compliance with PRC-024 R2. SPP RE has verified the completion of all mitigation activity.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Northeast Texas Electric Cooperative – HCPP (NTEC-HCPP) | NCR11607 | SPP2016015891 | FAC-008-3 | R6 | On July 8, 2016, NTEC-HCPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of noncompliance with FAC-008-3 R6. NTEC-HCPP did not include the 345 kV overhead ACSR conductors from the generator step-up transformer to the Lebrock substation in its facility rating. The Harrison County Power Project is the only facility owned by NTEC-HCPP. The duration of this instance of noncompliance was from January 1, 2016, the date NTEC-HCPP purchased the Harrison County Power Project, through October 24, 2016, the date NTEC-HCPP rated the conductor and entered it into its equipment rating spreadsheet. The root cause of this instance of noncompliance was NTEC-HCPP staff’s failure to recognize that the 345 kV conductor between the generator step-up and the point of interconnection was acquired with the purchase of the HCPP power plant. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to consider the interconnection conductors in determining the HCPP facility rating could have resulted in an incorrect facility rating for the facility. The incorrect facility rating could have resulted in errors in the planning and operational models utilized by the Transmission Operator, Reliability Coordinator, and Planning Authority. It is improbable that a power plant would be constructed with the interconnection conductors limiting the capacity of the facility, and if such a design error had been made, it would have been corrected during commissioning. Including the omitted interconnection conductors in the determination of the facility rating of HCPP did not change the existing HCPP facility rating. No harm is known to have occurred. NTEC-HCPP has no relevant prior violations for FAC-008-3 R6 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, NTEC-HCPP: 1) used the current FAC-008-3 facility rating methodology to rate the ACSR transmission conductor; 2) added the omitted conductors to its equipment rating spreadsheet; and 3) implemented a periodic review schedule to ensure all equipment is properly rated and included in the equipment rating spreadsheet. SPP RE has verified the completion of all mitigation activity.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Origin Wind Energy, LLC (Origin) | NCR11496 | SPP2016016245 | MOD-025-2 | R1; R1.1 | On September 30, 2016, Origin submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Origin is a wind farm generating facility with 75 generating units applicable to MOD-025-2. Origin did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Origin was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Origin underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through June 9, 2017, the date Origin has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Origin is a 150 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Origin’s violation history and determined that Origin has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Origin will complete the following mitigation activities by June 9, 2017: 1) complete preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Real Power capability of its generating units; and 3) submit a verification of the Real Power capability of its generating units to the TP within 90 days from the test date.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Rocky Ridge Wind Project, LLC (Rocky) | NCR11234 | SPP2016016257 | MOD-025-2 | R1; R1.1 | On September 30, 2016, Rocky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Rocky is a wind farm generating facility with 93 generating units applicable to MOD-025-2. Rocky did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Rocky was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Rocky underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 1, 2017, the date Rocky completed its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Rocky is a 148.8 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Rocky’s violation history and determined that Rocky has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Rocky: 1) completed preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conducted tests and verified the Real Power capability of its generating units; and 3) submitted a verification of the Real Power capability of its generating units to the TP.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Farm, LLC (Smoky) | NCR11049 | SPP2016016276 | MOD-025-2 | R1; R1.1 | On September 30, 2016, Smoky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Smoky is a wind farm generating facility with 56 generating units applicable to MOD-025-2. Smoky did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Smoky was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Smoky underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through July 7, 2017, the date Smoky has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Smoky is a 100.8 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Smoky’s violation history and determined that Smoky has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Smoky will complete the following mitigation activities by July 7, 2017: 1) complete preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Real Power capability of its generating units; and 3) submit a verification of the Real Power capability of its generating units to the TP within 90 days from the test date.
2017-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Project II, LLC (Smoky II) | NCR10316 | SPP2016016277 | MOD-025-2 | R1; R1.1 | On September 30, 2016, Smoky II submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with MOD-025-2 R1 and R1.1. Smoky II is a wind farm generating facility with 99 generating units applicable to MOD-025-2. Smoky II did not verify the Real Power capability of its generating units in accordance with Attachment 1 per R1.1. As a result, Smoky II was unable to provide its Transmission Planner (TP) with verification of the Real Power capability of its wind facility per R1. The root cause of this instance of noncompliance was lack of effective workforce management controls, resulting in delayed use of third-party support to conduct the necessary verification tests. Smoky II underestimated the time it would take to assess its internal resources, make a determination to utilize a consultant, and finalize a consultant contract to ensure that the required verification tests would be completed prior to the effective date of the standard. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through May 5, 2017, the date Smoky II has committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with MOD-025-2 has the potential to affect the reliability of the BPS by providing the opportunity for the TP to have inaccurate information about the capabilities of the generating units in planning models used to assess BPS reliability, which could affect identification of adverse reliability impacts in long-term and operating processes. Notwithstanding, Smoky II is a 148.5 MW variable generation wind farm that does not provide reactive power support. No harm is known to have occurred. SPP RE reviewed Smoky II’s violation history and determined that Smoky II has no prior instances of noncompliance with MOD-025. | To mitigate this issue, Smoky II will complete the following mitigation activities by May 5, 2017: 1) complete preparations for testing and verifying the Real Power capability of its generating units by: a. finalizing a contract with the intended technical consultant; b. developing a verification test plan and procedure; and c. coordinating the verification test plan schedule with its Transmission Operator; 2) conduct tests and verify the Real Power capability of its generating units; and 3) submit a verification of the Real Power capability of its generating units to the TP within 90 days from the test date.
2017-02-28 | Texas Reliability Entity (Texas RE) | Exelon Generation Company, LLC (Exelon) | NCR04057 | TRE2016016289 | BAL-001-TRE-1 | R7 | On September 30, 2016, Exelon submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with BAL-001-TRE-1 R7. Specifically, Exelon failed to operate one of its generating units that is connected to the interconnected transmission system with the Governor in service and responsive to frequency when the generating unit was online and released for dispatch. On April 24, 2015, Exelon installed a new turbine Electrohydraulic Control (EHC) system on a single generation unit. The EHC’s frequency response logic acts as the Governor for the unit in question by controlling the unit’s MW output in response to frequency changes. On April 27, 2016, Exelon performed certain troubleshooting activities on the unit at issue. As part of these activities, Exelon had to power down the EHC system. When Exelon did so, however, the primary frequency logic defaulted to “OFF” mode. As a result, Exelon began inadvertently operating the generation unit at issue without its Governor in service. Exelon subsequently discovered the issue when the generating unit failed to adequately respond to three Frequency Measurable Events in June and July 2016. On August 5, 2016, Exelon personnel returned the EHC frequency response logic to “ENABLED” mode, restoring the unit’s Governor to service. The root cause of this issue was inadequate internal controls to alert Exelon personnel that the unit’s Governor was offline. In particular, Exelon personnel were unaware that the EHC’s frequency response logic would default to “OFF” mode during a system reboot and Exelon did not have controls in place to detect such an inadvertent status change. Texas RE determined the issue duration to be from April 27, 2016, when the EHC system was rebooted and the Governor for the unit at issue did not come back into service, until August 5, 2016, when Exelon re-enabled the Governor for the unit at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the generation unit at issue was relatively small, with a maximum output capability of only 122 MW. Second, the ERCOT-wide primary frequency responses to the three frequency measurable events that occurred during the duration of this issue indicated that ERCOT possessed adequate primary frequency response to address system perturbations. Finally, the ERCOT Interconnection possesses several other methods to respond to frequency measurable events, including primary frequency response from units with mechanical governors and Load Resource Under Frequency Relays. No harm is known to have occurred. Texas RE considered Exelon’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Exelon: 1) re-enabled the Governor on the generation unit at issue; 2) added an alarm that will notify its operating personnel when the Governor for the unit at issue goes offline; 3) changed the behavior of the frequency response logic to default to “enabled” when the EHC system is rebooted. Furthermore, Exelon submitted a Mitigation Plan to address the following action that will be completed by February 28, 2017: 1) provide training to applicable Exelon personnel regarding the new Governor alarming function, as well as the required action following an alarm. Exelon needs until February 28, 2017 to complete its mitigation actions in order to finish the operator training on the alarming function indicated above.
2017-02-28 | Texas Reliability Entity (Texas RE) | NAES Corporation - Quail Run Energy Center (NCQREC) | NCR11508 | TRE2016016495 | VAR-002-4 | R3 | On November 7, 2016, NCQREC submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-4 R3. Specifically, NCQREC failed to notify its associated Transmission Operator (TOP) of a change in status of the power system stabilizer (PSS) within 30 minutes. At 9:36 a.m. on September 3, 2016, NCQREC returned the single generation unit to service following an outage. However, in the process of returning the generation unit in question to service, the generation unit’s PSS did not activate. At 10:25 a.m., NCQREC operators identified the issue with the generation unit’s PSS and NCQREC notified its TOP of the PSS status change. The root cause of this issue is that NCQREC possessed inadequate controls to ensure that the PSSs for its generation units either returned to service following an outage or operators could detect such a failure to activate. Specifically, NCQREC lacked specific checks in its startup process to ensure that PSSs returned to service following an outage and also did not possess alarms or other forms of operator notification to detect if PSSs remained offline. The issue duration was from 10:07 a.m. on September 3, 2016, which is 31 minutes after there was a change in status of the PSS for the unit in question, until 10:25 a.m. on September 3, 2016, when NCQREC informed the TOP of the change in status of the PSS. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following four reasons. First, for the duration of the issue, the single generation unit at issue only had approximately 65 MW of output. Second, the duration of the noncompliance was short, lasting only 18 minutes. Third, the affected generation unit’s automatic voltage regulator (AVR) remained in service throughout the duration of the issue, and would have likely operated to mitigate any voltage excursions that could impact the Bulk Electric System (BES) from generator disturbances. Finally, the single affected generation unit’s voltage was stable throughout the duration of the issue. No harm is known to have occurred. Texas RE considered NCQREC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, NCQREC: 1) notified its TOP that the PSS was inactive; 2) implemented a change to the generation unit control screens to show the status of the PSS for all units; 3) installed alarms to notify operators if a PSS is not in service; 4) revised its generation unit startup procedure to ensure that operators note the status of the PSS prior to starting the unit and once it has reached sufficient load that the PSS should be active; and 5) posted instructions to remind generation unit operators to both perform specific prestart checks to ensure the PSS is ready for operation and check to ensure the PSS is in service at specific points of output. Texas RE verified completion of NCQREC's mitigating activities.
2017-02-28 | Texas Reliability Entity (Texas RE) | Signal Hill Generating LLC (Signal Hill) | NCR11202 | TRE2016016459 | PRC-024-2 | R1 | On November 2, 2016, Signal Hill submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-024-2 R1. Specifically, Signal Hill failed to set its frequency protective relays such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1. In June 2016, Signal Hill hired a third-party consultant to perform testing to verify that the settings on its frequency protective relays were not set to trip within the designated “no trip zone” for the ERCOT region at a single generation Facility. The resulting study indicated that the Signal Hill generation Facility’s under frequency relay settings would need to be adjusted. Although Signal Hill personnel were aware of the need to perform the necessary relay setting adjustments, the Signal Hill personnel in question did not understand that the actual setting adjustments needed to be performed prior to PRC-024-2’s July 1, 2016 enforcement date. Signal Hill discovered the issue during its annual NERC compliance review in early October 2016. On October 13, 2016, Signal Hill performed the necessary frequency protective relay setting adjustments. The root cause of this instance of noncompliance was an inadequate process to ensure compliance with all aspects of newly applicable NERC Reliability Standards. Specifically, Signal Hill mistakenly believed that it only needed to perform testing on its frequency protection relays and not also implement any necessary relay setting adjustments by the July 1, 2016 enforcement date. The issue duration was from July 1, 2016, when PRC-024-2 R1 became effective, until October 13, 2016, when Signal Hill set its generation frequency protection relays to be compliant with PRC-024-2 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, the single Signal Hill generation Facility at issue is a small, 80 MW generator that runs infrequently as a quick start and peaker unit. Second, the duration of the issue was relatively short, lasting only 3 months. Finally, there are no known instances in which the Facility experienced a frequency trip due to the settings being within the no trip zone during the duration of the issue. No known harm is known to have occurred. Texas RE reviewed Signal Hill’s violation history and determined that Signal Hill has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Signal Hill: 1) reset the applicable generation frequency protective relay settings and verified that these settings were in compliance with PRC-024-2; 2) provided information to appropriate management and compliance personnel regarding the specific requirements of PRC-024-2 Standard; 3) engaged an outside NERC compliance contractor to ensure compliance with other affected PRC Standards; and 4) scheduled an action item in its compliance tracking system to remind Signal Hill personnel to conduct an annual review of PRC-024-2 compliance requirements, including generation frequency protective relay settings. Texas RE verified completion of Signal Hill's mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Alta Wind VIII, LLC (ALTA) | NCR11258 | WECC2016016378 | FAC-008-3 | R2 | On October 19, 2016, ALTA submitted a Self-Certification stating that as a Generator Owner, it had a possible issue of noncompliance with FAC-008-3 R2. Specifically, when ALTA revised its documentation for Facility Ratings methodology in preparation for Version 3 of the Standard, it failed to transfer all requisite information into the revised documentation. This issue began January 1, 2013, when the current version of the Standard became mandatory and enforceable to ALTA, and ended October 24, 2016, when ALTA revised its documented Facility Ratings methodology, for a total of 1,392 days of noncompliance. The root cause of this issue was less than adequate documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, ALTA failed to document its Facility Ratings methodology as prescribed by R2. Such failure could result in determination and designation of inaccurate Facility Ratings. However, this issue only concerned documentation. Although ALTA failed to document Facility Ratings methodology, it used acceptable methodology to establish Facility Ratings. Additionally, this issue concerned a single location with Facilities corresponding to 150 MW of generation; had this issue resulted in determination and designation of inaccurate Facility Ratings, the risk to the Bulk Power System would still have been limited. No harm was known to have occurred. ALTA does not have previous violations of this Standard and Requirement. | To mitigate this issue, ALTA revised its documented Facility Ratings methodology. WECC verified completion of ALTA’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2016016298 | BAL-001-2 | R2 | On October 3, 2016, AZPS submitted a Self-Report stating that as a Balancing Authority, it had a possible issue of noncompliance with BAL-001-2 R2. Specifically, AZPS reported that on September 5, 2016, while reducing load from peak hours, AZPS’s Reporting Area Control Error (ACE) exceeded the high Balancing Authority ACE Limit (BAAL) for 31 consecutive clock-minutes. AZPS discovered this issue during an internal review the following day. The root cause of this issue was less than adequate post-maintenance testing; an alarm that would have alerted AZPS’s operators within two minutes of this issue had been unintentionally silenced following an Energy Management System (EMS) change on July 14, 2016. This issue began and ended September 5, 2016, when AZPS’s Reporting ACE exceeded its BAAL for one minute beyond the timeframe permitted by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, AZPS failed to operate such that its Reporting ACE did not exceed its BAAL for 31 consecutive clock-minutes. Such failure could result in a frequency excursion beyond defined limits. However, during the period in question, AZPS operators were continuously aware of both the Reporting ACE and frequency, and were actively reducing generation to resolve the exceedance. AZPS discovered, resolved, and reported this issue timely. No harm is known to have occurred. AZPS does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, AZPS: 1) resolved the exceedance; 2) restored the two-minute alarm function in its EMS; 3) added BAAL limit numbers to the main operating screen to improve and maintain visibility of both the BAAL and Reporting ACE; 4) performed an extent of condition analysis to verify that no other issues of this nature occurred between the EMS change and the start date of this issue; and 5) notified operators of lessons learned. WECC verified completion of AZPS’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Cowlitz County PUD No. 1 (COWPD) | NCR05123 | WECC2016016120 | MOD-025-2 | R1 | On September 7, 2016, COWPD submitted Self-Reports stating that as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 R1. Specifically, COWPD reported that it failed to verify the Real Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of COWPD’s generating units, and ended November 8, 2016, when COWPD tested both of its units. The root cause of this issue was COWPD's misunderstanding of the enforceable date of this Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, COWPD failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as COWPD tested both of its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The combined capacity of both units is approximately 90 MVA. No harm is known to have occurred. COWPD does not have previous violations of this Standard and Requirement. | To mitigate this issue, COWPD: 1) tested both units; and 2) created a compliance reminder to verify the Real Power capability of the units prior to the five-year interval prescribed by Attachment 1. WECC verified completion of COWPD’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Cowlitz County PUD No. 1 (COWPD) | NCR05123 | WECC2016016121 | MOD-025-2 | R2 | On September 7, 2016, COWPD submitted Self-Reports stating that as a Generator Owner, it had possible issues of noncompliance with MOD-025-2 R2. Specifically, COWPD reported that it failed to verify the Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of COWPD’s generating units, and ended November 8, 2016, when COWPD tested both of its units. The root cause of this issue was COWPD's misunderstanding of the enforceable date of this Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, COWPD failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as COWPD tested both of its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The combined capacity of both units is approximately 90 MVA. No harm is known to have occurred. COWPD does not have previous violations of this Standard and Requirement. | To mitigate this issue, COWPD: 1) tested both units; and 2) created a compliance reminder to verify the Reactive Power capability of the units prior to the five-year interval prescribed by Attachment 1. WECC verified completion of COWPD’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | High Desert Power Project, LLC (HDPP) | NCR05184 | WECC2016016210 | PRC-019-2 | R1 | On September 26, 2016, HDPP submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, HDPP reported that it failed to coordinate voltage regulating system controls with equipment capabilities and Protection System device settings for at least 40 percent of its applicable Facilities by the effective date of the Standard. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of HDPP’s applicable Facilities, and ended December 6, 2016, when HDPP changed settings on applicable Facilities in accordance with the coordination items described in R1.1.1 and R1.1.2, for a total of 158 days of noncompliance. The root cause of this issue was a misinterpretation of the Standard’s implementation date; HDPP believed changes identified during testing could be completed up to 90 days after the implementation deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, HDPP failed to coordinate at least 40 percent of its applicable Facilities in accordance with R1. Such failure could result in over-voltage damage to HDPP’s applicable Facilities, or unnecessary trip of a generator during a system event that should not cause a generator to trip. However, the likelihood of the above-mentioned circumstances is limited due to operating constraints. HDPP follows a voltage schedule set by its Transmission Operator, which maintains voltage below the physical limits of HDPP’s applicable Facilities. Additionally, the minimum steady state operating limit of HDPP’s generators is only achieved during unit startup and shutdown. No harm is known to have occurred. HDPP does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, HDPP: 1) modified settings and completed coordination for all applicable Facilities in accordance with the Standard; and 2) established automated task reminders to ensure future coordination will be performed per the five-year interval of the Standard. WECC verified completion of HDPP’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Inland Empire Energy Center LLC (IEE) | NCR10267 | WECC2016016331 | PRC-019-2 | R1 | On October 8, 2016, IEE submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, IEE reported that it failed to verify coordination of voltage regulating system controls with equipment capabilities and Protection System device settings for at least 40 percent of its applicable Facilities by the effective date of the Standard. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for at least 40 percent of IEE’s applicable Facilities, and ended August 9, 2016, when IEE verified requisite coordination for all applicable Facilities. The root cause of this issue was a misunderstanding regarding the effective date of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, IEE failed to verify coordination items prescribed by R1.1.1 and R1.1.2 by the implementation deadline for 40 percent of its applicable Facilities. Such failure could result in over-voltage damage to IEE’s applicable Facilities, or unnecessary trip of a generator during a system event that should not cause a generator to trip. However, this issue was limited to the timeliness of IEE’s verification. IEE did not identify any required setting changes, and no harm is known to have occurred. IEE does not have previous violations of this Standard and Requirement. | To mitigate this issue, IEE: 1) completed requisite verification for both of its applicable Facilities; and 2) created automated notifications and reminders to ensure future verification is performed within a five-year interval. WECC verified completion of IEE’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Inland Empire Energy Center LLC (IEE) | NCR10267 | WECC2016016334 | MOD-025-2 | R1 | On October 8, 2016, IEE submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, IEE reported that it failed to verify the Real Power capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of IEE’s applicable Facilities, and ended September 1, 2016, when IEE tested both applicable Facilities. The root cause of this issue was a misunderstanding regarding the effective date of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, IEE failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to asses Bulk Electric System reliability. However, it was unlikely that this issue would have significantly affected current planning models as IEE tested both of its Facilities in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The combined capacity of the Facilities in scope is approximately 819 MVA. No harm is known to have occurred. IEE does not have previous violations of this Standard and Requirement. | To mitigate this issue, IEE: 1) tested all applicable Facilities; and 2) created automated notifications and reminders to ensure future testing is performed within a five-year interval. WECC verified completion of IEE’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Inland Empire Energy Center LLC (IEE) | NCR10267 | WECC2016016335 | MOD-025-2 | R2 | On October 8, 2016, IEE submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, IEE reported that it failed to verify the Reactive Power capability of at least 40 percent of its applicable Facilities in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of IEE’s applicable Facilities, and ended September 1, 2016, when IEE tested both applicable Facilities. The root cause of this issue was a misunderstanding regarding the effective date of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, IEE failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to asses Bulk Electric System reliability. However, it was unlikely that this issue would have significantly affected current planning models as IEE tested both of its Facilities in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The combined capacity of the Facilities in scope is approximately 819 MVA. No harm is known to have occurred. IEE does not have previous violations of this Standard and Requirement. | To mitigate this issue, IEE: 1) tested all applicable Facilities; and 2) created automated notifications and reminders to ensure future testing is performed within a five-year interval. WECC verified completion of IEE’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | KES-Kingsburg, LP (KESK) | NCR05504 | WECC2016016211 | MOD-025-2 | R1 | On September 28, 2016, KESK submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. During an internal compliance audit in August 2016, compliance staff discovered that the previous owner of the Kingsburg Cogeneration Plant did not prepare for implementation of MOD-025-2 prior to transferring ownership of the plant in the second quarter of 2016. As a result, KESK failed to verify the Real Power capability of its single applicable generator in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for KESK’s single applicable generator, and ended October 27, 2016, when KESK tested the generator. The root cause of this issue was KESK’s failure to ensure records and procedures were adequate to maintain compliance during transfer of the plant’s ownership. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, KESK failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single, 24.7 MVA generator, which was unlikely to have significantly affected current planning models. KESK’s Transmission Planner had applicable drawings for the generator, which included some of the data necessary for planning models. No harm is known to have occurred. KESK does not have previous violations of this Standard and Requirement. | To mitigate this issue, KESK tested the generator. Because this issue concerned a single generator, there is no risk of recurrent failure to implement this Standard in accordance with future percentage-based implementation deadlines. WECC verified completion of KESK’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | KES-Kingsburg, LP (KESK) | NCR05504 | WECC2016016212 | MOD-025-2 | R2 | On September 28, 2016, KESK submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. During an internal compliance audit in August 2016, compliance staff discovered that the previous owner of the Kingsburg Cogeneration Plant did not prepare for implementation of MOD-025-2 prior to transferring ownership of the plant in the second quarter of 2016. As a result, KESK failed to verify the Reactive Power capability of its single applicable generator in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for KESK’s single applicable generator, and ended October 27, 2016, when KESK tested the generator. The root cause of this issue was KESK’s failure to ensure records and procedures were adequate to maintain compliance during transfer of the plant’s ownership. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, KESK failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single, 24.7 MVA generator, which was unlikely to have significantly affected current planning models. KESK’s Transmission Planner had applicable drawings for the generator, which included some of the data necessary for planning models. No harm is known to have occurred. KESK does not have previous violations of this Standard and Requirement. | To mitigate this issue, KESK tested the generator. Because this issue concerned a single generator, there is no risk of recurrent failure to implement this Standard in accordance with future percentage-based implementation deadlines. WECC verified completion of KESK’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Los Angeles Department of Water and Power (LDWP) | NCR05223 | WECC2016016409 | VAR-002-4 | R3 | On October 24, 2016, LDWP submitted a Self-Report stating that as a Generator Operator, it had a possible issue of noncompliance with VAR-002-4 R3. Specifically, LDWP reported that on June 20, 2016, LDWP placed the automatic voltage regulator (AVR) on one of its units in manual mode in response to an alarm. The plant operator failed to notify LDWP’s primary control center (the associated Transmission Operator, or TOP) of the AVR status change until the following morning. This issue began June 20, 2016, 31 minutes after an LDWP operator failed to notify the TOP of a status change on the AVR, and ended roughly eight hours later, when LDWP notified the TOP that the AVR was operating in manual mode, for a total of less than one day of noncompliance. The root cause of this issue was human error; the plant operator failed to follow LDWP’s established procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, LDWP failed to notify the TOP regarding the AVR status of one of its generating units within the timeframe prescribed by VAR-002-4 R3. Such failure limited the TOP’s situational awareness, and could have resulted in unplanned tripping of the unit due to undamped voltage oscillations. However, this issue was limited to a single 25 MW unit over the course of roughly eight hours. LDWP’s plant operators maintained 24/7 visibility of the unit, ensuring voltage remained in the specified range throughout the duration of this issue. LDWP was also operating two other units in automatic voltage control mode at the same facility during the period in question, which would have compensated if the unit in scope had tripped unexpectedly. No harm is known to have occurred. LDWP’s relevant prior noncompliance with VAR-002 R3 includes NERC Violation IDs: WECC201002387 and WECC201102819. The previous violations were not considered aggravating factors because mitigating activities were completed more than three years prior to this issue. | To mitigate this issue, LDWP: 1) notified the primary control center of the AVR status; 2) completed a training exercise and exam for requisite staff regarding notification requirements of this Standard and LDWP’s associated procedures; 3) placed signs next to AVR auto/manual controls to remind plant operators of AVR status notification requirements; 4) distributed a lessons learned summary with management of all generation facilities; 5) implemented and performed a quarterly internal review of AVR and Protection System Stabilizer reports and control center logs to verify the scope of this issue was limited to a single incident. WECC verified completion of LDWP’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Manchief Power Company LLC (MCPC) | NCR05231 | WECC2016016124 | PRC-019-2 | R1 | On September 8, 2016, MCPC submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-019-2 R1. Specifically, MCPC reported that it failed to coordinate its voltage regulating system controls with generator capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. The root cause of this issue was less than adequate communication between MCPC and the electrical engineering firm contracted to perform the NERC PRC-019-2 Compliance Demonstration Study. This issue started on July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of MCPC’s applicable Facilities, and ended on November 17, 2016, when MCPC completed the NERC PRC-019-2 Compliance Demonstration Study and verified coordination of generating unit Facility voltage regulating controls, limit functions, equipment capabilities, and Protection System Settings, as required by the Standard; bringing it into compliance with the current implementation schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, MCPC failed to verify coordination items prescribed by R1.1.1 and R1.1.2 in accordance with the Standard’s implementation deadline. Such failure could result in loss of its generator field, instability, slipping poles, and/or damage to its turbines. However, MCPC’s in-service limiters were set to operate before the Protection System, in order to avoid disconnecting its generator unnecessarily. Additionally, from MCPC’s commercial operation date, all applicable in-service Protection System devices were set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. MCPC did not lose its generator field or experience instability, slipping poles, and/or damage to its turbines. Further, throughout the duration of this issue MCPC was both aware and in the process of completing PRC-019-2 coordination. MCPC followed up with the engineering contractor on multiple occasions approaching the enforcement date of the Standard, and was assured that the coordination would be completed before the enforcement date of the Standard. It was only after the enforcement date had passed that MCPC was informed that the engineering contractor lacked enough data to complete the coordination and failed to perform it on behalf of MCPC. The collective capacity of MCPC’s applicable Facilities is 300 MW. No harm is known to have occurred. WECC notes that MCPC has identified and self-reported the issues described herein, and does not have previous violations of either Standard and Requirement. For these reasons, WECC considers MCPC’s compliance history a factor in its designation of these remediated issues as CEs. | To remediate and mitigate this issue, MCPC: 1) Completed the Compliance Demonstration Study which was used to verify coordination of generating unit Facility voltage regulating controls, limit functions, equipment capabilities, and Protection System Settings as required by the Standard; 2) Utilized its other NERC-registered Generator Owner and Generator Operator facilities (Frederickson Power) as a resource to 1) share NERC/WECC compliance knowledge and training materials, and 2) collaborate on implementation of new Standards or revisions to existing; and 3) Implemented an enhanced automatic reminder system in the ManChief plant “Plant Center” utilized as a tracking method to send out reminders when applicable NERC Reliability Standards need to be revised or new Standards need to be implemented.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Manchief Power Company LLC (MCPC) | NCR05231 | WECC2016016125 | PRC-024-2 | R1 | On September 8, 2016, MCPC submitted a Self-Report stating that, as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R1. Specifically, MCPC reported that it failed to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding regarding the applicability of the Standard. MCPC believed that because its parent company was in compliance with the Standard that it too was in compliance. This issue started on July 1, 2016, when implementation of PRC-024-2 became mandatory and enforceable for 40 percent of MCPC’s protective relaying, and ended on July 29, 2016, when MCPC completed setting its protective relaying, per Attachment 1, bringing it into compliance with the current implementation schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In ithis nstance, MCPC failed to set 40 percent of its protective relaying such that generator voltage protective relaying would not trip applicable generating units unnecessarily. Such failure could result in the unnecessary trip of one or more generating units offline due to voltage excursions within the “no trip zone”. However, MCPC had contacted WECC for clarification of the Standard and immediately remediated the issue upon receiving a response. Additionally, the generating units did not trip offline due to voltage excursions within the “no trip zone”. The collective capacity of MCPC’s applicable Facilities is 300 MW. No harm is known to have occurred. WECC notes that MCPC has identified and Self-Reported the issues described herein, and does not have previous violations of either Standard and Requirement. For these reasons, WECC considers MCPC’s compliance history a factor in its designation of these remediated issues as CEs. | To remediate and mitigate this issue, MCPC: 1) Set the three underfrequency relay setting time delays in accordance with PRC-024 Attachment 1; 2) Utilized its other NERC-registered Generator Owner and Generator Operator facilities (Frederickson Power) as a resource to 1) share NERC/WECC compliance knowledge and training materials, and 2) collaborate on implementation of new Standards or revisions to existing; and 3) Implemented an enhanced automatic reminder system in the ManChief plant “Plant Center” utilized as a tracking method to send out reminders when applicable NERC Reliability Standards need to be revised or new Standards need to be implemented.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Mesquite Power LLC (MPL) | NCR05235 | WECC2016016461 | MOD-025-2 | R1 | On October 31, 2016, MPL submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, MPL reported that it failed to verify the Real Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of MPL’s generating units, and ended October 20, 2016, when MPL tested all of its generators. The root cause of this issue was a misunderstanding concerning the Attachment 1 testing criteria: MPL believed that data collected during previous testing was sufficient to meet the requirements of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MPL failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was unlikely to significantly affect current planning models as MPL tested all of its generators in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. No harm is known to have occurred. MPL does not have previous violations of this Standard and Requirement. | To mitigate this issue, MPL: 1) tested all applicable generators in accordance with all Attachment 1 criteria; and 2) scheduled maintenance tasks in its work management system to ensure future testing will be completed per the five-year interval of the Standard. WECC verified completion of MPL’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Mesquite Power LLC (MPL) | NCR05235 | WECC2016016543 | MOD-025-2 | R2 | On November 17, 2016, MPL submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, MPL reported that it failed to verify the Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of MPL’s generating units, and ended October 20, 2016, when MPL tested all of its generators. The root cause of this issue was a misunderstanding concerning the Attachment 1 testing criteria: MPL believed that data collected during previous testing was sufficient to meet the requirements of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MPL failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was unlikely to significantly affect current planning models as MPL tested all of its generators in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. No harm is known to have occurred. MPL does not have previous violations of this Standard and Requirement. | To mitigate this issue, MPL: 1) tested all applicable generators in accordance with all Attachment 1 criteria; and 2) scheduled maintenance tasks in its work management system to ensure future testing will be completed per the five-year interval of the Standard. WECC verified completion of MPL’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | PacifiCorp (PAC) | NCR05304 | WECC2016016066 | EOP-005-2 | R17 | WECC conducted a Compliance Audit of PAC as a Generator Operator from August 8, 2016 to August 12, 2016. During the audit, WECC identified a possible issue of noncompliance with EOP-005-2 R17; specifically, six operators responsible for tasks related to startup of Blackstart Resources had not completed training in accordance with the Standard. This issue began July 1, 2013, when EOP-005-2 became mandatory and enforceable for PAC, and ended June 23, 2016, when PAC provided requisite training to the operators in scope. The root cause of this issue was PAC’s interpretation of the Standard; PAC did not consider the operators to be directly responsible for Blackstart startup, and therefore did not require them to complete training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PAC failed to provide two hours of system restoration training to six operators responsible for tasks related to the startup of Blackstart Resources. Such failure could have delayed implementation of PAC’s System restoration plan during an event. However, this issue was limited to six operators. Had an event occurred which required implementation of PAC’s System restoration plan, management and other trained personnel would have directed all tasks related to startup of Blackstart Resources. Additionally, although the operators in scope had not completed formal training, each operator was required to review all applicable Blackstart policies and procedures on an annual basis, and therefore had some familiarity with PAC’s System restoration plan. No harm is known to have occurred. PAC does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PAC: 1) completed requisite training for all operators subject to this Standard and Requirement; and 2) developed a spreadsheet to track future training. WECC verified completion of PAC’s mitigating activities.
2017-02-28 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Sierra Nevada Region (WASN) | NCR05465 | WECC2016016383 | PRC-002-2 | R1 | On October 21, 2016, WASN submitted a Self-Report stating that as a Transmission Owner, it had a possible issue of noncompliance with PRC-002-2 R1. Specifically, WASN reported it did not use Attachment 1 methodology to correctly identify which Bulk Electric System (BES) buses require sequence of events recording (SER) and fault recording (FR) data to analyze system disturbances, as required by R1.1. The root cause of this issue was human error; the SME responsible for identifying applicable buses did not accurately apply instructions for Step 7 of Attachment 1. This issue began July 1, 2016, when PRC-002-2 became mandatory and enforceable for WASN, and ended September 21, 2016, when WASN revised the list to reflect accurate methodology, for a total of 82 days of noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WASN failed to accurately apply Attachment 1 methodology to identify which BES buses require SER and FR data to analyze system disturbances. Such failure could have limited WASN’s ability to properly analyze system disturbances. However, the MVA ratings of the incorrectly identified buses varied minimally from the ratings of the buses that should have been identified. WASN had SER and FR equipment on all buses with a maximum available calculated three phase short circuit higher than 1,500 MVA, in accordance with Attachment 1. No harm is known to have occurred. WASN does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WASN: 1) revised its list to reflect buses identified using the correct methodology; 2) developed a template to calculate percentiles in accordance with all Attachment 1 criteria; and 3) implemented a process whereby SMEs will peer review each other’s work and discuss potential issues related to recently-enforceable Standards. WECC verified completion of WASN’s mitigating activities.
2017-01-30 | Midwest Reliability Organization (MRO) | Montana-Dakota Utilities Company (MDU) | NCR01015 | MRO2016016187 | PRC-001-1.1(ii) | R3 | On July 6, 2016, MDU submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue of PRC-001-1.1(ii) R3. Specifically, MDU failed to coordinate with its neighboring TOP prior to updating a relay setting on a jointly owned facility. This occurred when MDU enabled a Load Encroachment Element on both the primary and secondary relays at a substation for a 230 kV line. The cause of this noncompliance was MDU subject-matter experts (SMEs) were not properly trained to know that changing a relay Load Encroachment Element is considered a change in protection system settings. This issue started on April 21, 2016, when MDU enabled a Load Encroachment Element without coordinating that change with the neighboring TOP, and ended on June 23, 2016, when MDU informed the neighboring TOP that it had enabled a relay Load Encroachment Element. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the noncompliance was relatively brief. Further, the load encroachment feature allows for higher loading without affecting the ability to detect faults and did not affect the protection system settings of the neighboring TOP. No harm is known to have occurred. MDU has no relevant history of noncompliance with PRC-001-1(ii). | To mitigate this issue, MDU: 1) notified the neighboring TOP that the Load Encroachment Element was enabled; and 2) to prevent recurrence, added PRC-001-related content to its weekly staff meeting. MDU stated that mitigating activities were complete as of July 6, 2016.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2015014842 | PER-005-1 | R1 | On March 30, 2015, IPL submitted a Self-Certification to ReliabilityFirst stating that, as a Transmission Operator, had an issue related to PER-005-1 R1. Although IPL conducted job task analysis for system operators, developed the required initial training programs, implemented the training programs, and implemented one-time task qualification in accordance with the requirements, IPL failed to implement a process to ensure that the initial and continuous training programs are maintained and updated. In short, IPL had performed gap analyses on its existing training program, but failed to establish a process to formally implement and document any recommendations that came out of the gap analyses for the 2015 training period. The root cause of this noncompliance was IPL’s failure to clearly define the roles and responsibilities for those who are responsible for supporting its operator training program. This major contributing factor involves the management practice of workforce management, which focuses on establishing and providing training, education, and awareness to employees. The issue started on May 1, 2014, the date by which IPL was required to have updated its training program, and ended on July 31, 2016, the date IPL completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, IPL provided training to its operators and reviewed that training on an annual basis. Although IPL failed to adequately document and ensure recommended updates to the training were incorporated into its formal training modules, IPL’s overall training program remained consistent with industry standards. Second, most of IPL’s operators have many years of experience and have gone through many years of training, which reduces the likelihood that any inadequacies in the training program would have a detrimental effect on their ability to perform their jobs. No harm is known to have occurred. ReliabilityFirst considered IPL’s PER-005 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, IPL: 1) reviewed and updated roles and responsibilities in IPL’s System Operator Training Program to clearly define who has responsibility for supporting its operator training program; 2) defined roles and responsibilities and applied an Annual Position Task List Review process; 3) defined roles and responsibilities and applied a review and requalification process for reliability-related tasks; 4) defined roles and responsibilities and applied an Annual Training Program Review process; 5) completed a gap analysis of existing training materials and developed missing training materials; and 6) completed a gap analysis of initial and continuing training materials. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | Southwest Power Pool Regional Entity (SPP RE) | CPV Keenan II Renewable Energy Company, LLC (KREC) | NCR11081 | SPP2016015838 | EOP-004-2 | R3 | On June 21, 2016, KREC submitted a Self-Report stating that, as a Generator Owner and a Generator Operator, it had an issue of noncompliance with EOP-004-2 R3 because it did not validate all contact information contained in the Operation Plan for the 2014-2015 calendar year. In May 2016, KREC performed an internal review and found that its email reminder software failed to include EOP-004-related prompts. As a result, contact information had not been validated and/or updated. The duration of this instance of noncompliance was from September 14, 2014, one year and one day after KREC’s last contact list verification, through June 15, 2016, the date KREC validated and updated its contact list. The root cause of this instance of noncompliance was a lack of internal controls to validate contact information each year. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). KREC had an Operating Plan that met the requirements of EOP-004-2, and the contact information in the plan was correct, notwithstanding the failure to verify the contact information. No harm occurred as a result of this noncompliance. SPP RE considered KREC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this minimal risk instance of noncompliance, KREC: 1) verified contacts verbally and via email; 2) added a requirement to annually prompt for contact information verification to its email software; and 3) added plans to conduct a gap analysis annually. SPP RE has verified the completion of all mitigation activity.
2017-01-30 | Texas Reliability Entity (Texas RE) | EIF Channelview Cogeneration, LLC (EIFCVC) | NCR11430 | TRE2016016556 | PRC-005-2 | R1; R1.2 | During a Compliance Audit conducted from November 8, 2016 through November 17, 2016, Texas RE determined that EIFCVC, as a Generator Owner (GO), had an issue with PRC-005-2 R1.2. Specifically, EIFCVC failed to include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. During the Compliance Audit, Texas RE determined that EIFCVC’s Protection System and Maintenance Program (PSMP) documentation extended the maintenance intervals on several Protection System Components beyond those applicable to unmonitored Protection System Components. In doing so, however, EIFCVC neglected to provide the corresponding monitoring attributes to support such an extension. Texas RE subsequently determined that EIFCVC timely performed maintenance and testing on its Protection System Components, including any unmonitored Components. Nevertheless, EIFCVC failed to reflect its actual testing and maintenance practices, including its actual testing intervals and its basis for those testing intervals, in its PSMP documentation. The root cause of this issue was inadequate internal controls for ensuring that EIFCVC’s documentation satisfied all applicable NERC Reliability Standard requirements. In particular, EIFCVC lacked a dedicated NERC Compliance Manager, and the EIFCVC personnel responsible for maintenance and testing activities failed to understand the need to document EIFCVC’s actual testing intervals, including the basis for those testing intervals, in its PSMP. Texas RE determined the issue duration to be from April 1, 2015, when PRC-005-2 R1 became effective, until December 7, 2016, when EIFCVC modified its PSMP to reflect the appropriate maintenance intervals for all of its Protection System Components. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for two reasons. First, the issue was solely related to EIFCVC’s maintenance and testing documentation. In particular, although EIFCVC failed to properly document the appropriate Component attributes and corresponding maintenance intervals, Texas RE determined that EIFCVC actually tested its Protection System devices using appropriate maintenance and testing intervals. Second, during the duration of the issue, the EIFCVC Facility at issue did not experience any Protection System misoperations. No harm is known to have occurred. Texas RE considered EIFCVC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EIFCVC: 1) updated its PSMP to incorporate the correct Component attributes and assigned the proper maximum maintenance intervals and maintenance activities to each applicable Protection System Component type; 2) distributed its updated PSMP to appropriate personnel; 3) hired a NERC Compliance Manager whose dedicated job function is NERC compliance; 4) issued an email to the operating staff stating the importance of maintaining a working knowledge of current NERC Standards; and 5) developed a NERC Planning Workbook program to identify and assess upcoming applicable NERC Standards in a timely manner. Texas RE has verified the completion of all mitigation activity.
2017-01-30 | Texas Reliability Entity (Texas RE) | NRG Texas Power, LLC (NRGTP) | NCR10090 | TRE2016016374 | BAL-001-TRE-1 | R8 | On October 18, 2016, NRGTP submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with BAL-001-TRE-1 R8. Specifically, NRGTP did not notify its BA within 30 minutes of its discovery of a status change of a generating unit Governor. On August 12, 2016, at 9:46 a.m., the generation plant that performs the functions of NRGTP’s Generation Owner (GO) called NRGTP’s Real Time Desk (RTD) to inform the RTD that it was beginning maintenance on a single generation unit and that the Governor for this unit was now out of service. The RTD operator on duty recorded this information in the RTD logs, but then neglected to contact NRGTP’s Balancing Authority (BA) as required. At 10:31 a.m., the GO completed the maintenance activities and returned the single generation unit’s Governor to service. The root cause of this noncompliance was a failure to follow the required notification procedure for Governor status changes. The RTD operator in question had previously received training regarding the requirements to notify the BA following a governor status change and had previously performed the required status change notification task. Additionally, the RTD operator screens provide an alarm for RTD operators when a unit Governor goes offline in circumstances like those at issue here, as well as procedures containing the requisite notification requirement. During the single instance, the RTD operator neglected these prompts to notify the BA. Texas RE determined the issue duration to be for 15 minutes on August 12, 2016, from 10:16 a.m., 31 minutes after NRGTP failed to notify its BA of the Governor status change on the generation unit at issue until 10:31 a.m., when NRGTP re-enabled the Governor on the generation unit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the duration of the issue was short, lasting only 15 minutes. Second, there were no Frequency Monitoring Events (FMEs) during the duration of the issue. Third, in the event frequency response was required, the ERCOT interconnection possesses several other responsive methods, including primary frequency response from units with mechanical governors and Load Resource Under Frequency Relays. No harm is known to have occurred. Texas RE considered NRGTP's compliance history in determining the disposition track. NRGTP's relevant compliance history includes an issue with VAR-002-2b R3 (TRE2014014002). Texas RE determined that NRGTP's previous instance of noncompliance should not serve as a basis for applying a penalty because the root cause of the previous instance is distinguishable from the current issue. In the previous instance related to VAR-002-2b R3, the NRGTP operators were unaware that the PSS was offline. In the current instance pertaining to BAL-001-TRE-1 R8, the NRGTP operators were aware of the status change and failed to make the required notification. | To mitigate this issue, NRGTP: 1) re-enabled the Governor on the generation unit at issue; and 2) provided refresher training to its RTD operating personnel that included an emphasis on the requirement to notify the BA when there is a status change on a generation unit’s Governor. Texas RE has verified the completion of all mitigation activity.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC2016015969 | VAR-501-WECC-2 | R1 | On August 1, 2016, AVGO submitted a Self-Report stating that as a Generator Operator, it had a possible instance of noncompliance with VAR-501-WECC-2 R1. Specifically, AVGO reported that it failed to re-enable the Power System Stabilizer (PSS) devices on three of its generators after completing exciter inspections and verifications. This issue began April 7, 2016, when one of the generators exceeded 2% of its second quarter operating hours without the PSS enabled, and ended July 19, 2016, when AVGO re-enabled PSS on all of the generators. This issue was caused by less than adequate controls for PSS status verification. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AVGO failed to keep PSS devices on three generators in service for 98% of all operating hours. Such failure limited AVGO’s situational awareness regarding the status of its PSS capability. However, each generator's Automatic Voltage Regulator (AVR) was in service, and none of the generators tripped offline due to undamped voltage oscillations during the period in question. AVGO resolved this issue immediately upon discovery. No harm is known to have occurred. AVGO does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, AVGO: 1) enabled the devices; 2) modified its shift turnover report to include bi-daily verification of PSS status; 3) revised its procedural documentation to ensure PSS is enabled after generator startup; 4) provided training to requisite staff regarding procedural revisions and the notification requirements of both Standards; and 5) implemented changes to its control system, which will alarm whenever PSS is disabled or malfunctions while a generator is in service.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC2016015970 | VAR-002-4 | R3 | On August 1, 2016, AVGO submitted a Self-Report stating that as a Generator Operator, it had a possible instance of noncompliance with VAR-002-4 R3. Specifically, AVGO reported that it failed to re-enable the Power System Stabilizer (PSS) devices on three of its generators after completing exciter inspections and verifications. Because AVGO did not discover this issue until it was preparing its second quarter periodic data submittal for VAR-501-WECC-2, it did not notify its Transmission Operator (TOP) of a status change on the devices within the thirty-minute notification window. This issue began April 6, 2016, thirty minutes after the notification window lapsed, and ended July 21, 2016, when AVGO informed the TOP of the oversight. This issue was caused by less than adequate controls for PSS status verification. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AVGO failed to keep PSS devices on three generators in service for 98% of all operating hours, and failed to notify its TOP of the status of its PSS devices. Such failure limited both AVGO’s and its TOP’s situational awareness of the status of AVGO’s PSS capability. However, each generator’s Automatic Voltage Regulator (AVR) was in service, and none of the generators tripped offline due to undamped voltage oscillations during the period in question. AVGO resolved this issue immediately upon discovery. No harm is known to have occurred. AVGO does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, AVGO: 1) informed its TOP of the issue and the current PSS status for the generators in scope; 2) modified its shift turnover report to include bi-daily verification of PSS status; 3) revised its procedural documentation to ensure PSS is enabled after generator startup; 4) provided training to requisite staff regarding procedural revisions and the notification requirements of both Standards; and 5) implemented changes to its control system, which will alarm whenever PSS is disabled or malfunctions while a generator is in service.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2016016118 | MOD-032-1 | R1 | On September 7, 2016, AVA submitted a Self-Report stating that as a Planning Authority and Transmission Planner, it had a possible instance of noncompliance with MOD-032-1 R1. Specifically, AVA reported that during an internal compliance review, it discovered that its data specification documentation had not been modified in accordance with MOD-032-1 by the effective date of the Standard. This issue began July 1, 2015, when the Standard became mandatory and enforceable on AVA, and ended May 28, 2016, when AVA discovered the issue and revised its documentation. The root cause of this issue was less than adequate means to track compliance tasks and processes. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, AVA failed to timely modify its data specification documentation, which could result in inconsistent modeling data requirements and reporting procedures between the Planning Authority and Transmission Planner. However, AVA performs both Planning Authority and Transmission Planner functions, and therefore 1) coordinates its own modeling data requirements, and 2) had access to all data necessary for the development of its planning horizon base cases. Accordingly, because MOD-032-1 did not add new data requirements or scheduling changes, and AVA was meeting the performance requirements of the Standard throughout the duration of the issue, this issue mainly concerned outdated documentation. No harm was known to have occurred. AVA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, AVA: 1) revised its documentation to comply with the Standard; and 2) implemented an automated compliance task management system, which will track compliance-related tasks, schedules, and documentation. WECC verified completion of AVA’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2015015437 | PRC-005-2(i) | R3 | On December 24, 2015, AVA submitted a Self-Report stating that it had a possible instance of noncompliance with PRC-005-2(i) R3. Specifically, AVA reported that in a quarterly compliance review, it discovered it had not performed minimum maintenance activities for its Protection System Components within the prescribed intervals. The Standard requires AVA to perform maintenance activities on a maximum maintenance interval of four calendar months for Protection System Station DC supply using Vented Lead-Acid (VLA) batteries. Although AVA inspected the VLA batteries at two of its substations per the Standard, AVA performed these maintenance activities two days outside the 4-month interval. On April 11 through 22, 2016, WECC conducted a Compliance Audit of AVA and reviewed AVA’s Self-Report. WECC determined that AVA missed maintenance intervals at three additional facilities. The cause of this issue was AVA's lack of an effective process control to verify that inspections were completed as required. This issue began on October 1, 2015, the earliest date in which devices in scope were due for testing, and ended March 1, 2016, when AVA completed testing for all devices. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AVA failed to maintain three batteries and two power line carriers within its maximum maintenance interval. Such failure could potentially result in degradation of equipment or the misoperation of associated protection systems devices. AVA implemented good preventive controls to prevent the likelihood of the above consequence from occurring. Specifically, AVA had alarms on the batteries such that if the DC voltages dropped below a threshold, an alarm would sound and an inspection would occur. However, AVA lacked a strong detective control process to verify that inspections were completed as required. No harm is known to have occurred. | To remediate and mitigate this noncompliance, AVA: 1) provided maintenance and testing records for the three battery banks and two power line carriers, and 2) established a PRC-005 task force project to ensure future compliance, establish documentation guidelines, and document internal controls. WECC verified completion of the Mitigation Plan.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2016015602 | PRC-004-WECC-1 | R1 | On March 14, 2016, AVA submitted a Self-Report stating that as a Transmission Owner and Generator Owner it had a possible instance of noncompliance with PRC-004-WECC-1 R1. Specifically, AVA reported that on August 16, 2014, a breaker tripped and reclosed on a 115 kV line associated with a Major WECC Transfer Path. While it is normal practice for AVA's System Operator to review and log such operations in the system log, no log entry was made for this operation. On August 19, 2014, approximately 84 hours after the trip, AVA's Protection Engineer reviewed, analyzed and recorded the operation in the System Protection Operations Database. The analysis showed that the trip was not a misoperation. On April 11 through 22, 2016, WECC conducted a Compliance Audit of AVA and reviewed AVA’s Self-Report. The WECC Audit Team confirmed that AVA’s failure to review all tripping of transmission elements and RAS operations within 24 hours was an issue of noncompliance with R1.1. The cause of this issue was AVA’s less-than-adequate compliance procedure to ensure timely review of possible misoperations. This issue began on August 16, 2014, when the breaker in question tripped, and ended August 19, 2014, when AVA analyzed the operation to verify that a misoperation had not occurred. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AVA did not review a trip of a major transmission element on a WECC Transfer Path within the 24-hour timeframe prescribed by R1.1. Such failure could result in delayed identification of a possible misoperation. However, although AVA failed to review the operation within the window prescribed by R1.1, it did perform an analysis of the operation within the 20-day window prescribed by R1.2. This analysis confirmed that the trip in question was not a misoperation. Additionally, AVA had detective controls in place to timely identify issues of this nature, which were only ineffective in this case as a result of individual human error. Specifically, AVA’s System Protection Group reviews the operations entered into the previous day’s system log. No harm was known to have occurred. WECC considered AVA's PRC-0004-WECC-1 R1 compliance history in determining the disposition track. AVA’s previous violation of PRC-004-WECC-1 R1, given Violation ID: WECC2013012247, concerned AVA’s failure to analyze multiple operations in accordance with R1.2. WECC considered the facts and circumstances separate and distinct from the current issue, and did not consider the current issue to be indicative of AVA’s failure to properly mitigate the previous violation. | To remediate and mitigate this noncompliance, AVA: 1) reviewed entries for this operation in its system log and its Protection system Operations Database to confirm that the operation was subject to follow-up analysis after the R1.1 review period lapsed, and 2) discussed compliance obligations related to this Standard, relay operation reporting, misoperation, and logging during a System Operator meeting on August 18, 2016. WECC verified completion of the Mitigation Plan.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016015728 | INT-006-4 | R1 | On May 6, 2016, BPA submitted a Self-Report stating that as a Balancing Authority, it had a possible instance of noncompliance with INT-006-4 R1. Specifically, BPA reported that in three separate incidents, BPA experienced technical issues on its scheduling software, which resulted in delayed processing of ten Arranged Interchange transactions (eTags). Each incident involved end-of-month system maintenance processes, and in each instance the software resolved the issues without intervention by BPA or the software vendor. This issue began February 29, 2016, the earliest date in which an eTag was not processed timely, and ended May 1, 2016, when the vendor resolved the underlying software problems that caused the issue. The root cause of this issue was the vendor's less than adequate corrective actions. | This noncompliance posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. In this instance, BPA failed to approve or deny Arranged Interchanges within the time period defined in Attachment 1, Column B of the Standard. Such failure could result in untimely or missed Interchange, which could cause an imbalance in BPA’s Area Control Error (ACE). However, this issue was limited to ten transactions over the course of three months. BPA had multiple controls in place, including software configurations to automatically process eTags prior to expiration of the defined time period, as well as manual monitoring by real-time schedulers in the event of a software issue. These controls brought the issue to BPA’s attention immediately; although the software issues were too severe to override manually, BPA’s schedulers contacted the vendor while the problems were still occurring. The controls also enabled BPA to track the exact scope of the issue in real time. No harm was known to have occurred. BPA had two previous issues of noncompliance with INT-006 R1, given Violation IDs: WECC200700350 and WECC2015014980. The first violation was not considered relevant because mitigating activities were completed more than three years prior to this issue, and the second issue was processed as a Compliance Exception. | To mitigate this noncompliance, BPA verified that the vendor identified and addressed the root causes of the software issues and provided evidence of this confirmation to WECC. WECC verified completion of BPA’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016015729 | INT-006-4 | R2 | On May 6, 2016, BPA submitted a Self-Report stating that as a Transmission Service Provider, it had a possible instance of noncompliance with INT-006-4 R2. Specifically, BPA reported that it experienced technical issues on its scheduling software, which resulted in delayed processing of four Arranged Interchange transactions (eTags). This issue involved end-of-month system maintenance processes, and the software resolved the issue without intervention by BPA or the software vendor. This issue began March 31, 2016, when the eTags were not processed timely, and ended May 1, 2016, when the vendor resolved the underlying software problems that caused the issue. The root cause of this issue was the vendor's less than adequate corrective actions. | This noncompliance posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. In this instance, BPA failed to approve or deny Arranged Interchanges within the time period defined in Attachment 1, Column B of the Standard. Such failure could result in untimely or missed Interchange, which could cause an imbalance in BPA’s Area Control Error (ACE). However, this issue was limited to four transactions over the course of three months. BPA had multiple controls in place, including software configurations to automatically process eTags prior to expiration of the defined time period, as well as manual monitoring by real-time schedulers in the event of a software issue. These controls brought the issue to BPA’s attention immediately; although the software issues were too severe to override manually, BPA’s schedulers contacted the vendor while the problems were still occurring. The controls also enabled BPA to track the exact scope of the issue in real-time. No harm was known to have occurred. BPA had one previous issue of noncompliance with INT-006 R2, given violation ID: WECC2015014981. This issue was not processed as a Compliance Exception and not considered relevant to the current issue. | To mitigate this noncompliance, BPA verified that the vendor identified and addressed the root causes of the software issues, and provided evidence of this confirmation to WECC. WECC verified completion of BPA’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | City of Redding (RDNG) | NCR05091 | WECC2016016027 | MOD-025-2 | R1 | On August 16, 2016, RDNG submitted a Self-Report stating that as a Generator Owner, it had a possible instance of noncompliance with MOD-025-2 R1. Specifically, RDNG reported that during an internal review of the testing report submitted to RDNG by the contractor that performed RDNG’s MOD-025-2 testing, RDNG discovered that the generators had not been tested in accordance with all Attachment 1 criteria. As a result, RDNG failed to verify the Real Power capability of at least 40 percent of its generators by the effective date of the Standard. The root cause of this issue was a failure to ensure that the contractor understood all Attachment 1 criteria prior to testing. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of RDNG’s generators, and ended August 3, 2016, when RDNG tested three of its generators in accordance with all Attachment 1 criteria. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, RDNG failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as RDNG tested all of its generators in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The collective capacity of all RDNG’s units is 183 MW. No harm is known to have occurred. Additionally, RDNG implemented multiple preventive measures to ensure requisite testing would be completed prior to the effective date of the Standard. RDNG scheduled testing for 40 percent of its applicable generators well in advance of the implementation deadline, and reviewed test records to identify and address deficiencies in the test report. Upon discovery of the issue, RDNG immediately scheduled re-testing to resolve deficiencies identified from the first test. RDNG does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, RDNG: 1) tested three of its generators in accordance with all Attachment 1 criteria; 2) tested all remaining generators, removing the possibility of recurrent failure to implement this Standard in accordance with future implementation deadlines; and 3) scheduled future MOD-025-2 verification and testing per the five-year interval of the Standard. WECC verified completion of RDNG’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | City of Redding (RDNG) | NCR05091 | WECC2016016569 | MOD-025-2 | R2 | On November 15, 2016, RDNG submitted a Self-Report stating that as a Generator Owner, it had a possible instance of noncompliance with MOD-025-2 R2. Specifically, RDNG reported that during an internal review of the testing report submitted to RDNG by the contractor that performed RDNG’s MOD-025-2 testing, RDNG discovered that the generators had not been tested in accordance with all Attachment 1 criteria. As a result, RDNG failed to verify the Reactive Power capability of at least 40 percent of its generators by the effective date of the Standard. The root cause of this issue was a failure to ensure that the contractor understood all Attachment 1 criteria prior to testing. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of RDNG’s generators, and ended August 3, 2016, when RDNG tested three of its generators in accordance with all Attachment 1 criteria. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, RDNG failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as RDNG tested all of its generators in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The collective capacity of all RDNG’s units is 183 MW. No harm is known to have occurred. Additionally, RDNG implemented multiple preventive measures to ensure requisite testing would be completed prior to the effective date of the Standard. RDNG scheduled testing for 40 percent of its applicable generators well in advance of the implementation deadline, and reviewed test records to identify and address deficiencies in the test report. Upon discovery of the issue, RDNG immediately scheduled re-testing to resolve deficiencies identified from the first test. RDNG does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, RDNG: 1) tested three of its generators in accordance with all Attachment 1 criteria; 2) tested all remaining generators, removing the possibility of recurrent failure to implement this Standard in accordance with future implementation deadlines; and 3) scheduled future MOD-025-2 verification and testing per the five-year interval of the Standard. WECC verified completion of RDNG’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Colorado Green Holdings, LLC (COGH) | NCR05104 | WECC2016015866 | PRC-019-2 | R1 | On July 1, 2016, COGH submitted a Self-Report stating that as a Generator Owner, it had a possible instance of noncompliance with PRC-019-2 R1. Specifically, COGH reported that it failed to coordinate voltage regulating system controls with equipment capabilities and Protection System device settings of at least 40 percent of its applicable Facilities by the effective date of the Standard. This issue began July 1, 2016, when implementation of PRC-019-2 became mandatory and enforceable for 40 percent of COGH’s applicable Facilities, and ended August 30, 2016, when COGH completed inverse time over-current diagrams of its applicable Facilities, bringing it into compliance with the current implementation schedule. The root cause is this issue was less than adequate planning in preparation of the implementation deadline; COGH underestimated the time needed to perform requisite coordination. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, COGH failed to verify coordination items prescribed by R1.1.1 and R1.1.2 in accordance with the Standard’s implementation deadline. Such failure could result in over-current damage to COGH’s applicable Facilities. However, throughout the duration of this issue, COGH was both aware of and in the process of completing PRC-019-2 coordination. The collective capacity of COGH’s applicable Facilities is 162 MW. No harm was known to have occurred. COGH does not have previous violations of this Standard and Requirement. | To mitigate this noncompliance, COGH: 1) completed requisite coordination for at least 40 percent of its applicable Facilities, meeting the currently-effective implementation schedule; 2) also met with its contractors and affiliates to discuss estimated timelines for tasks associated with Standards that will become effective in 2017; and 3) created a tool to track, manage, and schedule tasks related to implementation of upcoming Standards. WECC verified completion of COGH’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | WECC2016016135 | PER-005-1 | R1 | During a Compliance Audit conducted from July 11, 2016 through July 21, 2016, WECC determined that FEUS, as a Transmission Operator, had an issue of noncompliance with PER-005-1 R1. WECC determined that FEUS failed to use a systematic approach to training (SAT) in the FEUS Operating Personnel Training Program. WECC found that FEUS did not include a description of the analysis, design, development, implementation, and evaluation steps of a systematic approach; did not establish plans for initial and continuing training using the systematic approach; did not establish a process for conducting the annual update of the list of reliability-related tasks; and did not establish a process to conduct the annual evaluation of the training program. The WECC Audit team reviewed the program, the list of reliability-related tasks, and the learning activities provided; and found that both the reliability-related tasks and the learning activities were consistent with compliant programs the Audit team has reviewed for entities similar to FEUS. This review lends credibility to FEUS’s statements that they believe a SAT was utilized in designing the training program, determining reliability-related tasks, designing, developing, and evaluating the training, but personnel changes and lost documentation have reduced FEUS’s ability to demonstrate use of the SAT. The root cause of this noncompliance was a lack of continuity of the training program administrators. The last four administrators have all served less than two years and none have had the benefit of being oriented into the position by the predecessor. As such, the historic artifacts of the development and implementation of the training program were not properly documented and maintained. WECC determined that this issue began on November 9, 2013, one day after the completion date of a mitigation plan for a previous violation of this Standard and Requirement (Violation ID WECC2013012189), and is ongoing. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, FEUS failed to demonstrate that it used a systematic approach in its training program for the Bulk Electric System company-specific reliability-related tasks performed by its System Operators. Although FEUS implemented an Operating Personnel Training Program based on a SAT, it failed to document the description of the SAT it used to establish the program and the plans for initial and continuing training using the systematic approach. Without documentation of the implementation of a SAT, such failure could result in the System Operators not being trained on some reliability-related tasks. If those tasks are of a critical nature (difficult to perform, very important to reliability, or do not occur frequently), it is possible the operators may not perform at a sufficiently high level to maintain reliable operation. However, this issue would not likely occur because FEUS has maintained a consistent training program for its System Operators for many years, and has records showing training has been delivered during that time, including annual participation of all operators in annual regional restoration exercises. In addition, FEUS uses training vendors to provide all NERC continuing education hours to its System Operators to maintain NERC-certification. These vendor activities are submitted to NERC for authorization to award Continuing Education Hours. In part, the NERC review ensures the vendor used a systematic approach to training in developing the learning activity. No harm was known to have occurred. FEUS had one prior violation of this Standard and Requirement, given NERC Violation ID: WECC2013012189. In that instance, FEUS failed to establish and implement a training program for the BES company-specific reliability-related tasks performed by its System Operators, by the effective date of the Standard. To mitigate this issue, FEUS revised its Operating Personnel Training Program. WECC accepted this mitigation, and verified completion of FEUS’s Mitigation Plan. At that time, FUES relied on WECC’s verification as an indication that the training program was compliant with PER-005-1 R1. However, during FEUS’s July 2016 audit, WECC determined that the training program verified by WECC as part of FEUS’s prior mitigation did not include a systematic approach to training, and therefore was not compliant with the Standard. Accordingly, WECC did not consider the previous issue of noncompliance to be an aggravating factor, because FEUS relied on information from WECC that was in error. | On September 28, 2016, FEUS submitted a Mitigation Plan to address this issue, which identified May 14, 2017 as the completion date for associated mitigating activities. To mitigate this noncompliance, FEUS will: a. Review and select a bid proposal for third-party support to ensure that the FEUS training and documentation are compliant with PER-005 and aligned with internal consistency, b. Complete proposed revised training program, and c. Implement revised training program. The completion date of this Mitigation Plan will be May 14, 2017.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Modesto Irrigation District (MID) | NCR05244 | WECC2016015859 | IRO-010-1a | R3 | On June 29, 2016, MID submitted a Self-Report stating that as a Generator Owner, Generator Operator, Transmission Owner, and Transmission Operator, it had a possible instance of noncompliance with IRO-010-1a R3. MID reported that during an early spring 2016 internal audit, MID identified potential inadequacies in its current process for responding to the Reliability Coordinator’s (RC’s) annual data request. Specifically, the review highlighted concerns regarding MID’s lack of formal procedure to coordinate partial responses to the RC’s annual data request across multiple departments. The RC generally distributes its IRO-010-1a data specification (data request) on an annual basis, or whenever the RC makes updates to the data request. The data request includes an attachment which categorizes types of data, and specifies the transfer method and frequency by which a responsible entity must provide such data. Prior to MID’s spring 2016 review, MID provided most of the requested data–particularly its Inter-Control Center Communication Protocol (ICCP) data–through its associated Balancing Authorities (BAs), which would in turn forward the data to the RC. Because MID was not submitting its ICCP data to the RC directly, and because MID had not been contacted by the RC or BAs regarding missing information, MID believed its submissions were sufficient to meet the requirements of the RC’s data request. Following MID’s spring 2016 review, MID performed a thorough gap analysis to determine whether 1) the data specified in the RC’s annual data requests had been submitted timely, and 2) the data MID provided to its BAs was forwarded to the RC as expected. MID identified several deficiencies in its data request responses. This issue began October 1, 2011, when the Standard became mandatory and enforceable on MID, and ended August 1, 2016, when MID provided the missing data to the RC. The root cause of this issue was MID’s lack of formal procedure to coordinate partial responses to the RC’s annual data request across multiple departments. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MID failed to provide data and information, as specified, to its RC. Such failure could reduce the RC’s situational awareness and limit its ability to develop accurate operational models of real-time demands, contingency analyses, and system planning analyses. However, MID is an active user on the WECC Operations Network (WON), which allowed the RC visibility throughout the duration of the issue to most of the missing data identified in MID’s gap analysis. Additionally, although MID failed to track and ensure adequacy of its formal responses to data requests, it did provide informal data submissions to the RC. Upon discovery of this issue, MID contacted the RC to determine whether its gap analysis failed to identify all deficiencies; the RC was unable to quantify which data were missing, which is an indication that the deficiencies did not have any obvious, measurable effect on the RC’s ability to monitor and assess the operation of its area during the period in question. No harm was known to have occurred. MID does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, MID: 1) collaborated with the RC to determine the scope of the issue; 2) provided the data identified in its gap analysis to the RC; 3) created and implemented a formal procedure to ensure future data request responses are a) coordinated across departments, and b) tracked for adequacy of content and timely completion; and 4) established links to provide ICCP data directly to the RC. WECC verified completion of MID’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Nevada Irrigation District (NID) | NCR11469 | WECC2016015868 | MOD-025-2 | R1 | On July 1, 2016, NID submitted Self-Reports stating that as a Generator Owner, it had a possible issues of noncompliance with MOD-025-2 R1. Specifically, NID reported that it failed to verify the Real Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of NID’s generating units, and ended November 8, 2016, when NID tested one of its two generators. The root cause of this issue was NID's misunderstanding of the enforceable date of the Standard. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, NID failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess BPS reliability. However, this issue would not likely have significantly affected current planning models as NID tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The capacity of the units in scope is approximately 65 MVA. This issue largely concerned NID’s misunderstanding regarding the Standard’s implementation dates. Upon discovery of this misunderstanding, and prior to the July 1, 2016 implementation deadline, NID reviewed the most recent generator modeling testing data to determine whether it was sufficient to complete Attachment 2. NID then submitted a partially completed Attachment 2 form to its Transmission Planner, and scheduled testing for the remaining data. No harm was known to have occurred. NID does not have previous violations of this Standard and Requirement. | To mitigate this noncompliance, NID: 1) tested one of its two generators, meeting the 40 percent requirement; 2) scheduled testing for its remaining generator to be completed well in advance of the next Standard implementation deadline; 3) verified and updated automated reminders in its work management system to ensure future testing will be completed in accordance with the five-year interval of the Standard; and 4) will pursue clarification from WECC regarding potential ambiguity concerning implementation of upcoming Standards to prevent recurrence. WECC verified completion of NID’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Nevada Irrigation District (NID) | NCR11469 | WECC2016015869 | MOD-025-2 | R2 | On July 1, 2016, NID submitted Self-Reports stating that as a Generator Owner, it had a possible issues of noncompliance with MOD-025-2 R2. Specifically, NID reported that it failed to verify the Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of NID’s generating units, and ended November 8, 2016, when NID tested one of its two generators. The root cause of this issue was NID's misunderstanding of the enforceable date of the Standard. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, NID failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess BPS reliability. However, this issue would not likely have significantly affected current planning models as NID tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. The capacity of the units in scope is approximately 65 MVA. This issue largely concerned NID’s misunderstanding regarding the Standard’s implementation dates. Upon discovery of this misunderstanding, and prior to the July 1, 2016 implementation deadline, NID reviewed the most recent generator modeling testing data to determine whether it was sufficient to complete Attachment 2. NID then submitted a partially completed Attachment 2 form to its Transmission Planner, and scheduled testing for the remaining data. No harm was known to have occurred. NID does not have previous violations of this Standard and Requirement. | To mitigate this noncompliance, NID: 1) tested one of its two generators, meeting the 40 percent requirement; 2) scheduled testing for its remaining generator to be completed well in advance of the next Standard implementation deadline; 3) verified and updated automated reminders in its work management system to ensure future testing will be completed in accordance with the five-year interval of the Standard; and 4) will pursue clarification from WECC regarding potential ambiguity concerning implementation of upcoming Standards to prevent recurrence. WECC verified completion of NID’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Pacific-Ultrapower Chinese Station (PUPCS) | NCR11279 | WECC2016016167 | MOD-025-2 | R1 | On September 14, 2016, PUPCS submitted a Self-Report stating that as a Generator Owner, it had a possible instance of noncompliance with MOD-025-2 R1. Specifically, PUPCS reported that it failed to verify the Real Power capability of its single generator in accordance with Attachment 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding regarding the effective date of MOD-025-2 for single unit Facilities. The Standard does not require implementation for 100% of applicable units until July 1, 2019. PUPCS believed that because it owns a single applicable generator, it was not required to meet the 40% implementation deadline, as it could not test only 40% of its generator. PUPCS pursued clarification regarding this issue prior to the July 1, 2016 implementation deadline, but did not receive confirmation until after the deadline had passed. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for PUPCS’s single generator, and ended September 26, 2016, when PUPCS tested the generator. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PUPCS failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single, 25 MW generator, and no harm was known to have occurred. PUPCS does not have previous violations of this Standard and Requirement. | To mitigate this noncompliance, PUPCS: 1) tested its generator; and 2) added applicable tasks for MOD-025-2 to its compliance tracking tool to ensure the Real and Reactive Power capability of the generator is verified in advance of the next five-year interval. WECC verified completion of PUPCS’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Pacific-Ultrapower Chinese Station (PUPCS) | NCR11279 | WECC2016016168 | MOD-025-2 | R2 | On September 14, 2016, PUPCS submitted a Self-Report stating that as a Generator Owner, it had a possible instance of noncompliance with MOD-025-2 R2. Specifically, PUPCS reported that it failed to verify the Reactive Power capability of its single generator in accordance with Attachment 1 by the effective date of the Standard. The root cause of this issue was a misunderstanding regarding the effective date of MOD-025-2 for single unit Facilities. The Standard does not require implementation for 100% of applicable units until July 1, 2019. PUPCS believed that because it owns a single applicable generator, it was not required to meet the 40% implementation deadline, as it could not test only 40% of its generator. PUPCS pursued clarification regarding this issue prior to the July 1, 2016 implementation deadline, but did not receive confirmation until after the deadline had passed. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for PUPCS’s single generator, and ended September 26, 2016, when PUPCS tested the generator. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PUPCS failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue concerned a single, 25 MW generator, and no harm was known to have occurred. PUPCS does not have previous violations of this Standard and Requirement. | To mitigate this noncompliance, PUPCS: 1) tested its generator; and 2) added applicable tasks for MOD-025-2 to its compliance tracking tool to ensure the Real and Reactive Power capability of the generator is verified in advance of the next five-year interval. WECC verified completion of PUPCS’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Platte River Power Authority (PRPA) | NCR05321 | WECC2016016358 | MOD-025-2 | R1 | On October 13, 2016, PRPA submitted a Self-Report stating that as a Generator Owner, it had a possible instance of noncompliance with MOD-025-2 R1. Specifically, PRPA reported that it failed to verify the Real Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue concerned PRPA’s misunderstanding regarding the testing criteria and the Standard’s implementation dates. PRPA believed the data collected during its previous testing was sufficient to meet the requirements of the Standard, and that each of its applicable units was not subject to retesting until 2018. Upon discovery of the issue, PRPA initiated an internal compliance investigation to identify discrepancies between the testing criteria of the WECC Model Validation Policy and Attachment 1 of MOD-025-2, and immediately scheduled testing to collect sufficient data. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of PRPA’s generating units, and ended November 21, 2016, when PRPA tested one of its peaking units, bringing PRPA into compliance with the current implementation schedule. The root cause of this issue was PRPA's misunderstanding of the enforceable date of the Requirement. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PRPA failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as PRPA tested all of its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Additionally, PRPA tested its largest unit ahead of the implementation deadline—its remaining applicable units are peaker units with collective capacity of 388 MW. No harm was known to have occurred. PRPA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, PRPA: 1) tested one of its peaker units, meeting the currently-effective implementation schedule for at least 40 percent of its applicable units; 2) scheduled testing for its remaining units to be completed well in advance of the next Standard implementation deadline; and 3) verified future scheduled testing of all applicable units will meet the five-year interval of the Standard. WECC verified completion of PRPA’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Platte River Power Authority (PRPA) | NCR05321 | WECC2016016359 | MOD-025-2 | R2 | On October 13, 2016, PRPA submitted a Self-Report stating that as a Generator Owner, it had a possible instance of noncompliance with MOD-025-2 R2. Specifically, PRPA reported that it failed to verify the Reactive Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue concerned PRPA’s misunderstanding regarding the testing criteria and the Standard’s implementation dates. PRPA believed the data collected during its previous testing was sufficient to meet the requirements of the Standard, and that each of its applicable units was not subject to retesting until 2018. Upon discovery of the issue, PRPA initiated an internal compliance investigation to identify discrepancies between the testing criteria of the WECC Model Validation Policy and Attachment 1 of MOD-025-2, and immediately scheduled testing to collect sufficient data. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of PRPA’s generating units, and ended November 21, 2016, when PRPA tested one of its peaking units, bringing PRPA into compliance with the current implementation schedule. The root cause of this issue was PRPA's misunderstanding of the enforceable date of the Requirement. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PRPA failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as PRPA tested all of its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Additionally, PRPA tested its largest unit ahead of the implementation deadline—its remaining applicable units are peaker units with collective capacity of 388 MW. No harm was known to have occurred. PRPA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this noncompliance, PRPA: 1) tested one of its peaker units, meeting the currently-effective implementation schedule for at least 40 percent of its applicable units; 2) scheduled testing for its remaining units to be completed well in advance of the next Standard implementation deadline; and 3) verified future scheduled testing of all applicable units will meet the five-year interval of the Standard. WECC verified completion of PRPA’s mitigating activities.
2017-01-30 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | WECC2016016594 | PRC-005-1.1b | R2 | On October 28, 2016, BHP submitted a Self-Log stating that, as a Transmission Owner, it had a possible instance of noncompliance with PRC-005-1.1b R2. Specifically, BHP reported that during a periodic Protection System Test/Maintenance Policy (PSMP) review session, BHP discovered that it failed to test and maintain 14 Protection System devices within the defined intervals. The root cause of this issue was a lack of understanding regarding the transition from one Standard version to another. Specifically, while transitioning Protection System devices from PRC-005-1b to PRC-005-2, an employee misunderstood the guidance and mistakenly changed to the calendar year maintenance interval prior to transitioning the devices. WECC determined that this issue began on January 19, 2016, the earliest instance in which a device in scope became past due for testing and maintenance, and ended July 21, 2016, when BHP completed maintenance and testing for all devices in scope. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BHP failed to test and maintain 14 Protection System devices within the defined intervals. Such failure could result in deterioration or misoperation of Protection System devices. However, as a corrective control, BHP completed maintenance and testing on the 14 Protection System devices within two months of discovering that the devices had exceeded their maximum maintenance interval. Additionally, BHP implemented a periodic PSMP review and identified the Protection System devices that had exceeded their PRC-005-1(b) interval during transition to PRC-005-2. As further compensation, the 14 Protection System devices had no known failures during the time they were past their maximum maintenance interval, and the devices compromised only 0.7% of BHP’s total devices. No harm was known to have occurred. For these reasons, this issue posed minimal risk to the reliability of the bulk power system. | To mitigate this noncompliance, BHP: 1) Completed the required maintenance for the 14 devices. 2) Continues to have periodic PSMP review sessions as a preventive measure to ensure all involved parties have an accurate and common understanding of new and revised Standard Requirements. WECC verified completion of BHP’s mitigating activities.
2016-12-29 | Florida Reliability Coordinating Council (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2016016452 | BAL-005-0.2b | R17 | On November 2, 2016, NSB submitted a Self-Report stating that, as a Balancing Authority (BA), it was in violation of BAL-005-0.2b R17. Since the Reliability Standard became enforceable on 9/13/2012, NSB failed to test and verify the accuracy of the backup frequency metering equipment as required. The violation duration was from September 13, 2012, to November 7, 2016. The root cause for this violation was NSB did not recognize the need to test the backup as well as the primary equipment. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Failure to test and verify the accuracy of its backup frequency monitoring equipment could lead to a lack of situational awareness in the event of adverse system conditions on the Bulk Electric System (BES) by providing the NSB operator with potential inaccurate reading of system frequency. In addition, the NSB Area Control Error (ACE) calculation may be inaccurate, causing the NSB system operator to take unnecessary action based on an incorrect ACE value. The risk was reduced by the primary device being tested and only the back-up source was not tested, NSB’s load is only .20% of the FRCC Region load minimizing any potential impact to the BES, and NSB has no Automatic Generation Control (AGC). No harm is known to have occurred. | To mitigate this violation, NSB: 1) has modified the testing form used to verify the accuracy of the primary frequency metering equipment to more clearly demonstrate the distinct test values, and an additional section has been added to include the backup measuring equipment; 2) conducted training with the substation operating personnel to ensure testing of primary and backup frequency devices; and 3) tested and verified the accuracy of the backup frequency metering equipment as required on 11/7/2016.
2016-12-29 | Florida Reliability Coordinating Council (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 | FRCC2016016453 | PRC-006-2 | R9 | On November 2, 2016, NSB submitted a Self-Report stating that, as a Distribution Provider (DP), it was in violation of PRC-006-2 R9. Since the Reliability Standard became enforceable on 10/1/2015, NSB failed to set four of its nine load shedding relays with the required time delay range as required by the FRCC Underfrequency Load Shedding (UFLS) program set out by its Planning Authority (PA), the FRCC. NSB did not include the breaker and relay delay when establishing the settings resulting in a potential increase of an additional 0.05-0.08 seconds before the load would be shed within the 0.28 seconds required by the PA. The violation duration was from October 1, 2015, to October 28, 2016. The root cause for this violation was failure to understand the FRCC program requirement was to include breaker and relay delay. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The improper shedding of load when required could lead to a potential increase in underfrequency, increasing the effect on the Bulk Electric System (BES). NSB had the potential to lag by approximately 0.05-0.08 seconds when required to shed The risk was reduced, however, because NSB’s load is only .20% of the FRCC Region, minimizing any potential impact. No harm is known to have occurred. | To mitigate this violation, NSB: 1) held a meeting was held with the Director of System Operations and the Substation and Relay (S&R) personnel to review the new settings and the requirements for timing tests. (10/25/2016) 2) re-programmed its UFLS relays to meet the new program inplemented by the FRCC PA. In this new program, NSB will now be using a single step of UFLS protection (based on the fact that NSB has projected summer peak load of less that 100 MW, which requires shedding at least 35% of load at 59.5 Hz. NSB has tested the re-programmed relays and determined that the time from frequency deviation to breaker open is within the required 0.1-0.28 seconds, as required in the FRCC UFLS program); (10/27/2016) and 3) submitted revised UFLS data to the FRCC PA; (10/28/2016)
2016-12-29 | Northeast Power Coordinating Council (NPCC) | Indeck - Oswego, LP (Oswego) | NCR10362 | NPCC2016016158 | PRC-005-2(i) | R3 | During a Compliance Audit conducted from April 29, 2016 through August 2, 2016, NPCC determined that Oswego, as a Generator Owner and Generator Operator, had an issue of PRC-005-2(i) R3. While reviewing evidence in preparation for the off-site audit, Oswego discovered that the site's station service batteries were categorized as VLA (Vented Lead-Acid) when they should have been categorized as VRLA (Valve Regulated Lead-Acid). Under PRC-005-2(i) Table 1-4b, VRLA batteries are required to have an internal ohmic value measurement every six months. Since Oswego miscategorized the batteries as VLA, the ohmic value measurements were being performed annually rather than every six months. Ohmic values for the station service batteries were taken in April 2015 then again in April 2016, therefore Oswego missed the ohmic value measurements required in October 2015. The duration of the violation was from November 1, 2015, when the six month interval was missed, to April 19, 2016, when the next ohmic value measurements were performed. The root cause of this noncompliance was a miscategorization of the station service batteries which led Oswego to use incorrect maintenance intervals from PRC-005-2(i). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Indeck - Oswego generating site is a small generating plant in upstate NY with a capability of 56 MW and no restoration responsibilities. All other maintenance activities were performed within the proper intervals by Oswego. Missing the six month ohmic value measurement for the station service batteries could lead to battery failure, however Oswego did perform quarterly battery testing as required in PRC-005-2(i) which allowed for the assessment of the health and performance of the station service batteries. The issue was caused by a miscategorization of the station service batteries, which was self-identified by Oswego, and quickly corrected by adjusting the maintenance tracking documents to ensure future ohmic value measurements are performed in the proper six month interval. No harm is known to have occurred as a result of this noncompliance. NPCC considered Oswego's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, Indeck - Oswego, LP: 1) Performed ohmic value measurements on the station service batteries; 2) Updated the maintenance records of the station service batteries to indicate the string is composed of VRLA batteries; and 3) Updated the battery inspection task report to indicate that internal ohmic testing will be performed every six months as required in PRC-005-2(i). NPCC has verified the completion of all mitigation activity.
2016-12-29 | ReliabilityFirst Corporation (ReliabilityFirst) | CPV Shore, LLC (CPV Shore) | NCR11585 | RFC2016015929 | PRC-005-2(i) | R3 | On July 14, 2016, CPV Shore submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-2(i) R3. During an internal review of its CPVS PRC-005-2(i) procedure, CPV Shore discovered that protection system maintenance and testing intervals for its unmonitored communications system did not document the functionality of the communication system. PRC-005-2(i) R3 requires documenting the functionality of the communication system at CPV Shore because that is the minimum maintenance activity. The procedure did not require CPV Shore to document that the unmonitored communications system is functional. CPV Shore has two unmonitored communication systems that are necessary for the correct operation of protective functions. (The two unmonitored communication systems are 87LA (SEL-387L) - Line Current Differential Relay and 87LB (SEL-311L) - Line Distance Relay and Current Differential Relay.) CPV Shore believes it completed the tests to show the functionality of the unmonitored communications system, but it does not have documentation from Quarter 4 of 2015 and Quarter 1 of 2016 that show the two unmonitored communication systems are functional. This noncompliance involves the management practice of verification because CPV Shore did not have an effective procedure in place to ensure that CPV Shore checked and documented the functionality of its two unmonitored communication systems. There was no checklist or other document that CPV Shore personnel were required to use to verify that it had a functioning procedure in place to help achieve compliance with PRC-005-2(i) R3. The root cause of this noncompliance was the lack of an effective verification control such as a checklist or other preventive maintenance document. This issue started on January 1, 2016, when CPV Shore did not check the functionality of the two unmonitored communication systems for Quarter 4 of 2015 and ended on June 30, 2016, when CPV Shore completed its Mitigating Activities by documenting and confirming that the two unmonitored communication systems were functioning properly. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that CPV Shore may not be aware that its unmonitored communications system is malfunctioning because it did not have documentation showing that it checked to see if it was functioning in Quarter 4 of 2015 and Quarter 1 of 2016. The risk is minimal here, however, because CPV Shore personnel frequently check the switchyard enclosure where both relays are located for general alarms and anomalies as part of station walk downs. As a result of these additional checks, CPV shore would be able to discover if the unmonitored communications system was not working. Therefore, this is primarily a documentation issue and the lack of documentation did not adversely impact the functionality of the communications system. Further, the CPV Shore Interconnect is a single generator tie-line to one substation. Lastly, there was no actual impact to the BPS from a lack of documentation as the relays communicated effectively throughout the duration of the noncompliance. No harm is known to have occurred. ReliabilityFirst considered CPV Shore’s PRC-005 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue: CPV Shore created a Preventative Maintenance document that requires CPV Shore personnel to verify and record the functionality of any unmonitored communications system necessary for correct operation of protective functions. The Protection System Maintenance Communication System Check document will be completed by CPV Shore personnel to verify and record that the communication system is functional for the aforementioned 87LA (SEL-387L) and 87LB (SEL-311L) relays. This new Preventative Maintenance document bolsters and clarifies CPV Shore’s process for verifying the functionality of its unmonitored communications system. The Protection System Maintenance Communication System Check document was completed by CPV Shore personnel on June 30, 2016 and will be used every four months to ensure the unmonitored communications system is functional.
2016-12-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Hoosier Energy Rec, Inc. (Hoosier) | NCR00794 | RFC2015014841 | PRC-005-1b | R2 | On March 31, 2015, Hoosier submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-005-1b R2. On November 26, 2007 Hoosier tested 124 relays at its Taswell Substation. This included relays at Taswell substation which operate 161kV breakers. In 2010 Hoosier replaced 121 of the 124 relays as a part of an upgrade of Taswell Substation. The Taswell upgrade resulted in 26 new microprocessor-based relays and three non-upgraded relays. The 26 new microprocessor relays were tested per Hoosier’s Protection System Maintenance and Testing Program (PSMTP) in 2010 as a part of the upgrade. The three non-upgraded relays were not scheduled for comprehensive testing per Hoosier’s PSMTP in 2010 and therefore were only functionally tested as part of the Taswell relay upgrade. In 2012 a subject matter expert (SME) identified the three non-upgraded relays for testing, in accordance with Hoosier’s PSMTP, however the test was not performed due to a field technician erroneously thinking the relays were tested two years earlier in 2010 as part of the relay upgrade. The three old relays were not tested until November 12, 2014 at which time the relays were tested with the 26 new microprocessor-based relays. Specifically, the three relays should have been tested in 2012 (five year interval) however they were tested 2 years later in 2014. During Hoosier’s annual review of its relay testing program on February 27, 2015, a SME identified that the three non-upgraded relays were not tested within the five year interval prescribed by Hoosier’s PSMTP. The root cause of Hoosier’s failure to perform testing within its PSMTP’s stated interval requirement was Hoosier’s unclear documentation of the relays that were upgraded and therefore on a different testing cycle than relays that were not upgraded and remaining on the original five year interval. Additionally, Hoosier lacked a more rigorous control that would have closed the loop between the field technician and SME as to the field technician’s decision not to perform the interval testing on the three relays at issue. The root cause involves the management practice of asset and configuration management and work management. The issue started on November 27, 2012, the date by which Hoosier was required to have tested the devices at issue and ended on November 12, 2014, the date Hoosier completed its testing of the three relays at issue. | Failure to perform the prescribed PRC-005 maintenance and testing can result in degraded performance or equipment failure and possible negative impacts to the bulk power system (BPS) such as load loss. ReliabilityFirst determined that the subject noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS based on the following factors. First, when the three non-upgraded relays were tested in 2014, all three relays performed as designed within acceptable tolerances. Second, two of the three relays that were tested out of interval were distance relays that were used for backup to the primary distance relays. Third, one of the three relays at issue is an auxiliary relay that was functionally tested within interval, however was not tested as prescribed by Hoosier’s PSMTP. The functional testing performed on this relay would have satisfied PRC-005-2 requirements had it been in effect at the time. Fourth, the upgraded microprocessor primary relays were tested within the required intervals which ensures proper maintenance was conducted on the more critical asset. Finally, as an additional protection, the microprocessor primary relays are monitored 24/7 electronically by Hoosier’s System Control Center so that any failure would have set off an alarm at System Control. One of the distance relays is also monitored locally, and any failure would have been discovered within 30 days. Additionally, ReliabilityFirst notes the three relays at issue did not misoperate during the time of noncompliance. No harm is known to have occurred. ReliabilityFirst considered Hoosier's PRC-005 R2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Hoosier implemented a process to improve its Asset Change Management by having its field technicians document, with a standard form, all future Protection Relay equipment change-outs (including replacements or upgrades). The field technician will submit the completed form to the Protection Engineer, who will review them for accuracy before forwarding them on the SME. This additional step in the process will close the loop and ensure accuracy between the field technician and the SME.
2016-12-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2016015492 | EOP-001-2.1b | R5 | On January 25, 2016, IPL submitted a Self-Report stating that, as a Balancing Authority and Transmission Operator, it had an issue of EOP-001-2.1b R5. During a mock audit, IPL discovered a discrepancy in its annual review of its planning and procedure documents that are relevant to emergency operations. The Mock Audit/Gap Analysis included all applicable Operating and Planning Standards based on IPL’s functional registration. IPL determined that it had 12 emergency operations documents detailing its philosophies and practices for preventing, dealing with, and mitigating system emergencies associated with EOP-001-2.1b, EOP-004-2, and EOP-008-1. IPL failed to review and update eight of these 12 documents in 2013. IPL failed to review and update five of these 12 documents in 2014. IPL did review all 12 documents in 2015, but the failure to review all 12 documents in 2013 and 2014 constitutes a violation of EOP-001-2.1b R5. This noncompliance involves the management practice of work management because IPL did not have an effective process in place to ensure that all 12 emergency operations documents were timely reviewed in 2013 and 2014. The root cause was an ineffective process that allowed for the review of these emergency operations documents to be missed in 2013 and 2014. There was confusion over which personnel were responsible for ensuring that all 12 emergency operations documents were timely reviewed. This issue started on January 1, 2014, when IPL missed reviewing its 12 emergency operations documents in calendar year 2013 and ended on December 31, 2015, the date IPL finished reviewing and approving all 12 documents to complete its 2015 annual review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. A failure to timely review and update the emergency plans, procedures, and associated documentation at issue could negatively affect the BPS because IPL employees may not know what to do and who to communicate with during operating emergencies. The risk is mitigated here because much of the information in each document that was not timely reviewed was partially represented in other documents that were reviewed annually as required. Additionally, the information in each document typically does not change much on an annual basis. Some of the procedures involve shared responsibilities with MISO as the Balancing Authority, and IPL participated in MISO’s emergency drills and reviewed parts of its emergency documentation in those exercises as well. No harm is known to have occurred. ReliabilityFirst considered IPL’s EOP-001 R5 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, IPL: 1) reviewed all 12 emergency operations documents in 2015. During that review, IPL evaluated each document to be certain it was relevant and still applicable to IPL business practices. As part of an information consolidation effort, where possible, IPL reduced the number of documents requiring annual review. IPL also consolidated emergency contact information into a single listing to be referenced by all plans/procedures; 2) improved critical document review and approval processes by including additional monitoring and controls necessary to ensure documentation is reviewed and updated in a timely manner. IPL clarified which personnel were responsible for ensuring that emergency operations documents were timely reviewed; and 3) examined and improved its education, engagement, and accountability for reviewing and updating documentation concerning emergency operations. IPL will provide additional educational opportunities to all levels of responsibility outlining the importance of current and accurate plans and procedures for emergency operations. IPL will provide targeted education to the individuals and areas responsible for maintaining these critical documents. IPL will ensure document review tasks are part of all appropriate training programs and are a part of each individual’s annual goals and objectives. The IPL NERC Compliance group will closely monitor engagement through monthly Subject Matter Expert meetings, email reminders, targeted conversations, and, if necessary, escalation to upper management.
2016-12-29 | SERC Reliability Corporation (SERC) | Entergy - Nuclear (EntergyNUC) | NCR11166 | SERC2016015876 | PRC-002-NPCC-01 | R14 | On July 1, 2016, EntergyNUC submitted a Self-Report to SERC stating that, as a Generator Owner, it had an issue with PRC-002-NPCC-01 R14. Entergy submitted the Self-Report to SERC under an existing multi-regional registered entity agreement. EntergyNUC reported that it had not initiated monthly tests of its disturbance fault recorder (DFR). In May 2015, during a refueling outage, EntergyNuc installed upgrades to a DFR located at the Pilgrim nuclear station to monitor 31 parameters on its 345 kV system including current and voltage of the start-up transformer. The work included the issuance of a preventive maintenance order (PM) to verify all active analog quantities in the DFR. However, the maintenance crew discovered that the PM did not include work steps to perform monthly verifications and the engineer assigned to the modifications was a new employee with no experience on the equipment. As a result, EntergyNuc incorrectly placed the PM in the suspend status in the maintenance database and EntergyNuc did not perform monthly verification of analog inputs to the DFR. On April 20, 2016, during discussions at a project meeting following the DFR modification installation, EntergyNuc became aware of the suspended status. The root cause was human error. EntergyNuc failed to include the necessary work tasks in the PM. The issue lasted from October 21, 2015, the first day after compliance was required, and ended on July 1, 2016, when PRC-002-NPCC-01 was retired. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EntergyNuc’s failure to provide adequate disturbance monitoring equipment could impede the assessment of system events. However, the disturbance recorders do not affect the actual operation and reliability of the Bulk Electric System elements. The analysis of the data occurs after a system event, not during normal operation. EntergyNuc experienced no system events that would have utilized the data captured by the recorders during the time that they were lacking recording capability on their facilities. No harm is known to have occurred. SERC considered EntergyNUC’s compliance history and determined that there were no relevant instances of noncompliance. | EntergyNUC did not implement mitigation activities for this specific issue because the PRC-002-NPCC-01 R14 requirement was retired on July 1, 2016. However to prevent recurrence, EntergyNUC will complete the following mitigation activities by December 30, 2016: 1) update the PM task with additional specific steps needed to perform verification of active analog quantities; 2) complete the next scheduled PM with the additional step to perform the analog input verification; 3) communicate to design engineering that further design changes will require the system engineer to be included in the routing chain so that they have an understanding of the change and the potential impact to the maintenance on the equipment; and 4) issue a formal action to the systems engineer for future development of preventive maintenance tasks. This will allow for documentation of the task, and formalize the process of alerting, acknowledging, and completing the task. This will also allow for further actions to be created as necessary to document requests for further information, and turnover of new systems from the design phase to the system owner phase.
2016-12-29 | SERC Reliability Corporation (SERC) | Entergy - Nuclear (EntergyNUC) | NCR11166 | SERC2016015877 | PRC-002-NPCC-01 | R5 | On July 1, 2016, EntergyNUC submitted a Self-Report to SERC stating that, as a Generator Owner it had an issue with PRC-002-NPCC-01 R5. Entergy submitted the Self-Report to SERC under an existing multi-regional registered entity agreement. EntergyNUC reported that it did not have 100% of its required monitoring in place by the required date, October 20, 2015. In May 2015, during a refueling outage, EntergyNuc installed upgrades to a disturbance fault recorder (DFR) located at the Pilgrim nuclear plant to facilitate monitoring 31 parameters on its 345 kV system including current and voltage of the start-up transformer (SUT). The work for the SUT inputs required new test switches for the three-phase voltage and current and ground current measurements. EntergyNuc failed to enable monitoring of the SUT parameters prior to the outage ending. The project personnel were aware of this condition and discussed the situation at a project meeting. That discussion started the formal evaluation of the risk of closing the test switches online. While performing the evaluation, project personnel lost sight of the requirement for full compliance by October 20, 2015. On April 20, 2016, during discussions at a project meeting, EntergyNuc became aware that it was not monitoring the SUT parameters; therefore, the compliance date passed without the required DFR monitoring in place. The root cause was human error. EntergyNuc failed to enable monitoring of the SUT parameters during the system outage. The issue lasted from October 21, 2015, the first day after compliance was required, and ended on July 1, 2016, when PRC-002-NPCC-01 was retired. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EntergyNuc’s failure to provide adequate disturbance monitoring equipment could impede the assessment of system events. However, the disturbance recorders do not affect the actual operation and reliability of the Bulk Electric System elements. The analysis of the data occurs after a system event, not during normal operation. EntergyNuc experienced no system events that would have utilized the data captured by the recorders during the time that they were lacking recording capability on their facilities. No harm is known to have occurred. SERC considered EntergyNUC’s compliance history and determined that there were no relevant instances of noncompliance. | EntergyNUC did not implement mitigation activities for this specific issue because the PRC-002-NPCC-01 R5 requirement was retired on July 1, 2016. However to prevent recurrence, EntergyNUC will complete the following mitigation activities by December 30, 2016: 1) complete the work for the start-up transformer inputs and return the digital fault recorder to service; 2) communicate to design engineering that further design changes will require the system engineer to be included in the routing chain so that they have an understanding of the change and the potential impact to the maintenance on the equipment; and 3) issue a formal action to the systems engineer for future development of preventive maintenance tasks. This will allow for documentation of the task, and formalize the process of alerting, acknowledging, and completing the task. This will also allow for further actions to be created as necessary to document requests for further information, and turnover of new systems from the design phase to the system owner phase.
2016-12-29 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2015015435 | VAR-002-4 | R2 | During a Compliance Audit conducted from September 8, 2015 through December 15, 2015, as per an existing multi-regional registered entity agreement, SERC determined that Duke Energy Corporation (DEC), as a Generator Operator (GOP), had an issue with VAR-002-4 R2. DEC did not maintain the generator voltage schedule provided by the Transmission Operator (TOP), or otherwise meet the conditions of notification for deviations from the voltage schedule provided by the TOP. DEC’s TOP voltage schedules state that the GOPs are to maintain the target voltage for the applicable units, and not wait until the voltage reaches the bounds before adjusting. As the voltage deviates from the target voltage, the GOP is expected to use available reactive capability of its unit(s) to stay as close to the schedule as possible. It is the responsibility of the GOP to meet the voltage schedule after synchronization. If a unit is not meeting its schedule for more than 30 minutes, the GOP will notify the TOP to state the reason and for guidance or instructions from the TOP. DEC recorded a set of data at the point specified in the voltage schedules and a second set of data at a point in the interconnecting substation. The substation voltages were typically higher than the voltages recorded at the generator terminals. When SERC reviewed the voltages recorded at the point specified in the voltage schedule, it identified one period at one location where voltage was outside of the range allowed by the voltage schedule. The exceedance was by 1 kV. DEC provided a sample of the GOP notifying the TOP of operations outside the voltage schedule, but DEC did not provide a report for the identified exceedance. The apparent cause of the issue was a lack of awareness that the voltage had exceeded the voltage schedule for more than 30 minutes. The issue lasted from June 15, 2015, when DEC had the first instance of voltages outside of the voltage schedule, until mitigated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). DEC’s failure to maintain the assigned voltage schedule could result in equipment damage or insufficient reactive resource for reliable system operation. However, identified deviations were only 1 kV from the TOP’s voltage schedule. The automatic voltage regulators were in automatic voltage control mode and there were no instances of voltage excursions causing system voltage problems. DEC provided voltage schedules and recorded generator voltages for 32 sampled weeks for 14 units. In the evidence provided, data showed seven instances with voltages outside the voltage schedules for greater than 30 minutes. However, none of the excursions exceeded 1.6 percent above or below the scheduled range, which SERC assessed as a minimal risk. DEC provided evidence that demonstrates that it generally maintains the voltage at its generating plants within the assigned voltage schedules and exceedances are not a chronic operational problem. The TOP received real-time generator voltage from each generating plant and only asked DEC’s plant operators one time to correct the output voltage. There were no issues on the DEC transmission system during this period that would have prompted corrective action under the TOPs Voltage and Reactive Management procedure. No harm is known to have occurred. DEC and its affiliates do not have a relevant compliance history with VAR-002-4 R2. | To mitigate this issue, DEC will complete the following mitigation activities by November 28, 2017: 1) establish voltage readout and active alarming in manned area for all stations in DEC; 2) train all DEC operators on voltage schedule operating expectations; and 3) verify alarm set points annually. The primary reason for the lengthy mitigation plan is that DEC is establishing voltage readouts and active alarming for all DEC stations.
2016-12-29 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2016015846 | PRC-008-0 | R2 | On June 23, 2016, Duke submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-008-0 R2. Duke identified Under Frequency Load Shed (UFLS) relays that did not have supporting documentation of maintenance and testing. On April 15, 2016 while preparing for a SERC audit, a Duke relay technician was reviewing maintenance and testing documentation and discovered one relay with insufficient maintenance or test documentation. The relay technician identified a relay on the Statesville tie where Duke had properly applied the UFLS settings but failed to document the maintenance or test data. In addition, Duke had not correctly flagged the relay in Duke’s equipment database, nor did Duke have it flagged correctly in its UFLS program database. Therefore, Duke failed to perform maintenance and testing as required by its UFLS program. In January 2014, Duke performed setting updates on the relay in question but did not document the maintenance or testing records. Duke performed a detailed review of its UFLS system records and found two additional relays with similar noncompliance. In April 2013, Duke did not test a relay at the Tiger tie, and in May 2015, Duke did not test a Campobello tie relay. Duke utilizes a total of 111 relays in a 3-step UFLS program. The affected relays are all related to step 2 (59.0 Hz), and could trip 112 MWs of Duke’s total of 6,996 MW in the UFLS program. The cause of this issue is that Duke did not properly flag the relays in the databases as providing UFLS functions. The issue started on April 29, 2013, when Duke did not retain maintenance and testing data at Tiger tie, and ended on October 15, 2016 when Duke completed the required maintenance and testing and provided training to the relay technicians. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Duke’s UFLS systems provide a “last ditch” effort to maintain Bulk Power System integrity during a large load to generation mismatch. Improper maintenance could have resulted in premature operation resulting in unnecessary loss of load or failure to operate resulting in an exacerbation of an under frequency event. However, the issue affects three of 111 (3%) relays in Duke’s system and less than 2% of its load in its UFLS program. All three relays were in the second step of UFLS protection and may not have been required to operate during a UFLS event. No UFLS events occurred during the period the issue existed. Duke found no issues with the relays when they were tested. No harm is known to have occurred. SERC considered Duke’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Duke: 1) performed the maintenance and testing on the relays in question; 2) compared Transmission Planning Duke Energy Carolinas 2016 UFLS program list with the ASPEN (DEC equipment database) to ensure all other UFLS elements had been tested; 3) updated the Relay Testing System (RTS) protecting field name to include “_UFLS” to identify specific UFLS relays; 4) created tags and applied local tagging to UFLS relays; and 5) developed and implemented a more detailed training package to technicians, which included communicating remedial steps to Relay technicians.
2016-12-29 | SERC Reliability Corporation (SERC) | East Kentucky Power Cooperative (EKPC) | NCR01225 | SERC2016015645 | PRC-005-2(i) | R3 | On April 5, 2016, EKPC submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-005-2 R3. EKPC did not implement the four-month requirement to inspect for unintentional grounds for station direct current (DC) power supply. In preparation for compliance with PRC-005-2, EKPC developed a new Protection System Maintenance Program (PSMP) document with an effective date of April 1, 2015. The program includes a required maintenance activity to inspect for unintentional grounds on Protection System station DC supplies. However, EKPC failed to create a work order in its computer maintenance management system (CMMS) for inspecting unintentional grounds on Protection System station DC supplies. As a result, EKPC failed to complete an inspection for unintentional grounds on each of its 37 battery banks. On March 15, 2016, EKPC identified this issue during an internal review in preparation for PRC-005-6 changes. EKPC was in the process of updating its PSMP as part of its NERC compliance annual document review. As part of the document review process, EKPC asked subject matter experts to review the latest version of the PRC-005 Standard and Requirements, and verify that the maintenance activities required were included in the maintenance programs. After the identification of the instant issue, EKPC completed an assessment of all maintenance activities required for PRC-005-2(i) and the EKPC PSMP in its CMMS and verified that the issue was limited to the inspection of the unintentional grounds. EKPC could not provide documentation of inspections for unintentional grounds for station DC power supply within the defined four-month interval for 37 of 37 batteries (100%). In total, SERC determined that EKPC could not provide evidence that 37 of 3,210 (1.15 %) Protection System devices were compliant with PRC-005-2 R3. EKPC determined that the primary cause of this issue was the lack of the required maintenance activities in the CMMS for unintentional grounds. The issue lasted from October 1, 2015, when PRC-005-2(i) became mandatory for activities with maximum intervals less than 1 calendar year, and ended on March 18, 2016, when EKPC completed the inspection for unintentional grounds for station DC power supply. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EKPC’s failure to provide documentation of inspections for unintentional grounds for station DC power supply within the defined four-month interval could have allowed unintentional grounds to exist on each pole of the battery. If an unintentional ground exists on each pole of the battery, there is a risk of degradation of the station battery. This could prevent the operation of protection schemes powered by that station battery. However, EKPC did not find any station batteries with issues. Of the 37 battery banks, 23 of the banks have a feature on the battery charger that monitors the battery bank for unintentional DC grounds. For those battery banks, if the charger detects an unintentional DC ground on the battery bank, an indication light on the battery charger illuminates. EKPC technicians should observe the illuminated indication light and detect the issue during their routine visual inspections of the battery bank and battery charger every three calendar months. In addition, EKPC’s PSMP in effect prior to April 1, 2015 included a task for the inspection of unintentional DC grounds as part of the routine battery maintenance on an interval of every two years. However, EKPC did not require documentation of the results of these inspections during this time-period. No harm is known to have occurred. SERC considered EKPC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, EKPC: 1) performed an inspection for unintentional grounds on all of the battery banks that were not inspected in accordance with the requirements in PRC-005-2(i); 2) added a maintenance activity involving the inspection of unintentional grounds on battery banks in the details of the work order for substation inspections in the CMMS. The maintenance interval for this activity will be 3-calendar-months as designated in the EKPC Protection System Maintenance Program (PSMP) document; 3) completed an assessment to verify that each maintenance activity required by PRC-005-2(i) and the EKPC PSMP for all Protection System components are included in their associated work order details; 4) provided PRC-005-2(i) training to EKPC personnel involved with the testing and maintenance of Protection Systems; and 5) added additional approval signature page to the EKPC PSMP for SME acknowledgement.
2016-12-29 | SERC Reliability Corporation (SERC) | East Kentucky Power Cooperative (EKPC) | NCR01225 | SERC2016015883 | PRC-019-2 | R1 | On July 7, 2016, EKPC submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. EKPC did not complete the required coordination for 40% of its generation capacity by the July 1, 2016, NERC implementation date. EKPC misinterpreted the implementation schedule to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. On or about June 15, 2016 in preparation for performing the coordination studies, EKPC conducted a review of the requirements and measures for PRC-019 and identified gaps. EKPC determined it needed assistance from outside consultants to perform the coordination studies, and by July 1, 2016, it completed the study for 30% of the EKPC generation capacity and by July 5, 2016, it completed 40%. However, EKPC calculated the percentage utilizing the total MVA of EKPC generation, not the number of generating units. On July 27, 2016, EKPC personnel attended a peer group meeting to review NERC Standards. During this meeting, EKPC discovered that other entities did not use the percentage of MVA methodology that EKPC utilized to calculate the 40% completion requirement. EKPC requested clarification from SERC, and on August 5, 2016, SERC provided a response. Based on the SERC clarification, EKPC determined that it used an incorrect methodology to calculate implementation percentage completion. EKPC incorrectly used gross total MVA rather than a count of individual generating units. Therefore the studies completed on July 1, 2016 and July 5, 2016 did not meeting the 40% implementation requirement. The root cause of the issue is that EKPC’s subject matter expert (SME) misunderstood the implementation plan date to have the coordination completed for 40% of the EKPC generation capacity. The SME misunderstood the schedule in the implementation plan as the date when entities were to start the coordination instead of the compliance date. The issue lasted from July 1, 2016, when the Standard became mandatory and enforceable, through September 29, 2016, when EKPC completed the required coordination for 40% of its generation facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EKPC’s failure to properly coordinate between generator protective relays and generator voltage regulator controls and limit functions could result in generators unnecessarily tripping off-line. However, EKPC completed the required 40% coordination just three months late. In addition, EKPC has approximately 3,000 MW of generation on a transmission system that has 19 interconnections with other transmission systems and is a member of PJM Interconnection, LLC. that would be capable of instantaneous response to any unnecessary unit trips. The NERC implementation plan allows EKPC to verify only 40% of its generation by July 1, 2016 and allows two additional years for the coordination of the remaining generation therefore a three-month delay of the 40% coordination completion results in minimal additional risk. No harm is known to have occurred. SERC considered EKPC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, EKPC: 1) analyzed two additional facilities in order to meet the milestone criteria of 40% of the facilities; 2) made changes to the relay protection settings as needed; 3) implemented steps to improve the structure and process that supports compliance with NERC Standards. EKPC assigned the Manager of Production Engineering as the Standard Owner and assigned additional technical personnel in the Production Engineering Department to the compliance process; and 4) conducted a thorough review and related training for PRC-019-2 and personnel attended a NERC compliance seminar.
2016-12-29 | SERC Reliability Corporation (SERC) | East Kentucky Power Cooperative (EKPC) | NCR01225 | SERC2016016042 | PRC-024-2 | R1 | On August 23, 2016, EKPC submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. EKPC did not meet the NERC implementation plan requirement to have 40% of its generation compliant by July 1, 2016. EKPC misinterpreted the implementation schedule to set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1 in two different ways. On or about June 15, 2016, EKPC conducted a review of the requirements and measures for PRC-024 to prepare for the studies and identified this issue and determined that EKPC needed assistance from outside consultants to perform the studies. EKPC consultants completed the study for 30% of the EKPC generation capacity by July 1, 2016 and 40% on July 5, 2016 based on a percentage calculation utilizing the total MVA of EKPC generation. On July 27, 2016, EKPC personnel attended a peer group meeting to review NERC Standards. During this meeting, EKPC discovered that other entities did not use the percent MVA methodology that EKPC utilized to calculate the 40% completion requirement. EKPC requested clarification from SERC. On August 5, 2016, SERC provided clarification to EKPC. Based on this clarification, EKPC determined that it used an incorrect methodology to calculate implementation percentage completion. EKPC incorrectly used gross total MVA rather than a count of individual generating units therefore the studies completed on July 1, 2016 and July 5, 2016 did not meet the 40% implementation requirement. The root cause of the issue is that EKPC’s subject matter expert (SME) misunderstood the implementation plan date to have the relay setting verification completed for 40% of the EKPC generation capacity. The SME misunderstood the schedule in the implementation plan as the date when entities were to start the coordination instead of the compliance date. The issue lasted from July 1, 2016, when the Standard became mandatory and enforceable, through September 30, 2016, when EKPC completed the required coordination for 40% of its generation facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to set protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” could result in generators unnecessarily tripping off-line. However, EKPC did not identify any required relay setting changes needed to comply with the Standard. As of July 1, 2016, EKPC completed the 33% of the facilities and 40.6% of the total system MVA. In addition, EKPC has approximately 3,000 MW of generation on a transmission system that has 19 interconnections with other transmission systems and is a member of PJM Interconnection, LLC. that would be capable of instantaneous response to any unnecessary unit trips. The NERC implementation plan allows EKPC to verify only 40% of its generation by July 1, 2016 and allows two additional years for the coordination of the remaining generation therefore a three-month delay of the 40% coordination completion results in minimal additional risk. No harm is known to have occurred. SERC considered EKPC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, EKPC: 1) analyzed two additional facilities in order to meet the milestone criteria of 40% of the facilities; 2) implemented steps to improve the structure and process that supports compliance with NERC Standards. EKPC assigned the Manager of Production Engineering as the Standard Owner and assigned additional technical personnel in the Production Engineering Department to the compliance process; and 3) conducted a thorough review and provided training to the appropriate staff for this standard.
2016-12-29 | SERC Reliability Corporation (SERC) | East Kentucky Power Cooperative (EKPC) | NCR01225 | SERC2016016043 | MOD-025-2 | R2. | On August 23, 2016, EKPC submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. EKPC did not meet the NERC implementation plan requirement to perform the Reactive Power verification per Attachment 1 and to provide its Transmission Planner (TP) with verification of the Reactive Power capability of its applicable Facilities for 40% of its generation by July 1, 2016. On or about June 15, 2016, EKPC identified the issue in preparation for performing the verification. EKPC completed the verification for 30% of the EKPC generation capacity by July 1, 2016 and completed 40% by July 5, 2016. However, EKPC calculated the percentage utilizing the total MVA of EKPC generation, not the number of generating units. On July 27, 2016, EKPC personnel attended a peer group meeting to review NERC Standards. During this meeting, EKPC discovered that other entities did not use the percentage of MVA methodology that EKPC utilized to calculate the 40% completion requirement. EKPC requested clarification from SERC. On August 5, 2016, SERC provided a response. Based on this clarification, EKPC determined that it used an incorrect methodology to calculate implementation percentage completion. EKPC incorrectly used gross total MVA rather than a count of individual generating units, and therefore, the studies completed on July 1, 2016 and July 5, 2016 did not meet the 40% implementation requirement. The root cause of the issue is that EKPC’s subject matter expert (SME) misunderstood the schedule in the implementation plan as the date when entities were to start the verification instead of the compliance date. The issue lasted from July 1, 2016, when the Standard became mandatory and enforceable, through September 30, 2016, when EKPC completed the analysis of four more facilities to meet 40% of its generation facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EKPC’s incorrect modelling of unit capabilities could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, EKPC completed the required 40% verification just three months late. In addition, EKPC has approximately 3,000 MW of generation on a transmission system that has 19 interconnections with other transmission systems and is a member of PJM Interconnection, LLC that would be capable of instantaneous response to any generation situation. The NERC implementation plan allows EKPC to verify only 40% of its generation by July 1, 2016 and allows two additional years for the verification and notification to the TP of the remaining generation therefore a three-month delay of the 40% requirement results in minimal additional risk. No harm is known to have occurred. SERC considered EKPC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, EKPC: 1) analyzed four additional facilities in order to meet the milestone criteria of 40% of the facilities; 2) submitted data sheets to PJM, the EKPC Transmission Planner, showing reactive capability tests conducted; 3) assigned the Manager of Production Engineering as the Standard Owner and assigned additional technical personnel in the Production Engineering Department to the compliance process; and 4) conducted MOD-025-2 training to the appropriate staff. SERC has verified that all mitigating activities were completed.
2016-12-29 | SERC Reliability Corporation (SERC) | East Texas Electric Cooperative, Inc. (ETEC) | NCR01227 | SERC2015015238 | FAC-009-1 | R1. | During an off-site Compliance Audit conducted from September 9, 2015 to September 10, 2015, SERC determined that ETEC, as a Generator Owner, had an issue of FAC-009-1 R1. ETEC did not determine Facility Ratings in accordance with its Facility Rating Methodology (FRM). The audit team found that ETEC’s FRM states that emergency ratings are set to normal ratings for generation step-up (GSU) transformers. However, ETEC’s established ratings did not set the emergency ratings to normal in its spreadsheet for the GSU. ETEC owns two 168 MW peaking facilities and one 50 MW renewable power facility. ETEC had an issue with correctly determining the Facility ratings at two of the three Facilities. ETEC had incorrect FRM parameter ratings in 16 instances and missing ratings in two instances. Although ETEC failed to follow its FRM, the issues had no effect on the most limiting element. The root cause was training. ETEC performed previous internal reviews and failed to identify the errors in the rating calculations completed by the plant staff, and that elements had both normal and emergency ratings that violate the FRM. ETEC engineering did not review or correct the ratings that the plant staff provided. The issue started on July 18, 2009, when ETEC commissioned the Facility and ended on November 30, 2016, when ETEC completed its mitigation plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ETEC's planning and operating simulation-based studies depend on accurate ratings to plan construction and to establish operating criteria such that the BPS can withstand a variety of pre-determined contingencies. However, ETEC correctly identified its most limiting element at each Facility. ETEC provided the correct capabilities for the units to its Balancing Authorities. In addition, ETEC did not operate the generation facilities above the most limiting element rating. No harm is known to have occurred. SERC considered ETEC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, ETEC: 1) revised the ratings spreadsheets to match the Facility Ratings Methodology and provided to Plant staff; 2) reviewed the facility ratings for San Jacinto County Peaking Facility (SJCPF) and Hardin County Peaking Facility (HCPF) and correct the incorrect values in the rating spreadsheet; 3) added the ratings for the point of interconnection facilities; and 4) provided training to plant staff on correctly calculating the FRM. SERC has verified the completion of all mitigation activity.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2016016070 | VAR-002-4 | R2 | On September 1, 2016, AECC submitted a Self-Report stating that, as a Generation Operator, it had an issue of noncompliance with VAR-002-4 R2. On July 24, 2016, between 4:00 and 5:15 p.m., AECC did not maintain the generator voltage schedule provided by its Transmission Operator (TOP) at its Oswald Generating Station, nor did it notify its TOP of the deviation from the voltage schedule. The point of interconnect voltage at AECC’s Oswald Generating Station dropped below the lower limit of the applicable TOP voltage schedule of 516 kV . The point of interconnect voltage remained .4kV or less below the lower limit for five 15 minute periods. The Senior Operator on duty at the time did not adjust the plant voltage master control to raise the plant reactive output to compensate for the low voltage or notify the TOP of the deviation. When interviewed after the event, the Senior Operator stated that he was unaware of the excursion and never heard the audible alarm. The root cause of this instance of noncompliance was human error due to the on-shift Senior Operator not adhering to plant operating procedures, which if followed, would have alerted him to the declining system voltage. The duration of this instance of noncompliance was from July 24, 2016 at 4:00 p.m., when AECC’s system voltage dropped below the lower limit of the TOP voltage schedule, through July 24, 2016 at 5:30 p.m., when system voltage was restored to the threshold level of 516 kV. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure of AECC to maintain its voltage schedule could have adversely effected the BPS by allowing system voltage to deviate from an acceptable range. In this instance, the plant voltage master control continued to control generator voltage during the excursion causing system voltage to never be more than 0.4 kV, or approximately 0.07%, below the lower voltage limit. No harm is known to have occurred. A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including AECC’s noncompliance with VAR-002-1 R2; R2.2 (SPP2014013570) and VAR-002-2 R2; R2.2 (SPP2014014420) was posted on the NERC website on May 28, 2015. The 60-day review period passed on July 30, 2015. Although this is a repeat of VAR-002, the underlying conduct of the prior two instances of noncompliance are different because one dealt with computer software problems affecting the voltage levels over a three-day period and the other concerned voltage level issues at multiple plants over an extended period of time. The instant case was an isolated event lasting only an hour and 15 minutes with the voltage staying .4kV or less below the lower limit of the TOP voltage schedule. SPP RE considered this compliance history and determined that the instant issue was appropriate for Compliance Exception treatment. | To mitigate this minimal risk instance of noncompliance, AECC: 1) counseled the Senior Operator who was on duty when the event occurred on the importance of remaining vigilant and following plant procedures; 2) retrained the affected Senior Operator on plant procedures; 3) tested the voltage page visual and audible alarms and verified that the alarms are working properly; 4) alerted all affected Senior Operators that: a. the voltage web page audio alarm should not be disabled while the plant is operating unless it has been approved by the Plant Manager or Assistant Plant Manager; b. if the voltage web page audio alarm is disabled for any reason: i. the on-shift Senior Operator is responsible for placing a note in the plant log book with the reason the audible alarm was disabled; ii. each Senior Operator shall inform their relief personnel that the alarm is disabled during shift change; and iii. the on-shift Senior Operator must note in the plant log book the date and time the alarm is re-enabled. SPP RE has verified the completion of all mitigation activity.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Buffalo Dunes Wind Project, LLC (Buffalo) | NCR11407 | SPP2016016237 | PRC-024-2 | R2 | On September 29, 2016, Buffalo submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Buffalo is a wind farm generating facility with 135 generating units applicable to PRC-024-2. Buffalo did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Buffalo’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Buffalo mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Buffalo erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Buffalo committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Buffalo is a 249.75 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Buffalo attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the December 18, 2013, commissioning date of the facility. No harm occurred. SPP RE reviewed Buffalo’s violation history and determined that Buffalo has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Buffalo will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Buffalo Dunes Wind Project, LLC (Buffalo) | NCR11407 | SPP2016016239 | PRC-024-2 | R1 | On September 29, 2016, Buffalo submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Buffalo is a wind farm generating facility with 135 generating units applicable to PRC-024-2. Buffalo did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Buffalo’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Buffalo mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Buffalo erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Buffalo committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Buffalo is a 249.75 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Buffalo attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the December 18, 2013, commissioning date of the facility. No harm occurred. SPP RE reviewed Buffalo’s violation history and determined that Buffalo has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Buffalo will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Caney River Wind Project, LLC (Caney) | NCR11230 | SPP2016016221 | PRC-024-2 | R1 | On September 28, 2016, Caney submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Caney is a wind farm generating facility with 111 generating units applicable to PRC-024-2. Caney did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Caney’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Caney mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Caney erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Caney committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Caney is a 199.8 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Caney attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the May 18, 2012 commissioning date of the facility. No harm is known to have occurred. SPP RE reviewed Caney’s violation history and determined that Caney has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Caney will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Caney River Wind Project, LLC (Caney) | NCR11230 | SPP2016016225 | PRC-024-2 | R2 | On September 28, 2016, Caney submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Caney is a wind farm generating facility with 111 generating units applicable to PRC-024-2. Caney did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Caney’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Caney mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Caney erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Caney committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Caney is a 199.8 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Caney attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the May 18, 2012, commissioning date of the facility. No harm is known to have occurred. SPP RE reviewed Caney’s violation history and determined that Caney has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Caney will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (Chisholm) | NCR11291 | SPP2016016242 | PRC-024-2 | R1 | On September 29, 2016, Chisholm submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Chisholm is a wind farm generating facility with 140 generating units applicable to PRC-024-2. Chisholm did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Chisholm’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Chisholm mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Chisholm erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Chisholm committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Chisholm is a 235.2 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Chisholm attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the December 7, 2012 commissioning date of the facility. No harm occurred. SPP RE reviewed Chisholm’s violation history and determined that Chisholm has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Chisholm will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (Chisholm) | NCR11291 | SPP2016016243 | PRC-024-2 | R2 | On September 29, 2016, Chisholm submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Chisholm is a wind farm generating facility with 140 generating units applicable to PRC-024-2. Chisholm did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Chisholm’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Chisholm mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Chisholm erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Chisholm committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Chisholm is a 235.2 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Chisholm attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the December 7, 2012 commissioning date of the facility. No harm occurred. SPP RE reviewed Chisholm’s violation history and determined that Chisholm has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Chisholm will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Cleco Corporation (CLECO) | NCR01083 | SPP2016015687 | FAC-008-3 | R3 | During a Compliance Audit conducted from April 19, 2016 through April 21, 2016, SPP RE determined that Cleco, as a Transmission Owner, had a minimal risk instance of noncompliance with FAC-008-3 R3, R3.2, and R3.2.3. The Audit Team determined that Cleco’s Facility Rating Methodology (FRM) did not state that it was utilizing the summer ratings of its transmission facilities in its planning models and SCADA system, or clearly identify how it was utilizing the Ratekit software to change its transmission facility ratings in real time based upon changes in the ambient temperature. Regarding the use of summer ratings, Cleco’s FRM states that it will establish Summer, Winter, and Spring/Fall ratings for its transmission facilities. Although Cleco establishes seasonal ratings for its transmission facilities, only the Summer ratings, the most conservative ratings, are used by Cleco. The Audit Team determined that Cleco’s FRM did not clearly indicate that only the Summer ratings are utilized in Cleco’s planning models and SCADA system. As to the use of the Ratekit software, Cleco’s FRM references a separate document, i.e., Temporary Adjusted Ratings Procedure, wherein Cleco describes how the Ratekit software is utilized to automatically adjust the rating of transmission facilities in its SCADA system based upon the ambient temperature. Such adjustments are applied in real time to the Summer rating of Cleco’s transmission facilities where the change in the transmission conductor rating due to ambient temperature changes results in a change in the rating of the transmission facility. The Audit Team determined that Cleco did not clearly identify in its FRM how the changes in conductor ratings are compared with the ratings of other transmission components to ensure the most limiting element of a transmission facility becomes the rating of the facility. The duration of this instance of noncompliance was from November 23, 2013, the day after Cleco’s last Operation and Planning Audit, through September 7, 2016, the date Cleco completed its mitigation of the noncompliance. The root cause of this instance of noncompliance was Cleco’s failure to adequately describe in its FRM its use of the multiple facility ratings it was establishing. Additionally, staffing changes created a disconnect between procedure development and application of the FRM. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although Cleco’s FRM did not clearly describe its use of summer ratings and the Ratekit software, Cleco’s planning models and SCADA system accurately reflected the ratings of its facilities. Accordingly, the facility ratings of Cleco’s transmission facilities were unaffected by this noncompliance. No harm occurred due to the noncompliance. Cleco has no relevant prior violations for FAC-008-3 R3 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, Cleco: 1. updated its FRM to include additional details regarding how the facility ratings are determined in relation to ambient temperatures; 2. included in the FRM the properties for calculating conductor, autotransformers, breakers, current transformers, wave traps, shunt capacitors, series reactors, phase angle regulating transformers, generator, and generator step transformer ratings using ambient conditions; 3. clarified in the FRM who is responsible for developing the ratings and how they are used by Cleco’s Transmission Operations and Planning organizations; and 4. trained Transmission Operations, Transmission Planning, and Transmission Reliability Operations departments as to how the facility ratings are calculated and used by the different departments. SPP RE has verified the completion of all mitigation activity.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Goodwell Wind Project, LLC (Goodwell) | NCR11574 | SPP2016016228 | PRC-024-2 | R1 | On September 29, 2016, Goodwell submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Goodwell is a wind farm generating facility with 100 generating units applicable to PRC-024-2. Goodwell did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Goodwell’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Goodwell mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Goodwell erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Goodwell committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Goodwell is a 200 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Goodwell attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the October 8, 2015 commissioning date of the facility. No harm occurred. SPP RE reviewed Goodwell’s violation history and determined that Goodwell has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Goodwell will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Goodwell Wind Project, LLC (Goodwell) | NCR11574 | SPP2016016229 | PRC-024-2 | R2 | On September 29, 2016, Goodwell submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Goodwell is a wind farm generating facility with 100 generating units applicable to PRC-024-2. Goodwell did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Goodwell’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Goodwell mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Goodwell erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Goodwell committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Goodwell is a 200 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Goodwell attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the December 8, 2015 commissioning date of the facility. No harm occurred. SPP RE reviewed Goodwell’s violation history and determined that Goodwell has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Goodwell will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Kansas City Power & Light Company (KCPL) | NCR01107 | SPP2016015575 | PRC-001-1.1 | R1 | On February 29, 2016, KCPL submitted a Self-Certification stating that, as a Transmission Operator, Balancing Authority, and Generator Operator, it had an issue of noncompliance with PRC-001-1.1 R1. Four newly designated KCPL Generator Operators (plant shift supervisors) did not receive prior training on the purpose and limitations of Protection System schemes applied in their area. Specifically, the plant shift supervisors were not trained on the generator protective relaying schemes. The duration of this instance of noncompliance was from June 1, 2013, the date the plant shift supervisors took their positions without receiving prior training, through April 4, 2016, the date the untrained plant shift supervisors received training. The root cause of this instance of noncompliance was lack of internal controls to ensure that training had been conducted prior to KCPL employees taking the plant shift supervisor positions. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to familiarize plant shift supervisors with the purpose and limitations of Protection System schemes has the potential to limit the situational awareness of KCPL’s operators and affect the reliability of the BPS. Notwithstanding, only four of the forty-one plant shift supervisors did not receive training; other control operators and employees on shift previously had training on the generator protective relay schemes. No harm is known to have occurred. KCPL has no relevant prior violations for PRC-001-1.1 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, KCPL: 1) trained all affected plant shift supervisors on generator protection relaying; and 2) developed and implemented quarterly checks for the Operations Program Specialist to verify appropriate plant personnel have been properly trained. SPP RE has verified the completion of all mitigation activity.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Origin Wind Energy, LLC (Origin) | NCR11496 | SPP2016016247 | PRC-024-2 | R1 | On September 30, 2016, Origin submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Origin is a wind farm generating facility with 75 generating units applicable to PRC-024-2. Origin did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Origin’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Origin mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Origin erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Origin committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Origin is a 150 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Origin attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the November 4, 2014 commissioning date of the facility. No harm occurred. SPP RE reviewed Origin’s violation history and determined that Origin has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Origin will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Origin Wind Energy, LLC (Origin) | NCR11496 | SPP2016016249 | PRC-024-2 | R2 | On September 30, 2016, Origin submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Origin is a wind farm generating facility with 75 generating units applicable to PRC-024-2. Origin did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Origin’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Origin mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Origin erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Origin committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Origin is a 150 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Origin attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the November 4, 2014 commissioning date of the facility. No harm occurred. SPP RE reviewed Origin’s violation history and determined that Origin has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Origin will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Rocky Ridge Wind Project (Rocky) | NCR11234 | SPP2016016267 | PRC-024-2 | R1 | On September 30, 2016, Rocky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Rocky is a wind farm generating facility with 93 generating units applicable to PRC-024-2. Rocky did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Rocky’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Rocky mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Rocky erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Rocky committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Rocky is a 148.8 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Rocky attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the May 29, 2012 commissioning date of the facility. No harm occurred. SPP RE reviewed Rocky’s violation history and determined that Rocky has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Rocky will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Rocky Ridge Wind Project (Rocky) | NCR11234 | SPP2016016269 | PRC-024-2 | R2 | On September 30, 2016, Rocky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Rocky is a wind farm generating facility with 93 generating units applicable to PRC-024-2. Rocky did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Rocky’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Rocky mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Rocky erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through February 3, 2017, the date Rocky committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Rocky is a 148.8 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Rocky attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the May 29, 2012 commissioning date of the facility. No harm occurred. SPP RE reviewed Rocky’s violation history and determined that Rocky has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Rocky will complete the following mitigation activities by February 3, 2017: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Farm, LLC (Smoky) | NCR11049 | SPP2016016274 | PRC-024-2 | R1 | On September 30, 2016, Smoky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Smoky is a wind farm generating facility with 56 generating units applicable to PRC-024-2. Smoky did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Smoky’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Smoky mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Smoky erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Smoky committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Smoky is a 100.8 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Smoky attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the October 27, 2010 commissioning date of the facility. No harm occurred. SPP RE reviewed Smoky’s violation history and determined that Smoky has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Smoky will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Farm, LLC (Smoky) | NCR11049 | SPP2016016275 | PRC-024-2 | R2 | On September 30, 2016, Smoky submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Smoky is a wind farm generating facility with 56 generating units applicable to PRC-024-2. Smoky did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Smoky’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Smoky mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Smoky erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Smoky committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Smoky is a 100.8 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Smoky attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the October 27, 2010 commissioning date of the facility. No harm occurred. SPP RE reviewed Smoky’s violation history and determined that Smoky has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Smoky will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Project II, LLC (Smoky II) | NCR10316 | SPP2016016258 | PRC-024-2 | R1 | On September 30, 2016, Smoky II submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R1. Smoky II is a wind farm generating facility with 99 generating units applicable to PRC-024-2. Smoky II did not verify that its protective relays were set such that its generators would not trip when system frequency is within the “no trip zone” of PRC-024 Attachment 1. The root cause of this instance of noncompliance was Smoky II’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Smoky II mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Smoky II erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Smoky II committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator frequency protective relaying in accordance with PRC-024-2 R1 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system frequency excursion, further aggravating the frequency event. Notwithstanding, Smoky II is a 148.5 MW variable generation wind farm that is generally not available to system operators to support system frequency. Additionally, Smoky II attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the April 3, 2009 commissioning date of the facility. No harm occurred. SPP RE reviewed Smoky II’s violation history and determined that Smoky II has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Smoky II will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether the relay settings currently in place are compliant with PRC-024-2 R1; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator frequency protective relays in accordance with R1 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Southwest Power Pool Regional Entity (SPP RE) | Smoky Hills Wind Project II, LLC (Smoky II) | NCR10316 | SPP2016016259 | PRC-024-2 | R2 | On September 30, 2016, Smoky II submitted a Self-Certification stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-024-2 R2. Smoky II is a wind farm generating facility with 99 generating units applicable to PRC-024-2. Smoky II did not verify that its protective relays were set such that its generators would not trip following a voltage excursion within the “no trip zone” of PRC-024 Attachment 2. The root cause of this instance of noncompliance was Smoky II’s error in calculating the effective date of PRC-024-2. The Implementation Plan for version one of PRC-024 states that the standard becomes effective “the first day of the first quarter, two calendar years following applicable regulatory approval . . . .” Because version one of PRC-024 was approved by FERC on March 20, 2014, it became effective on April 1, 2016. The Reliability Standard incorrectly identifies July 1, 2016 as the effective date. Version 2 of PRC-024 was approved by FERC on May 29, 2015. The Implementation Plan for version two of PRC-024 provides that “[a]ll aspects of the Implementation Plan for PRC-024-1 will remain applicable to PRC-024-2 . . . .” Therefore, the effective date for version two of PRC-024 is April 1, 2016. Smoky II mistakenly applied the language from the Implementation Plan for version one of PRC-024, specifically, “the first day of the first quarter, two calendar years following applicable regulatory approval,” to the FERC approval date of version two of PRC-024. As a result, Smoky II erroneously calculated the effective date of PRC-024-2 as April 1, 2017. The duration of this instance of noncompliance was from July 1, 2016, the effective date of the standard, through December 30, 2016, the date Smoky II committed to complete its mitigation for the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to set generator voltage protective relaying in accordance with PRC-024-2 R2 has the potential to affect the reliability of the BPS by increasing the risk that a generator could trip unnecessarily during a minor system voltage excursion, further aggravating the voltage event. Notwithstanding, Smoky II is a 148.5 MW variable generation wind farm that is generally not available to system operators to support system voltage. Additionally, Smoky II attested that its generation facility has operated without experiencing any voltage controller, excitation system, or PRC-024 related issues since the April 3, 2009 commissioning date of the facility. No harm occurred. SPP RE reviewed Smoky II’s violation history and determined that Smoky II has no prior instances of noncompliance with PRC-024. | To mitigate this issue, Smoky II will complete the following mitigation activities by December 30, 2016: 1) conduct a verification of whether generator voltage protective relay settings currently in place are compliant with PRC-024-2 R2; 2) if the relay settings are verified to be compliant, inform SPP RE and submit supporting evidence demonstrating compliance; 3) if the relay settings are found not to be compliant, set generator voltage protective relays in accordance with R2 without delay; and 4) revise its NERC Reliability Compliance Policy to require NERC standard implementation dates to be reviewed quarterly instead of annually and undergo at least two levels of review.
2016-12-29 | Texas Reliability Entity (Texas RE) | Brazos Wind, LP (BWIND) | NCR10210 | TRE2016015870 | PRC-019-2 | R1 | On July 1, 2016, BWIND submitted a Self-Report stating that, as a Generation Owner (GO), it had an issue with PRC-019-2 R1. Specifically, BWIND did not coordinate its voltage regulating system controls, including in-service limiters and protection functions, with equipment capabilities and settings of the Protection System devices and functions for its single generation Facility by July 1, 2016. In April 2016, BWIND began the process of identifying a third-party vendor to perform a voltage coordination study to determine if its voltage regulating system controls were properly coordinated with the applicable Protection System capabilities and settings at its sole generation Facility. After receiving bids from three contractors, BWIND ultimately contracted with a vendor to perform the required analysis on June 1, 2016. However, due to the scope of the required work, the vendor in question was not able to complete the initial voltage coordination assessment of BWIND’s Facility until August 30, 2016. Subsequently, on November 2, 2016, BWIND submitted additional documentation indicating that the settings on one capacitor were not set to operate as required. Based on this information, Texas RE determined that BWIND has not performed all the necessary voltage coordination for their generation Facility. The root cause of this issue was an insufficient process to ensure timely compliance with the voltage control coordination requirements set forth in PRC-019-2 R1. In particular, BWIND did not identify third-party vendors with sufficient lead time to perform the necessary voltage coordination studies and implement any corresponding settings changes to comply with the new voltage coordination requirements. Texas RE determined the duration of the issue to be from July 1, 2016, when PRC-019-2 R1 became mandatory and enforceable, through the present. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because of the following factors. First, BWIND’s generation Facility has a capacity rating of only 160 MW. Second, as a wind generator, BWIND’s generation Facility operates on an intermittent basis and therefore is not typically relied upon for voltage support. Third, BWIND has not experienced any unit trips based on lack of coordination of the voltage regulating system controls and protections systems throughout the duration of the issue. No harm is known to have occurred. Texas RE considered BWIND’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BWIND: 1) instituted a web-based action tracking tool designed to identify, prioritize, assign, and track corrective actions; 2) conducted training that covered an impact review analysis of upcoming NERC Reliability Standards; and 3) developed procedures to ensure adequate lead times to perform necessary compliance activities for new NERC Reliability Standards. Furthermore, BWIND submitted a Mitigation Plan to address the following actions that will be completed by March 30, 2017: 1) provide an updated draft PRC-019 Coordination Study that identifies and addresses relay setting recommendations to Texas RE for review; and 2) finalize revised PRC-019 Coordination Study, perform recommended coordination activities, and submit finalized PRC-019 Coordination Study to Texas RE. BWIND needs until March 30, 2017 to complete its Mitigation Plan in order to coordinate certain work activities with a third-party contractor and schedule an outage at its generation Facility to perform the necessary voltage coordination.
2016-12-29 | Texas Reliability Entity (Texas RE) | Quail Run Energy Partners, LP (QREP) | NCR11525 | TRE2016016219 | PRC-024-2 | R1 | On September 28, 2016, QREP submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-024-2 R1. Specifically, QREP did not set its protective relaying at its sole generation Facility such that the generator frequency protective relaying would not trip the applicable generating units within the “no trip zone” of PRC-024 Attachment 1. In April 2016, QREP contracted with an engineering firm to perform a review of its frequency trip set points for its single generation Facility. The results showed frequency trip settings within the “no trip zone” set forth in PRC-024-2, Attachment 1. To address this issue, QREP made arrangements in June 2016 to have contractors perform the necessary relay settings changes to address the issue. On three occasions in June, contractors attempted to make the necessary relay settings changes. On two occasions, however, they could not effectively communicate with the applicable protective relay devices. On the third occasion, the contractor had to suspend work due to a personal matter. As a result, QREP’s contractors were unable to complete the necessary relay settings changes until July 7, 2016. The root cause of this issue was that QREP did not ensure sufficient lead time to complete the required protective relay settings changes before PRC-024-2’s July 1, 2016 enforceable date. Texas RE determined the issue duration to be from July 1, 2016, when PRC-024-2 R1 became enforceable, until July 7, 2016, when QREP changed the applicable relay trip settings to meet PRC-024 requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following three reasons. First, the issue occurred for a short period of time, as the new frequency set points were corrected within seven days. Second, throughout the duration of the issue, the ERCOT interconnection had physical responsive reserves well in excess of the QREP Facility’s corresponding generation output. As such, even if a unit trip had occurred, ERCOT possessed adequate reserves to respond to any issues. Third, the single generation Facility at issue has never experienced a unit trip due to the applicable relay trip settings being set within the “no trip zone.” No harm is known to have occurred. Texas RE considered QREP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, QREP: 1) entered new frequency set points that meet the Standard Requirement for the ERCOT Interconnection; 2) recorded the relay passwords in case future setting changes are needed; 3) placed PRC-024 compliance tasks in the compliance tracking calendar software. The reminder lists the task plan, the task frequency, the person responsible, and the completion status. QREP will check the set points annually; 4) reviewed documentation and procedures for compliance with other applicable Standards to ensure that the plant had procedures for all applicable NERC Standards; and 5) enhanced the compliance review of the QREP facility by: a) holding monthly NERC review meetings; b) adding all new and updated program documents to the SharePoint site so that program documents are kept in one place; and c) conducting sampling and spot-checking the compliance documentation for accuracy and consistency. Additionally, QREP is conducting tri-annual Assessments that assess all applicable NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2016-12-29 | Texas Reliability Entity (Texas RE) | Quail Run Energy Partners, LP (QREP) | NCR11525 | TRE2016016075 | PRC-005-1.1b | R1; R1.1; R1.2 | On August 30, 2016, QREP submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-1.1b R1. Texas RE subsequently determined that the duration of this issue was from January 21, 2015 until October 14, 2016. Accordingly, Texas RE determined that although PRC-005-1.1b R1 was originally applicable to the issue in question, PRC-005-2(i) R1 currently applies to the facts and circumstances described in the self-report. Texas RE further determined that, for purposes of this issue, there was no substantive change in QREP’s compliance obligations under the applicable PRC-005 versions at issue during the noncompliance duration. On January 21, 2015, QREP acquired a new generation Facility from another entity and registered as a GO. As part of this transaction, however, QREP failed to obtain some testing documentation and the Facility’s existing PSMP from the previous owner. On February 27, 2015, QREP attempted to address this issue by developing a new PSMP. However, in drafting the new PSMP, QREP incorrectly assigned a 12-year maintenance interval to the Facility’s Control Circuitry instead of the required 6-year interval and omitted 4 communications devices from the PSMP altogether. In March 2016, QREP performed a periodic review of its PSMP, identified the incorrect maintenance intervals for its Control Circuitry, and assigned the correct 6-year maintenance and testing intervals to those devices. Subsequently, in October 2016, QREP performed a physical review of its Protection System inventory and identified the 4 omitted communications devices. On October 14, 2016, QREP revised its PSMP to include the 4 communications devices at issue. The root cause of this issue was that QREP did not possess an adequate process for ensuring compliance with applicable Reliability Standards upon acquisition of the Facility at issue. In particular, QREP failed to obtain maintenance and testing documentation for the Facility during the acquisition process and had additional issues ensuring that all required Protection Systems were properly included in the Facility’s PSMP. Texas RE determined the issue duration to be from January 21, 2015, when QREP acquired the Facility at issue, registered as a GO, and did not possess a documented PSMP, until October 14, 2016, when QREP included all required Protection Systems in its PSMP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for four reasons. First, QREP did not have a documented PSMP for only a short period of time, approximately one month following its acquisition of the Facility at issue. Second, Texas RE determined that the Facility’s previous owner had a PSMP for the Facility and likely tested most of the devices at least during the Facility’s 2007 commissioning process. Third, during the duration of the maintenance and testing issues here, the Facility had no Protection System misoperations. Finally, all Protection System devices subsequently tested by QREP had no maintenance issues. No harm is known to have occurred. Texas RE considered QREP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, QREP: 1) updated the PSMP to include all PRC-005-2 required categories of protection devices; 2) provided training on its PRC-005 PSMP and Implementation of PRC-005 to personnel in charge of implementing PRC-005; 3) reviewed documentation and procedures for compliance with other applicable Standards to ensure that the plant had procedures for all applicable NERC Standards; 4) enhanced its review process of the QREP facility to ensure accuracy and consistency in its compliance program, including holding monthly NERC Reliability Standard review meetings and uploading all program documentation to a central location; and 5) implemented a sampling and spot check review process for compliance documentation pertaining to all applicable NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2016-12-29 | Texas Reliability Entity (Texas RE) | Quail Run Energy Partners, LP (QREP) | NCR11525 | TRE2016016076 | PRC-005-1.1b | R2; R2.1; R2.2 | On August 31, 2016, QREP submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-1.1b R2. Specifically, QREP did not have documentation that certain Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing Program (PSMP). Texas RE subsequently determined that the duration of this issue was from January 21, 2015 until the present. Accordingly, Texas RE determined that for Protection Systems with testing intervals of less than one year, PRC-005-2(i) R3 also applied to the facts and circumstances described in the Self-Report. Texas RE further determined that, for purposes of this issue, there was no substantive change in QREP’s compliance obligations under the applicable PRC-005 versions at issue. On January 21, 2015, QREP acquired a new generation Facility from another entity and registered as a GO. As part of this transaction, however, QREP failed to obtain some testing documentation from the previous owner. Specifically, QREP did not have any testing documentation for 41 current transformers (CTs)/potential transformers (PTs), 15 DC Control Circuitry devices, and 4 communication devices. QREP discovered the missing testing records for the 41 CTs/PTs and 15 DC Control Circuitry devices at issue during a March 2016 review of its PRC-005 program documentation. On April 14, 2016, QREP performed the required testing on the 41 CTs/PTs. In addition, QREP began making arrangements to test the 15 DC Control Circuitry devices at issue during its planned 2017 outage. QREP subsequently discovered that it was also missing records for four communications devices during a review of its physical facilities in connection with it mitigation activities for this Self-Report. QREP performed the required testing on those four communications devices on October 17, 2016. The root cause of this issue was that QREP did not possess an adequate process for ensuring compliance with applicable Reliability Standards upon acquisition of the Facility at issue. In particular, QREP failed to obtain the necessary maintenance and testing documentation for the Facility during the acquisition process and had additional issues ensuring that all required Protection Systems were properly accounted for, documented, and therefore tested as required. Texas RE determined the issue duration to be from January 21, 2015, when QREP registered as a GO, through the present. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, during the duration of the maintenance and testing issues, the Facility did not experience any Protection System misoperations. Second, all Protection Systems devices subsequently tested by QREP had no maintenance issues. Third, Texas RE determined that the Facility’s previous owner maintained tracking documentation indicating that all DC Control Circuitry was tested. Fourth, the CT/PT and DC Control Circuitry devices at issue have 12-year maintenance and testing intervals, and QREP has performed or has scheduled to perform all required testing on those Protection System device categories within 12 years of the Facility’s 2007 commissioning date. No harm is known to have occurred. Texas RE considered QREP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, QREP: 1) performed the required testing on the 41 CT/PTs and 4 communications devices at issue; 2) updated its PSMP to include all required categories of protection devices listed in PRC-005-2; 3) provided training regarding all PRC-005 testing requirements and updated maintenance and testing procedures to the QREP personnel tasked with performing maintenance and testing activities; 4) enhanced its review process to ensure accuracy and consistency in its compliance program; 5) implemented a sampling and spot check review process to ensure compliance with applicable NERC Reliability Standards, including a periodic review of PRC-005 test reports; and 6) upgraded the Computerized Maintenance Management System (CMMS) to track upcoming testing activities for the Facility at issue. Furthermore, QREP submitted a Mitigation Plan to address the following actions that will be completed by July 1, 2017: 1) complete testing on the remaining DC Control Circuitry devices at issue; and 2) enter the next required testing dates in the upgraded CMMS system following completion of the applicable testing activities to ensure all devices are subsequently tested. QREP needs until July 1, 2017 to complete its mitigation actions because the required testing will occur during maintenance windows.
2016-12-29 | Texas Reliability Entity (Texas RE) | Sandy Creek Services, LLC (SCS) | NCR11182 | TRE2016016116 | MOD-025-2 | R2 | On September 8, 2016, SCS submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with MOD-025-2 R2. Specifically, SCS did not verify the Reactive Power capability of its generation units and synchronous condenser units as specified in MOD-025-2, Attachment 1 by July 1, 2016. MOD-025-2, Attachment 2 sets forth four required Reactive Power tests. SCS completed one of the tests, related to Over-excited Full Load Reactive Power Verification, on June 7, 2016. However, SCS erroneously assumed that several previous Reactive Power tests conducted pursuant to ERCOT-specific parameters likewise satisfied the new MOD-025 requirements relating to Under-excited Full Load Reactive Power Verification, Over-excited Minimum Load Reactive Power Verification, and Under-excited Minimum Load Reactive Power Verification. Specifically, during a review of the testing information in early September 2016, SCS determined that the previous tests were not actually performed using the required minimum and maximum Real Power output levels. Following this discovery, SCS completed the three required verifications using the appropriate Real Power output levels by September 20, 2016. The root cause of the issue was that SCS was not sufficiently familiar with the new MOD-025, Attachment 1 Reactive Power verification requirements. Specifically, SCS incorrectly assumed that the results of its previous Reactive Power testing under different output conditions could also be utilized to demonstrate compliance with the new MOD-025-2 Reactive Power verification requirements. Texas RE determined the issue duration to be from July 1, 2016, when the Standard Requirement became enforceable, until September 20, 2016, when SCS completed all required Reactive Power tests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the duration of this issue was short, with SCS completing all required Reactive Power verifications using the proper Real Power output levels within three months. Second, SCS properly performed the required Real Power verification and provided this information to its Transmission Planner as required. Third, SCS also previously provided passing Reactive Power verifications under ERCOT-specific output conditions, further limiting the scope of the missing verification data. No harm is known to have occurred. Texas RE considered SCS’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SCS: 1) completed the required testing pertaining to MOD-025-2 R2; 2) provided its TP with the required notification of its Reactive Power capability; 3) modified a Preventative Maintenance (PM) item in its compliance management tool (Maximo) that addresses MOD-025-2 compliance; 4) provided training to affected employees concerning the PM item; and 5) conducted training pertaining to the MOD-025-2 verification requirements to personnel with Real and Reactive Power verification responsibilities. Texas RE has verified the completion of all mitigation activity.
2016-12-29 | Texas Reliability Entity (Texas RE) | Texas Municipal Power Agency (TMPA) | NCR04141 | TRE2016016062 | PRC-005-1 | R2; R2.1 | During a Compliance Audit conducted from August 9, 2016 through August 26, 2016, Texas RE determined that TMPA, as a Generator Owner (GO), had an issue with PRC-005-1 R2.1. Specifically, Texas RE determined that TMPA did not have the required maintenance and testing records for two current transformers (CTs). In March 2010, TMPA contracted with a third-party vendor to perform required testing on certain CT devices. In performing this testing for one of TMPA’s auxiliary transformers, however, the contractor inadvertently tested only those CTs on the auxiliary transformer’s low side. As a result, the contractor did not perform the necessary testing on two CTs on the high side of the auxiliary transformer in question. The root cause of this issue was that TMPA did not have a process in place to verify that all required PRC-005 testing was completed by the third-party vendor as specified in the TMPA work order. Texas RE determined the issue duration to be from September 3, 2008, when TMPA registered as a GO, until June 11, 2016, when TMPA provided documentation that testing was completed for the two CTs at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the devices at issue represent only 1.3% (2/152) of all devices in TMPA’s PSMP. Second, no issues were detected with the devices during the subsequent testing. Third, no additional Protection System maintenance and testing issues were discovered during TMPA’s 2016 Compliance Audit. No harm is known to have occurred. Texas RE considered TMPA's compliance history in determining the disposition track. TMPA's relevant prior noncompliance with PRC-005 R1 includes TRE201000090 and TRE2015015128. Texas RE determined that TMPA's compliance history should not serve as a basis for applying a penalty because the current issue is distinguishable from the previous instances. In the first previous instance, TMPA failed to include maintenance and testing intervals for certain devices in its PSMP. In the second previous instance, TMPA failed to establish a basis for testing its Protection Systems within its PSMP. The current issue pertains to TMPA's failure to verify that all required PRC-005 testing activities were completed as listed in the work order. | To mitigate this issue, TMPA: 1) completed testing of the two CTs at issue; 2) incorporated an updated Computerized Maintenance Management System (CMMS) process and workflow procedure to ensure all required testing is completed as specified in its work orders; 3) provided training on TMPA’s PRC-005 procedures to relevant personnel; and 4) notified key personnel of the updated CMMS process and workflow procedures. Texas RE has verified the completion of all mitigation activity.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016015703 | TOP-002-2.1b | R17 | On April 29, 2016, BPA submitted a Self-Report stating that as a Transmission Operator (TOP) and Balancing Authority (BA), it had possible issues of noncompliance with TOP-002-2.1b R17. Specifically, BPA reported it had not been notifying the Reliability Coordinator (RC) when de-rated equipment caused changes in transmission facility ratings as required by R17. This issue included sixteen instances in which BPA failed to notify the RC after de-rating a transformer. These issues began July 1, 2013, the first instance in which BPA failed to notify the RC after de-rating a transformer, and ended February 25, 2016, when BPA reported the information to the RC. The root cause was less than adequate procedures addressing the notification requirements of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, BPA failed to notify the RC of changes to transmission facility ratings. Such failure limited the RC’s situational awareness and could have resulted in a scenario in which a transformer bank could exceed its rating and trip. However, because BPA is registered as a BA and operates on the same system, this issue only concerned its failure to notify the RC. Following discovery of this issue, internal analysis on the de-rated equipment indicated no changes to System Operating Limits (SOLs); therefore, no SOLs were exceeded and BPA never operated in an unstudied state during the period in question. No harm was known to have occurred. BPA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, BPA: 1) notified the RC of the changes in transmission facility ratings; 2) discussed the issue with its senior dispatchers; 3) revised its procedures concerning notification requirements of the Standard; and 4) highlighted the issue and resultant procedural revisions during its biannual dispatcher training. WECC verified completion of BPA’s mitigating activities.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2016015704 | TOP-002-2.1b | R16.2 | On April 29, 2016, BPA submitted a Self-Report stating that as a Transmission Operator (TOP) and Balancing Authority (BA), it had possible issues of noncompliance with TOP-002-2.1b R16.2. Specifically, BPA reported it had not been notifying the Reliability Coordinator (RC) when de-rated equipment caused changes in transmission facility ratings as required by R16.2. This issue included sixteen instances in which BPA failed to notify the RC after de-rating a transformer. These issues began July 1, 2013, the first instance in which BPA failed to notify the RC after de-rating a transformer, and ended February 25, 2016, when BPA reported the information to the RC. The root cause was less than adequate procedures addressing the notification requirements of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, BPA failed to notify the RC of changes to transmission facility ratings. Such failure limited the RC’s situational awareness and could have resulted in a scenario in which a transformer bank could exceed its rating and trip. However, because BPA is registered as a BA, this issue only concerned its failure to notify the RC. Following discovery of this issue, internal analysis on the de-rated equipment indicated no changes to System Operating Limits (SOLs); therefore, no SOLs were exceeded and BPA never operated in an unstudied state during the period in question. No harm was known to have occurred. BPA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, BPA: 1) notified the RC of the changes in transmission facility ratings; 2) discussed the issue with its senior dispatchers; 3) revised its procedures concerning notification requirements of the Standard; and 4) highlighted the issue and resultant procedural revisions during its biannual dispatcher training. WECC verified completion of BPA’s mitigating activities.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Deseret Generation & Transmission Co-operative (DGTII) | NCR05126 | WECC2016015864 | MOD-025-2 | R1 | On July 1, 2016, DGTII submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, DGTII reported that, following several emission reduction modifications to its only generating unit in the spring of 2016, DGTII delayed testing and re-commissioning the unit. As a result, DGTII failed to verify the Real Power capability of the unit in accordance with Attachment 1 by the effective date of the Standard. This instance of noncompliance began July 1, 2016 and will end May 23, 2017, when mitigated. The root cause of this issue was extensive delays surrounding modifications of DGTII’s single generating unit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, DGTII failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was the result of extensive delays surrounding modifications of DGTII’s single generating unit. Although DGTII scheduled testing in advance of the July 1, 2016 enforcement deadline, DGTII determined that pushing the unit to various limits could 1) result in collection of inaccurate data, and 2) risk equipment damage. Following discussions with WECC, DGTII intentionally delayed MOD-025-2 testing in order to capture more accurate data once the unit reached a state of equilibrium. No harm is known to have occurred. DGTII does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, DGTII will test the unit. Because this issue concerns a single unit, there is no risk of recurrent failure to implement this Standard in accordance with future enforcement deadlines. The proposed completion date for the above-listed activities is May 23, 2017.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Deseret Generation & Transmission Co-operative (DGTII) | NCR05126 | WECC2016015865 | MOD-025-2 | R2 | On July 1, 2016, DGTII submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R2. Specifically, DGTII reported that, following several emission reduction modifications to its only generating unit in the spring of 2016, DGTII delayed testing and re-commissioning the unit. As a result, DGTII failed to verify the Reactive Power capability of the unit in accordance with Attachment 1 by the effective date of the Standard. This instance of noncompliance began July 1, 2016 and will end May 23, 2017, when mitigated. The root cause of this issue was extensive delays surrounding modifications of DGTII’s single generating unit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, DGTII failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue was the result of extensive delays surrounding modifications of DGTII’s single generating unit. Although DGTII scheduled testing in advance of the July 1, 2016 enforcement deadline, DGTII determined that pushing the unit to various limits could 1) result in collection of inaccurate data, and 2) risk equipment damage. Following discussions with WECC, DGTII intentionally delayed MOD-025-2 testing in order to capture more accurate data once the unit reached a state of equilibrium. No harm is known to have occurred. DGTII does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, DGTII will test the unit. Because this issue concerns a single unit, there is no risk of recurrent failure to implement this Standard in accordance with future enforcement deadlines. The proposed completion date for the above-listed activities is May 23, 2017.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2016015857 | BAL-004-WECC-02 | R3 | On June 24, 2016, IPCO submitted a Self-Report stating that as a Balancing Authority, it had a possible issue of noncompliance with BAL-004-WECC-02 R3. Specifically, IPCO reported that on May 13, 2016, one of its operators inadvertently disabled the WECC Automatic Time Error Correction (ATEC) in its system. On May 31, 2016, IPCO noted that the Accumulated On-Peak and Off-Peak Primary Inadvertent Interchange balances were getting larger, investigated the cause of the issue, and immediately enabled the ATEC. This issue began May 14, 2016, when IPCO exceeded the accumulated out-of-service allowable exception period for Quarter 2 of 2016, and ended June 30, 2016, when the allowable exception period reset for Quarter 3 of 2016. This issue was caused by human error; specifically, incorrect performance due to mental lapse. The operator was cycling between four screens and had no recollection of disabling the ATEC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, IPCO failed to keep its ATEC in service for a timeframe that exceeded its 24-hour quarterly exception period. Such failure could have resulted in excessive accumulation of Primary Inadvertent Interchange, which would have required frequent manual time error corrections and increased the likelihood of frequency deviations. However, IPCO continued to control its Area Control Error (ACE) and schedule throughout the duration of this issue. Additionally, in accordance with R1 of the Standard, as of May 31, 2016 IPCO’s On-Peak and Off-Peak Accumulated Primary Inadvertent Interchange values were individually less than 150% of the previous calendar year’s integrated hourly Peak Demand. No harm was known to have occurred. IPCO does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, IPCO: 1) re-enabled the ATEC; and 2) established an alarm to inform the operator when the ATEC is disabled in the future. WECC verified completion of IPCO’s mitigating activities.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Modesto Irrigation District (MID) | NCR05244 | WECC2016015860 | EOP-001-2.1b | R5 | On June 29, 2016, MID submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with EOP-001-2.1b R5. Specifically, MID reported that it failed to distribute its updated emergency plan to requisite entities in 2015. This issue began January 1, 2016, MID’s internal deadline for distributing the updated report, and ended April 29, 2016, when MID distributed the updated report. The root cause of this issue was insufficient internal controls to ensure distribution of the plan following MID’s annual review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, MID failed to timely provide a copy of its updated emergency plan to its Reliability Coordinator (RC) and to neighboring Transmission Operators (TOPs) and Balancing Authorities (BAs). Such failure could have delayed coordinated efforts to mitigate an operating emergency. However, during the period in question, MID’s RC and neighboring TOPs and BAs had copies of the previous version of MID’s emergency plan. MID only made minor revisions in its 2015 plan, which were not significant to neighboring entities and would not have been used by neighboring entities during an operating emergency. MID discovered this issue within four months of the oversight, and immediately distributed the plan when the issue was discovered. No harm is known to have occurred. MID does not have relevant prior noncompliance with this Standard and Requirement. | To mitigate this issue, MID: 1) provided a copy of its updated emergency plan to all requisite entities; 2) modified the automated reminder for its annual review to ensure personnel a) distribute the updated plan, and b) are aware of which entities require a copy of the updated plan; 3) revised its procedural documentation to ensure annual distribution is tracked; and 4) trained relevant staff regarding this revision. WECC verified completion of MID’s mitigating activities.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Public Service Company of New Mexico (PNM) | NCR05333 | WECC2016015563 | EOP-005-2 | R4 | On June 17, 2007, PNM was registered on the NERC Compliance Registry as a Transmission Operator. Therefore, PNM is required to comply with EOP-005-2 R4. On February 19, 2016, PNM submitted a Self-Report stating that, as a Transmission Operator, it had a possible issue of noncompliance with EOP-005-2 R4. Specifically, PNM reported that during a CIP-002 evaluation, it discovered that it had bisected a transmission line identified in the Restoration Plan as a primary element in the San Juan-Reeves cranking path, but it had not modified its Restoration Plan prior to making the planned Bulk Electric System (BES) modifications. Specifically, on October 23, 2015, PNM energized the San Juan-Rio Puerco 345 kV (WW) Line, and on October 28, 2015 PNM energized the Rio Puerco- BA 345 kV (CJ) Line, but did not modify the PNM Restoration Plan to include these changes until it submitted the restoration Plan to the Reliability Coordinator on December 17, 2015. The Reliability Coordinator approved the plan with an effective date of January 1, 2016. PNM performed a root cause analysis with a trained, independent facilitator and identified three root causes for the noncompliance: 1) PNM did not require an independent quality check for its Restoration Plan updates, 2) PNM had no administrative control for updates or changes to System Operations' documentation, and 3) PNM’s monthly Operations and Planning Meeting materials did not specifically identify associated NERC requirements. WECC determined that this issue began on October 23, 2015, when PNM energized the San Juan–Rio Puerco Line, but did not modify its Restoration Plan to include the changes. WECC determined that the end date of this issue is December 17, 2015, when PNM submitted its modified Restoration Plan to the Reliability Coordinator. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PNM failed to update its Restoration Plan prior to implementing planned BES modifications that would change the implementation of its Restoration Plan. Changes to system topology that affect implementation of the Restoration Plan, and in particular changes to a cranking path could result in a failure to establish startup power as planned. However, in this instance, breaking the line reduces the line charging during restoration and gives access to an additional 65 MVAR Reactor. Voltage is more manageable with the additional reactor, making system restoration easier. During the time PNM had not updated its Restoration Plan, the other two remaining primary cranking paths were available. No harm is known to have occurred. PNM implemented compensating controls. Specifically, PNM’s system operators would have carried out nearly the same procedures, would have visibility of the modified system, and would be able to restore it. Specifically, PNM has reminders to ensure that the annual reviews occur, although not specifically for modification projects. For these reasons, WECC determined that this issue posed a minimal risk to the reliability of the Bulk Power System (BPS). | To remediate this issue of noncompliance, PNM revised the Restoration Plan on December 17, 2015, to include the planned system updates on October 23, 2015 and October 28, 2015. On July 25, 2016, PNM submitted a Mitigation Plan to address its noncompliance with a proposed completion date of April 30, 2017, and on November 9, 2016, WECC accepted PNM’s Mitigation Plan. To mitigate the root-cause, PNM wil complete the following mitigation activities by Arpil 30, 2017: a) Revise its Restoration Plan for system modifications; b) Develop cross-references to applicable NERC Standards requirements in its Monthly Power Operations - Transmission Planning meeting; c) Develop an inventory list of Emergency Operations documents; d) Develop an inventory list of Compliance Policies; e) Develop an inventory list of Transmission and Reliability Guidelines; and f) Implement a formal process for Restoration Plan updates. The mitigation plan as proposed will reduce the likelihood of reoccurrence by implementing multiple new preventive internal controls, including formalize the Restoration Plan update process, adding independent reviews prior to publishing revisions to the Plan, and implementing a master list of operations documents and their characteristics for use as a quick reference guide by Operations personnel when updating documentation following notification of a planned system modification. This mitigation plan corrects the non-compliance, but also mitigates the root causes identified in PNM’s root cause analysis process.
2016-12-29 | Western Electricity Coordinating Council (WECC) | PUD No. 1 of Douglas County (DOPD) | NCR05343 | WECC2016015912 | PRC-024-2 | R2 | On July 8, 2016, DOPD submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-024-2 R2. Specifically, on June 30, 2016, DOPD discovered an error in the calculation for the time-delayed overvoltage trip setting on its generating units. As a result, protective relays associated with at least 40% of DOPD’s applicable Facilities—in this case, generating units subject to PRC-024-2—were not set in accordance with Attachment 2 by the effective date of the Standard. This issue began July 1, 2016, when implementation of PRC-024-2 R2 became mandatory and enforceable for 40% of DOPD’s applicable generating units, and ended July 5, 2016, when DOPD adjusted the setting. This issue was caused by less than adequate change management concerning PRC-024-2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, DOPD failed to set its protective relaying such that generator voltage protective relaying would not trip applicable generating units unnecessarily. Such failure could result in the premature trip of one or more generating units offline due to voltage excursions within the “no trip zone”. However, DOPD discovered this issue prior to, and remediated within days of the implementation deadline. The previous setting on the relays in scope has never caused a trip due to time-delayed overvoltage. No harm is known have occurred. DOPD does not have previous violations of this Standard and Requirement. | To mitigate this issue, DOPD: 1) corrected and tested the setting on protective relays associated with applicable generating units; and 2) added an annual review of the PRC-024-2 RSAW and supporting documentation in its compliance work management system. WECC verified completion of DOPD’s mitigating activities.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2016016015 | MOD-025-2 | R1 | On August 10, 2016, PSE submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with MOD-025-2 R1. Specifically, PSE reported that it failed to verify Real Power capability of at least 40 percent of its generating units in accordance with Attachment 1 by the effective date of the Standard. This issue began July 1, 2016, when implementation of MOD-025-2 became mandatory and enforceable for 40 percent of PSE’s generating units, and is ongoing. PSE is scheduled to complete testing of at least 40 percent of its generating units in accordance with Attachment 1 by November 30, 2016. The root cause of this issue was PSE's misunderstanding of the enforceable date of the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PSE failed to complete requisite testing and verification in accordance with the Standard’s implementation deadline. Such failure could result in use of untimely or inaccurate information in planning models used to assess Bulk Electric System reliability. However, this issue would not likely have significantly affected current planning models as PSE tested its units in accordance with the WECC Model Validation Policy prior to the effective date of MOD-025-2. Additionally, this issue largely concerned PSE’s misunderstanding regarding the Standard’s implementation dates. Prior to the effective date, PSE developed a testing procedure and test form, and scheduled tasks relating to implementation of the Standard in its work management system. This preparation enabled PSE to expedite mitigating efforts upon discovery of the issue. No harm is known to have occurred. PSE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) scheduled testing for 40 percent of its generating units; 2) verified and updated deadlines in its work management system to ensure future tasks will be completed per the implementation schedule in the Standard; and 3) revised its process for tracking and clarifying potential ambiguity concerning upcoming Standards.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2016016017 | IRO-010-1a | R3 | On August 12, 2016, PSE submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with IRO-010-1a R3. Specifically, PSE reported that it failed to notify its Reliability Coordinator (RC) that its Real-Time Contingency Analysis (RTCA) application tool was unavailable for more than fifteen minutes, in accordance with the RC’s protocol for such a scenario. On June 30, 2016, PSE installed two system updates on its Energy Management System (EMS). The RTCA tool did not automatically trigger following application of the first update at 12:15 p.m. PSE discovered and resolved the issue roughly eight hours later, and informed the RC of the incident on July 14, 2016. This issue began June 30, 2016, when the RTCA tool in PSE’s EMS became unavailable, and ended July 14, 2016, when PSE notified the RC of the incident. The root cause of this issue was PSE's failure to recognize that its loss of RTCA functionality required notification to the RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PSE failed to notify the RC that its RTCA tool was unavailable for more than fifteen minutes. Such failure limited the RC’s ability to prepare for issues related to PSE’s decreased visibility of potential contingencies on its system. However, the RC actively monitors and assesses the operation of all systems in its area, and uses its own RTCA tool. Additionally, PSE’s system is alarmed for System Operating Limit exceedances. PSE did not experience any events in its system during the period in question. Had an event occurred, the RC would have coordinated with PSE to resolve the issue. Although the application failure was likely caused by a technical error, neither PSE nor the EMS vendor could duplicate the problem. Both updates were cleared by PSE prior to implementation as part of its change control process. This issue represented failure on PSE’s part to fulfill only one of 53 specifications applicable to this Standard. No harm is known to have occurred. PSE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) troubleshot and reengaged the RTCA application; 2) notified the RC; 3) revised its EMS release checklist to ensure the RTCA application functions as expected after EMS updates; and 4) debriefed requisite staff regarding the issue and reemphasized existing protocol to contact the RC and document RTCA issues. To prevent recurrence of this issue, PSE is working with the EMS vendor to: 1) establish a root cause for the technical error; and 2) create an alarm to notify dispatchers when the RTCA is inactive for more than ten minutes. The proposed completion date for the above-listed activities is December 31, 2016.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Silicon Valley Power (SNCL) | NCR05392 | WECC2016015446 | PRC-005-2(i) | R3 | On January 5, 2016, SNCL submitted a Self-Report stating that, as a Transmission Owner, Generator Owner, and Distribution Provider, it had an issue of noncompliance with PRC-005-2(i) R3. Specifically, on December 9, 2015, while SNCL was performing maintenance and testing activities for its Protection System Components, the relay team identified a pair of SEL and ABB relays on substitute breaker 422 that had not been tested. Testing at this location requires approximately 30-days’ notice to coordinate activities with the interconnecting Transmission Operator, and the switching order to do the maintenance had not been placed. The devices were last maintained on November 4, 2009 and November 5, 2009. In order to meet the 6-year time-based testing intervals in SNCL’s maintenance program, SNCL was required to test the relays on or before December 31, 2015. WECC determined that this issue began on January 1, 2016, when SNCL failed to perform maintenance on the two relays, and ended on January 7, 2016, when testing was scheduled to be completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SNCL performed maintenance on two relays approximately seven days outside the maximum maintenance interval. Failing to maintain protections systems could lead to degradation or possible damage to associated devices if the relays failed to perform as expected. However, Breaker 422 is a substitute breaker and was not in service; the primary and backup line relays associated with this substitute breaker are utilized only in the event of Breaker 442 repairs, or failure of protective devices associated with Breaker 442. The line relays, DC trip path and any communication associated with substitute Breaker 422 were tested in November, 2009 and performed as expected. No harm is known to have occurred. As a compensating measure, SNCL discovered this issue before the relays were past their maximum maintenance interval. SNCL implemented a switching order, but the switching order that needed to be coordinated with the TOP took 35 days, putting the substitute relays past their maximum maintenance interval. As a compensating control, SNCL implemented a switching order with the TOP after the oversight was discovered. | To mitigate this issue, SNCL: 1) Coordinated the necessary switching orders with neighboring TOP and schedule the testing accordingly; and 2) Will prevent future recurrence by implementing MS Outlook calendar alerts and automated notifications to ensure that the necessary switching orders are placed at least 35 days in advance of the scheduled relay work.
2016-11-30 | Florida Reliability Coordinating Council (FRCC) | NAES Corporation - Shady Hills (NCSH) | NCR00069 | FRCC2016015976 | FAC-008-3 | R2; R2.4.1 | During a Spot Check conducted from March 3, 2016 to August 3, 2016, FRCC Auditors determined that NCSH, as a Generator Owner, had an issue of FAC-008-3 R2. This issue started on February 25, 2015, when the NCSH Facility Ratings methodology document was approved and enforceable and is on-going. Specifically, NCSH's facility rating methodology excluded relay protective devices from its facility rating methodology document; while these devices are explicitly required by FAC-008-3 R2, Part 2.4.1. The root cause of this noncompliance was that NCSH personnel incorrectly categorized its relay protective devices as "sensing devices," and would not affect the overall facility ratings; therefore NCSH did not include them in their facility rating methodology document. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NCSH's facility ratings methodology failed to document that relay protection devices ratings were included in its rating methodology, as required by FAC-008-3 Part 2.4.1. The Facility Ratings Methodology (from the previous owner) demonstrated that in the Facility Ratings of the facility, "Relay protective devices" had been considered as part of the methodology. However, when NAES took over the facility and implemented the NAES program (effective date of procedure 2/25/15) the "Relay Protective devices" were not included in the methodology. The actual Facility Ratings were not changed when NCSH took over the facility, only the Facility Ratings methodology were changed. No harm is known to have occurred. FRCC determined that NCSH’s compliance history should not serve as a basis for applying a penalty because they occurred under a previous owner in 2010. | To mitigate this issue, NCSH: 1) completed a walk down of the Facility to verify the accuracy of the Facility Rating Methodology, the walk down was by a third party (Senior Staff members from another NAES Facility); 2) modified the NCSH spreadsheet (Protection System Relays) to include relays as part of the Facility Rating Methodology. This spreadsheet lists the applicable Protection System Relays and identifies their settings do not limit the output of the facility; and 3) created a spreadsheet (Overcurrent Calculation to MVA) to convert overcurrent relay trip set points to an MVA value. This document demonstrates the trip settings of Protection System devices do not limit the output of the Facility. To mitigate this issue, NCSH will complete the following mitigation activities by 10/7/16: 1) update RCP-NERC-FAC-ATT-008 to include Protection System relays and all other feedback associated with the spot check.
2016-11-30 | Florida Reliability Coordinating Council (FRCC) | New Smyrna Beach, Utilities Commission of (NSB) | NCR00052 . | FRCC2016016104 | BAL-003-1.1 | R2 | On August 31, 2016, NSB submitted a Self-Report stating that, as a Balancing Authority (BA), it was in violation of BAL-003-1.1 R2. NSB failed to update the Frequency Bias Setting (FBS) component of its Area Control Error (ACE) calculation by the April 5, 2016 implementation period specified in the notification from the Electric Reliability Organization (ERO) on March 28, 2016 of the revised values. NSB had a value of -1.0 MW/0.1Hz and should have changed to the new ERO supplied value of -0.34 MW/0.1Hz. The root cause for this violation is NSB had no procedure to ensure that its personnel changed the Frequency Bias or the L10 value; therefore, the employee responsible forgot to ensure it was done correctly. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to update its FBS could have caused NSB to incorrectly compensate generation to varying conditions within its BA. In this instance, the small variation in FBS settings reduced the risk as NSB would have overcompensated by increasing or decreasing generation by .66 MW. The two utilities that NSB is interconnected to are Florida Power and Light (FPL) and Duke Energy Florida (DEF). The all-time peak load for FPL is 24,355 MW and the all-time peak load for DEF is 10,989 MW. The all-time peak load for NSB is 109 MW so the NSB incorrect compensation of generation is miniscule compare to its two interconnect utilities. No harm is known to have occurred. | To mitigate this violation, NSB: 1) modified its ACE equation to include the revised Frequency Bias value on August 24, 2016; To mitigate this violation, NSB will: 1) create a training module is being which will ensure the NSB System Operators review the Balancing Authority Overview (procedure document for System Operators), with specific emphasis on the revised BAL Standard, and the need to review and implement the ERO supplied values in a timely manner. (11/18/16)
2016-11-30 | Florida Reliability Coordinating Council (FRCC) | Florida Power Development (FPD) | NCR00010 | FRCC2016016110 | PRC-019-2 | R1 | On September 2, 2016, FPD submitted a Self-Report stating that, as a Generator Owner, it was in violation of PRC-019-2 Requirement R1. FPD had not verified 40% of its applicable Facilities by 7/1/16 as required by the Standard implementation plan. Therefore, FPD did not coordinate the voltage regulating system controls, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. The root cause for this violation was a failure to understand the requirements of the implementation plan and a lack of controls to ensure implementation per the FERC approved implementation plan. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk is that the units would be disconnected unnecessarily or the units be damaged as a result of FPD not verifying it had set the in-service limiters such that they would not operate before the Protection Systems of the units; or the verifying the Protection System devices would not isolate/de-energize the units to limit the extent of damage to the units if operator or stability limits are exceeded. The actual risk is minimal as FPD represents less than 0.2% of the generation capacity in the state of Florida and the unexpected loss of this generation would not negatively impact the reliability of the BES. No harm is known to have occurred. | To mitigate this issue, FPD has: 1) selected a vendor to perform required testing; To mitigate this issue, FPD will complete the following mitigation activities by April 1, 2017: 1) have the selected bidder complete required testing and make any changes to settings as required; and 2) implement a process where future standard requirements will be reviewed by facility and corporate compliance managers during monthly NERC Teleconference. Task requirements will be uploaded in FPD regulatory compliance matrix. If there is any confusion related to standard implementation schedule interpretation, FRCC will be immediately contacted by FPD management team.
2016-11-30 | Florida Reliability Coordinating Council (FRCC) | Florida Power Development (FPD) | NCR00010 | FRCC2016016111 | MOD-025-2 | R2 | On September 2, 2016, FPD submitted a Self-Report stating that, as a Generator Owner, it was in violation of MOD-025-2 Requirement R2. FPD did not verify the Reactive Power capacity of its applicable Facilities as required by the implementation plan for MOD-025-2. Since FPD had not verified 40% of its applicable Facilities by 7/1/16 as required by the Standard, FPD has not supplied the required information to its Transmission Planner. The root cause for this violation was a failure to understand the requirements of the implementation plan and a lack of controls to ensure implementation per the FERC approved implementation plan. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The actual risk is the Transmission Planner would have incorrect or no data on the Reactive Power Capability of the FPD units. By having this incorrect information the long term planning studies would be incorrect and the RC would have incorrect information on the units capabilities. The potential risk is that an incorrect decision could be made by the RC based on incomplete information. The potential and actual risks are minimal as FPD represents less than 0.2% of the generation capacity in the state of Florida. Therefore, the impact of the FRCC RC having incorrect data would be minimal. No harm is known to have occurred. | To mitigate this issue, FPD has: 1) selected a vendor to perform required testing; To mitigate this issue, FPD will complete the following mitigation activities by April 1, 2017: 1) have the selected bidder complete required testing; and 2) will submit a completed Attachment 2 form to its Transmission Planner; and 3) implement a process where future standard requirements will be reviewed by facility and corporate compliance managers during monthly NERC Teleconference. Task requirements will be uploaded in FPD regulatory compliance matrix. If there is any confusion related to standard implementation schedule interpretation, FRCC will be immediately contacted by FPD management team.
2016-11-30 | Florida Reliability Coordinating Council (FRCC) | Florida Power Development (FPD) | NCR00010 | FRCC2016016112 | PRC-024-2 | R1 | On September 2, 2016, FPD submitted a Self-Report stating that, as a Generator Owner, it was in violation of PRC-024-2 Requirement R1. FPD had not verified 40% of its applicable Facilities by 7/1/16 as required by the Standard implementation plan. Therefore, FPD did not verify it had set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1. The root cause for this violation was a failure to understand the requirements of the implementation plan and a lack of controls to ensure implementation per the FERC approved implementation plan. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk is that the generators could trip in the "no trip zone" as a result of FPD not verifying it had set its protective relaying in accordance with PRC-024 Attachment 1. The actual risk is minimal as FPD represents less than 0.2% of the generation capacity in the state of Florida and the unexpected loss of this generation would not negatively impact the reliability of the BES. No harm is known to have occurred. | To mitigate this issue, FPD has: 1) selected a vendor to perform required testing; To mitigate this issue, FPD will complete the following mitigation activities by April 1, 2017: 1) have the selected bidder complete required testing and make any changes to settings as required; and 2) implement a process where future standard requirements will be reviewed by facility and corporate compliance managers during monthly NERC Teleconference. Task requirements will be uploaded in FPD regulatory compliance matrix. If there is any confusion related to standard implementation schedule interpretation, FRCC will be immediately contacted by FPD management team.
2016-11-30 | Florida Reliability Coordinating Council (FRCC) | Florida Power Development (FPD) | NCR00010 | FRCC2016016113 | MOD-025-2 | R1 | On September 2, 2016, FPD submitted a Self-Report stating that, as a Generator Owner, it was in violation of MOD-025-2 Requirement R1. FPD did not verify the Real Power capacity of its applicable Facilities as required by the implementation plan for MOD-025-2. Since FPD had not verified 40% of its applicable Facilities by 7/1/16 as required by the Standard, FPD has not supplied the required information to its Transmission Planner. The root cause for this violation was a failure to understand the requirements of the implementation plan and a lack of controls to ensure implementation per the FERC approved implementation plan. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk is the Transmission Planner would have incorrect data on the Real Power Capability of the FPD units. By having this incorrect information, the long term planning studies would be incorrect and the RC would have incorrect information on the units capabilities. The actual risk is minimal as FPD represents less than 0.2% of the generation capacity in the state of Florida. Therefore, the impact of the FRCC RC having incorrect data would be minimal. No harm is known to have occurred. | To mitigate this issue, FPD has: 1) selected a vendor to perform required testing; To mitigate this issue, FPD will complete the following mitigation activities by April 1, 2017: 1) have the selected bidder complete required testing; and 2) will submit a completed Attachment 2 form to its Transmission Planner; and 3) implement a process where future standard requirements will be reviewed by facility and corporate compliance managers during monthly NERC Teleconference. Task requirements will be uploaded in FPD regulatory compliance matrix. If there is any confusion related to standard implementation schedule interpretation, FRCC will be immediately contacted by FPD management team.
2016-11-30 | Midwest Reliability Organization (MRO) | Lincoln Electric System (LES) | NCR01001 | MRO2016015899 | FAC-008-3 | R6 | On June 24, 2016, LES submitted a Self-Report stating that as a Transmission Owner (TO), it had an issue of FAC-008-3 R6. LES took a substation out of service to replace the substation's 115kV breakers and disconnect switches. The replacement elements all had individual ratings greater than or equal to the prior elements. These replacement elements increased the Facility Ratings of the substation. LES returned the substation to service on March 17, 2016 without recalculating the Facility Ratings of the substation with the replaced elements. On May 12, 2016, LES recalculated the Facility Ratings. The cause of this noncompliance was a lack of internal controls as LES did not have any procedures in place to ensure that the recalculation of Facility Rating changes would occur prior to energizing the substation. The noncompliance began on March 17, 2016, when LES energized the substation, and ended on May 12, 2016, when LES updated the Facility Ratings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Facility Ratings did not decrease because the replacement elements all had individual ratings greater than or equal to the retired elements. Two internal 115 kV lines had their ratings increase from 309 MVA to 319 and 309 MVA to 398 MVA, and two 345/115 kV transformers had an increase in summer and emergency ratings from 398 MVA to 403 MVA and 356 MVA to 403 MVA. Additionally, LES's Reliability Coordinator confirmed that no flowgates were impacted by the rating changes. Finally, the duration of the noncompliance was relatively brief. No harm is known to have occurred. LES has no relevant history of noncompliance with FAC-008-3. | To mitigate this issue, LES will complete the following activities by December 31, 2016: 1) update its Facility Ratings; 2) complete a review of all projects completed since January 1, 2013 to confirm there are no other instances in which Facility Ratings were altered, but were not captured in the LES Facility Ratings Database or communicated to the appropriate parties; 3) create a checklist that must be completed at least seven days prior to energization; this checklist will require that Facility Ratings are recalculated, in addition to all other required actions, including all necessary elements of FAC-008-3; and 4) create a management tool that ensures that the checklist is timely and accurately completed. LES states that mitigating activities will be complete by December 31, 2016.
2016-11-30 | Midwest Reliability Organization (MRO) | Lincoln Electric System (LES) | NCR01001 | MRO2016015900 | FAC-008-3 | R8 | On June 24, 2016, LES submitted a Self-Report stating that as a Transmission Owner (TO), it had an issue of FAC-008-3 R8. LES took a substation out of service to replace the substation's 115kV breakers and disconnect switches. The replacement elements all had individual ratings greater than or equal to the elements. The replacement elements increased the Facility Ratings of the substation. Under the terms of the Operating Criteria Appendix, LES was required to inform its Reliability Coordinator (RC) and Planning Coordinator (PC) of the new Facility Ratings at least seven days prior to returning the substation to service. LES failed to inform its RC or PC of the new Facility Ratings prior to returning the substation to service on March 17, 2016. On May 12, 2016, LES recalculated the Facility Ratings, and informed its RC and PC of the new Facility Ratings. The cause of this noncompliance was a lack of internal controls as LES did not have any procedures in place to ensure that the recalculation and the communication of Facility Rating changes would occur after equipment changes and prior to energizing the substation. In fact, LES's guidance document only required that the new Facility Ratings were communicated once the LES internal database has been updated, and gave no guidance on the issue as to whether this had to be communicated prior to energization. The noncompliance began on March 10, 2016, six days prior to when LES energized the substation, and ended on May 12, 2016, when LES updated the Facility Ratings and communicated those new Facility Ratings to its PC and RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The Facility Ratings did not decrease because the replacement elements all had individual ratings greater than or equal to the retired elements. Two internal 115 kV lines had their ratings increase from 309 MVA to 319 and 309 MVA to 398 MVA, and two 345/115 kV transformers had an increase in summer and emergency ratings from 398 MVA to 403 MVA and 356 MVA to 403 MVA. Additionally, LES's RC confirmed that no flowgates were impacted by the rating changes. Finally, the duration of the noncompliance was relatively brief. No harm is known to have occurred. LES has no relevant history of noncompliance with FAC-008-3. | To mitigate this issue, LES will complete the following activities by December 31, 2016: 1) communicate the change in Facility Ratings to its RC and PC; 2) complete a review of all projects completed since January 1, 2013 to confirm there are no other instances in which Facility Ratings were altered, but were not captured in the LES Facility Ratings Database or communicated to the appropriate parties; 3) update its internal guidance document to be consistent with the RC's and PC's seven day notification criteria; 4) create a checklist that must be completed at least seven days prior to energization; this checklist will require that Facility Ratings are communicated to its RC and PC, in addition to all other required actions, including all necessary elements of FAC-008-3; and 5) create a management tool that ensures that the checklist is timely and accurately completed. LES states that mitigating activities will be complete by December 31, 2016.
2016-11-30 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2016015816 | BAL-005-0.2b | R6 | On May 23, 2016, NSP submitted a Self-Report stating that, as a Balancing Authority, it had an issue of BAL-005-0.2b R6. Specifically, the Energy Management System (EMS) for the Public Service Company of Colorado (PSCO), NERC ID NCR05521, went from a "tie line bias mode" to a "flat frequency mode." This change occurred after a programmer completed some setting modifications to a screen display. The cause of this issue is that "flat frequency mode" was the default setting for the EMS program, and the EMS program was set to revert to this default setting after exiting the programing mode. The issue began on March 28, 2016, when the EMS went from a "tie line bias mode" to a "flat frequency mode," and ended 52 minutes later, on March 28, 2016, when the EMS went back to a "tie line bias." | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Per NSP, the duration of the noncompliance was only 52 minutes. Additionally, flat frequency response will allow response to frequency deviations but will not preserve tie line flows. This will cause Automatic Generation Control to dispatch generation in a non-ideal manner. However, this error should only impact transactions across the ties, and is primarily a market issue. Finally, per NSP, for the hour ending 16 (4 pm) (when the noncompliance occurred), the inadvertent flow recorded was -41 MWH compared to a total BA load of 4,694 MWH, or less than 0.87%. No harm is known to have occurred. NSP has no relevant history of noncompliance with BAL-005-0.2b. | To mitigate this issue, NSP: 1) changed the mode back to a "tie line bias mode"; 2) changed the default mode to "tie line bias"; and 3) discussed this issue in a Peer Review call with representatives from all Operating Control Centers. MRO verified that mitigating activities were complete as of March 29, 2016.
2016-11-30 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2016015667 | PRC-023-2 | R1 | On February 22, 2016, NSP submitted a Self-Report stating that as a Transmission Owner, it had an issue of PRC-023-2 R1. Specifically, a 230-kV transmission line in the Public Service Company of Colorado (PSCO), NERC ID NCR05521 system, was found to have an overcurrent supervisory element trip setting that was less than 150% of the highest Facility Rating. The trip setting was on an overcurrent element acting as a back-up to an ABB RADHL Pilot-Wire Differential relay system (electromechanical) in the event of a loss of communications, which, in this case, is a fiber optic channel. The cause of this noncompliance was human error by the field technicians. The System Protection Engineering group issued an instruction to the technicians to change the setting on the RADHL scheme. The technicians marked the settings as changed, but did not actually make the changes. The engineering group was not able to confirm the changes because electromechanical relays do not create a viewable data file that display the settings. The issue began on July 1, 2014, when the Standard and Requirement became mandatory on NSP, and ended on December 12, 2015, when the RADHL system was temporarily removed from service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS from the noncompliance is limited to the back-up protection system that only becomes effective when the multiplexed fiber optic communication system fails. The likelihood of failure is very small given that the fiber optic communication system has a high reliability rate. Additionally, the fiber optic communications system is not subject to common-mode failure, meaning that a communications failure will not be triggered by, nor is it more likely to occur during a high loading of the line. No harm is known to have occurred. NSP has no relevant history of noncompliance with PRC-023-2. | To mitigate this issue, NSP: 1) issued a revised setting that the technicians implemented; 2) performed testing to document and verify the settings change; 3) confirmed in all three operating companies (PSCO, NSP, Southwestern Public Service Company (SPS) that there were no other applications utilizing an RADHL relay that were subject to PRC-023-2; 4) sampled electromechanical relays settings across all three operating companies to confirm that the settings were correct; and 5) distributed a lessons-learned to the business units of all three operating companies regarding this issue. NSP stated that mitigating activities were complete as of December 21, 2015.
2016-11-30 | Northeast Power Coordinating Council (NPCC) | Binghamton BOP LLC (BBOP) | NCR11500 | NPCC2016015828 | PRC-005-2-1.1b | R2.1 | During an Off-site Audit conducted from March 2, 2016 through May 18, 2016, NPCC determined that Binghamton BOP LLC, as a Generator Owner (GO), had an instance of noncompliance with PRC-005-2-1.1b R2.1. While gathering audit documentation, BBOP self-reported to the auditors that battery test records prior to July 2015 were unavailable and that DC Control Circuit functionality test records for 3 relays were not available prior to April 8, 2016, the last documented test date for the relays. The duration of the noncompliance was from December 4, 2014, the starting date of the audit period, to April 8, 2016, when the DC Control Circuit testing was documented. The root cause of this noncompliance was the failure to properly document testing results in accordance with PRC-005. Battery testing at BBOP was not properly documented in accordance with PRC-005-2(i) prior to July 2015. The DC Control Circuit functionality test records for the affected 3 relays were unable to be located, while test records for all other BBOP relays were available. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While proper functionality of battery systems and relays are critical to the proper operation of the facility's protection system, the risk was reduced due to the fact that BBOP is a small generating unit, with a total generating capability of 45 MW, and is not a documented Blackstart unit in the NYISO restoration plan. BBOP has a total of 29 relays, the remaining 26 of which had documented test results available, so only 10% of the facilities protective relays were affected by the instance of noncompliance. BBOP was able to provide all required battery testing subsequent to the July 2015 testing. No harm is known to have occurred as a result of this instance of noncompliance. NPCC considered BBOP's compliance history and determined there were no relevant instances of noncompliance related to PRC-005-1.1b R2.1. | To mitigate this instance of noncompliance, BBOP: 1) Performed the required testing on batteries and DC control circuits. 2) Documented the components that had missing records in the Protection System Maintenance and Testing Program to ensure testing would be properly performed and documented in the future. 3) Conducted training with employees on PRC-005 to increase awareness on testing deadlines and documentation. NPCC has verified the completion of all mitigating activities.
2016-11-30 | Northeast Power Coordinating Council (NPCC) | Binghamton BOP LLC (BBOP) | NCR11500 | NPCC2016015965 | PRC-019-2 | R1 | On July 14, 2016, BBOP submitted a Self-Report stating that, as a Generator Owner (GO), it had an instance of noncompliance of PRC-019-2 R1. As part of the PRC-019-2 Implementation Plan, GOs were required to coordinate the voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions by July 1, 2016, the effective date of the new standard. BBOP had scheduled the tests to be performed by a contracting company on June 21, 2016, however due to a scheduling conflict, the testing had to be rescheduled after the July 1, 2016 effective date to July 8, 2016. The root cause of this noncompliance was an unanticipated scheduling conflict with the contracting company that was to perform the testing. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BBOP is a small generating unit, with a total generating capability of 45 MW, and is not a documented Blackstart unit in the NYISO restoration plan. The duration of the noncompliance was minimal, with the necessary testing being performed seven days after the required date. The potential risk of the noncompliance was possible disconnecting of the generator unnecessarily, however BBOP was aware of the risk during the seven day duration of the noncompliance, and no actual incidents occurred. No harm is known to have occurred as a result of this noncompliance. NPCC considered BBOP's compliance history and determined there were no relevant instances of noncompliance related to PRC-019 R1. | To mitigate this instance of noncompliance, BBOP: 1) Performed the voltage regulating system controls coordination on July 8, 2016. 2) Added the PRC-019 five calendar year testing requirement to the BBOP maintenance tracking calendar. NPCC has verified the completion of all mitigating activities.
2016-11-30 | Northeast Power Coordinating Council (NPCC) | Erie Boulevard Hydropower, LP, (EBH) | NCR10358 | NPCC2016015834 | PRC-005-1.1b | R2 | During an Off-Site Audit conducted from February 9, 2016 through May 19, 2016, NPCC has determined that EBH, as a GO, had an instance of noncompliance related to standard PRC-005-1.1b R2, as follows: a) EBH did not record and/or did not retain testing documentation for one of its electromechanical relays, therefore exceeding the 4-year test interval prescribed by its maintenance program document. This relay was last tested on April 27, 2010. b) EBH did not record and/or did not retain certain testing documentation for its Annual Battery Tests at two of its six hydro-electric generating stations (Spier Falls #9 and Stewart Bridge), for the years 2012 through 2014. The instance of noncompliance started on November 25, 2013 (the enforcement date of the standard) and ended on December 17, 2015 (the date when the aforementioned relay was re-tested). A complete Annual Battery Testing for the two aforementioned stations was also performed before the stated noncompliance end date. The root cause of this instance of non-compliance was poor record keeping and an intermittent use of Attachment C&D on annual battery testing due to inconsistent practices among EBH's six hydro-electric generating stations. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). All electrical equipment at the two affected generating facilities facility are in good working order, and no detriment to the generating capability of the two hydroelectric stations occurred as a result of the non-compliance. Additionally, the combined Nameplate Rating of the two hydro-electric generating stations (both located within the footprint of the New York Control Area) is less than 77 MW, which represents less than 4% of the NYISO's required Operating Reserve of approximately 1965 MW. Therefore, if this instance of non-compliance had impaired the generating capability of the two hydro-electric stations, the NYISO would have been able to replace the lost capacity. For all the above considerations, this instance of non-compliance represents a minimal impact on the reliable operation of the BPS system. No harm is known to have occurred as a result of this instance of noncompliance of non-compliance. NPCC considered Erie Boulevard Hydropower, LP,s compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this instance of noncompliance, EBH: 1) performed a complete Annual Battery Test at the Spier Falls #9 and Stewart Bridge stations, and a test of its electromechanical relay. 2) commissioned an internal team (the "NERC Team") to periodically review management practices with regard to testing and creation/storage of test data into the EBH intranet server; and 3) developed a new work order job tracking system called Metric Stream, which is specifically designed to automatically flag compliance items and track their progress. NPCC has verified the completion of all mitigation activity.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Lansing by Its Board of Water and Light (LBWL) | NCR00718 | RFC2016015768 | VAR-002-4 | R1 | On May 25, 2016, LBWL submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue of VAR-002-4 R1. LBWL discovered that a Steam Turbine Generator unit was being operated in VAR control mode with the automatic voltage regulator (AVR) turned off and without an exemption from the Transmission Operator (TOP) that would allow LBWL to operate the unit in VAR control mode. LBWL learned of the noncompliance on April 1, 2016 based on an email from a consultant who was performing testing at the plant on March 23, 2016. The Steam Turbine Generator was offline from April 1, 2016 through April 18, 2016. Upon further investigation, LBWL estimated that the Steam Turbine Generator had been operated in VAR control mode since the last time the unit had tripped offline on February 23, 2016. There were no displays at the unit to indicate the change in status from automatic mode to VAR control mode. On April 18, 2016, LBWL brought the Steam Turbine Generator Unit back online in automatic mode and notified the GOP and TOP of the change in status. This noncompliance implicates the management practice of workforce management through ineffective training and work management through a lack of implemented processes. LBWL had an operator training issue as the operator did not know that he or she needed to notify the TOP when changing the status from automatic mode to VAR control mode. LBWL also did not have fully implemented procedures surrounding the process for handling the different AVR modes on Steam Turbine Generators. Two root causes of this noncompliance were ineffective training and a lack of fully implemented procedures. This issue started on February 23, 2016, when the Steam Turbine Generator unit began operating in VAR control mode and ended on April 18, 2016, when the Steam Generator Unit came back online and LBWL put the unit back in automatic mode for AVR. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. There was no actual impact from this event because throughout the time period the Steam Turbine Generator unit was operated in VAR mode, the Steam Turbine Generator unit never deviated from its voltage schedule. The unit in question is a small unit that serves as a topping turbine to balance steam loads. Based upon this purpose, the unit operates at the lower end of its capabilities (2 MW), and even its full capabilities are low compared to the capabilities of LBWL (17% of total plant capabilities, 5% of the entities total fleet of generation). The small size of the unit, the fact the unit never deviated from its voltage, and the unit’s purpose minimize the risk posed by this noncompliance. No harm is known to have occurred. ReliabilityFirst considered LBWL’s VAR-002 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LBWL: 1) added confirmation screens to the Steam Turbine Generator control console. Operators will now be notified by a pop up screen prompting him or her to notify the GOP and require confirmation of such notification every time a unit is switched from automatic mode to VAR control mode. These confirmation screens notify and remind the individual at the controls to notify the GOP and TOP when a switch in mode is made pursuant to VAR-002-4 R1; 2) retrained operators on all of the NERC requirements under VAR-002-4, procedures for operating the unit with the AVR turned on and off, and communications protocols with the GOP when the AVR is switched off; 3) added alarms to the computer equipment responsible for changing the status so changing the voltage regulator status from automatic to VAR control mode will be logged. These alarms will remind the operator to log the change and make the proper notifications once the change has been made; 4) placed the Steam Turbine Generator unit back into automatic mode with the AVR turned on when LBWL brought the unit back online and notified the GOP and the TOP of the updated AVR status on April 18, 2016; and 5) renamed its voltage regulator status from “droop” to “Auto” to provide additional clarity to the operator of the actual control mode as there is no difference between “droop” and “Auto,” they both mean that the unit is being operated with the AVR on. ReliabilityFirst has verified the completion of all mitigation activity.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Lansing by Its Board of Water and Light (LBWL) | NCR00718 | RFC2016015769 | VAR-002-4 | R3 | On May 25, 2016, LBWL submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue of VAR-002-4 R3. LBWL discovered that a Steam Turbine Generator unit was being operated in VAR control mode, instead of the automatic mode with AVR turned on, which violates VAR-002-4 R1 based on an email from a consultant who was performing testing at the plant on March 23, 2016. LBWL did not inform its Transmission Operator (TOP) that the Steam Turbine Generator unit was not operating in automatic mode within 30 minutes of the change in status from automatic mode to VAR control mode. The Steam Turbine Generator was offline from April 1, 2016 through April 18, 2016. Upon further investigation, LBWL estimated that the Steam Turbine Generator had been operated in VAR control mode since the last time the unit had tripped offline on February 23, 2016. There were no displays at the unit to indicate the change in status from automatic mode to VAR control mode. On April 18, 2016, LBWL brought the Steam Generator Unit back online in automatic mode and notified the GOP and TOP of the change in status. This noncompliance implicates the management practice of workforce management through ineffective training and work management through a lack of implemented processes. LBWL had an operator training issue as the operator did not know that he or she needed to notify the TOP when changing the status from automatic mode to VAR control mode. LBWL also did not have fully implemented procedures surrounding the process for handling the different AVR modes and required TOP notifications on Steam Turbine Generators. Two root causes of this noncompliance were ineffective training and a lack of fully implemented procedures. This issue started on February 23, 2016, when the Steam Turbine Generator began operating in VAR control mode and ended on April 18, 2016, when LBWL brought the Steam Generator Unit back online in automatic mode for AVR and notified the TOP of the change in status. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, there was no actual impact from this event because throughout the time period the Steam Turbine Generator was operated in VAR control mode and the unit never deviated from its voltage schedule during that time period. Second, the unit in question is a small unit that serves as a topping turbine to balance steam loads. Based upon the unit’s small size and the fact that the unit operates at the lower end of its capabilities (2 MW), the impact to the bulk power system of this unit not maintaining its voltage within its voltage schedule is minimal. No harm is known to have occurred. ReliabilityFirst considered LBWL’s VAR-002 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LBWL: 1) added confirmation screens to the Steam Turbine Generator control console. Operators will now be notified by a pop up screen prompting him or her to notify the GOP and require confirmation of such notification every time a unit is switched from automatic mode to VAR control mode. These confirmation screens notify and remind the individual at the controls to notify the GOP and TOP when a switch in mode is made pursuant to VAR-002-4 R1; 2) retrained operators on all of the NERC requirements under VAR-002-4, procedures for operating the unit with the AVR turned on and off, and communications protocols with the GOP when the AVR is switched off; 3) added alarms to the computer equipment responsible for changing the status so changing the voltage regulator status from automatic to VAR control mode will be logged. These alarms will remind the operator to log the change and make the proper notifications once the change has been made; 4) placed the Steam Turbine Generator unit back into automatic mode with the AVR turned on when LBWL brought the unit back online and notified the GOP and the TOP of the updated AVR status on April 18, 2016; and 5) renamed its voltage regulator status from “droop” to “Auto” to provide additional clarity to the operator of the actual control mode as there is no difference between “droop” and “Auto,” they both mean that the unit is being operated with the AVR on. ReliabilityFirst has verified the completion of all mitigation activity.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE) | NCR00753 | RFC2016015596 | PRC-005-1 | R2 | On March 7, 2016, DTE submitted a Self-Report to ReliabilityFirst stating that as a Generator Owner, it had an issue with PRC-005-1.1b R2. While performing research for different NERC standards in January 2016, DTE commenced a review of records for various generator relay protection schemes. During this review, DTE discovered that the Auxiliary Transformer relays were not maintained for Belle River Power Plant CTGs 12 &13 in accordance with its maintenance plan. DTE could not provide documentation on these auxiliary transformer relays to confirm that maintenance and testing had been performed. Upon further investigation it was determined that Belle River Plant CTGs 12 & 13 were one year overdue for their periodic maintenance. Additionally, while investigating if the missing Auxiliary Transformer relay maintenance was a systemic issue, DTE found the Delray CTGs 11 & 12 were also one year overdue for their periodic maintenance. The relay units are maintained on a seven calendar year cycle. DTE conducted an After Action Review on February 9, 2016 and a Root Cause Analysis on February 29, 2016. The root cause of not maintaining the Belle River relays was DTE’s approach to testing protection systems by schemes instead of by individual component, which, as in this instance, can cause components to be missed. The relays' maintenance and testing records for auxiliary transformer schemes are in a different physical location than the rest of the generator relaying, causing the records to be missed when inspection scopes were created for those generators. DTE’s failure to maintain the Delray Peaker protection system is that DTE’s process to identify the need for the maintenance did not include a way to notify appropriate personnel if maintenance deadlines were approaching or missed. The maintenance was already late by one year when DTE’s Subject Matter Expert (SME) conducted his review and identified the noncompliance. The duration of the noncompliance for Delray Peaker is from November 25, 2013, when DTE was required to comply with PRC-005-1.1b R2 and ended on July 5, 2016, when DTE completed its Mitigation Plan. The duration of the noncompliance for Belle River CTG 12 &13 started June 18, 2007 under PRC-005-1 and ended on July 5, 2016 when DTE completed its Mitigation Plan. | DTE’s failure to test and maintain their auxiliary transformer relaying could have led to an increased potential for misoperation or failure of the relay. However, ReliabilityFirst determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the generators involved in this noncompliance are Combustion Turbine Generators of relatively small size, are not designated as Blackstart resources, and unlikely to cause any additional equipment loss, transmission loading or voltage deviations. As an aside, there were no misoperations or failures of the auxiliary transformer relays during the duration of this noncompliance. No harm is known to have occurred. ReliabilityFirst considered DTE’s PRC-005 R2 compliance history in determining the disposition track. DTE’s relevant prior noncompliances with PRC-005 R2 include: RFC201000663. A Settlement Agreement covering a violation of PRC-005-1 R2 was filed with FERC under NP11-232-000 on July 28, 2011. On August 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In the prior violation, DTE failed to test certain batteries within their defined intervals. The prior violation is distinguishable from the current violation. The prior violation resulted from having too many internal departments responsible for maintaining batteries, which resulted in no department being accountable for the maintenance. Conversely, the current violation resulted from DTE’s approach of testing protection systems by schemes instead of by individual component. RFC201100819. A Settlement Agreement covering violations of PRC-005-1 R2, R2.1 was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In the prior violation, DTE failed to test certain Protection System schemes due to a misunderstanding of its obligations under its transition plan for transitioning from the previous definition of “bulk electric system” to the new definition of “bulk electric system.” The prior violation is distinguishable from the instant violation because DTE was aware of and understood the requirement but did not have a process in place that alerted appropriate personnel to approaching or delinquent testing deadlines nor did DTE’s inventory practice clearly identify components to be tested. RFC2015014800. A Compliance Exception addressing a noncompliance with PRC-005-1 R2 was posted on the NERC website on June 29, 2016. The violation is distinguishable from the current violation. In the prior violation, DTE mistakenly believed that ITC owned the assets. However, in this instance, DTE was aware of and understood the requirement but did not have a process in place that alerted appropriate personnel to approaching or delinquent testing deadlines nor did DTE’s inventory practice clearly identify components to be tested. ReliabilityFirst determined that DTE’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, DTE: 1) reprogrammed the tracking sheets to give an earlier warning of upcoming maintenance due dates; and 2) performed protection system maintenance and testing on the Delray and Belle River CTGs. ReliabilityFirst has verified the completion of all mitigation activity.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Dynegy Inc. (Dynegy) | NCR00200 | RFC2016015622 | VAR-002-4 | R1 | On March 21, 2016, Dynegy submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-4 R1. On January 25, 2006, at Dynegy’s Newton Power Station, (The Newton Power Station is a 2 unit 1,273MW coal-fired facility located in Newton, IL, and interconnected at 345kV with Ameren.) Unit 2 went into an economic outage and the Automatic Voltage Regulator (AVR) switched to manual. On February 11, 2016, Unit 2 came online and synched to the grid at 7:13 a.m., while the AVR was still in manual mode. At 10:06 a.m., plant personnel identified the fact that the AVR was in manual mode as part of the startup process and changed the status to automatic. Both at 7:13 a.m. and 10:06 a.m., email alerts were generated and sent to all eight shift supervisors and the production manager at the plant notifying them to contact the Transmission Operator (TOP) within 30 minutes. However, these email alerts were missed by the recipients due to the heavy volume of emails coming through during the startup process. As a result, Dynegy failed to notify the TOP within 30 minutes of the AVR status changes. The root cause of this noncompliance was the lack of an adequate notification process to control operators. The fact that the operators were receiving a heavy volume of emails during the startup process together with the fact that AVRs are normally in automatic mode prior to startup, resulted in the responsible personnel failing to anticipate receiving AVR status change email alerts during the startup process. This major contributing factor implicates the management practices of (a) asset and configuration management, which includes controlling changes to assets; (b) implementation, which includes establishing an adequate process for implementing new system elements; and, (c) workforce management, which focuses on providing adequate training and education to employees. The duration of this noncompliance is from 7:43 a.m. on February 11, 2016, the date and time by which Dynegy was required to notify the TOP of the AVR status change, to 10:36 a.m. on February 11, 2016, the date and time by which Dynegy was required to notify the TOP of the last AVR status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, this issue was an isolated incident and not indicative of a systemic issue because, during the three years it has owned this plant, Dynegy identified no other instances where the TOP was not notified of AVR status changes. Second, Dynegy had an internal detective control in place (i.e., the email alerts) that identified this issue, but this control was not configured in a way that made it effective in this specific case. Additionally, ReliabilityFirst notes that during the time that the AVR was in manual mode, Unit 2 was within its voltage schedule and the TOP gave no indication of any voltage concerns during this time. (During the time that Unit 2 was in manual, Unit 1 was also online with its AVR in auto and within its voltage schedule.) No harm is known to have occurred. ReliabilityFirst considered Dynegy's VAR-002 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Dynegy: 1) added an alarm in the Newton Control Room to alert as a Priority 1 when the AVR is in manual or when a status change occurs; 2) increased those receiving the email alert to include the unit operators in addition to the shift supervisors; 3) developed a lesson learned document which was provided to other Dynegy Plants; and 4) conducted refresher training for plant personnel on the internal start-up procedure and Procedure RGC-G02, REV7, Compliance Guidance for NERC Standard VAR-002-4. ReliabilityFirst has verified the completion of all mitigation activity.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Dynegy Inc. (Dynegy) | NCR00200 | RFC2016015513 | VAR-002-3 | R2 | On January 28, 2016, Dynegy submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-3 R2. During a quarterly review of various NERC Standards, including VAR-002-3, Dynegy identified one hour on October 4, 2014, at 12:00 a.m., where the Baldwin generation plant’s hourly integrated voltage value was outside the voltage schedule. (The quarterly review at issue was performed in latter part of 2015. The reason that this particular quarterly review looked back to 2014 was that at the time that the Transmission Operator (TOP) notification requirement went into effect (i.e., October 1, 2014), Dynegy understood that such notification was not required when the plant was operating at its limits. Subsequently, Dynegy corrected this understanding and went back and reviewed logs from October 1, 2014, and forward for possible noncompliances.) At this time, the Baldwin plant was operating pursuant to a voltage directive from its TOP, Ameren, to change its voltage range from 358.8kV-365.5kV to 355kV-360kV. The hourly integrated voltage value for the hour in question was 360.86kV, or .86kV (.23%) outside the voltage directive schedule. In light of this deviation from the voltage directive schedule, Dynegy was required to meet the notification provisions provided by Ameren. However, based on Dynegy’s review of the plant logs, no notifications occurred for this 1 hour deviation. (Because the plant was operating at its limits during the course of this noncompliance, the violation is not for the deviation from the voltage directive schedule, but for failing to properly notify the TOP of the deviation.) The root cause of this noncompliance was the plant personnel’s failure to follow Dynegy’s established procedure for notifications resulting from voltage deviations. This contributing factor implicates the management practice of workforce management, which focuses on providing adequate training and education to employees. The duration of this noncompliance is from October 4, 2014, the date Dynegy was required to notify Ameren of the voltage deviation, to October 19, 2015, the next date that Dynegy contacted Ameren. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the amount by which Dynegy deviated from the voltage directive schedule and the duration of the deviation was very small (i.e., .23% deviation for 1 hour). Second, this issue was an isolated incident and not indicative of a systemic issue because Dynegy identified no other instance where a voltage deviation occurred requiring notification to the TOP since its last audit in 2013. Third, the TOP gave no indication of any voltage concerns during this time. No harm is known to have occurred. ReliabilityFirst considered Dynegy's VAR-002 R2 compliance history in determining the disposition track. Dynegy’s relevant prior noncompliance with VAR-002 R2 includes: RFC2012010906. A Find, Fix and Track Report (FFT) informational posting addressing a noncompliance with VAR-002-1.1b R2 was posted on the NERC website on January 31, 2013. The violation is distinguishable from the current violation. The prior violation related to Dynegy operating outside of its voltage schedule, and not for failing to notify the TOP, as is the basis of the instant noncompliance. ReliabilityFirst determined that Dynegy’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Dynegy: 1) conducted refresher training for all responsible personnel on the relevant process; and 2) added a message to the voltage alarm window to indicate that a call is required to the TOP when the voltage schedule is not being met.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Midcontinent Independent System Operator, Inc. (MISO) | NCR00826 | RFC2015015093 | PRC-023-3 | R6 | On July 15, 2015, MISO submitted a Self-Report stating that, as a Planning Authority/Planning Coordinator, it had an issue of PRC-023-3 R6. Pursuant to PRC-023-3 R6, MISO produces a list of circuits to which its members apply the relay setting provisions of PRC-023-3 R1-R5. MISO, as a Planning Coordinator, must complete this assessment and produce the circuit list once every calendar year with no more than 15 months between updates. MISO typically produces this circuit list as a part of its annual MISO Transmission Expansion Plan (MTEP), which is produced at the end of the year and includes a current list of all projects that will be built. For the 2014 calendar year, MISO did not produce the circuit list as required. MISO’s first MTEP reflecting the Integration of the Southern Region was its 2014 MTEP, which was not released until March 2015. To meet the calendar year requirement of PRC-023-002 R6, MISO completed an additional circuit list in September 2014 without utilizing Entergy’s circuit list, which included the Southern Region circuits. MISO completed its MTEP in March 2015 and produced an updated circuit list that included the Southern Region circuits. As a result, MISO did not complete a full circuit list each calendar year as MISO’s September 2014 circuit list did not include the Southern Region. The root cause of this noncompliance was a scheduling error involving the timing of both MISO’s MTEP and the integration of the Southern Region into MISO’s footprint. The integration of Southern Region’s circuit list was not included in MISO’s 2014 due to MISO’s failure to have this standard flagged so responsibility for the production of the circuit list transitioned within appropriate timing of MISO’s MTEP. This contributing factor relates to the management practices of integration and planning. This issue started on January 1, 2015, when MISO was required to produce its 2014 MTEP including an accurate circuit list that included the Southern Region circuits, and ended on March 31, 2015, when MISO actually produced the requisite circuit list. Per the standard, MISO must conduct an assessment at least once each calendar year, with no more than 15 months between assessments. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, this appears to be an isolated incident caused by the scheduling of the Southern Region circuits integration and MISO’s delay of publishing the 2014 MTEP. MISO understood that it needed to integrate the circuits within its newly acquired southern region, however it did not adjust its timeline to afford sufficient time to perform this task and meet the timing requirements of its compliance obligations (i.e. draft a complete and accurate circuit list) within the calendar year. Second, MISO has an established process to ensure the circuit list is accurate and produced on an annual basis and was able to detect and mitigate the noncompliance within a short duration of three months. Additionally, ReliabilityFirst notes that there were no significant changes in transmission topology, load levels or generation mix within the final list. No harm is known to have occurred. ReliabilityFirst considered MISO's PRC-023 R6 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MISO: 1) produced the required circuit list on March 31, 2015 addressing all regions within MISO’s footprint; 2) re-emphasized to Energy Management System (EMS) Shift Engineers responsible for implementing the EMS cases the critical nature of ensuring that all steps in the process are not just executed, but also reviewed for errors including encouraging independent review of cases by another EMS shift engineer prior to implementation; 3) implemented enhancements to advance the compilation of the circuit lists by six months for its 2015 MTEP and beyond; 4) established criteria that, when applicable to a circuit, will trigger the circuit’s inclusion on the PRC-023 list; and 5) implemented enhancements into MISO’s footprint to have this Standard flagged so responsibility for the production of the circuit list does not transition to MISO until that year’s MTEP is completed. ReliabilityFirst has verified the completion of all mitigation activity.
2016-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Midcontinent Independent System Operator, Inc. (MISO) | NCR00826 | RFC2015015233 | EOP-006-2 | R5 | On September 4, 2015, MISO submitted a Self-Report stating that, as a Reliability Coordinator, it had an issue of EOP-006-2 R5. On June 15, 2015, Indianapolis Power & Light (IPL) submitted its revision to a previously approved Power System Restoration Plan (PSR) to MISO’s Regional Transmission Operator’s (RTOps) Compliance mailbox for approval. The changes to the previously approved PSR plan (Revision 3.2) were minimal and made to align with MISO’s common language and terminology. On August 11, 2015, IPL emailed MISO to obtain historical approval notifications for its PSR plans from 2014-2015. In responding to this request, MISO discovered that the 2015 IPL PSR plan submitted June 15, 2015 had been overlooked in the RTOps Compliance mailbox. That same day, MISO completed the review and approval of the 2015 revised PSR plan and emailed the approval of the 2015 PSR plan along with the requested previously sent approvals of IPL’s 2013 and 2014 PSR plans to IPL. The root cause of this noncompliance was lack of oversight and safeguards which implicates the management practice of reliability quality management. MISO did not meet the 30 day requirement for completing review of the IPL’s revised 2015 PSR plan due to lack of oversight of the compliance mailbox and no safeguards to ensure MISO would be made aware if a request did not receive a response within the required timeframe which indicates a gap in MISO’s overall review process. This issue started on July 16, 2015, the date by which MISO was required to approve or disapprove, with stated reasons, IPL’s revised June 15, 2015 PSR plan, and ended on August 11, 2015 when MISO completed its review and approval of IPL’s 2015 restoration plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. During the period of noncompliance, the delay in MISO’s review and approval of the revised 2015 restoration plan would not have seriously impacted MISO and IPL’s ability to execute a coordinated restoration. First, the changes to the previously approved PSR plan (Revision 3.2) were minimal, so the MISO and IPL operators’ familiarity with the previous PSR plan was still relevant. Second, the Revision 3.3 of the IPL PSR plan involved updating titles and improving the synchronizing process to better align with MISO interconnection sheet to facilitate a smoother implementation through the use of common language and terminology. A comparison of the two plans indicates that there were no significant technical changes to the plan. No instance arose during the time period during which IPL’s PSR was implemented. Synchronization would not have been impacted by the continued use of Revision 3.2. No harm is known to have occurred. ReliabilityFirst considered MISO's EOP-006-2 R5 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MISO: 1) assigned multiple individuals to review the RTOps Compliance mailbox to ensure emails are not overlooked; 2) issued a notification to the Transmission Operators asking them to ensure they receive an acknowledgment within five days of any inquiries/requests sent to the RTOps Compliance mailbox and, if acknowledgement is not received, requesting they contact MISO; 3) explored the redesign and possible automation of the PSR workflow process with existing MISO enterprise tools. Due to documentation security concerns no automation tools were implemented; 4) created process flows and updated procedures incorporating the new proposed quality assurance oversight by the administrator of the PSR plans; and 5) incorporated quality metrics and error detection within the process to ensure the process is performing as it should.
2016-11-30 | SERC Reliability Corporation (SERC) | Duke Energy Progress (DEP) | NCR01298 | SERC2016015665 | FAC-009-1 | R1. | On April 13, 2016, Duke Energy Progress (DEP), on behalf of Duke Energy Florida, LLC (DEF) submitted a Self-Report to SERC stating that, as a Transmission Owner (TO), it had an issue with FAC-008-3 R6. DEP submitted the Self-Report to SERC under an existing multi-regional registered entity agreement. DEF did not develop a Facility Rating in accordance with its Facility Rating Methodology (FRM). SERC later determined that the issue extended back to FAC-009-1 R1. On March 1, 2016, as part of an upgrade project at another facility, DEF line engineering identified the possibility that a conductor from the Facility Ratings Spreadsheet (FRS) used to establish the Facility Rating of a 0.23-mile long segment of a substation tie line did not include all conductor types of the facility. The line segment in question connects a DEF network substation to a substation owned by an adjacent TO. The drawings had not accurately reflected the ownership of a segment of the line. DEF had considered the Facility Rating provided by the adjacent TO, but DEF believed that the adjacent TO owned the entire line. However, DEF actually owned the line segment but did not include it in its determination of the Facility Rating. On March 21, 2016, a field review of the existing line segment confirmed that 556 Aluminum Conductor Steel Reinforced Aluminum Wire (ACSR/AW) was present in the portion of the Facility owned by DEF, but the existing FRS for this section did not include 556 ACSR/AW in the determination of the Facility Rating. When DEF determined the Facility Rating including the 556 ACSR/AW conductor, it became the limiting element for the normal summer rating, but other seasonal and emergency ratings were unaffected. The root cause of the issue was human error. DEF incorrectly assumed the neighboring TO owned the line segment. The issue started on June 18, 2007, when the Standard became mandatory and enforceable and ended on March 30, 2016, when DEF corrected and communicated the Facility Rating. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DEF incorrectly documenting the Facility Ratings could result in operating decisions that jeopardize equipment life, personnel safety, and adequate contingency planning. However, in this case DEF used the incorrect rating without incident since 1989. The line is a 0.23-mile 115 kV-networked line that is not critical to operation of the BPS. When DEF recalculated the Facility Rating, the conductor became the limiting element for the normal summer rating. DEF reduced the normal summer Rating from 199 MVA to 173 MVA (-13.1%). All other Facility Ratings, including the emergency Ratings, remained unaffected. DEF reports that records show that power flows did not exceed the reduced line rating, no contingencies were in effect for the line, and no events are attributable to the incorrect rating. No harm is known to have occurred. SERC considered DEP’s FAC-008-3 R6 and FAC-009-1 R1 compliance history in determining the disposition track. DEP’s relevant prior noncompliance with FAC-008-3 R6 includes: NERC Violation ID SERC2015015322, FRCC2014014010, and FRCC2012011495. SERC determined that DEP’s FAC-008-3 R6 and FAC-009-1 compliance history should not serve as a basis for applying a penalty. In FRCC2012011495, DEF failed to include relay settings of a 115 kV radial line to a 32 MVA co-generator plant in its determination of the Facility Rating. DEF later identified the relay settings to be the most limiting element of the Facility. In FRCC2014014010, DEF identified a line segment was incorrectly rated following a construction project because a conductor was incorrectly classified. In SERC2015015322 DEF found a transmission line conductor other than specified in the Facility Rating spreadsheet. When DEF added the conductor, it became the limiting element. The instant issue involves a conductor present in the facility but not included in the determination of the Facility Rating; however, the circumstances leading to the omission date to 1989 and none of the mitigating activities for the previous issues would have detected or corrected the instant issue. SERC considered the FAC-008-3 R6 and FAC-009-1 R1 affiliate compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, DEF: 1) updated engineering documentation supporting the Facility Ratings Spreadsheets ; 2) updated Facility Ratings Spreadsheets. DEF updated the FRS based on the information contained in the FRM-TRMF-01038; 3) communicated the updated Facility Ratings to System Operations and Transmission Planning as well as the Reliability Coordinator; and 4) reviewed all tie-lines where DEF does not own conductors to ensure that the omission of conductors and this specific event does not recur. To mitigate this issue, DEF will complete the following mitigation activities by November 23, 2016: 1) will assess and review lines of older construction dates to re-validate that no further risks exist on the system. This validation includes approximately 28 lines that are a subset of DEF’s 115 kV population.
2016-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Post Rock Wind Power Project, LLC (PRWP) | NCR11264 | SPP2016015761 | PRC-005-1b | R1, R1.1, R1.2 | On May 20, 2016, Post Rock Wind Power Project, LLC (PRWP) submitted a Self-Report stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-005-1b R1.1 and R1.2. PRWP did not include two Protection System communication devices in its Protection System Maintenance and Testing Program (PSMP). The Communication System Protection System function was not tested on the two devices because of the omission. PRWP’s instance of noncompliance of PRC-005-1b R1.1 and R1.2 omitted two of 93 protection system devices in its PSMP. The root cause of this instance of noncompliance was human error. The PRWP staff failed to identify that these two devices performed both relay and communication functions. Only the relay function was included in the PSMP causing a failure to test the Communication Protection System function. The duration of this instance of noncompliance was from September 13, 2012, the date of Generator Owner registration through March 31, 2015, the date the PSMP was updated. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The omitted communication devices continuously self-test communication channels triggering an alarm for any instance of communication failure. PRWP reviewed the Communication System logs and found no Communication Systems alarms that would have resulted in an operation of the devices from September 13, 2012 to March 31, 2015. No harm is known to have occurred. | To mitigate this minimal risk instance of noncompliance, WR: 1) had an independent contractor test the devices to verify proper operation and functionality; 2) had device logs reviewed by the engineering department to ensure no alarms would have resulted in an operation of the device during the noncompliance period; and 3) updated the substation maintenance inspection form to incorporate relay communication status and alarm verification. SPP RE has verified the completion of all mitigation activity.
2016-11-30 | Texas Reliability Entity (Texas RE) | Brownsville Public Utilities Board BPUB Silas Ray (BPUB Silas Ray) | NCR04021 | TRE2016015917 | PRC-005-1 | R2; R2.1 | During a Compliance Audit conducted from June 14, 2016 through July 15, 2016, Texas RE determined that BPUB Silas Ray, as a Generator Owner (GO), had an issue with PRC-005-1 R2.1. Specifically, BPUB Silas Ray did not have documentation that it maintained and tested eight Protection System devices within the intervals defined in its Protection System Maintenance and Testing Program (PSMP). During the Compliance Audit, Texas RE determined that BPUB Silas Ray did not have the required maintenance and testing records for six relays and two current transformers (CTs). BPUB Silas Ray’s then-current PSMP required both categories of Protection Systems to be tested every five years. For the six relays at issue, BPUB Silas Ray provided evidence that it last tested those devices on July 31, 2004. As such, BPUB Silas Ray should have performed the required testing on July 31, 2009. However, BPUB Silas Ray did not perform the necessary maintenance and testing on the relay devices at issue until March 2013. Regarding the two CTs at issue, BPUB Silas Ray should have performed the required testing by June 28, 2007. However, BPUB Silas Ray did not provide any evidence of testing prior to the March 2013 testing records. The root cause of this issue was an inadequate process for ensuring all required testing and maintenance activities were performed in a timely manner. Specifically, BPUB Silas Ray lacked sufficient processes for tracking required maintenance activities and intervals for all devices within its PSMP. The issue duration was from June 28, 2007, the earliest date upon which BPUB Silas Ray should have performed the required testing on the two CTs at issue, until March 7, 2013, when BPUB Silas Ray completed testing on the last device at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for the following reasons. First, the devices at issue represent only 4.2% (8/189) of all devices in BPUB Silas Ray’s PSMP. Second, when BPUB Silas Ray performed the required testing, seven of the eight devices were found to have no issues, and the single other device at issue remained operative and did not require replacement. Third, BPUB Silas Ray performed the necessary maintenance and testing in 2013 and had no additional maintenance and testing issues in the subsequent three-year period before the Compliance Audit. No harm is known to have occurred. Texas RE considered BPUB Silas Ray’s compliance history in determining the disposition track. BPUB Silas Ray’s relevant prior noncompliance with PRC-005 R1 and PRC-005 R2 includes TRE201000103 and TRE201000125. Texas RE determined that BPUB Silas Ray’s compliance history should not serve as a basis for applying a penalty. The prior violations involved BPUB Silas Ray’s failure to have a documented PSMP and to perform additional testing after installation of the devices. The current issue pertains to BPUB Silas Ray’s failure to effectively track the testing intervals of all applicable relays and CTs. | To mitigate this issue, BPUB Silas Ray: 1) completed testing on all devices at issue; 2) developed an enhanced spreadsheet to track testing dates for all devices within the PSMP; and 3) acquired a computerized maintenance program (CMMS) to schedule and manage PSMP testing activities. Texas RE has verified the completion of all mitigation activity.
2016-11-30 | Texas Reliability Entity (Texas RE) | EDF Energy Services, LLC (EDF) | NCR00551 | TRE2016015847 | IRO-010-1a | R3 | During a Compliance Audit conducted from May 10, 2016 through June 14, 2016, Texas RE determined that EDF, as a Generator Operator (GOP), had an issue with IRO-010-1a R3. In particular, EDF failed to provide accurate data and information, as specified, to its Reliability Coordinator (RC). Specifically, EDF failed to provide the correct status of its generation Facilities’ Automatic Voltage Regulators (AVRs) and Power System Stabilizers (PSSs) via telemetry as specified by its RC. During the Compliance Audit, Texas RE identified seven instances at six generation Facilities in which the telemetered status of the AVR and/or PSS did not match the operational status of the associated generation Facility. In particular, EDF provided telemetered AVR statuses to the RC indicating that the AVR was either “OFFLINE” when then applicable generation Facility was in operation or, conversely, telemetered an “ONLINE” AVR status when the applicable generation Facility was not in operation. Similarly, EDF provided telemetered PSS statuses indicating that the PSS was “OFFLINE” at two generation Facilities during periods in which those Facilities were in fact operational. The root cause of this noncompliance was a lack of sufficient processes for updating AVR and/or PSS statuses to reflect operational status changes at the corresponding generation Facilities. Specifically, EDF lacked a sufficient process to independently determine the applicable generation Facility status and update AVR and/or PSS status information to reflect those changes. Texas RE determined the issue duration to be from October 1, 2011, when the Standard became mandatory and enforceable, until September 1, 2016, when the final telemetry issue was corrected. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for three reasons. First, the issue in question was limited solely to the telemetered AVR/PSS status provided to the RC, and at no time did any of the affected generation Facilities actually operate with their AVR/PSS out of service. Second, in most instances, the RC possesses a number of other mechanisms to ensure that it would be aware of any change in AVR/PSS status if it actually occurred, including direct notifications from the GOP when a generation Facility actually experiences an AVR/PSS status change. Finally, the generation Facilities at issue produce a relatively small amount of generation within the ERCOT footprint, with the largest single generation amount being 79.6 MW. No harm is known to have occurred. Texas RE considered EDF’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EDF: 1) corrected the telemetry issues for the generation Facilities in question; 2) implemented a new process to determine the operational statuses of generation Facilities and to update the associated telemetered AVR/PSS statuses for those Facilities; and 3) instituted logic changes whereby an alarm will alert EDF operators when the calculated AVR/PSS status it sends to the RC differs from the telemetry EDF receives from the applicable generation Facility. Texas RE has verified the completion of all mitigation activity.
2016-11-30 | Texas Reliability Entity (Texas RE) | Panda Sherman Power, LLC (PSPL) | NCR11470 | TRE2016016026 | EOP-004-2 | R3 | On August 19, 2016, PSPL submitted a Self-Report stating that, as a Generator Owner (GO) and Generator Operator (GOP), it had an issue with EOP-004-2 R3. In particular, PSPL failed to validate all contact information contained in its Operating Plan for the 2015 calendar year. Texas RE has determined that the root cause of the noncompliance was an insufficient process for tracking the completion of the contact information validation. Specifically, PSPL’s existing process lacked sufficient reminders or prompts to the PSPL personnel responsible for performing the contact information validation. As a result, the PSPL personnel responsible failed to perform the contact information validation within the required annual timeframe. Texas RE determined that the issue duration was from January 1, 2016, the day after the compliance information validation was due, until August 11, 2016, when PSPL performed its contact information validation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, the noncompliance was documentary in nature, and PSPL did not experience any events that required the use of its Operating Plan in 2015. Second, PSPL provided evidence that it possessed accurate contact information for the necessary critical organizations to respond to real-time emergencies. As such, if an emergency event had occurred, PSPL personnel would have been able to contact critical organizations immediately to address the issue. No harm is known to have occurred. Texas RE considered PSPL’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PSPL: 1) performed the required contact information validation; and 2) created an automatic work order reminder that prompts appropriate PSPL personnel to perform the contact information validation in January of every year. Texas RE has verified the completion of all mitigation activity.
2016-11-30 | Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2016015766 | PRC-023-3 | R6; R6.2 | On May 20, 2016, IID submitted a Self-Report stating that as a Planning Authority, it had a possible issue of noncompliance with PRC-023-3 R6.2. Specifically, IID’s annual PRC-023-3 Attachment B assessment resulted in minor changes to its established list of transmission circuits subject to R1 through R5 in its Planning Coordinator area. IID provided the updated list to its Regional Entity (WECC) nine days beyond the 30-day notification requirement. This issue began January 11, 2016, the day after the notification window lapsed, and ended January 19, 2016, when IID provided the updated list to WECC. This issue was caused by less than adequate communication between work groups. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, IID failed to distribute an updated list of its transmission circuits to its Regional Entity (WECC) within the timeframe prescribed by R6.2. Such failure could have affected WECC’s planning assessment results. However, IID has a documented procedure to ensure timely submittal of any revisions resulting from its annual assessment, and distributed its revisions on time to all other entities in accordance with the Standard. IID’s delayed submission to WECC was caused by an administrative oversight, and remediated within a very short time period. Additionally, the revisions were minor and would not have significantly affected WECC’s planning assessment; IID only removed circuits which no longer met loadability criteria. No harm is known to have occurred. IID does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, IID: 1) submitted its updated list to WECC; and 2) initiated an internal assessment to identify a) the root cause and potential impact of this issue, and b) whether revisions to its documented procedure were necessary in order to prevent recurrence. WECC verified completion of IID’s mitigating activities.
2016-10-31 | Florida Reliability Coordinating Council (FRCC) | Florida Municipal Power Agency (FMPA) | NCR00022 | FRCC2016015953 | FAC-009-1 | R1 | On July 26, 2016 FMPA submitted a Self-Report stating that, as a GO, it had an issue of FAC-008-3 R6. During a review of the facts and circumstances of the issue, FRCC determined the issue occurred under FAC-009-1 R1. This issue started on June 30, 2009, when FMPA first used the estimated manufacturer data for FMPA’s Facility Ratings and ended on August 1, 2016, when the Facility Rating for Treasure Coast Energy Center (TCEC) gas turbine generator was updated to the correct rating. The issue involved the rating for the generator, which was the most limiting element for the facility. During a review of FMPA’s Facility Ratings in January 2015, staff noted several formatting, organizational, backup/file storage, and other issues not related to compliance that FMPA wished to improve in its documentation. FMPA added engineering staff in January 2016 and the comprehensive review was the first assignment of the new staff member. FMPA completed this comprehensive review of its Facility Ratings, and found one area of concern. An incorrect value was calculated for the apparent power rating of the Treasure Coast Energy Center (TCEC) gas turbine generator which is the most limiting element for the facility. The value documented in FMPA’s Facility Ratings was 238 MVA, but it should have been 219.6 MVA. This error was caused by the use of incorrect source information from the interconnection study phase of construction of the unit rather than the correct as-built information. FMPA has determined the root cause was lack of review by staff with operational experience and routine interaction with the Facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk to the Bulk Power System is that the Transmission Operator (TOP) and/or Reliability Coordinator (RC) could have expected additional capacity from the unit. This risk is mitigated by the significant MW/MVAR support surrounding the TCEC in comparison to the capacity of the TCEC gas turbine generator (219.6 MVA). Specifically, the Florida Power and Light (FPL) Martin plant (3699 MW), FPL St. Lucie Plant (1821 MW), and West County Energy Center (3657 MW). Currently the unit capability of 167.5 MW / 63.5 MVAR (179 MVA) summer and 173 MW / 63.5 MVAR (184 MVA) winter are used in the FRCC power flow databank. There was minimal risk to the Bulk Power System due to the fact that seasonally adjusted, verified, and tested generator real and reactive power capacities (179 MVA summer and 184 MVA winter) are used in both operations and planning activities. The corrected value of 219.6 MVA for the TCEC gas turbine generator, while being the most limiting element for the facility, could never have been exceeded as it is physically limited by the gas-turbine. This was a minimal risk issue with no impact to the BES. On January 1, 2013 FAC-008-3 became effective, replacing FAC-009-1. Requirement R1 from FAC-009-1 was replaced by requirement R6 in FAC-008-3. The current issue is with FAC-009-1 R1, based on the start date of the issue. However, this is FMPA's second FAC-008-3 R6/FAC-009-1 R1 issue within two years. As noted in the Self-Report, FMPA has implemented internal controls to prevent recurrence. No harm is known to have occurred. FMPA has one relevant prior issue of same/similar Standard. FMPA2015-100850/FRCC2015014639 (FAC-008-3 R6) FRCC determined that FMPA's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, FMPA: 1) has updated its Facility Ratings to include the correct information; 2) has implemented an internal control process that lists the source document for every value used to determine the Facility Ratings and now links the source documents to the associated documentation for the Facility Ratings spreadsheet. This control prevents the use of incorrect source documents in determining Facility Ratings; and 3) has implemented a peer review of any changes made to Facility Ratings or their components and the associated source information used. This step ensures checks are performed to prevent the use of incorrect information. FMPA now uses only the manufacturer specification, and no longer performs a calculation to determine the apparent power rating.
2016-10-31 | SERC Reliability Corporation (SERC) | Broad River Energy, LLC (BroadRiver) | NCR11313 | SERC2016016071 | MOD-025-2 | R1 | On August 31, 2016, Broad River Energy, LLC (BroadRiver) submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R1. BroadRiver did not meet the NERC implementation schedule for verifying the Real Power capability at 40% of its Facilities by July 1, 2016. BroadRiver did not complete Real Power capability verification for 40% of its units by the July 1, 2016 implementation date due to a misunderstanding of the Reliability Standard Implementation Plan and therefore did not provide its Transmission Planner with the verification of the Real Power capability of its applicable Facilities. Because the five BroadRiver generators constitute a single Facility, BroadRiver’s consultant recommended an approach that used the 100% implementation date of July 1, 2019 as its implementation deadline for the Facility. On July 14, 2016, two weeks after the 40% implementation deadline, the consultant notified BroadRiver that the guidance was incorrect. The primary cause of the instant issue is BroadRiver’s insufficient oversight of its consultant and lack of awareness of the implementation schedule for the applicable NERC Reliability Standard. The issue lasted from July 1, 2016, when the Standard became mandatory and enforceable and ended on August 31, 2016, when Broad River provided the verification information to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BroadRiver’s incorrect modelling of unit capabilities could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, BroadRiver previously provided the same modeling data required by MOD-032-1 and the recently retired Standards MOD-010-0 and MOD-012-0. Also, on August 31, 2016, BroadRiver provided the verification information for all five units to its Transmission Planner, only two months after the deadline. The BroadRiver Facility consists of five 175 MW peaking units that are under contract to, and dispatched by, a utility with approximately 13,000 MWs of generation. No harm is known to have occurred. SERC considered BroadRiver’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BroadRiver: 1) scheduled and performed the required verification testing; 2) submitted the real power verification results to the Transmission Planner; 3) created a tracking spreadsheet/implementation plan that will allow it to monitor all new and revised Standards to ensure BroadRiver meets its requirements in the proper timeframe; and 4) changed its internal oversight process to include technical staff resources for oversight of its consultants and the NERC compliance requirements.
2016-10-31 | SERC Reliability Corporation (SERC) | Broad River Energy, LLC (BroadRiver) | NCR11313 | SERC2016016072 | MOD-025-2 | R2 | On August 31, 2016, Broad River Energy, LLC (BroadRiver) submitted a Self-Report stating that, as a Generator Owner, it had an issue of MOD-025-2 R2. BroadRiver did not meet the NERC implementation schedule for verifying Reactive Power capabilities at 40% of its Facilities by July 1, 2016. BroadRiver did not complete Reactive Power capability verification for 40% of its units by the July 1, 2016 implementation date due to a misunderstanding of the Reliability Standard Implementation Plan, and therefore, did not provide its Transmission Planner with the verification of the Reactive Power capability of its applicable Facilities. Because the five BroadRiver generators constitute a single Facility, BroadRiver’s consultant recommended an approach that used the 100% implementation date of July 1, 2019 as its implementation deadline for the Facility. On July 14, 2016, two weeks after the 40% implementation deadline, the consultant notified BroadRiver that this guidance was incorrect. The primary cause of the instant issue is BroadRiver’s insufficient oversight of its consultant and lack of awareness of the implementation schedule for the applicable NERC Reliability Standard. The issue lasted from July 1, 2016, when the Standard became mandatory and enforceable and ended on August 31, 2016, when Broad River provided the verification information to its Transmission Planner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BroadRiver’s incorrect modelling of unit capabilities could affect the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, BroadRiver previously provided all modeling data required by MOD-032-1 and the recently retired Standards MOD-010-0 and MOD-012-0. Also, on August 31, 2016, BroadRiver provided the verification information for all five units to its Transmission Planner, only two months after the deadline. The BroadRiver Facility consists of five 175 MW peaking units that are under contract to, and dispatched by, a utility with approximately 13,000 MWs of generation. No harm is known to have occurred. SERC considered BroadRiver’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BroadRiver: 1) scheduled and performed the required reactive power testing; 2) submitted the reactive power verification results to the Transmission Planner; 3) created a tracking spreadsheet/implementation plan that will allow it to monitor all new and revised Standards to ensure BroadRiver meets its requirements in the proper timeframe; and 4) changing its internal oversight process to include technical staff resources for oversight of its consultants and the NERC compliance requirements.
2016-10-31 | SERC Reliability Corporation (SERC) | Broad River Energy, LLC (BroadRiver) | NCR11313 | SERC2016016073 | PRC-019-2 | R1 | On August 31, 2016, Broad River Energy, LLC (BroadRiver) submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-019-2 R1. BroadRiver did not meet the NERC implementation schedule for verifying the proper coordination of its voltage regulating system controls for 40% of its Facilities by July 1, 2016. BroadRiver did not verify the proper coordination of its voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions for 40% of its units by the July 1, 2016 implementation date due to a misunderstanding of the Reliability Standard Implementation Plan. Since the five BroadRiver generators constitute a single Facility, the approach recommended by BroadRiver’s consultant used the 100% implementation date of July 1, 2019 as its implementation deadline for the Facility. On July 14, 2016, two weeks after the 40% implementation deadline, the consultant notified BroadRiver that this guidance was incorrect. On August 23, 2016, BroadRiver issued a purchase order to an engineering firm for the required data gathering and engineering studies. The primary cause of the instant issue is BroadRiver’s insufficient oversight of its consultant and lack of awareness of the implementation schedule for the applicable NERC Reliability Standard. The issue lasted from July 1, 2016, when the Standard became mandatory and enforceable until mitigated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BroadRiver’s failure to verify the voltage regulating system controls are properly coordinated with its Protection Systems could lead to an individual generator tripping for a system event that should not have caused the generator to trip or could fail to trip before equipment damage occurred. However, the BroadRiver Facility consists of five 175 MW peaking units that are under contract to, and dispatched by, a utility with approximately 13,000 MWs of generation therefore the two 175 MW units that were noncompliant would have a minimal impact if they tripped offline. BroadRiver reported that there were no unit trips based incorrect coordination of the voltage regulating system controls and Protection Systems since the commercial operation date of the Facility. No harm is known to have occurred. Broad River has no prior noncompliance. | To mitigate this issue, BroadRiver: 1) issued a purchase order to begin the work on all five (100%) of the generating units; 2) created a tracking spreadsheet/implementation plan that will allow it to monitor all new and revised Standards to ensure BroadRiver meets its requirements in the proper timeframe; and, 3) changed its internal oversight process to include technical staff resources for oversight of its consultants and the NERC compliance requirements. To mitigate this issue, BroadRiver will complete the following mitigation activities by January 16, 2017: 1) complete the required studies; and 2) correct the identified coordination issues for any of the control systems that do not coordinate correctly with the Protection System devices.
2016-10-31 | SERC Reliability Corporation (SERC) | Broad River Energy, LLC (BroadRiver) | NCR11313 | SERC2016016096 | PRC-024-2 | R1 | On September 2, 2016, Broad River Energy, LLC (BroadRiver) submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-024-2 R1. BroadRiver did not meet the NERC implementation schedule for verifying the generator frequency protection relay settings for 40% of its Facilities by July 1, 2016. BroadRiver did not verify the settings of its generator frequency protective relaying activated to trip the units to ensure that the relays do not trip in the ‘do not trip zone’ for 40% of its units by the July 1, 2016 implementation date due to a misunderstanding of the Reliability Standard Implementation Plan. Since the five BroadRiver generators constitute a single Facility, the approach recommended by BroadRiver’s consultant used the 100% implementation date of July 1, 2019 as its implementation deadline for the Facility. On July 14, 2016, two weeks after the 40% implementation deadline, the consultant notified BroadRiver that this guidance was incorrect. The primary cause of the instant issue is BroadRiver’s insufficient oversight of its consultant and lack of awareness of the implementation schedule for the applicable NERC Reliability Standard. The issue lasted from July 1, 2016, when the Standard became mandatory and enforceable until mitigated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BroadRiver’s failure to verify the frequency relays are set in the “no trip zone”, could allow a generator to trip incorrectly for a system event. However, the BroadRiver Facility consists of five 175 MW peaking units that are under contract to, and dispatched by, a utility with approximately 13,000 MWs of generation therefore the two 175 MW units that were noncompliant would have a minimal impact if they tripped offline. BroadRiver reported that there were no unit trips based on incorrect frequency relay settings occurring since the commercial operation date of the facility. No harm is known to have occurred. Broad River has no prior noncompliance. | To mitigate this issue, BroadRiver: 1) issued a purchase order to begin the evaluation work on all five (100%) of the generating units; 2) created a tracking spreadsheet/implementation plan that will allow it to monitor all new and revised Standards to ensure BroadRiver meets its requirements in the proper timeframe; and, 3) changed its internal oversight process to include technical staff resources for oversight of its consultants and the NERC compliance requirements. To mitigate this issue, BroadRiver will complete the following mitigation activities by January 16, 2017: 1) complete the required studies; and 2) correct the frequency relay settings for any of the frequency relay settings that do not meet the standard setting requirements.
2016-10-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2016015593 | VAR-002-4 | R3 | On March 10, 2016, Duke Energy Florida, LLC (DEF) submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-4 R3. DEF submitted the Self-Report to SERC under Duke Energy Progress and an existing multi-regional registered entity agreement. DEF did not notify its Transmission Operator (TOP) of a power system stabilizer (PSS) status change within 30 minutes. In November 2015, DEF replaced a unit automatic voltage regulator (AVR) with a new AVR that included a PSS. At the time of the replacement, DEF disabled the PSS. On February 7, 2016, DEF powered off the unit’s AVR as part of a unit outage. At 9:17 p.m. the same day, DEF restored power to the AVR and the programming automatically enabled the PSS. At that time, the unit was on-line at 125 MWs and, based on the configuration, PSS was in service. However, DEF failed to notify the TOP that the PSS was in service. Plant operators noted that the PSS status light on the control board was on and investigated the AVR local panel. Operators did not identify anything abnormal. On February 8, 2016, during the morning shift-turnover briefing, the outgoing shift briefed the oncoming shift of the situation and the oncoming shift contacted the TOP to report the unexpected condition. The TOP reviewed the unit’s Voltage Schedule and verified that the Voltage Schedule did not require the PSS to be in service. On February 8, 2016, at 9:03 a.m., DEF removed the PSS from service and notified the TOP of the change. The root cause of the issue was human error. DEF staff failed to make programming changes to the configuration file of the AVR to ensure the "PSS Enable" software block was defaulted to off. The issue started on February 7, 2016 at 9:47 p.m., when DEF failed to notify the TOP of the PSS status change and ended on February 8, 2016, at 9:03 a.m., when DEF removed the PSS from service and notified the TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEF’s failure to notify the TOP of the change of state of reactive devices may lead to inappropriate voltage-controlling action by the TOP. However, DEF maintained output voltage according to the assigned Voltage Schedule throughout the period. Although DEF had not completed verification of the PSS system parameters, DEF had tuned the PSS to provide voltage stability. In addition, the unit was operating in parallel with its twin unit where AVR was in automatic voltage control. DEF operated with the PSS for only 12 hours during which the TOP did not require DEF to make any voltage corrections to the unit, and DEF did not experience any voltage excursions during the noncompliance period. The unit accounts for 556 MW of the over 10,000 MW of power generated in DEF. No harm is known to have occurred. SERC considered DEF’s compliance history and determined that there were no relevant instances of noncompliance. SERC considered DEF’s affiliate compliance history in determining the disposition track. Duke Energy Corporation (DECorp)’s and Duke Energy Progress (DEP, formerly Progress Energy Carolinas) relevant prior noncompliance with VAR-002 R3 include RFC2014014482 and SERC201000624 respectively. SERC determined that DECorp’s compliance history should not serve as a basis for applying a penalty. In RFC2014014482, operators at one power plant failed to notify the TOP after an AVR returned to automatic voltage control mode following repairs. In SERC201000624 DEP identified 14 instances in which operators failed to notify the TOP of a status or capability change of its AVR or PSS and the expected duration of the change in status or capability. All of those instances related to normal operating conditions and operators experienced with the equipment. In the instant issue, a new PSS was inadvertently enabled and made active, resulting in a delay to notify the TOP. The facts and circumstances of the instant issue are substantially different and that the mitigating actions for the prior issues would not have prevented the instant issue. | To mitigate this issue, DEF: 1) made programming changes to the configuration file of the AVR to ensure the "PSS Enable" software block is defaulted to off; 2) prepared an internal event report to create lessons learned; and, 3) shared the lessons learned with other Duke generation stations.
2016-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Cleco Corporation (CLECO) | NCR01083 | SPP2016015685 | VAR-002-3 | R2; R2.1; R2.2; R2.3 | During a Compliance Audit conducted from April 19, 2016 through April 21, 2016, SPP RE determined that Cleco, as a Generator Operator, had a minimal risk instance of noncompliance with VAR-002-3 R2. The Acadia generating station has a winter and summer voltage schedule. Cleco did not maintain generator voltage within the assigned winter voltage schedule provided by its Transmission Operator (TOP) at one out of six sampled generation plants. Specifically, at the Acadia generating plant, the generator voltage exceeded the voltage schedule by one to two kV during three of the sampled 23-week period. The TOP was not notified of the voltage exceedances as required by VAR-002-3 R2. The duration of this instance of noncompliance began on January 1, 2015, the beginning of the period for data retention as required by the standard, and ended on May 1, 2016, the date the plant switched to its summer schedule and began maintaining generator voltage within the assigned summer voltage schedule. The root cause of this instance of noncompliance was lack of internal controls because a review by plant management was not adequately performed based on the assumption that the voltage schedules would not change. Therefore, the voltage schedules were not forwarded to the plant operators. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Cleco’s failure to maintain the generator voltage as directed by the TOP could have caused a mismatch between expected and actual generator output voltage, resulting in insufficient voltage support. However, this voltage schedule deviation provided extra reactive support to the BPS. Seven other generators on Cleco’s System were running within their voltage schedules, which minimized any effect of operating one generating unit outside the voltage schedule. No harm is known to have occurred. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities, including Cleco’s noncompliance with VAR-002-1.1b R3 (SPP2012010777) was filed with FERC under RC12-16-000 on September 28, 2012. The 60-day review period passed on November 27, 2012. SPP RE considered Cleco’s compliance history and determined that the instant compliance issue was appropriate for Compliance Exception treatment. The prior noncompliance involved a different VAR requirement, and the noncompliance was related to an AVR tripping to manual and not deviations from Cleco's voltage schedule. | To mitigate this minimal risk instance of noncompliance, Cleco: 1) conducted shift meetings to retrain control room operators on the voltage schedule document and the notification steps with the Transmission Operator; and 2) implemented a voltage alarming window containing both the summer and winter schedules on the main control screen at the Acadia Power Plant, which will send operators notification if voltage drifts outside the voltage tolerance band. SPP RE has verified the completion of all mitigation activity.
2016-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (WR) | NCR00658 | SPP2016015767 | PRC-005-2(i) | R3 | On May 26, 2016, Westar Energy, Inc. (WR) submitted a Self-Report stating that, as a Transmission Owner and Generator Owner, it had a minimal risk instance of noncompliance with PRC-005-2(i) R3. During an internal compliance self-assessment in April 2016, WR discovered it had not performed all battery maintenance activities in accordance with the maximum maintenance intervals defined in WR’s protection system maintenance and testing program (PSMTP). Specifically, 13 valve-regulated lead-acid batteries had not been inspected within the four-month interval specified in the PSMTP. Additionally, seven vented lead-acid batteries had not been inspected within the six-month interval defined in the PSMTP. The root cause of this instance of noncompliance was a lack of internal controls to ensure all battery maintenance activities were completed within the maximum maintenance intervals defined in WR’s PSMTP. Specifically, WR’s internal controls lacked follow up on the increased number of automated work orders that resulted from the implementation of version 2 of PRC-005 R3. The duration of this instance of noncompliance was from October 1, 2015, when PRC-005-2 was implemented until March 30, 2016, the date of the last battery maintenance activity. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to perform timely battery maintenance tests has the potential to affect the reliability of the BPS by increasing the risk that the batteries will fail and not provide power over the expected amount of time. The risk to the BPS was reduced by the following factors. WR timely identified and self-reported the noncompliance and immediately performed a full population of testing and maintenance activities. Only 20 battery inspections out of 209 battery banks were missed (10.45%) over a five-month period. All missed inspections were corrected during the same five months. No harm is known to have occurred. WR has no relevant prior violations of PRC-005-2(i) R3 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, WR: 1) performed a full population of battery inspection and maintenance activities to determine the scope of the noncompliance; 2) implemented additional internal controls, such as an increase in reminders of open work orders to affected personnel, including management, and mandatory managerial involvement, to ensure continued tracking and oversight of work order completion; and 3) developed awareness and training activities for affected personnel. SPP RE has verified the completion of all mitigation activity.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | WECC2016015655 | TOP-002-2.1b | R4 | On April 8, 2016, FEUS submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with TOP-002-2.1b R4. During an internal compliance audit, FEUS discovered that it did not update its seasonal studies to determine System Operating Limits (SOLs) in 2014 and 2015. Consequently, FEUS failed to coordinate seasonal planning and operations as required by R4. This issue began January 1, 2014, when the prior studies were no longer current, and ended February 13, 2016, when FEUS became an active member of the Southwest Area Subregional Group (SASG). The root cause of this issue was insufficient administrative oversight governing delegation of responsibility for seasonal studies following retirement of one of FEUS' engineering managers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, FEUS failed to perform seasonal Bulk Electric System studies, and therefore did not coordinate its seasonal planning with neighboring TOPs, Balancing Authorities, and its Reliability Coordinator. Such failure could have limited neighboring entities’ awareness of newly discovered operating contingencies or adjustments to SOLs. However, FEUS’ load profile did not change significantly throughout the duration of this issue. FEUS’ transmission assets primarily bring power into its service area; had this issue resulted in the loss of a transmission line, outages likely would have been limited to FEUS’ system. Additionally, although FEUS failed to perform seasonal studies, it did perform current-day, next-day, and heavy summer contingency studies, which provided load planning information and did not indicate a foreseen overload during the period in question. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. FEUS had one previous violation of this Standard and Requirement, given Violation ID: WECC200810036. The previous violation was not considered an aggravating factor because mitigating activities were completed more than three years prior to this issue. | To mitigate this issue, FEUS distributed updated studies via the SASG. Because FEUS will schedule, perform and coordinate future seasonal studies as part of its participation in the SASG, this issue is not likely to recur. WECC verified completion of FEUS’ mitigating activities.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | WECC2016015656 | TOP-002-2.1b | R11 | On April 8, 2016, FEUS submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with TOP-002-2.1b R11. During an internal compliance audit, FEUS discovered that it did not update its seasonal studies to determine System Operating Limits (SOLs) in 2014 and 2015. Consequently, FEUS did not make results of such studies available to neighboring TOPs, Balancing Authorities, and its Reliability Coordinator as required by R11. This issue began January 1, 2014, when the prior studies were no longer current, and ended February 13, 2016, when FEUS became an active member of the Southwest Area Subregional Group (SASG). The root cause of this issue was insufficient administrative oversight governing delegation of responsibility for seasonal studies following retirement of one of FEUS' engineering managers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, FEUS failed to perform seasonal Bulk Electric System studies, and therefore did not make updated studies available to neighboring TOPs, Balancing Authorities, and its Reliability Coordinator. Such failure could have limited neighboring entities’ awareness of newly discovered operating contingencies or adjustments to SOLs. However, FEUS’ load profile did not change significantly throughout the duration of this issue. FEUS’ transmission assets primarily bring power into its service area; had this issue resulted in the loss of a transmission line, outages likely would have been limited to FEUS’ system. Additionally, although FEUS failed to perform seasonal studies, it did perform current-day, next-day, and heavy summer contingency studies, which provided load planning information and did not indicate a foreseen overload during the period in question. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. | To mitigate this issue, FEUS distributed updated studies via the SASG. Because FEUS will schedule, perform and coordinate future seasonal studies as part of its participation in the SASG, this issue is not likely to recur. WECC verified completion of FEUS’ mitigating activities.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2015015153 | PRC-004-WECC-1 | R1; R1.1 | On August 14, 2015, PGE submitted a Self-Report stating that as a Transmission Owner, it had a possible issue of noncompliance with PRC-004-WECC-1 R1.Specifically, PGE reported that it failed to review a 230kV tie line operation within 24 hours as required by R1.1. On May 21, 2015, a lightning strike caused a 230kV line to trip and reclose at both ends. This incident occurred so quickly that the system used by PGE and the entity on the other end of the line for Inter-Control Center Communication Protocol (ICCP) communication did not detect the operation. PGE’s Energy Management System (EMS) also failed to detect the operation. Following discovery of this issue, PGE determined that this failure was caused by a programming problem which prevented the alarm from displaying on the EMS screen. Because this operation did not register on PGE’s EMS or ICCP systems, PGE did not review the operation until it was brought to its attention by the entity on the other end of the line on June 17, 2015. This issue began May 22, 2015; 24 hours after the line tripped, and ended June 18, 2015, when PGE’s analysis determined the Protection System operated correctly. The root cause of this issue was a programming problem which prevented the alarm from displaying on the EMS screen. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, PGE failed to review a 230kV tie line operation within the 24 hour timeframe prescribed in R1.1. If the event had resulted in incorrect operation, PGE may not have identified the Misoperation timely. However, this issue was limited to one incident and resulted in the correct operation of the Protection System. Although PGE did not begin to assess the operation within 24 hours, it did complete its analysis of the operation within the 20 day timeframe prescribed by R1.2. Additionally, the entity on the other end of the line investigated the operation timely and provided PGE evidence of its investigation. PGE reported that the ICCP system’s failure to detect this type of event was not unexpected – the event occurred so quickly that it was not captured between scans. The coincident failure of the EMS Systems alarm, however, posed a more significant risk. During its investigation of this issue, PGE’s EMS vendor acknowledged the alarm tagging issue as a known, system-wide programming problem. The vendor has since resolved the problem on PGE’s system. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. PGE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PGE: 1) performed an analysis of the operation and determined the Protection System operated correctly; 2) resolved the alarm tagging issue on PGE’s end of the line to ensure future trips will alarm and display correctly, and verified that there were no tagging or mapping issues on the neighboring entity’s end of the line; 3) distributed an email and provided supplemental training for this Standard; and 4) initiated a procedural change to improve alarm visibility and ensure timely delivery of alarm information to requisite staff. WECC verified that PGE completed the above-listed mitigating activities on July 21, 2016.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2016015579 | EOP-010-1 | R3; R3.2 | On February 29, 2016, PSE submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with EOP-010-1 R3. PSE reported that during an internal review on December 28, 2015, PSE discovered that its System Operator did not perform actions prescribed in PSE’s Geomagnetic Disturbance (GMD) Operating Process following receipt of a GMD warning notification from the Reliability Coordinator (RC). Specifically, at 5:18 a.m. PST on August 15, 2015, the RC issued a GMD warning regarding a K7-strength GMD event forecasted to affect PSE’s system between 4:45 a.m. PST and 7:00 a.m. PST. The RC usually issues notifications of this nature two or three days in advance of an event; however, in this instance PSE received the notification 33 minutes after the event was predicted to begin. Regardless of the notification’s unusual timing, personnel on shift during this event failed to implement certain actions required by PSE’s GMD Operating Process in accordance with EOP-010-1 R3.2. This issue began and ended on August 15, 2015 – the forecasted duration of the event. This issue was caused by human error; personnel's capability to perform work was hindered by cumbersome procedures. | In this instance, PSE failed to implement actions outlined in its GMD Operating Process following receipt of a GMD warning. Such failure could have resulted in an inappropriate or insufficient response to a GMD-related event. However, although PSE did not specifically follow its GMD Operating Process, it continued to monitor system alarms and perform other established procedures throughout the duration of the event. The event did not result in any system alarms or other adverse effects. Additionally, the potential risk posed by any geomagnetic-induced current associated with this event would only have affected a single transformer, impacting only three percent of PSE’s system. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. PSE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) conducted an internal review to verify that this issue was limited to a single event; 2) reevaluated its GMD Operating Process, and modified procedures therein to correspond with both the Standard and PSE’s system; 3) updated its annual training to reflect modifications to its GMD Operating Process; and 4) distributed formal communications regarding a) modifications to its GMD Operating Process and b) lessons learned regarding this issue to requisite staff. WECC verified completion of PSE’s mitigating activities.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Salt River Project Agricultural Improvement and Power District (SRP) | NCR05372 | WECC2015015438 | BAL-005-0.2 | R8 | On December 29, 2015, SRP submitted a Self-Report stating that, as a Balancing Authority, it had a possible issue of noncompliance with BAL-005-0.2b R8. During an annual compliance review conducted November 9, 2015, SRP discovered that data from two transmission tie lines it used in SRP’s Area Control Error (ACE) calculation, was not acquired at least every six seconds. Specifically, the scan intervals on the associated Remote Terminal Units (RTUs) were erroneously set to collect data from the tie lines every ten seconds instead of six seconds. This issue concerned a tie line to WAPA within the Duke 500 kV station and a tie line from the 138 kV Sulpherdale station to the Tushar station. This issue of noncompliance began November 25, 2013, when SRP failed to acquire and apply timely data from one of the tie lines, and ended November 9, 2015, when SRP discovered the issue and reset the scan intervals for both tie lines. The cause of this issue of noncompliance was less than adequate documented procedures; SRP’s procedure was not sufficient to ensure that the RTU settings were appropriate for correlating tie line types in six seconds. In this instance, the RTUs were inadvertently programmed for the scan rate associated with distribution tie lines, rather than transmission tie lines. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, SRP failed to ensure data acquisition at least every six seconds. Such failure could have resulted in delayed and/or erroneous load-generation balancing measures. However, this issue was limited to two of SRP’s sixty-six applicable tie lines, with a combined transfer capability of roughly 220 MW out of SRP’s 6,611 MW total generation. SRP’s energy management system (EMS) continued to calculate ACE and control generation on a two second cycle. And, the maximum delay of an issue would have been less than 8 seconds. SRP would have identified and corrected inadvertent issues during the end-of-hour time-line net checkouts. No harm was known to have occurred. Additionally, SRP implemented detective controls. SRP’s EMS displays the status of all tie lines and SRP performs annual reviews of its RTUs; however, this issue was not readily apparent because RTU scan intervals are only visible via manual review and individual editing of each RTU’s sample rate in SRP’s database model configuration. WECC notes that SRP has identified and self-reported the issues described herein, does not have previous violations of this Standard or any of its Requirements, and has provided documentation of its internal compliance program for WECC’s review. | SRP remediated this issue on November 9, 2015, when it discovered and corrected the scan intervals of the RTUs associated with the tie lines in scope. SRP also reviewed the scan intervals of all other transmission tie lines to verify that this issue was limited to the two tie lines originally reported. In an effort to prevent recurrence, SRP revised procedural documentation to ensure that RTU settings 1) correlate to the appropriate tie line types during input to SRP’s ACE monitoring software, and 2) are addressed during SRP’s annual review process.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Salt River Project Agricultural Improvement and Power District (SRP) | NCR05372 | WECC2015015439 | BAL-005-0.2b | R16 | On December 29, 2015, SRP submitted a Self-Report stating that, as a Balancing Authority, it had a possible issue of noncompliance with BAL-005-0.2b R16. During an annual compliance review conducted November 9, 2015, SRP discovered that data from two transmission tie lines it used in SRP’s Area Control Error (ACE) calculation, was not sampled every two seconds at the same periodicity with which ACE is calculated. Specifically, the scan intervals on the associated Remote Terminal Units (RTUs) were erroneously set to collect data from the tie lines every ten seconds. This issue concerned a tie line to WAPA within the Duke 500 kV station and a tie line from the 138 kV Sulpherdale station to the Tushar station. This issue of noncompliance began November 25, 2013, when SRP failed to acquire and apply timely data from one of the tie lines, and ended November 9, 2015, when SRP discovered the issue and reset the scan intervals for both tie lines. The cause of this issue of noncompliance was less than adequate documented procedures; SRP’s procedure was not sufficient to ensure that the RTU settings were appropriate for correlating tie line types in six seconds. In this instance, the RTUs were inadvertently programmed for the scan rate associated with distribution tie lines, rather than transmission tie lines. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, SRP failed to acquire data from two transmission tie lines every two seconds, and therefore fialed to smaple the data at the same periodicity with which ACE is calculated. Such failure could have resulted in delayed and/or erroneous load-generation balancing measures. However, this issue was limited to two of SRP’s sixty-six applicable tie lines, with a combined transfer capability of roughly 220 MW out of SRP’s 6,611 MW total generation. SRP’s energy management system (EMS) continued to calculate ACE and control generation on a two second cycle. And, the maximum delay of an issue would have been less than 8 seconds. SRP would have identified and corrected inadvertent issues during the end-of-hour time-line net checkouts. No harm was known to have occurred. Additionally, SRP implemented detective controls. SRP’s EMS displays the status of all tie lines and SRP performs annual reviews of its RTUs; however, this issue was not readily apparent because RTU scan intervals are only visible via manual review and individual editing of each RTU’s sample rate in SRP’s database model configuration. WECC notes that SRP has identified and self-reported the issues described herein, does not have previous violations of this Standard or any of its Requirements, and has provided documentation of its internal compliance program for WECC’s review. | SRP remediated this issue on November 9, 2015, when it discovered and corrected the scan intervals of the RTUs associated with the tie lines in scope. SRP also reviewed the scan intervals of all other transmission tie lines to verify that this issue was limited to the two tie lines originally reported. In an effort to prevent recurrence, SRP revised procedural documentation to ensure that RTU settings 1) correlate to the appropriate tie line types during input to SRP’s ACE monitoring software, and 2) are addressed during SRP’s annual review process.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Silicon Valley Power (SNCL) | NCR05392 | WECC2016015601 | EOP-008-1 | R4 | On March 1, 2016, SNCL submitted a Self-Report stating that as a Transmission Operator, it had a possible issue of noncompliance with EOP-008-1 R4. Specifically, SNCL reported that it had scheduled a planned outage of its Backup Electric Control Center (BECC) to move it to a newly acquired facility, but did not restore backup functionality within the two weeks specified in the Standard. SNCL’s Control Room and System Support staffs planned an outage of one month for the BECC outage, failing to recognize the relocation plan was not compliant with the two-week timeframe required by EOP-008-1 R4. SNCL’s Compliance staff identified the failure, and requested the BECC be returned to functionality as soon as possible. SNCL restored BECC functionality on March 10, 2016. The cause of this issue of noncompliance was SNCL's System Support and Control Room staff's less-than-adequate compliance understanding, leading to a failure to seek SNCL Compliance staff’s assistance in interpreting the applicable NERC Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SNCL failed to restore backup functionality in two weeks after a planned outage. If SNCL’s Primary Control Center (PCC) had been compromised, not having backup functionality could lead to SNCL losing complete visibility and control of its system. However, because this was a planned outage, SNCL had a robust contingency plan (Electric Control Center – Backup Functionality Operating Plan, Energy Distribution Standard S-0051), in place in the event of loss of its BES remote control and monitoring. According to SNCL’s contingency plan, if the PCC was compromised while the BECC was out of service, SNCL was prepared to dispatch field switching personnel to monitor and report at each BES substation. Because SNCL implemented both detective and corrective controls, as soon as SNCL Compliance staff learned that the BECC was being moved, the Control Room and System Support staff were informed that they should complete the work as quick as possible. The BECC move was completed a week ahead of the original plan. No harm was known to have occurred. WECC notes that SNCL has identified and self-reported the issue described herein, does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program for WECC’s review. | SNCL remediated this issue on March 10, 2016, when it reconnected the BECC and returned it to full functionality. To prevent future occurrence, SNCL Compliance staff discussed the issue with SNCL’s Control Room and System Support staffs, and reinforced its procedures to include SNCL Compliance staff whenever a NERC Standard is in question. Further, SNCL submitted an attestation that it had discussed the issue in a monthly Compliance Team meeting, and held a follow-up meeting with executive management on June 10, 2016.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Solar Star California XIII, LLC (SXIII) | NCR11549 | WECC2016015842 | PRC-005-2(i) | R1 | On June 21, 2016, SXIII submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with PRC-005-2(i) R1. Specifically, the Protection System Maintenance Program (PSMP) documentation for SXIII’s only Bulk Electric System (BES) facility was incomplete for a period of roughly three months. This issue began November 30, 2015, the commercial operation date of the facility, and ended March 8, 2016, when SXIII finalized its PSMP documentation. The root cause of this issue was less than adequate check of work. SXIII failed to verify that the PSMP documentation was complete and formalized prior to commercial operation of the facility. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, SXIII failed to appropriately document its PSMP prior to the commercial operation date of a new BES facility. Insufficient documentation could limit SXIII’s ability to ensure implementation of its PSMP. However, this issue concerned a single, recently-commissioned, 107 MW solar facility. SXIII tested all applicable Protection System equipment at the facility upon commissioning, and did not exceed any testing intervals over the duration of this issue. All alarms associated with BES equipment and Protection Systems are actively monitored in SXIII’s control center. SXIII discovered and resolved the issue expeditiously. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. SXIII does not have previous violations of this Standard and Requirement. | To mitigate this issue, SXIII: 1) completed and formalized its PSMP documentation; 2) hired additional compliance staff; 3) developed and implemented compliance management tools; 4) formalized an internal compliance program; 5) provided formal training to relevant staff regarding NERC compliance; and 6) revised its procedure to require a formal NERC compliance assessment prior to registration and commercial operation of any future facilities. WECC verified completion of SXIII’s mitigating activities.
2016-09-29 | Northeast Power Coordinating Council (NPCC) | Bridgeport Energy, LLC | NCR03035 | NPCC2016015760 | EOP-004-2 | R3. | On April 29, 2016, Bridgeport Energy, LLC submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it had an issue of EOP-004-2 R3. During a review of documents, Bridgeport Energy staff has determined that it cannot locate documented validations for all contact information in the Operating Plan under EOP-004-2 Requirement 3 for calendar years 2014 and 2015, although all contact information had in fact been updated in the ordinary course of business in a timely manner except for the FBI contact. Throughout this period, the Operating Plan under EOP-004-2 continued to exist as a plant resource with valid contact information and all outside contact information in the Operating Plan except for the FBI contact was validated in the ordinary course of plant business and only the final step of documenting the validation of contacts in the Operating Plan was not completed. The issue started on January 1, 2015 which is the first day after the conclusion of Bridgeport Energy's defined calendar year, and ended on August 23, 2016, when Bridgeport Energy updated their operating plan and verified their local law enforcement contact | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Throughout this period, there was no risk to the bulk power system that resulted from the lack of documented contact validations for 2014 and 2015. The standard requires the reporting of events, and the requirement at issue ensures that the contact information for reporting events that is contained in the Operating Plan remains valid. All outside contacts except the FBI contact were updated in a timely manner in the regular course of business. Plant staff has confirmed and documented that all outside contact information in the Operating Plan, including the FBI contact information, remains current and valid. No harm is known to have occurred. NPCC considered Bridgeport Energy's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate the issue, Bridgeport Energy, LLC: 1. Developed a standing work order in its work management system. This will ensure the appropriate personnel are automatically notified to complete the annual documented contact validations; 2. Formally validated all outside contacts; and 3. Updated its operational plan to include local law enforcement. NPCC has verified the completion of all mitigation activity.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2016016049 | PRC-023-3 | R1. | On April 15, 2016, AEP submitted a self-log stating that, as a Transmission Owner, Generator Owner, and Distribution Provider, it had an issue of PRC-023-3 R1. The Tristate – Sporn 345kV line was energized on October 11, 2015, with relay settings calculated using a CT ratio of 400:1 when AEP should have used a CT ratio of 240:1, which was the actual CT ratio as implemented. Using the 400:1 ratio, AEP performed a relay loadability evaluation prior to energization and determined that the relay trip limit was compliant with PRC-023-3, R1, Criterion 1. (AEP Transmission applies PRC-023-3 R1, Criterion 1 for all transmission lines applicable to the standard.) While reviewing a station one-line diagram on October 22, 2015, a protection and control engineer discovered that the CT ratio used in the relay setting calculation was shown on the diagram wired at 240:1, rather than the 400:1 ratio that was used to calculate the relay settings. Upon further investigation, AEP found that the CT ratio was left at 240:1 in the diagram because the CT ratio was not physically re-wired to the 400:1 ratio and instead was set at 240:1. AEP then calculated the relay setting using the actual CT ratio of 240:1 and determined that, with the 240.1 CT ratio, the actual relay loadability did not meet Requirement 1, Criterion 1. On October 29, 2015, the revised relay settings were applied to the relay using the 240:1 wired CT ratio in the trip setting calculation. A relay loadability evaluation performed prior to issuing settings determined that the settings were compliant with Requirement 1, Criteria 1. The root cause was a lack of effective verification because the AEP employee did not verify that the CT ratio in the diagram was the correct CT ratio. This issue started on October 11, 2015, when AEP incorrectly determined that the relay trip limit for the transmission line was compliant with PRC-023-3 R1 because AEP used an incorrect CT ratio in the calculation, and ended on October 29, 2015, when AEP applied the revised relay settings using the correct CT ratio to get the accurate relay trip limit for the transmission line. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. During the noncompliance, this line was at an increased risk to trip because the relay trip setting was the most limiting series element. However, during the time period, it was unlikely that the line would have loaded past the limit due to the short duration of the incident and the season during which it occurred. And, as expected, loading on the facility was well below the limit during this period of time. As a result, the likelihood of harm occurring as a result of this issue is minimal. No harm is known to have occurred. | To mitigate this issue, AEP: 1) revised the relay settings using a CT ratio of 240:1 in the trip setting calculation. These revised settings were applied to the relay on October 29, 2015; and 2) performed a relay loadability evaluation and determined that the settings were compliant with Requirement 1, Criterion 1.
2016-09-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Midland Cogeneration Venture, Limited Partnership (MCV) | NCR10282 | RFC2016015571 | PRC-005-2(i) | R3 | On February 22, 2016, following an audit notification sent by ReliabilityFirst on February 15, 2016, MCV submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-2(i) R3. In its Self-Report, MCV explained that it was missing evidence for tests on 12 relays (i.e., those required to have been performed in 2009) because the computer system in place at the time experienced errors that overwrote the prior test results when subsequent testing was performed (MCV has a total of 144 relays at its generating station.). During the ensuing Compliance Audit conducted from May 16, 2016, through June 1, 2016, ReliabilityFirst confirmed that the evidence was missing (i.e., from 2009) because the data was overwritten. However, MCV provided the months and years for when it attested that the previous testing was completed, but it did not have the test data sheets to support those months and years. In any event, MCV had evidence of its current tests from 2015 for all of its relays. ReliabilityFirst also identified additional instances of noncompliance including a lack of evidence that relay sample #4 (OC 50BF/6010) was maintained within its interval, and a lack of testing evidence for relay sample #21 (a Beckwith digital relay). The root cause of this noncompliance was the fact that MCV’s database would overwrite previous relay maintenance tests. Due to this malfunction, MCV was unable to produce evidence of previous relay maintenance tests results. This contributing factor involves the management practices of asset and configuration management, grid maintenance, and information management. This issue started on January 1, 2016, the date on which MCV was required to comply with PRC-005-2(i) R3 and ended on February 22, 2016, when MCV completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, this was a documentation issue. MCV attested and provided some evidence that it had completed the previous relay maintenance, but did not have the actual test results to confirm that the maintenance was performed on the relays. Second, the risk associated with failing to perform relay maintenance tests (i.e, the risk that a relay would malfunction or fail) was mitigated by MCV’s completion of the 2015 tests in accordance with the new PRC-005-2, which requires more intense testing than was previously prescribed by the prior version of PRC-005. No harm is know to have occurred. ReliabilityFirst considered MCV’s PRC-005 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MCV: 1) performed 2015 tests in accordance with the new PRC-005-2; 2) implemented a new file naming convention that prevents test records from being overwritten; 3) committed to provide training to relay technicians on the Megger Advanced Visual Test Software used to manage all aspects of protective relay testing; and 4) committed to explore the implementation of the Qualtrax workflow system to provide enhanced alerts related to relay testing.
2016-09-29 | SERC Reliability Corporation (SERC) | Prairie Power, Inc. (Prairie) | NCR09035 | SERC2016015878 | PRC-019-2 | R1 | On July 1, 2016, Prairie submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-019-2 R1. Prairie did not complete the required generation capacity study for 40% of its applicable Facilities by July 1, 2016. Prairie’s applicable Facilities consist of five simple-cycle natural gas fired combustion turbine peaking units located at the Alsey Generating Station. In November 2015, Prairie started construction on an additional simple-cycle natural gas fired unit at this site and it had an April 2016 expected commercial operation date. In addition, Prairie intended to upgrade the existing units’ relays and control systems in conjunction with control system and relay installations on the new unit. However, Prairie experienced unexpected construction delays that resulted in the new unit not being ready for operations by July 1, 2016. The delay resulted in a Prairie failing to upgrade its existing unit’s relays and control systems, which Prairie planned to upgrade prior to performing the required PRC-019 generation capacity studies. In June 2016, Prairie provided information to a third party to assist in completing the studies. However, on June 8, 2016, the third party informed Prairie that it could not complete the studies by July 1, 2016. The root cause was insufficient project management planning. Prairie integrated multiple unrelated scopes of work into one project and failed to meet compliance obligations. This issue started on July 1, 2016, when the Standard became mandatory and enforceable, and ended on September 1, 2016, when the third party completed the studies. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Prairie’s failure to properly coordinate between generator protective relays, generator voltage regulator controls and limit functions could result in generators unnecessarily tripping off-line. However, Alsey Generating Station’s existing units are small, simple-cycle peaking generators with an aggregate capacity rating of 121 MW. In addition, the units do not operate on a regular basis. The plant's capacity factor for the most recent three years has been 1.0%, 0.49% and 1.1% respectively. No harm is known to have occurred. SERC considered Prairie’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Prairie: 1) provided existing capability studies, relay settings, exciter settings, and relay instruction books for two of its units to a third party for assistance in completing the required studies. The two units equate to 40% of the existing generating units at the Facility; 2) recognized, and documented as a lesson learned, the effect of integrating multiple scopes of work into a single project; and, 3) completed the required study for the two units.
2016-09-29 | Southwest Power Pool Regional Entity (SPP RE) | Caney River Wind Project, LLC (CRWP) | NCR11230 | SPP2016015725 | PRC-005-2(i) | R3 | On May 5, 2016, Caney River Wind Project (CRWP) submitted a Self-Report stating that as a Generation Owner, it had a minimal risk instance of noncompliance with PRC-005-2(i) R3. CRWP’s Protection System maintenance and testing program calls for inspecting the condition of its valve regulated lead acid (VRLA) batteries by measuring the batteries’ cell/unit internal ohmic values on a six calendar month interval. CRWP missed the six calendar month interval inspection of its two VRLA batteries due on March 31, 2016, because the technician responsible for battery maintenance resigned unexpectedly. CRWP was unable to procure a contractor to complete the inspection by March 31st. The battery inspections were completed on April 4, 2016. The root cause of this issue was the unexpected resignation of the CRWP employee responsible for implementing the scheduled battery maintenance and the lack of a backup plan/procedure to prevent this type of issue from occurring. The issue began on April 1, 2016, when the six calendar month interval was missed and ended April 4, 2016, when the battery testing was completed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CRWP missed the six calendar month maximum interval for battery maintenance by 4 days. No harm is known to have occurred. SPP RE considered CRWP’s compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. The instant issue is appropriate for Compliance Exception. | To mitigate this minimal risk instance of noncompliance, CRWP: 1) programmed their maintenance tool to populate a work order and notifications four weeks before the battery maintenance due date; 2) outsourced the six-month battery tests to an electrical company. The new contractor has been scheduled for the next six-month battery test and will do this test moving forward; 3) tasked the site supervisor with overseeing the work orders and ensuring the test activity is planned and executed before the deadline; and 4). tasked the site supervisor with sharing the testing results with the electrical Subject Matter Experts for review and uploading into document management system. SPP Regional Entity has verified the completion of all mitigation activity.
2016-09-29 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (CVWP) | NCR11291 | SPP2016015726 | PRC-005-2(i) | R3 | On May 5, 2016, Chisholm View Wind Project (CVWP) submitted a Self-Report stating that as a Generation Owner, it had a minimal risk instance of noncompliance with PRC-005-2(i) R3. CVWP’s Protection System maintenance and testing program calls for inspecting the condition of its valve regulated lead acid (VRLA) batteries by measuring the batteries’ cell/unit internal ohmic values on a six calendar month interval. CVWP missed the six month interval inspection of its two VRLA batteries due on March 31, 2016, because the technician responsible for battery maintenance resigned unexpectedly. CVWP was unable to procure a contractor to complete the inspection by March 31st. The battery inspections were completed on April 5, 2016. The root cause of this issue was a combination of the unexpected resignation of the CVWP employee responsible for implementing the scheduled battery maintenance and the lack of a backup plan/procedure to prevent this type of issue from occurring. The duration of this instance of noncompliance was from April 1, 2016, the date the six calendar month interval was missed, until April 5, 2016 when the battery testing was completed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). CVWP missed the six month maximum interval for battery maintenance by five days. The failure to perform timely battery maintenance tests has the potential to affect the reliability of the BPS by increasing the risk that the batteries will fail and not provide power over the expected amount of time. The risk to the BPS was reduced by the following factors. CVWP personnel properly performed all other testing activities for the VRLA batteries, and all testing activities for all other station Components as required under PRC-005-2(i) R3. When CVWP performed the required six-month ohmic measurements, the VRLA batteries tested at acceptable levels. CVWP timely identified, self-reported, and mitigated the noncompliance. No harm is known to have occurred. CVWP has no relevant prior violations for PRC-005-2(i) R3 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, CVWP: 1) programmed their maintenance tool to populate a work order and notification four weeks before the battery maintenance due date; 2) outsourced the six-month battery tests to an electrical company. The new contractor has been scheduled for the next six-month battery test and will conduct tests moving forward; 3) tasked the site supervisor with overseeing the work orders and ensuring the test activity is planned and executed before the deadline; and 4). tasked the site supervisor with sharing the testing results with the electrical Subject Matter Experts for review and uploading into the document management system. SPP Regional Entity has verified the completion of all mitigation activity.
2016-09-29 | Southwest Power Pool Regional Entity (SPP RE) | Origin Wind Energy, LLC (ORGNWE) | NCR11496 | SPP2016015495 | PRC-005-2(i) | R3 | On January 29, 2016, Origin Wind Energy, LLC (ORGNWE) submitted a Self-Report stating that, as a Generation Owner, it had a minimal risk instance of noncompliance with PRC-005-2(i) R3. ORGNWE’s Protection System Maintenance and Testing Program calls for inspecting the condition of its two valve regulated lead acid (VRLA) batteries by measuring the batteries’ cell/unit internal ohmic values on a six-calendar-month interval. ORGNWE missed the six-month interval battery inspection, which was due on September 30, 2015, because of an error on its battery testing schedule. As part of the transition to PRC-005 Version 2, ORGNWE implemented an updated battery testing schedule in its battery testing schedule tool. When inputting data in the new schedule, an ORGNWE employee inadvertently entered the wrong date of the initial battery test to calculate the next six-month interval testing due date. As a result, the incorrect testing schedule reflected that ORGNWE’s initial six-month battery test was conducted in June 2015, thus requiring the next six-month interval test to be conducted in December 2015. Although the batteries were tested in December 2015, ORGNWE later discovered the typographical error and that the initial battery test was actually conducted in March 2015. Therefore, the next six-month interval battery test was due in September 2015. The duration of this instance of noncompliance was from September 19, 2015, the date the batteries were required to have been tested, through December 23, 2015, the date ORGNWE completed the battery test. The root cause of this instance of noncompliance was a combination of human error and a lack of internal controls to ensure accuracy of the battery testing schedule. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ORGNWE missed the six calendar month maximum interval for battery maintenance by three months. The failure to perform timely battery maintenance tests has the potential to affect the reliability of the BPS by increasing the risk that the batteries will fail and not provide power over the expected amount of time. The risk to the BPS was reduced by the following factors. ORGNWE missed the six-month battery testing interval by only three months and they immediately remedied the schedule error. ORGNWE personnel properly performed all other testing activities for the VRLA batteries, and all testing activities for all other station Components as required under PRC-005-2(i) R3. When ORGNWE performed the required six-month ohmic measurements, the VRLA batteries tested at acceptable levels. The generation units supported by the VRLA batteries are only 2 MW in size, and therefore would have a small impact in the event of battery failure. ORGNWE timely identified, self-reported, and mitigated the noncompliance. No harm is known to have occurred. ORGNWE has no relevant prior violations for PRC-005-2(i) R3 or any other standards that are similar in nature to this instance of noncompliance. | To mitigate this minimal risk instance of noncompliance, ORGNWE: 1) completed battery testing; and 2) hired an additional Wind Technician to monitor the testing schedule. SPP RE has verified the completion of all mitigation activity.
2016-09-29 | Southwest Power Pool Regional Entity (SPP RE) | Rocky Ridge Wind Project, LLC (RRWP) | NCR11234 | SPP2016015724 | PRC-005-2(i) | R3 | On May 5, 2016, Rocky Ridge Wind Project (RRWP) submitted a Self-Report stating that as a Generation Owner, it had a minimal risk instance of noncompliance with PRC-005-2(i) R3. RRWP’s Protection System Maintenance and Testing Program calls for inspecting the condition of its valve regulated lead acid (VRLA) batteries by measuring the batteries’ cell/unit internal ohmic values on a six calendar month interval. RRWP missed the six calendar month interval inspection of its two VRLA batteries due on March 31, 2016, because the technician responsible for battery maintenance resigned unexpectedly. RRWP was unable to procure a contractor to complete the inspection by March 31st. The battery inspection was completed on April 5, 2016. The root cause of this issue was a combination of the unexpected resignation of the RRWP employee responsible for implementing the scheduled battery maintenance, and the lack of a backup plan/procedure to prevent this type of issue from occurring. The issue began on April 1, 2016, when the six calendar month interval was missed and ended April 5, 2016, when the battery tests were completed. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RRWP missed the six calendar month maximum interval for battery maintenance by 5 days. No harm is known to have occurred. SPP RE considered RRWP’s compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. The instant issue is appropriate for Compliance Exception. | To mitigate this minimal risk instance of noncompliance, RRWP: 1) programmed their maintenance tool to populate a work order and notifications four weeks before the battery maintenance due date; 2) outsourced the six-month battery tests to an electrical company. The new contractor has been scheduled for the next six-month battery test and will do this test moving forward; 3) tasked the site supervisor with overseeing the work orders and ensuring the test activity is planned and executed before the deadline; and 4). tasked the site supervisor with sharing the testing results with the electrical Subject Matter Experts for review and uploading into document management system. SPP RE has verified the completion of all mitigation activity.
2016-09-29 | Texas Reliability Entity (Texas RE) | Keechi Wind, LLC (KWLLC) | NCR11497 | TRE2016015820 | VAR-002-4 | R4 | On June 10, 2016, KWLLC submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-4 R4. Specifically, KWLLC failed to notify its Transmission Operator (TOP) within 30 minutes of becoming aware of a change in its reactive capability. After an increasing number of instances of automatic capacitor switching at a single wind facility, KWLLC determined on January 1, 2016, that its wind turbine control system was not following commands issued by its reactive control system (DVAR) due to a communications loss. As a result of this inability to communicate with the DVAR, the wind turbine control system was unable to properly control reactive output at the wind turbines. However, upon becoming aware that it did not have full reactive control capabilities in this manner, KWLLC did not notify its TOP of the issue within the required 30-minute window. Texas RE determined that the root cause of the noncompliance was that KWLLC personnel were not aware that the loss of communication between the wind turbine control system and the DVAR resulted in a change in reactive capability requiring notification to the TOP. Texas RE determined the issue duration was approximately 3 hours on January 1, 2016, from when KWLLC failed to notify its TOP within 30 minutes of it becoming aware of the change in reactive capabilities until KWLLC restored reactive capabilities by reestablishing communications between the DVAR and wind turbine control system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although KWLLC did experience a degradation in its reactive control capabilities, the DVAR was still able to operate its integrated reactive elements and the station capacitors to partially control reactive output. Second, KWLLC was able to maintain its voltage profile, minimizing the possible impact of the reactive capability issue on the system. Third, KWLLC only produced an average of approximately 18 MW, with a maximum output of approximately 25 MW, during the period that KWLLC experienced its reactive capability issues. As a result, the single wind generation facility in question would have had only a negligible impact on the system’s ability to respond to reactive power demands. Lastly, the duration of KWLLC’s reactive capability issues was short, lasting only three hours. No harm is known to have occurred. Texas RE considered KWLLC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, KWLLC: 1) reset communication between the wind turbine control system and the DVAR, resolving the issue with KWLLC’s reactive control capabilities; 2) elevated the alarm logic associated with a communications loss between the DVAR and the wind turbine control system to the level requiring immediate action by operators to investigate and address the issue; 3) updated its Voltage Control Procedure to include instructions for its operators to notify the TOP within 30 minutes of any abnormal conditions identified by alarm signals; and 4) provided training to its operating personnel that emphasized the 30-minute notification requirement to the TOP after becoming aware of a change in reactive capability. Texas RE has verified the completion of all mitigation activity.
2016-09-29 | Texas Reliability Entity (Texas RE) | South Texas Electric Cooperative, Inc. (STEC) | NCR04124 | TRE2016015749 | EOP-008-1 | R1, R1.3, R1.6.2 | During a Compliance Audit conducted from April 11, 2016 through May 12, 2016, Texas RE determined that STEC, as a Transmission Operator (TOP), had an issue of with EOP-008-1 R1. In particular, Texas RE determined that STEC failed to possess a current Operating Plan describing the manner in which it continues to meet its functional obligations with regard to the reliable operation of the Bulk Electric System (BES) in the event that its primary control center (PCC) functionality is lost. Based on a review of STEC’s Operating Plan for Backup Functionality (Functionality OP), Texas RE determined that STEC’s Functionality OP lacked required information in two areas. First, STEC’s Functionality OP did not include the necessary steps that must be performed at STEC’s backup control center (BCC) in order to maintain consistent functionality with its PCC as required under EOP-008-1 R1.3. Second, STEC’s Functionality OP did not specifically indicate the actions necessary to manage the risk to the BES during the transition from primary to backup functionality as required under EOP-008-1 R1.6.2. The root cause of this issue was a lack of sufficient internal controls to ensure that STEC’s operational planning documentation satisfied all applicable NERC Reliability Standards. Texas RE determined the issue duration to be from July 26, 2013, one day after STEC’s last TOP audit, until April 28, 2016, when STEC revised its Functionality OP to include all required elements under EOP-008-1 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is documentation-related and not performance-related. Although STEC did not adequately document two required elements in its Functionality OP, STEC presented evidence that it successfully conducted annual testing of the transfer of operations to its BCC throughout the duration of the issue in question. Further, STEC provided evidence that its operators had received training regarding the operational transfer process from the PCC to BCC on a number of occasions. Finally, STEC’s System Operators demonstrated that they understood their responsibilities during a failover from the PCC to the BCC in the audit interview process. No harm is known to have occurred. Texas RE considered STEC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, STEC: 1) revised its Functionality OP to include all elements required under EOP-008-1 R1; 2) updated its Internal Compliance Program to specifically assign responsibility to STEC’s Compliance Coordinator to review STEC operational documentation to ensure it meets all applicable NERC Reliability Standard requirements; and 3) implemented a new template header for all operational plan documentation that includes verbiage indicating the NERC Reliability Standards that apply to each individual document. Texas RE has verified the completion of all mitigation activity.
2016-09-29 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC2015015276 | FAC-501-WECC-1 | R1.1 | During a Compliance Audit conducted from September 14, 2015 to September 25, 2015, WECC determined that PGAE, as a Transmission Owner, had an issue of noncompliance with FAC-501-WECC-1 R1.1. PGAE’s Transmission Maintenance and Inspection Plan (TMIP) documentation did not indicate whether or when PGAE performed annual reviews of its TMIP. This issue began on October 5, 2012, the completion date of the last audit in which PGAE had no findings related to this requirement, and ended July 1, 2016, when PGAE incorporated a revised annual review process into its work management system. The root cause of this issue was a lack of documentation in regards to process or ownership of PGAE's TMIP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, PGAE failed to document its annual TMIP review. Such failure could result in inadvertent omission of updates. However, this issue was limited to documentation. It is unlikely that an undocumented update would have a significant impact on the effectiveness of PGAE’s TMIP. Upon further review, WECC auditors determined that annual reviews during the audit period would have resulted in only minor changes to the documentation. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. PGAE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PGAE: 1) created a summary document to track annual reviews of its TMIP documentation. This document provides a high-level overview of component documents that comprise PGAE’s TMIP; 2) added automated task reminders for annual reviews of both the TMIP documentation and the summary document in its work management system; and 3) completed a thorough review to ensure TMIP documentation is up to date.
2016-09-29 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC2015015277 | PRC-005-1 | R2 | During a Compliance Audit conducted from September 14, 2015 to September 25, 2015, WECC determined that PGAE, as a Transmission Owner, Distribution Provider, and Generator Owner, had an issue of noncompliance with PRC-005-1 R2. Specifically, WECC identified two battery chargers and two relays with maintenance and testing activity documented outside the intervals prescribed in PGAE’s Protection System Maintenance and Testing Program (PSMP). On June 1, 2016, PGAE identified and reported an additional battery that missed one testing interval. PGAE expanded its mitigating activities for this issue to include the battery. This issue began on the respective dates when testing became past due for each of the devices in scope, and ended when PGAE tested the devices. As concerns the two relay schemes, this issue began March 8, 2010, and ended March 30, 2010. As concerns the two battery chargers, this issue began May 1, 2012, and ended February 13, 2015. As concerns the additional battery, this issue began March 1, 2015, and ended June 24, 2016. The root cause of this issue was a combination of human and documentation error. The devices discovered during audit were inadvertantly omitted from PGAE's work management system, and the additional battery discovered by PGAE was classified as a low priority (and therefore had lower visibility) in PGAE's work management system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, PGAE failed to perform maintenance and testing in accordance with the intervals defined in its PSMP for five of its 6,447 devices. Such failure could limit PGAE’s awareness of the working order of its Protection System devices. However, the devices addressed within the scope of this issue comprised less than one percent of PGAE’s Protection System devices. Additionally, PGAE’s detective controls and other mitigating factors concerning each device decreased the likelihood that unexpected or premature failure of any of the devices would not have been immediately detected and addressed by PGAE. For example, PGAE monitored DC voltage for the devices in scope in its Supervisory Control and Data Acquisition (SCADA) system, and loss of DC power to any of the devices would have triggered an alarm. PGAE also performed regular inspections of the battery systems in scope, increasing the likelihood that PGAE would have detected and corrected any abnormalities. All devices have since been tested in accordance with PGAE’s PSMP. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS PGAE has one relevant prior instance of noncompliance with PRC-005-1 R2, NERC VID: WECC200901422. In that circumstance, PGAE self-reported that it failed to maintain and test roughly 7% of its applicable Protection System devices within the intervals defined in its PSMP. PGAE completed mitigating activities for the prior violation in 2009. Because of the age and circumstances of the previous violation, WECC determined that PGAE’s compliance history should not preclude designation of this issue as a compliance exception. | To mitigate this issue, PGAE: 1) tested all devices in scope; 2) added the devices discovered during audit to its work management system; and 3) conducted a thorough review to verify extent of condition for this issue, and to ensure future maintenance and testing is performed and documented in accordance with its PSMP.
2016-09-29 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC2015015278 | PRC-017-0 | R2 | During a Compliance Audit conducted from September 14, 2015 to September 25, 2015, WECC determined that PGAE, as a Transmission Owner, Generator Owner, and Distribution Provider, had an issue of noncompliance with PRC-017-0 R2. Specifically, one of PGAE's substation batteries, which was installed in 2012, was not added to PGAE’s work management system until early 2015. This issue began May 1, 2012, the date the first monthly inspection was past due, and ended February 13, 2015, when PGAE performed annual maintenance on the battery system following discovery of the discrepancy. The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, PGAE failed to perform maintenance and testing in accordance with its SPS Maintenance and Testing Program for one battery and its associated battery chargers. Such failure could result in undetected premature failure of DC supply for SPS components. However, DC voltage for the battery system was monitored and alarmed through PGAE’s SCADA system. Additionally, PGAE performed monthly inspections of the battery system and likely would have detected any abnormalities. Further, the battery was installed as new, and was not likely to have failed during the period in question. PGAE provided commissioning test information indicating battery health was excellent. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. PGAE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PGAE: 1) tested the battery and its associated chargers; 2) added the devices to its work management system to ensure future maintenance and testing is performed consistently and timely; and 3) conducted a thorough review to verify extent of condition for this issue.
2016-09-29 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2016015747 | VAR-002-4 | R3 | On May 12, 2016, PSE submitted a Self-Report stating that as a Generator Operator, it had a possible issue of noncompliance with VAR-002-4 R3. Specifically, PSE reported that on March 30, 2016, the Power System Stabilizer (PSS) of one of its generating units did not automatically engage during start up. The device’s corresponding audio and visual alarms activated as designed; however, the operator on shift did not respond to the visual alarm. As a result, staff at the generating station did not notify the PSE’s Load Office (the associated Transmission Operator, or TOP) of the PSS status until the issue was discovered later in the day. This issue began March 30, 2016; 31 minutes after a PSE operator failed to respond to the visual PSS alarm, and ended the same day, when PSE notified the TOP that the PSS was not in operation. This issue was caused by human error; the operator was distracted by other balance of plant alarm notifications and did not respond to the visual alarm. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, PSE failed to notify the TOP regarding the PSS status of one of its generating units within the timeframe prescribed by VAR-002-4 R3. Such failure limited the TOP’s situational awareness, and could have resulted in the inability of the generator to respond to voltage excursions as expected by the TOP. However, this issue was limited to a single 130 MW unit over the course of roughly eight hours. The unit’s Automatic Voltage Regulator (AVR) was in service throughout the duration of this issue. PSE identified the issue as a result of follow-up verification by one of the engineers after reviewing PSS status via PSE’s Energy Management System. Upon discovery, PSE immediately notified the TOP that the PSS was not in operation. PSE investigated and resolved the issue within hours of the discovery. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. PSE had one previous violation of this Standard and Requirement, given Violation ID: WECC201102620. The previous violation was not considered relevant because mitigating activities were completed more than three years prior to this issue. | To mitigate this issue, PSE: 1) contacted the TOP regarding PSS status; 2) troubleshot the device, which operated as designed upon rebooting; 3) assessed PSS alarms at all thermal plants and implemented updates to increase visibility and awareness regarding procedures concerning alarms; and 4) provided refresher training to relevant staff regarding PSS and AVR operational procedures and VAR-002-4 compliance. WECC verified completion of PSE’s mitigating activities.
2016-09-29 | Western Electricity Coordinating Council (WECC) | Tucson Electric Power (TEPC) | NCR05434 | WECC2016015505 | PRC-005-1b | R2 | On January 28, 2016, TEPC submitted a Self-Report stating that as a Generator Owner, Transmission Owner and Distribution Provider, it had a possible issue of noncompliance with PRC-005-1b R2. Specifically, TEPC reported that on August 10, 2015, while preparing for transition to a new database program, it identified a breaker failure relay that had been erroneously removed from its work management database. Consequently, the device was not tested in accordance with the interval prescribed by TEPC’s Protection System maintenance and testing program (PSMP). This issue began August 31, 2012, when testing for the device became past due, and ended August 12, 2015, when TEPC discovered the issue and tested the device. This issue was caused by human error - the relay was removed from the database without proper verification. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, TEPC failed to test one relay in accordance with the interval prescribed in its PSMP. Such failure could have limited TEPC’s awareness of the working order of the relay. However, this issue was limited to one device which operated as expected when TEPC discovered and tested it. The device also posed limited risk to reliability; had the relay in scope failed, other protection redundancies in the circuit would have compensated. Additionally, in 2014 TEPC implemented an internal control requiring director approval for removal of any equipment records from its database. TEPC performed a comparative analysis of its Bulk Electric System relays and did not discover any additional discrepancies. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. TEPC had two previous violations of this Standard and Requirement, given Violation IDs: WECC200801090 and WECC201102897. The previous WECC200801090 violation was not considered relevant because mitigating activities were completed more than three years prior to this issue. The facts and circumstances of WECC201102897 concerned several instances of overdue maintenance, which TEPC mitigated by designating individuals to coordinate maintenance scheduling and records. WECC2016015505 concerned a single device that was erroneously removed from TEPC’s work management database, which TEPC mitigated by 1) verifying that its other relays were accounted for in the database, and 2) revising its procedure regarding removal of equipment from its database. Because of the age and circumstances of the previous violations, WECC determined that TEPC’s compliance history should not preclude designation of this issue as a compliance exception. | To mitigate this issue, TEPC: 1) tested the relay; 2) added the relay to its current work management database; 3) performed a comparative analysis to verify all relays were accounted for in its database; and 4) revised procedures to ensure existing protocol regarding equipment records will be followed in the future. WECC verified completion of TEPC’s mitigating activities.
2016-08-31 | Northeast Power Coordinating Council (NPCC) | SBF New York, L.L.C. (SBF) | NCR11534 | NPCC2016015756 | PRC-018-1 | R1; R1.1 | On May 16, 2016, SBF submitted a self-report stating that as a GO, it had an issue of PRC-018-1 R1. SBF New York LLC owns the Syracuse and Beaver Falls generating plants. Each generating plant consists of one 73 MVA Combustion Turbine and one 41 MVA Steam Turbine. The Syracuse facility does not own a Sequence of Events (SOE) recorder. The Beaver Falls Generating Plant has SOE, however the SOE does not monitor the Protection group which consists of protective relays, lockout relays, and breaker trip coils. Both generating facilities that SBF owns have microprocessor relays capable of event recording, however, these devices are not connected to GPS clocks as required by PRC -018 R.1. The duration of the noncompliance is from February 15, 2015, when SBF became the new owner of the facilities that were out of compliance with the Standard and requirement, through July 1, 2016, when PRC-018 R1.1 was no longer applicable to SBF because it did not meet the criteria in PRC-002-2. The reason for the non-compliance was SBF transitioned ownership of the plant on February 15, 2015. The initial analysis of the plant did not include a review of PRC-002-NPCC, however in October of 2015 a second analysis of the program was initiated. The second analysis identified that PRC-002-NPCC had not been addressed by the previous owner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SBF is a small independent power provider. Both generating facilities that SBF owns have microprocessor relays capable of event recording. Without adequate disturbance data, a BES event analysis cannot be facilitated in accordance with NERC reliability standards. However, SBF and their TO determined that it does not qualify to meet the criteria in the currently enforceable version of PRC-002-2 and by extension PRC-018-1 R1.1. NPCC considered SBF's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, SBF: 1. Contacted their TO to verify they are not applicable to PRC-002-2. NPCC has verified the completion of the mitigation activity.
2016-08-31 | Northeast Power Coordinating Council (NPCC) | SBF New York, L.L.C. (SBF) | NCR11534 | NPCC2016015671 | PRC-002-NPCC-1 | R1 | On April 15, 2016, SBF submitted a Self-Report stating that as a GO, it had an issue of PRC-002-NPCC-1 R1. SBF New York LLC owns the Syracuse and Beaver Falls generating plants. Each generating plant consists of one 73 MVA Combustion Turbine and one 41 MVA Steam Turbine. The Syracuse facility does not own a Sequence of Events (SOE) recorder. The Beaver Falls Generating Plant has SOE, however the SOE does not monitor the Protection group which consists of protective relays, lockout relays, and breaker trip coils. Both generating facilities that SBF owns have microprocessor relays capable of event recording, however, these devices are not connected to GPS clocks. The duration of the noncompliance is from February 15, 2015 to July 1, 2016. The reason for the non-compliance was SBF transitioned ownership of the plant on February 15, 2015. The initial analysis of the plant did not include a review of PRC-002-NPCC, however in October of 2015 a second analysis of the program was initiated. The second analysis identified that PRC-002-NPCC had not been addressed by the previous owner. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SBF is a small independent power provider. Both generating facilities that SBF owns have microprocessor relays capable of event recording. Without adequate disturbance data, a BES event analysis cannot be facilitated in accordance with NERC reliability standards. However, SBF and their TO determined that it does not qualify to meet the criteria in the currently enforceable version of PRC-002-2. NPCC considered SBF's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, SBF: 1. Contacted their TO to verify they are not applicable to PRC-002-2. NPCC has verified the completion of the mitigation activity.
2016-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2016015731 | EOP-001-2.1b | R2.2 | During a Compliance Investigation conducted on December 4, 2015, ReliabilityFirst determined that PJM, as a Balancing Authority and Transmission Operator, had an issue of EOP-001-2.1b R2.2. Unusually hot weather occurred from September 9 to September 11, 2013 in the Midwest and Mid-Atlantic states (the Hot Weather Event), and led to emergency conditions in the PJM service area. In order to avoid more serious impacts, PJM directed its member Transmission Owners (TOs) to implement controlled outages in a few localized areas for limited time periods. The localized areas affected by the controlled outages were located in southern Michigan, northeastern Ohio, northwestern Pennsylvania, and northeastern Indiana. During this period, temperatures reached up to 20 degrees Fahrenheit above normal, and demand for electricity reached an all-time high for September in parts of PJM’s footprint. At the same time, some generation and transmission facilities were scheduled to be out of service for routine maintenance because lighter electricity demand is generally experienced during the month of September. PJM did not follow all the steps set forth in its emergency plan to notify governmental authorities of a load shed event. PJM maintains a robust emergency plan, which is set forth in PJM Manual 13, and requires PJM to, among other things, notify FERC and governmental authorities in the event of a “manual load dump” (a load shed event). Specifically, the PJM notification requirements set forth in PJM Manual 13, Section 5.2, Step 9 include: a. PJM dispatch notifies PJM management, PJM public information personnel, and members. PJM dispatch notifies other Control Areas through the RCIS, and notifies DOE, FEMA, and NERC offices, using established procedures. b. PJM dispatch notifies FERC via the FERC Division of Reliability’s electronic pager system, consistent with FERC Order No. 659. PJM did not notify governmental authorities of a load shed event during the Hot Weather Event in accordance with its emergency plan. At the time of the Hot Weather Event, PJM had assigned many of the governmental authority notification tasks set forth in its emergency plan to its member TOs, particularly for local events. During the Hot Weather Event, PJM dispatchers spoke with the relevant member TOs, who, in turn, should have communicated any necessary notifications to local parties and state governmental authorities. In addition, PJM should have recorded these load shed directives in its PJM Emergency Procedures application as a secondary control to ensure authorities are notified. However, PJM did not make these directives in the application. As a result, parties who utilized the Emergency Procedures application for notification were not notified of these load shed events by this form of communication. PJM performed an internal analysis following the Hot Weather Event to determine the root cause of PJM's failure to record the load shed directives in the PJM Emergency Procedures application. During its internal analysis, PJM learned that its dispatchers were unaware of the intended purpose for the “Local Load Relief Action” category in its Emergency Procedures application because: (a) the category had rarely, if ever, been used prior to September 9, 2013; and (b) the “Local Load Relief Action” category title did not match the term “Post Contingency Local Load Relief Action” that is used in PJM’s emergency plan (Manual 13, Section 5.4). Because the PJM dispatchers were unaware of the intended purpose for the “Local Load Relief Action” category in the PJM Emergency Procedures application, they logged the load shed events as generic transmission events rather than as load shed events in the PJM Emergency Procedures application. PJM also determined that various internal PJM departments were not notified of the load shed events in a timely manner. PJM’s emergency procedure steps were predominately focused on specific notifications pursuant to Department of Energy, Federal Energy Regulatory Commission, NERC, or PJM Manual requirements. At the time of the Hot Weather Event, during emergency operations, PJM’s dispatchers followed an informal notification process. PJM determined that its dispatchers had no formal notification checklist to follow to activate the internal communications plan, which resulted in less effective internal communications to PJM support departments during the Hot Weather Event. The root cause was PJM's infrequent use of the procedure and the lack of awareness of PJM's dispatchers on the particular notification step in the PJM Emergency Procedures application. This root cause is related to workforce management. This issue started on September 9, 2013, the date PJM failed to notify governmental authorities of a load shed event and ended on June 14, 2014, the date PJM completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. While PJM did not follow all of the detailed steps set forth in its emergency plan, PJM did in fact notify governmental authorities of the load shed event and had assigned many of the notification tasks to its member TOs, particularly for local events. Additionally, PJM had a very robust emergency plan and it is important to not discourage PJM and other Registered Entities from developing robust emergency plans and incent them to remove valuable detail and steps from their emergency plans in an effort to avoid noncompliance with EOP-001-2. This could result in relegating emergency plans developed under EOP-001-2 to simplistic documents developed to ease the ability to demonstrate compliance rather than serving as a means to strive for operational reliability excellence. No harm is known to have occurred. ReliabilityFirst considered PJM's EOP-001 R2.2 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PJM: 1) streamlined the implementation of PJM Manual 13 by requiring PJM to notify the governmental authorities regardless of whether the member TOs have notified the governmental authorities. The member TOs are still obligated to notify the governmental authorities of a load shed event. However, PJM no longer relies upon or assumes the member TOs will do so; 2) established an Operational Event Response Team to provide guidance to PJM Shift Supervisors for when and how to notify PJM Dispatch Leadership of Operational Events. The Operational Event Response Team is a cross-divisional group designed to help prepare for, respond to, and communicate Operational Events to PJM members, stakeholders, government agencies, and neighbors; and 3) reviewed how the Emergency Procedures application is used in local load shed events and addressed process language for logging local load shed events; training to reinforce the process for logging local load shed events and the Emergency Procedures application; and ensured contact lists are updated and stakeholders are enrolled properly in the Emergency Procedures application. ReliabilityFirst has verified the completion of all mitigation activity.
2016-08-31 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2015015365 | VAR-002-4 | R2 | On November 19, 2015, Duke submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-4 R2. Duke did not maintain voltage within the assigned voltage schedule. On September 7, 2015, the Transmission Operator (TOP), Duke Energy Carolinas, issued the 2015 fall voltage schedule and requested implementation on September 21, 2015. Duke’s nuclear department acknowledged receipt on September 7, 2015. However, on September 21, 2015, operators at Catawba Nuclear Station (CNS) failed to implement the fall voltage schedule as requested by the TOP. Duke determined the root cause was human error and training. The individual responsible for ensuring CNS Operations voltage schedule implementation was on vacation, and the staff on duty failed to implement the schedule as requested. As a result, CNS did not implement the fall voltage schedule from September 21, 2015, until discovered on September 29, 2015, when the vacationing staff member returned. The issue lasted from September 21, 2015, when the TOP requested the implementation of the fall voltage schedule, through September 29, 2015, when Duke implemented the fall voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Duke’s failure to maintain the correct voltage could result in inadequate reactive supply and result in disturbances on the bulk power system. However, the fall target voltage schedule differed from the summer target voltage by a relatively small amount. For example, the weekend target voltage in fall was 21.1 kV versus 21.3 kV for the summer. During the duration of the issue, Catawba remained under operation of the summer voltage schedule and the unit output voltage was within 2% of the fall voltage schedule targets. Duke operates the Transmission Control Center (TCC) 24 hours a day, seven days a week, and monitors voltage at key points in the grid. The TCC is responsible for contacting the Nuclear Operations Control Rooms and request changes to operating voltage if necessary to optimize grid operations. However, the TCC did not request any modifications during the duration of the issue. No harm is known to have occurred. SERC considered Duke’s VAR-002 R2 compliance history in determining the disposition track. Duke’s relevant prior noncompliance with VAR-002 R2 includes: SERC2013012516. In the prior instance, Duke operated hydro generators at a specific location in a manner not ordered by the Transmission Operator (TOP). Duke completed its mitigation on October 7, 2013 by changing the mode of operation and removing the local operator’s ability to modify the set-point. The previous mitigation would not have addressed this instant issue, and the nature of the issues is different. Therefore, SERC determined that Duke's compliance history should not serve as a basis for applying a penalty. SERC considered the violation history of Duke Energy Florida, Duke Energy Corporation, Duke Energy Progress, and Duke Energy Generation Services and determined there were no additional relevant instances of noncompliance. | To mitigate this issue, Duke: 1) implemented the 2015 fall voltage schedule; 2) coached individuals involved on the responsibilities to update the voltage schedules quarterly; 3) created a repetitive task to assure the periodic update of the voltage schedule is performed quarterly; 4) implemented a process for the Duke Energy Carolinas TOP to have each nuclear site reply with acknowledgment once the new voltage schedules are updated and implemented; and, 5) communicated the cause and mitigation to all generation departments in all affiliates. To mitigate this issue, Duke will complete the following mitigation activities by July 1, 2017: 1) develop and implement a new voltage schedule acknowledge receipt process with all Duke business units and affiliates.
2016-08-31 | SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2015015203 | PRC-023-1 | R1 | On June 16, 2015, SERC sent Entergy an audit detail letter notifying it of a Compliance Audit scheduled for September 14, 2015 through October 2, 2015. On August 28, 2015, Entergy submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R1. Entergy identified a transmission relay trip setting that did not meet the assigned criterion. SERC later determined that this issue dated back to Version 1 of the Standard. Entergy utilized PRC-023-2 Criterion 1 (Version 1, R1.1) for the facilities involved. Criterion 1 required that Entergy set the relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit for the available defined loading duration nearest four hours. On February 23, 2015, Entergy re-energized the 230 kV Stuttgart Ricuskey facility with incorrect relay settings. The incorrect relay settings allowed the relay to operate at as little as 114% of the Facility Rating. The error affected the relay settings and did not affect the determination of the actual Facility Rating. Entergy discovered this issue on March 9, 2015, while updating its Facility Rating workbook for the facility, to accommodate a new Protection System panel. On September 4, 2015, Entergy submitted expansions of scope of two additional issues with PRC-023-2 R1. SERC later determined that this issue dated back to Version 1 of the Standard. On August 23, 2006, Entergy installed a new electronic relay on the Freeport – Horn Lake replacing a Zone 1 electromechanical relay, but a second electromechanical relay for Zone 3 remained installed. Entergy modified the electromechanical settings sheet to indicate the Zone 3 electromechanical relay was a “carrier start” relay. PRC-023 R1 is not applicable to carrier start relays because carrier start relays do not provide a trip function. Therefore, Entergy did not review the Zone 3 set points while verifying compliance upon installation. On June 29, 2015, while transitioning relay settings for the Freeport – Horn Lake 230 kV line from a relay settings spreadsheet to a database and performing a survey of switch-on-to-fault (SOTF) settings, Entergy discovered the electromechanical relay could cause a Zone 3 trip and was not “carrier start” only. Therefore, PRC-023 R1 did apply to this relay. Entergy verified the relay settings and determined that, under certain limited circuit conditions, the relay would operate at a loading of 79.8% (636 MVA) of the Facility Rating (797 MVA) rather than operating above 150% of the Facility Rating. Entergy down rated the Facility to ensure loadability was not limited until the Zone 3 trip was disabled. Later the same day, Entergy corrected the relay settings and restored the Facility Rating to 2000 Amps. On March 12, 2013, Entergy modified the relay SOTF settings for the Horn-Lake Getwell 230 kV facility for an unknown reason, resulting in settings that may operate at a loading of 125.8% (653 MVA) of the Facility Rating (519 MVA). On July 16, 2015, while updating settings documentation, as part of an ongoing system-wide project to include SOTF settings in all PRC-023 evaluations, Entergy discovered that the relay settings for the Horn Lake - Getwell 230 kV facility might limit loadability. Entergy confirmed the settings used prior to March 12, 2013 were adequate for compliance with PRC-023. On April 2, 2015, Entergy installed the correct settings and re-rated the Facility Rating to 300 MVA. Entergy performed a root cause evaluation (RCE) and determined human error caused the issue. Entergy staff used a calculation sheet that was not appropriate for the relay scheme and caused the insertion of a setting that the relay used as its SOTF setting. Entergy also found that a contributing cause for this issue was incomplete design/documentation in that the workbooks for line panels did not consider SOTF when evaluating settings for PRC-023 compliance. The issue lasted from July 1, 2010, the date the standard became mandatory and enforceable on Entergy, through April 2, 2015, when Entergy finished restoring the correct set points. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Entergy’s failure to properly set relay set points could result in premature tripping of circuit breakers or in the case of SOTF settings, the inability to close a breaker. The operational planning process includes long- and short-term studies, seasonal coordination, next-day analyses, current-day load flow, and state estimator analyses. Study results provide input to reliability operating plans. Coordination of outages and system conditions occurs multiple times for all timeframes leading up to and during current-day operations according to the various outage coordination and next-day processes. During this planning and coordination, Entergy conducts N-1 contingency studies to ensure reliable operation for expected conditions and for reasonable contingency scenarios while honoring all System Operating Limits. Entergy develops mitigation plans during the next-day analysis process as necessary. During these issues, Entergy did not identify a need for mitigation from the study results for the event of the loss of, or inability to energize, any of the affected facilities. In the case of the incorrect SOTF settings, SOTF relays do not affect normal breaker operation because SOTF protection is designed to operate only during a breaker reclosure following a fault or disturbance. No relay operations or mis-operations occurred as a result of these issues. No harm is known to have occurred. SERC considered Entergy’s PRC-023-1 R1 compliance history in determining the disposition track. Entergy’s relevant prior noncompliance with PRC-023-1 R1 includes: NERC Violation ID SERC2012010984. SERC determined that Entergy’s compliance history should not serve as a basis for applying a penalty. In SERC 2012010984, Entergy experienced incorrect relay set points caused by incorrect Facility Ratings and rounding errors in the calculations. Entergy completed mitigation for the prior violation by March 22, 2013 by correcting the Facility ratings and roundup errors for specific relays. Those mitigating activities would not have prevented the instant issues from occurring. | To mitigate this issue, Entergy: 1) immediately down rated each of the affected lines; 2) developed correct settings that would not limit loadability; 3) installed the correct settings on the applicable relays; and 4) provided lessons learned to the relay setting engineers, including discussion concerning human errors in the calculation process.
2016-08-31 | SERC Reliability Corporation (SERC) | NAES Corporation - Birchwood (NAES-Birch) | NCR11583 | SERC2016015813 | VAR-002-4 | R3 | On June 6, 2016, NAES-Birch submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R3. NAES-Birch did not notify its associated Transmission Operator (TOP) of a status change on the power system stabilizer (PSS) within 30 minutes of the change. In addition, on June 6, 2016, NAES-Birch submitted an additional Self-Report of VAR-002-4 R3. NAES-Birch failed to notify its associated TOP of a status change on the power system stabilizer within 30 minutes of the change. On May 25, 2016 at 10:28 a.m., NAES-Birch conducted a routine plant startup and synchronized the generator to the grid. At that time, the PSS was not in service and the control room operator did not notice that the PSS was not in service. At 1:12 p.m., the instrument and controls supervisor noticed that the PSS was not in service and informed the control room operator. Upon notification, the control room operator immediately placed the PSS in service at 1:12 p.m. The plant operator contacted NAES-Birch’s NERC subject matter expert (SME) to ensure that the operator’s understanding of the notification requirements were accurate. The SME informed the plant operator to notify the Transmission Owner (TO), who is required to notify the TOP, that NAES-Birch placed the PSS in service. At 2:04 p.m., NAES-Birch notified the TO that the PSS was in-service, and at 2:08 p.m., the TO notified the TOP. Therefore, NAES-Birch did not notify the TOP of a change in status of the PSS within 30 minutes. During the cause investigation of the PSS not being in service, NAES-Birch discovered that the PSS had been out of service since the completion of a planned outage on May 13, 2016. During the outage, NAES-Birch de-energized the excitation system for maintenance, which disabled the PSS. When NAES-Birch re-energized the excitation system, the PSS remained disabled. The TOP requires generators with PSS equipped generation resources to communicate PSS status to the appropriate TO as well as to the TOP via the outage reporting system. NAES-Birch reports the status of the PSS daily to the TOP. In addition, NAES-Birch is required to call the TOP to report any updates to the reported information. SERC reviewed NAES-Birch’s daily TOP status reports submitted from May 13, 2016 through May 25, 2016 and discovered that it erroneously reported that the PSS was in-service. NAES-Birch stated that the shift supervisor is responsible for generating the daily report and the shift supervisor was not aware that the PSS was not in-service thus incorrectly reported the status on the daily status report. This issue lasted from May 13, 2016, when the NAES-Birchwood failed to notify the TOP of the correct PSS status within 30 minutes of the status change, through May 25, 2016, when the TO notified the TOP of the correct PSS status. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to notify the TOP of the change of state of reactive devices may lead to inappropriate voltage-controlling action by the TOP. However, NAES-Birch maintained output voltage according to the assigned voltage schedule throughout the period. In addition, the automatic voltage regulator was in service and in automatic controlling voltage during the period. The NAES-Birchwood unit is only 247 MWs, which represented approximately 0.4% of TOP load during the duration of the issue. No harm is known to have occurred. SERC considered NAES-Birch’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, NAES-Birch: 1) conducted training with the operators and management staff on the requirement to report a change of status of the PSS and AVR within 30 minutes of the change; 2) required the control room operators to make an entry in the operator’s logbook that they have verified the PSS is in service when the generator is synchronized to the grid; 3) conducted training with the control room operators on the importance of verifying the PSS is in service when the generator is synchronized to the grid; 4) added a step to the plant startup checklist for the operator to indicate that the PSS has been verified to be in service; 5) added an alarm to indicate when the PSS not enabled; and 6) required the operators make a screen copy of a trend showing the PSS is not in alarm, indicating that it is enabled and include with the file copy of the daily status report to the TO.
2016-08-31 | SERC Reliability Corporation (SERC) | Prairie State Generating Company (PrairieSt) | NCR11175 | SERC2015015385 | PRC-005-1b | R2; R2.1 | On November 30, 2015, PrairieSt submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. PrairieSt failed to implement its Protection System program within the defined intervals for Unit 1 station batteries. SERC later determined that the issue extended back to PRC-005-1b R2. During the week of November 9, 2015, PrairieSt performed an internal audit on PRC-005 and discovered that it failed to conduct the required annual inspection of Unit 1 station batteries in 2014 and the third quarter inspection in 2015. While SERC was performing its assessment and determining the scope of the issue, PrairieSt reported the following instance. On January 8, 2016, PrairieSt reported that it failed to document the electrolyte levels and cell condition for each cell in the battery string for the two batteries at Unit 1 and the two batteries at Unit 2. PrairieSt discovered the issue while completing the SERC request for information (RFI) for the instant issue. PrairieSt determined that the issue occurred during two months for Unit 1 and five months for Unit 2 between August 2012 and August 2015. SERC reviewed the completed RFI and determined that PrairieSt did not implement its Protection System program for its station batteries within the defined intervals for four of four station batteries (100%). In total, SERC determined that PrairieSt could not provide PRC-005-1b compliance evidence for four of 198 (2%) Protection System devices. PrairieSt determined that the instant issue root cause was training. Some PrairieSt technicians did not understand the Protection System program requirements for station batteries. This issue lasted from August 1, 2012, when PrairieSt missed the first required interval through November 19, 2015 when PrairieSt completed the annual inspection. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PrairieSt’s failure to perform the maintenance and testing of the Protection System station batteries within the defined intervals could lead to the Protection System devices not operating as intended, potentially leading to false trips, remote clearing, delayed clearing, the overreach of protective relays or reliance on the interconnecting Transmission Owner’s Protection System devices to respond to a fault. However, each unit has redundant battery systems and batteries are alarmed and monitored. PrairieSt identified no issues with any components in the battery system when tested. No harm is known to have occurred. SERC considered PrairieSt’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, PrairieSt: 1) completed annual battery inspections which included associated activities for the monthly, quarterly and annual tests. PrairieSt identified no issues during the testing to indicate deficiencies; 2) trained the technicians on the PM activities associated with PRC-005 Version 1.1b and version 2; 3) engineering discussed with electrical maintenance the requirement to inspect and record each cell condition; 4) implemented the revised process flow charts for completing, validating and closing out the Compliance Work Orders/PMs and created three separate PMs: monthly, quarterly and annually. These PMs differentiate between the maintenance activities that need to be performed; 5) implemented a compliance tracking tool through Microsoft Outlook Calendar where notifications are sent to the respective individuals 30 days prior to due dates; and 6) procured and implemented a third party compliance tracking tool.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Board of Public Utilities, Kansas City, Kansas (BPU) | NCR01061 | SPP2016015587 | PER-005-1 | R3 | On March 2, 2016, BPU submitted a Self-Report stating that, as a Transmission Operator, it had a minimal risk instance of noncompliance with PER-005-1 R3 because in 2014, one of its nine NERC Certified System Operators did not complete the 32 hours of emergency operations training required by PER-005-1 R3. This instance of noncompliance started on January 1, 2015, the day after the 2014 emergency operations training was required to have been completed, and ended on February 4, 2015, the date the operator completed the training. The root cause of this instance of noncompliance was a lack of internal controls to ensure adherence to BPU’s System Operators training program. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of PER-005-1 R3 has the potential to affect the reliable operation of the BPS by increasing the likelihood that operations personnel will respond inappropriately or with unnecessary delay to system emergencies. Nevertheless, only one of BPU’s nine system operators did not complete the required training. The operator completed 23 of the 32 required hours of emergency operations training in 2014. Additionally, the operator has worked for BPU since April 13, 2009, and has previously completed the annual operator training requirement every year. No harm is known to have occurred as a result of this instance of noncompliance. BPU does not have any relevant prior violation history associated with PER-005-1 R3. | To mitigate this minimal risk instance of noncompliance, BPU now requires the Supervisor of EMS Operations to monitor and track System Operator training. SPPRE has verified the completion of all mitigation activity.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Board of Public Utilities, Kansas City, Kansas (BPU) | NCR01061 | SPP2016015588 | EOP-008-1 | R7; R7.2 | On March 2, 2016, BPU submitted a Self-Report stating that, as a Transmission Operator, it had a minimal risk instance of noncompliance with EOP-008-1 R7.2. On December 22, 2014, BPU conducted a Back-up Control Center (BUCC) functionality test for one hour and 31 minutes, falling 29 minutes short of the 2 hours required by EOP-008-1 R7.2. This instance of noncompliance started December 22, 2014, the day that the 2014 Operating Plan BUCC functionality test was conducted and ended December 22, 2015, the day that the 2015 Operating Plan BUCC functionality test was conducted, meeting the EOP-008-1 R7.2, two hour requirement. The root cause of this instance of noncompliance was BPU’s failure to properly train and supervise the four operators conducting the test. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to adequately test the BUCC increases the risk that the BUCC would be unavailable or not function properly following loss of the primary control center. However, in this instance, BPU tested the BUCC for an hour and 31 minutes, ensuring the BUCC could perform the critical reliability functions of the primary control center. No harm is known to have occurred. BPU does not have any relevant prior violation history associated with EOP-008-1. | To mitigate this minimal risk instance of noncompliance, BPU: 1) conducted a meeting with the NERC Compliance Officer, the Operations & Planning Compliance Engineer, the Supervisor of EMS Operations and the Acting Director of Electric Supply to discuss: the requirements for BUCC testing; the minimum continuous time required for BUCC testing; and coordination of event time logging; and 2) added the EOP-008-1 R7.2 requirement to the 2015 operator training curriculum. SPPRE has verified the completion of all mitigation activity.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | ITC Great Plains, LLC (ITCGP) | NCR10400 | SPP2014014213 | FAC-009-1 | R1 | On August 11, 2014, ITCGP submitted a Self-Report stating that, as a Transmission Owner, it had an issue of noncompliance with FAC-009-1 R1 because the equipment ratings it had established for two classes of transmission bus jumpers were inconsistent with its current Facility Rating Methodology (FRM). ITCGP utilizes an equipment database to document the ratings of equipment composing its transmission facilities. When the database was originally constructed, the summer rating for the identified transmission bus jumpers was utilized as the winter rating. ITCGP revised its FRM on October 27, 2010, to include individual summer and winter equipment ratings for these transmission bus jumpers. Following the revision of its FRM, ITCGP failed to revise its equipment database to include separate summer and winter ratings for the identified transmission bus jumpers. The addition of separate summer and winter ratings for the two classes of transmission bus jumpers resulted in changes to the equipment ratings associated with 17 ITCGP transmission circuits. Because the transmission bus jumpers were not the most limiting element in the 17 transmission circuits, the facility ratings for the affected transmission facilities did not change. The duration of this issue of noncompliance was from October 27, 2010, the date ITCGP revised its FRM to account for different summer and winter ratings but did not update its equipment database, through January 1, 2015, the date ITCGP mitigated this issue. The root cause of the noncompliance was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to establish accurate facility ratings creates the potential for inaccurate system models, incorrect SCADA alarm limits and the operation of system facilities above safe operating limits. Although the transmission bus jumper ratings in ITCGP’s equipment data base were not consistent with its FRM, the transmission bus jumpers were not the most limiting element of the 17 transmission facilities affected and did not result in a change to their facility ratings. Moreover, the use of summer ratings for the winter ratings, as was established in the prior version of ITCGP’s FRM, is a more conservative method of establishing equipment ratings and would have yielded a lower facility rating had the transmission bus jumpers been the most limiting element of the transmission facilities. No harm is known to have occurred due to this noncompliance. ITCGP has no relevant, related issues of noncompliance. | To mitigate this minimal risk instance of noncompliance, ITCGP updated the ratings of the bus jumpers in the database and published new rating sheets for all seventeen circuits in ITCGP. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Midwest Energy, Inc. (MIDW) | NCR01118 | SPP2015014890 | PRC-023-1 | R1; R1.1 | During a Compliance Audit conducted from April 13, 2015, through April 16, 2015, SPP RE determined that Midwest Energy, Inc. (MIDW), as a Distribution Provider and Transmission Owner, had a minimal risk instance of noncompliance with PRC-023-1 R1.1. The SPP RE Auditors reviewed the relay calculations and settings for seven MIDW transmission circuits. The Audit team found two 230 kV transmission circuits (South Hays to Post Rock and Rice County to Circle) where the transmission circuit protective relays were set to operate below 150% of the highest seasonal Facility Rating. Specifically, the South Hays to Post Rock transmission circuit overcurrent (OC) relay was set at 127% of the Facility Rating of the circuit and the Rice County to Circle transmission circuit OC relay was set at 72% of the Facility Rating of the circuit. The duration of this issue of noncompliance was from April 26, 2012, the end date of the previous SPP RE Compliance Audit, through May 15, 2015, the date MIDW mitigated this issue. The root cause of this issue was human error; the relays settings were not properly set and reviewed in accordance with MIDW procedures. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Setting protective relays below 150% of the Facility Rating creates the potential for misoperations and for operators to react improperly to changes on the transmission system. However, MIDW corrected the settings shortly after they were identified by the audit team and there were no unnecessary trips of the protected Facilities during the period of noncompliance. No actual harm is known to have occurred. MIDW has no relevant, related issues of noncompliance. | To mitigate this minimal risk instance of noncompliance, MIDW: 1) contacted Schweitzer Engineering Laboratories, the contractor that designed the relay system, to review the existing settings and issue revised relay loadability calculation reports and revised relay settings; 2) scheduled a relay testing contractor to install the new settings in the relays; and 3) completed testing on relays to ensure proper functionality. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | Texas Reliability Entity (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | TRE2016015567 | EOP-005-2 | R4 | During an audit Texas RE conducted of Oncor from February 1, 2016 until February 25, 2016, Texas RE discovered an issue with EOP-005-2 R4. In particular, Texas RE determined that Oncor, as a Transmission Operator (TOP), did not update its restoration plan prior to implementing a planned BES modification that changed the implementation of its restoration plan. On October 26, 2015, Oncor initiated a planned modification to a substation bus. Specifically, Oncor changed the relevant breaker configuration at the substation in question from a single breaker to two breakers in series. Oncor completed this planned modification on December 11, 2015. During its audit preparations, however, Oncor subsequently determined that this planned substation modification likewise changed the implementation of its restoration plan. As such, Oncor updated its restoration plan to reflect the completed breaker configuration changes and then submitted the revised plan to its Reliability Coordinator (RC) on January 15, 2016. The root cause of this issue was insufficient internal processes to identify equipment associated with Oncor’s restoration plan. In particular, Oncor lacked specific mechanisms to track equipment in the current restoration plan to alert Oncor personnel of the need to evaluate whether a planned modification to Oncor’s system required corresponding changes to Oncor’s restoration plan. Texas RE determined the issue duration to be from December 10, 2015, one day prior to the date Oncor implemented its modifications to applicable BES equipment, until January 15, 2016, when Oncor updated its restoration plan and submitted it to its RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on several factors. First, the substation in question is neither in the cranking path nor the primary synchronization corridor. Second, Oncor properly incorporated the breaker configuration changes into its Transmission Management System so that Oncor personnel would have recognized the configuration change and could have taken appropriate action to implement the restoration plan. Lastly, Oncor’s RC has since reviewed and approved Oncor’s updated restoration plan. No harm is known to have occurred. Texas RE considered Oncor’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Oncor: 1) updated its restoration plan to include the new breaker configuration; 2) provided the updated restoration plan to its RC; 3) modified its Transmission Outage Application (TOA) to explicitly identify all equipment included in the current restoration plan in order to alert Oncor Transmission Grid Operations (TGO) personnel to evaluate if the work request includes modifications that would change the implementation of the Oncor restoration plan; 4) established a requirement to notify Oncor’s TGO personnel prior to any planned modification to equipment identified as associated with Oncor’s restoration plan; and 5) modified its TOA to flag any BES element included in the Oncor restoration plan that is submitted in a work request in order to provide an additional prompt for TGO personnel to compare the restoration plan equipment list with equipment included within a specific work request. Texas RE has verified the completion of all mitigation activity.
2016-08-31 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | WECC2015015122 | PRC-005-2 | R1 | As a Transmission Owner, Generator Owner, and Distribution Provider, BHP is required to comply with PRC-005-2 R1. WECC conducted a Compliance Audit of BHP from July 13, 2015 to July 24, 2015. WECC determined that BHP had an issue of noncompliance with PRC-005-1b R2. During the audit, WECC found that BHP failed to include in its PSMP the maintenance methods used to address each protection system component type, and the applicable monitoring component attributes applied to each protection system component type used to extend the maintenance intervals beyond those specified for unmonitored protection system components. The cause of this issue of noncompliance is a less-than-adequate compliance process to ensure BHP's PSMP was drafted to be compliant with Version 2 of the Standard. This issue began April 1, 2015 when the Standard and Requirement became effective, and ended on May 16, 2016, when BHP revised its PSMP to specify that it is currently a “time-based” only plan, following the time intervals described in PRC-005-2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, although BHP updated its PSMP in anticipation of the requirements of Version 2 of the Standard, BHP failed to specify the chosen maintenance method for each protection system component type and the monitoring attributes used to extend the maintenance interval past those specified for unmonitored protection system components in its PSMP. In this case, BHP included in its PSMP the entire table that accompanies the Standard. Such failure could potentially result in inconsistent testing and/or documentation thereof, which could affect the working order of BHP’s Protection Systems. No harm is known to have occurred. However, given the recent enforcement date for this requirement (April 1, 2015), at the time of the audit BHP had not had significant time to perform maintenance under the new program, and was using its legacy program while it transitioned to PRC-005-2. The WECC audit team noted that BHP did not specify whether it would use a time-based or a performance-based method in its maintenance and testing; but in the audit data request and interview process, BHP stated that its maintenance method is time-based. Further, the audit team stated that most, if not all, entities in the Western Interconnection are using a time-based maintenance method this early in the implementation of the Standard. WECC considered BHP’s compliance history related to PRC-005-1b R1 (Version 1) when determining the disposition track. BHP’s relevant prior noncompliance with PRC-005-1b R1 includes NERC Violation ID WECC2014013716. The facts and circumstances of BHP’s earlier issue of noncompliance were related to BHP’s failure to include maintenance and testing intervals for its continuously monitored devices in its Protection System Maintenance and Testing Program for Version 1 of the Standard. The instant issue of noncompliance is related to BHP’s Version 2 PSMP and the lack of details regarding the methods for maintenance and testing. | To mitigate this issue of noncompliance, BHP revised its PSMP document (ATT-03 ENG-32-001 Rev 16.0) to state that it is a “time-based” only plan and strictly follows the time intervals in the Standard.
2016-08-31 | Western Electricity Coordinating Council (WECC) | California Department of Water Resources (CDWR) | NCR05047 | WECC2016015549 | PRC-004-2.1(i)a | R3 | On February 12, 2016, CDWR submitted a Self-Report stating that as a Transmission Owner and Generator Owner, it had a possible issue of noncompliance with PRC-004-2.1(i)a R3. Specifically, CDWR reported that it did not report documentation for one misoperation within the appropriate timeframe. This issue began December 1, 2015, the day after the documentation should have been reported, and ended December 18, 2015, when CDWR discovered the issue and submitted the documentation to WECC. This issue was caused by lack of clarity regarding misoperation log dates in CDWR's procedure documents. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, CDWR failed to provide documentation of its misoperation analysis and Corrective Action Plan for one misoperation in accordance with WECC’s reporting criteria. Such failure could have limited WECC’s situational awareness of the misoperation, and delayed associated guidance from WECC regarding the misoperation. However, this issue largely concerned timely documentation. The misoperation in question occurred on the last day of the quarter, and was mistakenly logged for reporting in the following quarter. Although CDWR did not provide requisite documentation to WECC within the appropriate reporting period, it conducted its misoperation analysis and completed the Corrective Action Plan expeditiously. Upon discovery of the oversight, CDWR immediately submitted the documentation to WECC. Additionally, the misoperation in scope did not result in any loss of BES equipment, load or generation. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. CDWR does not have previous violations of this Standard and Requirement. | To mitigate this issue, CDWR: 1) reported documentation of its misoperations analysis and Corrective Action Plan to WECC; 2) revised its procedure documents to ensure future misoperations are logged on the day they occur, rather than the date of CDWR’s internal incident reports, and 3) provided supplemental training to staff regarding this revision. WECC verified completion of CDWR’s mitigating activities.
2016-08-31 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | WECC2016015518 | PRC-004-2.1(i)a | R3 | FEUS is registered on the NERC Compliance Registry as a Transmission Owner, Generator Owner and a Distribution Provider, and therefore FEUS is required to comply with PRC-004-2.1(i)a Requirement 3. On February 8, 2016, FEUS submitted a Self-Report stating that it had a possible issue of noncompliance with PRC-004-2.1(i)a Requirement 3. Specifically, FEUS reported that on August 24, 2015, it had two relays misoperate in an unnecessary trip during a fault. FEUS analyzed, corrected and reported the misoperations internally to FEUS’ compliance division on November 13, 2015. On November 18, 2015, FEUS submitted to WECC its Reliability Assessments and Performance Analysis (RAPA) Quarterly Misoperation Report for Third Quarter 2015, including an associated Corrective Action Plan. However, FEUS included only one of the relays in its RAPA report. On January 8, 2016, when FEUS reviewed its Corrective Action Plan for the relay misoperation, it discovered it had not included the second relay in its RAPA report. FEUS contacted WECC staff to open the report for the Third Quarter 2015, so the omitted relay could be included. On January 11, 2016, FEUS revised its Third Quarter 2015 misoperations report to include the second relay. The reporting criteria outlined in WECC Criterion (PRC-003-WECC-CRT-1.3 WR1) requires FEUS to report misoperation information within two months following the quarter in which it occurred. In this case, FEUS timely reported the misoperation of one relay, and reported the other related relay misoperation approximately 5 weeks late. The cause of this issue of noncompliance is FEUS’ less-than-adequate process for review and coordination of misoperation identification and reporting. This issue began on November 30, 2015, two months following the quarter in which the misoperation occurred, and ended on January 11, 2016, when FEUS submitted a revised Third Quarter 2015 misoperations report, to include the second relay. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, FEUS failed to timely report the misoperation and Corrective Action Plan for a distance relay located on a 115 kV line by approximately five weeks. FEUS did not have a documented process that can help prevent the above consequence from occurring. FEUS did not implement detective controls to detect the above consequence. FEUS implemented its quarterly update of the Corrective Action Plan for the relay that was properly reported and noticed they forgot to report the second relay misoperation during the same fault. No harm is known to have occurred. The purpose of the relays is to protect the 115kV lines in the event of a fault. Failure to report the Misoperations and Corrective Action Plan to WECC in a timely manner could potentially result in the lack of valuable WECC RAPA guidance to FEUS. However, all necessary operational actions were completed to timely detect and mitigate the misoperation. WECC notes that FEUS has identified and self-reported the issue described herein, does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. For these reasons, WECC considers FEUS’ compliance history as a factor in its designation of this remediated issue as a CE. | FEUS remediated this issue of noncompliance when it revised its Third Quarter 2015 misoperations report. In its Corrective Action Plans, FEUS proposed to change all groups in Lakeview ABB REL512 to have identical settings for the first relay; and, to use test data to locate all P442 relays that internally divide the time dial setting by 7, update ASPEN model, correct relay settings, and upload corrected settings to relays, for the second relay. WECC verified completion of FEUS’ mitigating activities.
2016-08-31 | Western Electricity Coordinating Council (WECC) | La Paloma Generating Company LLC (LPGC) | NCR05210 | WECC2016015629 | FAC-008-3 | R6 | On March 24, 2016, LPGC submitted a Self-Report stating that as a Generator Owner, it had a possible issue of noncompliance with FAC-008-3 R6. Specifically, LPGC reported that during an internal audit on March 16, 2016, LPGC discovered 28 components (4 generator disconnects, 6 switchyard breakers, and 18 switchyard CTs) were not included with its current Facility Ratings documentation. This issue began January 1, 2013, the date the Standard became mandatory and enforceable to LPGC, and ended March 16, 2016, when LPGC discovered the oversight and revised its Facility Ratings documentation. This issue was caused by human error; the components were included in LPGC's Facility Ratings, but were inadvertently omitted in its documentation. | In this instance, LPGC failed to include 28 applicable components in its Facility Ratings documentation. Such failure could have resulted in inaccurate calculation and determination of System Operating Limits. However, upon discovery of this issue and subsequent assessment of the components, LPGC determined that the generator still had the most limiting applicable Equipment Rating for the Facility. Additionally, although the components were not included with LPGC’s Facility Ratings documentation, the Equipment Ratings for the components were readily available to LPGC. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. LPGC does not have previous violations of this Standard and Requirement. | To mitigate this issue, LPGC added the missing components to its documentation and provided refresher training regarding acceptable compliance documentation for this Standard and Requirement to relevant personnel. WECC verified completion of LPGC’s mitigating activities.
2016-07-28 | Florida Reliability Coordinating Council (FRCC) | Gainesville Renewable Energy Center (GREC) | NCR11363 | FRCC2016015636 | FAC-008-3 | R2; R2.4.1 | During a Spot Check, conducted from February 22, 2016 through February 26, 2016, FRCC determined that Gainesville Renewable Energy Center (GREC), as a Generator Owner (GO), had an issue with FAC-008-3 R2. Specifically, GREC's facility rating methodology excluded relay protective devices and terminal equipment (aluminum bus bars installed between the generator step-up (GSU) transformer's high side bushing and the CT) in its facility rating methodology document. The reason for the omission of devices: GREC personnel considered relay protective devices a form of "sensing devices" that would not affect the overall facility ratings; therefore GREC did not believe it needed to be included in its methodology document. The aluminum bars however, had been inadvertently omitted from GREC’s Facility Ratings Table, but were visually spotted during a station inspection by FRCC auditors conducting the Spot Check. Although neither device type was accounted for in its Facility Ratings Methodology document, GREC engineers were aware of, and understood that these elements were not the most limiting factor. Also, all facility ratings were verified during commisioning and performance testing. The duration of the issue was from August 16, 2013, when GREC omitted the devices, through April 8, 2016, when GREC revised its Facility Rating and Methodology document to include Relay Protective Devices and Aluminum Bars. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GREC documents demonstrate that even though its relay protection devices and aluminum bus ratings were missing from the Facilities Ratings methodology document, the actual ratings themselves were considered by GREC's design engineers, and were therefore not limiting factors for the facility. Data provided by GREC includes evidence from performance testing, revealing that the plant has operated at full load (115 MW), with no ratings limitation issues, while relay protection devices and the aluminum bars were in-service. And though GREC's Facility Rating Methodology documentation did not contain ratings evidence of its protection relay's and aluminum bars; GREC's design engineers purposely ensured that they would not become a limiting factor in their facility rating; which was verified during commissioning performance testing. GREC's mitigating actions have included adding relay protection devices and its aluminum bars to the Facility Rating Methodology document. The most limiting element in the facility is the generator at 137 MVA, while GREC evidence reveals that the bus bar is rated for 3000A, and protection relay ratings (358MVA) are well above the generator ratings. GREC does not have any compliance history of issues with FAC-008-3 R2 No harm is known to have occurred. | To mitigate this issue, GREC: 1) performed a Root Cause Analysis (RCA) of the noncompliance. 2) revised GREC Facility Rating and Methodology document to include Relay Protective Devices and Aluminum Bars as part of our Facility Ratings Methodology. 3) to prevent reoccurrence, added an SME for FAC‐008 and performed a walk down from the generator to the interconnect as a team. 4) to prevent reoccurrence, is working with another North American Energy Services (NAES) facility and is sharing SME resources in order to review each other’s FAC‐008 Ratings and Methodology. 5) to prevent reoccurrence, contracted the services of an independent consultant – Proven Compliance Solutions (PCS) to review GREC FAC‐008 documentation and methodology, and also to review Internal Compliance Program and internal controls in place for FAC‐008.
2016-07-28 | Florida Reliability Coordinating Council (FRCC) | Hardee PowerPartners Limited (HPS) | NCR00035 | FRCC2016015742 | PRC-005-1a | R2; R2.1 | During a Compliance Spot Check conducted from March 1, 2016 through May 12, 2016, FRCC determined that HPS, as a Generator Owner (GO), had an issue of PRC-005-1a, R2. HPS documents, as submitted, were not sufficient evidence to demonstrate that HPS implemented its Protection System program. Specifically, HPS generator step-up (GSU) transformer neutral time/over-current relay (HPS 137) failed to actuate within testing parameters, and was never subsequently calibrated to within specifications. HPS’s “Policy Fleet Protection System Maintenance” states that HPS will “Test the functioning of relays with simulated inputs, including calibration.” Additionally, the procedure states that HPS will “Test and calibrate the relays (other than microprocessor relays) with simulated electrical inputs; verify proper functioning of the relay trip outputs; and verify that settings are as specified.” The issue (HPS 137) was originally discovered February 24, 2012, HPS 137 Over Current Relay testing resulted in a pick-up current test time of 12.75 seconds, which is outside the acceptable range of 9.69 seconds to 10.76 seconds. The issue was corroborated during a spot check, in which the 2012 HPS 137 test record was discovered. After questioning HPS personnel, it was inconclusive as to whether the HPS 137 relay was ever calibrated or replaced. FRCC auditors requested that the relay be re-tested (April 23, 2016), which resulted in HPS 137 outside the boundary, with a value of 11.23 seconds. The duration of the issue was from February 24, 2012, when the test time was outside the acceptable range, through May 26, 2016, when relay testing was complete. There was no root cause analysis conducted, however the relay was replaced on June 15, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The relay that was flagged for this violation for its poor test results is a Generator Start Up (GSU) transformer neutral time-overcurrent relay (HPS 137) which protects for 230 kV phase to ground faults. However, HPS has separate transformer and line differential relaying to protect their 230 kV equipment which would isolate a ground fault regardless of whether the HPS 137 relay worked properly or not, which greatly mitigates the risk of HPS 137. Further risk mitigating factors are included in the testing process. Relays such as the HPS 137 are given several levels of testing, which measure pick-up (initiating current), and timing (initiating speed). HPS 137 properly tested and calibrated for the minimum pick-up test, the 4 x (multiplier) minimum pick-up current test, and the 6 x minimum pick-up current test. Only the 2 x the minimum pick-up current test failed (by 2 seconds); meaning that the relay responded only 2 seconds slower than required, as opposed to not operating at all. The significance of the testing, is that the two tests that HPS 137 passed (4 x the minimum pick-up current test and 6 x the minimum pick-up current test) are designed to operate at higher current levels, which therefore makes them more vital in their role of protecting the BPS. And lastly, the HPS 137 is a slow-acting relay by design. There are several fast-acting (no time delay) differential relays that are integrated into the HPS protection scheme that are designed to react/respond much quicker than the HPS 137 - There are (3) Line Differential (HPS 130-132), and (3) GSU Differential (HPS 134-136) relays that will initiate from a fault prior to the HPS 137. No harm is known to have occurred. | To mitigate this issue, HPS: 1) replaced and successfully retested the faulty HPS 137 relay. As additional remediation, by October 30, 2016, HPS will: 1) review existing relay records to ensure no additional discrepancies exist, and 2) incorporate a supplemental check sheet in the program for reviewing relay test records for compliance.
2016-07-28 | Midwest Reliability Organization (MRO) | Western Area Power Administration-Upper Great Plains East (WAPA) | NCR01036 | MRO2016015548 | PRC-005-1.1b | R2 | On December 16, 2015, WAPA submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-005-1.1b R2. Specifically, WAPA did not maintain six of its Vent Lead Acid (VLA) batteries within the defined 18 month interval outlined in its Protection System Maintenance Program (PSMP). The maintenance did not occur every 18 months because of an error in the implementation of its computerized maintenance management system (CMMS) for preventative maintenance on VLA batteries. The setting was for "annual", which only required that the maintenance be performed once in a calendar year (up to 24 months apart) instead of every 18 months. The cause of this issue was WAPA's misunderstanding of its PSMP interval requirements. WAPA's maintenance personnel believed that performing maintenance annually (once ever calendar year) met the requirements of the PSMP, but the once per calendar year interval did not ensure that maintenance would be performed once every 18 months. The issue began on September 1, 2014, when the first battery's maintenance exceeded 18 months, and ended on October 22, 2015, when the sixth battery received all required maintenance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The batteries did receive some level of maintenance as they were tested once during the calendar year. Further, four months was the longest period of time that a battery was found to be noncompliant. Finally, three of the six batteries were commissioned within the last five years, which reduces the risk of failure. No harm is known to have occurred. WAPA has no relevant history of noncompliance with PRC-005-1.1b R2. | To mitigate this issue, WAPA: 1) performed the required maintenance activities; 2) provided additional training; 3) updated its CMMS for VLS Batteries from annual to 18 months since the last maintenance; and 4) updated its CMMS to provide notification for all maintenance activities that are due in three months or less.
2016-07-28 | Southwest Power Pool Regional Entity (SPP RE) | Public Service Commission, Yazoo City (Yazoo) | NCR01139 | SPP2016015700 | PRC-005-2 | R1; R1.1; R1.2 | On April 27, 2016, Yazoo submitted a Self-Report stating that, as a Distribution Provider, it had a minimal risk instance of noncompliance with PRC-005-2 R1. While preparing its response to a PRC-005-6 Spot Check issued by SPP RE, Yazoo discovered that it had not revised its Protection System Maintenance and Testing Program (PSMP) to include all the applicable Underfrequency Load Shed (UFLS) protection system devices identified in Table 3 of PRC-005-2. Specifically, Yazoo failed to include one (1) battery bank, one (1) battery charger, nine (9) current transformers, five (5) potential transformers, and three (3) dc circuits in its PSMP. Yazoo’s noncompliance began on April 1, 2015, the enforceable implementation date for PRC-005-2 R1, and ended on April 27, 2016, the date Yazoo revised its “Maintenance Program for Underfrequency Load Shedding Protection Systems.” The root cause of Yazoo’s noncompliance was human error. Yazoo’s internal standards team failed to properly determine the requirements of Table 3 of PRC-005-2 and follow up with its consulting team to implement the requirements. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Yazoo’s failure to implement a UFLS protection system maintenance program inclusive of all the protection system devices identified in PRC-005-2 Table 3 creates the potential for its system to fail to respond appropriately to an underfrequency event. Nevertheless, Yazoo is a small municipal electric utility with a peak load of 32 MW and an average load of 20 MW. Because the number of MWs Yazoo contributes to the regional UFLS program is small, the failure of any individual UFLS device required to be included within the scope of its UFLS equipment maintenance and testing program would result in a minimal impact on the overall effectiveness of the regional program and the reliability of the BPS. Maintenance and testing of the three (3) Yazoo UFLS relays identified in Yazoo’s existing PRC-008-0 PSMP was up to date, and testing of these relays was not due until 2019. Additionally, testing of the PRC-005-2 Table 3 devices under the PRC-005-2 Implementation Plan is not required until April 1, 2017. Thus, Yazoo’s noncompliance is a failure to document the changes to its UFLS PSMP and is unrelated to performance of the required testing. No actual harm is known to have occurred as a result of Yazoo’s noncompliance. Yazoo does not have any relevant prior violation history associated with PRC-005-2 R1. | To mitigate this minimal risk instance of noncompliance, Yazoo: 1) added the omitted Table 3 protection system devices to its UFLS PSMP; and 2) implemented a check sheet and review process to track new standards and changes/additions to existing standards. SPP RE has verified the completion of all mitigation activity.
2016-07-28 | Texas Reliability Entity (Texas RE) | GEUS | NCR04075 | TRE2016015691 | PRC-005-2(i) | R3 | On April 26, 2016, GEUS submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2(i) R3. GEUS did not perform all required maintenance activities for a single 24VDC station battery as specified in PRC-005-2(i) Table 1-4(b). In particular, GEUS failed to measure the 24VDC station battery’s cell/unit internal ohmic values every six months as required. The root cause of this issue was that GEUS incorrectly identified the 24VDC station battery in question as an auxiliary system and, therefore, not subject to all PRC-005-2(i) maintenance requirements. As a result, GEUS personnel only performed certain monitoring and visual inspections of the 24VDC station battery and did not complete six-month ohmic measurement activities required under Table 1-4(b). Texas RE determined the issue duration to be from October 2, 2015, the day after GEUS was required to first perform all six-month maintenance activities for the single 24VDC station battery, until January 27, 2016, the day GEUS performed the required six-month ohmic measurements for the single 24VDC station battery in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on several factors. First, the single 24VDC station battery at issue represents only 1% of the total devices (1/100) in GEUS’s Protection System and Maintenance Program. Second, GEUS personnel properly performed all other testing activities for the 24VDC station battery device presently required under PRC-005 2(i) Table 1-4(b). Third, when GEUS performed the required six-month ohmic measurements, the 24 VDC station battery tested at acceptable levels. Finally, the generation units supported by the battery are only approximately 25 MW in size, and therefore would have a small impact in the event of an issue. On June 26, 2014, a Settlement Agreement covering PRC-005-1 R1 (TRE2013012892) and PRC-005-1 R2 (TRE2013012893) was filed with FERC under NP14-44-000. On July 25, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE considered this compliance history in determining that this issue is appropriate for Compliance Exception (CE) treatment and determined that it was distinguishable from the current circumstances. In particular, the prior instances involved GEUS’s failure to include a large number of protection system devices within its Protection System Maintenance and Testing Program. As a result, GEUS did not perform the required testing on such devices. In contrast, the current circumstances involved only a single station battery for which GEUS provided evidence that it performed maintenance and inspection activities, just not all activities as required under PRC-005-2(i)’s applicable maintenance intervals. | To mitigate this issue, GEUS: 1) performed the required maintenance testing on the 24VDC station battery; 2) added the 24VDC station battery at issue to the tracking sheet that documents all equipment subject to PRC-005-2 requirements; and 3) conducted a comprehensive review of all generation plant equipment to ensure that all protection systems and other equipment subject to PRC-005-2(i) maintenance intervals were being properly tested. Texas RE has verified the completion of all mitigation activity.
2016-07-28 | Texas Reliability Entity (Texas RE) | The Dow Chemical Co (DOWTXO) | NCR04146 | TRE2016015705 | PRC-005-1 | R2 | On May 3, 2016, DOWTXO submitted a Self-Report to Texas RE stating, as a Generator Owner (GO), that it had two issues with versions of PRC-005. In the first instance, DOWTXO did not perform required capacity testing on three battery banks within the intervals defined in its Protection System and Maintenance Testing Program (PSMP). Texas RE determined that this particular issue began on June 12, 2010. Accordingly, Texas RE determined that DOWTXO had an issue with PRC-005-1 R2.1, the version of PRC-005 in effect at the time when the first maintenance and testing issue began. Regarding the first instance in particular, DOWTXO uses a third-party contractor to perform the necessary maintenance and testing activities for its batteries. In the current circumstances, the contractor began performing the required 60-month maintenance and testing work on the three batteries in question, but had not completed all required testing activities. As part of this process, the contractor submitted time invoices to DOWTXO for its initial work. Upon seeing the charged time for this initial work, however, a DOWTXO employee incorrectly assumed that all relevant 60-month capacity testing activities had been completed. The DOWTXO employee therefore closed out the work orders associated with the capacity testing project and no additional 60-month capacity testing activities were performed. In the second instance, DOWTXO did not perform 20-year battery replacements for two batteries as required under DOWTXO’s PSMP. Texas RE determined that this particular issue began on March 1, 2013. Accordingly, Texas RE determined that DOWTXO had an issue with PRC-005-1b R2.1, the version of PRC-005 in effect at the time when the second maintenance and testing issue began. Regarding the second instance in particular, DOWTXO personnel did not properly enter the required 20-year battery replacement interval in DOWTXO’s maintenance tracking system for the two batteries in question. As a result, DOWTXO did not replace the two batteries as prescribed by DOWTXO's PSMP. The root cause of these two instances was an inadequate process for ensuring all requiring battery testing and maintenance activities were performed. Specifically, DOWTXO lacked sufficient processes for tracking required maintenance activities and intervals for battery devices within its PSMP and ensuring the completion of the requisite testing activities associated with those devices. The issue duration was from June 12, 2010, when DOWTXO missed testing in the first instance, until July 16, 2015, when DOWTXO completed the missed capacity testing on all the battery banks in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the battery devices at issue represent only 0.77% (5/646) of all devices in DOWTXO’s PSMP. Second, DOWTXO had several redundant systems in place to mitigate any failures of the battery banks, including redundant battery systems at two of the affected facilities and battery chargers capable of providing DC power at all three of the affected facilities. Third, DOWTXO had alarm systems in place at all affected facilities. These alarms are designed to notify DOWTXO operators of any issues with the affected battery systems. Fourth, when DOWTXO did perform the required testing, all battery banks functioned properly. Finally, most of DOWTXO’s generation is to serve its internal load. Accordingly, the loss of this generation would likely have a small impact on the Bulk Electric System. No harm is known to have occurred. Texas RE considered DOWTXO’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DOWTXO: 1) completed the missed capacity testing on the battery banks in question; 2) transitioned its PSMP to correspond with the requirements set forth in NERC Reliability Standard PRC-005-2; 3) updated its internal processes to transition oversight of battery testing responsibilities to the DOWTXO Plant Assessment Team, the group generally responsible for coordinating DOWTXO’s NERC compliance activities; 4) developed an explicit requirement that third-party contractors performing battery maintenance provide electronic service reports to DOWTXO plant personnel specifically tasked with overseeing maintenance and testing activities. This will ensure that such personnel can review these maintenance activities and confirm their completion prior to closing a work order; and 5) incorporated a review of upcoming PRC-005 maintenance and testing responsibilities in the DOWTXO Plant Assessment Team process to better track compliance obligations. Texas RE has verified the completion of all mitigation activity.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC2015015403 | PRC-005-1 | R2 | On December 11, 2015, CHPD submitted a Self-Report stating that as a TO, GO, and DP, it had a possible issue of noncompliance with PRC-005-1 R2. Specifically, CHPD reported that it failed to include a communication-aided protection scheme in its Protection System maintenance and testing program (PSMP) and had not tested the scheme since original commissioning. In April 2015, as part of an effort to transition communication-aided schemes to the longer maintenance intervals in PRC-005-2, CHPD tested the alarming of all known communication-aided tripping schemes. This process involved using device settings to determine where to “break” the communications path for every scheme in the field. In October 2015, CHPD compared the results of this process to its PSMP records, and discovered a discrepancy. Although physical assets of one of the communication-aided schemes had been tested in accordance with CHPD’s PSMP, the scheme itself was not identified as an asset and had not been tested since commissioning. This issue began June 18, 2007, when the Standard became mandatory and enforceable to CHPD, and ended October 22, 2015, when CHPD tested the scheme. The cause of this issue was lack of a robust documentation program prior to the auditable compliance date, which led to a failure to identify the scheme in 2007. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, CHPD failed to test a communication-aided protection scheme at one of its generating facilities. Such failure could have limited CHPD’s awareness of the working order of the scheme. However, the scheme in question is a backup protection and would only operate following failure of the primary system. If the scheme failed, the line protection or the bus differential relays would still clear a fault instantly. If communication were lost during a non-fault condition, the scheme would operate in a more secure mode, using delayed elements. Additionally, this issue was limited to one uniquely configured scheme (roughly 3% of CHPD's 34 communication-aided schemes), which operated as designed when CHPD discovered and tested it. Although CHPD was noncompliant in testing the scheme itself for 3,048 days, its associated physical assets were alarmed, and had been tested in accordance with CHPD’s PSMP. Further, the review that led to discovery of this issue was part of an extensive effort by CHPD to ensure compliance through its transition to PRC-005-2. This review involved a separate, physical accounting of assets to compensate for potential unknown deficiencies in CHPD’s documentation prior to implementation of the Reliability Standards. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WECC considered CHPD’s compliance history in determining disposition track. CHPD has two previous violations of this Standard and Requirement, given Violation IDs: WECC2012011538 and WECC2014013590. The first instance concerned CHPD’s failure to test 34 miscategorized devices within appropriate intervals. The second instance concerned insufficient documentation and CHPD’s failure to test three devices within defined intervals. The causes of the previous violations were clerical error; and inadequate controls, training and processes pertaining to work order completion, respectively. The facts, circumstances, and causes of the previous violations are separate and distinct from the issue addressed herein. Therefore, WECC did not consider this issue a reflection of an underlying programmatic issue and determined that CHPD’s compliance history should not preclude designation of this issue as a compliance exception. | To mitigate this issue, CHPD: 1) tested the scheme; 2) added the scheme to its automated work management system; and 3) verified its other communication-aided schemes were included in its listed assets, accounted for in its work management system, and tested in accordance with its PSMP. WECC verified completion of CHPD’s mitigating activities.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2016015590 | FAC-003-3 | R3 | On March 3, 2016, PSE submitted a Self-Report stating that as a GO, it had a possible issue of noncompliance with FAC-003-3 R3. PSE failed to include one 7.3 mile, 230kV generation line in its Transmission Vegetation Management Program (TVMP) documentation. This issue began January 1, 2015, the effective date of this requirement for Generator Owners, and ended March 2, 2016, when PSE inspected the line in accordance with its TVMP. The root cause of this issue was human error - misinterpretation of the requirements under version 3 of the Standard resulted in inadvertent omission of the line in PSE’s documentation. This is PSE's first issue of noncompliance with this requirement, was identified and reported timely, and posed minimal risk to the Bulk Power System. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PSE failed to modify its Transmission Vegetation Management Program to include one 7.3 mile, 230kV line that became applicable under version 3 of the Standard. Such failure could have resulted in limited awareness of risk to the line posed by vegetative conditions. However, the line was maintained under Lower Snake River’s Balance of Plant Maintenance Program in a manner consistent with both the Standard and PSE’s TVMP. There have been no unscheduled or forced outages related to vegetation on this line since it came into commercial operation. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. PSE does not have previous violations of this Standard and Requirement and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) completed an inspection of the line per the requirements of its TVMP; and 2) verified that the maintenance performed under Lower Snake River’s Balance of Plant Maintenance Program during the period in question either met or exceeded maintenance activities that would have been performed under PSE’s TVMP. In an effort to prevent recurrence, PSE will: 1) formalize areas of responsibility between PSE Management and Lower Snake River Plant Management; 2) update its TVMP to include the line addressed in this issue; 3) review all >200kV lines within its system, including lines outside of PSE’s service area; and 4) create a list of all lines and generation plants to compare annually with its TVMP The proposed completion date for the above-listed activities is August 31, 2016.
2016-07-28 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC2016015688 | PER-005-1 | R3 | On April 27, 2016, WACM submitted a Self-Report stating that as a BA and TOP, it had a possible issue of noncompliance with PER-005-1 R3. Specifically, WACM reported that one of its System Operators completed only 28 hours of emergency operations training in 2015. The operator in question was scheduled for at least 32 hours of training early in the year, but missed one day due to illness. WACM did not schedule the operator for an additional training opportunity later in the year because the operator gave notice one week prior to the training; however, the operator did not end up leaving WACM. This issue began January 1, 2016, the day after 2015 training should have been completed, and ended March 19, 2016, when the operator completed an additional five hours of training. This issue was caused by less than adequate communication between departments. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WACM failed to ensure one of its System Operators completed 32 hours of emergency operations training in 2015. Such failure could result in the operator’s inability to perform all duties required during emergency operations. However, this issue was limited to one operator, five hours short of the Requirement. Had inadequate training rendered the operator unable to perform during emergency operations, at least three other operators each shift would have been available to compensate. Additionally, although one operator did not complete requisite training hours, WACM implemented several preventive measures to ensure each operator met this Requirement in 2015. Specifically, WACM’s training personnel tracked each operator’s position, location and annual training progress in a database, provided annual training reports, and discussed collective and individual training requirements in one-on-one discussions with each supervisor. In this instance, the supervisor retired the same month the operator gave (and later retracted) notice. WACM discovered this oversight during an internal compliance review on February 12, 2016. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WACM does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WACM: 1) ensured the operator completed an additional five hours of training; and 2) revised its System Operator Training Plan to require formal communication between departments, including quarterly status updates for training requirements. This communication will enable supervisors and operators to self-monitor completed training hours. WECC verified completion of WACM’s mitigating activities.
2016-06-29 | Midwest Reliability Organization (MRO) | Benson Power, LLC (BEN) | NCR11300 | MRO2015015132 | PRC-005-1.1b | R2 | On March 25, 2015, BEN submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. BEN identified several pieces of equipment that had incomplete maintenance and testing records. Specifically, the records had dates that maintenance and/or testing was performed, but those documents were lacking the specific associated test or maintenance records and the results of what was performed. The affected equipment includes two out of three of BEN's Current Transformers, one Potential Transformer, two Direct Current control systems, seven out of ten of BEN's relays, two battery chargers, and one battery. The cause of this issue was a lack of commitment to NERC compliance knowledge by the plant's previous ownership, who sought a registration appeal and resisted mandatory NERC compliance. The issue began on December 20, 2012, when BEN was required to be compliant with the Standard, and ended on October 22, 2015, when all the required testing was completed and documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The records indicate that some level of testing and/or maintenance was performed during the period of noncompliance, however several required details were missing from testing records, so it can not be confirmed that BEN followed its Protection System Maintenance Procedure (PSMP). The maintenance and testing that was performed during mitigation did not identify any equipment that was in disrepair and required maintenance in the spring of 2015. Further, the risk is reduced because BEN has a low potential for causing a BPS disturbance. Specifically, it has only one generator with a 73.3 MVA nameplate rating, it is not a blackstart unit, and it is not associated with a Special Protection System or an Interconnection Reliability Operating Limit (IROL) flowgate. No harm is known to have occurred. This is BEN's first instance of noncompliance with PRC-005-1b R2. | To mitigate this issue, BEN: 1) performed maintenance and testing on the affected equipment in October 2014 and May 2015; 2) sufficiently documented the maintenance and testing that was performed; and 3) retained the documented testing and maintenance records. BEN stated that mitigating activities were complete as of October 22, 2015.
2016-06-29 | Midwest Reliability Organization (MRO) | Lincoln Electric System (LES) | NCR01001 | MRO2016015586 | EOP-005-2 | R4 | On November 12, 2015, LES submitted a Self-Report stating that, as a Transmission Operator, it had an issue of EOP-005-2 R4. On May 4, 2015, LES switched a new substation into service. This substation split an existing tie line between LES and a neighboring registered entity that modified the interconnection point in LES's Power System Restoration Procedure (PSRP). Even though this was a planned modification, LES failed to update its PSRP prior to the date the substation was switched into service. This issue was discovered during a system restoration drill on September 29, 2015. The cause of the noncompliance was that LES's controls were inadequate to ensure the PSRP was updated and submitted to the Reliability Coordinator (RC) prior to conducting the system modification. Specifically, the task of updating the PSRP was a 'Task Group C' activity, with those tasks only being completed after Task Group A and B activities are completed, and are typically not completed until after facility energization. This resulted in the PSRP not being updated and submitted to LES's RC prior to the substation being brought into service. LES submitted its updated PSRP to its RC on October 6, 2015, and the RC approved the updated PSRP sixteen days later, on October 22, 2015. The issue began on May 4, 2015, when the substation was brought into service, and ended on October 6, 2015, when LES submitted an updated PSRP to its RC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The interconnection point at issue is not a cranking path for LES's primary Blackstart Unit. Additionally, the interconnection point is one of seven options for interconnection of LES's system and a neighboring registered entity's system, and LES has three other interconnection options to neighboring Registered Entities for use in a power system restoration. Further, LES still had the ability to use the interconnection point in the event of system restoration, even if the plan was out of date. Finally, LES Transmission and Generator Operators receive training regarding system restoration and participate in annual system restoration drills. This training and the drills have increased the operators' competency to successfully restore the system. No harm is known to have occurred. This is LES's first issue with EOP-005-2. | To mitigate this issue, LES: 1) updated its PSRP to correct the identified deficiency and submitted the revised PSRP to its RC for approval; and 2) updated its Substation Equipment Project checklist to prioritize the task of updating the PSRP to a 'Task Group A' activity. LES stated that mitigating activities were complete as of October 6, 2015.
2016-06-29 | Midwest Reliability Organization (MRO) | Omaha Public Power District (OPPD) | NCR00860 | MRO2016015637 | PRC-005-1.1b | R2 | On July 27, 2015, OPPD submitted a Self-Report stating that, as a Transmission Owner, it had an issue of PRC-005-1.1b R2. Specifically, OPPD identified batteries at a single substation that were not tested within the interval defined in OPPD's Protection System Maintenance Program (PSMP). The batteries in question were required to have a Level 1 test every 90 days and a Level 2 test every 18 months. OPPD maintenance technicians have an asset management software that gives them alerts and instructions on what maintenance to perform. On September 10, 2013, a technician was performing testing on the batteries. The technician performed the Level 1 testing, and accidently marked both the Level 1 and the Level 2 testing complete without performing the Level 2 testing. The Level 2 testing became due on March 10, 2014, 18 months after the last test had been completed on September 10, 2012. OPPD detected this noncompliance while conducting an internal data spot check. OPPD conducted the Level 2 testing on April 2, 2014. The cause of this issue is the similarity between Level 1 and Level 2 questions in the automated system resulting in the technician not realizing he was marking two separate tests as complete. The issue began on March 10, 2014, when the interval was missed for the Level 2 testing, and ended on April 2, 2014, when the testing was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The batteries did have some level of testing as Level 1 inspections were conducted every 90 days. Additionally, the batteries and charger were constantly monitored and alarmed for issues related to voltage and charging. Further, after this issue was detected, OPPD reviewed all battery tests in 2014 and determined this was the only instance where this issue occurred. Finally, the risk is further reduced by the strong controls that OPPD has in place which are evidenced by OPPD's detection and mitigation of the noncompliance after a relatively short period of time (23 days). No harm is known to have occurred. MRO considered OPPD's PRC-005-1.1b R2 compliance history in determining the disposition track. OPPD's relevant prior noncompliance with PRC-005-1.1b R2 includes: NERC Violation ID MRO201000171 (PRC-005-1 R2) and MRO2012009549 (PRC-005-1 R2). MRO determined that OPPD's compliance history should not serve as a basis for applying a penalty. MRO201000171 involved a failure to do testing and maintenance on relays, and MRO2012009549 involved a failure to conduct Specific Gravity Testing for Substation Battery Systems. MRO determined that Compliance Exception treatment was still appropriate because the current issue was not caused by any failure to mitigate MRO201000171 or MRO2012009549. Additionally, the prior battery related noncompliance was caused by OPPD's decision to discontinue Specific Gravity Testing, but its failure to update its PSMP to reflect that change. Finally, MRO considered OPPD's utilization of preventive controls and its detective controls that appear to have limited the scope and duration of the current noncompliance. | To mitigate this issue, OPPD: 1) performed a Level 2 test on the batteries; 2) changed the questions for the Level 2 test in the asset management software so that they are more distinct from the Level 1 questions; 3) reviewed the test data sheets for all battery tests completed in 2014 to verify the accuracy of the testing; 4) will review all test data sheets within 30 days of a battery test to ensure the test was actually completed and completed accurately; and 5) has updated its procedure for technicians to increase proficiency in the use of OPPD's asset management software. OPPD stated that mitigating activities were complete as of April 30, 2015.
2016-06-29 | Northeast Power Coordinating Council (NPCC) | Brooklyn Navy Yard Cogeneration Partners, L.P. (BNY) | NCR10237 | NPCC2016015592 | PRC-018-1 | R1; R1.1 | On March 2, 2016, BNY submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-018-1 R1. During a self-performed gap analysis of BNY's NERC Compliance Program, it was identified that two microprocessor relays used to monitor protective relays and generator breaker positions on BNY's combustion turbine generators were not synchronized to within two milliseconds or less of Universal Coordinated Time scale (UTC) as required by PRC-018-1 R1.1. BNY owns two combined cycle units, each comprised of a combustion turbine generator and a steam turbine generator. All sequence of event recording capability at the facility is provided by an APP-601 multi-function recorder which monitors the 13.8 kV and 138 kV breakers along with the relays associated with the steam turbine generator protection systems, and two Siemens 7UM62 microprocessor relays which monitor the protective relays for each combustion turbine generator as well as the generator breaker positions. The APP-601 Multi-function recorder was found to be synchronized to UTC, however the two Siemens 7UM62 relays were not synchronized with two milliseconds of UTC. The issue duration was from October 20, 2015, the date entities were required to have 100% installation of sequence of events recorders in accordance with the PRC-002-NPCC-01 Implementation Plan, to May 4, 2016, when BNY completed installation of a GPS clock to synchronize the microprocessor relays to UTC. The root cause of the issue was the lack of functionality in the Siemens 7UM62 relays to automatically synchronize with UTC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). These devices are used for disturbance monitoring purposes and have no actual impact on the operation of the BPS. The lack of synchronization between the microprocessor relays and UTC only affects data that is used for events analysis purposes. To date, BNY has not experienced an event which necessitated the use of the data from said relays. No harm is known to have occurred. NPCC considered BNY's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BNY: 1) Purchased and installed a Global Positioning System (GPS) clock that is synchronized to within 2 milliseconds of UTC. The clock provides UTC to both affected microprocessor relays; and 2) Will prevent similar occurrences in the future by including all equipment updates and changes in their Management of Changes process. Documentation will be required from vendors stating the ability of new equipment to meet or exceed the necessary compliance and reliability. NPCC has verified the completion of all mitigation activity.
2016-06-29 | Northeast Power Coordinating Council (NPCC) | Plainfield Renewable Energy, LLC (PRE) | NCR11405 | NPCC2015015336 | EOP-004-2 | R3 | On November 6, 2015, PRE submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it had an issue of EOP-004-2 R3. Specifically, PRE did not validate all contact information contained in its Operating Plan pursuant to Requirement R3 in 2014. The root cause of this instance of non-compliance was that the previous owner of PRE did not properly establish responsibility for the contacts validation task, nor did it maintain any records to demonstrate that contact validation was performed in 2014. After Greenleaf Power took ownership of the PRE facilities in mid-2015, it addressed this issue by validating all contacts information in October 2015 and, additionally, by developing and implementing operating procedures that contain sufficient detail to ensure future compliance with the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PRE has a generation capacity of approximately 37.5 MWs. Although there are no records to indicate that anyone performed the specific task of verifying all contacts information referenced in their Operating Plan in 2014, Control Room Operators were, in fact, cognizant of contact information of critical organizations associated with the daily operation of PRE's generation facilities, as they were prominently displayed in the plants' ISO-NE communications log book. Furthermore, key contacts information such as phone numbers of responsible personnel at CONVEX, ISO-NE, ISO-NE Outage Coordination, and Connecticut Department of Energy and Environmental Protection, did not change from the previous year as a result of completing the validation exercise required by R3 of the standard in 2015. Additional contacts information (e.g. phone numbers of local emergency agencies) existed in other plant documents. For all the above considerations, this instance of non-compliance represents a minimal impact on the reliable operation of the BPS system. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered PRE's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, PRE: 1. On October 20, 2015, validated the contact information contained in their Operating Plan by implementing a contacts-specific procedure (Procedure No.: PRE-4030-A) that consolidates all contacts information pertinent to PRE's Operating Plan in one single document that explicitly requires an annual verification cycle; and 2.On November 5, 2015, also implemented a comprehensive overall Plant Operating Procedure -"Communications Voice and Data"- (Procedure No.: PRE-4030) that has itself an annual review cycle. This procedure contains a reference to the aforementioned contacts-specific procedure requiring PRE to maintain an up-to-date listing of telephone contacts. NPCC has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Dover | NCR00713 | RFC2016015488 | EOP-004-2 | R1 | On January 15, 2016, City of Dover submitted a Self-Report stating that, as a Distribution Provider, it had an issue of EOP-004-2 R1. During an internal gap analysis, City of Dover discovered that it did not have an event reporting Operating Plan dated for calendar year 2014. City of Dover does have a current event reporting Operating Plan dating back to 2015. The root cause of this noncompliance was recent turnover in the prior management staff at City of Dover. The prior management staff was employed at City of Dover when EOP-004-2 R1 took effect in January 2014, but failed to implement an event reporting Operating Plan due to their failure to monitor the implementation of new and modified NERC Reliability Standards. This issue started on January 1, 2014, when City of Dover was required to comply with EOP-004-2 R1 and ended on January 15, 2016, when City of Dover completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the Standard/Requirement requires the reporting of events after they occur and does not relate to actions taken to control the system on a real-time basis. Second, City of Dover identified this noncompliance during an internal gap analysis, which demonstrates City of Dover’s commitment to developing effective internal detective controls. ReliabilityFirst also notes that City of Dover did not experience any reportable system events during the period of noncompliance. No harm is known to have occurred. ReliabilityFirst considered City of Dover’s EOP-004 R1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, City of Dover: 1) began to monitor the NERC Reliability Standards more closely for any changes to current Standards or approval of new Standards that are developed by NERC; and 2) performed NERC reliability program gap analyses on a periodic basis to review and improve its compliance program. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Dover | NCR00713 | RFC2016015489 | PRC-005-2 | R1 | On January 15, 2016, City of Dover submitted a Self-Report stating that, as a Distribution Provider, it had an issue of PRC-005-2 R1. During an internal gap analysis, City of Dover discovered that it did not have a Protection System Maintenance and Testing program for the Underfrequency Load Shedding Systems (UFLS). However, City of Dover did complete the required testing of the UFLS equipment in accordance with its procedure for PRC-008 in June 2010, and was not required to perform this maintenance and testing again until 2020. The root cause of this noncompliance was the fact that City of Dover was not aware of the revision to PRC-005 including changes to the Protection System Maintenance and Testing program for its UFLS equipment. This issue started on April 1, 2015, when City of Dover was required to comply with PRC-005-2 R1 and ended on May 31, 2016, when City of Dover completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, City of Dover performed the requisite maintenance and testing within the prescribed intervals. Second, City of Dover identified this noncompliance during an internal gap analysis, which demonstrates City of Dover’s commitment to developing effective internal detective controls. Third, the total amount of UFLS is only 55 MW, which indicates that any potential harm would be minimal. Finally, ReliabilityFirst also notes that City of Dover did not experience a condition which required operation of the UFLS during the period of noncompliance. No harm is known to have occurred. | To mitigate this issue, City of Dover: 1) identified all UFLS equipment to be included in the Protection System Maintenance Program (PSMP) and established the maintenance intervals and activities; 2) completed all maintenance activities on all UFLS equipment listed in the PSMP as listed in Table 3 of NERC Standard PRC-005-2(i); 3) entered maintenance tasks in facility computerized maintenance management system with the intervals and maintenance tasks from Table 3 of NERC Standard PRC-005-2(i); 4) began to monitor the NERC Reliability Standards more closely for any changes to current Standards or approval of new Standards that are developed by NERC; and 5) performed NERC reliability program gap analyses on a periodic basis to review and improve its compliance program. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE) | NCR00753 | RFC2015014800 | PRC-005-1 | R2 | On March 30, 2015, DTE submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. ReliabilityFirst later determined that the violation duration began when PRC-005-1 R2 was in effect and is thus enforcing the violation under PRC-005-1 R2. DTE discovered 345 kV breaker flashover relays on four power plant units that were not in the maintenance and testing program. DTE determined that all references to these assets were inadvertently removed from the maintenance and testing program at the time DTE sold its transmission assets to ITC in 2003 based on the protection scheme categorization utilized by DTE and ITC at that time. The missed relays were identified by a DTE engineer reviewing test results and prints after an outage, which was not caused by the missed relays. As part of its mitigation, DTE and ITC created guidelines for determining ownership of protective relays and associated equipment. DTE did not identify any additional relays or associated equipment that it owned and did not test. The root cause of this noncompliance was a lack of verification controls to confirm DTE’s and ITC’s understanding of their maintenance and testing responsibilities based on the protection scheme categorization as part of the sale in 2003. This issue started on June 18, 2007, the date DTE was required to comply with PRC-005-1 R2 and ended on October 16, 2015, the date DTE completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The breaker flashover relays at issue are designed to be active only when the 345 kV breakers are open, but the breakers are normally closed because they connect the generating units to the system and are thus closed when the generating unit is online. Additionally, this was a baseload unit and is thus generally only offline for forced outages. Thus, there was only a limited amount of time that there was the potential for the relay to misoperate. No harm is known to have occurred. ReliabilityFirst considered DTE's PRC-005 R2 compliance history in determining the disposition track. DTE's relevant prior noncompliances with PRC-005 R2 include: a. RFC201000663. A Settlement Agreement covering a violation of PRC-005-1 R2 was filed with FERC under NP11-232-000 on July 28, 2011. On August 29, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In the prior violation, DTE failed to test certain batteries within their defined intervals. The prior violation is distinguishable from the instant violation because, unlike the prior violation, the instant violation occurred as a result of a mistaken belief that ITC owned the assets. b. RFC201100819. A Settlement Agreement covering violations of PRC-005-1 R2, R2.1 was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. In the prior violation, DTE failed to test certain Protection System schemes due to a misunderstanding of its obligations under its transition plan for transitioning from the previous definition of “bulk electric system” to the new definition of “bulk electric system.” The prior violation is distinguishable from the instant violation because the instant violation occurred as a result of a mistaken belief that ITC owned the assets. ReliabilityFirst determined that DTE's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, DTE: 1) tested the missed relays; and 2) created and signed a document jointly with ITC to clarify ownership responsibilities and operational guidelines for protective relays and associated equipment common to both DTE and ITC. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE) | NCR00753 | RFC2014014199 | VAR-002-2b | R1 | On August 1, 2014, DTE submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-2b R1. DTE determined that a portion of a newly acquired wind farm was operating with the automatic voltage regulator (AVR) out of service, but failed to notify the Transmission Operator (TOP). Specifically, on May 30, 2014, DTE purchased Brookfield Wind Farm (44 turbines, 83 MWs connected to the 345 KV transmission system). Once the purchase was complete, DTE shut down the wind farm for modifications to communication networks and certain maintenance work. During testing on June 26, 2014, DTE closed one of three feeder breakers in an effort to clear individual wind turbine faults. On June 27, 2014, at 1400 hours, a portion of the wind farm came on line (maximum 20 MWs) with the AVR not in service. The portion of the wind farm remained online through June 30, 2014 at 0730 hours. At that time, DTE notified the Balancing Authority that this portion of the wind farm was generating power, but it did not notify the TOP that the wind farm was in service with the AVR out of service. The root cause was lack of workforce management practices in that DTE did not sufficiently train the personnel responsible for operating the equipment. More specifically, the wind farm manager was inexperienced and did not fully understand the operational aspects of the AVR once the individual wind turbine faults were cleared. All controls and equipment were still in the process of being checked prior to becoming operational when this violation occurred and the AVR controls were not set for desired operation when the wind farm generation came online. Prior to this violation, the wind farm manager requested the Renewable Generation Compliance Program Manager meet with him to discuss his NERC Compliance obligations and required communications. Unfortunately, the meeting did not take place before the violation occurred. This issue started on June 27, 2014, when DTE operated without the AVR in service and without making proper notification to the TOP, and ended on June 30, 2014, when DTE took the relevant portion of the wind farm offline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The wind farm generation capability for the portion of the wind farm at issue was only 20 megawatts, roughly one quarter of the maximum generating capability for the wind farm. Additionally, the wind farm at issue and NextEra Pheasant Run Wind Farm share a common interconnection to the transmission system. The NextEra Pheasant Run Wind Farm is responsible for maintaining voltage at the interconnection point and according to that wind farm, voltage was in schedule during the time period of the violation. If there were voltage issues, NextEra Pheasant Run Wind Farm likely would have notified DTE who then could have remedied the issue. No harm is known to have occurred. ReliabilityFirst considered DTE's VAR-002 R1 compliance history in determining the disposition track. DTE’s relevant prior noncompliance with VAR-002 R1 includes: RFC2011001056. A Find, Fix and Track covering a violation of VAR-002-1.1b R1 was filed with FERC on January 31, 2012. In the prior violation, DTE started the AVR on one of its generators in manual mode without notifying the TOP, which was deemed an isolated event corrected through personnel training. Unlike the prior violation, the current issue occurred on a newly acquired wind farm while the controls and equipment were still being tested. Here, DTE informed the Balancing Authority that a portion of the windfarm was generating, but failed to notify the TOP that the wind farm was in service with the AVR out of service. ReliabilityFirst determined that DTE's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, DTE: 1) installed AVR status alarming for Brookfield Wind Farm at the NextEra Control Center; 2) modified NextEra Control Center Procedures to require NextEra Control Center to notify DTE Systems Operations Center of changes in voltage status; and 3) developed a process map to guide future Wind Park start-ups, including required notifications. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE) | NCR00753 | RFC2015014856 | VAR-002-3 | R2 | On April 1, 2015, DTE submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-3 R2. DTE determined that for a brief period of time, it did not follow a generator voltage schedule (with a small deviation) and despite DTE’s prior communication with the Transmission Operator (TOP), the TOP did not expressly grant DTE an exemption. Specifically, DTE failed to maintain the generator bus voltage on St. Clair Bus 102 within the TOP provided voltage schedule. DTE promptly called the TOP to notify the TOP that the requested increase in voltage could not be reached because Saint Claire Unit 4, which ties into bus 102, came online but was in the early stages of start-up and the other units lacked the room to increase. The TOP stated the voltage should correct itself during the start up. An hour later, DTE informed the TOP the automatic voltage regulator (AVR) was not in automatic mode, but that the bus voltage was back within the scheduled limits. However, approximately a half-hour later the bus voltage dropped under the scheduled low limit again. No additional communication occurred, and from 5:15 pm to 6:27 pm the voltage was .3 volts outside of the schedule limits. DTE notified the TOP about the deviation at 6:27 pm. DTE determined that it did not notify the TOP of the voltage deviation because the personnel responsible for making the notification mistakenly believed the bus voltage was back within scheduled limits. Thus, the root cause was a lack of verification controls to ensure or verify that the bus voltage remained within scheduled limits. The duration of this noncompliance is from 5:15 pm to 6:27 pm on February 23, 2015, which is the total time the voltage was outside of the schedule limits without notification to the TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The overall risk to the BPS for this violation was very low because of the deviation from the schedule was very small (.3 volts) and occurred for a relatively brief span of time (72 minutes). Additionally, the TOP was aware that DTE was operating without the AVR in automatic mode, and thus was on notice that the voltage may vary slightly. Therefore, these factors minimize the risk that the voltage deviation would have negatively affected the system. No harm is known to have occurred. DTE’s relevant prior noncompliance with VAR-002 R2 includes: RFC2012011203. A Find, Fix and Track covering a violation of VAR-002-1.1b R2 was filed with FERC on March 27, 2013. In the prior violation, a newly operating wind farm operated outside the provided voltage schedule numerous times for a period of more than six months. Unlike the prior violation, the current issue relates to a Bus voltage deviation that occurred during a start-up process for a unit and dropped below the schedule once for a very brief span of time. ReliabilityFirst determined that DTE's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, DTE: 1) checked metering on SCPP Bus 102; and 2) set up audible notification for generator bus voltage points. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2016015477 | VAR-002-4 | R3 | On January 15, 2016, EPOPP submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-4 R3. EPOPP failed to inform PJM, its Transmission Operator, of a status change on its Power System Stabilizer (PSS) within 30 minutes of the change in status. On November 25, 2015, EPOPP completed a maintenance outage for EPOPP Combustion Turbine 1 (CT1). While performing testing to comply with the MOD-026 and MOD-027 NERC Reliability Standards on December 2, 2015, EPOPP’s third-party testing service provider discovered that the PSS on CT1 was disabled. Per VAR-002-4 R3 and Essential Power’s VAR-002 Procedure, EPOPP is to operate either with the PSS enabled or to notify PJM within 30 minutes of a change in status on the PSS. EPOPP could not provide a record that shows it notified PJM when the PSS was disabled, which constitutes a violation of VAR-002-4 R3. EPOPP cannot find a record of it notifying PJM of a status change on the PSS because the PSS status point, which tells whether the PSS is enabled or disabled, is not captured in EPOPP’s data historian, the PSS status point is not available to EPOPP’s operators in the control room, there is no alarm for when the status on the PSS changes, and there is no operator log entry identifying a change in PSS status. EPOPP does not know the last time the PSS was enabled before EPOPP discovered it was disabled on December 2, 2015 and therefore does not know how long the PSS was disabled. Typically, the status of the PSS does not change when the unit is online or offline. This noncompliance involves the management practice of grid maintenance because EPOPP was not tracking PSS status changes on EPOPP’s CT1. EPOPP was not proactively monitoring the equipment to determine when the PSS was enabled or disabled. The root cause of this noncompliance was that EPOPP did not have tools in place to remotely monitor the status of the PSS. This issue started on May 29, 2015. The start date of this noncompliance is May 29, 2015 because EPOPP does not know how long the PSS was disabled and could not provide any evidence to RF of the last time the PSS was enabled. This means that EPOPP has been noncompliant since the Standard and Requirement went into effect. This issue ended on April 29, 2016, when EPOPP enabled the PSS on Generating Unit CT1 and Notified PJM of this change in status. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. At the time of the noncompliance, EPOPP could not monitor the PSS status remotely and it was not feasible to have continuous local monitoring. The unit at issue operates infrequently, only about once a month. The generator in question is rated at 234 MW and is only connected to a single 230 kV transmission line. There were no abnormal conditions that occurred on the bulk power system during the period when the PSS was disabled and this was an isolated issue with a single Combustion Turbine of less than 300 MWs. No harm is known to have occurred. ReliabilityFirst considered EPOPP's VAR-002 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EPOPP: 1) added the PSS status points to the data historian; 2) added the PSS status as a point on the generator operator Human Machine Interface (HMI) with an alarm for any change in status; 3) placed the PSS on EPOPP CT1 back in-service and notified PJM that it was placed back-in-service; and 4) committed to retrain the EPOPP operators on the requirements of VAR-002 and Essential Power’s procedure for maintaining compliance with VAR-002. These mitigation steps will give EPOPP operators visibility to the status of the PSS and will notify the operators, via an alarm, of a change in status of the PSS. All of the mitigation steps taken together will reduce the likelihood that this noncompliance reoccurs.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW) | NCR03006 | RFC2015015419 | VAR-002-4 | R3 | On December 22, 2015, Flat Rock Windpower, LLC (Flat Rock) submitted a Self-Report (via MLW and an applicable MRRE agreement) stating that, as a Generator Operator, it had an issue of VAR-002-4 R3. On October 27, 2015, EDP Renewables' (owner and operator of Flat Rock) Remote Operations Control Center (ROCC) in conjunction with the SCADA team and a third party service provider performed tests on Flat Rock’s remote operations as part of an update to the Wind Energy Management System. Part of this testing included remotely operating the breakers for the capacitor bank at selected wind farms, including Flat Rock. Opening the breakers changes the status of the capacitor banks by placing the capacitor bank’s controller into manual mode from automatic mode. This change in status occurred on October 27, 2015 at 14:11 CPT. The ROCC Operator notified its Transmission Operator (TOP), NYISO, of the change in status on Flat Rock’s capacitor banks on October 28, 2015 at 9:07 CPT after the ROCC Operator returned Flat Rock capacitor bank’s controller to automatic mode, which occurred on October 28, 2015 at 8:58 CPT. The ROCC notified its TOP 18 hours and 56 minutes after it made the change in status. That time period is more than the 30 minutes VAR-002-4 R3 allows for a notification to be made after a capacitor bank status change. Flat Rock is a dispersed power generation resource. It is not equipped with an Automatic Voltage Regulator (AVR). Instead, Flat Rock controls the voltage at its point of interconnection using capacitor banks with a total of 76.8 MVAR, managed by a Capacitor Bank Controller, since the installed wind turbine generators do not have reactive capability. The capacitor banks can be operated in manual mode or in automatic mode. In automatic mode, which is the usual mode of operation, the capacitors are coordinated by a single controller to support voltage at the Chases Lake Substation. This noncompliance involves the management practice of workforce management through ineffective training. All ROCC Operators were not fully aware that the TOP needed to be identified of any status changes of their capacitor banks. Ineffective training is the root cause because the ROCC Operators should have been properly trained to always notify the TOP when an applicable status change is made. This issue started on October 27, 2015, the date Flat Rock made the status change on its capacitor banks without notifying their TOP within 30 minutes of making the change and ended on October 28, 2015, the date Flat Rock notified their TOP of its status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The ROCC Operator was still monitoring and controlling the facility during the event and the 76.8 MVAR capacitor banks were available for use; the capacitor banks just would have needed to be switched on manually. The ROCC Operator was available to respond to an alarm indication that the plant was outside of its required power factor range and respond to a request for power factor support by its Transmission Owner throughout the event. During this event, the wind farm did not go outside of the required voltage range, the wind farm remained within the power factor range, and reactive power support was not requested. The risk is also minimal because Flat Rock offers a medium total capability of 321.75 MWs with 76.8 MVAR of reactive power connecting to the bulk power system at the Chases Lake Substation. Flat Rock is a medium generator that is also an intermittent resource that operates at a capacity factor of approximately 28%. No harm is known to have occurred. ReliabilityFirst considered Flat Rock's VAR-002 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Flat Rock: 1) performed a detailed investigation of the event. This investigation involved all ROCC personnel on duty on October 27th and 28th, the Director of the Control Center and HV Operations, and the ROCC Supervisor. 2) reviewed the procedures for monitoring alarms and email notifications with the personnel involved and reviewed shift turnover procedures with all relevant ROCC personnel. This training will help ensure that all ROCC Operators will be better equipped to handle similar events in the future; and 3) incorporated the lessons learned from this event into the next periodic ROCC training.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Meadow Lake Wind Farm, LLC (MLW) | NCR03006 | RFC2015015420 | VAR-002-4 | R3 | On December 22, 2015, Lost Lakes Wind Farm, LLC (Lost Lakes) submitted a Self-Report (via MLW and an applicable MRRE agreement) stating that, as a Generator Operator, it had an issue of VAR-002-4 R3. On October 27, 2015, EDP Renewables' (owner and operator of Lost Lakes) Remote Operations Control Center (ROCC) in conjunction with the SCADA team and a third party service provider performed tests on Lost Lakes’ remote operations as part of an update to the Wind Energy Management System. Part of this testing included remotely operating the breakers for the capacitor bank at selected wind farms, including Lost Lakes. Opening the breakers changes the status of the capacitor banks by placing the capacitor bank’s controller into manual mode from automatic mode. This change in status occurred on October 27, 2015 at 14:06 CPT. The ROCC Operator notified its Transmission Operator (TOP), ITC Midwest, of a change in status on October 28, 2015 at 7:50 CPT after the ROCC Operator returned Lost Lakes’ capacitor bank to automatic mode, which occurred on October 28, 2015 at 7:31 CPT. The ROCC Operator notified its TOP 17 hours and 44 minutes after it made the change in status. That time period is more than the 30 minutes VAR-002-4 R3 allows for a notification to be made after a capacitor bank status change. Lost Lakes is a dispersed power generation resource. It is not equipped with an AVR. Instead, Lost Lakes controls the voltage at its point of interconnection using five capacitor banks with a total of 55.5 MVAR, managed by a Capacitor Bank Controller, since the installed wind turbine generators do not have reactive capability. The capacitor banks can be operated in manual mode or in automatic mode. In automatic mode, which is the usual mode of operation, the capacitors are coordinated by a single controller to support voltage at the Cayler Substation. This noncompliance involves the management practice of workforce management through ineffective training. All ROCC Operators were not fully aware that the TOP needed to be identified of any status changes of their capacitor banks. Ineffective training is the root cause because the ROCC Operators should have been properly trained to always notify the TOP when an applicable status change is made. This issue started on October 27, 2015, the date Lost Lakes made the status change on its capacitor banks without notifying their TOP within 30 minutes of making the change and ended on October 28, 2015, the date Lost Lakes notified their TOP of its status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The ROCC Operator was still monitoring and controlling the facility during the event and the 55.5 MVAR capacitor banks were available for use; the capacitor banks just would have needed to be switched on manually. The ROCC Operator was available to respond to an alarm indication that the plant was outside of its required power factor range and respond to a request for power factor support by its Transmission Owner throughout the event. During this event, the wind farm did not go outside of the required voltage range, the wind farm remained within the power factor range, and reactive power support was not requested. The risk is also minimal because Lost Lakes offers a small total capability of 100.65 MWs with 55.5 MVAR of reactive power connecting to the bulk power system at the Cayler Substation. Lost Lakes is a small generator that is also an intermittent resource that operates at a capacity factor of approximately 39%. No harm is known to have occurred. ReliabilityFirst considered Lost Lakes' VAR-002 R3 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Lost Lakes: 1) performed a detailed investigation of the event. This investigation involved all ROCC personnel on duty on October 27th and 28th, the Director of the Control Center and HV Operations, and the ROCC Supervisor. 2) reviewed the procedures for monitoring alarms and email notifications with the personnel involved and reviewed shift turnover procedures with all relevant ROCC personnel. This training will help ensure that all ROCC Operators will be better equipped to handle similar events in the future; and 3) incorporated the lessons learned from this event into the next periodic ROCC training.
2016-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2015015398 | EOP-008-1 | R5 | On December 2, 2015, PJM submitted a Self-Report stating that, as a Balancing Authority, Reliability Coordinator, and Transmission Operator, it had an issue of EOP-008-1 R5. PJM failed to annually approve its Operating Plan for backup functionality as required by EOP-008-1 R5.1. PJM conducts annual control center evacuation drills and, in doing so, annually reviews its Operating Plan. However, in 2014, PJM timely reviewed the Operating Plan during its control center evacuation drill, but failed to reflect its annual approval of the Operating Plan in the Operating Plan’s revision history. PJM conducted the subsequent annual review on January 21, 2015, and, at that time, documented it approval of the Operating Plan. The root cause of this noncompliance was lack of verification controls to ensure PJM carried out all required steps of reviewing and approving the Operating Plan, including reflecting the approval in the revision history of the Operating Plan. This issue started on October 18, 2014, the date by which the Operating Plan was required to be approved and ended on January 21, 2015, when PJM approved the Operating Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance does not have an effect on the actual Operating Plan because PJM reviewed the actual Operating Plan as part of its annual evacuation drill. The noncompliance was a mere documentation error as PJM failed to reflect the annual approval in the revision history of the Operating Plan. No harm is known to have occurred. ReliabilityFirst considered PJM’s EOP-008 R5 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PJM: 1) completed the annual review and approval of the Operating Agreement; and 2) implemented additional controls to prevent recurrence, including: (a) an outlook calendar reminder for the responsible group to review and approve the Operating Plan; (b) a reminder in SharePoint to review and approve the Operating Plan; and (c) an additional step in the annual evacuation drill procedure with the specific requirement to both review and approve the Operating Plan. ReliabilityFirst has verified the completion of all mitigation activity.
2016-06-29 | SERC Reliability Corporation (SERC) | Alabama Power Company (APC) | NCR01166 | SERC2015014942 | PRC-005-1.1b | R2.; R2.1 | On April 21, 2015, SERC sent APC an audit detail letter notifying it of a compliance audit scheduled for July 20, 2015, through August 7, 2015. On May 20, 2015, APC submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-005-1.1b R2. APC failed to conduct maintenance and testing on a single battery as required by its Protection System program. On April 1, 2015, an APC engineer, while developing several new queries of battery data, determined that APC could not produce evidence that it conducted commissioning testing for one 115 kV switching station battery. The APC commissioning procedures require preventive diagnostic inspections (PDI) prior to the battery’s in-service date and acceptance testing following the in-service date. APC placed the battery in service on April 29, 2014, but did not test the battery until August 25, 2014. APC performed two inspections on the battery in 2014, but could not provide evidence that it conducting the PDI prior to placing the battery in service. APC conducted the PDI on August 25, 2014, approximately four months after the in-service date. Using random sampling, SERC reviewed and assessed compliance with PRC-005-1.1b approximately 10% of the inventory of the APC Protection System devices and did not identify additional non-compliance. APC could not provide evidence that it performed maintenance and testing within the defined interval for one of 29 batteries (3.4%) reviewed. In total, APC could not provide evidence that it tested and maintained one of 1,446 (0.069%) Protection System devices within the defined interval. The cause of the issue was a failure to perform and document a PDI on the battery prior to placing it in service. APC failed to close out the initial work order for a PDI acceptance test on the battery when it closed out the initial work orders for other equipment at the site. In addition, management reviews of work completion status did not detect this issue because the database queries used in these reviews relied on the last performed date field in the database in order to calculate the next due date. For the battery at issue, the last performed date field was null, thus preventing the database from calculating a due date during this period. With no due date, the battery did not show up on a backlog report for overdue battery inspections. However, on August 25, 2014, an AECI crew performed a standard maintenance PDI on the battery, without a work-order, while in the area performing the same test on an adjacent substation. This issue lasted from April 29, 2014, when APC put the battery in service prior to performing a PDI, until August 25, 2014, when APC performed the PDI. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. APC’s failure to perform the maintenance and testing of the Protection System device within the defined interval could lead to the device not operating as intended, potentially leading to false trips, remote clearing, delayed clearing, the overreach of protective relays or reliance on the interconnecting Transmission Owner’s Protection System device to respond to a fault. However, APC utilized the monitoring and alarming function in its SCADA system for the battery and charger involved. APC tested and documented the performance of these remote monitoring capabilities during the commissioning of the protective relaying and prior to placing the station in service on April 29, 2014. Monitored and alarmed parameters included battery string voltage and charger string current. APC control center personnel monitored the status of all substation batteries and charging systems 24x7. In addition, APC trained field personnel to observe batteries and charging systems, as well as other equipment, as part of routine inspections upon entering any substation. The meter and annunciator trouble lights on the battery charger panel were easily observable by field personnel entering the substation throughout the duration of the issue. During the issue, the battery bank properly performed its intended functions. No harm is known to have occurred. SERC considered APC’s and its affiliates’ PRC-005-1.1b R2 compliance history in determining the disposition track. APC’s and its affiliates’ relevant prior noncompliance with PRC-005-1.1b R2 includes: NERC Violation IDs SERC2012010332, SERC200900258, SERC200900282, SERC200900301, SERC200800237, SERC2013012138, SERC200800240, SERC200800245, SERC200900259, SERC2012009778, SERC200800151, SERC200800238, SERC2013012373, SERC200800236, and SERC200800239. APC completed the mitigating actions for all previous issues more than three years prior to the instant issue with the exception of SERC2012010332. The Mitigation Plan for SERC2012010332 addresses the omission of six Farley Nuclear Plant Protection System batteries and did not address the cause of the instant issue. APC’s affiliate Gulf Power completed the mitigating actions for all previous issues more than three years prior to the instant issue with the exception of SERC2012009778 The Mitigation Plan for SERC2012009778 addresses six spare relays and did not address the cause of the instant issue. APC’s affiliate Southern Power Company completed the mitigating actions for all previous issues more than three years prior with the exception of SERC2013012138 and SERC2013012373, both of which Southern Power Company completed in 2013. In SERC2013012138, APC’s affiliate Georgia Power Company failed to document that it maintained and tested ten of its 26,589 (.038%) Protection System devices within defined intervals. The Mitigation Plan for this issue did not address the cause of the instant issue. The mitigation included adding batteries to a database and procedure revisions to prevent recurrence. In SERC2013012373, APC’s affiliate Mississippi Power Company failed to test two of its 3,843 Protection System devices (0.052%) within the defined interval. The Mitigation Plan for this issue did not address the cause of the instant issue. The mitigation addressed an application long file error and would not have prevented the instant issue. SERC determined that APC’s PRC-005-1.1b R2 compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, APC conducted the PDI for the battery. To mitigate this issue, APC will complete the following mitigation activities by July 29, 2016: 1) create queries against the project planning database which will identify new BES equipment to be installed. This will allow the maintenance organization to populate inspection due dates in advance of construction activities starting, thereby assuring that due dates are populated for the commissioning of new BES equipment; and 2) educate transmission construction to set the default maintenance interval for all batteries to four months maximum instead of the existing six month default as a safeguard against the possibility of batteries not being set to the proper interval.
2016-06-29 | SERC Reliability Corporation (SERC) | Southeastern Power Administration (SEPA) | NCR00070 | SERC2016015680 | BAL-005-0.2b | R8 | On April 25, 2016, SEPA submitted a Self-Report stating that, as a Balancing Authority, it had an issue of BAL-005-0.2b R8. SEPA failed to ensure that data acquisition for and calculation of Area Control Error (ACE) occurred at least every six seconds. In June 2013, during an Energy Management System (EMS) software update, SEPA inadvertently changed the interval for the calculation of ACE from a four-second interval to a ten-second interval. On April 19, 2016, SEPA identified that the calculation of ACE for its control area was occurring on a ten-second interval instead of at least every six seconds. SEPA identified the issue when it submitted data to NERC required for the implementation of BAL-003-1 Frequency Response and Frequency Bias Setting. SEPA received follow up questions regarding the data, and discovered that it had inadvertently programmed the EMS ACE calculation to occur on ten-second intervals. This issue lasted from June 1, 2013, when SEPA programmed the EMS update with a ten-second ACE calculation interval, until April 19, 2016, when SEPA reprogrammed the EMS update with a four-second ACE calculation interval. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SEPA calculating the ACE at ten-second intervals instead of six-second intervals could result in SEPA being slower to react to changing system conditions. However, while the interval was improper, the longer interval did not introduce an evident error in SEPA’s ACE calculation and thereby did not jeopardize reliability. In addition, SEPA did not follow real time instantaneous load changes. SEPA was a partial requirements power supplier that satisfied its portion of customer’s power requirements by dispatching generation from the Corps of Engineers hydroelectric facilities to meet the customer’s hourly block schedules. SEPA’s Balancing Area consists of three generation switchyards with 1446 MV normal operating capacity. No harm is known to have occurred. SERC considered SEPA’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SEPA: 1) changed the ACE calculation setting on the EMS to a four-second interval; 2) amended its internal control process to establish an internal working group that will work in conjunction with staff and contractors at times when changes to the EMS system are required. When such changes to the system are required, the internal working group will review proposed modifications prior to implementation and will participate in the product delivery team in order to provide information, guidance and assistance as appropriate. The internal working group consists of individuals from the power resources team including a lead system operator and the assistant administrator; and 3) provided additional training to staff members that are primarily responsible for maintaining and updating the EMS.
2016-06-29 | SERC Reliability Corporation (SERC) | Southern Power Company (SoPC) | NCR01322 | SERC2015015116 | PRC-005-1.1b | R2; R2.1 | On July 27, 2015, SoPC submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. SoPC failed to conduct DC control circuitry trip tests within the defined interval at a single site. On July 2, 2015, during a review of test records in advance of the 2015 SERC audit, SoPC discovered that it incorrectly logged the testing year for DC control circuitry tests conducted at Plant Rowan. SoPC performed the tests November 3, 2008 through November 10, 2008, but incorrectly recorded 2009 as the testing year in the record spreadsheet. The error resulted in scheduling the next test in calendar year 2015 rather than calendar year 2014. SoPC's documented methodology for Protection System maintenance and testing specifies a test interval of six calendar years for the Rowan DC control circuitry. SoPC should have completed the next test on or before December 31, 2014. SERC selected approximately 25% of the inventory of the SoPC Protection System devices for an extent of condition assessment. SERC reviewed the SoPC’s Protection System inventory spreadsheet and did not identify additional instances of non-compliance. SERC determined that SoPC did not perform maintenance and testing within the defined interval for one of 44 DC control circuits (2.27%) reviewed. In total, SoPC could not provide evidence that it tested one of 748 (0.13%) Protection System devices within the defined interval. The cause of the issue was a human performance error. SoPC incorrectly documented the test completion year as 2009 when it had actually completed testing in 2008. This issue lasted from January 1, 2015, when SoPC missed the testing interval, until November 3, 2015, when SoPC tested the DC control circuitry. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SoPC’s failure to perform the maintenance and testing of the Plan Rowan DC control circuitry within the defined interval could lead to a loss of generation from Plant Rowan. However, since the 420 MWs of generation from Plant Rowan is included in the Southern Power Pool, contingency reserves would be available from Southern Company’s generation resources to meet any loss of generation from Plant Rowan with minimal impact to Area Control Error. In addition, this issue potentially affects approximately only 420 MWs of SoPC's 9,000 MWs (4.67%) of generation. While alarming is not available, there is reasonable assurance that the DC control circuitry would function properly when called upon as evidenced by nine protective relay operations occurring since the last testing of the DC control circuitry at Plant Rowan. SoPC conducted an analysis and determined that DC control circuitry did not contribute to any relay mis-operations. Generation units depend on the DC control circuitry for normal unit startups and shutdown, none of which experienced issues since the last test in 2008. No harm is known to have occurred. SERC considered SoPC and its affiliates’ PRC-005-1.1b R2 compliance history in determining the disposition track. SoPC and its affiliates’ relevant prior noncompliance with PRC-005-1.1b R2 includes: NERC Violation IDs SERC2012010332, SERC200900258, SERC200900282, SERC200900301, SERC200800237, SERC2013012138, SERC200800240, SERC200800245, SERC200900259, SERC2012009778, SERC200800151, SERC200800238, SERC2013012373, SERC200800236, and SERC200800239. SERC determined that SoPC and its affiliates’ PRC-005-1.1b R2 compliance history should not serve as a basis for applying a penalty. SoPC and its affiliates completed the mitigating actions for all prior noncompliance more than three years before the start of the instant violation, with the exception of SERC2013012138 and SERC2013012373, both of which SoPC completed in 2013. In SERC2013012138, SoPC’s affiliate Georgia Power Company failed to document that it maintained and tested ten of its 26,589 (.038%) Protection System devices within defined intervals. In SERC2013012373, SoPC’s affiliate Mississippi Power Company failed to test two of its 3,843 (0.052%) Protection System devices within the defined interval. The Mitigation Plans for those issues did not address the cause of the instant issue. | To mitigate this issue, SoPC: 1) completed the testing of the DC control circuitry (trip checks) at Plant Rowan; and 2) entered the correct date into the maintenance tracking system to calculate an accurate date for the next scheduled test. To mitigate this issue, SoPC will complete the following mitigation activities by August 31, 2016: 1) assess Southern Company’s operating companies for PRC-005 compliance vulnerabilities similar to that experienced at SoPC with the entry of an incorrect date into the maintenance tracking spreadsheet; and 2) add an internal control for annual review of changes to Southern Company’s generation PRC-005 test records to verify the actual calendar year date of work completion matches the field service report date.
2016-06-29 | Texas Reliability Entity (Texas RE) | CenterPoint Energy Houston Electric, LLC (CNP) | NCR04028 | TRE2016015542 | FAC-009-1 | R1 | During a Compliance Audit conducted from January 11, 2016 through February 18, 2016, Texas RE determined that CNP, as a Transmission Owner, had an issue with FAC-009-1 R1. Specifically, CNP failed to establish Facility Ratings for one of its Facilities in a manner consistent with its associated Facility Ratings methodology or documentation for determining its Facility Ratings. Texas RE subsequently determined that the duration of the issue was from June 2, 2010 until January 20, 2016. Accordingly, Texas RE determined that CNP had an issue with FAC-009-1 R1 from June 2, 2010 until December 31, 2012, when that Standard was retired. CNP then had an issue with FAC-008-3 R6 from January 1, 2013 until January 20, 2016. Texas RE further determined that, for purposes of this issue, there was no substantive change in CNP’s compliance obligations under the two applicable Standards. On June 2, 2010, CNP replaced a failed 600 MVA-rated autotransformer (ATI) with an 800 MVA-rated ATI as part of unplanned maintenance activities at a CNP substation. The failed 600 MVA ATI had constituted the Most Limiting Series Element (MLSE) at the substation facility in question. Based on this fact, CNP personnel assumed that the new 800 MVA ATI likewise served as the substation facility’s MLSE. Accordingly, CNP personnel assigned the substation a new 800 MVA Facility Rating based on the rating of the newly installed 800 MVA ATI. In doing so, however, CNP personnel did not recognize that two switches in series with the ATI possessed 717 MVA ratings and, therefore, constituted the new MLSEs for the substation facility. As such, CNP should have assigned the substation facility a 717 MVA Facility Rating instead of the 800 MVA rating actually assigned. The root cause of this issue was that CNP did not have a documented process in place to review and verify Facility Ratings following unplanned maintenance projects. Texas RE determined the issue duration to be from June 2, 2010, when CNP assigned the incorrect Facility Rating for the new autotransformer at the substation facility in question, until January 20, 2016, when CNP corrected the Facility Rating in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the current issue involved only a single unplanned project. Second, multiple contingency analyses established that the substation facility would not exceed its proper emergency rating even under extreme, multiple contingency events. In fact, throughout the period in which CNP was using an incorrect Facility Rating, the actual load at the substation facility never exceeded 500 MVA. Finally, the substation facility at issue was equipped with alarms that would be triggered before the substation exceeded its 788 MVA emergency rating, alerting CNP personnel to loading issues and allowing them to take appropriate actions. No harm is known to have occurred. Texas RE considered CNP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CNP: 1) corrected the Facility Ratings and communicated the revised ratings to CNP’s Reliability Coordinator; 2) updated its processes to include provisions for reviewing, modifying, and communicating Facility Ratings following unplanned projects; and 3) provided training to its Substation Engineering, Standards and Materials, Transmission Planning, System Protection, and Transmission Engineering departments to reinforce the unplanned project ratings review process, the associated MLSE update process, and the individual group roles. Texas RE has verified the completion of all mitigation activity.
2016-06-29 | Texas Reliability Entity (Texas RE) | Paris Generation, LP (PEC) | NCR04138 | TRE2016015672 | IRO-010-1a | R3 | During a Compliance Audit conducted from March 22, 2016 through April 18, 2016, Texas RE determined that PEC, as a Generator Operator, had an issue with IRO-010-1a R3. Specifically, PEC failed to provide its Reliability Coordinator (RC) with correct AVR status information as specified by the RC for two generation units at a PEC generation facility. The PEC generation facility in question is programmed so as to only operate with its AVRs in automatic or “online” mode unless a PEC operator provides an explicit manual override instruction. However, during the audit review period, PI data indicated two instances in which the AVRs for two units at the PEC facility changed status to manual or “offline” mode while those units were in operation and no manual override instruction had been issued. Rather than indicating an AVR status change, however, Texas RE determined that these changes reflected changes in the status of the PEC facility’s duct burners. Specifically, the purported AVR status changes in the telemetered data actually reflected instances in which the PEC facility’s duct burners were taken out of automatic mode and placed into manual mode to perform certain load adjustments. The root cause of this issue was that the PEC generation facility’s telemetry logic had been incorrectly programmed. Specifically, the PEC facility’s telemetered “AVR status tag” incorrectly reflected the duct burner status for two of the PEC facility’s generation units rather than their actual AVR status. Texas RE determined the issue duration to be from April 25, 2014, the day after the end date of the previous Compliance Audit, until April 6, 2016, when PEC reprogrammed the telemetry logic to correctly monitor the AVR status on the two generation units at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for four reasons. First, PEC uses a control system program that will only allow the plant to operate with the AVR in automatic or “online” mode in the absence of an explicit manual override instruction. Second, PEC has a number of other controls to ensure that the RC would be aware of any change in AVR status if it in fact occurred. Specifically, PEC conducts a daily conference call with its Qualified Scheduling Entity (the entity typically responsible for providing the actual notice to the RC within the Electric Reliability Council of Texas, Inc. (ERCOT) market) regarding the PEC facility’s AVR status. In addition, PEC has a process in place that requires PEC operators to notify its QSE within 30 minutes of any AVR status change. PEC operators are further instructed to notify PEC’s TOP of any AVR status change. Third, all other telemetry points in the deployment model correctly reflected the generation facility’s actual operational status. Finally, the two units at issue produce only approximately 160 MW, a relatively small amount of generation within the ERCOT footprint. No harm is known to have occurred. Texas RE considered PEC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PEC: 1) reprogrammed the telemetry logic for the two PEC units in question to correctly monitor their AVR status; 2) verified that the logic change had corrected the issue such that the telemetered data properly reflected the AVR status at the two units; and 3) compared all other telemetered data with the generation facility’s actual operational status to verify that there were no other logic programming issues and all information is being correctly read and conveyed.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | WECC2015015425 | VAR-STD-002b-1 | WR1 | On December 16, 2015, SCEC submitted a Self-Report stating that as a Generator Operator, it had a possible issue of noncompliance with VAR-STD-002b-1 WR1. Specifically, SCEC reported that on August 4, 2015, a technician noticed that the Human Machine Interface (HMI) screen on the McGrath peaker unit wasn’t displaying the status of its Power System Stabilizer (PSS) device. After further investigation, SCEC discovered that the PSS device had been miswired relative to the generator breaker status, and was only energized when the breaker was open and the unit was disconnected from the grid. On August 12, 2015, SCEC reviewed alarm activity records for four additional peaker units equipped with the same PSS device. Following this review, SCEC discovered that the PSS device on its Center peaker unit was missing one of the jumpers providing power to the PSS on/off circuit, and therefore was not operational. As concerns the Center unit, this issue began the first quarter of 2008, three months after the unit achieved commercial operation, and ended August 13, 2015 when SCEC installed the missing jumper wire and verified the device was functional. As concerns the McGrath unit, this issue began the first quarter of 2013, three months after the unit achieved commercial operation, and ended August 11, 2015 when SCEC corrected the wiring error and verified the device was functional. The root cause of this issue was installation of, and less than adequate detection of, miswired devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, SCEC failed to keep the PSS devices on two of its peaker units in service at all times. However, the devices were obtained directly from, and installed by the original equipment manufacturer (General Electric). Initial commissioning test results did not indicate a problem with either device because during testing the on/off mechanism is bypassed to facilitate injection of test signals. The status indicator on SCEC’s Supervisory Control System (SCS) showed the devices were enabled and functioning normally. Additionally, both generators in scope of this issue are peaking units and operate infrequently; each unit was only in service long enough to qualify for applicability under this Standard in roughly half the calendar quarters throughout the duration of the issue. The units operated for a combined 3,834 hours over an eight-year period (roughly 6% of the total operating time) and represent less than 2% of SCEC’s total generation. For these reasons, and because no harm was known to have occurred, this issue posed minimal risk to the reliability of the (BPS). SCEC does not have previous violations of this Standard and requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, SCEC: 1) corrected the wiring in both devices; 2) modified the status indicator in its SCS to reflect accurate indication of PSS status; 3) revised its testing procedure to include a step verifying the SCS PSS on/off status agrees with the HMI screen; 4) notified General Electric that the drawings and wiring were incorrect for the devices and requested changes to make the devices functional; and 5) informed peer user groups of both the discovery and remediation of this issue. The proposed completion date for the above-listed activities is June 30, 2016.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC2015014676 | PRC-001-1.1 | R1 | On March 2, 2015, WACM submitted a Self-Certification stating that as a Transmission Operator and Balancing Authority it had a possible issue of noncompliance with PRC-001-1.1 R1. Specifically, WACM reported that it failed to retain evidence that six of its system operators were familiar with the purpose and limitations of Protection System schemes applied in its area. This issue began January 1, 2014, the last date in which WACM could provide evidence that its system operators had reviewed information related to PRC-001 R1, and ended March 9, 2015, when all operators, supervisors and technical writers were tested on WACM’s formal Protection System training. The root cause of this issue was a combination of significant turnover and unrecognized requirement to provide familiarity with the protection schemes to all dispatchers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WACM failed to provide and/or document formal Protection System training over a period of roughly two years. In that timeframe, six new operators may not have completed the training, and therefore may not have been familiar with the purpose and limitations of Protection System schemes applied in WACM’s area. Such failure could have limited the situational awareness of WACM’s operators. However, this issue was limited to six operators. One of the operators had extensive power plant operating experience and another was a relay technician at another utility prior to working for WACM. All procedures related to the Protection System training were available and up-to-date throughout the duration of this issue, and WECC did not identify any circumstances in which a system operator failed to respond appropriately due to lack of training. Additionally, WACM employs at least four system operators in the control room at all times, limiting the likelihood that situational awareness was impaired during the period in question. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WACM does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WACM: 1) completed Protection System training for all employees in a position which requires a NERC System Operator certification; 2) required all operators, supervisors, and technical writers to review training material and pass a test for comprehension; and 3) now includes this training in its checklist for new operators in its training program, and will provide refresher material to current staff as needed. WECC verified that WACM completed mitigating activities.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | WECC2015014925 | VAR-001-1 | R4 | On May 18, 2015, WACM submitted a Self-Report stating that as a Transmission Operator (TOP) it had a possible issue of noncompliance with VAR-001-1 R4. Specifically, WACM reported that it failed to include tolerance bands and reference points in the voltage schedules provided to Generator Operators (GOPs) in its operating area. This issue began June 18, 2007, when the Standard became mandatory and enforceable to WACM, and ended December 9, 2014, when WACM reissued voltage schedules with all required information. The root cause of this issue was failure to recognize and include all necessary details in the voltage schedule as prescribed by the Requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WACM failed to specify tolerance bands and reference points in voltage schedules provided to GOPs. Omission of this information could limit the GOPs' ability to determine whether or when a voltage set point was out of tolerance. However, WACM monitors voltage levels and would likely have detected any unacceptable deviations. Additionally, all GOPs that weren’t excluded from this Requirement had voltage schedules specifying their operating set points, and the reference points could not be misunderstood because low and high side generator step-up transformer voltages are significantly+H4 different in every case. Further, no Cyber Assets or Critical Cyber Assets were affected by this issue. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WACM does not have previous violations of this Standard and requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, WACM: 1) distributed voltage schedules with all required information to the requisite GOPs; and 2) updated its procedures and revised its voltage schedule template to include tolerance bands and reference points to prevent recurrence. WECC verified that WACM completed mitigating activities.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2016015465 | PER-005-1 | R2 | On January 14, 2016, IID submitted a Self-Report stating that as a Balancing Authority (BA) and Transmission Operator (TOP), it had a possible issue of noncompliance with PER-005-1 R2. On September 9, 2015, following an internal review, IID discovered it had not performed the one-time verification of Generation Balancing and Interchange Operator (GBIO) tasks as required by IID’s training program for three of its Transmission Reliability Operators and four of its Generation Balancing and Interchange Operators. The review identified six instances in which none of the operators on shift had been subject to one-time verification prescribed by R2. This issue began August 29, 2013, the date of the first shift identified by the review, and ended November 18, 2014, when IID verified GBIO capabilities for all Shift Supervisors. The root cause of this issue was inadvertant oversight of one-time verification for previously certified legacy staff. This is IID's first issue of noncompliance with this requirement, was identified and reported timely, and posed minimal risk to the bulk power system (BPS). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, IID failed to verify GBIO-related tasks and capabilities for each of its System Operators. Failure to verify each System Operator’s capabilities as required by IID’s training program at least once could limit IID’s awareness of the individual and collective competencies of its staff. However, in each of the six instances identified in IID’s review, all operators were certified NERC System Operators, and at least one of the operators on shift was either GBIO-certified prior to implementation of the Standard (and overlooked for the one-time verification) or actively working towards certification. IID implemented effective controls to resolve this issue nearly one year prior to discovering it by verifying GBIO-related tasks for all relevant staff. IID initiated the internal review that identified this issue after participating in a WECC Outreach Forum for this Standard. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. IID does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, IID: 1) verified GBIO-related tasks and capabilities for all Shift Supervisors; 2) completed the one-time verification for all overlooked staff; and 3) reviewed its training program to verify circumstances that led to this issue a) did not reflect a broader problem with the program, and b) have been resolved and are unlikely to recur.
2016-06-29 | Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2015015394 | EOP-004-2 | R2 | On December 18, 2015, PGE submitted a Self-Report stating that as a Transmission Operator (TOP), it had a possible issue of noncompliance with EOP-004-2 R2. Specifically, PGE reported that following an internal review conducted in September 2015, it identified three instances in which it did not submit an event report after an event that met the designated “Transmission loss” event type threshold in Attachment 1 of EOP-004-2. This issue began May 9, 2014, 24 hours after an event resulted in the loss of eight Bulk Electric System elements, and ended October 19, 2015, when PGE reported all three events identified during its review. The root cause of this issue was less than adequate documentation - PGE’s system operators did not recognize the three events in scope as reportable because the “Transmission loss” event type was inadvertently omitted from their operation procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, PGE failed to submit an event report following three events which met the “Transmission loss” Threshold for Reporting in Attachment 1 of EOP-004-2. Such failure could limit NERC’s and/or other organizations’ situational awareness of events and delay mitigating or preventative measures. The root cause of this issue was less than adequate documentation. PGE’s system operators did not recognize the three events in scope as reportable because the “Transmission loss” event type was inadvertently omitted from their operation procedure. However, although the operation procedure did not include reporting criterion for “Transmission loss”, criteria for all event types was included in PGE’s Operating Plan (in accordance with R1). Upon discovery, PGE conducted an internal review to determine the full scope of this issue. PGE identified all applicable events and submitted requisite event reports within weeks of the discovery. All three events were assessed as Category 1a events. Based on this information, and because no harm is known to have occurred from the failure to report, this issue posed minimal risk to the reliability of the BPS. PGE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PGE: 1) submitted event reports for all events in scope of this issue; 2) revised its operation procedure and required all operators to review the revised procedure prior to beginning their next shift; and 3) reviewed and discussed this issue in three internal compliance meetings.
2016-05-31 | Midwest Reliability Organization (MRO) | Benson Power, LLC (BEN) | NCR11300 | MRO2015015133 | VAR-002-1.1b | R2 | On March 25, 2015, BEN submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-1.1b R2. Specifically, BEN was not following its assigned voltage schedule. The cause of this issue was a lack of NERC compliance knowledge by its Control Room Operators, who were unaware of BEN's assigned Voltage Schedule. This noncompliance began under BEN's previous ownership. The issue began on December 20, 2012, the date that BEN was required to be compliant the Standard, and ended on March 20, 2015, when BEN completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). BEN's deviation from its assigned Voltage Schedule was small enough that it was not detected by its Transmission Operator. Further, the risk is further reduced because BEN has a low potential for causing a BPS disturbance. Specifically, it has only one generator with a 73.3 MVA nameplate rating, it is not a blackstart unit, and it is not associated with a Special Protection System or a Interconnection Reliability Operating Limit (IROL) flowgate. No harm is known to have occurred. This is BEN's first instance of noncompliance with VAR-002-1.1b R2. | To mitigate this issue, BEN: 1) updated its procedures to require operators to check the voltage levels at the beginning of each shift and throughout to shift to verify that voltage levels are within the appropriate range; and 2) added alarming to alert the operators if the voltage falls outside the allowable voltage band (13.6 kV to 13.92 kV). BEN stated that mitigating activities were complete as of March 20, 2015.
2016-05-31 | Midwest Reliability Organization (MRO) | Western Area Power Administration - Upper Great Plains East (WAPA) | NCR01036 | MRO2015015305 | BAL-003-0.1b | R2 | On July 28, 2015, WAPA submitted a Self-Report stating that, as a Balancing Authority, it had an issue of BAL-003-0.1b R2. Specifically, during the process of setting its 2015 Frequency Bias Setting for WAPA's Automatic Generation Control (AGC), WAPA discovered that it failed to adjust its 2014 Frequency Bias Setting. WAPA's 2014 Frequency Bias Setting was set to -37MW/.01 Hz, when it should have been set to -44MW/.01 Hz. The cause of this issue was WAPA's failure to have adequate internal controls in place to verify that the Frequency Bias Setting had been properly adjusted. This issue started on April 1, 2014, when WAPA had an incorrect Frequency Bias Setting, and ended on March 17, 2015, when WAPA applied the 2015 Frequency Bias Setting. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. By having a Frequency Bias that was less negative than the required setting, WAPA's AGC could potentially respond less than required to contingency events involving frequency excursions. A Frequency Bias Setting ensures generation under WAPA’s control does not withdraw primary frequency response provided by governor action in response to a frequency disturbance on the Eastern Interconnection. However, in this case, the risk was minimal because a deviation of 7MW/.01 Hz is unlikely to adversely affect the frequency response of generation in the Eastern Interconnection during an event involving a frequency excursion. Further, a registered entity that is under-biased presents less risk as the Eastern Interconnection is currently over-biased due to the Balancing Authorities' typical use of 1% of peak load to calculate Frequency Bias Setting instead of deriving the Natural Response of the system. Finally, there were no frequency excursion events reported on the MRO system during the period of noncompliance. No harm is known to have occurred. This is WAPA's first issue with BAL-003-0.1b R2. | To mitigate this issue, WAPA: 1) updated the Frequency Bias Setting to -44MW/0.1 Hz; 2) added internal controls related to changes in Frequency Bias Settings, specifically, changes to the setting will be made by the on-duty System Operator, recorded in the electronic Dispatch Log, and screenshots of the setting will document that the change was made; 3) added additional documentation requirements regarding the Frequency Bias Settings. specifically, the Operations Specialist will document the implemented settings, and send this report to WAPA's Generation Control Manager for validation and WAPA's Compliance Manager for review; and 4) has transferred its Balancing Authority responsibility's to another Registered Entity and is currently in the process of de-registering as a Balancing Authority. WAPA stated that mitigating activities were complete as of April 5, 2016.
2016-05-31 | Northeast Power Coordinating Council (NPCC) | Materials Innovation and Recycling Authority (MIRA) | NCR07045 | NPCC2016015576 | PRC-002-NPCC-01 | R1; R1.1; R1.2 | On February 23, 2016, MIRA submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-002-NPCC-01, R1.1 and R1.2. The issue is related to the 50% implementation milestone of October 20, 2013 for installation of Sequence of Event (SOE) recording capability dictated by PRC-002-NPCC-01 R1. MIRA initially believed that only one of its two facilities met the applicability requirements for installation of SOE equipment, therefore full implementation would not be necessary until October 20, 2015 as stated in the implementation plan. However, subsequent follow up discussions with NPCC's Standards group in December 2013 determined that both of MIRA's facilities would require the installation of SOE recording equipment. MIRA began the process for procurement and installation of the SOE devices for both facilities, however the 50% implementation milestone had already passed, therefore MIRA was noncompliant starting on October 20, 2013. SOE recorder installation and commissioning was completed at one of MIRA's facilities on January 15, 2015, bringing MIRA back into compliance with the PRC-002-NPCC-01 Implementation schedule. MIRA completed SOE recorder installation at both facilities on March 26, 2015, meeting the 100% completion milestone. The root cause of this issue was an initial misinterpretation of PRC-002-NPCC-01 by MIRA, which led them to believe that installation of SOE recorders would not need to be completed until October 20, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The actual operation and reliability of the Bulk Electric System (BES) elements would not be affected by the delayed installation of the SOE recorders. The data from the recorders is used for events analysis after a system event occurs that affects the BES elements. Additionally, MIRA experienced no system events that would have utilized the data captured by the SOE recorders during the time that they were lacking SOE recording capability on their facilities. No harm is known to have occurred. NPCC considered MIRA's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MIRA: 1) Completed installation of SOE recorders at one of its facilities on January 15, 2015 to meet the 50% implementation milestone; and 2) Provided training to all personnel involved in day to day compliance to promote a better understanding of compliance guidelines, milestones, and implementation plans. NPCC has verified the completion of all mitigation activity.
2016-05-31 | Northeast Power Coordinating Council (NPCC) | Materials Innovation and Recycling Authority (MIRA) | NCR07045 | NPCC2016015577 | PRC-002-NPCC-01 | R14. | On February 23, 2016, MIRA submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-002-NPCC-01, R14. In accordance with the implementation plan for PRC-002-NPCC-01, MIRA installed and commissioned sequence of events (SOE) recorders on its two facilities on March 26, 2015. In January 2016, MIRA discovered that it did not have a formally documented maintenance and testing program for its SOE recorders as required by PRC-002-NPCC-01 R14. The issue duration was from January 15, 2015, when MIRA installed the first of the SOE recorders at its facilities, to January 19, 2016 when the maintenance and testing program was formally implemented. The root cause of this issue was MIRA's use of the self-monitoring capabilities of the SOE devices in place of a formal maintenance and testing program. MIRA still made periodic checks of the devices since the commissioning, however these checks were not documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The actual operation and reliability of the Bulk Electric System (BES) elements would not be affected by the lack of a maintenance and testing program for the SOE recorders. The SOE devices installed have self-testing capabilities that perform internal diagnostics, time synchronization checks, and other routine verifications. Additionally, undocumented periodic checks were made to verify proper operation of all SOE recording devices via the status lights located on the front panel. Additionally, MIRA experienced no system events that would have utilized the data captured by the SOE recorders during the time that they were lacking SOE recording capability on their facilities. No harm is known to have occurred. NPCC considered MIRA's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MIRA: 1) Developed a formal maintenance and testing program for the SOE recorders; and 2) Provided training to all personnel involved in day to day compliance to promote a better understanding of compliance guidelines, milestones, and implementation plans. NPCC has verified the completion of all mitigation activity.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2014014419 | EOP-008-1 | R6 | On October 24, 2014, IPL submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Operator, it was in violation of TOP-006-2 R5. During a thunderstorm on August 22, 2014, a substation breaker operated causing a voltage sag to occur on a 13 kV bus at 4:48 a.m. IPL’s operation center is served from an adjacent circuit on the same 13 kV bus, which experienced low voltage and caused a 208 v breaker to operate. This breaker served the 208 v feed to the UPS that supports the primary Transmission Operations Control Center (TOCC) and ancillary equipment. Once the 208 v breaker operated, the Uninterruptible Power Supply (UPS) system automatically activated as designed. However, the automated alert notification, which was intended to signal appropriate IPL personnel to reset the breaker, failed to operate. Because no one reset the breaker, the TOCC continued to operate on the UPS. Approximately 2.5 hours later, the UPS batteries depleted causing a loss of power to the communications equipment. At 7:14 a.m., the TOCC began losing communication capability with some Remote Terminal Unit (RTU) data. TOCC operators contacted operations technology support staff at 7:16 a.m. after they determined that the issue was more than one isolated RTU failure. At 7:20 a.m., IPL implemented its Loss of Control Center Plan, which included (a) sending an operator to the backup TOCC; (b) requesting that MISO and interconnected transmission operators monitor the IPL system; (c) having field personnel manually monitor and control significant substations; (d) engaging the IPL System Energy Coordination operators to monitor generation; (e) notifying appropriate leadership of the situation; and, (f) involving relevant personnel to resolve the identified root cause by restoring power to the UPS. At 7:40 a.m., IPL switched to its backup Energy Control System at the backup TOCC. However, consistent communication with some RTUs was unsuccessful. Subsequently, IPL restored UPS power to the primary control center communication equipment, and TOCC staff switched back to the primary Energy Control system (ECS) and full system communication capability was restored at 9:30 a.m. The root cause of this noncompliance was the failure of the automated alert notification intended to signal appropriate IPL personnel to reset the breaker. The automated alert notification system was email-based. The recipients on the email notification distribution list were not configured to receive email from external senders, which was how the UPS system was viewed by the email system. This failure relates to the management practice areas of grid operations and reliability quality management. The facts described above constitute a noncompliance with EOP-008-1 R6 because the limitation on IPL's communication capability affected both the primary ECS as well as the backup ECS. The duration of the noncompliance is from August 22, 2014, at 7:14 a.m., when IPL began losing communication capability, to 9:30 a.m., the time when IPL restored full system communications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although IPL experienced limited situation awareness for only approximately 2 hours and 15 minutes. Second, IPL effectively executed its emergency plan, which minimized any potential harm by, among other things, having MISO and interconnected transmission operators monitoring its system with field personnel manually monitoring and controlling significant substations. Third, IPL’s system is situated such that IPL’s four interconnected Transmission Operators and MISO have the ability to monitor IPL’s entire system. This is IPL's first instance of noncompliance with EOP-008 R6. | To mitigate this issue, IPL: 1) improved its UPS Alarm Notification System by: (a) reviewing and changing the email configuration to enable automated notifications; (b) initiating regular testing of the email notification; and, (c) installing a hardwired alarm to connect to the RTU at the primary control center and tie directly to the ECS; 2) reviewed and improved documentation including: (a) updating UPS electrical drawings and posting them in the UPS electrical room; (b) updating Operations Technology (OT) On-Call procedures and TOCC operating instructions; (c) updating UPS and throw-over switch operating instructions for Distribution Operations Control Center (DOCC); and (d) training OT, DOCC, and TOCC staff on new UPS and throw-over switch instructions; 3) improved the robustness of its Internet IP Network for SCADA communications by: (a) completing an IP network architecture review; (b) addressing a short-term solution by installing Layer 3 switches at Northeast Substation, Morris Street and Arlington facilities; (c) developing a long-term solution through the implementation of a four-year plan designed to improve the security of IPL’s Internet IP Network by (i) fortifying the security of the connection between the communications network and the ECS network; (ii) increasing the efficiency and simplicity of the communications system by deploying multiprotocol label switching; and (iii) developing a private, wireless solution to expand the footprint of the OT network; 4) reassessed the design of the UPS sources by completing the design and providing recommendations for the primary and alternative sources to the UPS; 5) selected a vendor to implement the recommended UPS solution; and 6) completed the implementation of recommended UPS solution.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2014014446 | TOP-006-2 | R1 | OOn October 24, 2014, IPL submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Operator, it was in violation of TOP-006-2 R5. During a thunderstorm on August 22, 2014, a substation breaker operated causing a voltage sag to occur on a 13 kV bus at 4:48 a.m. IPL’s operation center is served from an adjacent circuit on the same 13 kV bus, which experienced low voltage and caused a 208 v breaker to operate. This breaker served the 208 v feed to the UPS that supports the primary Transmission Operations Control Center (TOCC) and ancillary equipment. Once the 208 v breaker operated, the Uninterruptible Power Supply (UPS) system automatically activated as designed. However, the automated alert notification, which was intended to signal appropriate IPL personnel to reset the breaker, failed to operate. Because no one reset the breaker, the TOCC continued to operate on the UPS. Approximately 2.5 hours later, the UPS batteries depleted causing a loss of power to the communications equipment. At 7:14 a.m., the TOCC began losing communication capability with some Remote Terminal Unit (RTU) data. TOCC operators contacted operations technology support staff at 7:16 a.m. after they determined that the issue was more than one isolated RTU failure. At 7:20 a.m., IPL implemented its Loss of Control Center Plan, which included (a) sending an operator to the backup TOCC; (b) requesting that MISO and interconnected transmission operators monitor the IPL system; (c) having field personnel manually monitor and control significant substations; (d) engaging the IPL System Energy Coordination operators to monitor generation; (e) notifying appropriate leadership of the situation; and, (f) involving relevant personnel to resolve the identified root cause by restoring power to the UPS. At 7:40 a.m., IPL switched to its backup Energy Control System at the backup TOCC. However, consistent communication with some RTUs was unsuccessful. Subsequently, IPL restored UPS power to the primary control center communication equipment, and TOCC staff switched back to the primary Energy Control system (ECS) and full system communication capability was restored at 9:30 a.m. The root cause of this noncompliance was the failure of the automated alert notification intended to signal appropriate IPL personnel to reset the breaker. The automated alert notification system was email based. The recipients on the email notification distribution list were not configured to receive email from external senders, which was how the UPS system was viewed by the email system. This failure relates to the management practice areas of grid operations and reliability quality management. The facts described above constitute noncompliance with TOP-006-2 R1 because IPL experienced limited system communication capability, meaning that IPL was unable to know the status of all generation and transmission resources available for use. The duration of the noncompliance is from August 22, 2014, at 7:14 a.m., when IPL began losing system communication capability, to 9:30 a.m., the time when IPL restored full system communications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although IPL experienced limited situation awareness for only approximately 2 hours and 15 minutes. Second, IPL effectively executed its emergency plan, which minimized any potential harm by, among other things, having MISO and interconnected transmission operators monitoring its system with field personnel manually monitoring and controlling significant substations. Third, IPL’s system is situated such that IPL’s four interconnected Transmission Operators and MISO have the ability to monitor IPL’s entire system. ReliabilityFirst determined that IPL's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, IPL: 1) improved its UPS Alarm Notification System by: (a) reviewing and changing the email configuration to enable automated notifications; (b) initiating regular testing of the email notification; and, (c) installing a hardwired alarm to connect to the RTU at the primary control center and tie directly to the ECS; 2) reviewed and improved documentation including: (a) updating UPS electrical drawings and posting them in the UPS electrical room; (b) updating Operations Technology (OT) On-Call procedures and TOCC operating instructions; (c) updating UPS and throw-over switch operating instructions for Distribution Operations Control Center (DOCC); and (d) training OT, DOCC, and TOCC staff on new UPS and throw-over switch instructions; 3) reassessed the design of the UPS sources by completing the design and providing recommendations for the primary and alternative sources to the UPS; 4) selected a vendor to implement the recommended UPS solution; and 5) completed the implementation of recommended UPS solution.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2014014447 | TOP-006-2 | R2 | On October 24, 2014, IPL submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Operator, it was in violation of TOP-006-2 R5. During a thunderstorm on August 22, 2014, a substation breaker operated causing a voltage sag to occur on a 13 kV bus at 4:48 a.m. IPL’s operation center is served from an adjacent circuit on the same 13 kV bus, which experienced low voltage and caused a 208 v breaker to operate. This breaker served the 208 v feed to the UPS that supports the primary Transmission Operations Control Center (TOCC) and ancillary equipment. Once the 208 v breaker operated, the Uninterruptible Power Supply (UPS) system automatically activated as designed. However, the automated alert notification, which was intended to signal appropriate IPL personnel to reset the breaker, failed to operate. Because no one reset the breaker, the TOCC continued to operate on the UPS. Approximately 2.5 hours later, the UPS batteries depleted causing a loss of power to the communications equipment. At 7:14 a.m., the TOCC began losing communication capability with some Remote Terminal Unit (RTU) data. TOCC operators contacted operations technology support staff at 7:16 a.m. after they determined that the issue was more than one isolated RTU failure. At 7:20 a.m., IPL implemented its Loss of Control Center Plan, which included (a) sending an operator to the backup TOCC; (b) requesting that MISO and interconnected transmission operators monitor the IPL system; (c) having field personnel manually monitor and control significant substations; (d) engaging the IPL System Energy Coordination operators to monitor generation; (e) notifying appropriate leadership of the situation; and, (f) involving relevant personnel to resolve the identified root cause by restoring power to the UPS. At 7:40 a.m., IPL switched to its backup Energy Control System at the backup TOCC. However, consistent communication with some RTUs was unsuccessful. Subsequently, IPL restored UPS power to the primary control center communication equipment, and TOCC staff switched back to the primary Energy Control system (ECS) and full system communication capability was restored at 9:30 a.m. The root cause of this noncompliance was the failure of the automated alert notification intended to signal appropriate IPL personnel to reset the breaker. The automated alert notification system was email based. The recipients on the email notification distribution list were not configured to receive email from external senders, which was how the UPS system was viewed by the email system. This failure relates to the management practice areas of grid operations and reliability quality management. The facts described above constitute noncompliance with TOP-006-2 R2 because IPL experienced limited system communication capability, meaning that IPL was unable to monitor applicable transmission line status, real and reactive power flows, voltage, load-tap-changer settings, and status of rotating and static reactive resources. The duration of the noncompliance is from August 22, 2014, at 7:14 a.m., when IPL began losing system communication capability, to 9:30 a.m., the time when IPL restored full system communications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although IPL experienced limited situation awareness for only approximately 2 hours and 15 minutes. Second, IPL effectively executed its emergency plan, which minimized any potential harm by, among other things, having MISO and interconnected transmission operators monitoring its system with field personnel manually monitoring and controlling significant substations. Third, IPL’s system is situated such that IPL’s four interconnected Transmission Operators and MISO have the ability to monitor IPL’s entire system. ReliabilityFirst determined that IPL's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, IPL: 1) improved its UPS Alarm Notification System by: (a) reviewing and changing the email configuration to enable automated notifications; (b) initiating regular testing of the email notification; and, (c) installing a hardwired alarm to connect to the RTU at the primary control center and tie directly to the ECS; 2) reviewed and improved documentation including: (a) updating UPS electrical drawings and posting them in the UPS electrical room; (b) updating Operations Technology (OT) On-Call procedures and TOCC operating instructions; (c) updating UPS and throw-over switch operating instructions for Distribution Operations Control Center (DOCC); and (d) training OT, DOCC, and TOCC staff on new UPS and throw-over switch instructions; 3) reassessed the design of the UPS sources by completing the design and providing recommendations for the primary and alternative sources to the UPS; 4) selected a vendor to implement the recommended UPS solution; and 5) completed the implementation of recommended UPS solution.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC2014014448 | TOP-006-2 | R5 | On October 24, 2014, IPL submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Operator, it was in violation of TOP-006-2 R5. During a thunderstorm on August 22, 2014, a substation breaker operated causing a voltage sag to occur on a 13 kV bus at 4:48 a.m. IPL’s operation center is served from an adjacent circuit on the same 13 kV bus, which experienced low voltage and caused a 208 v breaker to operate. This breaker served the 208 v feed to the UPS that supports the primary Transmission Operations Control Center (TOCC) and ancillary equipment. Once the 208 v breaker operated, the Uninterruptible Power Supply (UPS) system automatically activated as designed. However, the automated alert notification, which was intended to signal appropriate IPL personnel to reset the breaker, failed to operate. Because no one reset the breaker, the TOCC continued to operate on the UPS. Approximately 2.5 hours later, the UPS batteries depleted causing a loss of power to the communications equipment. At 7:14 a.m., the TOCC began losing communication capability with some Remote Terminal Unit (RTU) data. TOCC operators contacted operations technology support staff at 7:16 a.m. after they determined that the issue was more than one isolated RTU failure. At 7:20 a.m., IPL implemented its Loss of Control Center Plan, which included (a) sending an operator to the backup TOCC; (b) requesting that MISO and interconnected transmission operators monitor the IPL system; (c) having field personnel manually monitor and control significant substations; (d) engaging the IPL System Energy Coordination operators to monitor generation; (e) notifying appropriate leadership of the situation; and, (f) involving relevant personnel to resolve the identified root cause by restoring power to the UPS. At 7:40 a.m., IPL switched to its backup Energy Control System at the backup TOCC. However, consistent communication with some RTUs was unsuccessful. Subsequently, IPL restored UPS power to the primary control center communication equipment, and TOCC staff switched back to the primary Energy Control system (ECS) and full system communication capability was restored at 9:30 a.m. The root cause of this noncompliance was the failure of the automated alert notification intended to signal appropriate IPL personnel to reset the breaker. The automated alert notification system was email based. The recipients on the email notification distribution list were not configured to receive email from external senders, which was how the UPS system was viewed by the email system. This failure relates to the management practice areas of grid operations and reliability quality management. The facts described above constitute noncompliance with TOP-006-2 R5 because IPL experienced limited system communication capability, meaning that IPL was unable to use monitoring equipment to bring to the attention of operating personnel important deviations in operating conditions and to indicate, if appropriate, the need for corrective action. The duration of the noncompliance is from August 22, 2014, at 7:14 a.m., when IPL began losing system communication capability, to 9:30 a.m., the time when IPL restored full system communications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although IPL experienced limited situation awareness for only approximately 2 hours and 15 minutes. Second, IPL effectively executed its emergency plan, which minimized any potential harm by, among other things, having MISO and interconnected transmission operators monitoring its system with field personnel manually monitoring and controlling significant substations. Third, IPL’s system is situated such that IPL’s four interconnected Transmission Operators and MISO have the ability to monitor IPL’s entire system. ReliabilityFirst determined that IPL's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, IPL: 1) improved its UPS Alarm Notification System by: (a) reviewing and changing the email configuration to enable automated notifications; (b) initiating regular testing of the email notification; and, (c) installing a hardwired alarm to connect to the RTU at the primary control center and tie directly to the ECS; 2) reviewed and improved documentation including: (a) updating UPS electrical drawings and posting them in the UPS electrical room; (b) updating Operations Technology (OT) On-Call procedures and TOCC operating instructions; (c) updating UPS and throw-over switch operating instructions for Distribution Operations Control Center (DOCC); and (d) training OT, DOCC, and TOCC staff on new UPS and throw-over switch instructions; 3) improved the robustness of its Internet IP Network for SCADA communications by: (a) completing an IP network architecture review; (b) addressing a short-term solution by installing Layer 3 switches at Northeast Substation, Morris Street and Arlington facilities; (c) developing a long-term solution through the implementation of a four-year plan designed to improve the security of IPL’s Internet IP Network by (i) fortifying the security of the connection between the communications network and the ECS network; (ii) increasing the efficiency and simplicity of the communications system by deploying multiprotocol label switching; and (iii) developing a private, wireless solution to expand the footprint of the OT network; 4) reassessed the design of the UPS sources by completing the design and providing recommendations for the primary and alternative sources to the UPS; 5) selected a vendor to implement the recommended UPS solution; and 6) completed the implementation of recommended UPS solution.
2016-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Ohio Valley Electric Corporation (OVEC) | NCR00857 | RFC2016015491 | EOP-004-2 | R3 | On January 26, 2016, OVEC submitted a Self-Report stating that, as a Balancing Authority, Generator Owner, Generator Operator, Transmission Owner, and Transmission Operator, it had an issue of EOP-004-2 R3. The OVEC Subject Matter Expert (SME) responsible for performing the calendar year validation of the contact information in OVEC’s Operating Plan did not validate all of the necessary contact information. (The contact information that was not updated in this noncompliance was for law enforcement. This includes everything from the contact information for the Adams County Sheriff’s Office to the Kentucky State Police. EOP-004 requires Registered Entities like OVEC to notify local law enforcement of certain events and disturbances. An example of a situation where OVEC would want to contact law enforcement would be if an individual broke into an OVEC substation and stole copper wire.) The SME was not aware that all of the law enforcement contacts listed in Attachment 1 to the Operating Plan were part of the Operating Plan and needed to be validated. Therefore the SME did not verify the contact information of all of the law enforcement contacts listed in the Operating Plan. This noncompliance implicates the management practice of workforce management and verification because the SME responsible for performing the calendar year validation of the contact information in the Operating Plan did not know that all of the law enforcement contacts listed in Attachment 1 were part of the Operating Plan and needed to be verified. The SME was ineffectively trained on what contact information in the Operating Plan needed to be verified in order to show compliance with EOP-004-2 R3. Additionally, the SME received automated reminders through Microsoft SharePoint informing him to perform the calendar year validation on time, but he failed to follow those reminders. Ineffective training was the root cause of this noncompliance. The duration of this noncompliance is from January 1, 2016, the date OVEC was required to show that it had performed the calendar year validation of all of the contact information listed in the Operating Plan, to February 2, 2016, the date OVEC finished performing the calendar year validation of all contact information listed in the Operating Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The contact information that was not validated was for entities that do not change contact information on a regular basis. The list was completely validated in 2014 with no changes made. OVEC also had no events to report during 2015. Lastly, OVEC performed the calendar year validation of all of the contact information listed in the Operating Plan only a little more than one month late. No harm is known to have occurred. This is OVEC's first instance of noncompliance with EOP-004 R3. | To mitigate this issue, OVEC: 1) coached the SME that is responsible for performing the calendar year validation of the contact information in the Operating Plan on the requirements of the Standard and that the annual validation of the law enforcement contacts in Attachment 1 were in fact part of the Operating Plan. This coaching also involved reminding the SME of the importance of reading and following the annual reminders that he had received through Microsoft SharePoint informing him to perform the calendar year validation on time; 2) retrained the SME’s back-up reviewers, which are two individuals in the OVEC Compliance Department, on the importance of making sure that the SME, or someone in Compliance, correctly completes the calendar year validation on time; 3) reviewed the contacts in the Operating Plan to gain awareness of all of the contacts listed; and 4) performed the calendar year validation of all contact information by revising and updating the information on February 2, 2016. ReliabilityFirst has verified the completion of all mitigation activity.
2016-05-31 | SERC Reliability Corporation (SERC) | Entergy Nuclear Palisades, LLC (Palisades) | NCR08052 | SERC2016015457 | FAC-003-3 | R3 | On January 11, 2016, Palisades submitted a Self-Report (via Entergy - Nuclear and an applicable MRRE agreement) that, as a Generator Owner (GO) it had an issue with FAC-003-3 R3 because it did not have strategies or procedures to explain the required level of vegetation management. During completion of the FAC-003-3 Vegetation Management Report for GOs, for the fourth quarter of 2015, Palisades determined that FAC-003-3 is applicable to the 345 kV overhead transmission line connecting the Palisades nuclear generating station to the interconnected transmission system. FAC-003-3 includes an exemption for lines less than 1 mile in length, but requires that these lines have a clear line of site from end to end. Although the line is less than 0.5 mile long, there is no clear line of sight from the generating station fence to the point of interconnection with the Transmission Owner (TO). Palisades performed annual inspections of the line and structures that included checking for excessive vegetation. However, the procedure governing that inspection did not explain what level of vegetation management was necessary. The procedure primarily stated that “excessive vegetation growth” should be addressed but did not define “excessive” in terms of line movement or vegetation growth rates. Palisades contacted the interconnected TO and confirmed that the TO had not performed vegetation related maintenance on the subject line. The issue lasted from January 1, 2015 when the Standard became mandatory and enforceable for GOs until January 26, 2016 when the procedure was revised to include the required strategy. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Inadequate vegetation control strategy could result in vegetation contact with the generator leads resulting in loss of generation and the potential for disturbances on the transmission system. However, the instant issue relates to documentation of vegetation management strategies rather than the actual practice of vegetation management. Palisades did conduct inspections during this time and identified no vegetation related issues for the applicable lines. No encroachments of the Minimum Vegetation Clearance Distance occurred. No momentary or sustained outages related to vegetation occurred and no harm is known to have occurred. SERC considered Palisades' compliance history and determined there were no relevant instances of noncompliance. SERC considered the relevant compliance history of the following affiliates of Palisades determined there were no relevant instances of noncompliance: Entergy (NCR01234), Entergy - Fossil & Hydroelectric Generation (NCRI I 167), Entergy Nuclear (NCR1 1166), Entergy Nuclear Fitzpatrick, LLC (NCR0707J), Entergy Nuclear Generation Company (NCR07072), Entergy Nuclear Indian Point 2, LLC (NCR07073), Entergy Nuclear Indian Point 3, LLC (NCR07074), Entergy Nuclear Palisades, LLC (NCR08052), and Entergy Nuclear Vermont Yankee, LLC (NCR07075). | To mitigate this issue, Palisades developed and implemented a preventive maintenance process to perform annual inspection which requires clearing of the right of way. SERC has verified the completion of all mitigation activity.
2016-05-31 | Texas Reliability Entity (Texas RE) | American Electric Power Service Corp as agent for AEP Texas North Co, AEP Texas Central Co, and Public Service of Oklahoma (AEP) | NCR04006 | TRE2015015416 | PRC-005-1.1b | R2; R2.1 | On December 22, 2015, AEP submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue with PRC-005-1.1b R2.1. Specifically, AEP did not have documentation that Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing Program (PSMP). During the duration of the issue here, AEP’s PSMP required periodic inspections of substation batteries and battery chargers at least every 90 days. In the current circumstances, AEP tested a newly installed substation battery and battery charger on September 18, 2014. Pursuant to AEP’s PSMP, therefore, AEP should have performed the next testing and maintenance activities on these devices by December 17, 2014. However, AEP did not actually perform the required inspection and testing until January 7, 2015, or 21 days after such inspection and testing was required. The root cause of this issue was that AEP personnel used the date AEP energized its substation rather than the date AEP actually installed the battery and battery charger as the initial “in service” date for the new battery and battery charger devices. In particular, AEP energized the substation on December 17, 2014, and AEP personnel recorded this as the “in service” date in AEP’s asset management database for purposes of establishing the start date for the required 90-day testing window. Texas RE determined the issue duration to be from December 18, 2014, the day after the battery and battery charger were due to be inspected, until January 7, 2015, when AEP actually inspected the battery and battery charger. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on several factors. First, the battery and battery charger at issue represent only 0.31% of the battery and battery chargers and 0.0075% of the total devices (2/26,599) in AEP’s PSMP. Second, the duration of the issue was short, lasting only 20 days. Finally, AEP did not identify any issues with the single battery and battery charger when it performed the required testing and inspection. No harm is known to have occurred. Compliance History with PRC-005 R2 for AEP (NCR01056, NCR00682, and NCR04006): On May 30, 2012, a Settlement Agreement covering PRC-005-1 R2 (SPP200900137, SPP201100449, RFC201000668, and TRE201100300) was filed with FERC under NP12-30-000. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation was that AEP did not test some of its relays. The root cause was that asset tracking database included incorrect testing dates, relays not being properly inventoried, and trip testing paths that were lacking sufficient data. This issue was mitigated by requiring technicians to verify completeness of database entries against the equipment at substations and defining, in a guideline, the relays within the system to be included in the asset tracking database. On October 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE2012010184, RFC2012010261, and SPP2012010129) was filed with FERC under NP14-4-000. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. In other regions (RF and SPP), AEP Generation did not perform testing on batteries. Mitigation around that issue included development and training for generation plant staff and reviewing generation batteries in RF and SPP regions to identify all batteries. Compliance History with PRC-005 R2 for AEP's affiliate, ETT (NCR10211): On March 31, 2014, a Settlement Agreement covering PRC-005-1 R2 (TRE2012011136) was filed with FERC under NP14-35-000. On April 30, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. Texas RE considered AEP's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the root causes of AEP’s prior violations of PRC-005 R2.1 are distinguishable from the instant issue. The previous instances generally involved AEP’s failure to properly track existing devices within its PSMP. In contrast, the current issue involved the incorrect entry of “in service” dates for two new devices into AEP’s PSMP. | To mitigate this issue, AEP will complete the following mitigation activities by March 31, 2017: 1) develop an Internal Spot Check Data Review Policy & Procedure for new assets; 2) create a report within the asset management database to identify new PRC-005 applicable assets that are added to the database and correlate device data within the database and actual device status in the field; 3) develop and begin the implementation of a Capital Checklist to ensure that new devices are appropriately entered into AEP’s asset management database; 4) perform an assessment on existing training curriculum to ensure quality and focus of compliance responsibilities associated with battery/charger maintenance; 5) perform an assessment of station assets/labor resources; and 6) provide examples of completed internal spot checks to front-line employees. AEP needs until March 31, 2017 to complete its mitigation actions in order to assess station assets and labor resources that comprise a large number of assets and protection system devices. Additionally, AEP will provide examples of completed internal spot checks to front-line employees in the first quarter of 2017.
2016-05-31 | Texas Reliability Entity (Texas RE) | Desert Sky Wind Farm, LP (Desert Sky) | NCR04150 | TRE2016015454 | PRC-005-1.1b | R2; R2.1 | On January 11, 2016, American Electric Power Service Corp as agent for Desert Sky submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-1.1b R2.1. Specifically, Desert Sky did not have documentation that Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing Program (PSMP). During the duration of the issue here, Desert Sky’s PSMP required semi-annual battery inspections. The Desert Sky PSMP defines “semi-annual” as one inspection during the first six months of a calendar year and one inspection during the second six months of a calendar year. In the current circumstances, Desert Sky contractors performed an inspection on two batteries on July 19, 2013. According to the Desert Sky PSMP, therefore, the next semi-annual inspection on the two batteries in question should have been performed on or before June 30, 2014. However, Desert Sky contractors did not actually perform the required battery inspections until July 1, 2014, one day after the inspection deadline. The root cause of this issue was that Desert Sky did not clearly articulate to the facility’s new operations managers the resources and time needed to perform required maintenance and testing activities. As a result, the new Desert Sky operations managers did not adequately account for the length of time required to complete the requisite inspections, including the amount of time required to procure contractors to perform them. Texas RE determined the issue duration to be from July 1, 2014, the date after the inspection of the two batteries was due, until July 1, 2014, when Desert Sky actually inspected the batteries. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on several factors. First, the two batteries at issue represent only approximately 1.35% (2/148) of devices in Desert Sky’s PSMP. Second, the two batteries are only used as fail safes or as backups in case AC service is lost at the station. Third, the duration of the issue was short, lasting only one day. Finally, there were no Misoperations related to batteries. No harm is known to have occurred. Desert Sky has no prior violations of PRC-005 R2. Affiliate Compliance History Compliance History with PRC-005 R2 for ETT (NCR10211): On May 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE201100246) was filed with FERC under NP13-37-000. On June 28, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation was that AEP failed to follow its commissioning verification procedures when replacing relays and instrument transformers. This issue was mitigated by issuing guidance that corrective maintenance activities that equate to activities outlined in AEP's preventative maintenance and testing program shall be documented in AEP's maintenance and testing database. On March 31, 2014, a Settlement Agreement covering PRC-005-1 R2 (TRE2012011136) was filed with FERC under NP14-35-000. On April 30, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. Compliance History for AEP (NCR01056, NCR00682, and NCR04006): On May 30, 2012, a Settlement Agreement covering PRC-005-1 R2 (SPP200900137, SPP201100449, RFC201000668, and TRE201100300) was filed with FERC under NP12-30-000. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation was that AEP did not test some of its relays. The root cause was that asset tracking database included incorrect testing dates, relays not being properly inventoried, and trip testing paths that were lacking sufficient data. This issue was mitigated by requiring technicians to verify completeness of database entries against the equipment at substations and defining, in a guideline, the relays within the system to be included in the asset tracking database. On October 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE2012010184, RFC2012010261, and SPP2012010129) was filed with FERC under NP14-4-000. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. In other regions (RF and SPP), AEP Generation did not perform testing on batteries. Mitigation around that issue included development and training for generation plant staff and reviewing generation batteries in RF and SPP regions to identify all batteries. Texas RE considered the compliance history of Desert Sky’s affiliates and determined that the instant issue was appropriate for Compliance Exception treatment because the root causes of the previous PRC-005 R2.1 violations are distinguishable from the instant issue. The previous instances generally involved the failure to properly track existing devices within its PSMP. In contrast, the current issue was due to new management’s lack of understanding of the time required to complete the required inspection activities. | To mitigate this issue, Desert Sky will complete the following mitigation activities by November 30, 2016: 1) conduct IPS-Energy training workshops for Desert Sky facilities; 2) implement a process to communicate policy changes to Desert Sky facilities; and 3) hold a briefing session with the new plant operators to stress the importance of planning for completing protection system testing in appropriate timeframes, including accounting for manpower and availability issues. Desert Sky needs until November 30, 2016 to complete all communication outreach sessions and training across various AEP Generation sites.
2016-05-31 | Texas Reliability Entity (Texas RE) | Electric Transmission Texas, LLC | NCR10211 | TRE2015015414 | PRC-005-1b | R2; R2.1 | On December 22, 2015, American Electric Power Service Corp as agent for ETT submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue with PRC-005-1b R2.1. Specifically, ETT did not have documentation that Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing Program (PSMP). During the duration of the issue here, ETT’s PSMP required periodic inspections of substation batteries and battery chargers at least every 90 days. In the current circumstances, ETT tested the two substation batteries and four battery chargers on August 13, 2013. Pursuant to ETT’s PSMP, therefore, ETT should have performed the next testing and maintenance activities on these devices by November 11, 2013. However, ETT did not actually perform the required inspection and testing until November 19, 2013, or 8 days after such inspection and testing was required. The root cause of this issue was that ETT personnel used the date ETT energized its substation rather than the date ETT actually installed the batteries and battery chargers as the initial “in service” date for the new battery and battery charger devices. In particular, ETT energized the substation on October 15, 2013, and ETT personnel recorded this as the “in service” date in ETT’s asset management database for purposes of establishing the start date for the required 90-day testing window. Texas RE determined the issue duration to be from November 12, 2013, the day after the batteries and battery chargers were due to be inspected, until November 19, 2013, when ETT actually inspected the batteries and battery chargers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on several factors. First, the battery and battery charger at issue represent only 5% of the batteries and battery chargers and 0.0078% of the total devices (6/7748) in ETT’s PSMP. Second, the duration of the issue was short, lasting only 7 days. Finally, ETT did not identify any issues with the batteries and battery chargers when it performed the required testing and inspection. No harm is known to have occurred. Compliance History with PRC-005 R2 for ETT (NCR10211): On May 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE201100246) was filed with FERC under NP13-37-000. On June 28, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation was that AEP failed to follow its commissioning verification procedures when replacing relays and instrument transformers. This issue was mitigated by issuing guidance that corrective maintenance activities that equate to activities outlined in AEP's preventative maintenance and testing program shall be documented in AEP's maintenance and testing database. On March 31, 2014, a Settlement Agreement covering PRC-005-1 R2 (TRE2012011136) was filed with FERC under NP14-35-000. On April 30, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. Compliance History with PRC-005 R2 for ETT’s affiliate, AEP (NCR01056, NCR00682, and NCR04006): On May 30, 2012, a Settlement Agreement covering PRC-005-1 R2 (SPP200900137, SPP201100449, RFC201000668, and TRE201100300) was filed with FERC under NP12-30-000. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation was that AEP did not test some of its relays. The root cause was that asset tracking database included incorrect testing dates, relays not being properly inventoried, and trip testing paths that were lacking sufficient data. This issue was mitigated by requiring technicians to verify completeness of database entries against the equipment at substations and defining, in a guideline, the relays within the system to be included in the asset tracking database. On October 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE2012010184, RFC2012010261, and SPP2012010129) was filed with FERC under NP14-4-000. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. In other regions (RF and SPP), AEP Generation did not perform testing on batteries. Mitigation around that issue included development and training for generation plant staff and reviewing generation batteries in RF and SPP regions to identify all batteries. Texas RE considered ETT's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the root causes of ETT’s prior violations of PRC-005 R2.1 are distinguishable from the instant issue. The previous instances generally involved ETT’s failure to properly track existing devices within its PSMP. In contrast, the current issue involved the incorrect entry of “in service” dates for two new devices into ETT’s PSMP. | To mitigate this issue, ETT will complete the following mitigation activities by March 31, 2017: 1) develop an Internal Spot Check Data Review Policy & Procedure for new assets; 2) create a report within the asset management database to identify new PRC-005 applicable assets that are added to the database and correlate device data within the database and actual device status in the field; 3) develop and begin the implementation of a Capital Checklist to ensure that new devices are appropriately entered into ETT’s asset management database; 4) perform an assessment on existing training curriculum to ensure quality and focus of compliance responsibilities associated with battery/charger maintenance; 5) perform an assessment of station assets/labor resources; and 6) provide examples of completed internal spot checks to front-line employees. ETT needs until March 31, 2017 to complete its mitigation actions in order to assess station assets and labor resources that comprise a large number of assets and protection system devices. Additionally, ETT will provide examples of completed internal spot checks to front-line employees in the first quarter of 2017.
2016-05-31 | Texas Reliability Entity (Texas RE) | Trent Wind Farm LP (TRENT) | NCR04148 | TRE2016015453 | PRC-005-1.1b | R2; R2.1 | On January 11, 2016, American Electric Power Service Corp as agent for TRENT submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-1.1b R2.1. Specifically, TRENT did not have documentation that Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing Program (PSMP). During the duration of the issue here, TRENT’s PSMP required semi-annual battery inspections. The TRENT PSMP defines “semi-annual” as one inspection during the first six months of a calendar year and one inspection during the second six months of a calendar year. In the current circumstances, TRENT contractors performed an inspection on the single battery at issue on December 10, 2013. According to the TRENT PSMP, therefore, the next semi-annual inspection on the battery device should have been performed on or before June 30, 2014. However, TRENT contractors did not actually perform the required inspection until July 2, 2014, or two days after the inspection deadline. The root cause of this issue was that TRENT did not clearly articulate to the facility’s new operations managers the resources and time needed to perform required maintenance and testing activities. As a result, the new TRENT operations managers did not adequately account for the length of time required to complete the requisite inspections, including the amount of time required to procure contractors to perform them. Texas RE determined the issue duration to be from July 1, 2014, the date after the battery was due to be tested, until July 2, 2014, when TRENT actually inspected the battery. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on several factors. First, the single battery at issue represents only approximately 0.75% (1/133) of devices in TRENT’s PSMP. Second, the single battery issue is only used as a fail safe or backup in case AC service was lost at the station. Third, the duration of the issue was short, lasting only two days. Fourth, when TRENT contractors performed the required battery inspections, the battery float voltage and cell voltage were within acceptable limits. Finally, there were no Misoperations related to batteries. No harm is known to have occurred. TRENT has no prior violations of PRC-005 R2. Affiliate Compliance History Compliance History with PRC-005 R2 for ETT (NCR10211): On May 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE201100246) was filed with FERC under NP13-37-000. On June 28, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation was that AEP failed to follow its commissioning verification procedures when replacing relays and instrument transformers. This issue was mitigated by issuing guidance that corrective maintenance activities that equate to activities outlined in AEP's preventative maintenance and testing program shall be documented in AEP's maintenance and testing database. On March 31, 2014, a Settlement Agreement covering PRC-005-1 R2 (TRE2012011136) was filed with FERC under NP14-35-000. On April 30, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. Compliance History for AEP (NCR01056, NCR00682, and NCR04006): On May 30, 2012, a Settlement Agreement covering PRC-005-1 R2 (SPP200900137, SPP201100449, RFC201000668, and TRE201100300) was filed with FERC under NP12-30-000. On June 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation was that AEP did not test some of its relays. The root cause was that asset tracking database included incorrect testing dates, relays not being properly inventoried, and trip testing paths that were lacking sufficient data. This issue was mitigated by requiring technicians to verify completeness of database entries against the equipment at substations and defining, in a guideline, the relays within the system to be included in the asset tracking database. On October 30, 2013, a Settlement Agreement covering PRC-005-1 R2 (TRE2012010184, RFC2012010261, and SPP2012010129) was filed with FERC under NP14-4-000. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. This previous violation involved certain tests that were not performed for instrument transformers within the defined intervals. The root cause was misunderstanding of staff of the revised maintenance and testing requirements. This issue was mitigated by the development of a discussion guide that discussed the changes to the program and development of a standardized instrument transformer testing procedure and form. Mitigation also included completing inventory of carrier and relays above 200kV that were applicable to the program. In other regions (RF and SPP), AEP Generation did not perform testing on batteries. Mitigation around that issue included development and training for generation plant staff and reviewing generation batteries in RF and SPP regions to identify all batteries. Texas RE considered the compliance history of TRENT’s affiliates and determined that the instant issue was appropriate for Compliance Exception treatment because the root causes of the previous PRC-005 R2.1 violations are distinguishable from the instant issue. The previous instances generally involved the failure to properly track existing devices within its PSMP. In contrast, the current issue was due to new management’s lack of understanding of the time required to complete the required inspection activities. | To mitigate this issue, TRENT will complete the following mitigation activities by November 30, 2016: 1) conduct IPS-Energy training workshops for TRENT facilities; 2) implement a process to communicate policy changes to TRENT facilities; and 3) hold a briefing session with the new plant operators to stress the importance of planning for completing protection system testing in appropriate timeframes, including manpower and availability issues. TRENT needs until November 30, 2016 to complete all communication outreach sessions and training across various AEP Generation sites.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | WECC2015015121 | PRC-005-1b | R2 | During a Compliance Audit conducted from July 13-24, 2015, WECC determined that BHP, as a Transmission Owner, Distribution Provider and Generator Owner, had an issue of noncompliance with PRC-005-1b R2. BHP failed to maintain one substation battery within the interval required by its Protection System maintenance and testing program. Specifically, BHP’s battery and charger systems for its Campbell Street Substation were not tested and maintained in accordance with the Black Hills Corporation Protection Systems Test/Maintenance Policy, ENG-32-001 Rev. Ver: 13.0. As part of an internal review, BHP discovered it had left the battery out of its maintenance and testing program, and added it during the first quarter of 2015. BHP was performing periodic testing of the battery and charger systems, but not at the intervals outlined in ENG-32-001 Rev. Ver: 13.0. BHP tested the devices on 1/3/13 and 2/23/15, and one battery exceeded the listed maintenance and testing interval of 24 months. WECC Enforcement reviewed the Audit findings, and determined that BHP had an issue of noncompliance with PRC-005-1b R2, for its failure to ensure that its Protection System devices were maintained and tested within the defined intervals of its maintenance and testing program. The root cause of this issue of noncompliance is a less than adequate compliance process, causing BHP to fail to include one battery in its Protection System maintenance and testing program. This compliance exception started on 12/01/2012, the first day following BHP’s completion of a prior mitigation plan for an earlier issue of noncompliance of this Standard; and ended on 2/23/2015, the date BHP tested the battery in question. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, BHP failed to test one battery of thirty, within the intervals in its Protection System maintenance and testing program. Failing to perform timely battery maintenance tests puts the batteries at a higher risk of failure, and the battery may not provide power over the expected amount of time. As a detective control, BHP discovered the omission in an internal review. As a corrective control, BHP quickly performed maintenance on the battery in question. To prevent future recurrence, BHP has included all Underfrequency Load-Shedding (UFLS) components in its revised PSMP. No harm is known to have occurred. WECC determined that BHP’s compliance history should not serve as a basis for applying a penalty. In 2008, BHP acquired BHCE and BHCI from Aquila Energy in Colorado. These Colorado entities had separate regulatory status, with their own separate compliance departments, separate procedures and their own control room in Colorado. BHP, as a corporate entity spent the next years from 2008 to 2014 working toward a consolidation of its facilities in South Dakota and Colorado. BHP proposed consolidating these entities into one NERC registration when it felt it had aligned processes and procedures across the entities (BHP, BHCE, BHG, and BHP). All affiliates were consolidated on June 30, 2014, under NCR05030. BHP has no direct relevant prior noncompliance with PRC-005-1b R2. BHCE, (a BHP affiliate), has two previous instances of noncompliance: (1) Violation ID WECC2012010604; in which BHCE failed to test one of 317 relays (a start date of 2/13/2012, mitigated on 4/20/2012); and (1) Violation ID WECC2012011473; in which BHCE tested four battery banks 21 days late (a start date of 6/1/2012, mitigated on 11/30/2012. BHCI, another BHP affiliate, has one previous instance of noncompliance, Violation ID WECC2012011474; in which BHCI tested 6 of 132 total battery banks 10 days late against the six month test cycle. Based on one-line drawings, the present issue of noncompliance is on the BHP system in South Dakota. WECC did not consider these previous violations to be aggravating factors in determining a CE track for the present issue of noncompliance, because the facts and circumstances of these previous violations are distinct to each of the entities, and the recurrence does not suggest a programmatic or systemic issue, as the earlier violations occurred under different compliance programs or systems. Accordingly, WECC will view noncompliance that occurs after 2014 as related under BHP’s consolidation effort. BHP provided documentation of its internal compliance program for WECC’s review, and WECC considers BHP’s internal compliance program (ICP) to be a mitigating factor in determining compliance exception treatment for this issue of noncompliance because of the following strengths: 1) BHP’s training includes a NERC Annual Refresher training course, including knowledge checks throughout the course to verify comprehension of the training material; 2) BHP makes its ICP and associated NERC Internal Compliance Procedures document and other compliance documents available to all employees and authorized third parties on the company intranet site via a “NERC Compliance Web Page"; 3) BHP has designed its incentive and rewards programs to help encourage behaviors that promote a culture of compliance. Its Incentive Program provides an annual bonus to employees, which is based, in part, on assessment factors related to the culture of compliance; and 4) BHP’s Internal Self-Review process requires an annual, comprehensive review of all applicable Reliability Standards. BHP uses NERC or WECC RSAWs as templates for this review. | To mitigate this issue and prevent recurrence, BHP identified and incorporated the battery and charger system as part of an overall review of the Black Hills Protection System Maintenance Program in preparation for implementation of PRC-005-2. This program modification included all other Protection System components (besides relays) associated with the UFLS equipment maintenance and testing.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | WECC2015015123 | PRC-008-0 | R2 | During a Compliance Audit conducted from July 13-24, 2015, the WECC Audit Team determined that BHP, as a Transmission Owner and Distribution Provider, had an issue of noncompliance with PRC-008-0 R2, for its failure to maintain and test 6 of 20 substation batteries that were part of its UFLS equipment, within the intervals required in its maintenance and testing program. WECC Enforcement reviewed the Audit findings and determined BHP had an issue of noncompliance with PRC-008-0 R2, for failing to implement its UFLS equipment maintenance and testing program for 6 of 20 substation batteries within the intervals in the program. The root cause of the issue of noncompliance is a less than adequate compliance process to ensure that all BHP UFLS equipment is identified and included in BHP’s Protection System maintenance and testing program, and is maintained and tested according to that program. The compliance exception started on 4/30/2014; one day after BHP completed a mitigation plan for an earlier issue of noncompliance with this Standard; and ended on 5/14/2015, the date BHP tested the UFLS batteries. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, BHP failed to test 6 of 20 of its UFLS batteries. Failing to perform timely battery maintenance tests puts the batteries at a higher risk of failure, and the battery may not provide power over the expected amount of time. As a detective control, BHP discovered the omission in an internal review. As a corrective control, BHP quickly performed maintenance on the batteries in question. To prevent future recurrence, BHP has included all UFLS components in its revised PSMP. No harm is known to have occurred. WECC determined that BHP’s compliance history should not serve as a basis for applying a penalty. BHP’s relevant prior noncompliance with PRC-008-0 R2 includes one previous occurrence: Violation ID WECC2013012770. In the prior CE, BHP missed the testing interval for six UFLS relays, from 78 to 161 days overdue. BHP mitigated this issue of noncompliance on 6/12/2013. WECC determined this issue was appropriate for Compliance Exception because of the following reasons. BHP provided documentation of its internal compliance program for WECC’s review, and WECC considers BHP’s internal compliance program (ICP) to be a mitigating factor in determining compliance exception treatment for this issue of noncompliance because of the following strengths: 1) BHP’s training includes a NERC Annual Refresher training course, including knowledge checks throughout the course to verify comprehension of the training material; 2) BHP makes its ICP and associated NERC Internal Compliance Procedures document and other compliance documents available to all employees and authorized third parties on the company intranet site via a “NERC Compliance Web Page"; 3) BHP has designed its incentive and rewards programs to help encourage behaviors that promote a culture of compliance. Its Incentive Program provides an annual bonus to employees, which is based, in part, on assessment factors related to the culture of compliance; and 4) BHP’s Internal Self-Review process requires an annual, comprehensive review of all applicable Reliability Standards. BHP uses NERC or WECC RSAWs as templates for this review. The discovery method of the issue of noncompliance was at the Compliance Audit; however, BHP had identified and added the missing UFLS equipment in its overall review of its program in preparation for the implementation of Version 2 prior to the audit. In addition, BHP is above average in the percentage of self-identified issues as compared to average WECC entities. BHP is also always cooperative when working with WECC on compliance matters. | To mitigate this issue and prevent recurrence, BHP (1) identified the balance of Protection System components (in addition to relays), associated with the UFLS equipment maintenance program in Q1 of 2015, as part of an overall review of its program in preparation for the implementation of NERC Reliability Standard PRC-005-2, and (2) tested the six identified batteries (DC Supplies) per the intervals defined in PRC-005-2, per BHP’s document ENG-32-001 Rev 15. WECC verified completion of the mitigation plan.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2015015239 | PRC-008-0 | R2 | On September 17, 2015, BPA submitted a Self-Report stating that as a Transmission Owner, it had a possible issue of noncompliance with PRC-008-0 R2. Following an internal review, BPA discovered it had missed one or more monthly battery inspections at four of its substations. This issue began June 1, 2014, the earliest instance of a missed inspection identified during the review, and ended May 13, 2015, when BPA revised internal inspection reports to reflect the correct inspection frequency. The root cause of this issue was less than adequate implementation of updated program requirements. This is BPA's first issue of noncompliance with this requirement in more than three years, was identified and reported timely, and posed minimal risk to the bulk power system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, BPA failed to conduct monthly battery inspections in accordance with its UFLS equipment maintenance and testing program. Such failure could have decreased BPA’s situational awareness of the condition of the batteries in scope. However, BPA implemented internal controls to identify, correct and report this issue. BPA incorporated monthly battery inspections in response to a recommendation from WECC auditors. Additionally, BPA discovered this issue following an annual internal review, and has since tested all batteries identified during the review. The condition of the batteries in scope did not change and no system events occurred throughout the duration of this issue. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the bulk power system. BPA has one previous violation of PRC-008-0 R2, given Violation ID: WECC200810021. The previous violation was not considered an aggravating factor because mitigating activities were completed more than three years prior to this issue. | To mitigate this issue, BPA: 1) developed and implemented a new inspection report for field employees responsible for battery inspections. BPA will use the report to increase management visibility of all battery inspections. WECC verified that BPA completed its mitigating activities.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2015014980 | INT-006-4 | R1 | On June 15, 2015, BPA submitted a Self-Report stating that as a Balancing Authority, it had an issue of noncompliance with INT-006-4 R1. On December 6, 2014, from 9:17 a.m. to 11:15 a.m. CST, BPA’s scheduling systems vendor experienced a widespread system network issue. This issue caused intermittent connectivity in BPA’s scheduling systems, and as a result, BPA processed nine Arranged Interchange transactions (eTags) beyond the timeframes defined in Attachment 1, Column B. This issue began and ended on December 6, 2014. BPA provided the incident report, which explained the incident was isolated to network equipment, not a database or application server problem. The incident originated from a failed distribution switch within a data center. The switch failure propagated to other network devices, causing a switching loop. The root cause of this behavior was a bug in the switch software. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BPA failed to approve or deny Arranged Interchanges within the required time period. However, this issue was limited to nine transactions, which only exceeded the time period by 7.5 minutes on average. BPA was not responsible for the root cause, and made reasonable attempts to adjust and/or resubmit the tags within appropriate timeframes. Additionally, when this issue occurred, the Reliability Coordinator declared an Interchange Authority emergency for the region. BPA implemented the WECC Interchange Authority Backup procedure and verbally confirmed Net Schedule Interchange with adjacent BAs throughout the duration of the issue. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. BPA has one previous violation of INT-006 R1, given Violation ID: WECC200700350. The previous violation was not considered relevant because mitigating activities were completed more than three years prior to this issue. | This issue resolved itself on December 6, 2014, when the vendor corrected its system network issue and restored connectivity. BPA verified that the vendor identified and addressed the root cause, and provided evidence of this confirmation to WECC. The vendor made a configuration change to the software to address the bug and implemented this change. WECC verified completion of BPA’s mitigating activities.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2015014981 | INT-006-4 | R2 | On June 15, 2015, BPA submitted a Self-Report stating that as a Transmission Service Provider, it had an issue of noncompliance with INT-006-4 R2. On December 6, 2014, from 9:17 a.m. to 11:15 a.m. CST, BPA’s scheduling systems vendor experienced a widespread system network issue. This issue caused intermittent connectivity in BPA’s scheduling systems, and as a result, BPA processed nine Arranged Interchange transactions (eTags) beyond the timeframes defined in Attachment 1, Column B. This issue began and ended on December 6, 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BPA failed to approve or deny Arranged Interchanges within the required time period. However, this issue was limited to nine transactions, which only exceeded the time period by 7.5 minutes on average. BPA was not responsible for the root cause, and made reasonable attempts to adjust and/or resubmit the tags within appropriate timeframes. Additionally, when this issue occurred, the Reliability Coordinator declared an Interchange Authority emergency for the region. BPA implemented the WECC Interchange Authority Backup procedure and verbally confirmed Net Schedule Interchange with adjacent BAs throughout the duration of the issue. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. BPA does not have previous violations of this Standard and Requirement. | This issue resolved itself on December 6, 2014, when the vendor corrected its system network issue and restored connectivity. BPA verified that the vendor identified and addressed the root cause, and provided evidence of this confirmation to WECC. WECC verified completion of BPA’s mitigating activities.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2016015659 | MOD-026-1 | R4 | On March 1, 2016, IPCO submitted a Self-Log stating that as a Generator Owner, it had an issue of MOD-026-1 R4. Specifically, IPCO failed to provide its revised model data for an applicable generating unit to its Transmission Planner (TP) within 180 calendar days of making changes to the excitation control system that altered the equipment response characteristic. The root cause of this issue was the absence of a written process or specific controls, other than a spreadsheet to ensure accurate tracking and timely compliance. IPCO discovered the issue on December 24, 2015, during an in-depth scheduled review. Specifically, while IPCO performed validation work on the existing dynamic data models as part of its 5-year modeling data re-certification program (required by the WECC Generator Testing and Model Validation Policy) IPCO discovered correspondence records between the GO and TP that were reviewed; however no record of the GO providing the required revised model data to the TP could be found. From the date IPCO modified its excitation system at the generating unit, to the date it provided the revised model data to the TP, was 311 days. The issue started on August 20, 2015, the date IPCO failed to provide the revised data to the TP within the 180 day timeframe and the issue end date is December 29, 2015, the date IPCO provided the revised data to the TP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. No harm is known to have occurred. The system would have performed adequately with the older information. If IPCO’s generating unit excitation system had failed, there would have been a low probability of occurrence that the remaining generating units would have been isolated for a failure of the in-scope generating unit’s excitation system. The units represent 2.3% of IPCO’s peak Balancing Area (BA) load, 1.6% of generation in its BA area, and 2.3% of IPCO’s generation owned. Finally, MOD-026-1 R4 allows a GO to provide revised data to the TP within 180 days; this duration is very long in terms of real time operations, reducing the risk. | To mitigate this issue, IPCO: 1) Performed the necessary model verification; and 2) Supplied the revised model data to the TP. Further, to prevent recurrence of this noncompliance, IPCO will develop a written process and controls for MOD-026-1 R4 to ensure revised model data or plans to perform model verification are provided to the TP in a timely manner, with an expected completion date of May 31, 2016.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Valley Electric Association, Inc. (VEA) | NCR05447 | WECC2015015129 | EOP-004-2 | R2 | On August 5, 2015, VEA submitted a Self-Report stating that as a Transmission Operator it had a possible issue of noncompliance with EOP-004-2 R2. During an internal review on August 4, 2015, VEA discovered it failed to submit an event report for an event which met the “Transmission loss” event type threshold in Attachment 1 of EOP-004-2. This issue began on July 13, 2015, at the end of the business day following the event, and ended August 5, 2015, when VEA reported the event. The root cause of this issue was human error; the System Operator on shift did not recognize the event as a reportable event, and therefore did not notify the Manager of Engineering as required by VEA’s Operating Plan procedures. This is VEA's first issue of noncompliance with this requirement, was identified and reported timely, and posed minimal risk to the bulk power system (BPS). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, VEA failed to report an event within the timeline prescribed by both the Standard and VEA’s Operating Plan. Such failure could limit WECC’s and/or other organizations’ situational awareness of events and delay mitigating or preventative measures. However, although the operator did not recognize the event as a reportable event, the operator did notify other VEA staff as the event occurred, recorded details of the event in the operator’s log book, and initiated investigation of the causes of the event. VEA discovered this issue within three weeks of the event, and upon discovery immediately reported both the event and potential noncompliance. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. VEA does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, VEA: 1) submitted the event report; 2) conducted an internal analysis and post-event review to identify circumstances and underlying causes of the event; 3) implemented a corrective action plan to address findings from the review in an effort to prevent recurrence; and 4) provided supplemental training regarding its reporting procedures to all relevant personnel. WECC verified completion of VEA’s mitigating activities.
2016-05-31 | Western Electricity Coordinating Council (WECC) | Windy Flats Partners, LLC (WFLA) | NCR10350 | WECC2015014960 | PRC-005-1 | R1; R1.2 | During a Compliance Audit conducted from May 28, 2015 through June 1, 2015, WECC determined that WFLA, as a Generator Owner, had an issue of noncompliance with PRC-005-1.1b R1. WFLA was unable to provide a documented summary of its procedures for maintenance and testing in accordance with R1.2 because it contracts all maintenance and testing work through a third-party contractor. The root cause of this issue was less than adequate documentation in that WFLA did not understand it needed to include this information within its own documents even though the maintenance and testing is done through a third party. This issue began on July 31, 2009, when WFLA registered as a Generator Owner, and ended July 1, 2015 when WFLA revised its PSMP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WFLA failed to include a summary of maintenance and testing procedures in its PSMP documentation. Such failure could complicate WFLA’s ability to verify that contracted work meets NERC standards, and could limit WFLA’s capacity to perform maintenance and/or testing upon termination of its contractual relationship with the third-party contractor. However, although WFLA’s PSMP did not include a summary of procedures, its Protection Systems did receive regular testing and maintenance. WECC had no findings of noncompliance for PRC-005-1.1b R2, which is an indication that this issue had no impact on the effectiveness of WLFA’s program during the period in question. Additionally, as of May 29, 2015, WFLA is required to comply with PRC-005-2, which requires Generator Owners to specify maintenance methods and associated maintenance and testing activities in their PSMP. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WFLA does not have previous noncompliance with this Standard and Requirement. | To mitigate this issue, WFLA revised its PSMP to specify maintenance methods and associated maintenance and testing activities.
2016-04-28 | Northeast Power Coordinating Council (NPCC) | Cayuga Operating Company, LLC (COC) | NCR11254 | NPCC2016015485 | PRC-018-1 | R6; SR6.1 | On December 28, 2015, Cayuga Operating Company, LLC submitted a Self-Report stating that, as a GO, it had an issue of PRC-018-1, R6.1. COC had two monthly tasks as part of their Sequence of Events Recorder (SER) maintenance procedures that they were not performing on a monthly basis: Clock Sync Observation, and SER Data Archive Observation. Specifically, they required visual confirmation that “Satellite Lock” status was achieved on the satellite synchronized clock, and confirmation that all SER recordings were archived to backup drives. COC was unable to provide evidence of these tests being performed from November 2013 to November 2014, as the data for these months was contained in a flash drive inside the SER that was replaced when the SER was upgraded in December 2014, and COC has been unable to retrieve the data from the drive. From December 2014 to January 2016, COC had set the SER to self monitor these tasks, and the SER was not reporting this data to the control room. The functions were automatically being performed by the SER, however COC was not confirming them on a monthly basis, rather they would be confirmed during quarterly data collection for mis-operations. Thus, COC was not meeting their monthly requirements to visually confirm satellite clock synchronization and confirm that all SER recordings were being archived to backup drives. The violation duration was from November 2013 to January 2016, however the violation only occurred in 17 months as quarterly data collection met the requirements. The root cause of the violation was COC believing that the SER was automatically reporting status to the control room, as other locations owned by the parent company were set up in that way. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The SER has no actual effect on the BPS, rather the data that it collects is used for post-event analysis. There was no loss of recording functionality associated with this violation, however COC was not confirming monthly tasks that were being performed automatically by the SER. When the issue was discovered, COC performed the required maintenance to ensure that the SER functioned properly, and found that both data collection and history were intact and complete. A review of the data history from the SER found that no SER functionality events had occurred during the issue duration. Satellite lock status and data archiving records would be manually checked on a quarterly basis during the data collection process for misoperations. No harm is known to have occurred as a result of this issue. NPCC considered COC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, COC: 1. Evaluated the SER to determine its ability to provide automatic notifications for the tasks included in COC's procedure for PRC-018-1 R6.2. The evaluation indicated the task notifications were eligible, however COC chose to revise manual procedures instead as they were found to be more efficient. 2. Revised their PRC-018-1 R6.2 procedure to ensure that SER maintenance procedures would be manually performed and confirmed. NPCC has verified the completion of all mitigation activity.
2016-04-28 | Northeast Power Coordinating Council (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2015015335 | FAC-008-3 | R2 | On November 6, 2015, Plainfield Renewable Energy, LLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of FAC-008-3 R2. In the period spanning from December 12, 2013 through November 6, 2015, Plainfield Renewable Energy, LLC did not have in place a fully documented Facility Ratings Methodology that should have been used to determine ratings for its generator lead line. The root cause of the issue was that the previous owner of the generating facilities had been using a simplified template as the essential outline for determining facility ratings that did not contain sufficient detail to be compliant with the standard. When Greenleaf took ownership of the PRE facilities in mid-2015, it developed and put into effect a Facility Ratings Methodology on November 5, 2015 that is compliant with the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The scope of equipment associated with the generator lead line is limited, and the associated components are all engineered to greatly exceed the plant’s power production capability. The facility ratings for the generator lead line did not change as a result of implementing the 2015 Facility Ratings Methodology. As the facility ratings did not change as a result of implementing the current Facility Ratings Methodology, the lack of a formal documented methodology during the specified non-compliance period represents a minimal impact on the reliable operation of the BES system. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered Plainfield Renewable Energy, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, Plainfield Renewable Energy, LLC: 1. has put in place a procedure for documenting its Facility Rating Methodology, effective November 5, 2015; and 2. currently requires for its procedure a review cycle of 3 years or less as dictated by changes to future versions of this NERC standard. NPCC has verified the completion of all mitigation activity.
2016-04-28 | Northeast Power Coordinating Council (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2015015333 | FAC-008-3 | R6 | On November 6, 2015, Plainfield Renewable Energy, LLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of FAC-008-3 R6. In the period spanning from December 12, 2013 through November 6, 2015, Plainfield Renewable Energy, LLC did not have in place a fully documented Facility Ratings Methodology that is consistent with its established facility ratings. The root cause of the issue was that the previous owner of the generating facilities had been using a simplified template as the essential outline for determining facility ratings that did not contain sufficient detail to be compliant with the standard. When Greenleaf took ownership of the PRE facilities in mid-2015, it developed and implemented a Facility Ratings Methodology on November 5, 2015, thus ensuring that its facility ratings are determined in accordance with the rating methodology currently in effect. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For example, the scope of equipment associated with the generator lead line is limited, and the associated components are all engineered to greatly exceed the plant’s power production capability. Furthermore, PRE's facility ratings did not change as a result of implementing the current Facility Ratings Methodology. In conclusion, the lack of consistency between facility ratings and the former, poorly documented, rating methodology during the specified non-compliance period represents a minimal impact on the reliable operation of the BES system. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered Plainfield Renewable Energy, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, Plainfield Renewable Energy, LLC: 1. has put in place a procedure for documenting its Facility Rating Methodology, effective November 5, 2015; and 2. currently requires for its procedure a review cycle of 3 years or less as dictated by changes to future versions of this NERC standard. NPCC has verified the completion of all mitigation activity.
2016-04-28 | ReliabilityFirst Corporation (ReliabilityFirst) | PPL Electric Utilities Corporation (PPL EU) | NCR00884 | RFC2015015272 | PRC-023-3 | R1 | On October 5, 2015, ReliabilityFirst determined that PPL EU, as a Transmission Owner, had an issue of PRC-023-3 R1 as a result of a Compliance Audit conducted from September 14, 2015 through October 2, 2015. In preparation for their 2015 Compliance Audit, PPL EU identified two 230 kV lines (Brunner Island-West Shore and Paupack-Pocono) that were classified as Criterion 1 but failed to meet the minimum relay settings for that Criterion. Criterion 1 specifies that the identified transmission line relays will not operate at or below 150% of the highest seasonal Facility Ratings of the circuit. In this instance, the Brunner Island-West Shore and Paupack-Pocono line had relay settings well below the 150% minimum for Criterion 1 classification, with circuits tripping at 125% and 128% respectively. The Brunner Island-West Shore line failed to meet the Criterion 1 requirements after a Facility Rating change that occurred in December 2014. The Paupack-Pocono line failed to meet the Criterion 1 requirements due to a miscalculation of the Facility Rating. PRC-023-3 R1 was violated because both relays were classified as Criterion 1 and did not meet the minimum requirements of that Criterion. This noncompliance implicates the management practice of implementation because there were not adequate detective controls in place to quickly identify incorrect classifications. Implementation is also implicated because PPL EU had the Transmission & Substation Asset Management Operations Analysis group reviewing the PRC-023-3 spreadsheet when the Relay Engineering group was more appropriate to review the spreadsheet. The root cause was the lack of effective detective controls in place to identify and correct misclassifications. The duration of this noncompliance is from October 1, 2014, the date PPL EU was required to comply with PRC-023-3 R1, to August 3, 2015, the date PPL EU reclassified the two 230 kV lines as Criterion 2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the two lines are not part of an Interconnection Reliability Operating Limit (“IROL”). Because the two lines at issue are not part of an IROL, a line tripping below 150% of its highest rating will not significantly impact other lines or lead to cascading outages. If the lines were part of an IROL, the two lines would have significant impact on the BES as being part of an IROL would increase the risk of this noncompliance. Second, the misclassification did not require PPL EU to change the relay settings on the two 230 kV lines at issue to meet Criterion 1 requirements. PJM was made aware of the re-classification and has not required any additional corrective action for these two lines. With no change to the relay settings, the lines pose the same minimal risk of tripping prematurely as they did when they were originally installed. The risk level would be heightened if PJM were to ask PPL to adjust the relay settings to meet Criterion 1 or if PJM does not accept the reclassification because that would show there is still risk associated with these circuits tripping at 125% and 128% of its highest seasonal Facility Rating. Additionally, the two lines are below 345 kV and have less of an impact on the BES if they were to overload. No harm is known to have occurred. This is PPL EU's first instance of noncompliance with PRC-023 R1. | To mitigate this issue, PPL EU: 1) reclassified the two 230kV lines as Criterion 2, which allows a lower minimum setting (115% of the highest seasonal 15-minute Facility Rating of a circuit); 2) notified PJM, PPL EU’s Balancing Authority, Reliability Coordinator, and Transmission Operator, that it reclassified the two 230 kV transmission lines as Criterion 2; 3) fully transferred responsibility for the PRC-023 process and reporting tool from its Transmission & Substation Asset Management Operations Analysis group to its Relay Engineering group. The Relay Engineering group will be responsible for updating the PRC-023 reporting tool when changes to facility ratings or relay settings occur, and for performing reviews of all applicable data. The Relay Engineering group is more appropriate to review the PRC-023 process and reporting tool because they have the expertise and resources to better identify misclassifications or other related issues; 4) updated the PRC-023 reporting tool to include a human performance tool for criteria identification meaning the criteria cell turns red when Criterion 1 is not met and added a revision history tab to track updates; 5) updated the PRC-023 procedure to include more details on step by step actions to assess relay loadability and to perform a review with Relay Engineering staff. ReliabilityFirst has verified the completion of all mitigation activity.
2016-04-28 | SERC Reliability Corporation (SERC) | Ameren Missouri (AUE) | NCR10248 | SERC2015015384 | VAR-002-4 | R2 | On December 1, 2015, AUE submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R2. AUE failed to maintain the generator voltage schedule provided by the Transmission Operator (TOP) at its Labadie Energy Center (LEC). On November 1, 2015, the transmission operations supervisor called the LEC shift supervisor to discuss whether the shift supervisor could lower the voltage on the 345 kV switchyard bus by 0.5 kV to lower overall system voltages. However, the transmission operations supervisor stated the shift supervisor should not lower the voltage below the bottom of the normal voltage schedule issued for LEC. The TOP provided a voltage schedule that was a range between 358.8 – 362.5 kV as measured on an hourly average basis. The shift supervisor ordered lowering of the maximum and minimum alarm set points based on the shift supervisor’s understanding of the discussion with the transmission operations supervisor. The shift supervisor lowered the 345 KV voltage level by altering the control band within the automatic bus voltage control system which lowered the bus voltage. However, the control band permitted the bus voltage to drift below the minimum bus voltage in the voltage schedule. Except for two hours, the hourly average on the 345 kV switchyard voltage fell below the 358.8 kV bottom of the normal voltage schedule from November 1, 2015 at 6:00 p.m. until November 2, 2015 at 3:00 p.m. On November 2, 2015, a Labadie plant engineer observed on the monitoring equipment that the voltage was below the normal voltage schedule minimum of 358.8 kV. The engineer contacted the plant control room and the shift supervisor contacted Transmission Operations. The shift supervisor consulted with the transmission operations supervisor prior to adjusting the voltage to return to the voltage schedule range. The shift supervisor then ordered the bus voltage brought back up inside the normal voltage schedule. The primary cause of the issue was a misunderstanding between the shift supervisor and the transmission operations supervisor regarding the voltage change request and the design of the of the LEC automatic voltage control equipment. The issue occurred from 6:00 p.m. on November 1, 2015, the first instance of a voltage schedule excursion, until 3:00 p.m. on November 2, 2015, when AUE returned the voltage to the voltage schedule requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AUE’s failure to maintain the generator voltage as directed by the TOP could have caused a mismatch between expected and actual generator output voltage, resulting in insufficient voltage support. However, this voltage schedule excursion provided extra reactive support to the BPS. The lowest hourly voltage during the time of this issue was only 0.4 kV (0.11%) below the 358.8 kV bottom of the voltage schedule. No harm is known to have occurred. SERC considered AUE’s compliance history and determined there were no relevant instances of noncompliance | To mitigate this issue, AUE: 1) consulted with the TOS and then raised the voltages to ensure compliance with the normal Voltage Schedule; 2) executed its Corrective Action Process to determine the root cause of the issue; 3) implemented design change LB-2016-DC-0004 to allow operations to enter a 345KV voltage control setpoint anywhere within the current voltage schedule and informed transmission operators of the change; and 4) considered possible distribution and use throughout the Ameren Missouri generation fleet as a Lessons Learned or Operational Experience (OE).
2016-04-28 | SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2015015381 | EOP-010-1 | R3 | On November 25, 2015, Entergy submitted a Self-Report stating that, as a Transmission Operator, it had an issue with EOP-010-1 R3. Entergy stated that after receiving notification of a triggering event, it failed to implement its Geomagnetic Disturbance (GMD) procedure. On June 22, 2015 at 2:15 p.m., the Entergy System Operating Center (SOC) received alert on its Reliability Coordinator Communication System that a K-8 level GMD had occurred. Entergy’s GMD procedure requires it to implement its procedure when a GMD exceeds the threshold of K-7. On July 13, 2015, Entergy was performing a verification of GMD events as part of an internal control procedure. Entergy called the Reliability Coordinator (RC) to confirm the number of GMD procedure triggering events and the RC informed it of the June 22, 2016 K-8 level GMD alert. Entergy could not verify the implementation of the GMD procedure for the triggering event. In the event of a K-8 level GMD, Entergy’s GMD procedure requires log entries, various phone notifications, monitoring of system parameters, and generator coordination to maintain a unity power factor. Entergy is unable to produce evidence that it performed any of the activities required by its procedure after receiving a K-8 alert. Entergy determined the root cause to be human error. Entergy failed to follow its documented procedures in response to the GMD alert. Entergy performed an extent of condition and confirmed that this issue was an isolated event. The issue lasted from June 22, 2015, when Entergy failed to implement the GMD procedure, through March 30, 2016, when Entergy updated its operating policy in a new procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GMD events have the ability to disrupt normal operations of the BPS. However, per the National Oceanic and Atmospheric Administration, the area of impact for K-8 GMD events is primarily north of 45 degrees Geomagnetic Latitude, Entergy’s geography is not in the expected affected area as Entergy’s northernmost facility is in Arkansas at 36°30' North Latitude. Based on impacts to utilities north of Entergy during previous GMD events, if a K-8 GMD event were to cause impacts south of 45 degrees, there is no evidence the impacts would be substantive or require Entergy to take corrective actions. During normal operation, Entergy constantly monitors system parameters, communicates with the RC and other entities and takes corrective action when necessary. In this instant issue, no abnormal operating conditions were observed, no special communications were required and no mitigating actions were needed. No harm is known to have occurred. SERC considered Entergy's EOP-010-1 R3 compliance history in determining the disposition track. Entergy does not have relevant prior noncompliance with EOP-010-1 R3. | To mitigate this issue, Entergy: 1) provided coaching to the SOC Senior Operator, emphasizing the importance of consulting written procedures to ensure that the correct action is taken and not taking action if a procedure cannot be located; 2) reminded all SOC Operators to follow the steps within the applicable SOC procedure in the event they received notification from the RC of a severe GMD warning; 3) developed Lessons Learned and added associated training to the System Operator training schedule; and, 4) relocated Entergy’s GMD Operating Process, originally embedded in SOC-P-016, to a new procedure specifically addressing EOP-010-1.
2016-04-28 | SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2016015481 | PRC-005-1.1b | R2 | On January 22, 2016, Entergy submitted a Self-Report stating that, as a Transmission Owner (TO) it had an issue with PRC-005-1.1b R2. Entergy failed to perform the required maintenance and testing tasks within the defined interval. Entergy scheduled multiple substation maintenance tasks for September 14, 2015, at the Grand Gulf Nuclear Station (GGNS). However, GGNS engineering personnel identified potential risks to the off-site power to the plant stemming from that work and recommended that Entergy Transmission conduct the work during a refueling outage for the plant. On the recommendation of GGNS engineering personnel, Entergy Transmission rescheduled the work to start February 19, 2016. On September 16, 2015, as Entergy rescheduled the work, it discovered two issues. First, the battery impedance tests associated with each of two 125V DC battery banks at GGNS substation were already overdue by 16 days. Entergy originally scheduled the tests with other work on September 14, 2015, but failed to recognize that the tasks were due by the end of August 2015. Entergy completed both battery impedance maintenance tasks on September 16, 2015. Second, Entergy should have performed the DC operational tests and panel inspections associated with the J5204 Breaker Control Panel and J5208/ST21 HV Transmission Line Panel in the GGNS substation by January 1, 2016. Entergy had to delay the tasks beyond the due date because of concerns related to the possible loss of offsite power to an operating nuclear plant. This issue lasted from September 1, 2015, the first day after the maximum interval for battery testing at GGNS, until mitigation completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to maintain Protection System devices could result in a failure to trip or premature tripping of protective features resulting in unplanned outages or inability to control system facilities. However, Entergy completed monthly battery checks in the months prior to the impedance checks, and the checks identified no problems. Also, Entergy completed the battery impedance maintenance task associated with two 125V DC battery banks upon discovering that it was overdue by 16 days, minimizing the likelihood of these devices failing when required to perform their protective function. These batteries are redundant for many of the conditions in which they may be required. The batteries were only 25% into their 20 year life expectancy. Entergy did not note any issues upon completion of the impedance tests. In addition, the breaker control panel is related to a fail-to-trip circuit of a transformer protection system. Entergy relies upon the DC control circuit if a fault occurs on the transformer’s circuit accompanied by a failure of both primary and backup protection systems and/or the related circuit breaker does not function. Should this multiple failure occur, the fault would clear remotely by opening the next breakers in the system with a clearing time of 25 cycles. The clearing will also trip GGNS off line. Entergy and its Reliability Coordinator plan for such an event in the next day and operational planning processes. Entergy had updated its next day and operational contingency models to include the loss of other possibly affected units caused by the delayed clearing. Entergy did not identify any misoperations attributable to the delayed maintenance activities and no harm is known to have occurred. SERC considered Entergy’s PRC-005-1 R2 compliance history in determining the disposition track. Entergy’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID SERC2012011079 and SERC2013013258. In SERC2013013258, Entergy failed to perform maintenance and testing on nine relays. As part of the mitigation, Entergy assessed maintenance records of all transmission devices and determined that six additional relays had not been listed, had been mis-categorized as not requiring maintenance and testing, or testing had been suspended and remained incomplete. In SERC2012011079, Entergy incorrectly installed associated communication systems resulting in the devices requiring more frequent testing than was scheduled. In the instant issue, Entergy incorrectly scheduled or rescheduled maintenance and testing to accommodate a nuclear power station outage schedule. The previous violations were for mis-categorization of relays and failing to correctly install communication equipment. Therefore, the cause of the instant issue is different from the prior violations and the mitigation of the prior violations would not have corrected the instant issue. SERC also considered the relevant compliance history of the following affiliates: Entergy Nuclear Palisades’(NCR08952); Entergy - Fossil & Hydroelectric Generation (NCR11167), Entergy Nuclear (NCR1 1166), Entergy Nuclear Fitzpatrick, LLC (NCR0707J), Entergy Nuclear Generation Company (NCR07072), Entergy Nuclear Indian Point 2, LLC (NCR07073), Entergy Nuclear Indian Point 3, LLC (NCR07074), Entergy Nuclear Palisades, LLC (NCR08052), and Entergy Nuclear Vermont Yankee, LLC (NCR07075). SERC considered Entergy's affiliates’ compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Entergy 1) performed the required panel inspections and maintenance tests on the batteries. 2) assigned a system-wide nuclear maintenance coordinator to ensure that all future transmission maintenance is incorporated into all Entergy nuclear sites’ refueling outage work plans.
2016-04-28 | SERC Reliability Corporation (SERC) | Georgia Power Company (GPC) | NCR01247 | SERC2016015486 | PRC-005-1.1b | R2; R2.1 | On January 25, 2016, GPC submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-005-1.1b R2. GPC failed to conduct maintenance and testing on a single battery as required by its Protection System program. On August 4, 2015, during a six-month routine preventive diagnostic inspection, a substation electrician observed low battery water. The substation electrician attempted to report the low battery water as an abnormal situation work order but the work order system failed to allow the work ticket creation. GPC incorrectly coded the maintenance code for the battery as “No Maintenance,” which prevented the system from generating work orders for any periodic maintenance or testing for the battery. GPC put this battery in-service on June 16, 2014, and GPC’s maintenance and testing program required that the first maintenance inspection occur between July 1, 2014 and December 31, 2014. GPC could not provide documentation of maintenance and testing within the defined interval for one of approximately 450 (0.22%) batteries. In total, GPC could not provide evidence that one of approximately 6,600 (0.015%) Protection System devices were compliant with PRC-005-1.1b R2. GPC determined that two process failures occurred, both due to human error. First, GPC incorrectly coded the battery in its work order system as “No Maintenance.” Second, the crew responsible for performing the initial testing did not report the difficulty it experienced in attempting to create the initial work order. This issue lasted from January 1, 2015, the day after GPC should have performed a maintenance inspection on the battery, through August 6, 2015, when GPC completed the battery maintenance inspection. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GPC’s failure to perform the maintenance and testing of the Protection System device within the defined interval could lead to the device not operating as intended, potentially leading to false trips, remote clearing, delayed clearing, the overreach of protective relays or reliance on the interconnecting Transmission Owner’s Protection System device to respond to a fault. However, GPC had monitoring and alarming enabled for the subject battery and charger via SCADA. Control center personnel monitored the status of all substation batteries and charging systems 24x7. An alarm would have actuated if a problem occurred affecting the battery’s ability to perform its protective functions. GPC’s process included dispatching field personnel to the facility, with high priority, to identify and correct any problems if an alarm occurred. GPC trained field personnel to observe batteries and charging systems, as well as other equipment, as part of routine inspections upon entering any substation. The battery properly performed its intended functions throughout the period. GPC identified no issues during maintenance and testing on August 6, 2015. No harm is known to have occurred. SERC considered GPC and its affiliates’ PRC-005 R2 compliance history in determining the disposition track. GPC and its affiliates’ relevant prior noncompliance with PRC-005 R2 includes NERC Violation ID SERC2013012138. SERC determined that GPC and its affiliates’ compliance history should not serve as a basis for applying a penalty. SERC2013012138 occurred because GPC did not have a clear process in place to enter contractor-installed batteries into the work order system. As part of the mitigation of this violation, GPC established a process for reviewing all pending battery installations to ensure appropriate transfer of asset records from contractors to GPC. This mitigating plan would not have prevented the instant issue. The instant issue occurred because of two human performance issues. First, GPC made an administrative error in coding the new battery in the work order system. Second, the maintenance crew failed to report the inability to create the initial work order following initial test completion. | To mitigate this issue, GPC: 1) completed the battery inspection on August 6, 2015; 2) changed the default practice for batteries identified with the bi-monthly transmission estimating and management (TEAM) system’s query to require the maintenance spec code be marked in the work order system to assign the responsibility for battery maintenance to the transmission maintenance center. Changing the maintenance spec code in the work order system will require an additional layer of approval for NERC battery sets; 3) revised the current NERC battery list to include location and the organization responsible for maintenance. Additionally, both generation and substation support personnel will review the list on a fixed interval to verify the appropriate divisions of responsibilities ensuring GPC meets maintenance schedules. 4) assessed Southern Company’s operating companies for PRC-005 compliance vulnerabilities similar to that experienced at GPC with the transfer of battery maintenance responsibility from generation to transmission; 5) discussed the facts and circumstances of this issue at a bi-weekly compliance oversight team meeting, which is regularly attended by representatives from Southern Company’s operating companies and business units representing various NERC functional roles. GPC and affiliates assessed similar vulnerabilities in other areas of the company subject to PRC-005 requirements.
2016-04-28 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2015015315 | MOD-030-2 | R5; R5.3 | On October 30, 2015, LGE and KU submitted a Self-Report stating that, as a Transmission Service Provider (TSP), it had an issue with MOD-030-2 R5.3. LGE and KU failed to use the Available Flowgate Capability (AFC) provided by the TSP for external Flowgates identified in R2.1.4, to calculate AFCs. On September 1, 2012, LGE and KU transitioned to a new independent transmission organization (ITO). During this transition, an error in the default time zone setting in the OATI webTrans system occurred. In March 2015, LGE and KU determined that, due to the time zone setting error it did not use the AFC provided by the TSP. The AFC overrides due to the incorrect time zone settings caused some monthly AFC calculations to be incorrect. The error occurred daily but was limited to Flowgates owned by TVA, which represented approximately 16 of the 181 (8.8%) LGE and KU AFC Flowgates. The AFC is a daily calculation that covers a rolling 18-month time horizon. This issue was limited to instances where the TVA Flowgate with the incorrect override capacity was the limiting Flowgate for an Available Transfer Capability (ATC) path. LGE and KU discovered a potential error in the AFC calculation during a review of a transmission service request. In order to determine the cause of the error, LGE and KU engaged in discussions with TVA, which performs the load forecast and outage portion of the AFC calculation on the behalf of LGE and KU. LGE and KU completed an internal assessment to verify that it identified the scope of the issue correctly. This issue lasted from September 1, 2012, when LGE and KU utilized the incorrect AFC overrides after transitioning to a new ITO, through March 25, 2015, when LGE and KU corrected the AFC overrides. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The AFC calculation errors could have resulted in LGE and KU selling more transmission service across its system than it actually had available. However, the issue occurred in three to four months of each 18-month AFC time horizon and represents less than 2% of the total AFC calculations performed during the period. LGE and KU, as the TSP, received only 23 confirmed requests and did not curtail any requests for monthly service during this issue. If LGE and KU sold more transmission than it had available, LGE and KU Reliability Coordinator (RC) and neighboring RCs could have reduced overloads on their systems by redispatch, reconfiguration, and eliminating schedules. No harm is known to have occurred. SERC considered LGE and KU’s MOD-030 R5 compliance history in determining the disposition track. LGE and KU’s relevant prior noncompliance with MOD-030-2 R5 includes: NERC Violation ID SERC2013013151 and SERC2014014144. SERC determined that LGE and KU’s MOD-030-2 R5 compliance history should not serve as a basis for applying a penalty. The underlying conduct involved in both prior instances was different than this issue. In SERC2013013151, the SDX Scrubber process stopped and did not restart, causing the ATC process to run against a stale data file. In SERC2014014144, the legacy server on which a portion of the SDX process ran was rebooted, but did not return the server to service. While the SDX Scrubber was offline, missed changes to existing and new transmission and generation outages. To mitigate this violation, implemented a file data checking mechanism to ensure that not only the files themselves are updated, but that the data within the files that are used by the ATC process are updated as well. The prior Mitigation Plans would not have prevented the instant issue. | To mitigate this issue, LGE and KU: 1) worked with its ITO and OATI to implement changes to the webTrans system to ensure that the proper TVA AFC overrides, in the correct time zone, are imported correctly and included in the AFC calculations. Specifically, LGE and KU had the parameters for importing time zones updated in the AFC calculator initialization files, to allow the calculator to correctly convert different time zones into EST; and 2) worked with its ITO to implement an overall ATC and AFC verification process that includes monthly, weekly, and daily checks to ensure the AFC and ATC calculations are being correctly performed. The ITO added a daily AFC override checking process to the ATC and AFC verification process, to check and compare the accuracy of AFC override postings on the OASIS.
2016-04-28 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2015015316 | MOD-030-2 | R9 | On October 30, 2015, LGE and KU submitted a Self-Report stating that, as a Transmission Service Provider, it had an issue with of MOD-030-2 R9. LGE and KU failed to use the correct algorithm for non-firm Available Flowgate Capability (AFC) calculations. LGE and KU incorrectly configured its OATI webTrans non-firm Available Flowgate Capacity (AFC) calculation to deduct the Capacity Benefit Margin (CBM) that is reserved in the firm AFC calculation instead of the actual CBM usage, which is requested via schedules from entities using the CBM in real-time. As a result, LGE and KU reduced the amount of transmission service available for non-firm transactions by the CBM reserved when it should have reduced it by only the actual CBM usage scheduled. In March 2015, LGE and KU discovered the error when LGE and KU noticed no difference in the CBM for firm and non-firm ATC postings. LGE and KU determined that the error was caused by an oversight in the initial implementation of CBM in the AFC calculations. This issue lasted from December 5, 2012, when LGE and KU first included the CBM reserve in the non-firm AFC calculations, through March 19, 2015, when LGE and KU corrected the non-firm AFC calculation configuration. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). LGE and KU’s failure to deduct scheduled CBM instead of reserved CBM in the non-firm AFC calculations could have limited a LGE and KU transmission customer’s ability to import energy using non-firm transmission service prior to a capacity deficiency. However, the configuration issue had no impact on the amount of CBM available for use if needed. LGE and KU set-aside CBM on a relatively small number of Flowgates. In 2014, LGE and KU reserved CBM on 12 of 108 LGE and KU Flowgates, with the average CBM set-aside accounting for only 5% of the Flowgate rating. In addition, no capacity emergencies occurred during this issue. No harm is known to have occurred. SERC considered LGE and KU’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LGE and KU: 1) worked with its ITO and OATI to implement changes to ensure the CBM reserve was not deducted from non-firm AFCs, by setting the non-firm CBM multiplier to “zero”; and 2) worked with its ITO to implement an overall ATC and AFC verification process that includes monthly, weekly, and daily checks to ensure the AFC and ATC calculations are being correctly performed.
2016-04-28 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2015015317 | MOD-030-2 | R6; R6.4 | On October 30, 2015, LGE and KU submitted a Self-Report stating that, as a Transmission Service Provider (TSP), it had an issue with MOD-030-2 R6.4. LGE and KU failed to include the impact of some firm transmission service sold by adjacent TSPs that have coordination agreements with LGE and KU when calculating the impact of Existing Transmission Commitments (ETC) for firm commitments. The LGE and KU Independent Transmission Organization (ITO) utilizes OATI webTrans to perform the Available Flowgate Capability (AFC) calculation for LGE and KU. In September 2012, LGE and KU transitioned to a new ITO and reconfigured the File Transfer Protocol (FTP) site of the OATI webTrans system. During this transition, LGE and KU incorrectly configured an import mechanism setting in webTrans responsible for processing transmission service request (TSR) coordination files. The system failed to process the Midcontinent Independent System Operator, Inc., PJM Interconnection, LLC, and Tennessee Valley Authority TSR coordination files. As a result, the firm AFC calculations did not include the impact of firm transmission service sold by adjacent TSPs that have coordination agreements with LGE and KU. LGE and KU found the error during an expanded review of the Available Transfer Capability (ATC) calculation. The LGE and KU ITO did not detect the configuration error because it did not actively monitor the log file that captured the coordination file updates. LGE and KU determined that the source of the error was in a software application. This issue lasted from September 1, 2012, when LGE and KU incorrectly configured the import mechanism setting responsible for processing TSR coordination files, through July 1, 2015, when LGE and KU corrected the setting and began importing TSR coordination files correctly. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LGE and KU’s failure to correctly calculate AFC could have resulted in LGE and KU selling more firm transmission service across its system than it actually had available. However, the LGE and KU Reliability Coordinator (RC) and neighboring RC’s had options such as redispatch, reconfiguration, and eliminating non-firm schedules to minimize transmission overloads on their systems. This issue had no reliability impact on neighboring systems because each neighbor manages impacting flows on their own Flowgates. In addition, the missing external TSRs impacted only 14 of the 101 LGE and KU Flowgates, thereby limiting the number of posted firm ATCs likely impacted and reducing the likelihood that LGE and KU sold firm transmission service beyond the capability of the transmission system. No harm is known to have occurred. SERC considered LGE and KU’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LGE and KU: 1) worked with its ITO and OATI to correct the configuration problem that prevented proper processing of the TSR coordination input files; and 2) worked with its ITO to implement an overall ATC and AFC verification process that includes monthly, weekly, and daily checks to ensure the ATC and AFC calculations and TSR coordination process are performed correctly. The process includes monitoring the TSR coordination log file.
2016-04-28 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | SERC2015015318 | MOD-030-2 | R7; R7.2 | On October 30, 2015, LGE and KU submitted a Self-Report stating that, as a Transmission Service Provider (TSP), it had an issue with MOD-030-2 R7.2. LGE and KU failed to include the impact of some confirmed non-firm Point-to-Point Transmission Service sold by adjacent Transmission Service Providers (TSP) that have coordination agreements with LGE and KU when calculating the impact of Existing Transmission Commitments (ETC) for non-firm commitments for all time periods for a Flowgate. The LGE and KU Independent Transmission Organization (ITO) uses OATI webTrans to perform the Available Flowgate Capability (AFC) calculation for LGE and KU. In September 2012, LGE and KU transitioned to a new ITO and reconfigured the the File Transfer Protocol (FTP) site of the OATI webTrans system. During this transition, LGE and KU incorrectly configured an import mechanism setting in webTrans responsible for processing transmission service request (TSR) coordination files. The system failed to process the Midcontinent Independent System Operator, Inc., PJM Interconnection, LLC, and Tennessee Valley Authority TSR coordination files. As a result, the non-firm AFC calculations did not include the impact of non-firm transmission service sold by adjacent TSPs that have coordination agreements with LGE and KU. LGE and KU found the error during an expanded review of the ATC calculation. The LGE and KU ITO did not detect the configuration error because it did not actively monitor the log file that captured the coordination file updates. This issue lasted from September 1, 2012, when LGE and KU incorrectly configured the import mechanism setting responsible for processing TSR coordination files, through July 1, 2015, when LGE and KU corrected the setting and began importing TSR coordination files correctly. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LGE and KU’s failure to correctly calculate AFC could have resulted in LGE and KU selling more firm transmission service across its system than it actually had available. However, LGE and KU Reliability Coordinator (RC) and neighboring RC’s have options such as redispatch, reconfiguration, and eliminating non-firm schedules to minimize transmission overloads on their systems. This issue had no reliability impacts on neighboring systems because each neighbor manages impacting flows on their own Flowgates. In addition, the missing external TSRs affected only 14 of the 101 LGE and KU Flowgates, thereby limiting the number of posted firm ATCs likely impacted and reducing the likelihood that LGE and KU sold firm transmission service beyond the capability of the transmission system. No harm is known to have occurred. SERC considered LGE and KU’s MOD-030-2 R7 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LGE and KU: 1) worked with its ITO and OATI to correct the configuration problem that prevented proper processing of the TSR coordination input files; and 2) worked with its ITO to implement an overall ATC and AFC verification process that includes monthly, weekly, and daily checks to ensure the ATC and AFC calculations and TSR coordination process are performed correctly. This process includes monitoring the TSR coordination log file.
2016-04-28 | SERC Reliability Corporation (SERC) | Louisiana Generating, LLC (LAGN) | NCR01265 | SERC2015015319 | PRC-005-1.1b | R2 | On November 3, 2015, LAGN submitted a Self-Report stating that, as a Transmission Owner (TO) and Generation Owner (GO), it was in violation of PRC-005-1a R2. LAGN could not produce evidence that 21 relays and one DC Control Circuit had been tested within the assigned interval. In May of 2015, LAGN began a process improvement program that included digitizing maintenance and testing evidence for all Protection System devices. During that process, LAGN discovered it did not have documentation to support relay maintenance work for 21 relays and one DC control circuit. Based on LAGN historical maintenance practices during scheduled outages and schedules showing technicians were on site during such outages, LAGN believes it performed maintenance on at least 16 relays. However, LAGN’s process did not require archiving the test data prior to closing the maintenance work order. Incomplete device lists caused the remaining instances. The devices lists did not include all the devices that required maintenance and testing, which resulted in device missed intervals. SERC determined that the issue affects 21 of 560 relays (3.75 %) and 1 of 647 (0.,2%) DC Control circuits. LAGN has completed a record review of all Protection System devices and verified the scope of this issue. The SERC audit team also examined a random sample of maintenance and testing records and found no additional issues. The root cause of the issue was human error. LAGN failed to archive maintenance and test data and did not maintain a complete device list. The issue lasted from November 9, 2009, the earliest missed maintenance interval missed, through January 1, 2016, when LAGN developed a more thorough PRC-005 testing program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to perform maintenance and testing of Protection System devices could prevent proper operation leading to widespread system disturbances. However, all devices have a minimum of one layer of backup protection, with most devices having three layers of backup protection. Therefore, a relay failure would have triggered the backup protection with no additional impact on the Bulk Electric System. Additionally, LAGN’s operations center is manned with monitoring of all relevant sites to allow for immediate identification of and response to a relay failure. No trips or failure to trip occurred during the duration of the issue. No harm is known to have occurred. SERC considered LAGN’s PRC-005-1 R2 compliance history in determining the disposition track. LAGN’s relevant prior noncompliance with PRC-005-1 R2 includes NERC Violation ID SERC2011008220. SERC determined that LAGN’s PRC-005-1 R2 compliance history should not serve as a basis for aggravating the penalty. The instant issue involves a failure to include certain devices for testing and failing to maintain documentation of testing of others. SERC2011008220 involved failure of an automated system to schedule maintenance and testing on relays. The issue was mitigated on January 7, 2012 and is not considered relevant to the instant issue. The instant issue was caused by human error, while the previous instance was due to system failure. | To mitigate this issue, LAGN: 1) performed maintenance the required maintenance; 2) developed a plan for the LaGen PRC-005 testing program to include device lists being issued with testing assignments and requiring all test results to be uploaded to a shared drive before the testing can be marked complete; and 3) conducted training on the PRC-005 test work flow procedure.
2016-04-28 | SERC Reliability Corporation (SERC) | Sam Rayburn G&T Electric Cooperative Inc. (SRGT) | NCR01307 | SERC2015014732 | PRC-005-1b | R2; R2.1 | On February 26, 2015, SRGT submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue with PRC-005-1b R2. SRGT failed to conduct the Protection System maintenance and testing within the defined intervals for some Protection System devices. Through a three years self-assessment conducted from December 2014 through February 2015, SRGT discovered that two SRGT members missed the maintenance and testing dates for battery chargers and relays. SRGT performed a full assessment and verified that the issue was only related to battery chargers and relays as previously identified by SRGT. SRGT could not provide documentation of maintenance and testing within the defined interval for 28 of 152 (18%) protective relays and 3 of 26 (12%) battery chargers. In total, SERC determined that SRGT could not provide evidence that 31 of 444 (7%) Protection System devices were compliant with PRC-005-1b R2. SRGT determined that the primary causes of non-compliance were personnel changes and lack of understanding as to what relays are Protection System relays. This issue occurred from April 1, 2013, when the battery chargers were included in the Protection System definition, until mitigated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SRGT’s failure to perform the maintenance and testing of these Protection System devices within the defined interval could lead to devices not operating as intended, potentially leading to false trips, remote clearing, delayed clearing, the overreach of protective relays or reliance on the interconnecting Transmission Owner’s Protection System devices to respond to a fault. However, battery chargers, communication paths and relays are monitored and alarmed on the SRGT SCADA. Alarms are sent to the operator who should dispatch personnel to check the status of the equipment. In addition, other protection schemes should activate and trigger clearing the bus if the non-compliant relays did not perform as designed. The instant issue is an administrative failure for not documenting the maintenance and test results. SRGT did not identify any issues during the testing and maintenance. Therefore the devices should have performed as designed if needed. No harm is known to have occurred. SERC considered SRGT’s PRC-005-1 R2 compliance history in determining the disposition track. SRGT’s relevant prior noncompliance with PRC-005-1 R2 includes NERC Violation ID SERC200900268. SERC determined that SRGT's compliance history should not serve as a basis for applying a penalty. The Mitigation Plan for the prior issue was completed in March 2010 and should not be considered for the instant issue as completion was more than three years prior to the instant issue. The instant issue was self-identified by an internal control and promptly self-reported. | To mitigate this issue, SRGT: 1) conducted maintenance and testing on all missed transmission protection system elements and on those elements where prior records could not be located; 2) updated the summary report of all transmission protection system elements, the date they were tested, and a field showing the location of the supporting documentation; 3) conducted a lessons learned meeting with SRGT transmission owning members to discuss this violation and how to prevent future occurrences; 4) revised the SRGT Internal Compliance Program to include internal spot checks, at least twice a year, to review the transmission protection system maintenance and testing records; and 5) developed and provided the SRGT members with training on the transmission protection system maintenance and testing program. Training will be conducted at least once every year.
2016-04-28 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2015014913 | PRC-008-0 | R2 | On February 10, 2015, SERC sent TVA an audit detail letter notifying it of a compliance audit scheduled for May 11, 2015 through May 29, 2015. On May 7, 2015, TVA submitted a Self-Report stating that, as a Transmission Owner, it was in violation of PRC-008-0 R2. TVA failed to implement its Under Frequency Load Shedding (UFLS) equipment maintenance and testing program for one UFLS relay. On April 9, 2015, while reviewing documentation for its compliance audit, TVA discovered that it had failed to properly enter the required maintenance schedule for one UFLS relay in its work order management system. TVA originally entered the relay maintenance and testing intervals into the work order management system in June, 2007 and should have included a four year DC control check and an eight year extensive relay calibration with DC control check. However, TVA failed to enter the information required for the four-year DC control check. Therefore, it failed to complete the maintenance and testing activities as required. TVA determined that the primary cause of the issue was human performance. TVA staff failed to correctly assign maintenance and testing activities in the work order management system. This issue lasted from June 18, 2007, when PRC-008-0 R2 became enforceable, until April 10, 2015, when TVA completed the four-year maintenance and testing activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TVA’s failure to maintain and test may cause UFLS devices to not operate as planned to help restore system frequency to the appropriate value. However, TVA would have met the load shed requirement had the relay failed to operate. The relay is connected to trip approximately 6.3 MW or 0.02% of TVA’s load. TVA had been conducting the eight-year maintenance and testing activities on the subject relay, and it discovered no issues when the four-year maintenance and testing was conducted. If this relay had misoperated, potential impact would have been to customer loads, not the BPS. TVA completed an assessment and verified that only one of the 487 (0.2%) UFLS relays was out of compliance. No harm is known to have occurred. SERC considered TVA’s PRC-008-0 R2 compliance history in determining the disposition track. TVA’s relevant prior noncompliance with PRC-008-0 R2 includes NERC Violation ID SERC2013013133. SERC determined that TVA's compliance history should not serve as a basis for applying a penalty. TVA did not identify the instant issue during the execution of the Mitigation Plan for SERC2013013133 as TVA relied on manual checking of the work management system to discover missing preventive maintenance (PM) activities. In the prior Mitigation Plan, TVA verified that it had done the maintenance and testing within the intervals in the management system; TVA did not verify that the assigned intervals with the management system were correctly assigned. TVA implemented intelligence in the work management system with Mitigation Plan SERC2015-402203. A script will run once a month and it will identify any missing PMs or inappropriate PM frequency assignments for relays. | To mitigate this issue, TVA: 1) completed the required maintenance and testing on the relay; 2) performed an extent of condition on all UFLS relays and verify appropriate PM durations; 3) added the checks to the transmission organizations asset cut-in process; and 4) created a monthly exception report that contains logic that maps the required preventive maintenance program to the correct relay terminal based on the type and function of the relays associated with the terminal. The report flags any relay terminal that does not meet the logic criteria that aligns with the program, whether caused by human error or some other means.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | American Electric Power Corp. as Agent for AEP Oklahoma Transmission Company, Inc., Public Service Company of Oklahoma, and Southwestern Electric Power Company | NCR01056 | SPP2014014421 | EOP-005-2 | R15 | On October 30, 2014, AEP submitted a Self-Report stating that, as a Generator Operator, it had an issue of noncompliance with EOP-005-2 R15 because it did not notify the Transmission Operator of a change to the capability of a Blackstart Resource within 24 hours following such change. Diesel generators provided auxiliary power through a bus (station reserve power bus) to the three units at the Wilkes generating station, providing them with Blackstart capabilities. The reserve power bus between the diesel generators and the units incurred a fault, resulting in a loss of Blackstart capability for the three units. The Transmission Operator was not notified of this change to the Blackstart capabilities of the three Wilkes generating units. The duration of this issue was from June 25, 2014, the date the cable connecting the diesel generators to the units failed, through July 14, 2014, the date the repairs were made to the cable, allowing diesel generators to tie in to the units. The root cause of this issue was a lack of operator training regarding their responsibilities during the loss of a Blackstart Resource. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to notify the Transmission Operator that a Blackstart Resource was unavailable has the potential to compromise the ability of the Transmission Operator to successfully implement its restoration plan. Notwithstanding, AEP’s restoration plan includes contingencies to address the unanticipated loss of Blackstart units, including utilizing redundant Blackstart Resources to restore its transmission system. No harm is known to have occurred in this instance. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including AEP’s noncompliance with EOP-008-0 R1; R1.3; R1.6 was filed with FERC under RC13-2-000 on 11/30/2012. The 60-day review period passed on 1/30/2013. SPP RE considered AEP’s compliance history and determined that the instant issue was appropriate for FFT treatment because the prior issues involved different standards and requirements unrelated to system restoration from Blackstart Resources. | To mitigate this minimal risk instance of noncompliance, AEP: 1) retrained all affected personnel on its Blackstart Resource availability status change notification procedure; 2) notified maintenance crews of its Blackstart policies to assist operations from a technical perspective regarding work that needs communicated for Blackstart availability; and 3) placed a copy of the Blackstart Resource policy in the Operator Instruction book and a placard above the Blackstart computer screen in the control room detailing action items to be conducted in the event Blackstart Resources are unable to be restored.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Lea Power Partners, LLC (LEAPP) | NCR10301 | SPP2015015323 | PRC-005-1b | R1; R1.1; R1.2 | On November 6, 2015, Lea Power Partners (LEAPP) submitted a Self-Report stating that, as a Generation Owner, it had a minimal risk instance of noncompliance with PRC-005-1b R1.1 and R1.2 because it did not include six protection system communications system devices at the Hobbs Generating Station in its Protection System Maintenance and Testing Program (PSMP). Because LEAPP did not include these devices in their inventory of protection system devices, they were not maintained in accordance with the testing/maintenance interval prescribed in their PSMP. LEAPP’s violation of PRC-005 involved 6 of 125 or 4.8 percent of the protection system devices in its PSMP. The duration of this instance of noncompliance was from June 14, 2013, the end date of LEAPP’s last compliance audit through November 1, 2015, the completion of LEAPP’s mitigating activities. The root cause of this instance of noncompliance was human error. The LEAPP staff did not thoroughly review its original facility drawings when constructing its inventory of protective system devices, inadvertently omitting the six communications system devices. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The relays associated with these communications system devices are equipped with trouble alarm indication located on the relay panel and are inspected daily by the LEAPP Operators to ensure they are functioning and communicating properly. Should an issue be found during these inspections, the Operation Staff would initiate corrective action. No alarms, indicating a communication connectivity failure, were documented by LEAPP's Operators and no recorded events were found during the maintenance and testing of the relays in October 2015. No harm is known to have occurred. A FFT informational filing addressing a remediated issue for LEAP’s noncompliance with PRC-005-1 R1 (SPP2012009182) was filed with FERC under Docket RC13-7-000 on March 27, 2013. The 60-day review period passed on May 26, 2013. SPP RE considered LEAPP's compliance history and determined that this issue of noncompliance was appropriate for Compliance Exception treatment. Although the instances of noncompliance involved the same Standard and Requirement, the underlying conduct resulting in the noncompliance is different. The prior violation (SPP2012009182) was related to not having detailed testing requirements for the protection system devices in its PSMP, while the instant issue is related to omitting communication devices, which are not normally utilized at generation facilities. | To mitigate this minimal risk instance of noncompliance, LEAPP: • updated their Protection Systems Maintenance and Testing Program and protection system device list to include the six communication system devices; • performed the required testing and maintenance associated with the six devices; and, • trained affected staff on updates to its Protection Systems Maintenance and Testing Program and protection system device list. SPPRE has verified the completion of all mitigation activity.
2016-04-28 | Southwest Power Pool Regional Entity (SPP RE) | Westar Energy, Inc. (Westar) | NCR00658 | SPP2015015244 | PRC-023-1 | R1; R1.1 | On September 23, 2015, Westar submitted a Self-Report stating that, as a Transmission Owner, it had a minimal risk instance of noncompliance with PRC-023-1 R1.1. During Westar’s semi-annual review of its PRC-023 Transmission Relay Loadability Spreadsheet, Westar discovered an error in the formula for comparing the actual relay settings with the required settings. Specifically, the formula utilized to establish the verification point for their transmission line relays was incorrect because the formula calculated the comparison value for relay operation at less than or equal to 150%, instead of greater than 150% of the highest seasonal Facility Rating of the circuits per R1.1. When Westar corrected the formula they found that seven of the 162 transmission relays were set at 150% and not greater than the 150% as required by the standard. The remaining 155 were set greater than the 150%. The root cause of this instance of noncompliance was Westar’s misinterpretation of the standard, specifically, the interpretation of transmission line relay setting limits, when applying the formula to the Transmission Relay Loadability Spreadsheet. The duration of the noncompliance began on July 1, 2010, the date Westar applied the incorrect formula for the relay settings to the Transmission Relay Loadability Spreadsheet, and ended on June 29, 2015, the date spreadsheet was revised to adhere to PRC-023 R1.1. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Failing to identify relay settings that are lower than what the standard allows could have caused the relays to trip prematurely resulting in an unnecessary loss of load. Notwithstanding, the formula was off by only .01% and affected only seven of the 162 relays in Westar's system. No harm is known to have occurred. Westar has not had any previous violations related to this standard. | To mitigate this minimal risk instance of noncompliance, Westar revised the formula for verification of its relay settings in its Transmission Relay Loadability Spreadsheet to adhere to PRC-023 R1.1. SPP RE has verified the completion of all mitigation activity.
2016-04-28 | Texas Reliability Entity (Texas RE) | GDF Suez Energy Generation NA, Inc. (MELP) | NCR04098 | TRE2016015551 | PRC-005-2(i) | R3 | During a Compliance Audit conducted from January 26, 2016 through January 28, 2016, Texas RE determined that MELP, as a Generator Owner, had an issue with PRC-005-2(i) R3. Specifically, MELP did not maintain two communications devices in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed in PRC-005-2(i) Table 1-2. MELP originally considered the two communications devices in question (both of which were the same device type) to be fully monitored and, therefore, not subject to the 4-month functional testing intervals for unmonitored communications devices set forth in PRC-005-2(i) Table 1.2. During its preparations for the Texas RE audit, however, MELP determined that these two communications devices did not satisfy PRC-005-2(i)’s requirements to designate such devices as continuously monitored. Based on this conclusion, MELP recategorized the two communications devices as unmonitored. Pursuant to PRC-005-2(i) Table 1-2, the maximum maintenance for unmonitored communication devices is four months. Because this maximum testing interval is less than one year, the PRC-005-2 R3 and R4 Implementation Timeline in turn required MELP to complete its functional testing for these devices by October 1, 2015. However, MELP did not complete functional testing for the two communications devices until November 19, 2015. The root cause of the issue was that MELP plant personnel incorrectly concluded that the two communications devices satisfied the various requirements to be designated as continuously monitored under PRC-005-2. In particular, MELP had characterized these particular devices as fully monitored under its legacy maintenance program and did not properly account for the new PRC-005-2 requirements for continuous monitoring in updating its maintenance processes. Texas RE determined the issue duration to be from October 2, 2015, the day after MELP was required to complete all functional testing of the two communications devices under PRC-005-2(i) R3, until November 19, 2015, when MELP actually completed all functional testing on the two devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MELP only improperly designated a single device type consisting of the two communications devices at issue as continuously monitored. MELP properly categorized and tested all other communication devices. As such, the two devices represent approximately 4% of MELP’s total communication devices and approximately 0.10% of all devices in MELP’s maintenance program. Further, no issues were found when MELP performed the required functional testing for these two devices. No harm is known to have occurred. Texas RE considered MELP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MELP: 1) reclassified the two communication devices as unmonitored communications devices under PRC-005-2; 2) tested the two communication devices; 3) updated the daily operator checklist to include the two communications devices at issue so that the devices are functionally tested daily; and 4) provided detailed instructions to operations personnel on how to perform functional testing on the particular communications device-type at issue as an unmonitored communications device-type. Texas RE has verified the completion of all mitigation activity.
2016-04-28 | Texas Reliability Entity (Texas RE) | Texas Medical Center Central Heating and Cooling Services Corp (TECO) | NCR11116 | TRE2016015497 | EOP-004-2 | R3 | On February 1, 2016, TECO submitted a Self-Report stating that, as a Generator Owner, it had an issue with EOP-004-2 R3. Specifically, TECO failed to validate all contact information contained in its event reporting Operating Plan for the 2015 calendar year. Texas RE has determined that the root cause of the noncompliance was an insufficient process for tracking the completion of the contact information validation. Specifically, TECO’s process lacked sufficient reminders or prompts to the TECO personnel responsible for performing the contact information validation. Accordingly, the Compliance Administrator tasked with validating of the relevant contact information mistakenly believed that such an update was no longer required. Moreover, TECO’s process called for TECO personnel to begin to validate the event reporting Operating Plan contact information on December 19th of each year, reducing the margin of error for timely completing the contact information validation process by the end of the calendar year. Texas RE determined that the issue duration was from January 1, 2016, the day after the compliance information validation was due, until January 29, 2016, when TECO performed its contact information validation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, the noncompliance was documentary in nature and did not affect TECO’s actual operations. TECO would have only needed the contact information in question in circumstances in which it was required to use its event reporting Operating Plan, which has never occurred. Second, the duration by which TECO was in noncompliance was less than one calendar month. Lastly, the generation resource has a maximum nameplate capability of only 60.5 MW, and most of this generation serves load solely within TECO’s Private Use Network. No harm is known to have occurred. Texas RE considered TECO’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TECO: 1) performed the contact information validation; 2) added an automatic annual work order into its Enterprise Asset Management (EAM) System to ensure that the contact information is validated every calendar year; and 3) changed the date upon which the contact validation process occurs such that under TECO’s new process, TECO will issue the automatic EAM annual work order on January 1 for the calendar year in which the contact information validation is to be performed to ensure sufficient time is available to complete the required contact information validation process for that calendar year. Texas RE has verified the completion of all mitigation activity.
2016-04-28 | Western Electricity Coordinating Council (WECC) | Basin Electric Power Cooperative (BEPC) | NCR05023 | WECC2015015229 | PRC-005-2 | R1 | During a Compliance Audit of BEPC from September 8 to September 11, 2015, WECC discovered that BEPC, as a Transmission Owner (TO), Generator Owner (GO), and Distribution Provider (DP), had an issue of noncompliance with PRC-005-2 R1. The root cause of this issue was outdated documentation. This issue began on April 1, 2015, the date PRC-005-2 became enforceable, and is ongoing. This is BEPC's first issue relating to this requirement and posed minimal risk to the BPS. During the audit, WECC determined that BEPC’s PSMP did not include information indicating maintenance intervals chosen, minimum maintenance activities required, and monitoring methods (whether monitored or unmonitored) for all protection system components or component types. Documentation for the PSMP in effect prior to April 1, 2015 indicated that some communication devices are fully monitored and do not require maintenance or testing; however, this information was not included in the PSMP provided during the audit, nor was information concerning the transition of maintenance practices from the legacy program to the current program. Although both programs clearly acknowledged the requirement of time-based maintenance methods, neither specified how BEPC implements this requirement beyond the reference tables included in the PRC-005-2 Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BEPC failed to document the intervals and monitoring methods for protection system component types within its PSMP. Such failure could potentially result in inconsistent testing and/or documentation thereof, which could affect the working order of BEPC’s Protection Systems. However, given the enforcement date of the requirement and the timing of the audit, BEPC had not had significant time to perform maintenance to the updated program, and was using its legacy program while it transitioned to PRC-005-2. During the audit WECC had no findings of noncompliance for PRC-005-1.1b R1 and R2, which is an indication that this issue had no impact on the BPS. For these reasons, and because no harm occurred, this issue posed minimal risk to the reliability of the BPS. BEPC is continuing to maintain and test its Protection System devices per its PSMP while it completes its mitigation activities. BEPC does not have previous violations of this Standard and Requirement. | To mitigate this issue, BEPC will complete the following mitigation activities by December 30, 2016: 1) complete a field inventory and analysis of all protection system components either owned by BEPC or for which BEPC has been designated as the responsible entity; and 2) update its PSMP to designate monitoring methods and intervals for all protection system component types.
2016-04-28 | Western Electricity Coordinating Council (WECC) | Basin Electric Power Cooperative (BEPC) | NCR05023 | WECC2015015230 | PRC-008-0 | R1 | During a Compliance Audit of BEPC from September 8 to September 11, 2015, WECC discovered that BEPC, as a Transmission Owner (TO) and Distribution Provider (DP), had an issue of noncompliance with PRC-008-0 R1.The root cause of this issue was inadequate documentation. This issue began on October 24, 2009, the completion date of the last audit in which BEPC had no findings relating to this requirement, and is ongoing. This is BEPC's first issue relating to this requirement and posed minimal risk to the BPS. During the audit, WECC identified a possible issue with BEPC’s UFLS equipment maintenance and testing program. BEPC’s program did not include maintenance and testing intervals, nor the basis for such intervals, for instrument transformers, DC circuits, batteries and battery chargers. WECC requested additional evidence for these component types and discussed the omissions in an interview with BEPC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BEPC failed to identify all UFLS equipment and did not provide a schedule for maintenance and testing of all component types. Such failure could potentially result in inconsistent testing and maintenance activity and/or documentation thereof, which could limit BEPC’s awareness of the working order of its UFLS equipment. However, only one member of BEPC’s cooperative group owns UFLS equipment. The entity in question is relatively small within the WECC region, and at the time of the audit was transitioning to PRC-005-2, which requires set intervals and maintenance activities for all UFLS component types. For these reasons, and because no harm occurred, this issue posed minimal risk to the reliability of the BPS. BEPC is continuing to maintain and test its Protection System devices per its PSMP while it completes its mitigation activities. BEPC does not have previous violations of this Standard and Requirement. | To mitigate this issue, BEPC will complete the following mitigation activities by December 30, 2016: 1) complete a field inventory and analysis of all UFLS equipment either owned by BEPC or for which BEPC has been designated as the responsible entity; and 2) update its PSMP to designate monitoring methods and intervals for all protection system component types.
2016-04-28 | Western Electricity Coordinating Council (WECC) | Basin Electric Power Cooperative (BEPC) | NCR05023 | WECC2015015231 | PRC-008-0 | R2 | During a Compliance Audit of BEPC from September 8 to September 11, 2015, WECC discovered that BEPC, as a Transmission Owner (TO) and Distribution Provider (DP), had an issue of noncompliance with PRC-008-0 R2. The root cause of this issue was inadequate documentation. This issue began on October 24, 2009, the completion date of the last audit in which BEPC had no findings relating to this requirement, and is ongoing. This is BEPC's first issue relating to this requirement and posed minimal risk to the BPS. During the audit, WECC issued a data request for maintenance and testing records of a random sample of BEPC’s UFLS equipment. WECC discussed concerns regarding these records in an interview with BEPC and determined that BEPC failed to perform maintenance and testing in accordance with its UFLS maintenance and testing program for one protection relay and four sets of instrument transformers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, BEPC failed to perform maintenance and testing of UFLS equipment in accordance with its UFLS maintenance and testing program. Inconsistent testing and/or maintenance could have resulted in unreliable operation of the equipment. However, although BEPC did not perform maintenance and testing per the intervals prescribed in its program, it did perform regular testing and maintenance. Additionally, only one member of BEPC’s cooperative group owns UFLS equipment. The entity in question is relatively small within the WECC region. For these reasons, and because no harm occurred, this issue posed minimal risk to the reliability of the BPS. BEPC is continuing to maintain and test its equipment per its program while it completes its mitigation activities. BEPC does not have previous violations of this Standard and Requirement. | To mitigate this issue, BEPC will complete the following mitigation activities by December 30, 2016: 1) test the relay and instrument transformers identified by WECC during the audit; 2) complete a field inventory and analysis of all UFLS equipment either owned by BEPC or for which BEPC has been designated as the responsible entity; and 3) update its PSMP to assign responsibility for UFLS equipment maintenance and designate monitoring methods and intervals for all protection system component types.
2016-04-28 | Western Electricity Coordinating Council (WECC) | City of Tacoma, Department of Public Utilities, Light Division (TPWR) | NCR05097 | WECC2015015393 | PRC-005-1 | R2 | On December 4, 2015, TPWR submitted a Self-Report stating that as a Transmission Owner, Distribution Provider and Generator Owner, it had a possible issue of noncompliance with PRC-005-1 R2. The root cause of this issue was administrative oversight. This issue began June 18, 2007, when PRC-005-1 became enforceable, and ended September 22, 2015, when TPWR performed maintenance and testing on the device. This is TPWR's second issue of noncompliance with this requirement, was identified and reported timely, and posed minimal risk to the BPS. In June 2015, a power supply failure to a communication device triggered an alarm. Upon further investigation, TPWR determined that the device had never been tested/maintained under TPWR’s Protection System maintenance and testing program (PSMP). Prior to this event, TPWR discussed ownership and responsibility for this device internally and with Public Utility District #1 of Lewis County (LCPD). Although the terms of the Interconnection Agreement between TPWR and LCPD did not specify ownership for this equipment, after the device failed, TPWR assumed ownership and maintenance responsibility since the device is located in “Interconnection Facilities” on TPWR’s side of the interconnection. WECC conducted a Compliance Audit of TPWR from March 7 to March 18, 2016. During the audit, WECC reviewed the details of the Self-Report, the status of TPWR’s mitigating activities, and TPWR’s overall compliance with the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, TPWR failed to include one communication device in its Protection System maintenance and testing program (PSMP). Such failure could have resulted in unreliable operation of the device, which could slow TPWR’s ability to clear a fault on the line. However, the scope issue was limited to one device with one isolated incident. Failure of the device did not result in delayed fault clearance on the line, and had no actual impact to the Bulk Power System. Additionally, WECC had no findings of noncompliance with this Standard during TPWR’s 2016 Compliance Audit. Further, TPWR’s system is not on a Major WECC Transfer Path. For these reasons, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. TPWR has one previous violation of this Standard and Requirement, given Violation ID: WECC201001848. In that circumstance, TPWR Self-Certified that it failed to maintain Protection System devices identified in its PSMP within intervals defined by its PSMP. Because of the circumstances of the previous violation, WECC determined that TPWR’s compliance history should not preclude designation of this issue as a compliance exception. | To mitigate this issue, TPWR: 1) assumed ownership and added the device to its PSMP; 2) performed maintenance and testing on the device; and 3) reviewed other facilities interconnecting with adjacent TOs and GOs to verify there were no other “overlooked” devices in its system. WECC verified completion of TPWR’s mitigating activities.
2016-04-28 | Western Electricity Coordinating Council (WECC) | Frederickson Power LP (FPWR) | NCR05164 | WECC2015015049 | EOP-004-2 | R1 | On July 1, 2015, FPWR submitted a Self-Report stating that, as a Generator Owner and a Generator Operator, it is a Responsible Entity under EOP-004-2 R1, and it had an issue of noncompliance with EOP-004-2 R1. This Standard superseded and replaced the combined requirements of CIP-001-2a and EOP-004-1, effective January 1, 2014. According to the Self-Report, On December 8-11, 2014, FPWR’s parent organization (Atlantic Power Corporation) conducted an internal audit to assess FPWR’s NERC compliance, and discovered that FPWR had failed to sign the new EOP-004-2 event reporting Operating Plan Version 2 of this Standard, by January 1, 2014, the effective date of the Standard. WECC Compliance Risk Analysis (CRA) staff reviewed the Self-Report, conducted interviews with FPWR compliance staff and requested additional evidence. WECC Enforcement reviewed the Self-Report and the CRA analyst’s findings; including (1) an email from Atlantic Power Corporation’s Director, Compliance, dated 12/11/2013, providing FPWR with a new template to create an Operating Plan for FPWR, to replace CIP-000-2a (Sabotage Reporting) and EOP-004-1 (Disturbance Reporting) by December 31, 2013; and (2) a new FPWR Event Reporting Operating Plan, Revision 0, dated 12/9/2014. For these reasons, WECC Enforcement determined that FPWR had a compliance exception with EOP-004-2 R1, for its failure to have an executed event reporting Operating Plan, by January 1, 2014, the date the Standard was applicable to FPWR. The root cause of the issue of noncompliance was a less than adequate compliance process, causing FPWR's failure to timely update its event reporting Operating Plan in compliance with the new version of the Standard. The compliance exception started on January 1, 2014, the date the Standard was effective, and ended on December 9, 2014; the date FPWR management signed the new event reporting Operating Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, FPWR failed to sign the new EOP-004-2 R1 event reporting Operating Plan for version 2 of the Standard before the effective date of January 1, 2014. However, FPWR had strong compensating controls in place for its event reporting procedures. The WECC CRA analyst reviewed FPWR’s CIP-001-2a and EOP-004-1 procedures and concluded that together they meet all of the criteria for an Operating Plan in compliance with EOP-004-2 Attachment 1. FPWR reduced the risk of this compliance exception for the duration by complying with the two older standards, reducing the risk of violating EOP-004-2 R1. No harm was known to have occurred. FPWR also has corrective controls in place. In the case of an act of sabotage or an operating emergency, FPWR still has a process to follow the procedures of CIP-001 and EOP-004, the two standards incorporated into the new EOP-004-2 R1 requirements. WECC considered FPWR’s compliance history and determined there were no relevant instances of noncompliance. In consideration of FPWR’s compliance history, WECC notes that FPWR has identified and self-reported the possible compliance exception addressed herein, does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. For these reasons, WECC considers FPWR’s compliance history as a factor in its designation of these remediated issues for CE treatment. | To mitigate this compliance exception, FPWR signed the Version 2 event reporting Operating Plan.
2016-04-28 | Western Electricity Coordinating Council (WECC) | Otay Mesa Energy Center, LLC (OTAY) | NCR10396 | WECC2015015296 | PRC-005-2 | R1 | During a Compliance Audit of OTAY from September 29 to 30, 2015, WECC discovered that OTAY, as a Generator Owner (GO), had an issue of noncompliance with PRC-005-2 R1. The root cause of this issue was inadequate documentation. This issue began April 1, 2015, the date PRC-005-2 became enforceable, and ended November 2, 2015, when OTAY revised its tracking documentation to include monitoring methods. During the audit, WECC discovered a possible issue in OTAY’s Protection System Maintenance Program (PSMP). Although the PSMP specified that OTAY utilizes a time-based maintenance method for Protection System Component Types, it did not designate specific intervals or monitoring methods. WECC requested additional information regarding monitoring attributes used to determine extended maintenance intervals and discussed the omissions in an interview with OTAY. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, OTAY failed to specify intervals and monitoring methods for all Protection System Component Types within its PSMP. Such failure could potentially result in insufficient maintenance and/or documentation thereof, which could affect the working order of OTAY’s Protection Systems. However, during the audit period OTAY was transitioning to PRC-005-2 and performing maintenance and testing in accordance with PRC-005-1.1b during this transition. Although the intervals and monitoring methods weren’t specified in the PSMP, OTAY provided evidence of specific maintenance intervals within its Attachment G Supplement. For these reasons, and given the recent enforcement date for this requirement, this issue posed minimal risk to the reliability of the Bulk Power System. OTAY does not have previous violations of this Standard and Requirement. | To mitigate this issue, OTAY revised its procedure and tracking documentation to designate monitoring methods for all Protection System Component Types. WECC verified that OTAY completed mitigating activities.
2016-04-28 | Western Electricity Coordinating Council (WECC) | Otay Mesa Energy Center, LLC (OTAY) | NCR10396 | WECC2015015295 | PRC-005-1 | R2 | During a Compliance Audit of OTAY from September 29 to 30, 2015, WECC discovered that OTAY, as a Generator Owner (GO), had an issue of noncompliance with PRC-005-1 R2. The root cause of this issue was inadequate documentation. This issue began October 23, 2009, when OTAY registered as a GO, and ended November 6, 2015, when it revised its documentation procedure and retested the DC circuit. During the audit, WECC compared testing records to intervals identified in OTAY’s PSMP to verify that OTAY was performing testing and maintenance accordingly. WECC requested additional evidence for three protection relays and one DC circuit test associated with a generating unit. WECC discussed concerns in an interview with OTAY and determined that the evidence provided was insufficient to demonstrate compliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, OTAY failed to provide sufficient evidence to demonstrate all its protection system devices were maintained and tested in accordance with its PSMP. Failure to provide adequate documentation requires WECC to assume the OTAY is not maintaining and testing its Protection System devices, the failure of which could lead to a loss of load. However, OTAY provided sufficient evidence that it maintained and tested the majority of its Protection System devices in accordance with its PSMP. The three protective relays comprised 12% of the population of protection relays, and the DC circuit was 33% of the population of DC control circuits. Additionally, the devices in scope were tested at regular intervals even though the documentation was insufficient to demonstrate compliance. While OTAY did not have adequate proof that the three protective relays were tested in 2009, test records showed they were last tested in 2014, rendering mitigation efforts unnecessary. And, although OTAY could not produce documentation proving that the DC circuit devices were tripped during its 2014 test, OTAY did provide a report listing lockout devices for the generator and an attestation that the breakers were tripped from the vendor that performed the test. Further, OTAY was transitioning to PRC-005-2 during the audit period, and given the recent enforcement date for this requirement may not have adopted all of the changes addressed in version 2 that could have remediated this issue. For these reasons, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. OTAY does not have previous violations of this Standard and Requirement. | To mitigate this issue, OTAY: 1) retested the DC circuit; and 2) revised its procedures to ensure the plant manager verifies that required maintenance and testing activity is documented properly, and that such documentation is retained.. WECC verified that OTAY completed mitigating activitie.