2016-04-28 | Western Electricity Coordinating Council (WECC) | Salt River Project Agricultural Improvement and Power District (SRP) | NCR05372 | WECC2015015263 | PRC-005-1b | R2 | On October 5, 2015, SRP submitted a Self-Report stating that as a Distribution Provider, Generator Owner and Transmission Owner, it had an issue of noncompliance with PRC-005-1b R2. According to the Self-Report, in August 2015, SRP determined that maintenance for five protective relays at the Hassayampa Switchyard was not performed in accordance with SRP’s Protection Systems Maintenance Plan (PSMP). The PSMP calls for relays associated with WECC Paths (equivalent to WECC Major Transfer Paths) to be maintained on a three year interval, which lapsed on May 1, 2012. However, the relays were not tested timely because the Hassayampa Switchyard was not identified as part of a WECC Major Transfer Path in SRP's work management system (Cascade), which incorrectly listed 6 year intervals for the relays as a result of the miscategorization. A WECC Subject Matter Expert (SME) reviewed the Self-Report, held discussions with SRP compliance staff, and found that SRP failed to provide evidence that it had maintained and tested five relays within the defined intervals. WECC Enforcement reviewed the Self-Report and the SME’s findings and determined that SRP had an issue of noncompliance with PRC-005-1b R2, for its failure to maintain and test five relays within the intervals specified in its PSMP. The root cause of this issue of noncompliance was a less-than-adequate compliance process to ensure all relays were categorized as required by SRP's PSMP. This issue began May 1, 2012, the first day of Fiscal Year 2012, when maintenance was due, and ended February 7, 2014, when SRP maintained and tested the relays. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, SRP miscategorized a switchyard on a WECC Major Transfer Path in its work management system and missed the three year maintenance and testing interval for five relays. However, SRP performed maintenance and testing on the relays on February 7, 2014, well within the interval for relays not included in WECC Major Transfer Paths. No harm is known to have occurred. SRP implements preventative controls. Specifically, SRP implemented a monthly report identifying all maintenance required for completion in the upcoming 90 days. Reports are distributed to all supervisors, the manager, and the director responsible for Protection System maintenance. In this case, SRP personnel were aware the equipment needed to be maintained, but the system had the incorrect interval for the devices. SRP also implements detective and corrective controls by monitoring the relays. If the relays had malfunctioned an alarm would have triggered within SRP’s control room that would have been addressed by an immediate review of equipment by field personnel. In consideration of SRP’s compliance history, WECC notes that SRP has identified and self-reported the possible issue of noncompliance addressed herein, and has provided documentation of its internal compliance program. WECC determined that SRP’s compliance history should not preclude designation of this issue as a compliance exception. SRP’s prior noncompliance with PRC-005-1 R2 includes NERC Violation IDs: WECC200801237 and WECC2014014496. WECC did not consider the first violation (WECC200801237) relevant because SRP completed mitigating activities more than three years prior to this issue. The second issue, WECC2014014496, concerned batteries tested roughly 4 months outside their designated interval, and was also processed as a Compliance Exception. WECC determined that the facts, circumstances and root cause of that issue are not a reflection of a programmatic or systemic problem, and considers that issue separate and distinct from the issue addressed herein. | To mitigate this issue of noncompliance, SRP will revise its PSMP in alignment with the NERC Reliability Standard PRC-005-6 for all relays, and will not have an accelerated maintenance schedule for relays on a WECC transfer path. In addition to this revision, SRP will implement an annual review with appropriate departments, of all of the Protection Systems included under the PRC-005-6 Standard. By aligning the PSMP with the requirements of PRC-005-6 and implementing an annual review the likelihood of recurrence of this violation is reduced. SRP proposed a completion date of May 1, 2016.
2016-04-28 | Western Electricity Coordinating Council (WECC) | San Diego Gas & Electric (SDGE) | NCR05377 | WECC2015014757 | PRC-005-1 | R1 | On March 19, 2015, SDGE submitted a Self-Report stating that as a Transmission Owner, Distribution Provider and Generator Owner it had a potential issue of noncompliance with PRC-005-1 R1. Specifically, SDGE reported that its Protection System Maintenance and Testing Program (PSMP) did not include sufficient basis information to support the listed intervals and sufficient summaries of procedures. This issue began October 31, 2009, the date SDGE’s previous program went into effect, and ended September 1, 2015, when SDGE finished mitigation. The root cause of this issue was less than adequate documentation. This is SDGE's first issue of noncompliance with this requirement and posed minimal risk to the Bulk Power System. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, SDGE's PSMP did not include sufficient basis to support the listed intervals and sufficient summaries of procedures. This could potentially lead to Protection System maintenance and testing being performed in a manner that is inconsistent with the intent of the PSMP. However, this is largely a documentation issue. In the case of the basis information, SDGE did have intervals listed for all of the protection system components, so maintenance and testing was being performed for all of the business units. In the case of the lack of summaries of procedures, SDGE did have procedures developed as part of its maintenance management systems in which the maintenance and testing was performed, even if it was not explicitly referred to by the PSMP. Additionally, with the adoption of version 2 of this Standard, the basis information and summary of procedures are no longer required. No harm is known to have occurred. SDGE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, SDGE: 1) modified its PSMP to be compliant with the new version of the Standard, PRC-005-2. WECC verified that SDGE completed mitigating activities.
2016-04-28 | Western Electricity Coordinating Council (WECC) | San Diego Gas & Electric (SDGE) | NCR05377 | WECC2014013596 | PRC-005-1b | R2 | On March 4, 2014, SDGE submitted a Self-Certification stating that as a Transmission Owner, it had a potential issue of noncompliance with PRC-005-1b R2. Specifically, SDGE reported that it failed to perform maintenance on a substation battery within the interval prescribed by its maintenance and testing program. This issue began November 4, 2013, the due date for the maintenance of the battery, and ended February 19, 2014, when SDGE conducted the required maintenance on the battery. The root cause of this issue was human error - the trigger date in SDGE's maintenance management system was incorrect. This issue was identified and reported timely, and posed minimal risk to the Bulk Power System. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, SDGE failed to maintain a battery system in accordance with its defined maintenance interval, which could potentially result in a premature failure of the battery. However, SDGE implemented a maintenance management system to track preventive maintenance and provide reminders of when maintenance is due. SDGE also conducts monthly and quarterly maintenance of the batteries. Additionally, SDGE implemented good detective controls to detect a battery failure. Specifically, SDGE implemented an alarm system that alerts operators in the case of a loss of AC power and/or battery charger trouble. The monthly and quarterly maintenance of the battery system may also detect any trouble with the battery. Further, had SDGE detected the missed interval, it likely would have corrected the condition due to its good corrective controls. For example, SDGE conducted the battery maintenance within a week of detecting the missed maintenance interval. SDGE also implemented compensating controls to lessen the risk to the BPS. Specifically, SDGE has a redundant battery charger as part of the system that may provide the needed DC power in the case of failure of the battery, given that AC power is still available. SDGE’s relevant prior noncompliance with PRC-005-1b R2 includes NERC Violation IDs: WECC2012011056. WECC did not consider WECC2012011056 a factor in determination of CE treatment because it had a different root cause. In that instance, SDGE overlooked maintenance for a battery during major construction at one of its substations. | To mitigate this issue, SDGE: 1) performed required maintenance on the battery; 2) implemented an additional review process for its battery maintenance work order schedule dates; 3) created a report that will allow it to annually monitor and review the accuracy of scheduled maintenance dates at the beginning of each year; and 4) verified that all scheduled maintenance was completed on time and in accordance with SDGE's maintenance program during its annual review. WECC verified that SDGE’s completed mitigating activities.
2016-03-31 | Florida Reliability Coordinating Council (FRCC) | Tallahassee, City of (TAL) | NCR00073 | FRCC2015015152 | EOP-005-2 | R6 | On August 14, 2015, TAL submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue of EOP-005-2 R6. TAL could not verify the capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial loads, because TAL units were modeled with a much larger MVAR capability than the units are actually capable of. TAL evidence shows each TAL unit capable of 99,999 MVAr. This discrepancy between the model and unit capability demonstrates the simulations performed on July 18-19, 2013 did not verify the capability of generating resources required to control voltages within acceptable operating limits since the model would allow the TAL units to produce more VARs during the simulation than is possible. Also, TAL evidence states “Island blackout will occur if any bus voltage goes below 0.3 per unit and above 2.0 per unit. Island blackout will occur if frequency goes beyond 60 Hz +/- 5 Hz”, demonstrating the simulations performed on July 18-19, 2013 did not verify the location and magnitude of Loads or capability of generating resources required to control voltages and frequency within acceptable operating limits. These values (0.3 to 2.0 per unit voltage and 55 to 65 Hz) are well outside TAL’s acceptable operating limits which is shown in separate TAL evidence that TAL’s acceptable operating limits for voltage and frequency are +/- 10% and 59.9 to 61.0 Hz respectively. Root Cause: TAL personnel did not correctly order a dynamic study from their contractor, and did not realize it, until performing an internal compliance evidence review. TAL did attempt to contact the Reliability Coordinator (RC) and submit a RC study from July 18 - July 19, 2013, as evidence of compliance, however FRCC Compliance does not agree that the RC's study parameters as described above meets TAL's EOP-005-2 R6 obligations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity had a documented restoration procedure in place that was approved during FRCC's 2013 Restoration Drill, as required by EOP-006-2 R10. However, there were no Dynamic analysis studies used in the drill, and TAL admittedly had not conducted a dynamic study to verify its restoration capabilities. TAL’s risk to the BPS, however, was mitigated by the fact that neither of the two larger registered entities with which TAL is interconnected (Duke Energy and Southern Company) are dependent on TAL resources for generation or transfer, during a blackout event. And conversely, TAL’s restoration plan documents the capability it has to restore TAL’s system by using its ties to Duke Energy Florida (DEF) and Southern Company assets. No harm is known to have resulted from this issue. FRCC considered TAL’s compliance history in determining the disposition track. TAL’s relevant prior noncompliance with EOP-005-1 R7 includes a 2009 audit finding, FRCC200900283, where the entity failed to demonstrate verification of its restoration procedure by actual testing or by simulation. TAL's subsequent mitigation plan (FRCMIT002929) was completed and certified on 10/1/2010. The mitigating activities and milestones of the plan centered around TAL securing a valid restoration simulation study, and in September of 2010, Florida State University delivered to TAL the following study: Simulation-Assisted Analysis of System Restoration from Black Start Resources for City of Tallahassee Electric Utility. This version of the EOP-005 standard did not require TAL to have performed a dynamic simulation, as is now required by EOP-005-2 R6. | To mitigate this issue, TAL completed the following mitigation activities by: 1) Performing a dynamic simulation study as required by EOP-005-2 R6; 2) Developing a process document wherein TAL conducts a dynamic simulation of its system at least every five years. Including provisions (controls) that take into account system changes where: • The study will be performed if TAL encounters system changes have been made that are judged sufficient to render the latest dynamic study inadequate; • The study will be performed if TAL’s interconnects encounters system changes have been made that are judged sufficient to render the latest dynamic study inadequate; • Once the dynamic study is completed, TAL responsible staff will verify that the study tests and verifies the TAL black start restoration plan (SOP-33), and complies with NERC Standard EOP-005-2, R6. FRCC verified completion of the mitigation on 1/20/2016.
2016-03-31 | Midwest Reliability Organization (MRO) | American Transmission Co., LLC (ATC) | NCR00685 | MRO2016015461 | PER-003-1 | R2 | On December 30, 2015 ATC submitted a Self-Log stating that as a Transmission Operator, it had an issue of PER-003-1 R2. Specifically, the ATC System Control Operator assigned to perform real-time Transmission Operator reliability related tasks allowed his NERC Certification to expire on July 18, 2013. The Operator renewed his NERC Certification on July 29, 2013. Between July 18, 2013 and July 29 2013, the Operator performed real-time Transmission Operator reliability tasks. This issue resulted from an administrative failure to ensure the timely renewal of a NERC Certification by the System Control Operator. The Operator failed to complete the administrative actions necessary for the renewal of his certification and ATC’s administrative tracking system was insufficient to ensure the NERC Certification remained current. The issue began on July 18, 2013, when the Operator let his certification lapse, and ended on July 29, 2013, when the Operator renewed his certification. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is minimal as the Operator had completed all his training hours and had the necessary certification qualifications. The issue was solely related to the Operator failing to take the administrative actions necessary to timely renew his certification. Further, the duration of the issue was brief (11 days). Finally, ATC's Operations Management team conducted a review and determined that NERC Certifications for all other ATC real-time System Control Operators were valid and current. This is ATC's first issue with PER-003-1. | To mitigate this issue, ATC: 1) confirmed that the Operator renewed his NERC Certification; 2) transitioned its Operation Management team from using an Excel spreadsheet to using Quality Training Systems’ Quality Training Database (QTD). The QTD has internal controls including a warning that must be acknowledged each time the database is opened. This warning lists all of the System Control Operators whose NERC Certification will expire within the next 6 months and the associated expiration dates; and 3) created a policy requiring its Control Center managers to review the QTD bi-monthly. ATC stated that mitigating activities were complete as of July 29, 2013.
2016-03-31 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC) | NCR00824 | MRO2015015289 | FAC-008-3 | R6 | On September 18, 2015, MEC submitted a Self-Log stating that as a Generation Owner, it had an issue with FAC-008-3 R6. Specifically, MEC identified a wind farm generator (251.02 MW) lead line rating (345 kV) that was not documented in either the generator or transmission Facility Rating documentation. The cause of this issue was the lack of effective coordination between the transmission and the generation departments. The two departments initially agreed upon where to document the lead line rating, but a subsequent review changed the location, and the documentation never occurred. The issue began on July 31, 2015, when the wind farm came online, and ended on August 7, 2015, when the lead line was added to generator ratings. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to document the lead line did not lead to a Facility Rating error. Further, the risk is reduced because MEC's design standard methodology is to not have the lead line be the most limiting element. Additionally, the lead line was part of a radial generation interconnection facility which could not affect networked flows on the Bulk Electric System. Further, MEC reviewed all wind farms commissioned since September 2014 and confirmed that there were no similar instances. Finally, the risk was reduced by the brief (8 days) duration of the issue. MRO considered MEC's FAC-008-3 R6 compliance history in determining the disposition track. MEC's relevant prior noncompliance with FAC-008-3 R6 includes: NERC Violation ID MRO2014014474 (FAC-009-1 R1). MRO determined that MEC's compliance history should not serve as a basis for applying a penalty. MRO2014014474 involved two lead lines that were not documented at two wind farms. But the current issue was not caused by any failure to mitigate MRO2014014474, and it appears that MRO2014014474 led to an increased level of awareness at MEC that contributed to the short duration of the current issue. | To mitigate this issue MEC: 1) added the omitted generator lead line to generator ratings documentation; 2) verified and confirmed all series components had been listed for wind farms commissioned 12 months prior to the Self-Log; and 3) instituted an internal control to confirm that all documentation is completed prior to the in service date of wind farms. MEC stated that mitigating activities were complete as of September 30, 2015.
2016-03-31 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC) | NCR00824 | MRO2016015470 | PRC-005-2(i) | R3 | On December 28, 2015, MEC submitted a Self-Log stating that as a Transmission Owner, it had two battery maintenance issues with PRC-005-2(i) R3. Regarding the first issue, MEC’s time-based maintenance program established under PRC-005-2(i) R1 contains maximum maintenance intervals for measuring the internal ohmic values of batteries. MEC’s inventory tracking system included valve regulated lead acid (VRLA) batteries at two substations which had been incorrectly identified as vented lead acid (VLA) batteries. Because VLA batteries have longer maintenance intervals than VRLA batteries, the two incorrectly identified batteries missed the six-month interval for measurement of the internal ohmic value. Regarding the second issue, MEC's 2015 schedule for performing internal ohmic value measurements was set in February, 2015. In May 2015, two VRLA batteries at a new substation were installed and tested, but not added to the 2015 maintenance schedule. This resulted in the two VRLA batteries at issue not being tested for internal ohmic value within the six month interval. The cause of the first issue was an identification error when entering the battery types into MEC's inventory tracking system. MEC incorrectly entered the batteries as VLA batteries instead of VRLA batteries. The cause of the second issue resulted from the fact that the batteries were added to a new facility and MEC had no internal procedures to update the facility's maintenance schedule. The first issue began on September 30, 2015, when the six month interval for internal ohmic value measurement was missed, and ended on December 2, 2015 when the batteries were tested. The second issue began on November 30, 2015, when the six month interval for internal ohmic value measurement was missed, and ended on December 21, 2015, when the batteries were tested. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For the first instance, MEC missed the maintenance interval by a short period of time (63 days). Further, MEC reviewed all VLA batteries in its inventory system and confirmed that these batteries were the only misclassified VRLA batteries. Finally, partial maintenance, including verification of station dc supply voltage and visual inspection for unintentional grounds, occurred within the required four month interval. For the second instance, MEC missed the maintenance interval by less than a month (21 days). Other required maintenance activities were performed within the required intervals. Finally, MEC reviewed its inventory of batteries installed at substations commissioned in 2015 and confirmed that there were no other issues. MRO considered MEC's PRC-005-2(i) R3 compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. | To mitigate this issue MEC: 1) corrected the inventory tracking spreadsheet for the batteries related to the first issue and performed the required measurements; 2) took the measurements for the batteries related to the second issue; and 3) instituted a policy to review VRLA battery measurement schedules at least once every three calendar months to prevent new facilities and/or batteries from being overlooked. MEC stated that mitigating activities were complete as of December 21, 2015.
2016-03-31 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC) | NCR00824 | MRO2016015471 | VAR-002-4 | R3 | On December 28, 2015, MEC submitted a Self-Log stating that, as a Generator Operator, it had an issue of VAR-002-4 R3. Specifically, MEC failed to notify the associated Transmission Operator (TOP) within 30 minutes of a change when one of its wind generation facilities stopped operating in automatic voltage control mode. MEC operates numerous wind farms within the MRO region. MEC is the associated TOP for all but three of its wind farms. MEC has configured two of these three wind farms so that automatic alerts, such as a change in the automatic voltage control mode, be sent to the associated TOP. On November 18, 2015, at the affected wind farm, where automatic alerts are not sent to the TOP, the wind farm experienced a change in status and stopped operating in automatic voltage control mode. The automatic EMS alarm went to MEC's control center and MEC control center personnel did not inform the associated TOP within 30 minutes. The cause of this issue was the wind farm’s EMS alarm for loss of automatic voltage control being routed to MEC’s control center and not the associated TOP. MEC control center personnel were unaware the alarm was not also routing to the associated TOP, and therefore did not take action to manually inform the TOP of the automatic voltage control loss within 30 minutes of the status change This issue began on November 18, 2015, when MEC did not inform the associated TOP within 30 minutes of the change, and ended five minutes later on November 18, 2015 when automatic voltage control mode was re-established. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Wind generation facilities have limited voltage control capabilities as compared to conventional dispatchable generation, and are not as heavily relied upon for voltage regulation by system operators. Additionally, due to the small generation output of this wind farm (140 MW), this facility would have a minor impact on the system's ability to respond to reactive power demands. Moreover, the risk was further reduced by the short duration (five minutes) of the issue. No harm is known to have occurred. MRO considered MEC's VAR-002-4 R3 compliance history in determining the disposition track. MEC's relevant prior noncompliance with VAR-002-4 R3 include(s): NERC Violation ID MRO2014014443 (VAR-002-1b R3). MRO determined that MEC's compliance history should not serve as a basis for applying a penalty. MRO2014014443 involved 20 distinct instances where MEC failed to tell the associated TOP the expected duration of the change in status of an automatic voltage regulator. The current issue does not involve failing to inform a TOP of the expected duration of a change in status of an automatic voltage regulator. Further, stating the expected duration is no longer a requirement under VAR-002-4 R3, and it would not be justified to impose a penalty upon past history that no longer constitutes noncompliance. Finally, the current issue was not caused by any failure to mitigate MRO2014014443. | To mitigate this issue MEC: 1) returned the wind farm to automatic voltage control mode; 2) added an EMS alarm point for automatic voltage control status to ICCP to automatically notify the TOP for the affected wind farm and verified that the alarm is working; 3) added a step to its compliance checklist for commissioning new wind farms to verify voltage control status change alarms are programmed to automatically notify all associated TOPs, including TOPs that are not MEC; 4) implemented automated alarms for voltage control status changes for all wind farms, regardless of whether MEC is the associated TOP; and 5) revised its operator guide and EMS alarm text to instruct MEC to call the associated TOP when the TOP is not MEC. MEC stated that mitigating activities were complete as of December 16, 2015.
2016-03-31 | Northeast Power Coordinating Council (NPCC) | Entergy Nuclear Indian Point 2, LLC (EIP2) | NCR07073 | NPCC2015015367 | PRC-002-NPCC-01 | R4 | On November 17, 2015, Entergy Nuclear Indian Point 2, LLC submitted a Self-Report stating that, as a GO, it had an issue of PRC-002-NPCC-01, R4. The standard had a phased implementation plan, requiring entities to be compliant by 10/20/2015. Installation of the new Disturbance Monitoring Equipment (DME) required by PRC-002-NPCC-01 was not completed by EIP2 by 10/20/15. DME installation could only be completed on the nuclear unit during a refueling outage, which EIP2 has scheduled every 24 months. EIP2 had originally intended to complete the DME installation during their outage in 2014. However, delays in project scoping prevented the work from being completed during the 2014 refueling outage, and delayed the work until the 2016 refueling outage. The root cause of the violation was determined to be an ineffective project management procedure which did not require peer checks or SME discussions prior to approval. This caused the installation to be delayed past the intended refueling outage. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The necessary DMEs are not utilized for the actual operation of the system, rather the data they collect is used to analyze system events. EIP2 already has some sequence of event data currently available for Indian Point Unit 2 BES elements to assist in BES event analysis. Monitoring and reporting capabilities also exist for the EIP2 345 kV switchyard BES elements. This was also an isolated incident, as Entergy is in compliance with PRC-002-NPCC-01 for Indian Point Unit 3 because they completed the necessary DME installation. No harm is known to have occurred as a result of the noncompliance. NPCC considered EIP2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, EIP2 will complete the following mitigation activities by April 30, 2016 : 1) Will complete installation of the necessary DME during their refueling outage in the spring of 2016. 2) Replaced their project management procedure with a new procedure that requires discussions with subject matter experts or management prior to project initiation.
2016-03-31 | Northeast Power Coordinating Council (NPCC) | Middletown Power LLC (MP) | NCR07141 | NPCC2015015377 | PRC-005-2 | R3 | During an Off-site Compliance Audit conducted from June 1, 2015 to September 11, 2015, NPCC determined that Middletown Power LLC, as a GO, had an issue of PRC-005-2, R3. In 2011, MP installed a Gas Insulated Switchgear that tied their Unit 4 generator to the Middletown substation. As part of the installation, the Unit 4 relays were tested, and a trip-test procedure was developed to document the procedure to be followed in testing the breaker relay circuits. When the relays were tested, it was incorrectly determined that this testing was also sufficient to serve as a DC functional trip test. Although the trip-test procedure was not properly performed, MP updated their PRC-005 tracking spreadsheet as if the testing was completed, which negated the need to perform the test in 2012 as was originally required by their four year testing interval. The violation started January 1, 2012, when the four year interval from the previous trip test was passed, and concluded on September 22, 2015, when the trip test was performed. The root cause of the issue was determined to be the 2011 incorrect decision to use the protective relay tests as a substitute for a DC functional trip test. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were no misoperations of the protection system during the time period of the violation. Backup protection systems are in place to operate in the event that any part of the primary relaying system fails. The DC functional trip test performed on September 22, 2015 showed that there were no issues with the DC circuitry. This was an isolated incident, as the DC functional trip testing was performed for the other Middletown generators as scheduled. No harm is known to have occurred as a result of the noncompliance. NPCC considered MP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MP: 1) Performed the DC functional trip test on Unit 4 on September 22, 2015. 2) All NRG plants, including MP, have been instructed to routinely contact NRG's Regulatory Compliance group for any future compliance issues to ensure their actions are compliant. NPCC has verified the completion of all mitigation activity.
2016-03-31 | Northeast Power Coordinating Council (NPCC) | Plainfield Renewable Energy, LLC | NCR11405 | NPCC2015015332 | PRC-005-1.1b | R1 | On November 6, 2015, Plainfield Renewable Energy, LLC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-005-1.1b R1. In the period spanning from December 12, 2013 through March 1, 2016, Plainfield Renewable Energy, LLC did not have in place a fully documented Protection System Mainteneace and Testing Program. The root cause of the issue was that the previous owner of the generating facilities had been using a simplified template, or guide, as the essential outline for carrying out maintenance activities. After Plainfield Renewable Energy, LLC took ownership of the facilities in mid-2015, it realized that this guideline did not contain sufficient detail to be compliant with the standard, and proceeded to draft a more formal and comprehensive procedural document. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). All protection systems at the facility are in good working order. The generating facility was commissioned in December 2013 when all systems were tested, and additional maintenance thereafter has been performed in accordance with recommendations issued by the respective manufacturers of various components of its Protection System. Such maintenance practices are in compliance with the standard. Therefore, the lack of a formal maintenance procedure in place is strictly a documentary issue, and represents a minimal impact on the reliable operation of the BES system. No harm is known to have occurred as a result of this issue of noncompliance. NPCC considered Plainfield Renewable Energy, LLC's compliance history and determined there are no prior relevant instances of noncompliance. | To mitigate this issue, Plainfield Renewable Energy, LLC: 1) has put in place a procedure for documenting the Protection System maintenance and testing program for its Protection Systems, effective 3/2/2016 (Procedure No.: PRE-3050, v.3); and 2) currently requires for its maintenance procedure a review cycle of 3 years or less as dictated by changes to future versions of this NERC standard. NPCC has verified the completion of all mitigation activity.
2016-03-31 | Northeast Power Coordinating Council (NPCC) | ReEnergy Livermore Falls (RLF) | NCR11514 | NPCC2016015447 | TOP-002-2.1b | R13 | On January 5, 2016, ReEnergy Livermore Falls submitted a Self-Report stating that, as a GOP, it had an issue of TOP-002-2.1b, R13. In accordance with ISO-NE operating procedure, Reactive Capability testing is to be performed on a 5 year schedule. The last Reactive Capability testing was completed by RLF in 2010, therefore RLF was scheduled to complete a Reactive Capability test in 2015. The ISO-NE specified time windows for Reactive Capability testing is June 1-September 15 for lagging testing, and March 1-October 31 for leading testing. The plant manager at RLF discovered in October that the testing should be completed in 2015. RLF immediately scheduled the testing, and completed the Reactive Capability testing for both the leading and lagging capabilities on October 30. The leading Reactive Capability testing was accepted by ISO-NE, however the lagging testing was rejected as the testing was completed outside of the specified window of June 1-September 15. A review after the missed testing determined that ISO-NE had sent a notification to RLF in early 2015 stating the need for testing to be completed that year. However, the email was sent to a corporate ReEnergy contact rather than a plant level contact, and the notification was not passed on to the RLF plant manager. The root causes of this violation were determined to be listing the ReEnergy corporate contact as the lead contact for ISO-NE's Customer and Asset Management System, as well as the lack of a compliance tracker to dictate when periodic activities needed to be completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Due to the size of the RLF facility (39 MW), the potential impact on the BPS is minimal. The October 2015 testing of the lagging reactive capability did show similar results to the lagging reactive capability data that had been provided to ISO-NE in the past. Even in the event of a significant change in reactive capability of the facility, the impact on the BPS would still be minimal due to the generator's relatively small contribution to the BPS. No harm is known to have occurred as a result of the noncompliance. NPCC considered RS's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RLF will complete the following mitigation activities by June 15, 2016 : 1) Will complete lagging Reactive Capability testing once the window for testing opens on June 1. 2) Has developed a compliance calender to track all periodic activites required by RLF. The calender will be reviewed monthly during regularly scheduled RLF compliance committee conference calls. 3) Has updated the lead contact in ISO-NE's Customer and Asset Management System to be in the RLF plant manager to ensure that all information requests and testing reminders make it directly to the facility.
2016-03-31 | Northeast Power Coordinating Council (NPCC) | ReEnergy Stratton (RS) | NCR10352 | NPCC2016015448 | TOP-002-2.1b | R13 | On January 5, 2016, ReEnergy Stratton submitted a Self-Report stating that, as a GOP, it had an issue of TOP-002-2.1b, R13. In accordance with ISO-NE operating procedure, Reactive Capability testing is to be performed on a 5 year schedule. A testing variance was granted to RS in 2010 by ISO-NE resetting the periodic testing requirement, therefore RS was scheduled to complete a Reactive Capability test in 2015. The ISO-NE specified time windows for Reactive Capability testing is June 1-September 15 for lagging testing, and March 1-October 31 for leading testing. The plant manager at RS discovered in October that the testing should be completed in 2015. RS immediately scheduled the testing, however a significant failure at the facility caused a forced outage for the remainder of October and November and the testing was unable to be completed. A review after the missed testing determined that ISO-NE had sent a notification to RS in early 2015 stating the need for testing to be completed that year. However, the email was sent to a corporate ReEnergy contact rather than a plant level contact, and the notification was not passed on to the RS plant manager. The root causes of this violation were determined to be listing the ReEnergy corporate contact as the lead contact for ISO-NE's Customer and Asset Management System, as well as the lack of a compliance tracker to dictate when periodic activities needed to be completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Due to the size of the RS facility (48 MW) the potential impact on the BPS is minimal. The 2010 waiver granted by ISO-NE allowing RS to not perform the testing was due to the non-essential nature of the RS facility. Even in the event of a significant change in reactive capability of the facility, the impact on the BPS would still be minimal due to the generator's relatively small contribution to the BPS. No harm is known to have occurred as a result of the noncompliance. NPCC considered RS's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RS will complete the following mitigation activities by June 15, 2016 : 1) Will complete both leading and lagging Reactive Capability testing by early June 2016. The window for leading testing opens on March 1, while the window for lagging testing opens on June 1. 2) Has developed a compliance calender to track all periodic activites required by RS. The calender will be reviewed monthly during regularly scheduled RS compliance committee conference calls. 3) Has updated the lead contact in ISO-NE's Customer and Asset Management System to be in the RS plant manager to ensure that all information requests and testing reminders make it directly to the facility.
2016-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Baltimore Gas and Electric Company (BGE) | NCR00689 | RFC2015014797 | FAC-003-3 | R6 | On March 27, 2015, BGE submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of FAC-003-3 R6. BGE had an issue related to the timing of its inspection of 9 transmission lines’ rights-of-way. Prior to July 1, 2014, FAC-003-1 governed how TOs were supposed to manage vegetation located on or near transmission rights-of-way to minimize outages. FAC-003-1 R1 required the TO to have a formal Transmission Vegetation Management Program (TVMP) in place that included the TO’s objectives, practices, approved procedures, and work specifications. FAC-003-1 R2 also required TOs to have an annual plan for vegetation management work to ensure the reliability of the system. Under BGE’s TVMP in place at the beginning of 2014, BGE conducted its vegetation inspection period during the dormant vegetation season lasting from autumn to early spring and performed rights-of-way inspections within 18 months of the prior inspection for each rights-of-way. This meant that if BGE conducted a rights-of-way inspection in October 2013, it did not need to complete another rights-of-way inspection on that same transmission line until April 2015. FAC-003-3 replaced FAC-003-1 and became effective on July 1, 2014. FAC-003-3 changed the requirements for transmission vegetation management and FAC-003-3 R6 required each TO and applicable Generator Owner to perform a vegetation inspection of 100% of its applicable transmission lines at least once per calendar year and with no more than 18 calendar months between inspections on the same rights-of-way. This change meant that BGE would be in violation if it followed its existing TVMP and performed a rights-of-way inspection in October 2013 and did not perform another inspection on that same transmission line until April 2015. Following an internal compliance review, BGE discovered that it did not schedule or perform inspections on 9 transmission rights-of-way in the calendar year 2014. BGE performed all 33 of its required rights-of-way inspections between October 2013 and April 2014. BGE performed 9 of those 33 inspections during that time frame in late 2013 and those 9 inspections were neither scheduled nor performed during 2014. BGE did not comply with FAC-003-3 R6 because it did not perform 9 rights-of-way inspections during the 2014 calendar year. BGE did not perform the inspection during the 2014 calendar year because BGE believed completing the inspections in accordance with its TVMP in place in 2014 was enough for compliance. This noncompliance concerned the management practice of implementation. Implementation is involved because BGE did not fully understand how to comply with FAC-003-3 R6. BGE incorrectly believed it was compliant with FAC-003-3 R6 based off of its TVMP in effect in 2014 that required performing rights-of-way inspections within 18 months of the prior inspection for each right-of-way. BGE believed that following its TVMP would achieve compliance with FAC-003-3 R6. This incorrect belief was the root cause of the noncompliance. The duration of this noncompliance is from July 1, 2014, the date BGE was required to comply with FAC-003-3 R6, to April 2, 2015, the date BGE completed its 9 rights-of-way inspections that were last inspected in 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. BGE has other redundant controls built into its vegetation management program that minimize the risk of trees and other vegetation growing too large where the vegetation makes contact with transmission lines. These controls include performing additional trimming, spraying, repairs, and culvert inspections on an as needed basis. BGE’s transmission inspections were traditionally conducted during the dormant vegetation season meaning any vegetation growth conditions observed during inspections in late 2013 such as tree height and branch length would remain largely unchanged until the following April. These redundant controls would prevent and address any issues associated with vegetation growth in 2014 for the 9 rights-of-way at issue. No harm is known to have occurred. Although this is BGE’s first issue with FAC-003-3 R6, BGE had a prior violation of FAC-003-1 R2 where an overgrown tree made contact with a 230 kV transmission line that caused an outage. Per NERC Guidance from April 2015, the Regions have discretion as to whether or not they will aggravate a penalty based on prior violations for which mitigation was completed more than three years prior to the date on which the instant noncompliance began. Here, ReliabilityFirst will not aggravate the penalty based on that prior violation because BGE has demonstrated its ability to identify and correct these types of noncompliances, the quality of BGE’s TVMP in place in 2014, and because the instant noncompliance is minimal risk. ReliabilityFirst determined that BGE's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, BGE: 1) Transitioned its vegetation management program to conform to the annual 18 month and calendar year inspection requirements in FAC-003-3 R6. 2) Shifted its 2015 inspection period for 230 kV and 500 kV transmission facilities to a January-April timeframe; 2) Completed its 9 rights-of-way inspections that were last inspected in 2013 as of April 2, 2015; and 3) Added an internal control to its Annual Ground Inspections report, which BGE uses to track ground inspections for its rights-of-way, to ensure that all inspections are completed within 18 months of the prior inspection and within the calendar year. ReliabilityFirst has verified the completion of all mitigation activity.
2016-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Commonwealth Edison Company (ComEd) | NCR08013 | RFC2015014798 | FAC-008-3 | R8 | On March 30, 2015, ComEd submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of FAC-008-3 R8. ComEd did not follow its internal process for notifying PJM, ComEd’s Transmission Operator, of a facility ratings change. On February 20, 2015, during ComEd’s process to review the elements that limit the facility rating of a 345kV line for a potential upgrade, ComEd’s planning engineers discovered a potential discrepancy in the ratings of the line. The discrepancy dated back to a system improvement project ComEd underwent in the fall of 2012 to upgrade the relays on this 345kV line. Prior to this project, the relay settings were the limiting element for Long-Term Emergency (LTE), Short-Term Emergency (STE), and Load Dump (LD) ratings on this line. After completing the project, the relays settings were no longer the limiting element for any ratings on this 345kV line. On March 2, 2015, ComEd completed a review of the ratings of this 345kV line and discovered that the LTE, STE, and LD ratings on the 345kV line were each too low and that ComEd did not update its facility ratings database or notify PJM of the ratings change following the completion of the 2012 project. After discovering this, ComEd issued updated ratings and increased the LTE, STE, and LD ratings on the 345kV line. After increasing the ratings on this 345kV line, ComEd performed an extent of condition analysis that reviewed the ratings for all transmission facilities where relay trip settings and/or relay thermal limits are the limiting element for at least one rating category associated with that facility. This analysis was performed to confirm that all changes had been reported to PJM and that the current ratings were correctly entered into the database. ComEd identified additional issues with information in its facility ratings database during this analysis. These issues included: two additional instances where the relays had been upgraded and notification sent to the engineering planning group, but the database was not updated or the rating change communicated to PJM, six instances where the Current Transformer (CT) thermal limit had been entered incorrectly in the facility ratings database as the relay thermal limit, and missing relay thermal trip values for certain 138kV lines, which are characterized as Operationally Significant Circuits (OSC) under PRC-023. This noncompliance concerned the management practice of implementation because ComEd employees failed to follow ComEd’s process for updating ratings information and communicating updated ratings to PJM. ComEd did not ensure that the facility ratings database had correct and updated ratings at all times. The root cause was ComEd's failure to follow the process for updating ratings information. The duration of this noncompliance is from January 1, 2013, the date ComEd was required to comply with FAC-008-3 R8, to July 31, 2016 the date ComEd will complete its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For the 345kV line rating issue, the actual line ratings were higher than the ratings being used by ComEd meaning the ratings ComEd was using were more conservative than the actual ratings. ComEd reviewed real time flows on this line and the line only reached 64% of its maximum rating. This means that the line was never overloaded and was operated at a low risk of failure. The risk presented by this noncompliance was that PJM did not have accurate ratings in their model. PJM not having accurate ratings in their model is a risk because using inaccurate ratings makes PJM’s model less accurate. PJM’s model covers 13 states and the District of Columbia. Since the actual ratings are higher than the communicated ratings, PJM was not aware that this line had additional ampacity if needed. This could have provided PJM additional options when mitigating contingencies and dispatching generation. It is important that PJM as the Transmission Operator is operating the BES with accurate information and models with data provided by the Transmission Owners, in this case ComEd. For the additional issues discovered during ComEd’s extent of condition analysis, the risk is also minimal because of the reasons stated above. No harm is known to have occurred. This is ComEd’s first issue with FAC-008-3 R8. | To mitigate this issue, ComEd will complete the following mitigation activities by July 31, 2016: 1) Determine the best practice or tool for tracking ratings database updates; 2) Implement the best practice method identified in Milestone Activity 1; 3) Calculate thermal ratings for any 138 kV BES relays that do not currently have calculated values and communicate those ratings to Transmission Planning; 4) Develop a checklist and/or improve the peer check process to confirm all potentially limiting elements of a facility have been reviewed and verified correct in the ratings database; 5) Update Transmission Ratings Update Procedure, AM-CE-4023, to include the approved mechanism for tracking pending and completed projects that impact the ratings of a facility, and notifications; 6) Use the thermal limit relay results and to evaluate the calculated ratings against the facilities and determine any potential deviations; 7) Review AM-CE-4023-R0001, ComEd’s Transmission Ratings Methodology, for potential clarification and update as needed; 8) Perform a risk based analysis of all deviations, create corrective actions to develop and initiate an appropriate mitigation plan for each, and create follow-up assignments to implement the plan; 9) Implement change management, to notify all affected personnel of new processes and related procedures updates, and to notify peers at other Exelon utilities; and 10) Conduct an effectiveness review of corrective actions. ComEd needs until July 31, 2016 to complete its mitigation actions because of the large size and scope of the mitigation actions. ComEd is developing and implementing a best practice or tool for tracking ratings database updates, calculating thermal ratings for any 138kV BES line that does not have them, and performing a risk based analysis of all deviations among others. The lengthy and wide-ranging scope of these mitigation actions cause a longer completion timeline.
2016-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2015015214 | PRC-005-1 | R2 | On August 31, 2015, Consumers submitted a Self-Report stating that, as a Distribution Provider, it had an issue of PRC-005-1 R2. On August 20, 2015, Consumers conducted an engineering review of a project to modify relaying and control equipment to accommodate a new control house at a particular substation. During this review, a Consumers engineer discovered that two of the relays scheduled to be removed as part of the project scope were not listed in the company’s protection system database. Further review by Consumers determined that these two relays had not been maintained in accordance with the company’s PRC-005 maintenance program. The root cause of this noncompliance was Consumers’ failure to accurately and completely identify its protection system equipment following its sale of transmission assets to Michigan Electric Transmission Company, LLC (METC) in 2002. After this sale, Consumers and METC split all of the assets between the two companies. However, Consumers mistakenly listed METC as the owner of the two relays at issue in this noncompliance when, in fact, Consumers owned them. Consequently, Consumers did not list these two relays in its PRC-005 maintenance program. This failure implicates the management practices of: (a) implementation because the failure related to the modification of grid assets that could have compromised grid reliability; and, (b) asset and configuration management because Consumers failed to maintain an accurate inventory of assets. The duration of this noncompliance is from December 31, 2009, the date Consumers was required to comply with PRC-005-1 R2, to August 21, 2015, the date Consumers performed the requisite maintenance on the two relays at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, this misidentification only affected two out of the approximately 1,500 NERC relay schemes owned by Consumers. So, this noncompliance is not indicative of a systemic issue at Consumers. Second, had either of these relays failed to operate, the backup fault clearing system would have cleared any fault remotely with a minimal time delay. ReliabilityFirst also notes that Consumers conducted a review of its fault analysis database and determined that no faults occurred on the affected Bulk Electric System elements during the period of this noncompliance. No harm is known to have occurred. ReliabilityFirst considered Consumers' PRC-005 R2 compliance history in determining the disposition track. Consumers' relevant prior noncompliance with PRC-005 R2 includes: RFC200900186. A Settlement Agreement covering violations of PRC-005-1 R2.1 was filed with FERC under NP11-112-000 on February 23, 2011. On March 25, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. The prior violation is distinguishable from the instant violation because the prior violation related to Consumers’ failure to test or maintain station batteries and DC control circuits, not relays. ReliabilityFirst determined that Consumers' compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Consumers: 1) immediately performed the requisite maintenance on the two relays at issue and added them to the PRC-005 maintenance program; and 2) reviewed and confirmed the accuracy of all (approximately 4,300) protection schemes that are listed as having been sold to METC to ensure no other relays were misidentified.
2016-03-31 | SERC Reliability Corporation (SERC) | Alabama Municipal Electric Authority (AMEA) | NCR01165 | SERC2015015429 | VAR-002-4 | R1 | On December 18, 2015, AMEA submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-4 R1. AMEA failed to operate an automatic voltage regulator (AVR) in automatic controlling voltage without prior notification to, or exemption by, the Transmission Operator (TOP). On October 22, 2015, AMEA began plant operations for the day at 9:00 a.m. The plant received instructions to generate from 10:00 a.m. to 9:00 p.m. and to maintain voltage in accordance with the assigned voltage schedule. The assigned voltage schedule required the plant to maintain voltage at 115 kV, while minimizing excursions outside of +/- 1.0 kV. AMEA started and operated both generators normally. At 4:48: p.m. the voltage regulator on generator “A” switched to manual control for an unknown reason. The switch to manual triggered a generic AVR trouble alarm that the on-shift operator did not recognize as a reportable event. Standing orders required the operator to notify the TOP of changes in the AVR status within 30 minutes, but the operator did not have procedures to identify that the cause of the generic alarm may require notification. AMEA shut down the units at 9:00 p.m. The following morning, an operator discovered the incorrect AVR operating mode while performing the normal verifications in preparation to start the plant as scheduled. The operator promptly notified the plant manager, who directed the operator to notify the TOP via electronic messaging and phone. On October 23, 2015 at 9:03 a.m., the operator received an acknowledgement from the TOP. This issue lasted from October 22, 2015 at 4:48 p.m. when the AVR status changed and the TOP was not notified, through October 22, 2015 at 9:00 p.m. when the unit was shut down. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AMEA failing to notify the TOP of changes to the AVR status could result in the TOP's inability to control transmission line voltages resulting in disturbances and loss of load. However, because the plant was in close proximity to larger generators interconnected to the same 115 kV circuit, its effect on voltage was minimal. The Planning Coordinator had not determined the transmission line to which the plant was interconnected to be critical to the reliability of the BPS. AMEA operated the AVR in manual for only about four hours before shutting down the units. While AMEA operated one unit in manual, it operated the other unit in automatic controlling voltage. AMEA maintained voltage in accordance with the voltage schedule throughout the issue. No harm is known to have occurred. SERC considered AMEA’s VAR-002-4 R1 compliance history in determining the disposition track. AMEA does not have a relevant compliance history. | To mitigate this issue, AMEA: 1) provided both operators refresher training; and 2) reviewed the procedures associated with reporting AVR status. In addition, AMEA will complete the following mitigation activities by October 1, 2016: 1) edit the plant managers standing orders to include additional guidance on investigating all alarms and alarm management; 2) work with the vendor to revise the actual alarms that are presented during a status change of the AVR. During the issue, the alarm that indicated the AVR had switched to manual mode indicated “AVR Fault” and was presented in the same color as all other non-critical alarms. AMEA has requested GE change the alarm to be more descriptive (“AVR in Manual”) and change the color of the alarm to red to indicate an issue that needs immediate attention; and 3) provide the AVR status to the TOP via telemetering processes.
2016-03-31 | SERC Reliability Corporation (SERC) | Alabama Municipal Electric Authority (AMEA) | NCR01165 | SERC2015015427 | VAR-002-4 | R3 | On December 18, 2015, AMEA submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-4 R3. AMEA failed to notify its Transmission Operator (TOP) of a change of state of the automatic voltage regulator (AVR) within 30 minutes. On October 22, 2015, AMEA began plant operations for the day at 9:00 a.m. The plant received instructions to generate from 10:00 a.m. to 9:00 p.m. and to maintain voltage in accordance with the assigned voltage schedule . The assigned voltage schedules required the plant to maintain voltage at 115 kV, while minimizing excursions outside of +/- 1.0 kV. AMEA started up and operated both generators normally. At 4:48 p.m. the AVR on generator “A” switched to manual control for an unknown reason. The switch to manual triggered a generic AVR trouble alarm. Standing orders required the operator to notify the TOP of changes in the AVR status within 30 minutes, but the operator did not have procedures to identify that the cause of the generic alarm may require notification. AMEA shut down the units at 9:00 p.m. An operator discovered the incorrect AVR operating mode the following morning while performing the normal verifications in preparation to start the plant as scheduled. The operator promptly notified the plant manager, who directed the operator to notify the TOP via electronic messaging and phone. On October 23, 2015 at 9:03 a.m., the operator received an acknowledgement from the TOP. This issue lasted from October 22, 2015 when the AVR status changed and the TOP was not notified within 30 minutes, through October 23, 2015 when the TOP was notified. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AMEA failing to notify the TOP of changes to the AVR status could result in the TOP’s inability to control transmission line voltages resulting in disturbances and loss of load. However, because the plant was in close proximity to larger generators interconnected to the same 115 kV circuit, its effect on voltage was minimal. The Planning Coordinator had not determined the transmission line to which the plant was interconnected to be critical to the reliability of the BPS. AMEA operated the AVR in manual for only about four hours before shutting down the units. While AMEA operated one unit in manual, it operated the other unit in automatic controlling voltage. AMEA maintained voltage in accordance with the voltage schedule throughout the issue. No harm is known to have occurred. SERC considered AMEA’s VAR-002-4 R3 compliance history in determining the disposition track. AMEA does not have a relevant compliance history. | To mitigate this issue, AMEA: 1) provided both operators refresher training; and 2) reviewed the procedures associated with reporting AVR status. In addition, AMEA will complete the following mitigation activities by October 1, 2016: 1) edit the plant managers standing orders to include additional guidance on investigating all alarms and alarm management; 2) work with the vendor to revise the actual alarms that are presented during a status change of the AVR. During the issue, the alarm that indicated the AVR had switched to manual mode indicated “AVR Fault” and was presented in the same color as all other non-critical alarms. AMEA has requested GE change the alarm to be more descriptive (“AVR in Manual”) and change the color of the alarm to red to indicate an issue that needs immediate attention; and 3) provide the AVR status to the TOP via telemetering processes.
2016-03-31 | SERC Reliability Corporation (SERC) | Osage Wind, LLC (Osage) | NCR11554 | SERC2015015173 | VAR-002-4 | R1 | On August 19, 2015, Osage submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-3 R1. Osage failed to operate in automatic voltage control mode and had not informed the Transmission Operator (TOP) of the change. SERC later determined that the issue related to Version 4 of the Standard. Osage entered commercial operation on June 5, 2015, while in a transition phase and not yet fully operational. Osage’s engineering and construction department maintained control of a portion of the facility where construction was still occurring. The operations department controlled the remainder of the facility. Osage’s control monitoring room in Massachusetts operated and monitored Osage remotely, along with six other sites. Osage consisted of wind turbine generators, each 1.79 MWs. Osage stepped up the combined generator output to 138 kV and transmitted it to the Bulk Power System (BPS) via a single 1.75 mile transmission line to one interconnection point. Osage did not have an automatic voltage regulator (AVR) in the usual sense of the term because it did not control voltage or power factor using a conventional excitation system. Osage controlled the reactive power (voltage and phase) supplied to the BPS at the high side of the 138 kV transformer using a solid state power electronics control system known as the wind farm management system (WFMS). Osage normally operated the voltage controller in automatic voltage control mode set for 141 kV. On June 11, 2015, technicians conducted maintenance at the site. Osage speculated that the maintenance inadvertently caused a malfunction of the site's WFMS causing the device to switch from automatic voltage control to the default unity power factor mode. Since the site was not fully operational, the control monitoring room within the operations and maintenance department had not yet fully implemented its processes to remotely monitor the state of the controller and to receive alarms for any status change of the voltage control device immediately, in order to make notifications to the TOP in a timely manner. Therefore, Osage did not immediately observe the status change and did not report the change of state to the TOP. On June 17, 2015, Osage discovered the change of state and coordinated the automatic voltage control mode restoration with the TOP. The root cause of this issue was that Osage personnel were not aware of the switch from automatic voltage control mode. This issue lasted from June 11, 2015, when the voltage controller switched from automatic voltage control mode to the default mode, through June 17, 2015, when Osage restored automatic voltage control mode. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. Operation of the voltage regulator in a mode other than automatic voltage control may lead to unanticipated responses to disturbances on the BPS. However, The BPS does not rely on wind farm output for voltage or load support because of the intermittent nature of wind energy. Based on recorded data, the reactive component Osage imposed onto the BPS during the issue was small, less than 10 MVA. After this issue Osage received a voltage schedule from the TOP allowing operation within 5 percent of the target voltage and during this issue Osage maintained within 2 percent of the target voltage. No harm is known to have occurred. SERC considered Osage and its affiliates’ VAR-002 R1 compliance history in determining the disposition track. Osage and its affiliates’ relevant prior noncompliance with VAR-002-4 R1 includes: NERC Violation ID SPP2015014829. In SPP2015014829, Osage’s affiliate, Chisholm View Wind Project, LLC (Chisholm), was fully operational. Here, Osage was in a transition stage, meaning it was only partially operational. To prevent recurrence, Chisholm made revisions to its operational procedures. Since Osage’s issue occurred during a transitional phase, similar changes at Osage would not have prevented the instant issue. SERC determined that Osage’s affiliate’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Osage: 1) restored voltage control and notified the TOP of the mode change; 2) contacted the TOP to obtain not just a target set point but also a set point range; and 3) gave the control monitoring room full access to voltage control, data, and alarms . Osage will also complete the following mitigation activities by 5/1/16: 1) improve control monitoring room procedures on responding to voltage control alarms and other reporting requirements, and make control room operators aware of the changes. 2) improve the procedure that covers when a site moves from the engineering and construction phase into operation, to include provisions to obtain the voltage schedule and full remote alarm and control capability prior to commercial operation. 3) ENEL (parent of Osage) will provide training to affected Engineering, Construction, Operations and Maintenance crews and managers.
2016-03-31 | SERC Reliability Corporation (SERC) | Osage Wind, LLC (Osage) | NCR11554 | SERC2015015175 | VAR-002-4 | R3 | On August 19, 2015, Osage submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-3 R3. Osage failed to operate its automatic voltage controller in automatic controlling voltage and had not informed the Transmission Operator (TOP) within 30 minutes of the change. SERC later determined that the issue related to Version 4 of the Standard. Osage entered commercial operation on June 5, 2015, while in a transitional phase and not yet fully operational. Osage’s engineering and construction department maintained control of a portion of the facility where construction was still occurring. The operations department controlled the remainder of the facility. Osage’s control monitoring room in Massachusetts operated and monitored Osage remotely, along with six other sites. Osage consisted of wind turbine generators, each 1.79 MWs. Osage stepped up the combined generator output to 138 kV and transmitted it to the Bulk Power System (BPS) via a single 1.75 mile transmission line to one interconnection point. Osage did not have an automatic voltage regulator (AVR) in the usual sense of the term because it did not control voltage or power factor using a conventional excitation system. Osage controlled the reactive power (voltage and phase) supplied to the BPS at the high side of the 138 kV transformer using a solid state power electronics control system known as the wind farm management system (WFMS). Osage normally operated the voltage controller in automatic voltage control mode set for 141 kV. On June 11, 2015, technicians conducted maintenance at the site. Osage speculated that the maintenance inadvertently caused a malfunction of the site's WFMS causing the device to switch from automatic voltage control to the default unity power factor mode. Since the site was not fully operational, the control monitoring room within the operations and maintenance department had not yet fully implemented its processes to remotely monitor the state of the controller and to receive alarms for any status change of the voltage control device immediately, in order to make notifications to the TOP in a timely manner. Therefore, Osage did not immediately observe the status change and did not report the change of state to the TOP. On June 17, 2015, Osage discovered the change of state and coordinated the automatic voltage control mode restoration with the TOP. The root cause of this issue was that Osage personnel were not aware of the switch from automatic voltage control mode. This issue lasted from June 11, 2015, when Osage did not communicate the status change within 30 minutes, through June 17, 2015, when Osage coordinated automatic control mode restoration with the TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. Failure to notify the TOP of a change in status of a reactive control could result in the TOP taking inappropriate action to respond to a disturbance on the BPS. However, the BPS does not rely on wind farm output for voltage or load support because of the intermittent nature of wind energy. Based on recorded data, the reactive component Osage imposed onto the BPS during the issue was small, less than 10 MVA. Further, Osage maintained voltage within 2 percent of the target voltage, 141 kV, during this issue. No harm is known to have occurred. SERC considered Osage and its affiliates’ VAR-002 R3 compliance history in determining the disposition track. Osage and its affiliates’ relevant prior noncompliance with VAR-002 R3 includes: NERC Violation ID SPP2013012628 and SPP2015014830. In SPP2013012628, Osage’s affiliate, Smoky Hills Wind Farm, LLC (Smoky I), had capacitor banks and had disabled one of the capacitor banks and not notified the TOP. Since Osage did not have capacitor banks the conduct involved in this issue is different from Smoky I’s prior noncompliance. In SPP2015014830, Chisholm View Wind Project, LLC (Chisholm), was fully operational. Here, Osage was in a transition stage, meaning it was only partially operational. To prevent recurrence, Chisholm made revisions to its operational procedures. Since Osage’s issue occurred during a transitional phase, similar changes at Osage would not have prevented the instant issue. SERC determined that Osage’s affiliates’ compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Osage: 1) restored voltage control and notified the TOP of the mode change; 2) contacted the TOP to obtain not just a target set point but also a set point range; and 3) gave the control monitoring room full access to voltage control, data, and alarms. Osage will also complete the following mitigation activities by 5/1/16: 1) improve control monitoring room procedures on responding to voltage control alarms and other reporting requirements, and make control room operators aware of the changes; and 2) improve the procedure that covers when a site moves from the engineering and construction phase into operation, to include provisions to obtain the voltage schedule and full remote alarm and control capability prior to commercial operation. 3) ENEL (parent of Osage) will provide training to affected Engineering, Construction, Operations and Maintenance crews and managers.
2016-03-31 | Texas Reliability Entity (Texas RE) | WorleyParsons Group Inc. (WPGINC) | NCR11506 | TRE2015015391 | VAR-002-4 | R3 | On December 4, 2015, WPGINC submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R3. Specifically, WPGINC did not notify its Transmission Operator (TOP) of a change in the status of its power system stabilizer (PSS) within 30 minutes. At 5:44 p.m. on October 28, 2015, WPGINC returned a single generation unit to service following a unit trip. Upon bringing the unit back online, however, WPGINC operators did not recognize that the unit’s PSS was switched “OFF.” WPGINC did not identify the PSS status change until a routine inspection two days later on October 30, 2015. Following the identification of the PSS status change, WPGINC operators returned the PSS to “ON” mode and notified WPGINC’s TOP. The root cause of the issue was a deficient notification system to alert the WPGINC Control Room Operators that the PSS unit was not put in the "ON" state when a generation unit is brought online. Texas RE determined that the issue duration was from October 28, 2015, when the WPGIP generation unit in question returned to service with its PSS offline, until October 30, 2015, when WPGINC placed the PSS in the “ON” state and notified its TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, the PSSs for the two other generation units at the WPGINC facility in question were on and functioning for the entire duration of the issue. Second, the Automatic Voltage Regulators (AVR) for all three units remained in service during this time. With the PSSs and AVRs in service for these units, any voltage excursions could have been mitigated by the other devices. Lastly, a PSS does not protect the BES from generator disturbances but rather serves to protect the generating unit from disturbances on the BES. No harm is known to have occurred. Texas RE considered WPGINC’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WPGINC: 1) switched the PSS for the single generation unit at issue back to the “ON” state and notified the TOP; 2) added necessary data points to the generation facility’s historian archive which are now available to track future PSS status changes; 3) created new alarms in the generating facility’s control system that will provide the Control Room Operator with an audible and visual indication of a PSS status change when a generation unit is synchronized to the grid; and 4) provided training to the Control Room Operators to reinforce the importance of having the turbines’ PSS turned “ON” when the units are in service. The training emphasized the need to verify that the PSS is placed into service during each startup and that the status of the PSS is verified during the routine inspections. Texas RE has verified the completion of all mitigation activity.
2016-03-31 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2016015441 | TPL-001-0.1 | R1; R1.1 | On December 31, 2015, EWEB submitted a Self-Report stating that, as a Transmission Planner, it had a potential issue of noncompliance with TPL-001-0.1 R1.1. EWEB failed to complete the review and approval of its 2015 annual Transmission Assessment for Category A. The root cause of this issue was human error in anticipation of implementation of TPL-001-4. This issue began July 2, 2015, the day after the EWEB’s annual deadline to complete its Transmission Assessment for Category A, and ended December 14, 2015, when EWEB’s management signed and approved the assessment. This is EWEB's first violation of this requirement in more than three years, was identified and reported timely, and posed minimal risk to the BPS. EWEB reported that although it performed its 2015 Transmission Assessments within the timeframes prescribed in the Standards, EWEB’s management did not review and approve these assessments on time. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, EWEB failed to complete its 2015 Transmission Assessment for Category A within the timeframe prescribed in TPL-001-0.1 R1.1. If the delay had resulted in EWEB’s failure to identify future system performance issues, EWEB may not have had adequate time to prevent and/or mitigate such issues. However, although the assessment was not reviewed and approved in accordance with the timeframe in the Standard, EWEB performed the assessment in April 2015, three months ahead of the deadline. The results of the assessment validated the prior year’s assessment, with no system performance issues identified in the 5 and 10-year horizons. The results did not change as a result of management review. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. WECC considered EWEB’s compliance history in determining the disposition track. EWEB’s relevant prior noncompliance with TPL-001-0.1 R1 includes NERC Violation ID WECC200901478. The previous violation was not considered an aggravating factor because mitigating activities were completed more than three years prior to this issue. EWEB has provided documentation of its internal compliance program. | To mitigate this issue, EWEB's management: 1) reviewed, approved, and signed its 2015 Transmission Assessment for Category A; WECC verified completion of EWEB’s mitigating activities and is not requiring EWEB to submit a formal mitigation plan for this issue.
2016-03-31 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2016015442 | TPL-002-0b | R1; R1.1 | On December 31, 2015, EWEB submitted a Self-Report stating that, as a Transmission Planner, it had a potential issue of noncompliance with TPL-002-0b R1.1. EWEB failed to complete the review and approval of its 2015 annual Transmission Assessment for Category B. The root cause of this issue was human error in anticipation of implementation of TPL-001-4. This issue began July 2, 2015, the day after the EWEB’s annual deadline to complete its Transmission Assessment for Category B, and ended December 14, 2015, when EWEB’s management signed and approved the assessment. This is EWEB's first violation of this requirement in more than three years, was identified and reported timely, and posed minimal risk to the BPS. EWEB reported that although it performed its 2015 Transmission Assessments within the timeframes prescribed in the Standards, EWEB’s management did not review and approve these assessments on time. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, EWEB failed to complete its 2015 Transmission Assessment for Category B within the timeframe prescribed in TPL-002-0b R1.1. If the delay had resulted in EWEB’s failure to identify future system performance issues, EWEB may not have had adequate time to prevent and/or mitigate such issues. However, although the assessment was not reviewed and approved in accordance with the timeframe in the Standard, EWEB performed the assessment in April 2015, three months ahead of the deadline. The results of the assessment validated the prior year’s assessment, with no system performance issues identified in the 5 and 10-year horizons. The results did not change as a result of management review. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. WECC considered EWEB’s compliance history in determining the disposition track. EWEB’s relevant prior noncompliance with TPL-002-0b R1 includes NERC Violation ID WECC200901481. The previous violation was not considered an aggravating factor because mitigating activities were completed more than three years prior to this issue. EWEB has provided documentation of its internal compliance program. | To mitigate this issue, EWEB's management: 1) reviewed, approved, and signed its 2015 Transmission Assessment for Category B; WECC verified completion of EWEB’s mitigating activities and is not requiring EWEB to submit a formal mitigation plan for this issue.
2016-03-31 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2016015443 | TPL-003-0b | R1; R1.1 | On December 31, 2015, EWEB submitted a Self-Report stating that, as a Transmission Planner, it had a potential issue of noncompliance with TPL-003-0b R1.1. EWEB failed to complete the review and approval of its 2015 annual Transmission Assessment for Category C. The root cause of this issue was human error in anticipation of implementation of TPL-001-4. This issue began July 2, 2015, the day after the EWEB’s annual deadline to complete its Transmission Assessment for Category C, and ended December 14, 2015, when EWEB’s management signed and approved the assessment. This is EWEB's first violation of this requirement in more than three years, was identified and reported timely, and posed minimal risk to the BPS. EWEB reported that although it performed its 2015 Transmission Assessments within the timeframes prescribed in the Standards, EWEB’s management did not review and approve these assessments on time. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, EWEB failed to complete its 2015 Transmission Assessment for Category C within the timeframe prescribed in TPL-003-0b R1.1. If the delay had resulted in EWEB’s failure to identify future system performance issues, EWEB may not have had adequate time to prevent and/or mitigate such issues. However, although the assessment was not reviewed and approved in accordance with the timeframe in the Standard, EWEB performed the assessment in April 2015, three months ahead of the deadline. The results of the assessment validated the prior year’s assessment, with no system performance issues identified in the 5 and 10-year horizons. The results did not change as a result of management review. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. WECC considered EWEB’s compliance history in determining the disposition track. EWEB’s relevant prior noncompliance with TPL-003-0b R1 includes NERC Violation ID WECC200901484. The previous violation was not considered an aggravating factor because mitigating activities were completed more than three years prior to this issue. | To mitigate this issue, EWEB's management: 1) reviewed, approved, and signed its 2015 Transmission Assessment for Category C; WECC verified completion of EWEB’s mitigating activities and is not requiring EWEB to submit a formal mitigation plan for this issue.
2016-03-31 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2016015444 | TPL-004-0a | R1; R1.1 | On December 31, 2015, EWEB submitted a Self-Report stating that, as a Transmission Planner, it had a potential issue of noncompliance with TPL-004-0a R1.1. EWEB failed to complete the review and approval of its 2015 annual Transmission Assessment for Category D. The root cause of this issue was human error in anticipation of implementation of TPL-001-4. This issue began July 2, 2015, the day after the EWEB’s annual deadline to complete its Transmission Assessment for Category D, and ended December 14, 2015, when EWEB’s management signed and approved the assessment. This is EWEB's first violation of this requirement in more than three years, was identified and reported timely, and posed minimal risk to the BPS. EWEB reported that although it performed its 2015 Transmission Assessments within the timeframes prescribed in the Standards, EWEB’s management did not review and approve these assessments on time. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, EWEB failed to complete its 2015 Transmission Assessment for Category D within the timeframe prescribed in TPL-004-0a R1.1. If the delay had resulted in EWEB’s failure to identify future system performance issues, EWEB may not have had adequate time to prevent and/or mitigate such issues. However, although the assessment was not reviewed and approved in accordance with the timeframe in the Standard, EWEB performed the assessment in April 2015, three months ahead of the deadline. The results of the assessment validated the prior year’s assessment, with no system performance issues identified in the 5 and 10-year horizons. The results did not change as a result of management review. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. WECC considered EWEB’s compliance history in determining the disposition track. EWEB’s relevant prior noncompliance with TPL-004-0a R1 includes NERC Violation ID WECC200901487. The previous violation was not considered an aggravating factor because mitigating activities were completed more than three years prior to this issue. | To mitigate this issue, EWEB's management: 1) reviewed, approved, and signed its 2015 Transmission Assessment for Category D; WECC verified completion of EWEB’s mitigating activities and is not requiring EWEB to submit a formal mitigation plan for this issue.
2016-03-31 | Western Electricity Coordinating Council (WECC) | Public Service Company of Colorado (PSCO) | NCR05521 | WECC2013012982 | PRC-001-1 | R3 | During a Spot Check conducted on July 29, 2013, WECC determined that PSCO, as a Transmission Operator, had an issue of noncompliance with PRC-001-1 R3. PSCO failed to document its coordination of one new protective system, a new Zone 3 function of a multi-function relay, with neighboring Transmission Operators and Balancing Authorities. WECC determined PSCO added a new protective system with a single zone of ground distance (Z1G), set to reach 70% of line with no time delay, in lieu of the relay’s ground directional instantaneous over current element. The Z1G has a reach of 70% of the line; the same reach as the relay it replaced. PSCO provided evidence showing the relay function and setting were functionally the same for the new protective system. PSCO’s new protective system also had an additional M3P relay reaching to the Midway bus with a 40 cycle time delay (the M3P relay setting is specific to the zone 3 phase distance), adding new functionality to the protective system. The M3P’s zone of protection wholly overlaps with the next line segment. WECC determined that PSCO failed to provide evidence the new protective system was coordinated with neighboring Transmission Operators and Balancing Authorities, as required by R3.2. The root cause of the alleged violation was PSCO's lack of compliance understanding, leading to PSCO's failure to document the basis for its determination that no external neighboring entities were impacted by this protection system device change. The compliance exception start date was August 11, 2011, when PSCO installed a new zone of protection on its Comanche-Boone 230 kV line. The compliance exception end date was August 16, 2013, when PSCO completed its review of the new relay with neighboring elements, to determine the effect. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PSCO had a reporting procedure in place at the time of the Spot Check for new and changed protective systems. However, for the protective system associated with this issue, PSCO did not document the analysis used to determine that no neighboring entities were affected by this changed protective system, (specifically, the new function of a multi-function relay), designed to protect the Comanche-Boone line, a 230 kV transmission line 12 miles from the Comanche Substation. As compensating measures, the protective system was not installed on an interconnection or a major transmission line and analysis has confirmed that the change did not affect neighboring entities. In addition, the lines protected by the protective device are wholly within PSCO’s system and thus no neighboring entities external to the PSCO system were affected by the change in the protective system device. PSCO also coordinated the changes to its system internally. In this case, Zone 3 is redundant, so that if Zone 3 fails, another system would respond. Zone 3 of one protective system overlaps with the Zone 3 of an adjacent protective system. No harm is known to have occurred. Above and Beyond Activities: PSCO completed the following reliability enhancements, above and beyond the mitigating activities associated with PRC-001-1 R3: • In 2015, PSCO worked to implement the charter of its Strategic Team (peer team). The peer team is collectively drafting comments and voting recommendations around new or revised standards (e.g., PRC-026 and PRC-027). And, it is developing common implementation plans for new or revised standards (e.g., PRC-004-3, PRC-002-2 and PRC-026-1). In addition, peer team discussions are resulting in more consistent interpretations (e.g., definition of a misoperation), process improvements (clear relay setting boundaries) and applied best practices (e.g., misoperations handling). PSCO reported that during the second half of 2015, peer sharing team activities included working on implementation plans and implementation of the upcoming version of the PRC-004 standard as well as documenting evaluations of recent NERC Lessons Learned. The team has also spent considerable effort in evaluating PSCO’s various misoperation practices against the North American Transmission Forum’s recommended practices. • PSCO finalized Version 2 of its “Protection System Coordination” document. • PSCO reported that its protection system coordination re-base lining effort with PSCO generators is in progress and on track (approximately 50% completed) with the internal schedule developed. WECC considered PSCO’s PRC-001-1 R3 compliance history in determining a compliance exception disposition track, and determined there were no relevant instances of noncompliance, and that PSCO’s compliance history should not serve as a basis for assessing a penalty. WECC also considered PSCO’s internal compliance program (ICP) and found PSCO's ICP to be a comprehensive, established program that is supported by PSCO's leadership, independently managed by its Chief Compliance Officer, with independent access to PSCO's executives. | To mitigate this issue, PSCO: 1) conducted a review of the new relay with neighboring elements to determine impact/effect; 2) implemented a revised procedure for protection system coordination that indicates when coordination with other entities is needed; and 3) provided training for the revised procedure. Since the training was completed on June 30, 2015, WECC verified the mitigation plan was complete on that date.
2016-03-31 | Western Electricity Coordinating Council (WECC) | Public Service Company of Colorado (PSCO) | NCR05521 | WECC2013013265 | PRC-023-2 | R1 | On December 19, 2013, PSCO submitted a Self-Report stating that, as a Transmission Owner, it was in possible non-compliance with PRC-023-2 R1. WECC reviewed the Self-Report and conducted interviews with PSCO compliance staff, and determined that PSCO had an issue of non-compliance with PRC-023-2 R1, for its failure to properly apply the criteria of R1 for four of its 194 Switch-on-to-Fault (SOTF) Protection System devices. Specifically, PSCO failed to have the correct settings on the under voltage element for these four schemes. WECC determined PSCO failed to evaluate relay loadability at 0.85 per unit voltage necessary to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BPS for all fault conditions, as of October 1, 2013, the effective date of PRC-023-2 R1 for SOTF circuits. Specifically, PSCO failed to meet the 85% under voltage requirement of the Standard for the following four SOTF schemes: 1) the Lamar to Colorado Green 230 kV line (5511) (the setting was at 67.75 V but should have been set below 56.5 V); 2) the Hopkins to Malta 230 kV line (5245) (the setting was at 60 V but should have been set below 56.5 V); 3) the Barr Lake to Reunion 230 kV line (5875) (the setting was at 60 V but should have been set below 56.5 V); and 4) the Valmont to Spindle 230 KV line (5385) (the setting was at 60 V but should have been set below 56.5 V). The root cause of the violation was PSCO's lack of compliance understanding and its failure to timely conform its relay loadability specifications to Version 2 of the Standard. The compliance exception start date was October 1, 2013, when R1 of Version 2 of the Standard became effective for SOTF circuits. The compliance exception end date was December 20, 2013, when the last of the non-compliant settings was corrected. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PSCO failed to properly apply the criteria of R1 for four SOTF Protection System schemes. More specifically, PSCO failed to include the undercurrent element at 85% of the voltage level for these four of 194 SOTF schemes. No harm is known to have occurred. The SOTF schemes in this issue of non-compliance are only activated once a transmission element has been lost and then restored during a fault. Once the element is returned to service the SOTF protection is on for 30 to 60 cycles (approximately 0.5 - 1 second) to detect if the fault condition still exists on the transmission line. For these schemes to be activated and result in the loss of all four 230 kV transmission lines there must be a fault that occurs and remains on all four transmission lines for a minimum of 30 cycles after returning the line to service. This fault must cause the voltage to drop below 85% of the transmission line ratings within the 30 to 60 cycles for all four lines. If this were to happen, all four of the 230 kV transmission lines would be lost. However, the likelihood of a fault occurring on all four lines is very low. This protection scheme is a corrective control in itself. WECC considered PSCO’s PRC-023-2 R1 compliance history in determining the compliance exception disposition track, and determined there were no relevant instances of noncompliance, and that PSCO’s compliance history should not serve as a basis for assessing a penalty. WECC also considered PSCO’s prior PRC-023 PSCO’s relevant prior noncompliance with PRC-023 R1 includes: NERC Violation ID numbers SPP2013012644, SPP201100630 and WECC201102725. The previous occurrence in WECC was mitigated on August 30, 2011; three years before 4/3/2014, the completion date of the mitigation plan for this compliance exception, and well before 10/1/2013, the effective date of Version 2. The prior violation was related to seventeen relay settings that were not in compliance and the current issue is related to SOTF protection schemes, which did not become effective until Version 2 of the Standard became enforceable for SOTF protection schemes. WECC reviewed PSCO’s internal compliance program, (ICP) and found PSCO's ICP to be a comprehensive, established program that is supported by PSCO's leadership, independently managed by its Chief Compliance Officer, with independent access to PSCO's executives. | To mitigate this issue, PSCO: 1) corrected the four initial non-compliant SOTF settings; 2) enhanced the PRC-023 setting evaluation form, to increase visibility of the SOTF settings to the system protection engineer; 3) trained system protection engineers on SOTF designs and the PRC-023 requirements related to SOTF; 4) conducted an internal independent review of existing SOTF circuits and settings to confirm no additional non-compliant SOFT settings were identified; and 5) reviewed process documents to determine if enhancements can be made to improve checks of SOTF settings. WECC verified that the mitigation plan was completed on April 3, 2014, the date the training was completed.
2016-02-29 | Midwest Reliability Organization (MRO) | American Transmission Co., LLC (ATC) | NCR00685 | MRO2014014478 | FAC-009-1 | R1 | On February 28, 2014, ATC submitted a Self-Report stating that as a Transmission Owner (TO), it had an issue with FAC-009-1 R1. Specifically, ATC self-reported, that it had undertaken an initiative to verify the actual rating of all substation equipment, and that after a walk-down of numerous substations, it determined that numerous substations contained inaccurate element information. Many of these substations and transmission facilities were inherited from previous owners and a number of these substations came with documentation errors. The root cause of these inaccuracies is legacy documentation errors that were entered into ATC's Substation Equipment and Line Database. This database currently has 580,000 Equipment Rating data fields. The instance of noncompliance began on June 18, 2007, when the Standard became mandatory, and is currently ongoing, but should end on or before December 31, 2016, when mitigating activities are anticipated to be completed. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). ATC identified 106 bus section rating errors, but none of these resulted in Facility Rating errors for the adjacent transmission facilities. ATC identified one current transformer error that resulted in a Facility Rating error for a Bulk Electric System (BES) transformer that reduced its emergency rating from 286 MVA to a corrected rating of 239 MVA, but ATC analyzed operations records for this element going back to 2007 and determined that actual loadings had not exceeded even 50% of the corrected rating. ATC identified 27 line rating errors that resulted in Facility Rating errors. Seventeen of these ratings decreased with an average ratings decrease of 11%. ATC analyzed operational records for these 17 facilities and determined that none of these 17 facilities had exceeded the new, corrected ratings. ATC also performed a post-contingency loading analysis to determine the likelihood that one of these facilities would be loaded above the corrected ratings and determined that post-contingency loading would have been less than the new corrected loadings in all but one instance. ATC determined that in that single instance where a specific contingency could have caused an overload, an outage was unlikely due to system configuration. In determining the disposition, MRO also considered ATC's compliance history, and its commitment to reliability as evidenced by the fact that it is proactively verifying 580,000 equipment ratings. No harm is known to have occurred. This is ATCs first issue with FAC-009-1. | To mitigate this issue, ATC will complete the following mitigation activities by December 31, 2016: 1) perform a field verification of all BES equipment ratings and update the substation equipment and line database as errors are discovered; and 2) will update all equipment rating data fields as errors are discovered, and modify any Facility Ratings that are impacted by any equipment rating error.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Homer City Generation, L.P. (Homer City) | NCR11297 | RFC2015015085 | PRC-005-1b | R2 R2.1 R2.2 | On July 6, 2015, ReliabilityFirst determined that Homer City, as a Generator Owner, had an issue of PRC-005-1.1b R2 as a result of a Compliance Audit conducted from June 16, 2015 through June 26, 2015. In short, Homer City failed to produce maintenance and testing records for the DC control circuitry for two relays on one of the generating units at the plant. Notably, General Electric Capital Corporation (GECC), Homer City's current owner, did not own the plant the last time that the protection systems on this particular generating unit were tested. The most recent maintenance and testing of the protection systems for the other two generating units was performed by GECC, in 2013. The ReliabilityFirst audit team did not find any issues with those records. The root cause of this noncompliance was a failure by Homer City to document and preserve information related to maintenance and testing of protection systems. This failure relates to the management practice areas of information management, grid maintenance, and verification. This noncompliance implicates the management practice of information management because Homer City did not ensure the integrity of the prior owner’s test records related to the DC circuitry testing. This noncompliance implicates the management practice of grid maintenance because the failure to ensure the integrity of the prior owner’s test records reduced Homer City’s ability to proactively monitor its equipment and to detect indicators of equipment failure. This noncompliance implicates the management practice of verification because Homer City failed to ensure that the prior owner performed and documented the requisite testing. The duration of this noncompliance is from December 14, 2012, the beginning of the audit assessment period, to November 11, 2015, the date Homer City completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the noncompliance affected only one of the three generating units at this plant. If a problem were to have occurred at that particular generating unit, the other two generating units at this plant could have supplied the needed power. Second, the two missed relays represented only 7% of the sample examined during the audit, which indicates that this noncompliance was not indicative of a larger, systemic problem. Third, this noncompliance was a documentation issue. In other words, the fact that Homer City failed to produce maintenance and testing records for these two relays does not necessarily indicate that the relays would have failed to operate if required. No harm is known to have occurred. This is Homer City's first instance of noncompliance with PRC-005 R2. | To mitigate this issue, Homer City: 1) re-wrote the DC trip check testing procedure to ensure all affected Unit 1 relays are included; and 2) performed DC functional trip tests on all applicable Unit 1 relays to meet compliance during the scheduled October/November maintenance outage.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | MEG Generating Company, LLC (MEG Genco) | NCR00838 | RFC2015015155 | PRC-005-1 | R2 | On August 14, 2015, MEG Genco submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1 R2. MEG Genco discovered that some of its protection system components, relays, DC control circuitry, and current transformers (CTs), were not tested in accordance with the requirements of PRC-005 or MEG Genco’s PRC-005 R1 compliance program. While conducting an internal compliance review to prepare to implement PRC-005-2, MEG Genco compared its maintenance and testing tracking tools against its trip schematics. This comparison revealed that certain relays, CTs, and DC circuits had not been tested. Some MEG Genco facilities also did not test the auxiliary power systems associated with its 4,160 volt transformers due to the configuration of the transformers. A total of 79 protection components were not tested across the four MEG Genco facilities in the ReliabilityFirst region including: 17 relays, 39 CTs, and 23 DC Circuits. MEG Genco has a total of 1,077 components and devices requiring testing in the ReliabilityFirst region, which means that 7% of all of MEG Genco’s protection system components and devices were not tested. This noncompliance concerned the management practice of verification because of MEG Genco’s initial flaw in compiling the lists of protection system devices subject to PRC-005 testing in 2007 that was not discovered until the 2015 review. The root cause of this noncompliance was human error in compiling the lists of protection system devices. Verification is implicated because MEG Genco did not have an effective process in place to verify that no mistakes were made when it was compiling the lists of protection system devices in 2007 that needed to be tested. MEG Genco also did not verify after 2007 that its list of protection system devices subject to PRC-005 testing was accurate. The duration of this noncompliance is from June 18, 2007, the date MEG Genco was required to comply with PRC-005-1 R2, to July 31, 2015, the date MEG Genco completed all of the overdue testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Each of MEG Genco’s four generating facilities have a capacity of less than 165 MWs. The issues reported represent only 7% of the total protection system devices at MEG Genco that require testing. The MEG Genco auxiliary transformer back-up relays and breakers would activate if there was a failure to trip, which would isolate a fault within the generator facility. Additionally, MEG Genco has not experienced any misoperations of facility protection systems. Various unit trips for reasons such as water levels, vibration, and auxiliary equipment malfunctions had no impact on the Bulk Electric System. No harm is known to have occurred. This is MEG Genco's first instance of noncompliance with PRC-005-1 R2. | To mitigate this issue, MEG Genco will complete the following mitigation activities by June 30, 2016: 1) MEG Genco committed to complete all missing testing; 2) MEG Genco committed to draft a Management of Change (“MOC”) policy and procedure for any NERC related activities; 3) MEG Genco committed to internally review and revise the draft MOC policy; 4) MEG Genco committed to develop standardized PRC-005 testing specifications and documentation for all MEG Genco NERC facilities and to standardize existing processes for third party testing; 5) MEG Genco committed to have formal management acceptance of the MOC policy and to distribute the policy to all affected parties and provide training on the policy as needed; 6) MEG Genco committed to implement the standard test report form and to provide training on that form as needed; 7) MEG Genco committed to develop trip circuit test tables for each facility; and 8) MEG Genco committed to distribute the standard report form and trip circuit tables to all MEG Genco NERC facilities. MEG Genco will also conduct a periodic review of facility device lists to verify that devices are properly included in the PRC-005 program. These device lists will be used to track the devices and components and their intervals to ensure future intervals for testing are not missed. MEG Genco is drafting and implementing a company-wide MOC policy for NERC-related activities. Drafting, reviewing, implementing, and training staff on a MOC policy is an enormous and time consuming project. The large size and scope of the MOC project explains why the mitigation plan will not be finished until June 2016.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Baltimore Gas and Electric Company (BGE) | NCR00689 | RFC2015015146 | FAC-008-3 | R6 | On August 11, 2015, BGE submitted a Self-Report stating that, as a Transmission Owner, it had an issue of FAC-008-3 R6. BGE is in the process of updating its Transmission Ratings Methodology to include relay thermal limitations. In preparation for this transition, BGE conducted a review of the BGE ratings application to verify that the ratings application reflected the correct relays for each rated Bulk Electric System (BES) facility. As part of this review, BGE created and utilized new BES Facility Boundary Diagrams to improve the accuracy of mapping the correct relays to each BES facility. BGE used the drawings to determine which relays correspond to each rated BES facility. During the course of this mapping, BGE identified 2 Facility Ratings discrepancies. For Riverside to Riverside 7/8 (Circuit 112478), the loadability settings of three applicable relays were not captured as part of the Facility Rating thus making the Facility Rating inaccurate and violating FAC-008-3 R6. The relays are fed from current transformers on the circuit breaker that separates the Riverside 115 kV bus from Riverside Generation Units 7 and 8. The relays are in place to protect the generator step-up (GSU) transformer and the connected high side circuit from faults, but their loadability settings are based on the capacity of the GSU transformer. Adding in the three relays that were missed decreased the Facility Ratings. Prior to the decrease, BGE’s Facility Ratings were conservative, meaning BGE’s facilities were operating below equipment capacity. Generally, having incorrect Facility Ratings could lead to a facility operating above its equipment capacity, which could overload a transmission line and cause damage to equipment. In this case, BGE had conservative relay settings that were below equipment capacity, which greatly reduces the likelihood of that risk occurring. For Riverside to Riverside 110-3 (Circuit 115001), the loadability settings of three applicable relays were also not captured as part of the Facility Rating thus violating FAC-008-3 R6. The relays are fed from current transformers on the circuit breaker that separates the Riverside 115kV bus from the Riverside to Riverside 110-3 transformer and are in place to protect the connected high side circuit and the 110-3 transformer. The relay loadability settings are based on the 110-3 transformer. Adding in the three relays that were missed decreased the Facility Ratings. Prior to the decrease, BGE’s Facility Ratings were conservative, meaning BGE’s facilities were operating below equipment capacity. Generally, having incorrect Facility Ratings could lead to a facility operating above its equipment capacity, which could overload a transmission line and cause damage to equipment. In this case, BGE had conservative relay settings that were below equipment capacity, which greatly reduces the likelihood of that risk occurring. The root cause was human error. This noncompliance concerned the management practices of workforce management and asset and configuration management. Workforce management is implicated because the two Facility Ratings discrepancies were the result of human performance errors in determining which relays applied to each applicable BES facility. Ineffective training is also implicated because the individuals responsible for determining which relays applied were not effectively trained on how to make that determination. Asset and configuration management is implicated because BGE had no process in place to detect and did not detect that the Facility Ratings were incorrect until 2015. The duration of this noncompliance is from January 1, 2013, the date BGE was required to comply with FAC-008-3 R6, to May 6, 2015, the date BGE modified and updated the Facility Ratings at issue in the BGE ratings application and in the Energy Control System. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Although the inclusion of the loadability settings of the relays caused the Facility Ratings to decrease for Circuit 112478, the combined output of Riverside Generation Units 7 and 8 is far less than the loadability setting of the missing relays. Additionally, for Circuit 115001, the capacity of the Riverside to Riverside 110-3 transformer is also far less than the loadability setting of the missing relays. Even though the risk posed by having incorrect facility ratings could overload a transmission line and cause damage to equipment, the relay settings were conservative and below equipment capacity at all times which greatly reduced the likelihood of that risk occurring. Lastly, only two BES facilities rated at a lower voltage of 115kV were affected by the incorrect Facility Ratings. No harm is known to have occurred. BGE had one prior issue with FAC-008 R6, as follows: RFC2014014269. A Compliance Exception covering a violation of FAC-008-3 R6 was filed with FERC on May 28, 2015. The violation is distinguishable from the current violation. In the prior violation, BGE identified that four related BGE facilities had incorrect Facility Ratings. The Facility Ratings were incorrect and not updated on time because the engineer in charge of one project updated the Facility Ratings late and the engineer in charge of a second project incorrectly believed that Facility Ratings changes should be communicated at the end of a multi-facility project rather on a per-facility basis. The current noncompliance is distinguishable because it involved the loadability settings of six relays not being captured as part of the Facility Ratings and not the overdue updating of Facility Ratings. Although both the prior violation and instant noncompliance have similar root causes of human error and ineffective training, the similar root causes are not problematic because both BGE’s prior violation and the instant noncompliance were identified through proactive BGE efforts to update Facility Ratings. As a result, ReliabilityFirst determined that BGE’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, BGE: 1) modified and updated the Facility Ratings at issue in the BGE ratings application and in the Energy Control System; 2) communicated the new ratings to PJM. This communication to PJM was for informational purposes only as PJM does not model these particular BES facilities; 3) completed its review of all relays in the BGE ratings application, a total of approximately 2,000 relays, and no other ratings discrepancies were identified; 4) implemented the BES Facility Boundary Diagrams tool to aid in relay mapping and to reduce the possibility of future human error. This tool will reduce the possibility of future misses because it makes sure that the correct relays are mapped to each rated BES facility, which means more accurate Facility Ratings; and 5) implemented a peer review process for all relay mapping activities, which reduces the risk of future misses by having another person check the accuracy of a key input into Facility Ratings.
2016-02-29 | SERC Reliability Corporation (SERC) | Big Rivers Electric Corporation (BREC) | NCR01180 | SERC2015014636 | PRC-005-1 | R2 | On February 10, 2015, BREC submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-1.1b R2. BREC reported that it was missing monthly battery maintenance documentation for September through December of 2013 and February through June of 2014 for one station, and June and September of 2013 and June 2014 at another station. During SERC’s assessment of the scope of noncompliance, it determined that the issues of noncompliance began with PRC-005-1 R2. While reviewing maintenance records, a BREC protection system subject matter expert (SME) discovered a possible battery issue, which is the subject of the instant Self-Report. Once discovered, the SME initiated a more detailed review of the GO devices and found no other instances of noncompliance. While conducting a Protection System inventory assessment to respond to the SERC Request for Information (RFI) for the instant Self-Report, which includes a complete inventory of all the BREC Protection System devices, the defined intervals for each device type, and maintenance and test dates for the most current and previous dates listed for each BREC Protection System device, BREC identified additional transmission system Protection System devices that were non-compliant. SERC reviewed the spreadsheet completed by BREC and determined that BREC did not perform maintenance and testing within the defined interval for 175 of 1,289 protective relays (14%), 32 of 168 ACS devices (19%), 2 of 88 batteries and chargers (2%) and 24 of 116 PTs/CTs (21%). In total, BREC could not provide evidence that 233 of 1,783 (13%) Protection System devices were compliant with PRC-005-1 R2. The primary causes of noncompliance were inexperienced personnel who did not understand the need to follow a strict interpretation of the approved maintenance interval. BREC's procedures allow for verbal approval to extend the intervals, therefore there was no evidence of approval. A lack of independent access to all Protection System maintenance and testing records limited the ability of BREC compliance staff to efficiently audit the records on a routine basis. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). BREC’s failure to perform the maintenance and testing of these Protection System devices within the defined interval could lead to devices not operating as intended, potentially leading to false trips, remote clearing, delayed clearing, the overreach of protective relays, a loss of generating units or reliance on the interconnecting Transmission Owner’s Protection System devices to respond to a fault. However, the plant battery banks and all communication equipment are monitored and alarmed on a 24x7 basis. All non-compliant devices have been tested and maintained and BREC did not identify any issues. In addition, 119 of the non-compliant relays, 12 ACS devices, and 7 PTs/CTs were due to verbal and not written approval granted to extend the interval as allowed for in the procedure. Also, BREC has 1,444 MWs of generation with eight units ranging from 65 MWs to 417 MWs and is interconnected with the MISO, TVA and LG&E and KU systems. The loss of a BREC generating unit would result in minimal impact to the BPS. No misoperations occurred as a result of the issues. No harm is known to have occurred. SERC considered BREC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BREC: 1) updated its enterprise asset management system; 2) completed maintenance and testing for all out of interval equipment; 3) updated system protection documentation and provided training; 4) purchased and installed protection suite software solution; and 5) implemented and trained on new compliance software and new protection suite software.
2016-02-29 | SERC Reliability Corporation (SERC) | Duke Energy Progress, LLC (DEP) | NCR01298 | SERC2015014778 | PRC-007-0 | R1 | On February 6, 2015, Duke Energy Florida, LLC (DEF) submitted a Self-Report (via Duke Energy Progress per MRRE agreement) stating that, as a Distribution Provider (DP), it was in violation of PRC-006-1 R9. DEF stated that its Underfrequency Load Shed (UFLS) system would not shed load in accordance with the Planning Authority’s Program. SERC determined that the issue spanned the effective dates of PRC-007-0 R1 and PRC-006-1 R9. On December 18, 2014, DEF was reviewing its UFLS obligations as defined in the FRCC Automatic Underfrequency Load Shed Program which became effective November 1, 2014. That program requires the first six steps of UFLS protection to occur between 0.1 and 0.28 seconds after the low frequency setpoint is reached. It also explains that the allowable delay is the total of any intentional delay plus the delay caused by the relay actuation plus the time required for proper breaker operation. DEF had applied an intentional delay of 12 cycles for all of its UFLS relays. However, for an oil breaker, the total clearing time is 12 cycles + 1 cycle for the relay + 5 cycles for the breaker = 18 cycles, which is 0.30 seconds. Therefore, the total clearing time for the 129 oil breakers in the DEF UFLS system was 0.02 seconds too long. DEF’s analysis of the amount of load being shed in each step concluded that 82.9% of the UFLS load shed requirement would be shed on time. The remaining 27.1% would be shed 0.02 seconds later than required. SERC reviewed the UFLS program dated May 24, 2009 and learned that the regional requirements imposed a similar maximum time delay of 0.28 seconds. The setpoint error was introduced when the setpoints were originally determined. DEF was not aware of the setpoint error until it was discovered. This issue lasted from May 24, 2009 the earliest known date that the maximum UFLS delay of a 0.28 second was enforceable until mitigated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEF’s failure to follow its documented automatic UFLS load shedding program could result in inadequate response to an Underfrequency condition and could exacerbate the disturbance. However, the appropriate amount of load was armed and it would have been shed. At least two thirds of the required load would be shed by the required 0.28 seconds. The remaining would be shed no later than 0.02 seconds later. In a report discussing the regional UFLS design study, DEF attests that a sensitivity study of 15% over and under shedding provided adequate frequency response. Therefore, the 6.2% of total load compromised by the violation is well within the sensitivity. No UFLS events occurred during the period of noncompliance and no harm is known to have occurred. SERC considered DEF's PRC-007-0 R1 and PRC-006-1 R9 compliance history in determining the disposition track. Neither DEF nor its affiliates have a relevant compliance history. | To mitigate the issue, DEF: 1) accomplished the planning, engineering, and resource allocation activities; and 2) reset all 129 feeders to the proper delay. To mitigate the issue, DEF will complete following actions by November 1, 2016: 1) participate in refresher training on the FRCC Automatic UFLS Program as well as DEF’s internal procedure DST-EDGX-00052, Procedure for the development, programming, and filing of UFLS set points; 2) review the roles and responsibilities listed in DST-EDGX-00052 to ensure that personnel understand what actions are required of them; 3) communicate any updates to the FRCC Automatic UFLS Program to the responsible personnel listed in DST-EDGX-00052 to ensure that they are aware of any impending changes; and 4) be compliant with the “new” UFLS program that requires DEF to reset UFLS setpoints to comply with the new frequency distribution and amount being shed at each frequency.
2016-02-29 | SERC Reliability Corporation (SERC) | Duke Energy Progress, LLC (DEP) | NCR01298 | SERC2015015248 | PRC-005-2 | R3 | On September 21, 2015, Duke Energy Florida, LLC (DEF) submitted a Self-Report (via Duke Energy Progress per MRRE agreement) stating that, as a Transmission Owner (TO), it had an issue with PRC-005-2 R3. DEF reported that it did not have evidence that it has maintained its Protection System Components included within its time-based program in accordance with R3. DEF scheduled and performed annual maintenance of the Quincy substation battery and chargers on February 19, 2015. That was the first scheduled maintenance in accordance with PRC-005-2 for the Quincy battery. DEF personnel reported the required maintenance was completed and closed the work order. As an action resulting from an earlier Mitigation Plan, a compliance analyst reviews all required documentation to verify that the maintenance was completed. During the review on August 3, 2015, the analyst determined that the available documentation for the 2015 annual maintenance at the Quincy station was incomplete and was insufficient to show compliance with Table 1-4(a) for DC supplies using vented lead-acid storage batteries. Specifically missing were forms verifying float voltage, cell condition and condition of battery racks for one battery. Some existing forms were also missing header information identifying the battery being maintained. All of the missing information is required by DEF’s procedure. DEF states that they have determined the issue to be a personnel issue and that retraining has occurred to prevent a recurrence. DEF maintains 153 battery banks. No other issues have been identified during the periodic reviews. This issue lasted from April 1, 2015 when evidence of required maintenance and testing was not available until mitigation completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEF’s failure to properly maintain batteries could lead to batteries that may not properly interrupt circuits during faults or other unsafe conditions. However, the batteries and chargers at the Quincy 115 kV substation are also inspected quarterly and monthly. During these inspections field staff view conditions both in the switchyard and in the control house where batteries reside. Through the inspections, DEF did not identify any issues with the Quincy 115 kV substation batteries and chargers during the period of non-compliance. DEF monitors battery voltage on its batteries, with any existing alarms communicated automatically to the Energy Control Center (ECC). Also, DEF monitors communications between the ECC and the substation to identify any loss of communications. No requests were initiated for battery alarms at Quincy during the period of non-compliance. A subsequent investigation revealed no sustained alarms and no corrective work orders during the period of non-compliance. No harm is known to have occurred. SERC reviewed the posted violations of PRC-005 for affiliates Duke Energy Carolinas (DEC), Duke Energy Corp. (DECorp), Duke Energy Progress (DEP), and Duke Energy Florida (DEF) and did not identify circumstances similar to that of the instant issue. SERC considered DEF’s PRC-005-1 R2 compliance history in determining the disposition track. DEF’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation FRCC2013012446. In FRCC2013012446 DEF did not have evidence that one set of Protection System devices was maintained and tested within the defined intervals because one pair of relays that had been listed in the database as distribution relay. Mitigation was completed on June 27, 2013. SERC determined that DEF compliance history should not serve as a basis for applying a penalty because the instant violation is of different nature and the mitigation plan did not address the instant issue. SERC considered DEP’s PRC-005-1 R2 compliance history in determining the disposition track. DEP’s relevant prior noncompliance with PRC-005-1 R2 includes SERC CE ID SERC2014014141 and SERC2013012434. SERC determined that DEP’s compliance history should not serve as a basis for applying a penalty. In SERC2014014141 battery maintenance at one power plant that was performed but was scheduled and performed before the quarter in which it should have been performed. This CE was successfully mitigated and has no bearing on the instant issue. SERC2013012434 concerns testing of an associated communication system that was delayed due to work on the terminal of an adjacent Transmission Owner. This FFT was successfully mitigated and has no bearing on the instant issue. SERC considered DEC’s PRC-005-1 compliance history in determining the disposition track. DEC’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID SERC201000544. SERC determined that DEC’s compliance history should not serve as a basis for applying a penalty. In SERC201000544 approximately 1.9% of its devices had not been tested within the defined interval. The instant violation is of different nature and the mitigation plan did not address the instant issue. SERC considered DECorp’s relevant compliance history in determining the disposition track. DECorp does not have a relevant compliance history. Each Duke Energy affiliate is responsible for its own maintenance and testing program and the completed mitigation plans would not have addressed the instant issue. Therefore, SERC staff did not consider the previous violations by affiliates as aggravating circumstances, nor did it identify a programmatic issue based on that history. | To mitigate this issue, DEF: 1) completed the annual maintenance on the batteries and chargers at the Quincy 115 kV substation; and 2) conducted refresher training/coaching with the personnel involved to further the actions required when closing out compliance related maintenance/activities.
2016-02-29 | SERC Reliability Corporation (SERC) | Duke Energy Progress, LLC (DEP) | NCR01298 | SERC2015015322 | FAC-009-1 | R1 | On November 3, 2015, Duke Energy Florida, LLC (DEF) submitted a Self-Report (via DEP as an MRRE) stating that, as a Transmission Owner, it had an issue with FAC-008-3 R6. DEF failed to document a Facility Rating in a manner consistent with its Facility Rating Methodology (FRM). SERC later determined that the issue was present on June 18, 2007 when FAC-009-1 was in effect. On September 4, 2015, while reviewing records in preparation for a new project, DEF line engineering identified the possibility that DEF had omitted a line conductor type on existing Facility Ratings Spreadsheets (FRSs) for the JQ-115 kV line. DEF uses FRSs to establish Facility Ratings of transmission Facilities. DEF found that one line segment between Hanson and Drifton substations and another between Drifton and Bradfordville West substations were missing 2/0 HDB Cu (stranded hard-drawn bare copper) as a line conductor type for the determination of the Facility Rating. On September 9, 2015, a field review of the existing Drifton substation confirmed the 2/0 HDB Cu conductor type was present in both line segments but was missing on both FRSs. DEF reviewed the remainder of the JQ-115 kV line and identified similar findings on line segments, between Jasper to Suwannee and Suwannee to Hanson substations. DEF learned that the 2/0 HDB Cu line conductor is part of the original design and construction that occurred in the 1950s, but was not properly identified during the creation of line engineering’s supporting documentation required for these FRS. That supporting documentation included only the 4/0 ACSR (aluminum core steel reinforced) line conductor. As a result, the copper conductor became the limiting component and required a reduction in the Facility Rating for the four transmission line segments. This issue lasted from June 18, 2007 when the standard became mandatory and enforceable until October 20, 2015 when DEF corrected the ratings in the FRS. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DEF’s failure to document a Facility Rating in a manner consistent with its FRM could have led to equipment damage, unplanned outages, or reduced equipment lifetimes. However, the lines have been in successful operation since their construction in the 1950. A total length of 386 feet of 115 kV circuit is affected. In the worst case, the Facility Rating was decreased from 84 to 60 MVA (28%) however, DEF reviewed operating data from the past year and identified only three times where the corrected, derated Facility Rating was exceeded. The worst exceedance was for a period of 1.5 hours but was within the 2-hour emergency rating of the line. There were no instances of instability on the BPS, no damage is apparent to any of the line segments, and no harm is known to have occurred. SERC considered DEF’s FAC-009-1 R1 and FAC-008-3 R6 compliance history in determining the disposition track. DEF’s relevant prior noncompliance with FAC-009-1 R1 and FAC-008-3 R6 include(s): NERC Violation ID FRCC2012011495 and FRCC2014014010. SERC determined that DEF’s compliance history should not serve as a basis for applying a penalty. In FRCC2012011495 DEF submitted a Self-Report stating that, DEF failed to include Facility Ratings for the relay settings of a 115 kV radial line to a 32 MVA co-generator plant. The relay settings were identified to be the most limiting element of the Facility. The Facility Rating for the 115 kV line was originally 199 MVA and was reduced to 90 MVA. Mitigating actions that were completed March 14, 2014 would not have addressed the instant issue. In FRCC2014014010 DEF submitted a Self-Report stating that DEF identified during the “as-built” review following a transmission project, that the documentation for the segment was improperly identified with the same description as another conductor in series with the segment. The rating for the new replaced segment was higher than the original rating of the older segments. The root cause for this issue was that, during the documentation for completing a transmission project, a conductor was improperly classified which resulted in an incorrect Rating being determined for the transmission line segment. Mitigation was complete May 12, 2014, when DEF corrected the Rating for the transmission line segment with the higher rating. Although this is a similar issue, it occurred following a new construction project and its mitigation would not have addressed the instant issue. SERC considered the compliance history of DEF affiliates in determining the enforcement track. Duke Energy Progress, Duke Energy Corporation, Duke Energy Carolinas do not have applicable relevant compliance history | To mitigate this issue, DEF: 1) updated engineering documentation supporting FRSs per internal controls identified in EGR-TRMF-00009, Florida Line Engineering Limiting Element and Physical Statistics Procedure, Section 5. DEF will also complete the following mitigation activities by 5/30/2016: 1) initiate and implement projects to change out the conductors on the JQ-6, JQ-7.1, JQ-1.7 and JQ-2 segments from 2/0 HDB Cu to 4/0 ACSR. There will be two projects to address this issue. One project for line segment JQ-6 and JQ-7.1 and another project for JQ-1.7 and JQ-2; and 2) update the FRSs and FRM-TRMF-01038, Line Engineering Limiting Element and Physical Statistic Data Form and communicate these updates to System Operations and Transmission Planning.
2016-02-29 | SERC Reliability Corporation (SERC) | Entergy | NCR01234 | SERC2015015080 | PRC-008-0 | R2 | On June 16, 2015, SERC sent Entergy an audit detail letter notifying it of a compliance audit scheduled for September 14, 2015 through October 2, 2015. On July 9, 2015, Entergy submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-008-0 R2. Entergy could not produce maintenance and testing records for three relays in the Under Frequency Load Shedding (UFLS) program. On March 16, 2015, during a records review following maintenance activities at the South Canton substation, Entergy discovered that it could not produce documentation that the relays for three feeder breakers which are part of the UFLS program had been maintained in accordance with the UFLS equipment maintenance and testing program. The three relays are part of a UFLS system that includes 962 relays capable of tripping a total of 7,032 MW of load. The peak load tripped by these three relays is 23 MW. The last documented maintenance/testing of these devices, which Entergy had assigned five year maintenance intervals, occurred in 2006. The maintenance was due by December 31, 2011. The root cause of this issue is that a technician failed to respond appropriately in 2011 when work could not be completed due to a malfunctioned bypass switch. The technician documented the malfunctioning switch as an annotation to the work order and incorrectly closed the work request. The proper action would have been to identify the work request as “constrained” and generate a new work request to have the malfunctioning switch repaired before completing the original work request. Entergy reviewed a random sample of 64 transmission and distribution work requests with annotations and found no additional discrepancies in the documentation associated with those work orders. This issue lasted from January 1, 2012, the first day following the planned maintenance interval, through April 17, 2015 when Entergy completed the relay testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Entergy’s failure to implement its UFLS maintenance and testing could lead to the loss or premature operation of these three relays which could have affected its UFLS program’s capabilities. However, the loss or premature operation of these three relays would only affected the UFLS capability by up to 0.2% of the system’s total summer peak load. Therefore, during the period of this issue, Entergy’s UFLS program would have been able to shed 29.9% to 30.8% of the system’s total summer peak load, well within the allowable range for total UFLS of 29.0% to 35.0% per the Regional Reliability Organization’s program in effect at the time. In addition the relays are microprocessor relays that historically incur a lower failure rate, Misoperation rate or setpoint drift when compared to equivalent electromechanical relays. Further the microprocessor relays are self-monitoring and would have some type of notification enabled. Finally, when the relays were maintained/tested they were found to operate within tolerance and passed all tests. Therefore, the UFLS should have operated as designed when actuated. No harm is known to have occurred. Entergy has not had a prior violation of PRC-008-0 which was in effect from June 18, 2007 until UFLS maintenance and testing requirements were included in PRC-005-2 (effective April 1, 2015, enforcement is phased in over 12-year period). SERC considered Entergy’s PRC-005 R2 compliance history in determining the disposition track. Entergy’s relevant prior noncompliance with PRC-005 R2 includes: SERC200900275, SERC200900298, SERC201000636, and SERC201000637. SERC determined that Entergy's compliance history should not serve as a basis for aggravating the penalty. None of the previous issues were caused by closing a work order without proper documentation as is the case of the instant issue. Actions implemented in April of 2013 would possibly have prevented the instant issue, however the instant issue occurred in 2011 prior to that action and was not detected until March 16, 2015. | To mitigate this issue, Entergy: 1) revised AM-PC-AD-001 to improve documentation of completion of preventative maintenance work such that it requires more thorough closure review by the supervisor; 2) completed all potentially overdue maintenance tasks of the three identified feeders (Relay Calibration, DC Operational Test and Panel Inspection, and AC Acceptance Test) for the affected feeder breakers; 3) developed and shared lessons learned with technicians to ensure that they understand what went wrong in this instance and the impacts of not following procedure(s); and 4) performed a review of prior closed preventative maintenance work requests which have notes that could indicate an interruption of work. This review consisted of querying the work management system to identify work requests with notes entered into notes fields, performing a sampling of those work requests, reviewing those work requests to confirm the assumption that this is was not a common occurrence.
2016-02-29 | SERC Reliability Corporation (SERC) | Georgia Transmission Corporation (GTC) | NCR01249 | SERC2015015329 | MOD-027-1 | R5 | On November 12, 2015, GTC submitted a Self-Report stating that, as a Transmission Planner, it had an issue with MOD-027-1 R5. GTC failed to provide a written response to the Generator Owner (GO) within 90 calendar days of receiving the turbine/governor and load control or active power/frequency control system verified model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 5.1 through 5.3) or is not usable. On October 1, 2015, while reviewing a tracking document for MOD-027-1, GTC discovered that it did not respond to a GO data submission within the 90 calendar day period as required. The notice from the GO, per Requirement 2, was sent to GTC on June 30, 2015. GTC’s required response should have been sent to the GO no later than September 28, 2015. GTC responded on September 29, 2015, one day past the 90 calendar day period. The causes for the noncompliance are that the responsible subject matter expert (SME) did not complete the analysis to determine if the data was usable until September 29, 2015, the bulk planning (BP) compliance specialist did not follow up with SME or check the tracking log prior to the due date, and BP management did not have a process in place to trigger a reminder for a due date. This issue lasted for one day, September 29, 2015, a day after GTC’s response to the GO was due and when GTC responded to the GO. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). GTC’s failure to respond within the required 90 days could have led to incorrect models being used for transient and dynamic analysis that could have resulted in erroneous assessments or in an incorrect corrective action plan. However, the response was one day late and no transient or dynamic studies were done between day 90, when a GTC response was due, and day 91, when GTC responded. No harm is known to have occurred. SERC considered GTC’s compliance history in determining the disposition track. GTC has no prior issues or violations of any MOD Reliability Standard. | To mitigate this issue, GTC: 1) sent a response to the GO on September 29, 2015; and 2) developed and implemented a process that sets a shorter time period to respond to a notice and requires generating automated reminder(s).
2016-02-29 | SERC Reliability Corporation (SERC) | Georgia Transmission Corporation (GTC) | NCR01249 | SERC2015015330 | MOD-026-1 | R6 | On November 12, 2015, GTC submitted a Self-Report stating that, as a Transmission Planner, it had an issue with MOD-026-1 R6. GTC failed to provide a written response to the Generator Owner (GO) within 90 calendar days of receiving the verified excitation control system or plant Volt/VAR control function model information in accordance with Requirement R2 that the model is usable (meets the criteria specified in Parts 6.1 through 6.3) or is not usable. On October 1, 2015, while reviewing a tracking document for MOD-026-1, GTC discovered that it did not respond to two separate notices from a GO within the 90 calendar day period as required. A GO sent the first notice regarding a generator model, per Requirement 2 to GTC on June 30, 2015. GTC was required to respond to the GO by September 28, 2015. GTC responded on September 29, 2015, one day past the 90 calendar day period. The same GO sent the second notice regarding another generator model to GTC on July 2, 2015. GTC was required to respond to the GO by September 30, 2015. GTC responded on October 1, 2015, one day past the 90 calendar day period. The causes for the noncompliance were that the responsible subject matter expert (SME) did not complete the analysis on the first notice to determine if the model data was “usable” until September 29, 2015 and did not believe a response was necessary for the second notice based on the fact that the model had been verified by the GO in 2012 and GTC was using that model. In addition, the Bulk Planning (BP) compliance specialist did not follow up with the SME or check the tracking log prior to the due dates, and BP management did not have a process in place to trigger a reminder for a due date. This issue lasted for one day on September 9, 2015, a day after GTC’s response to the GO was due and when GTC responded to the GO, and one day on October 1, 2015, a day after GTC’s response to the GO was due and when GTC responded to the GO. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). GTC’s failure to respond within the required 90 days could have led to incorrect models being used for transient and dynamic analysis that could have resulted in erroneous assessments or in an incorrect corrective action plan. However, in the instance of the first notice, no transient or dynamic studies that would have resulted in an erroneous assessment or in an incorrect Corrective Action Plan were performed between day 90, when a GTC response was due, and day 91, when GTC responded. In the instance of the second notice, the newly submitted data was an exact match to the data submitted to GTC in 2012 and is currently used for transient and dynamic simulation. No harm is known to have occurred. SERC considered GTC’s compliance history in determining the disposition track. GTC has no prior issues or violations of any MOD Reliability Standard. | To mitigate this issue, GTC: 1) sent a response to the GO regarding the first notice on September 29, 2015; 2) sent a response to the GO regarding the second notice on October 1, 2015.; and 2) developed and implemented a process that sets a shorter time period to respond to a notice and requires generating automated reminder(s).
2016-02-29 | Southwest Power Pool Regional Entity (SPP RE) | KODE Novus I, LLC (KODE) | NCR11329 | SPP2015014721 | PRC-005-1b | R2; R2.1, R2.2 | On March 6, 2015, KODE submitted a Self-Certification stating that, as a Generator Owner, it had an issue of noncompliance with PRC-005-1b R2; R2.1, R2.2 because it did not have evidence that the 67 Protection System devices at its newly commissioned Novus 1 wind farm had been maintained or tested within the intervals defined in its Protection System Maintenance and Testing Program (PSMTP). As a result, KODE could not affirmatively establish the date its Protection System devices were last tested or maintained. This instance of non-compliance began on March 13, 2013, the day KODE registered with NERC as a Generator Owner, and ended on June 6, 2015, the day KODE successfully mitigated the instance of noncompliance. The root cause of this issue was KODE’s failure to acquire the protection system test and maintenance records from its construction and commissioning contractor prior to Novus I becoming operational. Attempts to acquire the commissioning and testing/maintenance records before submission of the self-certification were not successful. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although KODE did not have evidence to substantiate the maintenance and testing of the Novus 1 Protection System devices, Novus 1 was commissioned in 2013. The Protection System devices were new and had been in operation for a very short time. Except for the battery bank and battery charger, all of the Novus 1 Protection System devices would have been within the intervals prescribed in Table 1 of the PRC-005-2 NERC Standards and Requirements. Because Novus 1 is a small wind farm (peak capacity of 80 MW), operates intermittently, and provides no reactive support to the Bulk Power System (BPS), it has minimal effect on BES reliability. No actual harm occurred to the BPS as a result of this issue of non-compliance. No Violation History. | To mitigate this minimal risk instance of noncompliance, KODE: 1) Inventoried its Protection System Devices; and 2) Performed maintenance and testing on all of its identified Protection System Devices. SPP RE has verified the completion of all mitigation activity.
2016-02-29 | Southwest Power Pool Regional Entity (SPP RE) | Western Farmers Electric Cooperative (WFEC) | NCR01160 | SPP2015015249 | EOP-004-2 | R2 | On September 25, 2015, WFEC submitted a Self-Report stating that, as a Transmission Operator, it had a minimal risk instance of noncompliance with EOP-004-2 R2 because it failed to report a reportable event within 24 hours of the occurrence of the event. On April 9, 2014, WFEC experienced the loss of three 138 kV transmission lines when a contractor inadvertently bumped a relay cabinet, causing seven breakers in the Hugo Power Plant switch yard to trip. The Hugo Power Plant was offline for scheduled maintenance at the time of the event. WFEC contacted its Reliability Coordinator when the event occurred, and again when the transmission lines were returned to service. WFEC, however, did not report the event to the Electric Reliability Organization (ERO) within 24 hours as prescribed in EOP-004-2 R2. This issue of noncompliance began on April 9, 2014, when WFEC failed to submit an Event Report within twenty-four (24) hours of the reportable event, and ended on September 25, 2015, the date WFEC reported the event. The root cause of this issue was a lack of training to ensure that WFEC operators were aware of the WFEC Operating Plan requirements for reporting events. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The reportable event had minimal impact on BES reliability because it occurred while the Hugo Power Plant was offline, involved lower voltage transmission lines and lasted only twenty-eight (28) minutes. Although the ERO was not notified in accordance with the requirements EOP-004-2, WFEC did make a timely report of the event to its Reliability Coordinator. Finally, no actual harm occurred as a result of this issue. | To mitigate this minimal risk instance of noncompliance, WFEC: 1) Submitted the required Event Report to the ERO; 2) Created a reference chart for the operators illustrating when and how to report an event per the WFEC Operating Plan; 3) Implemented an improved operator log review process that requires a review of the operator's log at the end of each shift; 4) Implemented a review of the previous operator's log by the next operator on duty at the beginning of a shift; and 5) Conducted additional training on EOP-004-2 R2 reportable events at its annual operator training. SPP RE has verified the completion of all mitigation activity.
2016-02-29 | Texas Reliability Entity (Texas RE) | CPS Energy | NCR04038 | TRE2015015370 | VAR-002-4 | R3 | On November 20, 2015, CPS Energy submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R4. Based upon the review of the Self-Report provided by CPS Energy, Texas RE determined the issue pertained to VAR-002-4 R3. Specifically, CPS Energy did not notify its Transmission Operator (TOP) of a change in the status of its power system stabilizer (PSS) within 30 minutes. On May 29, 2015, CPS Energy returned a single generation unit to service following a planned maintenance outage. In the process of bringing the generation unit back online, however, CPS Energy operators failed to notice that the unit’s PSS was disabled. On May 31, 2015, a CPS Energy operator recognized that the PSS was offline and returned the PSS to automatic mode. During this time, CPS Energy did not provide notification to its TOP that the PSS in question was offline. CPS Energy did provide notice to its Qualified Scheduling Entity (QSE) that the PSS was offline and had been returned to service. However, CPS Energy’s QSE failed to notify CPS Energy’s TOP regarding the PSS status change. Accordingly, Texas RE determined that issue duration was from May 29, 2015, when CPS Energy disabled the PSS unit until May 31, 2015, when CPS Energy returned the PSS to automatic mode. The root cause of the issue was that CPS Energy’s control system was not properly configured to effectively notify CPS Energy operators that the PSS was out of service when the generation unit was brought back online. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). First, all four of the generation units at the facility in question were operating with Automatic Voltage Regulators (AVR) throughout the duration of the issue. Second, two other generation units had their PSSs in service for the entire duration of the issue, and the third unit’s PSS was in service for the majority of the time in question. With the PSSs and AVRs in service for these units, any voltage excursions likely would have been mitigated by the other devices. Lastly, PSSs do not protect the BES from generator disturbances but rather serve to protect the generating unit from disturbances on the BES. No harm is known to have occurred. Texas RE considered CPS Energy’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CPS Energy: 1) implemented an email notification system to inform operators and appropriate personnel when a PSS status changes on a generation unit; 2) provided additional training for all control room personnel concerning their notification responsibilities when a PSS changes status; 3) placed placards on the exciter control cubicle to remind maintenance to enable the PSS if somehow disabled; 4) modified plant operator procedures to include verifying the PSS status during rounds; 5) modified the plant control system to issue an alarm when a PSS becomes disabled; and 6) trained QSE operators on the requirement to notify CPS Energy’s TOP during any PSS status change. Texas RE has verified the completion of all mitigation activity.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2015015051 | PRC-001-1.1 | R4 | On July 1, 2015, IID submitted a Self-Report stating that, as a Transmission Operator (TOP), it had a issue of noncompliance with PRC-001-1.1 R4. IID failed to coordinate protection system changes with its Balancing Authorities (BAs). This issue began March 27, 2014, the first instance in which IID changed relay settings without coordinating with its BA, and ended July 16, 2015 when the BA confirmed and accepted the changes. During a mock audit on April 23, 2015, IID identified three instances in which protection system setting changes were not coordinated with one of IID’s interconnected BAs. WECC discussed details of the Self-Report in an interview with IID and requested additional information. In the first instance, on March 27, 2014, IID changed relay settings in order to maintain relay coordination following a change in Current Transformer (CT) ratios on two 230 kV lines. Although IID changed the relay elements settings, the base values monitored by the relay did not change. IID coordinated these changes with the relevant neighboring TOP. In the second instance, on November 26, 2014, IID changed relay settings after an upgraded conductor improved facility ratings. The 230 kV line in this instance was one of lines involved in the March 27, 2014 instance. IID coordinated these changes with the relevant neighboring TOP. In the third instance, on January 15, 2015, IID changed relay settings in order to enable the Phasor Measurement Unit on a 230 kV line. These changes did not affect any relay protection elements and were coordinated with the relevant neighboring TOP. The root cause of this issue was human error. This is IID's first issue of noncompliance with this requirement, and was identified and reported timely. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, IID failed to coordinate protection system changes for major transmission lines with a neighboring BAs. If these changes had impacted BA functions, such failure could have resulted in incorrect operation and/or loss of a line. However, upon discovery of the issue, IID conducted an assessment and determined that none of the relay settings changes 1) involved settings for Special Protection Systems, 2) affected facility ratings, System Operating Limits, or Interconnection Reliability Operating Limits, nor 3) reduced system reliability. As a compensating measure, although IID failed to coordinate the changes with the BA, in each instance it did coordinate the changes with applicable neighboring TOPs. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. IID does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, IID: 1) confirmed settings changes with the BA; 2) conducted an assessment to verify none of the relay settings changes a) involved settings for Special Protection Systems, b) affected facility ratings, System Operating Limits, or Interconnection Reliability Operating Limits, nor c) reduced system reliability; and 3) updated its Protection System Coordination Procedure to prevent recurrence of the issue. WECC verified completion of IID’s mitigating activities and is not requiring IID to submit a formal mitigation plan for this issue.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Portland General Electric Company (PGE) | NCR05325 | WECC2015015193 | TOP-002-2.1b | R14 | On September 1, 2015, PGE submitted a Self-Report stating that, as a Generator Operator, it had a issue of noncompliance with TOP-002-2.1b R14. On April 6, 2015, PGE failed to notify its Balancing Authority (BA) and Transmission Operator (TOP) that one of its generating units was unavailable during testing. In a separate incident on December 27, 2015, PGE failed to notify its Transmission Operator that one of its generating units was unavailable during testing. The root cause of this issue was human error. The first incident began April 6, 2015 and ended April 7, 2015. On December 30, 2015, PGE informed WECC of a second incident, which began December 27, 2015, and ended roughly one hour later. This is PGE's first issue of noncompliance with this requirement, was identified and reported timely, and posed minimal risk to the bulk power system (BPS). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In these instances, PGE failed to notify its BA and TOP when one of its generating units was unavailable. This could have posed a problem had the BA or TOP required the unit for peaking or reserve capability. In the first instance, the BA and TOP did not know a unit was unavailable for roughly thirteen and a half hours. The name plate rating of that unit is 60 MW, and at the time of the incident PGE had an additional 1,278 MW of generation capacity to call upon, if required. In the second instance, a unit was unavailable for roughly one hour, and only the TOP was unaware. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. PGE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue in both instances, PGE: 1) notified the BA and TOP that a unit was unavailable upon discovery of the oversight; 2) modified procedures in its reliability manuals to clarify standard language; 3) revised its annual training and plant reliability assessments to improve situational awareness; and 4) distributed a memorandum to relevant staff emphasizing the importance of reporting changes in real output capabilities.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2015014602 | INT-006-4 | R1; R1.2 | On January 30, 2015, PSE submitted a Self-Report stating that as a Balancing Authority (BA) it had a noncompliance with INT-006-4 R1. PSE failed to deny an Arranged Interchange request (eTag) which did not reflect proper connectivity between adjacent Balancing Authorities (BAs). This issue began on October 5, 2014, when PSE approved an eTag after it failed adjacency validation, and ended roughly one hour later when PSE terminated the transaction. This is PSE's first issue relating to this requirement, was identified and reported timely, and posed minimal risk to the BPS. The root cause of this issue was human error in wake of newly implemented process changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, PSE failed to deny an Arranged Interchange request (eTag) which did not reflect proper connectivity between adjacent BAs as prescribed in R1.2. Such failure could have adverse impacts on unscheduled parallel energy flow, Inadvertent Energy between BAs, and possible unplanned overload of transmission systems. However, the impact and potential risks of this issue are directly dependent on the magnitude, duration and effects of the improper Interchange on adjacent entities. The eTag in question was 5 MW, was revoked within one hour, and had no effect on adjacent entities. Had this issue resulted in Interchange scheduling beyond physical transmission limitations, Transmission Operators (TOPs), which are also responsible for monitoring physical limitations to Scheduling Paths, would likely have caught the error. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. PSE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) discussed the issue in person with the transmission scheduler directly involved; and 2) distributed information to all transmission schedulers to further improve awareness of path description similarities.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2015014601 | INT-006-4 | R2; R2.1 | On January 30, 2015, PSE submitted a Self-Report stating that as a Transmission Service Provider (TSP) it had a issue with INT-006-4 R2. PSE failed to deny an Arranged Interchange request (eTag) which did not reflect proper connectivity between adjacent Transmission Service Providers (TSPs). This issue began on October 5, 2014, when PSE approved an eTag after it failed Scheduling Path validation, and ended roughly one hour later when PSE terminated the transaction. This is PSE's first issue relating to this requirement, was identified and reported timely, and posed minimal risk to the Bulk Power System (BPS). The root cause of this issue was human error in wake of newly implemented process changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, PSE failed to deny an Arranged Interchange request (eTag) which did not reflect proper connectivity between adjacent TSPs as prescribed in R2.1. Such failure could have adverse impacts on unscheduled parallel energy flow, Inadvertent Energy between Balancing Authorities (BAs), and possible unplanned overload of transmission systems. However, the impact and potential risks of this issue are directly dependent on the magnitude, duration and effects of the improper Interchange on adjacent entities. The eTag in question was 5 MW, was revoked within one hour, and had no effect on adjacent entities. Had this issue resulted in Interchange scheduling beyond physical transmission limitations, Transmission Operators (TOPs), which are also responsible for monitoring physical limitations to Scheduling Paths, would likely have caught the error. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. PSE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) discussed the issue in person with the transmission scheduler directly involved; and 2) distributed information to all transmission schedulers to further improve awareness of path description similarities.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC2015014600 | INT-006-4 | R3; R3.1 | On January 30, 2015, PSE submitted a Self-Report stating that as a Balancing Authority (BA) it had a issue of noncompliance with INT-006-4 R3. PSE failed to notify the RC within ten minutes of denying a Reliability Adjustment Arranged Interchange. This issue began October 7, 2014, the first instance in which PSE failed to notify the RC within 10 minutes of denying a curtailment, and ended November 7, 2014, the last such instance. This is PSE's first issue relating to this requirement, was identified and reported timely, and posed minimal risk to the Bulk Power System (BPS). In preparation for version 4 of INT-006, PSE revised its system and processes to reflect changes in the language of the standard. Concurrently, adjacent BAs increased their use of intra-hour scheduling, which required PSE to make further revisions in order to respond to increased scheduling activities. These revisions resulted in changes to the routine of the Transmission Schedulers and their understanding of how and when eTags were to be processed. PSE’s management was aware of increased risk of potential issues occurring as a result of these changes. On November 13, 2014, PSE’s reviewed the previous month’s records and identified five instances in which it denied eTag curtailment requests, which are considered Reliability Adjustment Arranged Interchanges, without notifying the Reliability Coordinator (RC) within the 10 minute window required by R3.1. The root cause of this issue was human error in wake of newly implemented process changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In these instances, PSE failed to notify the RC within ten minutes of denying a Reliability Adjustment Arranged Interchange. Failure to notify the RC during situations in which adjustments such as curtailments cannot be fully implemented could undermine the RC’s ability to monitor and mitigate potential overloads on the transmission system. However, the individual and collective impact of the instances in scope would not have resulted in the consequences described above. In three of the instances, PSE restored the curtailment within 13 minutes from the time of denial, and did not require any consequential actions by the RC. In the remaining two instances, the curtailments were requested in order to limit flow (rather than to reduce existing flow) and would neither have resulted in any observable difference to, nor required any consequential actions by the RC. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. PSE does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, PSE: 1) modified its scheduling application to a) increase visibility and alarm when eTags near the end of their review period; b) automatically approve curtailment requests after they pass applicable validation; and c) retain visibility of curtailment requests as they’re implemented into the Area Control Error calculation; and 2) distributed information regarding the 10 minute response window and these modifications to its Balancing Dispatchers and Transmission Schedulers.
2016-02-29 | Western Electricity Coordinating Council (WECC) | Tucson Electric Power (TEPC) | NCR05434 | WECC2015015409 | EOP-008-1 | R5; R5.1 | On December 15, 2015, TEPC submitted a Self-Report stating that as a Balancing Authority (BA) and Transmission Operator (TOP), it had a issue of noncompliance with EOP-008-1 R5. TEPC failed to update the location of its new backup control center in its Operating Plan documentation within sixty calendar days of the change. This issue began February 4, 2015, sixty-one days after TEPC’s new backup control center became functional, and ended June 19, 2015 during TEPC’s annual review of its Operating Plan. This is TEPC's first issue of noncompliance with this requirement, was identified and reported timely, and posed minimal risk to the Bulk Power System (BPS). During an internal spot check in September 2015, TEPC discovered that it did not revise documentation for its Operating Plan for backup functionality within sixty calendar days following relocation of its backup control center. The root cause of this issue was lack of internal controls for subrequirement R5.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, TEPC failed to update the location of its new backup control center in its Operating Plan documentation within sixty calendar days of the change. Such failure could have decreased situational awareness or delayed response time during restoration if relevant staff relied solely on documentation to locate the backup control center. However, TEPC’s System Operators, Reliability Coordinator, and adjacent Balancing Authority and Transmission Operator were aware of the new location and the date it became functional. Additionally, all relevant staff physically visited the new location during drills and periodic equipment checks. Further, TEPC did not need to operate from the backup control center at any time during the period in question. For these reasons, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. TEPC does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, TEPC: 1) revised its Operating Plan documentation; and 2) classified this Standard as time-sensitive so its deadlines are subject to the same controls as other time-sensitive Standards. WECC verified completion of TEPC’s mitigating activities and is not requiring TEPC to submit a formal mitigation plan for this issue.
2016-01-28 | Northeast Power Coordinating Council (NPCC) | New York Independent System Operator (NYISO) | NCR07160 | NPCC2015015291 | COM-002-2 | R2. | On September 11, 2015, NYISO submitted a Self-Report stating that, as a Balancing Authority (BA), Reliability Coordinator (RC), and Transmission Operator (TOP), it had an issue of COM-002-2 R2. On August 21, 2015, the system experienced a contingency that resulted in an Interconnection Reliability Operating Limit (IROL). The system condition constitutes an emergency in NYISO. During the course of taking corrective actions, one of fifteen directives issued in a ten minute time frame failed to include a completed three part communication. The NYISO has identified a contributing factor to be a non-standard exchange of information with the receiver of the directive that may have shifted the focus of the three part communication. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The incomplete action of three part communication did not result in an incorrect action or additional reliability concerns. The directive was executed timely and correctly, as confirmed by telemetered data and the expected increase in the limit. The IROL exceedance was cleared by a combination of actions including reducing flows and energizing system equipment that increased the real time limit above the actual flow. In the event that the directive was not followed, there could have been a delay in clearing the IROL exceedance by not raising the limit as expected for this action. However, if the directive was not followed, the NYISO System Operator would have identified the issue through supervisory control and data acquisition (SCADA) and reissued the directive or taken additional steps to clear the IROL in the time required. No harm is known to have occurred. NPCC considered NYISO's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, NYISO: 1) reviewed the tape and applicable operating procedures with the operator who issued the directive; 2) updated operator training simulator sessions to include examples of non-standard communications to reinforce skills taught on managing communications to ensure three part communication is accomplished at all times. NPCC has verified the completion of all mitigation activities.
2016-01-28 | Southwest Power Pool Regional Entity (SPP RE) | Southwest Power Administration (SPA) | NCR01144 | SPP2015015350 | PRC-005-1.1b | R2; R2.1, R2.2 | On November 16, 2015, SPA submitted a Self-Report stating that, as a Transmission Owner, it had a minimal risk instance of noncompliance with PRC-005-1.1b R2 because it failed to test one power line carrier within the defined test intervals. During a review of its transition to PRC-005 version 2, SPA discovered that the power line carrier (PLC) inspection for one substation was scheduled to be performed per PRC-005-2 maintenance cycle before it had been officially transitioned from PRC-005-1b. The PLC Subject Matter Expert understood that upon implementation of the revised maintenance program document PRC-005-2 R1, the monitored PLC components of the program were fully transitioned from the 15 months cycle to the new 12-year cycle. As a result, testing was performed on the 96th day past the PRC-005-1b cycle due date. The noncompliance affected less than 5% of SPA’s total Protection Systems. The duration of the non-compliance began on August 1, 2015, the identified date of testing, and ended November 5, 2015, the date that SPA completed the testing of the power line carrier that was 96 days out of interval. The root cause of the minimal risk instance of noncompliance was human error. SPA technicians did not adhere to SPA’s current Program when scheduling and testing these Protection Systems. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The missed interval was a result of a misunderstanding of the PRC-005- 2 implementation guidelines and did not constitute a risk. SWPA's PRC-005-1b testing cycle is much shorter than what has been determined by the industry to be necessary under PRC-005-2. Additionally, the carrier is monitored by a check-back system that performs a test roughly every 24 hours with alarms coming into SCADA for 24/7 System Operator awareness and response. There was only a 96-day delay in testing from the version 1 cycle due date. No harm is known to have occurred to any SPA Protection System as a result of the issue. A Settlement Agreement covering a violation of PRC-005-1 R2.1 was filed with FERC under NP15-19-000 on January 30, 2015. On February 27, 2015, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP201100550 involved the failure to provide evidence of a Protection System maintenance and testing program. SPP RE considered SPA’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the instances were of the same Standard and Requirement, the underlying conduct of the two instances was different. The prior violation was related to lack of documentation of testing due to employee oversight of testing the devices within the defined intervals and not properly documenting the test results, while the instant issue was related to a 96-day delay in testing for one power line carrier. This minimal risk instance of noncompliance was self-reported and promptly mitigated by SPA. Additionally, the instant noncompliance, albeit a repeat, does not indicate a systemic issue of compliance for SPA. | To mitigate this minimal risk instance of noncompliance, SPA: 1. completed testing of the power line carrier on November 5, 2015, and 2. reset the maintenance management system (CASCADE) to trigger PLC testing notifications at version 1 intervals. SPP RE has verified the completion of all mitigation activity.
2016-01-28 | Texas Reliability Entity (Texas RE) | Tex-La Electric Cooperative of Texas, Inc. (TEXL) | NCR01342 | TRE2015015228 | PRC-006-1 | R9 | During a Compliance Audit conducted from September 9, 2015 through September 10, 2015, Texas RE determined that Tex-La Electric Cooperative of Texas, Inc. (TEXL), as a Distribution Provider (DP), had an issue with PRC-006-1 R9. Specifically, TEXL failed to provide automatic tripping of Load in accordance with the Under-Frequency Load Shedding (UFLS) program design as determined by its Planning Coordinator (PC). Texas RE determined that TEXL failed to meet the UFLS Program requirements. TEXL’s 2015 UFLS report included an accumulated Load relief of 16.88% instead of the required automatic Load Shedding amount of at least 25%. Additionally, TEXL did not provide UFLS data in 2014 as required. Lastly, TEXL’s 2013 UFLS report reflected an accumulated Load relief of 23.28% instead of the required automatic Load Shedding amount of at least 25%. The root cause of this issue was TEXL’s failure to develop a UFLS plan to adequately identify and address load growth on its cooperative member systems. Texas RE determined the duration of the issue to be from October 1, 2013, when the Standard became mandatory and enforceable, through the present. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TEXL is a small DP with a peak Load of 173 MW in the ERCOT Interconnection. Further, according to TEXL’s 2015 UFLS survey, TEXL’s UFLS program should have included only an additional 4.3 MW of Load relief to comply with the UFLS Program accumulated Load relief requirements. No harm is known to have occurred. Texas RE considered TEXL’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TEXL will complete the following mitigation activities by December 31, 2016: 1) develop and send to the TEXL ERCOT Members, ERCOT, STEC, Oncor, and Texas RE a preliminary UFLS program designed to meet the ERCOT requirements. This plan will incorporate the Oncor UFLS Point that shed TEXL Load; 2) hold discussions with the TEXL ERCOT Members, ERCOT, STEC, Oncor, and Texas RE to better define the new UFLS plan; 3) request each TEXL ERCOT Member to report: • the load by distribution circuit for all distribution circuits; • the transmission station where each circuit located; • the winter, fall, summer, and spring peak load for each circuit; • the winter, fall, summer, and spring minimum load for each circuit; • any circuits that are part of the primary Manual Load Shed plan; • the circuits that are part of the primary Manual Load Shed plan; and • the circuits which already have in-service UFLS equipment installed. 4) request each TEXL ERCOT Member that has UFLS Relays to report: • the frequency trip setting for each UFLS relay; • the intentional time delay for each UFLS relay; • the breaker operating time for each breaker associated with a UFLS relay; and • the relay operating time for each UFLS relay, exclusive of any intentional delay. 5) complete a study of the TEXL Member Loads and determine the best locations for new UFLS Points; 6) revise the TEXL UFLS Plan to require each Member with Load in ERCOT to participate in the UFLS program, unless the only Load in ERCOT is on a Manual Load Shed circuit; 7) develop a formal operating process that addresses the UFLS requirements of the ERCOT Operating Guides and puts in place a mechanism for a review of the UFLS program when new end-user load is added to the TEXL Members’ System; 8) hold a meeting with all applicable Members to review and approve the revised UFLS program; 9) ensure each Member implements the UFLS program changes/additions; and 10) hold a UFLS test in October 2016 to determine if each Member and TEXL meet the ERCOT requirements. TEXL requires until December 31, 2016, to complete mitigation because it will take that amount of time to complete the number of steps that are referenced above. Additionally, TEXL must obtain funding from each pertinent Member.
2016-01-28 | Western Electricity Coordinating Council (WECC) | La Paloma Generating Company LLC (LPGC) | NCR05210 | WECC2014014003 | VAR-002-1.1b | R2; R2.2 | On June 23, 2014, LPGC submitted a Self-Report stating that, as a Generator Operator (GOP), it was in noncompliance with VAR-002-1.1b R2. The root cause of this issue was a combination of incorrect settings limiting or defaulting voltage below schedule and human error. This issue began on July 18, 2012 and ended May 9, 2014. This is LPGC's first issue relating to this requirement and posed minimal risk to the bulk power system (BPS). On April 15, 2014, an equipment malfunction caused one of LPGC’s generating units to default to a voltage variant of what was directed by the Transmission Operator (TOP). LPGC contacted the TOP the following morning to explain the deviation from the voltage order. Although this incident was triggered by equipment malfunction, LPGC considered whether the variant voltage and delayed notification to the TOP were issues of noncompliance with VAR-002-1.1b R2. LPGC initiated an internal review of voltage order observance to determine whether similar events occurred during the period between LPGC’s last audit and the date of the review. The review indicated that one or more of LPGC’s four generating units failed to maintain voltage as directed by the TOP for a collective 191 hours from July 28, 2011 through May 15, 2014. Roughly half of the hours were the result of the operator’s failure to change the voltage at the prescribed time; the remainder occurred during testing or as the result of equipment failure. This issue began on July 18, 2012, the earliest instance of deviating voltage identified during the review, and ended May 9, 2014, the latest instance identified during the review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In these instances, LPGC failed to maintain the generator voltage as directed by the TOP. Such failure could have effected a mismatch between expected and actual generator output voltage, resulting in insufficient voltage support. However, LPGC implemented compensating measures to decrease the likelihood of the consequence described above. In all instances, each unit remained in AVR, insuring the system’s ability to adjust to voltage fluctuations, and in most instances, at least one of the other units followed the appropriate voltage schedule. Further, although no harm is known to have occurred, the voltage deviations identified in the review were relatively small and would have had limited impact on BES components. Based on this information, this issue posed minimal risk to the reliability of the Bulk Power System. LPGC does not have previous violations of this Standard and Requirement. | To mitigate this issue, LPGC: 1) tested each generating unit and corrected the settings for the automatic voltage regulators to prevent voltages from defaulting below scheduled voltage; 2) performed a thorough review of voltage order observance on an hour-by-hour basis to identify all instances in which one or more units failed to maintain voltage as directed by the TOP, and to determine the cause and extent of each deviation; 3) implemented an automatic DCS voltage schedule scheme to insure voltage changes will meet the schedule with minimal operator involvement; 4) installed additional DCS alarms to each unit requiring operator acknowledgement of any voltage deviations; 5) administered weekly reviews of voltage schedule observance; and 6) adopted annual training of internal procedures regarding maintenance of voltage schedules and changes, with emphasis on TOP communication during instances in which schedules cannot be met. WECC verified that LPGC completed mitigating activities on July 15, 2014.
2016-01-28 | Western Electricity Coordinating Council (WECC) | La Paloma Generating Company LLC (LPGC) | NCR05210 | WECC2015015046 | VAR-002-3 | R2; R2.2 | On June 30, 2015, LPGC submitted a Self-Report stating that, as a Generator Operator (GOP), it was in noncompliance with VAR-002-3 R2. LPGC failed to maintain the generator voltage as directed by the Transmission Operator (TOP). The root cause of this issue was a misunderstanding of verbal communication with the TOP. This issue began and ended on April 13, 2015 (one hour duration). This is LPGC's second issue relating to this requirement, was identified and reported timely, and posed minimal risk to the BPS. On April 20, 2015, a weekly review of voltage schedule observance indicated that on April 13, 2015 LPGC adjusted voltage on one of its units one hour before the scheduled change. This issue was the result of a misunderstanding of time notation during communication with the TOP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, LPGC failed to maintain the generator voltage as directed by the TOP. Such a failure could have effected a mismatch between expected and actual generator output voltage, resulting in insufficient voltage support. However, LPGC implemented compensating measures to decrease the likelihood of the consequence described above. The unit in question was the only unit operating at the time, had an output voltage 1kV below schedule for one hour, and remained in AVR, insuring the system’s ability to adjust to voltage fluctuations. For these reasons, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. LPGC has one previous issue relating to this Standard and Requirement (WECC2014014003). The previous issue was not considered an aggravating factor because mitigating activities implemented as a result of the previous issue led to timely identification, correction and reporting of this issue. | To mitigate this issue, LPGC: 1) revised procedures to emphasize clarity of time notation in all communications; and 2) implemented policy whereby operators communicate, perform and log actions using real time rather than hour ending format. WECC verified completion of LPGC’s mitigating activities.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Seattle City Light (SCL) | NCR05382 | WECC2015014631 | BAL-005-0.2b | R9 | On February 12, 2015 SCL submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue of potential noncompliance with BAL-005-0.2b R9. This issue began and ended on November 2, 2014, when SCL failed to correctly include the eTag in its calculation of Net Scheduled Interchange for use in the Area Control Error (ACE) equation. The duration of this issue was roughly 40 minutes. On November 2, 2014, between 4:33 p.m. and 7:30 p.m. PST, SCL experienced an internet outage. Although SCL’s primary internet provider continued to accept outbound data from SCL during the outage, it did not pass on most of the data. Some data was carried by a secondary provider, including most of SCL’s eTag scheduling data, which was carried by a direct T-1 line connecting SCL’s power operations application with Open Access Technology International, Inc., (OATI). However, as the undelivered data held by the primary provider accumulated, internet-based applications began to degrade and fail. As a result of this loss, SCL was eventually unable to automatically send/receive Hourly Interchange Numbers, and could not issue/respond to eTags automatically. At 6:41 p.m., a reliability curtailment of 1 MW was requested for eTag SCL PWX01Z507113 CISO to be effected at 7:00 p.m., and at 6:49 p.m. OATI’s “Backstop” service automatically approved the request. Due to the outage, this curtailment was entered into SCL’s schedule at 7:37 p.m. and implemented at 7:40 p.m. This is SCL's first violation of this requirement. The root cause of this issue was lack of technology management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SCL failed to implement a 1 MW reliability curtailment eTag during an internet outage. As a result, this eTag was not included in the calculation of Net Scheduled Interchange for the ACE equation. An incorrect ACE value could result in over or under generation. However, 24/7 staffing of the System Operations Control Center and Power Marketing operation enabled SCL to notice degradation of affected applications and commence alternative actions. SCL leveraged its Energy Management System, which is independent of the Internet and provides full situational awareness of real-time transmission limits, loadings, and alarming during this type of event; implemented manual balancing and control processes from its emergency plan; and informed the RC and neighboring BAs of the situation. Since SCL is neither a Transmission Service Provider nor a Path Operator, these measures ensured SCL was made aware of any significant curtailments, equipment outages, or large power flow changes during the outage. Based in this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. SCL does not have previous violations of this Standard and Requirement. | To mitigate this issue, SCL: 1) improved visibility of connectivity to OATI by configuring monitoring of the direct T-1 line by URL rather than IP address; 2) installed an additional work station in its System Operation Center with connection to an alternate internet provider. SCL operators reviewed SCL’s process for operating this work station during future outages of primary or secondary service, and logged into OATI and other internet-based applications to test functionality; and 3) installed an additional work station on its Power Operations & Marketing floor with connection to an alternate internet provider. SCL Real-time Power Marketers reviewed its revised Emergency Preparedness Standard Operating Procedure for operating this work station during future outages of primary or secondary service, and logged into OATI and other internet-based applications to test functionality.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Seattle City Light (SCL) | NCR05382 | WECC2015014852 | BAL-006-2 | R4 | On February 12, 2015, SCL submitted a Self-Certification stating that, as a Balancing Authority, it had an issue of potential noncompliance with BAL-006-2 R4. This issue began and ended on November 2, 2014, when SCL failed to operate with adjacent BAs to a common Net Interchange Schedule and Actual Net Interchange value for a duration of roughly 40 minutes. On November 2, 2014, between 4:33 p.m. and 7:30 p.m. PST, SCL experienced an internet outage. Although SCL’s primary internet provider continued to accept outbound data from SCL during the outage, it did not pass on most of the data. Some data was carried by a secondary provider, including most of SCL’s eTag scheduling data, which was carried by a direct T-1 line connecting SCL’s power operations application with Open Access Technology International, Inc., (OATI). However, as the undelivered data held by the primary provider accumulated, internet-based applications began to degrade and fail. As a result of this loss, SCL was eventually unable to automatically send/receive Hourly Interchange Numbers, and could not issue/respond to eTags automatically. At 6:41 p.m., a reliability curtailment of 1 MW was requested for eTag SCL PWX01Z507113 CISO to be effected at 7:00 p.m., and at 6:49 p.m. OATI’s “Backstop” service automatically approved the request. Due to the outage, this curtailment was entered into SCL’s schedule at 7:37 p.m. and implemented at 7:40 p.m. This is SCL's first violation of this requirement. The root cause of this issue was lack of technology management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SCL briefly failed to operate to a common Net Interchange Schedule and Actual Net Interchange value. Such failure could result in inaccurate Inadvertent Interchange accounting, which could lead to load and resource imbalance. However, 24/7 staffing of the System Operations Control Center and Power Marketing operation enabled SLC to notice degradation of affected applications and commence alternative actions. SCL leveraged its Energy Management System, which is independent of the Internet and provides full situational awareness of real-time transmission limits, loadings, and alarming during this type of event; implemented manual balancing and control processes from its emergency plan; and informed the RC and neighboring BAs of the situation. Since SCL is neither a Transmission Service Provider nor a Path Operator, these measures ensured SCL was made aware of any significant curtailments, equipment outages, or large power flow changes during the outage. Based in this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. SCL does not have previous violations of this Standard and Requirement. | To mitigate this issue, SCL: 1) improved visibility of connectivity to OATI by configuring monitoring of the direct T-1 line by URL rather than IP address; 2) installed an additional work station in its System Operation Center with connection to an alternate internet provider. SCL operators reviewed SCL’s process for operating this work station during future outages of primary or secondary service, and logged into OATI and other internet-based applications to test functionality; and 3) installed an additional work station on its Power Operations & Marketing floor with connection to an alternate internet provider. SCL Real-time Power Marketers reviewed its revised Emergency Preparedness Standard Operating Procedure for operating this work station during future outages of primary or secondary service, and logged into OATI and other internet-based applications to test functionality.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2015014736 | PRC-023-1 | R1 | On March 10, 2015, AZPS submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R1. AZPS failed to set a transmission line relay so it did not operate at or below 150% of the highest seasonal Facility Rating of the circuit. AZPS reported that it utilizes switch-on-to-fault (SOTF) relay schemes. The primary purpose of the SOTF scheme is to trip a transmission line breaker if it is closed in to a faulted line during a restoration procedure. The SOTF scheme is not armed while the line is in operation. The scheme only arms when the breaker opens and remains armed until 10 cycles past the closing of the breaker. In September 2013, AZPS adjusted all but one relay setting to comply with PRC-023-2. The one omitted relay setting is an SEL-311L relay at the North Gila Substation on the North Gila-Imperial Valley 525 kV line. The one relay function protecting the North Gila-Imperial Valley 525 kV line was not set in accordance with PRC-023-2 R1 Criteria 1. The relay was set to operate above 137% of the highest seasonal Facility Rating rather than being set so that the relay does not operate at or below 150% of the highest seasonal Facility Rating. The North Gila-Imperial Valley line is not owned by AZPS. The owner of the line used a logic equation configuration different from AZPS’s standard logic equation. AZPS uses the setting 50P1 for SOTF function and 50P2 for loss of potential tripping function. The protocol used for the relay in scope reversed this using 50P1 for loss of potential and 50P2 for SOTF. This set up a scenario where the engineer performing the check failed to recognize the different configuration and checked the wrong relay setting for SOTF. In December 2014, AZPS reviewed SOTF relays settings using a step-by-step process. This annual review revealed non-standard configuration and an inaccuracy in the SEL-311L relay setting. AZPS investigated the setting and coordinated with the owner of the North Gila-Imperial Valley line. On January 6, 2015, AZPS confirmed the relay setting was incorrect and immediately changed the setting. The compliance exception start date was October 1, 2013, when Requirement 1 became applicable to the SOTF scheme. The compliance exception end date was January 6, 2015, when AZPS changed the relay setting to comply with PRC-023-2 R1. The root cause of the compliance exception was a lack of detail in the procedure used during the annual review of relay settings; the procedure did not require a check of the logic equation. | This issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AZPS failed to set a transmission line relay so it did not operate at or below 150% of the highest seasonal Facility Rating of the circuit. Failure to set the relay correctly could have caused an inadvertent trip of the North Gila – Imperial Valley transmission line if the breaker was closed and the load current immediately flowing was greater than 137% of line rating. This could potentially lead to the loss of a single 525 kV line. However, AZPS implemented controls to mitigate the potential risk. AZPS has real-time, twenty four hours a day seven days a week monitoring of its system. In the event of a protection system operation, AZPS’s System Operators would receive an alarm and are trained to respond appropriately. Information utilized to analyze the protection system operation would have revealed the incorrect setting. AZPS installed Phasor Measurement Units at North Gila to monitor phase angles across the open line; preventing closing during a large phase angle difference. This ensures that there would not be a large increase in MW flow and also reduces the potential for SOTF tripping during restoration. Additionally, AZPS checks SOTF relay settings annually using a step-by-step Protective Metering and Control procedure. No harm is known to have occurred. WECC considered AZPS’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, AZPS: 1) re-checked all SOTF relays on the Bulk Electric System (BES) to verify compliance with PRC-023 and determine protocol used in logic equation; 2) coordinated with line owner to confirm correct SOTF setting; 3) changed relay setting to comply with the loadability requirement in PRC-023 R1 Criteria 1; 4) changed relay protocol to match the AZPS standard; 5) used internal Corrective Action Program to identify root cause for this situation; 6) developed plan to prevent future incidents based on root cause analysis; 7) implemented new procedure and notified personnel of change; and 8) updated Protective Metering and Control procedure for PRC-023 to include check of the logic equation and addition of peer check. WECC has verified the completion of all mitigation activity.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Calpine Corporation (CPN) | NCR00006 | WECC2015014850 | PRC-005-1.1b | R2 | On April 9, 2015, CPN submitted a Self-Report, stating that, as a Generator Owner, it had a possible issue with PRC-005-1.1b R2. CPN failed to conduct monthly battery maintenance for the first two months of 2014 for five battery systems, including battery chargers, out of 72 total battery systems. CPN company compliance personnel reviewed CPN’s Gilroy generation facility records, talked with plant personnel, and determined that site personnel completed monthly battery logs (required by company policy) for January and February 2014 without performing the battery inspections. Further investigation by CPN showed that all other required inspection and maintenance, including more extensive quarterly battery inspections covering the same equipment and period, had been properly performed. A WECC SME reviewed the Self-Report and interviewed CPN compliance personnel, and determined that CPN had a compliance exception with PRC-005-1.1b R2, for its failure to perform monthly inspections on its battery systems, according to its maintenance and testing program, for the months of January and February 2014. The SME confirmed that CPN performed quarterly and annual maintenance and/or testing on the battery systems, as well as a five year load/performance test. WECC reviewed the Self-Report and the SME’s findings, and determined that CPN had a compliance exception of PRC-005-1.1b R2, for its failure to show evidence that it had performed maintenance and testing within the defined intervals, for the months of January and February 2014, for its battery systems. No harm was known to have occurred. This compliance exception started on January 1, 2014 and ended on February 28, 2014. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CPN failed to conduct monthly battery maintenance for the first two months of 2014 for five battery systems, including battery chargers, out of 72 total battery systems. By not performing this maintenance, it is possible that an early degradation of the battery systems could have gone undetected, and the related protection system would not have operated correctly. As a compensating control, CPN performed quarterly, annual, and five year maintenance and testing of the battery systems in the required intervals. CPN operates a combined-cycle 130MW unit and three 60MW single cycle units at the Gilroy generation station. Each unit (four combustion turbines and a steam turbine) has a battery and battery charger. The Gilroy generation station is manned continuously, and an operator makes daily rounds of the battery systems, inspecting for unusual conditions. WECC considered CPN's compliance history and determined there were no relevant instances of noncompliance. | CPN remediated this compliance exception by resuming its monthly inspections in March, 2014. CPN has not submitted a Mitigation Plan to address this compliance exception. CPN is required to submit a Mitigation Plan to remediate the compliance exception addressed herein within twelve months. Failure to complete mitigation in the established timeframe will result in rescission of the eligibility for compliance exception treatment for the noncompliance in question.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2015014964 | MOD-026-1 | R6 | On June 3, 2015, AZPS submitted a Self-Report stating that, as a Transmission Planner, it had a possible issue of noncompliance with MOD-026-1 R6. AZPS reported that its Transmission Planning department failed to provide a written response indicating whether a generator model was usable to its Technical Projects Engineering department within the time frame required by MOD-026-1 R6. AZPS’s Technical Engineering department performs testing of AZPS’s generators on behalf of the Generator Owner (GO). The root cause of this issue was less than adequate internal controls for tracking and meeting the 90 day deadline.This issue began February 9, 2015, the day after the written response was due, and ended March 4, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, AZPS failed to provide a written response to the GO regarding model information for a generator excitation and voltage regulator control system within 90 days. However, a previously validated generator model was already in place and functioning properly during the period in question. Updates to the model were non-material, would not have affected the outcome of the Transmission Planning study, and were unacknowledged for only 24 days beyond the response deadline. In the unlikely event that the updates would have rendered the model not usable, AZPS would have continued to use the previous model. Further, this issue was limited to a single 133 MVA generator. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. AZPS does not have previous violations of this Standard and Requirement. | To mitigate this issue, AZPS: 1) provided a written response to the GO; 2) developed a formalized process to track completion of standard-mandated timelines and provided training to requisite staff; and 3) directed all Generator Operators GOPs in AZPS’s Transmission Planning area to send all modeling data and response requests to its Transmission Planning department inbox, rather than to individuals. WECC verified completion of AZPS’s mitigating activities on December 11, 2015.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2015014965 | MOD-027-1 | R5 | On June 3, 2015, AZPS submitted a Self-Report stating that, as a Transmission Planner, it had a possible issue of noncompliance with MOD-027-1 R5. AZPS failed to provide a written response to the Generator Owner (GO) regarding model information for a generator turbine/governor control model within 90 days. AZPS reported that its Transmission Planning department did not provide a written response indicating whether a generator model was usable to its Technical Projects Engineering department within the time frame required by MOD-027-1 R5. AZPS’s Technical Engineering department performs testing of AZPS’s generators on behalf of the GO. The root cause of this issue was less than adequate internal controls for tracking and meeting the 90 day deadline.This issue began February 9, 2015, the day after the written response was due, and ended March 4, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, AZPS failed to provide a written response to the GO regarding model information for a generator turbine/governor control model within 90 days. However, a previously validated generator model was already in place and functioning properly during the period in question. Updates to the model were non-material, would not have affected the outcome of the Transmission Planning study, and were unacknowledged for only 24 days beyond the response deadline. In the unlikely event that the updates would have rendered the model not usable, AZPS would have continued to use the previous model. Further, this issue was limited to a single 133 MVA generator. Based on this information, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. AZPS does not have previous violations of this Standard and Requirement. | To mitigate this issue, AZPS: 1) provided a written response to the GO; 2) developed a formalized process to track completion of standard-mandated timelines and provided training to requisite staff; and 3) directed all Generator Operators GOPs in AZPS’s Transmission Planning area to send all modeling data and response requests to its Transmission Planning department inbox, rather than to individuals. WECC verified completion of AZPS’s mitigating activities on December 11, 2015.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Pend Oreille County Public Utility District No. 1 (POPD) | NCR05315 | WECC2015015087 | PRC-005-1 | R1 | During a Compliance Audit conducted from June 29 to July 10, 2015, WECC determined that, as a Transmission Owner and a Distribution Provider, POPD had an issue of noncompliance with PRC-005-1 R1. WECC determined that POPD’s Protection System Maintenance Plan (PSMP) for PRC-005-1.1b did not identify a summary of tests for DC control circuits. Although POPD stated in its PSMP that control circuit verification is performed at the same time the relays are tested, there is no detailed summary of maintenance for DC circuit testing. According to POPD SMEs, POPD applies current and voltage quantities to the relay while performing maintenance and the relay operates at this time, but there is no indication the control circuit was verified. The audit team determined there was not sufficient evidence the control circuits were verified from the output of the relay to the circuit breaker. In addition, POPD’s PSMP included an exception for extending the maintenance and testing intervals for all protection system elements in the PSMP, leaving them open-ended. Specifically, POPD’s “Facility Protection Testing & Maintenance Program – Transmission & Distribution”, dated April 27, 2012, states that “testing intervals can vary up to eight (8) months beyond the indicated next scheduled test date due to the availability of testing personnel, etc. Also, the testing intervals can be lengthened or reduced as determined by ongoing maintenance requirements.” WECC determined that POPD has an issue of noncompliance with PRC-005-1 R1, for (1) its failure to identify a summary of maintenance and testing procedures for DC control circuits in its PSMP, and (2) for including exception language related to its intervals for maintenance and testing, in its PSMP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk to POPD for failing to identify a summary of maintenance and testing procedures for DC control circuits is that POPD may not know if the breaker will trip when called upon, or during a fault, overload or disturbance. As compensating measures, POPD provided records indicating that all devices are and were current, and that testing and maintenance is occurring within the intervals stated in the PSMP. Furthermore, POPD updated the maintenance and testing procedures for DC control circuits, and removed the exception language in the new PSMP for PRC-005 Version 2. In addition, although POPD had exception language in its PSMP, there was no evidence that it ever used the exception to extend maintenance intervals. WECC considered POPD's PRC-005-1 R1 compliance history in determining the disposition track. WECC considered POPD's compliance history and determined there were no relevant instances of noncompliance. WECC determined that POPD's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue of noncompliance, POPD revised its PSMP in compliance with PRC-005-2. POPD’s document titled Protection System Maintenance Program, Document No. REA-1003-0, dated April 1, 2015, identifies the minimum maintenance requirements for all elements including DC Control Circuitry, and does not allow POPD to extend maintenance beyond the maximum interval. WECC will not require further mitigating activities for this issue of noncompliance.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Pend Oreille County Public Utility District No. 1 (POPD) | NCR05315 | WECC2015015088 | PRC-005-1 | R2 | During a Compliance Audit conducted from June 29 to July 10, 2015, WECC determined that, as a Transmission Owner and a Distribution Provider, POPD had an issue of noncompliance with PRC-005-1 R2. According to the WECC Audit Team, POPD did not fully implement its Protection System Maintenance and Testing Program, including documentation that all the applicable protection system devices were maintained and tested within the defined intervals for its DC Control Circuitry. Although POPD’s PSMP says, “For electrical mechanical relays, measure and record the ‘voltage’ at the relay case input terminals and clamp-on ‘current’ reads at the relay case input terminals or relay terminal strip, as appropriate:” it does not provide a summary of maintenance procedures for DC circuit testing. POPD confirmed this at the Audit, clarifying that there is no detailed summary of maintenance in the PSMP. This failure was corrected in the new version of its PSMP. Enforcement reviewed the Audit findings and determined that POPD has an issue of noncompliance with PRC-005-1 R2, for its failure to provide evidence that it had maintained and tested its DC Control Circuitry within the required intervals, and the date each protection system device was last tested and maintained. The compliance exception started on June 18, 2007, the date the Standard was applicable to POPD; and ended on July 9, 2013, the last documented test date for POPD’s DC Control Circuitry. | This compliance exception posed a minimal risk, but did not pose a serious or substantial risk to the reliability of the bulk power system. The risk to POPD for failing to identify a summary of maintenance and testing procedures for DC control circuits, is that POPD may not know if the breaker will trip when called upon, or during a fault, overload or disturbance. As compensating measures, POPD provided records at the Audit indicating that all devices are and were current, and that testing and maintenance is occurring within the intervals stated in the PSMP. Going forward, as a preventive control, POPD made changes in its revised PSMP for Version 2 outlining the minimum maintenance requirement and the maximum maintenance intervals for DC Control Circuitry, to ensure the maintenance is performed. WECC considered POPD's PRC-005-1 R2 compliance history in determining the disposition track. POPD's relevant prior noncompliance with PRC-005-1 R2 is limited to NERC Violation ID WECC200901525. In this occurence, 14 POPD protection system devices were five months late for maintenance and testing in 2009, according to POPD's defined intervals. POPD completed its mitigation actions by July 24, 2009. WECC did not consider this occurrence as an aggravating factor in this compliance exception, as mitigation was completed over three years ago. Therefore, WECC determined that POPD's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue of noncompliance, POPD revised its PSMP in compliance with PRC-005-2. POPD’s document titled Protection System Maintenance Program, Document No. REA-1003-0, dated April 1, 2015, identifies the minimum maintenance requirements for all elements including DC Control Circuitry, and does not allow POPD to extend maintenance beyond the maximum interval. POPD. WECC will not require further mitigating activities for this issue of noncompliance.
2016-01-28 | Western Electricity Coordinating Council (WECC) | PUD No. 1 of Douglas County (DOPD) | NCR05343 | WECC2015015091 | EOP-005-2 | R4 | On July 20, 2015, DOPD submitted a Self-Report stating that, as a Transmission Operator, it was in noncompliance with EOP-005-2 R4. DOPD failed to update its restoration plan prior to implementing a planned BES modification. The root cause of this issue was human error and less than adequate internal controls. This issue began May 22, 2014, when DOPD energized the line, and ended July 17, 2015, when DOPD provided its updated restoration plan to the RC. This is DOPD's first violation of this requirement and posed minimal risk to the BPS. On July 20, 2015, DOPD self-reported an issue identified during an internal review. The review indicated that DOPD energized a 230 kV line without first submitting an updated restoration plan to its RC. The RC approved an updated restoration plan in November 2014; however, that plan did not include the new line. DOPD energized the line on May 22, 2014, and discovered the oversight on June 25, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, DOPD failed to update its restoration plan prior to implementing a planned BES modification. Such failure could have resulted in the RC’s inaccurate understanding of DOPD’s restoration plan during an event. However, DOPD’s relatively small size limits its ability to project adverse effects beyond its own system. DOPD serves a primarily rural area, does not share additional responsibilities with other entities, and did not affect any neighboring entities during the period in question. Additionally, the line in scope is a parallel path to the existing 115 kV distribution network, and failure to restore the line during implementation of the restoration plan would have little to no impact on the reliability of the BES. Further, no events required implementation of the restoration plan during the period in question. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the BPS. DOPD does not have previous violations of this Standard and Requirement. | To mitigate this issue, DOPD: 1) provided its updated restoration plan to the RC; 2) notified adjacent entities of the updated plan; 3) modified company policies and revised automated task reminders to include planned BES modifications; and 4) provided training regarding modifications to requisite staff. WECC verified completion of DOPD’s mitigating activities on October 30, 2015.
2016-01-28 | Western Electricity Coordinating Council (WECC) | High Desert Power Project, LLC (HDPP) | NCR05184 | WECC2015015111 | VAR-501-WECC-2 | R1 | On July 30, 2015, HDPP submitted a Self-Report citing possible non-compliance with VAR-501-WECC-2 R1. HDPP failed to ensure that the Power System Stabilizer (PSS) was in service 98% of all operating hours. HDPP stated in its Self-Report that while ramping down its generator for shutdown on June 2, 2015, its steam turbine PSS tripped off for an unknown reason. HDPP’s default setting for its PSS is always on, therefore, during any startup its PSS automatically goes into service. However, since the PSS tripped off-line, it remained in this tripped state for the subsequent startup. As a result, when the plant re-started on June 5, 2015, the steam turbine PSS remained out of service. On June 10, 2015, HDPP’s plant control room operator discovered the PSS operational state and immediately placed it in service. A WECC Subject Matter Expert (SME) reviewed the Self-Report and discussed the possible non-compliance with HDPP. The SME determined that when HDPP shut-down its generator for maintenance its steam turbine PSS had tripped off. Then when the generator was turned back online the alarm was inadvertently missed due to the multitude of alarms associated with startup of the generating unit. WECC determined that HDPPs failure to ensure the PSS was in service for 98% for all operating hours in accordance to the Standard is a Compliance Exception of VAR-501-WECC-2 R1. The total time the PSS was turned off for second quarter 2011 was 136.37 hours. The total run time for the unit during the second quarter 2015 was 1,349.68 hours. Therefore, the PSS was in service for 89.90% of the operating time for the second quarter, which falls below the 98% threshold. The start date of this issue was June 6, 2015, when the PSS tripped off-line and the end date of this issue was June 10, 2015, when the PSS was placed into service. The root cause of this Compliance Exception is human error – The HDPP operators did not see that the PSS was off during the time which the violation occurred. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. HDPP failed to have its PSS in service 98% of all operating hours for its steam turbine generator equipped with PSS, as required by VAR-501-WECC-2 R1. Failure to have its PSS in service could cause uncontrolled voltage oscillations, which could cause a voltage collapse. However, HDPP implemented preventative controls. Specifically, one combustion turbine generator (197 MVA) was in service for .55 hours, two combustion turbine generators (394 MVA) were in service for 40.42 hours, and three combustion turbine generators (591 MVA) were in service for 95.43 hours, for a total of 136.4 hours during the time when the STG’s PSS was off. Therefore, by having the other generating units operating with their PSS in service, the risk of uncontrollable voltage oscillations is greatly reduced. In this instance the unit operated with the PSS in service for the majority of the calendar quarter, reducing the probability of instability, thus reducing the probability of an unnecessary loss of a facility during an event. For these reasons, WECC determined posed minimal risk to the reliability of the BES. HDPP has a prior violation of VAR-501-WECC-1 R1 identified by NERC ID WECC2012009813. WECC determined that HDPP failed to operate its voltage regulators without the PSS in service for 93.7% of the operating time for the quarter 2011, which fell below the 98% threshold. However, given the three year lapse in time from the date the prior violation was mitigated to the start date of the current issue, WECC determined that HDPP's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, HDPP: 1) Added a PSS status check to the control room operator turn over sheet; 2) Added a PSS status to the PI data historian to allow additional monitoring of these parameters; 3) Conducted a training for Operations on NERC Standard VAR-002-4, VAR-002-WECC-2 and VAR-501-WECC-2; and 4) Created a "PSS Not Active" flashing alarm on the CEMS Overview screen. The CEMS Overview screen is always displayed and the alarm will not clear until the appropriate PSS is placed in service.
2016-01-28 | Western Electricity Coordinating Council (WECC) | PacifiCorp (PAC) | NCR05304 | WECC2015015271 | MOD-008-1 | R4 | On October 6, 2015, PAC submitted a Self-Report stating that, as a Transmission Operator, it had an issue with MOD-008-1 R4. PAC did not establish TRM values within 13 months. On March 17, 2014, PAC reviewed and established its TRM values in accordance with its TRM Implementation Document (TRMID). Based on the 2014 date, PAC was required to establish TRM values by April 17, 2015. On July 25, 2015, PAC’s compliance office performed an internal review of MOD-008-1 R4. As a result of the internal review, PAC discovered that it had not established TRM values at least once every 13 months. PAC established TRM values in July 2015, three months beyond the 13 month requirement. As part of the 2015 review, one path had a TRM adjustment. The TRM value for the Major WECC Transfer Path TOT 4B was revised down from 289MW to 260MW. This reduction potentially allowed more transmission capability for the path than was previously allotted. The compliance exception start date was April 18, 2015, when PAC was required to establish TRM values in accordance with the TRMID. The compliance exception end date was July 18, 2015, when PAC completed the review and established TRM values in accordance with the TRMID. The root cause of this issue was that an employee retired and the new employee responsible was not aware that TRM values needed to be reviewed and established once every 13 months instead of once every calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, PAC did not establish TRM values within 13 months which could lead to possible transmission congestion issues if sufficient reliability margin was not properly determined and maintained. However, PAC implemented an internal review of this Standard and Requirement resulting in timely discovery and remediation. PAC reviewed and established the TRM values within three months of when they were due. Only one path required adjustment; a reduction that may result in more transmission capability than the prior TRM value. The adjusted TRM did not further constrain the path. No harm is known to have occurred. WECC considered PAC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PAC: 1) reviewed and established TRM values in accordance with the TRMID; 2) conducted training on the review cycle associated with the Standard; and 3) implemented an automatic control that will automatically issue an email notification to five transmission and compliance employees as a reminder that the 13 month review period has started. WECC has verified the completion of all mitigation activity.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2015015359 | PRC-005-1.1b | R2 | On September 1, 2015, IPCO submitted a self-log stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. IPCO failed to provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Entity on request (within 30 calendar days) in two instances. In the first instance, The Langley Gulch Power Plant (Langley) has a station battery supply as part of a generator protective system. The station battery supply consists of a bank of vented (flooded cell) 130vdc lead-acid batteries and charger. In accordance with PRC-005-1.1b, the entity's Power Production department has developed and implemented a maintenance and testing plan for the battery bank (Battery M&T Plan). Among other requirements, the Battery M&T Plan requires annual inspections to ensure the proper operation of the battery bank and associated charger. On April 3, 2015, the Power Production Manager reported to Regulatory Compliance that the annual maintenance and testing were not conducted for the Langley station battery bank as required by the Battery M&T Plan. Per discussion with the Power Production Manager, he received a Project Work Order report on April 1, 2015 from the entity’s Asset Suite system that showed the annual requirements were not completed by the March 19, 2015, due date established in Asset Suite. The Power Production Manager notified the Power Plant Area Maintenance Leader of the uncompleted maintenance and testing on the same day he received the report. The Power Plant Area Maintenance Leader completed the annual testing on April 10, 2015. Power Supply uses Asset Suite to help manage and document the implementation of the Battery M&T Plan. The Power Plant Area Maintenance Leader is responsible for reviewing project work orders generated from Asset Suite and overseeing the completion of the maintenance activities. For Langley, Asset Suite generates project work orders 60 days in advance of the Asset Suite due date for maintenance activities. The Asset Suite due date is based on the date testing was completed in the prior year as the Asset Suite reminder is programmed to set the next due date 365 days from the date the current test is completed. As the annual portion of the Battery M&T Plan was completed on March 19, 2014, Asset Suite set the next due date for March 19, 2015. Although the Battery M&T Plan requires annual inspections of the battery bank and associated charger, the term “annual” is not defined in the Battery M&T Plan. The Power Production group has implemented this annual requirement as each 365 days through the use of Asset Suite, but this implementation of the plan was not clearly defined. In the second instance, on September 1, 2015, IPCO submitted a self-log stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R1.On May 20, 2015, Regulatory Compliance was advised by a Power Production Engineering Leader and Principal Engineer that preparations for the upcoming WECC audit revealed one protective relay for the Twin Falls Power Plant generation unit #2 (Twin Fall Unit #2) excitation transformer was not included in the implementation of the Protection System Maintenance Plan (PSMP). Power Production was concerned at the time that other excitation transformers may have been missed. Then, on June 17, 2015, Power Production confirmed that Milner power Plant generation unit #1 (Milner Unit #1), which is the same vintage as Twin Falls Unit #2, has a similar excitation transformer with relay protection that was not included in the implementation of the PSMP. As a result, a total of two excitation transformers, one for each unit identified above, were not included in the implementation of the PSMP. According to the Principal Engineer, the relays are original to the plant (the Milner and Twin Falls excitation systems were actually manufactured in Sweden) and were overlooked because they are not commonly used on the entity’s generators, which typically rely on fuses for protection of the excitation transformer. As described by the Engineering Leader, the excitation transformer and protective relay system were packaged as a unit and, to the best of his knowledge, were installed by a vendor. The only other similar relay is on Brownlee generating unit #5, which the Power Production engineers were aware of and included in the PSMP because it was installed by the entity. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Normal operations for Langley is 290MW. A fault cascade would be prevented by the following: A station battery low voltage relay would trip the generator(s) breakers before the DC voltage would drop to critical point, and the generation would be replaced by picking up the load with other resources or purchased power. The probability of this event is extremely low as the battery charger normally supplies the DC load. If the charger(s) failed, the load would be supplied by the station battery, and if the battery failed the load is normally supplied by the charger(s). The control and protection scheme would guarantee that generator breakers would clear the generator(s) in the event of a fault or if the generators are isolated from the load. A fault in the switchyard would isolate the generator from the lines by tripping all the transmission line breakers and/or generator breakers or isolate the affected portion of the switchyard bus. A fault on an individual transmission line would isolate the generators by tripping the individual transmission line breaker(s). In all scenarios, the generators would be protected and no other BPS elements would be impacted. Additionally, as required by PRC-005-1.1b R1, the entity’s Battery M&T Plan was developed, including maintenance and testing intervals and their basis, and implemented. Although the annual maintenance and testing requirements were not completed within 365 days required by the undefined implementation of the annual requirement included in the Battery M&T Plan, they were completed less than a month after the Asset Suite due date. Additionally, the missed deadline was identified by a control in place within the Power Production business unit and promptly reported to Regulatory Compliance and addressed by the business unit. No harm is known to have occurred. | To eliminate potential confusion between the interval defined in the Battery M&T Plan and the implementation of the interval within Power Production, Power Production updated the Battery M&T Plan to more precisely define the required intervals consistent with intervals and terms required by PRC-005-2.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2015015360 | PRC-005-1.1b | R1 | On September 1, 2015, IPCO submitted a self-log stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R1. On May 20, 2015, Regulatory Compliance was advised by a Power Production Engineering Leader and Principal Engineer that preparations for the upcoming WECC audit revealed one protective relay for the Twin Falls Power Plant generation unit #2 (Twin Fall Unit #2) excitation transformer was not included in the implementation of the Protection System Maintenance Plan (PSMP). Power Production was concerned at the time that other excitation transformers may have been missed. Then, on June 17, 2015, Power Production confirmed that Milner power Plant generation unit #1 (Milner Unit #1), which is the same vintage as Twin Falls Unit #2, has a similar excitation transformer with relay protection that was not included in the implementation of the PSMP. As a result, a total of two excitation transformers, one for each unit identified above, were not included in the implementation of the PSMP. According to the Principal Engineer, the relays are original to the plant (the Milner and Twin Falls excitation systems were actually manufactured in Sweden) and were overlooked because they are not commonly used on the entity’s generators, which typically rely on fuses for protection of the excitation transformer. As described by the engineering leader, the excitation transformer and protective relay system were packaged as a unit and, to the best of his knowledge, were installed by a vendor. The only other similar relay is on Brownlee generating unit #5, which the Power Production engineers were aware of and included in the PSMP because it was installed by the entity. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The two protective relays are applied on the excitation system transformers of Milner Unit #1 and Twin Falls Unit #2 respectively. Milner Unit #1 is rated at 49 MVA, while Twin Falls Unit #2 is rated at 46.8 MVA. These relays provide overcurrent protection for the excitation transformer on each respective generator. While these two relays are being discussed together, it is important to note that they are, in fact, located at different power plants and are operationally independent of one another—that is, the function of one has no impact on the function of the other. In the event the relays operate, they perform an emergency shutdown and trip their respective generator from the BPS. In the event a relay operates, only the single generator it is associated with would be lost. A failure or misoperation of one of the relays would not cause a cascading event for the following reasons: 1) Small size – Twin Falls Unit #2 and Milner Unit #1 are small generators and represent less than 1.5% of the entity’s generation nameplate capacity each. The amount of generation that could be lost from each unit is easily covered by the entity’s Contingency Reserve requirements. 2) Not used for generation regulation – Twin Falls Unit #2 and Milner Unit #1 are not used for generation regulation in the entity’s Balancing Area. 3) Limited operation – Twin Falls Unit #2 and Milner Unit #1 operate seasonally as “run of river” generation. Each unit may be online only 180 days per year and not at rated capacity. No harm is known to have occurred. | To mitigate this issue, IPCO: 1) added the relays to the implementation list for the PSMP; and 2) scheduled the relays to be tested by the end of 2015. The relays were added to the implementation list for the PSMP on or before July 8, 2015.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Balancing Authority of Northern California (BANC) | NCR11118 | WECC2015015362 | PER-005-1 | R3; R3.1 | On November 18, 2015, BANC submitted a Self-Report stating that, as a Balancing Authority (BA), it had a possible issue of noncompliance with PER-005-1 R3. BANC failed to provide a minimum of thirty-two hours of emergency operations training to one of its operators. During an internal review of System Operator training records, BANC discovered that one Power System Operator completed only twenty-nine hours of emergency operations training in 2014. The root cause of this issue was human error. This issue began on January 1, 2015, the day after 2014 training should have been completed, and ended March 26, 2015, when the operator completed an additional three hours of training. This is BANC's first violation of this requirement, was identified and reported timely, and posed minimal risk to the BPS. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, BANC failed to provide a minimum of thirty-two hours of emergency operations training to one of its operators. Such failure could result in the operator’s inability to perform all duties required during emergency operations. However, this issue was limited to one operator, three hours short of the requirement. Had inadequate training rendered the operator unable to perform during emergency operations, other operators in the control center would have compensated. The operator in question has over nine years of experience as an operator at BANC; and completed over two hundred EOP training hours over last five years, with an average of 41 hours of EOP training each year. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. BANC does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, BANC: 1) provided the operator three additional hours of training; and 2) implemented a process in which its training manager will provide monthly reports tracking training requirements to the Power Systems Operations Manager and other relevant staff. WECC verified that BANC completed mitigating activities on March 26, 2015.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Sacramento Municipal Utility District (SMUD) | NCR05368 | WECC2015015363 | PER-005-1 | R3; R3.1 | On November 18, 2015, SMUD submitted a Self-Report stating that, as a Transmission Operator, it had a possible issue of noncompliance with PER-005-1 R3. SMUD failed to provide a minimum of thirty-two hours of emergency operations training to one of its operators. During an internal review of System Operator training records, SMUD discovered that one Power System Operator completed only twenty-nine hours of emergency operations training in 2014. The root cause of this issue was human error. This issue began on January 1, 2015, the day after 2014 training should have been completed, and ended March 26, 2015, when the operator completed an additional three hours of training. This is SMUD's first violation of this requirement, was identified and reported timely, and posed minimal risk to the BPS. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, SMUD failed to provide a minimum of thirty-two hours of emergency operations training to one of its operators. Such failure could result in the operator’s inability to perform all duties required during emergency operations. However, this issue was limited to one operator, three hours short of the requirement. Had inadequate training rendered the operator unable to perform during emergency operations, other operators in the control center would have compensated. The operator in question has over nine years of experience as an operator at SMUD; and completed over two hundred EOP training hours over last five years, with an average of 41 hours of EOP training each year. Based on this information, and because no harm occurred, this issue posed minimal risk to the reliability of the Bulk Power System. SMUD does not have previous violations of this Standard and Requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, SMUD: 1) provided the operator three additional hours of training; and 2) implemented a process in which its training manager will provide monthly reports tracking training requirements to the Power Systems Operations Manager and other relevant staff. WECC verified that SMUD completed mitigating activities on March 26, 2015.
2015-12-30 | Florida Reliability Coordinating Council (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2015015294 | PRC-006-1 | R9 | During a Compliance Audit conducted from July 13, 2015 through October 14, 2015, FRCC determined that SEC, as a Distribution Provider (DP) and Load-Serving Entity (LSE), was in violation of PRC-006-1 R9 from October 1, 2013 to the present. SEC audit documentation was not sufficient evidence to demonstrate that SEC provided automatic tripping of load in accordance with the underfrequency load shedding (UFLS) program design and schedule for application determined by its Planning Coordinator(s) (PC) in each Planning Coordinator area in which it owns assets. When FRCC auditors reviewed SEC relay test records, of the twenty-nine (29) relay samples taken, thirteen (13) had a total time delay greater than 0.28 seconds as tested. The root cause for this violation was the failure of SEC to recognize the relays were set in a way that when calculated correctly, the individual time delays (where the total time delay = intentional delay + relay delay + breaker delay) would exceed the required total time delay limits set by the PC of 0.1-0.28 seconds. The person performing the testing of the relays was not taking into account the breaker time delays, which, when accounted for as required by the additive equation, increased the total time delay to over the required 0.28 secs limit and would exceed the limits set by the PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a minimal risk because the largest UFLS time delay discrepancy for SEC's UFLS relays was 0.03 seconds. Had a UFLS event occurred, approximately 55% of SEC's UFLS relays would have shed load within the 0.1 to 0.28 second time delay requirement, while the remaining 45% would have shed load up to 0.03 seconds slower than required. No harm is known to have occurred. FRCC considered SEC’s compliance history above and determined that the instant issue was SEC's first instance of noncompliance with PRC-006-1 R9. | To mitigate this issue, SEC will complete the following mitigation activities by November 1, 2016: 1) update and streamline UFLS test documents for use by SEC and SEC members' field staff to reflect the updated UFLS settings requirements; hold workshop with members on updated documents; 2) provide examples of the new test documents to applicable SEC and SEC members' field staff and conduct training on the new requirements in a member workshop; 3) re-test all audit-sampled UFLS relays whose total time delay exceeded the time delay for the applicable UFLS step; adjust settings as necessary; if adjustments are made, retest modified settings to demonstrate that the time delay is within the range of the applicable UFLS step; 4) evaluate all remaining in-service UFLS relay settings that were not sampled as part of the audit; determine whether their documentation demonstrates that the applicable time delays are within the range of the applicable UFLS step; and 5) for UFLS relays identified in milestone #4, retest relays if the settings or documentation do not clearly demonstrate that the time delay is within the range of the applicable UFLS step; if necessary, adjust settings; use contractors as needed; coordinate feeder outages with SEC members to enable testing and adjustment. SEC is an electric cooperative with 9 member companies. Training to both SEC and SEC members is required to align the changes decribed above, and explains the lengthier timeline to mitigation completion.
2015-12-30 | Florida Reliability Coordinating Council (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC2015015293 | PRC-008-0 | R2 | During a Compliance Audit conducted from July 13, 2015 through October 14, 2015, FRCC determined that SEC, as a Distribution Provider (DP), was in violation of PRC-008-0 R2 from May 7, 2009 to the present. SEC documents were insufficient evidence to demonstrate that SEC implemented its own underfrequency load shedding (UFLS) equipment maintenance and testing program correctly. Specifically, SEC, when implementing its practice titled "Underfrequency Load Shedding Equipment Maintenance Programs" (dated October 1, 2013) did not “adjust components as needed, to operate within required parameters” in accordance with the FRCC UFLS program as stated in Section 1.0 of its practice. The FRCC UFLS total time delay range required is 0.1-0.28 seconds (where the total time delay = intentional delay + relay delay + breaker delay) for relay steps 1-7 (fka A-F). When FRCC auditors reviewed SEC relay test records, of the twenty-nine (29) relay samples taken, thirteen (13) had a total time delay greater than 0.28 seconds as tested. There was no evidence that adjustments or calibrations were then performed to bring the total time delay back within the required 0.1-0.28 seconds total time delay. The root cause for this violation was the failure of SEC to recognize the relays were set in a way that when calculated correctly, the individual time delays (where the total time delay = intentional delay + relay delay + breaker delay) would exceed the required total time delay limits set by the PC of 0.1-0.28 seconds. The person performing the testing of the relays was not taking into account the breaker time delays, which, when accounted for as required by the additive equation, increased the total time delay to over the required 0.28 seconds limit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk to the bulk power system was minimal since the largest UFLS time delay discrepancy for SEC's UFLS relays was 0.03 seconds. Had a UFLS event occurred, approximately 55% of SEC's UFLS relays would have shed load within the 0.1 to 0.28 second time delay requirement, while the remaining 45% would have shed load up to 0.03 seconds slower than required. No harm is known to have occurred. FRCC considered SEC’s compliance history above and determined that the instant issue was SEC's first instance of noncompliance with PRC-008-0 R2. | To mitigate this issue, SEC will complete the following mitigation activities by November 1, 2016: 1) update and streamline UFLS test documents for use by SEC and SEC members' field staff to reflect the updated UFLS settings requirements; hold workshop with members on updated documents; 2) provide examples of the new test documents to applicable SEC and SEC members' field staff and conduct training on the new requirements in a member workshop; 3) re-test all audit-sampled UFLS relays whose total time delay exceeded the time delay for the applicable UFLS step; adjust settings as necessary; if adjustments are made, retest modified settings to demonstrate that the time delay is within the range of the applicable UFLS step; 4) evaluate all remaining in-service UFLS relay settings that were not sampled as part of the audit; determine whether their documentation demonstrates that the applicable time delays are within the range of the applicable UFLS step; and 5) for UFLS relays identified in milestone #4, retest relays if the settings or documentation do not clearly demonstrate that the time delay is within the range of the applicable UFLS step; if necessary, adjust settings; use contractors as needed; coordinate feeder outages with SEC members to enable testing and adjustment. SEC is an electric cooperative with 9 member companies. Training to both SEC and SEC members is required to align the changes decribed above, and explains the lengthier timeline to mitigation completion.
2015-12-30 | Northeast Power Coordinating Council (NPCC) | GenConn Middletown LLC | NCR11111 | NPCC2015015284 | TOP-002-2.1b | R14 | On September 11, 2015, GenConn Middletown LLC submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue of TOP-002-2.1b R14. In 2015, temporary deratings affected the operating capacity of the GenConn Middletown Units #14 and #15, whose Dependable Maximum Net Capacity (DMNC) values are 46.9 MW each. The 2015 Claimed Capability Auditing (CCA) testing showed that generating Unit #14 underperformed by 0.956 MW from July 11, 2015 to August 7, 2015, while generating Unit #15 underperformed by 1.056 MW from July 11, 2015 to August 4, 2015. The entity did not report the aforementioned changes in real output capacity to its Balancing Authority (BA) or Transmission Operator (TOP) (ISO-NE). GenConn Middletown LLC reported the issue to the ISO-NE on August 21, 2015, over a month later. The root cause of the issue was that the derates, although having been logged into the Generating Availability Data System (GADS) system, were not entered into the GenConn Middletown shift supervisor log books. Consequently, successive shift supervisors were not informed of the derates, thus hindering a timely report of the temporary capacity changes to ISO-NE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The combined DMNC value of the two generating units is 93.8 MW and the total reduction in their operating capacity, in the period July 11, 2015 to August 7, 2015, was approximately 2 MW, or 2% of their combined DMNC. This temporary loss in operating capacity was restored in less than a month. These two combustion turbine units are peaking units, as demonstrated by the fact that they were operated at a capacity factor of less than 1.3% in the 2015 summer period, according to dispatch records. Moreover, ISO-NE carries a required Operating Reserve of approximately 2500 MW, and has historically exceeded that requirement by a significant margin (ranging from a few hundred to more than two thousand MWs). Therefore, the entity's lack of timely reporting to its BA/TOP for its two GenConn Middletown units represents a minimal impact on the reliability of the BPS system because ISO-NE could have replaced the lost capacity, if needed. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered GenConn Middletown LLC's compliance history and determined there are no relevant instances of noncompliance. | To mitigate this issue, GenConn Middletown LLC: 1) formally notified ISO-NE of its capacity reporting incident on August 21, 2015; and 2) implemented a new procedure titled "Middletown Power LLC - CCA/SCC Review Policy" that provides a method for ensuring that all pertinent personnel (e.g. operations managers, shift supervisors) are concurrently made aware of the current CCA or Seasonal CCA test. This higher level of awareness ensures that the test data is entered into log books in a timely fashion, enabling the Entity to comply fully with TOP-002-2.1b R14. NPCC has verified the completion of all mitigation activity.
2015-12-30 | Northeast Power Coordinating Council (NPCC) | Middletown Power LLC | NCR07141 | NPCC2015015399 | TOP-002-2.1b | R14 | During an Off-Site Audit conducted from June 1, 2015 to September 11, 2015, NPCC determined that Middletown Power LLC, as a Generator Operator (GOP), had an issue related to TOP-002-2.1b R14. In 2015, a temporary derating affected the operating capacity of the Middletown Unit #10, whose Dependable Maximum Net Capacity (DMNC) value is 15.7 MW. The 2015 Claimed Capability Auditing (CCA) testing showed that generating Unit #10 underperformed by 0.956 MW from July 11, 2015 to August 12, 2015. The entity did not report the aforementioned changes in real output capacity to its Balancing Authority (BA) or Transmission Operator (TOP) (ISO-NE). The entity eventually reported the issue to ISO-NE on August 21, 2015, over a month later. The root cause of the issue was that the derate, although having been logged into the Generating Availability Data System (GADS) system, was not entered into the Middletown shift supervisor log books. Consequently, successive shift supervisors were not informed of the derate, thus hindering a timely report of the temporary capacity change to ISO-NE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The DMNC value of the Middletown generating unit #10 is 15.7 MW, and the total reduction in its operating capacity, in the period July 11, 2015 to August 12, 2015, was less than 1 MW, or 6% of its DMNC. This temporary loss in operating capacity was restored in approximately a month time. This combustion turbine unit is a peaking unit, as demonstrated by the fact that it was operated at a capacity factor of less than 0.6% in the summer 2015 period, according to dispatch records provided by the entity. Moreover, ISO-NE carries a required Operating Reserve of approximately 2500 MW, and has historically exceeded that requirement by a significant margin (ranging from a few hundred to more than two thousand MWs). Therefore, the entity's lack of timely reporting to its BA/TOP for its Middletown unit #10 represents a minimal impact on the reliability of the BPS system because ISO-NE could have easily replaced the lost capacity, if needed. No harm is known to have occurred as a result of this issue of non-compliance. NPCC considered Middletown Power LLC's compliance history and determined there are no relevant instances of noncompliance. | To mitigate this issue, Middletown Power LLC: 1) formally notified ISO-NE of its capacity reporting incident on August 21, 2015; and 2) implemented a new procedure titled "Middletown Power LLC - CCA/SCC Review Policy" that provides a method for ensuring that all pertinent personnel (e.g. operations managers, shift supervisors) are concurrently made aware of the current CCA or Seasonal CCA test. This higher level of awareness ensures that the test data is entered into log books in a timely fashion, enabling the Entity to comply fully with TOP-002-2.1b R14. NPCC has verified the completion of all mitigation activity.
2015-12-30 | Northeast Power Coordinating Council (NPCC) | Consolidated Edison Co of NY, Inc (ConEd) | NCR07046 | NPCC2015015326 | IRO-010-1a | R3 | On October 7, 2015, ConEd submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of IRO-010-1a, R3. ConEd failed to provide its Reliability Coordinator (RC), which is the New York Independent System Operator (NYISO), with modeling data for a replacement part within the time period required by the NYISO's specifications. Specifically, ConEd identified that a 345 kV Phase Angle Regulator (PAR) had been replaced with an in-kind spare in February 2012 due to a failure, with an in-service date of February 6, 2012, however the modeling data for the replacement PAR was not provided to the NYISO at the time. The NYISO's specifications require that modeling data for new equipment be provided at least 60 days in advance of the in-service date. The modeling data for the replacement PAR was provided to the NYISO in October 2015, failing to meet the NYISO's reporting requirements for modeling data. The duration of the violation was from December 9, 2011 (59 days prior to the in-service date as NYISO requires data 60 days in advance) to October 7, 2015. The root cause of the violation was failure to establish a robust internal communication process regarding the transformer impedance data. The PAR being an in-kind replacement, rather than an addition to the Bulk Electric System (BES), was a contributing factor. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were no thermal or voltage impacts on the system caused by the replacement PAR. There was a slight difference in impedance between the old PAR and the replacement PAR, however the replacement PAR did not have any effect on any of the ConEd system operating limits, and the NYISO did not have any issues caused by the differences in the values reported. The issue was detected by ConEd during an internal audit, during which the Transmission Planning engineers reviewed all elements replaced since 2010 to ensure they were properly reported to the NYISO. NPCC considered ConEd's compliance history and determined that there were no relevant instances of noncompliance related to IRO-010-1a R3. | To mitigate this issue, ConEd: 1) created a new position of Manager of Asset Management; and 2) will revise their COP 5-0-23 (implemented in 2011 to facilitate compliance with IRO-010-1a) to change the reporting obligation for new or replacement equipment from Project Engineers to the newly created Manager of Asset Management. This revision has an expected completion date of December 31, 2015.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Southern Maryland Electric Cooperative, Inc. (SMECO) | NCR00918 | RFC2015014863 | NUC-001-2.1 | R4 | On April 10, 2015, SMECO submitted a Self-Report stating that, as a Distribution Provider, it had an issue of NUC-001-2.1 R4. On March 17, 2015, at 5:26 p.m., SMECO’s Supervisory Control and Data Acquisition (SCADA) system became inoperable. The SMECO operator immediately consulted with the appropriate SMECO information technology specialist and restored SCADA data delivery to Calvert Cliffs Nuclear Power Plant, LLC (CCNPP) by successfully switching over to the back-up server at 6:42 p.m., 76 minutes later. However, pursuant to SMECO’s letter agreement with CCNPP, SMECO was required to notify CCNPP that its SCADA system had become unavailable within 60 minutes of the occurrence. The root cause of this noncompliance was human error. Specifically, the SMECO operator was focused on restoring the SCADA system and failed to follow the company’s documented procedure that required the operator to notify CCNPP within 60 minutes. More broadly, this root cause relates to the management practice area of workforce management, which ensures the ongoing suitability and competence of personnel to minimize the frequency and consequences of events related to Bulk Electric System reliability and resilience. The duration of this noncompliance is from 5:26 p.m., March 17, 2015, the date and time that SMECO’s SCADA system became unavailable, to 6:42 p.m., March 17, 2015, 76 minutes later, when SMECO successfully switched over to the back-up server, and SCADA data on its delivery point to CCNPP was restored. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, SMECO’s loss of its SCADA system did not affect its ability to provide the requisite 13.8 kV distribution level offsite power source for CCNPP. Second, SMECO’s 13.8 kV distribution level offsite power source is not needed for CCNPP’s normal operations. In fact, CCNPP confirmed that, during the 76 minutes that SMECO’s SCADA system was down, the preferred 500 kV offsite power sources were available. No harm is known to have occurred. This is SMECO's first instance of noncompliance with NUC-001-2.1 R4. | To mitigate this issue, SMECO: 1) completed an internal investigation to identify the cause of the noncompliance; 2) provided additional training to all system operations personnel with regard to required notifications to CCNPP; 3) developed a new “quick reference guide” spreadsheet that was placed on desktops of all operations personnel that provides specific scenarios which require notifications, with reference to corresponding detailed procedures; and 4) reinforced its pre-shift turnover process to remind operators of all notifications that could be necessary during the upcoming shift.
2015-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | PECO Energy Company (PECO) | NCR08026 | RFC2015014974 | NUC-001-2 | R6 | On June 5, 2015, PECO submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue of NUC-001-2 R6. On May 7, 2015, while providing training to field personnel responsible for battery inspections, PECO learned that the quarterly battery inspections at Limerick Generating Stations (Limerick) interconnected substations were not being performed in accordance with the agreements between Exelon Generation Company, LLC (Exelon) and PECO implementing the Nuclear Plant Interface Requirements (NPIR) for Limerick Generating Station Units 1 and 2. Under the NPIRs, PECO is the owner and service provider for the substation batteries. At the Limerick substation, the NPIRs require quarterly testing of all cells for voltage and specific gravity. Limerick is the only PECO substation subject to the NPIR that requires a quarterly test recording voltage and specific gravity of each cell and overall battery voltage. At Limerick, PECO was testing 100% of cells for voltage, but incorrectly testing only 10% of cells for specific gravity quarterly. The standard practice for battery testing under PECO’s overall program for battery maintenance that applies to all other PECO substations is to quarterly test only 10% of cells for specific gravity. Due to an unclear field procedure, PECO personnel responsible for battery testing at Limerick did not understand the distinction that 100% of cells should be tested for specific gravity quarterly at Limerick. The noncompliance consisted of Limerick not testing 100% of cells for specific gravity on a quarterly basis for almost a five-year period. This noncompliance concerned the management practices of workforce management and asset and configuration management. Workforce management was involved because personnel were not aware of the unique requirements for quarterly battery cell testing at Limerick, which demonstrates a lack of effective training. Asset and configuration management was involved because PECO’s field procedure that describes how testing is to be performed is not sufficiently clear on the enhanced testing requirements at Limerick. The duration of this noncompliance is from April 1, 2010, the date PECO was required to comply with NUC-001-2 R6, to May 11, 2015, the date PECO completed testing 100% of the cells at Limerick for specific gravity. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although PECO was not performing quarterly testing on 100% of all cells for specific gravity as required, PECO was performing other battery tests that are indicators of battery cell performance. For example, PECO was testing 10% of all cells for specific gravity quarterly and 100% of all cells for voltage quarterly, PECO performs a complete voltage and specific gravity test of each cell annually, and PECO measures and records the battery float current at Limerick to verify the state of charge for the battery string every five weeks. If any of these tests do not go as expected at any time, this would be an indication for PECO to conduct a deeper investigation into the performance of the battery cell at issue. No harm is known to have occurred. This is PECO's first instance of noncompliance with NUC-001-2 R6. | To mitigate this issue, PECO: 1) communicated the enhanced testing requirements to the personnel who perform station inspections; 2) revised its field testing procedure for quarterly battery testing to include the enhanced testing requirements at Limerick and to provide training on the revised procedure; and 3) added enhanced battery testing requirements at Limerick in its Cascade system. Also, PECO will require a check or sign-off in the inspection form to acknowledge completion of inspection on 100% of the cells for specific gravity. ReliabilityFirst has verified the completion of all mitigation activity.
2015-12-30 | SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, LSE, TO) (VEP-Trans) | NCR01214 | SERC2015015037 | PRC-005-1.1b | R2 | On June 23, 2015, VEP-Trans submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-005-1.1b R2. VEP-Trans tested a single station DC supply device outside of the defined quarterly interval. As part of the mitigating actions for a prior PRC-005-1 R2 noncompliance, VEP-Trans added third-party-owned voltage and current sensing devices and station DC supply devices at 12 delivery points to its Protection System maintenance and testing program. Although VEP-Trans did not own these voltage and current sensing devices and station DC supply elements, they provide power or data to VEP-Trans’ associated communications equipment and thus have the ability to impact lines owned by VEP-Trans. VEP-Trans created oversight work orders in the VEP-Trans work management program, to track when maintenance and testing was due by the third-party owners of the equipment. While setting up these new work orders, VEP-Trans made a data entry error, which created a discrepancy between the defined maintenance and testing interval and the compliance interval in the work management program. VEP-Trans entered a three-month plan period and a 60-day grace period, totaling a five-month interval equal to 150 days. VEP-Trans should have entered a three-month plan period and a 30-day grace period, totaling a four-month interval equal to 120 days. This error resulted in the third-party owner conducting impedance testing for one station DC supply device eight days after it should have been tested based on the defined interval. VEP-Trans verified it set up the work management program for all other delivery points correctly and tested all other third-party-owned delivery point Protection System devices within the defined interval. VEP-Trans identified this issue in preparation for data gathering from the third-party Protection System owners for the next maintenance and testing interval reporting. SERC determined that VEP-Trans had an issue with PRC-005-1.1b R2.1 because VEP-Trans could not provide evidence that one of 8,532 (0.012%) Protection System devices was tested and maintained within the defined interval. This issue lasted from January 9, 2015, the day after the Protection System devices should have been tested, through January 15, 2015, when the third-party owner tested the Protection System device. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. VEP-Trans’ failure to ensure that the third-party owner tested a single station DC supply device within the defined interval could cause VEP-Trans’ associated communications devices to not operate as expected, potentially resulting in line outages. However, any resulting line outage would likely be limited to the networked transmission line from which the delivery point was tapped. The third-party owner installed the battery at issue on May 17, 2013, and tested it on a regular basis. In addition, loss of a signal to the VEP-Trans associated communication device would have activated an alarm in the system operations center, and VEP-Trans would have dispatched personnel to investigate. During the issue, VEP-Trans experienced no outages on its networked transmission system attributed to the station DC supply element at issue. No harm is known to have occurred. SERC considered VEP-Trans’ PRC-005 R2 compliance history in determining the disposition track. VEP-Trans’ relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID SERC2012011323. SERC determined that VEP-Trans' compliance history should not serve as a basis for applying a penalty. The prior noncompliance involved a failure by VEP-Trans to document the maintenance and testing of Protection System devices owned by third-party wholesale and industrial customers of VEP-Trans that had the ability to impact VEP-Trans-owned Protection System devices. The instant issue is a result of human error while entering a quarterly testing interval for a single Protection System device, owned by one of the customers that was part of the prior noncompliance, into the VEP-Trans Protection System database, which resulted in an eight-day delay in conducting the required testing. The prior mitigation plan activities would not have prevented this issue. | To mitigate this issue, VEP-Trans: 1) updated the work management system to reflect the correct intervals as stated in its Protection System maintenance and testing program; 2) reviewed all plan period and grace period intervals, for all 12 Distribution Provider locations listed in its Protection System maintenance and testing program, to ensure no other discrepancies existed that could create a noncompliance; and 3) created an exception report to look for errors in both the plan period and grace period to serve as a control to find errors in the work orders for these locations. An error will send an automatic email alert to the compliance team to advise them of the error so it can be corrected. SERC has verified the completion of all mitigation activity.
2015-12-30 | SERC Reliability Corporation (SERC) | East Kentucky Power Cooperative (EKPC) | NCR01225 | SERC2015014741 | FAC-008-3 | R6 | On February 27, 2015, EKPC submitted a Self-Certification stating that, as a Generator Owner (GO), it had an issue with FAC-008-3 R6. EKPC failed to have a Facility Rating at one of its Facilities that was consistent with the associated Facility Ratings methodology. EKPC discovered this issue in 2015 during its annual model-building process, which included reviewing rating changes that occurred since the last model build. EKPC's Transmission Owner (TO) function was responsible for the methodology for rating generator step-up (GSU) transformers. EKPC's GO function considered the ratings of the GSU transformers along with all other equipment in series to determine the limiting ratings for a generating facility. On November 21, 2013, a cooling pump on the GSU transformer for H.L. Spurlock Unit #1 failed, causing EKPC TO to de-rate the MVA rating of the GSU transformer. After the cooling pump failure, EKPC determined that the rating of the GSU transformer should change from 375 MVA to 300 MVA, making the GSU transformer the limiting element for the overall rating of the Spurlock Unit #1 generating facility. Prior to the de-rate on November 21, 2013, the least-rated element was the generator, at 312 MVA. EKPC TO applied the GSU transformer de-rate in its Facility Ratings database and in its energy management system (EMS), and submitted the change to PJM Interconnection, LLC (PJM). However, EKPC TO failed to communicate the change to the EKPC GO’s subject matter expert (SME) responsible for developing Facility Ratings for generating facilities. Therefore, EKPC GO maintained a higher Facility Rating (312 MVA) for the Spurlock Unit #1 generating facility than was appropriate pursuant to the Facility Rating methodology (300 MVA). This discrepancy continued until February 10, 2015, when EKPC TO notified EKPC GO that the de-rate was no longer in effect. At that time, EKPC GO realized that it had not been notified of the de-rate and therefore had not updated its Facility Ratings database to incorporate this change. EKPC identified the lack of a detailed procedure for communicating changes in ratings for transmission and generation facilities as a significant contributing factor to this issue. The communication section of EKPC’s most-recent Facility Ratings methodology, effective September 2, 2014 (after the de-rate at issue occurred), states that updated Facility Ratings shall be calculated and provided in a timely manner by EKPC to all internal EKPC departments and external entities requiring those ratings. EKPC also identified a lack of clarity regarding roles and responsibilities as another contributing factor to this issue. The EKPC power delivery maintenance staff communicated the de-rate to the EKPC power delivery operations staff, which ensured that EKPC TO implemented the correct rating in its transmission Facility Ratings database and that EKPC communicated the correct rating to PJM. However, EKPC did not identify who should communicate the de-rate to the EKPC SME responsible for maintaining the Facility Ratings for generating facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). EKPC’s failure to update the Facility Rating after the cooling pump failed resulted in the continued use of a higher Facility Rating than should have been used pursuant to its Facility Rating methodology, which could have led the Generator Operator to operate the generating unit above the maximum capability of the GSU transformer, potentially damaging it. If the transformer failed, it would have taken the Spurlock Unit #1 completely off-line. However, EKPC established the 300 MVA limit on the generating facility as an alarm point in the EKPC EMS and submitted the limit to PJM after the cooling pump failed. Therefore, the EKPC energy control center and the PJM Reliability Coordinator and Transmission Operator had the correct limits monitored to ensure the unit output stayed within the proper limits during this issue. In addition, the day after the cooling pump failed, EKPC issued an ambient temperature chart to Spurlock Station that provided updated ratings for the GSU transformer based on the loss of the cooling pump and the ambient temperature, reducing the risk that Spurlock Station would operate outside of the proper limits. Thus, EKPC’s failure to update the GO Facility Ratings database by documenting the Facility Ratings change had a limited impact, if any, on actual operations. In addition, because the unit at issue was not identified as critical to the operation of the BPS, the likelihood was low that an unplanned outage would have resulted in any significant reliability consequences. No harm is known to have occurred. SERC considered EKPC’s compliance history in determining the disposition track. EKPC’s relevant prior noncompliance with FAC-009-1 R1 (now FAC-008-3 R6) includes: NERC Violation ID SERC2012009883. SERC determined that EKPC's compliance history should not serve as a basis for applying a penalty. The prior violation resulted from incorrect database and ratings calculations, while the root cause of the instant issue was a communications failure. EKPC’s mitigating actions for the prior violation corrected the power factors used to determine Facility Ratings and corrected the calculation error, but would not have prevented the communications failure involved in the instant issue. | To mitigate this issue, EKPC: 1) developed a formal procedure that defines roles and responsibilities, educated all involved personnel on that procedure, and implemented the procedure and monitored it to ensure that it is being utilized adequately; and 2) established adequate communication channels to ensure that information is flowing as necessary in order to rate equipment as specified in EKPC Facility Ratings Methodologies.
2015-12-30 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2015014868 | PRC-005-1.1b | R2 | On March 3, 2015, Duke Energy Corporation (DECorp) submitted a Self-Report to Reliability First (RF) stating that, as a Transmission Owner (TO), it was in violation of PRC-005-1.1b R2. DECorp reported that it had not tested a device with its assigned interval. On April 10, 2015, as part of the Coordinated Oversight program, RF transferred the reported violation to SERC as the identified Lead Regional Entity for Duke Energy affiliates. This issue is being processed under Duke in accordance with the agreement under the Coordinated Oversight program. On January 30, 2015, while performing device testing, DECorp maintenance and testing staff noticed that a device that was to receive annual maintenance and testing was tested in 2012 but not in 2013. In 2011, DECorp replaced the relays and carrier sets on the 138 kV circuit between the Charles and Rochelle substations. Both the primary and backup systems were installed and tested in 2011, and at that time, DECorp miscategorized the primary scheme as using direct fiber like the backup system, which would mean that annual testing was not required. DECorp attributes the miscategorization to human error. Despite the miscategorization, DECorp tested both systems in 2012. However, because of the miscategorization, DECorp did not generate a work request for testing in 2013. In 2014, technicians tested the primary scheme while they were on site investigating monitoring attributes of communication systems in preparation for PRC-005-2 implementation. The device remained categorized incorrectly because the work order does not address the category. It only addresses the work to be performed. DECorp identified this incorrect categorization while its technicians were performing Self-Certification reviews for 2015. DECorp transmission department initiated a review of all carrier relay test records and compared them with devices installed on each circuit to determine if other systems had been mischaracterized. The review identified one more discrepancy of a different nature. In 2006, DECorp installed a direct trip carrier set at the Todhunter and Trenton substations. DECorp tested and commissioned the set but never put it into the maintenance system for annual testing. While verifying that paper test records were available for each equipment test date, DECorp maintenance and testing staff noticed that they had a paper record for the test for Todhunter-Trenton carrier test for 2014, but the equipment was not in the Maximo work order system. In 2014, while doing related site maintenance activities, the technicians tested the carrier set devices and logged that test. The device was not in the substation work order but it was tested because the technicians were on site investigating monitoring attributes of all communication systems in preparation for PRC-005-2 implementation. This equipment should have been tested annually from 2007 through 2013 as prescribed in the DECorp protection system maintenance and testing program but had not been included in Maximo following commissioning. The review validated that all other carrier sets in the Protection System Maintenance Plan were accounted for and had been tested according to test plans. In addition to the above, SERC initiated a request for DECorp to provide a list of all Protection System devices and the latest test and previous test date per the DECorp program requirements. While gathering data to fulfill that request, DECop identified the following discrepancies: 1) The annual battery testing data for two batteries at Gallagher Station for 2013 and 2014 was stored on their MeggerBite 2 test device. When attempting to download the data, the program locked up, resulting in the data being corrupted. Multiple attempts were made to recover the data but with no success. Maximo completed work orders show that maintenance was performed every month in 2014. 2) Cayuga Station could not locate any records of battery maintenance being performed in 2014 for one battery at Cayuga Unit 2. The last reported annual maintenance was performed on December 12, 2013. SERC reviewed a survey of maintenance and testing records and determined that DECorp failed to provide evidence of testing and maintenance for two of 552 (0.36%) associated communication devices and three of 250 (1.2 %) batteries/chargers. In total, five of over 9,000 Protection System devices lacked evidence of maintenance and testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DECorp’s failure to complete maintenance and testing according to the defined interval could result in Protection System misoperations endangering equipment, personal safety, and reliability. However, in this case the issue affects a very small percentage of DECorp's devices at locations remote from each other. In the original violation, the missed testing date for device is question was in 2013, but DECorp tested the device in 2014 and it was functioning as expected. Also, the primary system does alarm for relay failure. Further, DECorp installed the redundant backup protection relays using direct fiber communication to continuously verify its integrity. Similarly, the Todhunter-Trenton carrier set functioned normally throughout the period. The low risk associated with missing annual testing is also indicated by attributing a six-year test cycle to devices of this type when implementing PRC-005-2. DECorp tested the batteries at Gallagher, however DECorp could not retrieve and archive the data. The DECorp PSMP requires only annual testing, however individual stations could be more conservative and provide more frequent services. Records for more frequent testing are available for Gallagher but not for Cayuga. Both Gallagher and Cayuga utilize alarms to alert operators to abnormal battery conditions. When DECorp performed battery testing, the results were satisfactory. No events related to battery performance were reported. DECorp’s current practices at all fossil generation stations include weekly and monthly, as well as annual testing and maintenance. No harm is known to have occurred. SERC considered DECorp’s PRC-005 R2 compliance history in determining the disposition track. DECorp’s relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID RFC2011001122 and RFC201000665. SERC considered DECorp’s compliance history and determined that the instant issue was appropriate for compliance exception treatment because the instant issue concerns the miscategorization of a single communication system rather than failing to test protective relays as is the case in the previous violations. The causes of missing battery test records are substantially different than those in prior issues. Mitigation activities for each of the previous violations would not have addressed the instant issue, and the risk imposed onto the BPS is sufficiently minimal to warrant treatment as a compliance exception. Therefore, SERC staff did not consider the previous violations as aggravating circumstances. Duke Energy Florida (DEF) SERC considered DEF’s PRC-005 R2 compliance history in determining the disposition track. DEF’s relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID FRCC2013012446. SERC determined that DEF compliance history should not serve as a basis for applying a penalty. DEF’s prior violation involved failure to perform maintenance on one pair of relays that had been listed in the database as distribution relays. The instant violation is ofa different nature and the mitigation plan did not address the instant issue. Duke Energy Progress (DEP) SERC considered DEP’s PRC-005 R2 compliance history in determining the disposition track. DEP’s relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID SERC2011006760. SERC determined that DEP’s compliance history should not serve as a basis for applying a penalty. The DEP violation resulted from missing documentation of the previous maintenance and testing for 111 devices of different types. The instant violation is of different nature and the mitigation plan did not address the instant issue. Duke Energy Carolinas (Duke) SERC considered Duke’s PRC-005 R2 compliance history in determining the disposition track. Duke’s relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID SERC201000544. SERC determined that DEC’s compliance history should not serve as a basis for applying a penalty. In SERC201000544 approximately 1.9% of its devices had not been tested within the defined interval. The instant violation is of different nature and the mitigation plan did not address the instant issue. SERC reviewed the posted violations of PRC-005 for affiliates Duke Energy Carolinas, Duke Energy Progress, and Duke Energy Florida and did not identify circumstances similar to that of the instant issue. Each Duke Energy affiliate is responsible for its own maintenance and testing program and the completed mitigation plans would not have addressed the instant issue. Therefore, SERC staff did not consider the previous violations by affiliates or the presence of a common programmatic failure as aggravating circumstances. | To mitigate this issue, DECorp: 1) tested the devices in question; 2) verified that the miscategorization of the device was corrected in both the work management tool and in the primary system that contains assets and their categories; and 3) conducted an internal meeting with Protection and Controls, Relay, and Equipment Engineering personnel to review the application of this particular and any future carrier sets.
2015-12-30 | SERC Reliability Corporation (SERC) | LG&E & KU Services Company as agent for Louisville Gas and Electric and Kentucky (LG&E & KU) | NCR01223 | SERC2015014780 | VAR-002-3 | R2 | On January 13, 2015, SERC sent LG&E and KU an audit detail notice of a Compliance Audit scheduled for April 13, 2015 through May 1, 2015. On March 26, 2015, LG&E and KU submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-3 R2. LG&E and KU failed to maintain the generator voltage schedule at one generating station on November 21, 2014. Effective October 1, 2014, the Transmission Operator (TOP), which is also LG&E and KU, modified Green River Generating Station’s 138 kV transmission bus voltage schedule, with a target of 141 kV and a tolerance band of 139 kV to 143 kV. LG&E and KU’s established metric for adhering to the voltage schedule was based on an integrated hourly average of the voltage during a clock hour. On November 21, 2014, the integrated hourly average of the voltage for the clock-hours ending at 7:00 a.m. through 11:00 a.m. was below the tolerance band. At the lowest hour, the bus voltage was 136 kV. The Green River Unit 3 operator was distracted from fully following proper procedure by difficulty in bringing the unit back online and by a shift change that occurred from 6:30 a.m. to 7:00 a.m. The TOP did not exempt the unit through its voltage and reactive schedule. LG&E and KU identified this issue during its internal GOP VAR-002 monthly audit. During the internal VAR-002 monthly audits, LG&E and KU reviewed the previous month’s integrated hourly average voltages for each bus and the units associated with each bus in order to detect any instances where a unit did not adhere to the voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. LG&E and KU’s failure to maintain the voltage schedule on the 138 kV Green River bus could, in certain circumstances, cause real-time and post contingent System Operating Limit (SOL) issues. However, had an SOL issue occurred, the TOP would have been prepared to take actions to correct the issue. LG&E and KU conducted a study that modeled the conditions for the period in question and performed an N-1 contingency analysis. LG&E and KU determined no thermal or voltage violations occurred due to this issue. LG&E and KU did not receive reports of system disturbances during the issue. In addition, Green River is a 161 MW coal facility in a fleet of 7,900 MW of generation (approximately 2% of LG&E and KU’s total generation). No harm is known to have occurred. SERC considered LG&E and KU’s VAR-002 R2 compliance history in determining the disposition track. LG&E and KU’s relevant prior noncompliance with VAR-002 R2 includes: SERC2012011080. SERC determined that LG&E and KU’s compliance history should not serve as a basis for applying a penalty. The prior violation in SERC2012011080 occurred for approximately one hour more than two years before the instant issue occurred, and was caused in part by a communication failure between the station and the LG&E and KU energy management system, disrupting LG&E and KU’s ability to monitor the voltage. The instant issue was caused by an operator’s human error in not following procedures during start-up of a generating unit. In addition, the mitigation activities for the prior violation would not have prevented the instant issue. The length of time between the prior violation and the instant issue suggests that this was an isolated failure and not an ongoing or significant compliance failure. In addition, as part of the mitigating activities for the instant issue, LG&E and KU tested and installed an alarm on the unit at issue that alerts operators to place the unit in “Cascade” mode when bringing the unit back online, which would have prevented the instant issue. | To mitigate this issue, LG&E and KU installed and tested an alarm on Green River Unit 3 to alert the Unit Operator that the Generator Reactive Capability is to be placed in “Cascade” mode once the Unit has been above 5 MW for 5 minutes.
2015-12-30 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2015015010 | PRC-005-1.1b | R2 | On June 19, 2015, DEP submitted a Self-Report stating that, as Transmission Owner (TO), it had an issue with PRC-005-1.1b R2. On April 15, 2015, during a routine review of the battery maintenance data sheets for the first quarter of 2015, DEP identified that at the Smith Energy Complex (SEC) Unit 3, the battery record did not have the electrolyte temperature recorded for 10% of the cells as required by its procedure. DEP had completed all of the other required maintenance and testing, including the specific gravity measurements. DEP conducted a review of the quarterly battery maintenance records for 2014 at SEC and eight additional quarterly data sheets were missing electrolyte temperatures for 10% of the cells (Unit 3, second and third quarters of 2014; Unit 9, second, third and fourth quarter 2014; Steam Turbine 5, second, third and fourth quarter 2014). This issue affected three batteries out of over 200 total DEP batteries. SEC uses rotating crews to perform maintenance. One crew’s misunderstanding of the maintenance requirements stemmed from the fact that DEP records the battery temperature on the pilot cells during the monthly and weekly testing. The crew was unaware of the requirement to take temperatures of the additional cells for the quarterly testing. As of February 25, 2015, DEP requires plant managers to review quarterly battery reports. No other instances of missing cell temperatures have been reported. The source of this issue appears to be limited to a single crew at SEC. This issue lasted from July 1, 2014, the first day of the third quarter of 2014, until October 16, 2015 when DEP completed mitigation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The SEC units 3, 9 and ST5 have a combined generating capability of approximately 674 MWs compared to the DEP generation capability of 14,470 MWs. If all three batteries at SEC were rendered inoperable simultaneously approximately 4.66% of DEPs capacity would be at risk. The records show that the majority of the maintenance for the SEC’s batteries was performed per the DEP program. The only item missing is the 10% of the cell electrolyte temperatures for the listed quarterly tests. Annual tests and subsequent quarterly tests show the battery condition was good and that they should have performed as expected. Plant operation is not known to have been effected by the failure to record the cell temperatures. No harm is known to have occurred. SERC considered DEP’s PRC-005-1 compliance history in determining the disposition track. DEP’s relevant prior noncompliance with PRC-005-1 R2 includes: SERC200900306, SERC2011006760, SERC2013012434, and SERC2014014141. SERC determined that DEP's compliance history should not serve as a basis for applying a penalty. As explained below, the causes of the extant issues were not addressed by the previous Mitigation Plans. SERC200900306 involved a failure by DEP to conduct maintenance on CCVTs as called for in its Protection System maintenance and testing program. DEP determined that the root cause of the violation was database corruption and as part of its Mitigation Plan, DEP undertook an inventory of its substations and reconciled the remainder of the field inventory with its database. Mitigation was complete on September 30, 2010. In SERC2011006760, DEP self-reported missing or incomplete maintenance or testing records for less than 5% of the Protection System devices. Mitigation included performing maintenance and testing on those devices and revising their record keeping methods for those, but not all, devices. Mitigation was complete on November 9, 2012. For SERC2013012434, DEP had inadvertently closed a work order before testing on a single line trap that had been successfully completed. DEP identified the root cause was the failure to require evidence of work completion to be attached to the work order prior to closing the order. The requirement to do so was added to the work order process for all Protection System devices and the required maintenance was completed as steps of a Mitigation Plan that was completed July 23, 2013. For SERC2014014141, DEP was not able to provide one quarterly battery inspection report at one power plant and had prematurely scheduled and performed a quarterly inspection at another plant. The issue was mitigated by issuing standing orders concerning quarterly battery checks, developing and presenting lessons learned and requiring plant managers to perform quarterly battery maintenance reviews. These actions were completed February 25, 2015. SERC considered Duke Energy Florida’s (DEF) PRC-005-1 R2 compliance history in determining the disposition track. DEF’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation FRCC2013012446. In FRCC2013012446, DEF did not have evidence that one set of Protection System devices was maintained and tested within the defined intervals because one pair of relays that had been listed in the database as a distribution relay. Mitigation was completed on June 27, 2013 but would not have addressed the instant issue. SERC considered Duke Energy Carolinas’ (DEC) PRC-005-1 compliance history in determining the disposition track. DEC’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation ID SERC201000544. In SERC201000544, approximately 1.9% of DEC’s Protection System devices had not been tested within the defined interval. The instant violation is of different nature and the Mitigation Plan did not address the instant issue. SERC considered Duke Energy Corp’s (DECorp) PRC-005-1 compliance history in determining the disposition track. DECorp’s relevant prior noncompliance with PRC-005-1 R2 includes: NERC Violation IDRFC2011001122 and RFC201000665. However, each of these instances is over three years old and SERC doesn’t consider them relevant given the circumstances. DECorp completed mitigation for RFC2011001122 in 2011 and completed mitigation for RFC201000665 in 2010. As described above, SERC reviewed the posted violations of PRC-005 for affiliates DEC, DECorp, and DEF and did not identify circumstances similar to that of the instant issue. Each Duke Energy affiliate is responsible for its own maintenance and testing program and the completed Mitigation Plans would not have addressed the instant issue. Therefore, SERC did not consider the previous violations by affiliates as aggravating circumstances, nor did it identify a programmatic issue based on that history. | To mitigate this issue, DEP issued a quarterly review memo to all DEP Fossil Hydro Organization (FHO) generating stations requiring a review of the quarterly battery maintenance records for completeness and that they are stored in the proper electronic file repository. SERC has verified the completion of all mitigation activity.
2015-12-30 | Southwest Power Pool Regional Entity (SPP RE) | KODE Novus I, LLC (KODE) | NCR11329 | SPP2015014908 | PRC-005-1b | R1; R1.1, R1.2 | On May 4, 2015, KODE submitted a Self-Report stating that, as a Generator Owner, it had a minimal risk instance of noncompliance with PRC-005-1.1b R1. Specifically, KODE’s documented protection system maintenance and testing program (PSMTP) did not include maintenance and testing intervals, including their bases, for KODE’s battery and battery charger; nor did it include a summary of maintenance and testing procedures for its battery and battery charger. This instance of non-compliance began on March 3, 2013, the day KODE registered with NERC as a Generator Owner, and ended on February 25, 2015, the day KODE successfully mitigated the instance of noncompliance. The root cause of this issue was lack of internal controls to ensure documentation was up-to-date and accurate. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, KODE did have a PSMTP in place at the time it registered with NERC as a Generator Owner that included all its protection system devices except its one battery bank and associated battery charger. Furthermore, KODE is a wind farm generator with a peak capacity of 80 MW that began operations 2013. No actual harm occurred to the Bulk Power System as a result of this issue of non-compliance. No Violation History | To mitigate this minimal risk instance of noncompliance, KODE updated its PSMTP to include batteries and battery chargers.
2015-11-30 | Midwest Reliability Organization (MRO) | Northern States Power (Xcel Energy) (NSP) | NCR01020 | MRO2015015306 | EOP-005-2 | R15 | On August 19, 2015, NSP submitted a Self-Report stating that as a Generator Operator (GOP), it had an issue with EOP-005-2 R5. Specifically NSP self-reported that it failed to notify its Transmission Operator (TOP) of a change to the capability of a Blackstart Resource within 24 hours of a change in the Blackstart Resource's capability. This occurred on June 29, 2015 when NSP removed one of its diesel generators for service for 11 hours to perform maintenance. This generator was necessary to perform a black start restart at the Inver Hills generation station. This issue was discovered during a monthly review of operator logs. The root cause of these instances of non-compliance was a lack of training and lack of familiarity with the process, as the employee in question ignored the written process, and seemingly did not know about this reporting requirement, in part due to the infrequency of these reports. The instance of noncompliance began on June 29, 2015 and ended on July 15, 2015. | The issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The standard requires that the TOP be notified within 24 hours of the change in capacity. In this case, the change in capacity only lasted 11 hours, meaning that the Blackstart unit was fully operational at the time that NSP missed the standard's reporting requirement. The risk is further mitigated by the internal controls that NSP had in place at the time of the noncompliance, specifically, the maintenance process required personnel to notify the TOP, which was reinforced through signage, but the personnel in question did not know the process and failed to read signage prior to beginning the maintenance. No harm is known to have occurred. This is NSP's first issue with EOP-005-2. | To mitigate this issue, NSP: 1) created automated distributed control system (DCS) alarms to alert generator operators of their obligation to notify the TOP and to make a log entry when the Inver Hills Diesels are switched away from the auto position; 2) updated maintenance work orders to specifically state that the TOP should be notified, and to log the diesel unit in and out of service during maintenance; 3) created automated DCS alarms at other Blackstart facilities that require a diesel generator; 4) updated process management tools to ensure the job plan includes a reminder for the generator operators to notify the TOP, to log the diesel unit in and out of service, and to conduct a planning meeting (also known as a tailgate session) prior to beginning the work; and 5) required each Blackstart facility to review this incident, review NSP Policy ESO 6.410, and the EOP-005 reporting requirements. NSP stated that mitigating activities were complete as of September 18, 2015.
2015-11-30 | SERC Reliability Corporation (SERC) | South Carolina Electric & Gas Company (SCE&G) | NCR00915 | SERC2015015156 | PRC-018-1 | R6 | On August 17, 2015, SCE&G submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-018-1 R6. SCE&G failed to implement its maintenance and testing program for its Disturbance Monitoring Equipment (DME) during 2014. SCE&G is required to have four DME devices: fault recorders at the VC Summer Station and Jasper Station and dynamic disturbance recorders at the VC Summer Station and the Savannah River Station. On May 19, 2015, while planning fault recorder maintenance and testing activities for 2015, SCE&G discovered that it failed to perform maintenance on the DME devices during the 2014 calendar year at the Savannah River Station and VC Summer Station. In a subsequent extent of conditions review to determine the full scope of the potential noncompliance, SCE&G reviewed all testing and maintenance activities associated with the DME devices for the last three years and discovered that it failed to perform periodic testing on the DME device located at the Jasper Station as scheduled during the 2014 calendar year. The primary cause of this issue is that personnel responsible for manually entering the maintenance and testing activities into spreadsheets were unaware that maintenance and testing needed to be performed. There was no other mechanism to trigger the maintenance and testing activities or otherwise alert that the maintenance was due in 2014. This issue lasted from January 1, 2015, the date that the 2014 maintenance and testing was out of interval, until mitigation completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The loss of DME recording capability for a system event would result in the loss of post event forensics information. However, for each location, there is at least one fault recorder located at a remote bus to provide partial overlap and the information from these devices would be used to perform a forensic analysis. In addition, there are microprocessor relays located at each location that utilize oscillography and record events, which can be used for post event investigation. Further, the purpose of this Standard is to facilitate event analyses and this issue would not impact the BPS in real-time. No harm is known to have occurred. SERC determined that SCE&G had no relevant compliance history. | To mitigate this issue, SCE&G: 1) removed the noncompliant Jasper Station DME device from service and installed a new DME device; and 2) performed the required maintenance on the Savannah River Station DME device. To mitigate this issue, SCE&G will complete the following mitigation activities by December 31, 2015: 1) perform the required maintenance on the VC Sumner Station DME devices; and 2) utilize a database, which is an asset management tool and work activity database that schedules maintenance and testing activities, as an internal control to help prevent recurrence. SCE&G needs until December 31, 2015 to complete its mitigation because it cannot perform maintenance at VC Sumner Station until the fall 2015 outage.
2015-11-30 | Texas Reliability Entity (Texas RE) | Turkey Track Wind Energy Center (Turkey Track) | NCR10277 | TRE2015015126 | VAR-002-4 | R3 | On August 4, 2015, Turkey Track submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R3. Specifically, Turkey Track failed to notify its associated Transmission Operator (TOP) of a status change on the automatic voltage regulator (AVR) within 30 minutes of the change. On June 9, 2015, at 8:45 p.m., Turkey Track called its TOP to notify it that an outage was complete and that Turkey Track would be bringing its wind turbines back online. As it restored its wind generation facilities to service, however, Turkey Track did not recognize that its AVR was offline. Turkey Track’s AVR requires a functioning Wind Farm Management System (WFMS) to operate. However, Turkey Track’s WFMS was not functioning at the time Turkey Track restored its wind generation facilities to service. Turkey Track subsequently identified an issue with the battery backup power sources for its WFMS, which caused the WFMS to fail. Upon recognizing that its WFMS was not functional, Turkey Track informed its TOP that Turkey Track’s AVR was offline at 2:30 p.m. on June 10, 2015. On June 11, 2015, Turkey Track subsequently notified its TOP that the WFMS was again running properly and the AVR was in service. The root cause of this issue was human performance error. As part of its operational checks for completing an outage, Turkey Track has a procedure in place to verify that the WFMS is functioning. In restoring Turkey Track’s wind generation facility to service, however, Turkey Track operators overlooked this step in the process. Had Turkey Track’s operators recognized that the WFMS was not functioning, they would have known that the AVR was offline. Texas RE determined that the issue duration was from 9:15 p.m. on June 9, 2015, which is 30 minutes following the AVR status change, until 2:03 p.m. on June 10, 2015, when Turkey Track notified its TOP that the AVR was offline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, Turkey Track was only outputting a small amount generation, as the hourly average generation varied from 0.22 MW to 27 MW. Second, Turkey Track's voltage never exceeded its voltage profile while the AVR was out of service. Finally, Turkey Track was in communication with its TOP throughout the duration of the issue and provided manual updates regarding the status of its wind generation facilities until the WFMS was restored. No harm is known to have occurred. Texas RE considered Turkey Track’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Turkey Track: 1) notified its TOP that the AVR was offline; 2) restored the WFMS to service; and 3) provided training to control room operators regarding the procedures in the ICC Control Room Operator Guide, including verifying and monitoring WFMS status, along with related steps to monitor VAR controls such as its AVR. Texas RE has verified the completion of all mitigation activity.
2015-11-30 | Texas Reliability Entity (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | TRE2015015045 | PRC-005-1b | R2; R2.1 | On June 29, 2015, Oncor submitted a Self-Report stating that, as a Distribution Provider (DP) and Transmission Owner (TO), it had an issue with PRC-005-1b R2.1. Specifically, Oncor failed to perform maintenance on protection system devices associated with four systems within the time intervals defined in Oncor's Protection System Maintenance and Testing program. Regarding the first impacted system, Oncor failed to perform the required 9-year interval Operational Test maintenance for devices associated with a relay system. Oncor performed the required maintenance for the devices associated with the relay system on December 20, 2013, eight days after the December 12, 2013 deadline for performing such maintenance under its Protection System Maintenance and Testing program. The root cause of the issue was that the maintenance information for the relay system was not properly entered into Oncor’s BPS maintenance tracking tool, and the Oncor Transmission District responsible for conducting the maintenance was using an outdated report to track its maintenance due dates. With regard to the second and third impacted systems, Oncor failed to perform the required 7-year interval Calibration and Operational Test maintenance for the devices associated with two protection system relays. Under its Protection System Maintenance and Testing program, Oncor was required to perform the indicated maintenance on these systems by October 9, 2013. Oncor in fact performed the required maintenance for the devices associated with one protection system relay on December 23, 2013. Oncor performed the required maintenance for the devices associated with the other protection system relay on January 9, 2014. The root cause of the issue was that the ring bus location names of the two relays were unclear in the tools used to track maintenance. As a result, the testing dates for two other breakers were inadvertently transposed, resulting in incorrect maintenance due dates being displayed in Oncor’s Validation tool. Regarding the fourth impacted system, Oncor failed to perform Operational Test maintenance on the devices associated with an autotransformer within the 5-year interval defined in Oncor's Protection System Maintenance and Testing program. Oncor was required to perform the indicated maintenance on the devices associated with the autotransformer system by October 19, 2012. However, Oncor did not perform the required maintenance until August 18, 2014. The root cause of the issue was that Oncor had incorrectly identified the autotransformer as a distribution transformer in the system that issues work orders for BPS maintenance. As a result, that system did not issue the appropriate work order. Texas RE determined the issue duration to be from October 20, 2012, the day after testing was due for the devices associated with the autotransformer (the earliest required maintenance date for the four systems at issue), until August 18, 2014, when all Oncor completed maintenance on the devices associated with the final impacted system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the impacted devices associated with the 4 systems at issue represent less than 0.5% of Oncor’s PRC-005 applicable devices. Second, the issue duration period was short for the majority of the impacted devices. Third, the test results demonstrated that devices associated with the impacted systems were in satisfactory working condition and no issues were detected with those devices during the testing. Fourth, there were no misoperations on any devices associated with the impacted systems during the duration of the issue. In addition, Oncor possessed a number of protective elements on the devices associated with the impacted systems to mitigate reliability risks. For instance, all remote terminals can detect bus faults in standard remote clearing times, which allows the isolation of the faulted equipment while maintaining system stability. Also, remote back-up protection is setup to operate for faults so that there is no abnormal system impact. For the autotransformer system and associated devices, there are two sets of three transformer differential relays connected to this autotransformer, with the current transformers connected in a delta configuration. A relay in both sets of differential protection schemes can fail at the same time, and both protection systems will still operate properly for any single phase or multi-phase fault. The autotransformer system and associated devices are also equipped with sudden pressure relay protection and non-directional time over-current protection. Finally, the impacted autotransformer system and its associated devices were only placed in service in 2007. No harm is known to have occurred. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 (TRE201100459) for Oncor was filed with FERC under RC13-9-000 on May 30, 2013. The 60-day review period passed on July 29, 2013. A Settlement Agreement covering PRC-005-1 R2 (TRE201000280) for Oncor was filed with FERC under NP12-26-000 on April 30, 2012. On May 30, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE considered Oncor's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the root causes of Oncor’s prior violations of PRC-005 R2.1 are distinguishable from the instant issue. The prior noncompliance pertaining to TRE201100459 was related to the following causes: 1) a work order was incorrectly closed prior to testing the applicable Protection Systems. Additionally, a new work order was created, but the date did not match the next maintenance due date; 2) a battery was erroneously classified as a non-Oncor asset and therefore was not tested by Oncor in accordance with Oncor's maintenance and testing program. Furthermore, TRE201000280 pertained to 23 relay systems that were not tested within the appropriate intervals because the incorrect benchmark date was used. Since this benchmark date establishes the starting point for maintenance intervals, the work-order triggers were inappropriately extended beyond the required date. In contrast, the instant noncompliance related to the following causes: 1) Oncor failed to properly enter all relay maintenance information in the tracking tool; 2) the Oncor Transmission District responsible for conducting the maintenance at Roanoke was using an outdated report to track its maintenance due dates; 3) the maintenance testing due dates were reflected incorrectly in the Validation tool because two other breakers were inadvertently transposed for the subject breakers; and 4) Oncor incorrectly identified an autotransformer as a distribution transformer in the system that issues work orders for BPS maintenance. A Settlement Agreement covering PRC-005-1 R2 (TRE201000272, TRE201000273, and TRE201000274) for Oncor’s affiliates Big Brown, LGC, and Tradinghouse was filed with FERC under NP12-10-000 on December 30, 2011. On January 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE also reviewed Oncor’s affiliate compliance history and did not consider the prior conduct of its affiliates an aggravating factor. In the previous instance, the affiliates failed to test all relays and instrument transformers in its Protection System Maintenance and Testing Program because the TO had been previously responsible for protection system maintenance in the switchyard. Additionally, the affiliates operated under separate compliance responsibilities than Oncor. | To mitigate this issue, Oncor: 1) completed the past due testing maintenance according to the governing procedure for the relay systems; 2) completed the past due testing maintenance according to the governing procedure for the autotransformer; 3) removed transmission district employees’ access to outdated maintenance tracking tools and limited access to those in the group responsible for Maximo; 4) conducted training for Forth Worth and Graham Transmission District on the use of Oncor's online validation tool (tool used to track correct maintenance due dates) to ensure the responsible personnel understand which tools should be used to track maintenance dates; 5) improved location descriptions in the tracking tool to clarify subject ring bus locations by adding a new column titled “Location Notes”; 6) increased the frequency of emails provided to all Transmission Districts to highlight the upcoming maintenance deadlines in each district (emails now sent monthly); and 7) reviewed its autotransformer equipment list and compared it to the autotransformer relay location list. In addition, all stations with both 345kV and 138kV equipment were reviewed to verify that additional 345kV/138/kV autotransformers are on the relay location list. Texas RE has verified the completion of all mitigation activity.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Goshen Phase II LLC (GPL) | NCR11089 | WECC2015014861 | PRC-005-1.1b | R2; R2.1 | On February 26, 2015, GPL, as a Generator Owner, submitted a Self-Certification citing possible non-compliance with PRC-005-1.1b R2. Specifically, GPL reported it failed to test two battery systems within the interval defined in its Protection System Maintenance and Testing Program (“PSMP”) GPL also stated in its Self-Certification that the scheduled interval was missed due to an inaccurate testing due date set forth in Compliance Task Manager ("CTM") for GPL's annual battery-related test. The CTM due date for the annual specific gravity check are established on a rolling 12-month basis based on the date the CTM task is closed out as completed. This means that, when the annual specific gravity check is completed and the CTM task is subsequently closed, a new CTM due date is established 12 months after the date the CTM was closed. In this instance, because the CTM task for 2013 was closed on October 25, 2013, even though the testing date occurred on August 24, 2013 and August 27, 2013, a due date of October 25, 2014 was established for the annual specific gravity check for 2014. A WECC Subject Matter Expert (“SME”) reviewed the Self-Certification and discussed the possible non-compliance with GPL. The SME determined that GPL’s two Energy Battery Systems were measured on August 24, 2013 (Battery Bank 1) and August 27, 2013 (Battery Bank 2); and then again the following year on September 23, 2014, for both Battery Bank 1 and 2. As such, the Battery Systems were not tested with the 12 month interval, as mandated by GPL’s PSMP. The SME determined that GPL had a possible noncompliance with PRC-005-1.1b R2, and forwarded the findings to Enforcement for review. Enforcement reviewed the Self-Certification and the SME’s findings and determined that GPL’s failure to test 2 Battery Systems in accordance with the intervals defined in its PSMP is a compliance exception of PRC-005-1.1b R2. Enforcement further determined that the compliance exception began on August 24, 2014, when GPL should have maintained and tested the Battery Systems, and ended on September 23, 2014, when GPL completed maintenance and testing on the two Battery Systems. The root cause of this Compliance Exception is GPL's believed the scheduled interval was missed due to an inaccurate testing due date set forth in Compliance Task Manager ("CTM") for Goshen's annual battery-related test to measure specific gravity. In this instance, because the CTM task for 2013 was closed on October 25, 2013, even though the testing date occurred on August 24, 2013 and August 27, 2013, a due date of October 25, 2014 was established for the annual specific gravity check for 2014. Therefore, WECC believes the root cause of this issue is GPL’s less than adequate procedure for closing CTM tasks for interval testing. WECC determined there was no known harm from this noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As a preventative measure, GPL performs monthly battery checks, which included a visual inspection, Digital Low Resistance Ohmmeter (“DLRO”) tests on 10% of randomly selected cells, a voltage and amperage check on the entire battery system, and a specific gravity check on the pilot cells of the top and bottom racks of the battery banks. Additionally, when used correctly, GPL utilizes a maintenance management system (CTM) for accurate scheduling and tracking maintenance on its batteries. This task tracking software generates automatic work orders, reminders, and alarms to proactively notify the site of upcoming requirements and tasks, and which helps to ensure that tasks are performed according to schedule. WECC considered GPL's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GPL: 1) Verified that its CTM has the appropriate tasks and due dates for annual battery testing entered into the system. 2) Combined the CTM task for the annual specific gravity check with the CTM task for annual DLRO testing. Further, a new due date of July 24, 2015 was established for 2015 testing based on the date the annual DLRO testing was performed for Goshen in 2014, which was July 24, 2014. The CTM tasks were combined on February 3, 2015. To further enhance internal controls, BP Wind’s Regulatory Compliance organization intends to implement periodic checks for PRC-005 compliance documentation to allow for even more prompt detection of instances of non-compliance. In addition, CTM will be checked periodically to ensure that the due dates for protection system maintenance and testing program are correct.
2015-11-30 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 2 of Grant County, Washington (GCPD) | NCR05342 | WECC2015014658 | TOP-007-0 | R1 | On February 26, 2015, GCPD submitted a Self-Report stating that, as a Transmission Operator, it was in noncompliance with TOP-007-0 R1. On May 22, 2014, one of GCPD’s 115kV transmission lines to a neighboring entity exceeded its SOL by 1.9% for ninety-one seconds. GCPD had an erroneous alarm setting on the neighboring end of the line, was unaware of the exceedance, and did not inform the RC of the exceedance nor the actions taken to return the system to within limits. The neighboring entity, which owns the equipment on the end of the line in question, was alarmed and performed actions to mitigate the alarm condition. The root cause of this issue was an inadequate alarm configuration that resulted in undetectable errors. This issue began on May 22, 2014, when an unreported SOL violation occurred, and ended March 19, 2015, when GCPD completed correction of alarm setting discrepancies. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, GCPD failed to inform the RC when an SOL was exceeded and actions were taken to restore the system to within limits. The alarming capability of the neighboring entity reduced the risk of this issue. No harm is known to have occurred. GCPD does not have previous violations of this Standard and Requirement and has provided documentation of its internal compliance program. | To mitigate this issue, GCPD: 1) reconciled all established SOL limits and associated alarms in its EMS; 2) provided identified areas of concern to System Operators for manual monitoring until alarm settings were adjusted; 3) verified that the neighboring entity had the appropriate SOL alarm setting, was alarmed, and performed actions to mitigate the alarm condition during this incident; 4) verified redundant monitoring of interconnection points by neighboring BAs; 5) corrected alarm settings for established SOLs; and 6) revised internal procedure to improve situational awareness and prevent recurrence, including EMS monitoring for portions of facilities not owned by GCPD. WECC verified that GCPD completed mitigating activities.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Fortistar North Tonawanda (FNT) | NCR07090 | NPCC2015015097 | PRC-005-1.1b | R1.1 | During a Compliance Audit conducted from January 25, 2015 to May 1, 2015, the auditors determined that FNT, as a Generator Owner, had an issue of PRC-005-1.1b R1.1. FNT has a Protection System Maintenance and Testing program in place, however the auditors determined that the program was insufficient as it did not contain a process to "Verify the integrity of current and voltage transformers and associated circuity" as required. Specifically, FNT did not have a program in place to verify AC signals from PTs and CTs to their respective devices. Since the process for CT and PT signal verification did not exist, FNT was unable to provide a previous testing date as required by R2. The PRC-005-1.1b R1.1 violation lasted from June 21, 2007 to July 31, 2015. The root cause of the issue was a misinterpretation of the standard by the entity, as they believed that by visually inspecting the CTs and PTs, and having the connections checked, they were in compliance with the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The generator's DMNC has a (Demonstrated Maximum Net Capability) of 53.9 MW and 62.3 MW for Summer 2014 and Winter 2014/2015 respectively. All other protection system components were addressed in FNT's Protection System Maintenance and Testing program, and were properly tested within the time periods dictated in the program. There were no misoperations of the Protection System during the duration of the violation. In the previous maintenance and testing program, CTs and PTs were visually inspected and had their connections checked. No harm is known to have occurred as a result of the violation. NPCC considered FNT's's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FNT: 1) Updated their Protection System Maintenance and Testing Program to include CT and PT signal verification; and 2) Will complete signal verification for PTs and CTs by January 31, 2016. FNT will attempt to complete the testing sooner if possible.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Fortistar North Tonawanda (FNT) | NCR07090 | NPCC2015015141 | PRC-005-1.1b | R2.1 | During a Compliance Audit conducted from January 25, 2015 to May 1, 2015, the auditors determined that FNT, as a Generator Owner, had an issue of PRC-005-1.1b R2.1. FNT has a Protection System Maintenance and Testing program in place, however the auditors determined that the program was insufficient as it did not contain a process to "Verify the integrity of current and voltage transformers and associated circuity" as required. Specifically, FNT did not have a program in place to verify AC signals from PTs and CTs to their respective devices. Since the process for CT and PT signal verification did not exist, FNT was unable to provide a previous testing date as required by R2. The PRC-005-1.1b violation began on June 21, 2007, and is still ongoing. The violation end date will be the date that FNT completes signal verification on CTs and PTs (will be completed by January 31, 2016). The root cause of the issue was a misinterpretation of the standard by the entity, as they believed that by visually inspecting the CTs and PTs, and having the connections checked, they were in compliance with the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The generator's DMNC has a (Demonstrated Maximum Net Capability) of 53.9 MW and 62.3 MW for Summer 2014 and Winter 2014/2015 respectively. All other protection system components were addressed in FNT's Protection System Maintenance and Testing program, and were properly tested within the time periods dictated in the program. There were no misoperations of the Protection System during the duration of the violation. In the previous maintenance and testing program, CTs and PTs were visually inspected and had their connections checked. No harm is known to have occurred as a result of the violation. NPCC considered FNT's's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FNT: 1) Updated their Protection System Maintenance and Testing Program to include CT and PT signal verification; and 2) Will complete signal verification for PTs and CTs by January 31, 2016. FNT will attempt to complete the testing sooner if possible.
2015-10-29 | Northeast Power Coordinating Council (NPCC) | Dartmouth Power Associates, LP (DPA) | NCR02922 | NPCC2015015215 | PRC-005-1.1b | R2.1, R2.2 | On August 14, 2015, Dartmouth Power Associates, LP submitted a self-report stating that as a Generator Owner, it had an issue of PRC-005-1.1b, R2.1 and R2.2. Sapphire Power, Dartmouth's owner, was conducting an internal compliance review to implement PRC-005-2. As part of the review, the maintenance and testing tracking tools were compared against trip schematics and it was discovered that certain DC circuits had not been tested. While a maintenance and testing program existed and was implemented for DPA, certain components had not been included in the program and therefore had not been tested. The components that had not been tested were DC circuits and included lockout relays and trip paths associated with the switchyard. In total, seven DC trip circuits had not been tested. The PRC-005-1.1b R2.1 and R2.2, violations lasted from October 8, 2007, to June 27, 2015, when the DC circuits were tested. A root cause analysis determined that there was an initial flaw in compiling the lists of Protection System devices subject to PRC-005 that was not discovered until the 2015 review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The missing DC trip circuits make up 7 of 285 devices in DPA's protection system, or 2.4%. All other devices in DPA's protection system were addressed in the maintenance and testing program and were properly tested according to their intervals. The Dartmouth facility has a claimed Summer capability of 81 MW. DPA has had no misoperations of facility protection systems, and has had trip events where the relaying has operated correctly. No harm is known to have occurred as a result of not performing the DC trip testing. NPCC considered DPA's compliance history and determined there were no relevent instances of noncompliance. | To mitigate this issue, DPA: 1) Performed testing on the devices in question on June 27, 2015. All devices passed testing; 2) Updated internal R2 compliance tracking tools to account for the devices that were previously missing; and 3) Will conduct future periodic reviews of facility device lists to verify devices included in the PRC-005 program. This will prevent future issues of a similar nature from occurring. NPCC has verified the completion of all mitigating activities.
2015-10-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Duke Energy Corporation (Duke) | NCR00761 | RFC2014014482 | VAR-002-2b | R3 | On November 19, 2014, Duke submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-2b R3. When Duke’s Gibson Unit 5 generator returned to service from an outage on July 28, 2014, the Automatic Voltage Regulator (AVR) was not operating correctly in the automatic mode. Duke responded by placing the AVR in manual mode and notified generation dispatch who notified the Transmission Operator (TOP) within 30 minutes of the AVR being placed in manual mode as required by VAR-002. A service technician arrived on July 30, 2014 to assist in troubleshooting the AVR problem and to make repairs. At 9:43 (CDT) on July 30, 2014, the control room operator contacted generation dispatch and stated they were going to try to put the AVR into automatic mode while troubleshooting. The generator dispatch operator did not make the notification to the TOP that the AVR was being put back into automatic mode within 30 minutes of the switch being made. The control room operator made a notification at 13:53 (CDT) that the AVR would remain in automatic mode until further notice. This information was then quickly relayed from the generation dispatch operator to the TOP. The notice to the TOP of placing the AVR in automatic mode was made four hours after the AVR was placed in automatic mode and VAR-002 requires notification within 30 minutes of a change in AVR mode. The root cause of this noncompliance concerned the management practices of workforce management and verification. Workforce management was implicated because generation dispatch operators were not effectively trained to understand that the TOP had to be notified within 30 minutes of a change in AVR. Verification was implicated because Duke did not confirm that the generation dispatch operator was always making timely notifications to its TOP about changes in AVR. The duration of this noncompliance is from 10:13 (CDT) on July 30, 2014, the time by which Duke was required to notify its TOP that it had switched the generator’s AVR back from manual to automatic mode, to 13:53 (CDT) on July 30, 2014, when Duke notified the TOP about the change in AVR. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. At the time of the noncompliance, the Gibson Unit 5 AVR had been returned to automatic mode which per VAR-002, requires generators to operate their AVRs in automatic mode. Additionally, the noncompliance lasted for less than four hours. Throughout the noncompliance, the AVR was in automatic mode and the generator maintained its voltage schedule while troubleshooting a problem with the AVR’s automatic capability. No harm is to known to have occurred. A Find, Fix and Track Report covering a violation of VAR-002-2b R3 was filed with FERC on July 31, 2014. The prior violation is distinguishable from the current noncompliance. In the prior violation, there were two separate instances where Duke operated a generator connected to the interconnected transmission system in manual voltage control mode without notifying the TSO within 30 minutes of changes in status. The first instance occurred during the synchronization process after the generator had been tripped offline. The second instance occurred when the energy management system did not receive a signal to indicate a change in AVR status that would have notified the generation dispatch operator of the change. In contrast, the current noncompliance is an isolated incident and occurred while a service technician was troubleshooting an AVR problem and switched the generator into auto mode without the generator dispatch operator making the proper notification to the TOP. Although both the prior violation and the current noncompliance share root causes of poor workforce management and verification, the similar root causes are not problematic because Duke’s prior violation and the instant noncompliance were both identified and corrected. Additionally, the mitigation plan for the instant noncompliance will prevent future violations as it expands on the mitigation plan of the prior violation by implementing a script to be followed when communicating a change in AVR status that will ensure the station operators, generation dispatch operators, and the TOP are all timely notified of the change in AVR mode. ReliabilityFirst demined that Duke's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Duke: 1) created an order that requires personnel at Gibson Station to have a production supervisor present whenever a notification phone call is made regarding a change in AVR status. To ensure proper three-way communication is used during AVR status changes with the Load Center, the Operation Team Supervisor (OTS) will monitor the conversation between the unit operator and the Load Center. The OTS will validate that proper communication is used and the call status is logged in Duke’s plant view software; 2) reviewed this order with all Gibson Station operations personnel; 3) developed a script to be used when communicating a change in AVR status to ensure that all personnel involved are aware that this communication is for the purpose of complying with VAR-002 and is consistent for all change in status communications between the station operators, generation dispatch operators, and the TOP; and 4) conducted a review session with all affected personnel to review the script.
2015-10-29 | ReliabilityFirst Corporation (ReliabilityFirst) | METC | NCR00820 | RFC2014013450 | PRC-023-2 | R1 | On February 24, 2014, METC submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of PRC-023-2 R1. METC determined that the switch-onto-fault (SOTF) relay settings at two locations did not meet PRC-023-2 R1 Criterion 1 for relay loadability. Under Criterion 1, the relay settings must not trip for less than 150 percent of the highest seasonal Facility Rating of a circuit. At the Nelson Road location, the SOTF relay settings were set to trip for 142 percent of the Facility Rating. At the Tompkins location, the SOTF relays settings were set to trip for 125 percent of the Facility Rating. The root cause of this noncompliance relates to the sampling method METC used to ensure that its relays were compliant when PRC-023-2 R1 initially became effective. During this sampling process, METC selected a sample set of relays and found no errors in the relay settings for this sample set. Based on this finding, METC did not expand its review to ensure the relay settings met PRC-023-2 R1 and thus did not identify the subject noncompliance at that time. METC indicated that it did not have the necessary tools to do a comprehensive review of the relays at the time PRC-023-2 R1 went into effect. The duration of this noncompliance is from October 1, 2013, the date METC was required to comply with PRC-023-2 R1, to February 12, 2014, the date METC corrected the relay settings at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. At the Nelson Road location, even though the relay settings were set to trip at 142% of the Facility Rating, the line connects radially to generation that is not capable of producing enough current to pick up the SOTF setting (i.e. trip the relay). At the Tompkins location, the SOTF settings are only enabled for 10 cycles after the breaker closes. The remote end reclosing is delayed for six seconds, hence the SOTF setting would not be picked up when load is applied since that setting is only enabled for 10 cycles (less than six seconds). For the relay to trip, an operator would have to manually close the line at the remote end first, and then at Tompkins. This is unlikely to occur as it would be normal operating procedures for METC to run a study before closing a line manually, in which case the operators would verify that closing the line would not exceed the Facility Rating. No harm is known to have occurred. This is METC’s first instance of noncompliance with PRC-023 R1. | To mitigate this issue, METC: 1) implemented a relay setting database and software that allows for a comprehensive evaluation of whether or not all relays meet PRC-023 Criteria. For future PRC-023 changes, METC will perform an evaluation prior to the effective date of the revised standard to identify relay settings that are not compliant and will correct any issues prior to the standard becoming effective; and 2) performed a comprehensive evaluation and did not identify additional issues. METC has verified the completion of all mitigation activity.
2015-10-29 | ReliabilityFirst Corporation (ReliabilityFirst) | METC | NCR00820 | RFC2015014788 | PRC-023-3 | R1 | On March 30, 2015, METC submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue of PRC-023-3 R1. METC determined that the phase protective relays at two locations did not meet PRC-023-3 R1 Criterion 1 for relay loadability because they were set to operate at 148 percent of the highest seasonal Facility Rating. The Facility Rating of the line at issue was raised as a result of construction work that increased the line’s sag limit. On March 4, 2015, the new Facility Rating was published. METC discovered the issue on March 10, 2015 while preparing evidence for PRC-023 self-certification and corrected the relay settings that day. The root cause of the noncompliance is that the an employee manually bypassed the control that notifies METC if a rating about to be published is not in compliance with PRC-023 Requirements. The duration of this noncompliance is from March 4, 2015, the date METC was required to comply with PRC-023-3 R1, to March 10, 2015, the date METC corrected the relay settings at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The relay was set to trip at approximately 48 percent above the Facility Rating, which is only two percent under the limit set forth in PRC-023-3 R1 Criterion 1. If there was an event during the noncompliance, it is very unlikely that this minor discrepancy would have made a difference in the operators’ actions in response to the overload or would have been the difference in determining whether or not the line tripped prematurely. No harm is known to have occurred. METC has a prior issue of noncompliance with PRC-023 R1 (RFC2014013450), which is being resolved as a compliance exception. The root cause of the prior noncompliance did not contribute to and is distinguishable from the more recent noncompliance. The prior noncompliance occurred as a result of the process by which METC initially ensured it was compliant with PRC-023 while the more recent noncompliance occurred as a result of a change in a Facility Rating due to construction and the manual process by which employees could publish a Facility Rating change. ReliabilityFirst determined that METC's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, METC reprogramed the manual input control that prevented publishing Facility Ratings that do not meet PRC-023 Requirements to now automatically prevent publishing of a Facility Rating where trip settings are not in compliance with PRC-023 Requirements future activity.
2015-10-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Consumers Energy Company (Consumers) | NCR00740 | RFC2015014831 | EOP-004-2 | R2 | On March 31, 2015, Consumers submitted a Self-Report and Self-Certification to ReliabilityFirst stating that, as a Distribution Provider, it was in violation of EOP-004-2 R2. When reporting an event with more than 50,000 customer outages, Consumers’ system operators did not use the current Department of Energy (DOE) email address provided in the company’s operating plan. Rather, the system operators used an old email address that was included in the company’s system control and monitoring operating procedure. The root cause of this noncompliance was a failure in the management practice areas of asset and configuration management and information management. When updating the DOE email address for event reporting in its operating plan, Consumers failed to make the same update in the corresponding procedure. The duration of this noncompliance is from April 12, 2014, the date that Consumers was required to send the event report to the DOE pursuant to EOP-004-2 R2, to September 1, 2015, the date that Consumers completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, Consumers verified with the DOE that the email address to which Consumers sent the report was still functional for the purpose of DOE event reporting. Thus, the DOE was notified within the 24 hour timeframe required by the Standard. Second, EOP-004-2 R2 is a reporting/notification requirement the violation of which would not have caused direct harm to the reliability of the BES. No harm is known to have occurred. This issue is Consumers’ first issue with EOP-004-2 R2. | To mitigate this issue, Consumers: 1) Created a change management plan and training to effectively roll out company approved procedures plans, etc. to appropriate staff; and 2) Enhanced its document management process to ensure operating procedures align with company-approved operating plans.
2015-10-29 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2015015253 | VAR-002-4 | R2 | On September 25, 2015, AECC submitted a Self-Report stating that, as a Generator Operator, it had a minimal risk instance of noncompliance with VAR-002-4 R2. On August 16, 2015, at 09:01, AECC’s Bailey Generating Station was scheduled to perform a voltage change from its “off peak” schedule to its “on peak” schedule as required by its Transmission Operator. However, the plant operator did not immediately adjust the unit’s AVR to meet the “on peak” schedule. As a result, between 09:01 and 09:30, AECC’s voltage went below its voltage schedule by .04 kV. The duration of this minimal risk instance of noncompliance was from 09:01, August 16, 2015, when AECC’s Bailey Station deviated from its “on peak,” voltage schedule to 09:30, August 16, 2015, when the Bailey Station returned to within its voltage schedule. The root cause of this instance of noncompliance was human error, i.e., the inattentiveness of the plant operator. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure of a generator operator to operate within its voltage schedule could result in localized system voltages that deviate from established norms. In this instance, AECC’s deviation from its voltage schedule was by only 0.4 kV and the duration of the deviation was for less than 30 minutes. No actual harm occurred as a result of this instance. A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including AECC’s noncompliance with VAR-002-1 R2; R2.2 (SPP2014013570) and VAR-002-2 R2; R2.2 (SPP2014014420) was posted on the NERC website on May 28, 2015. The 60-day review period passed on July 30, 2015. SPP RE considered this compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the VAR-002-4 issue was isolated and not representative of a systemic compliance problem. Additionally, the facts and circumstances of the prior issues of non-compliance did not mirror the circumstances that caused the current instance of non-compliance. | To mitigate this minimal risk instance of noncompliance, AECC: 1) Counseled the plant operator who was on duty the day of the instance of noncompliance; and 2) Developed an audible alarm to sound when the plant is supposed to change its voltage schedule. SPP RE has verified the completion of all mitigation activity.
2015-10-29 | Texas Reliability Entity (Texas RE) | Lower Colorado River Authority (LCRA) | NCR04092 | TRE2015015092 | VAR-002-4 | R3 | On July 20, 2015, LCRA submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-4 R3. Specifically, LCRA failed to notify its Transmission Operator (TOP) that the power system stabilizer (PSS) at an LCRA generation facility had changed status from “on” to “off.” On June 17, 2015, at 7:59 a.m., an auto transformer fault caused a momentary voltage dip on a LCRA generation facility’s 138kV substation bus. The voltage dip caused the generation facility’s Unit 3 PSS to turn off. As LCRA’s operations personnel took steps to address issues related to the voltage dip, they neglected to notify the LCRA GenDesk regarding the PSS status change. Because the LCRA GenDesk was in turn responsible for notifying LCRA’s TOP about the PSS status change, LCRA did not provide notice to its TOP within the required 30-minute window. At 9:00 a.m., LCRA operations personnel noticed that the Unit 3 PSS had changed status and contacted the LCRA GenDesk. At 9:07 a.m., operations personnel placed the PSS back into “on” mode. At 9:08 a.m., the LCRA GenDesk contacted LCRA’s TOP to notify it of both the original 7:59 a.m. and the 9:07 a.m. Unit 3 PSS status changes. The root cause of the issue was human performance error. In addressing other issues related to the momentary voltage dip, LCRA plant operators did not communicate to the LCRA GenDesk that the Unit 3 PSS had changed status as specified in LCRA’s operating procedures. As a result, the LCRA GenDesk did not notify LCRA’s TOP of the PSS status change within the required 30-minute window. The issue duration was 38 minutes from, 8:30 a.m. until 9:08 a.m., which is 30 minutes following the Unit 3 PSS status change until the time LCRA notified the TOP of the PSS status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the duration of the issue was only 38 minutes. Second, while LCRA did not provide notice to the TOP that the PSS was out of service, the status of the PSS was still being telemetered to the TOP. Lastly, a PSS does not protect the bulk electric system (BES) from generator disturbances but rather serves to protect the generating unit from disturbances on the BES. No harm is known to have occurred. Texas RE considered LCRA’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, LCRA: 1) notified the TOP of the Unit 3 PSS status change; 2) implemented additional alarms screens that will specifically show PSS and automatic voltage regulator (AVR) status changes at the LCRA GenDesk; and 3) implemented an automated text and email notification system that will trigger notifications to the LCRA GenDesk Manager when a PSS device status flag shows that the device is out of service. Texas RE has verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | PUD No. 1 of Douglas County (DOPD) | NCR05343 | WECC2014014179 | PRC-005-1 | R2; R2.1; R2.2 | From July 7, 2014 to July 18, 2014, WECC Auditors conducted an onsite audit of DOPD’s compliance with PRC-005-1 for the period July 23, 2011 through April 7, 2014. PRC-005-1 R2 requires DOPD to provide evidence that its Protection System devices were maintained and tested within the defined intervals and provide a date each Protection System device was last tested/maintained. WECC Auditors reviewed DOPD’s evidence for Data Requests 20 and 40 and found that four (4) test records could not be located out of 69 instrument transformer maintenance and testing records. The Audit team determined that due to the missing records, this could be a possible issue of PRC-005-1 R2. The Audit team forwarded the information to Enforcement. Enforcement reviewed the information provided by the Audit team and DOPD. Enforcement determined that DOPD did not fully implement the Protection System Maintenance and Testing Program including documentation that all the protection system devices were maintained and tested within the defined intervals. Specifically, DOPD was not able to provide maintenance and testing records for four (4) out of 69 instrument transformers. This issue began on June 17, 2007, the date DOPD began its compliance with PRC-005-1 R2. Enforcement also determined that this issue ended on October 31, 2014. The root cause of this compliance exception was DOPD’s less than adequate procedure for separately tracking the maintenance and testing records for its CT’s and PT’s, because they were grouped together with protective relays in DOPD’s maintenance management system. For that reason, the summary report did not specify whether or not all CTs and PTs were being tested and maintained. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, DOPD failed to provide maintenance and testing records for 4 out of 69 instrument transformers. The BES portion of DOPD’s area includes 81 miles of 230kV and 144 miles of 115kV transmission lines. DOPD has six interconnection points with a large entity and a single point of interconnection with a small entity. DOPD’s has a peak load of 394 MW. DOPD serves a primarily rural area and performs some RP functions for the smaller entity and does not share any additional responsibilities with other entities. No harm is known to have occurred. DOPD’s small size and limited connection to other entities limits its ability to project adverse impacts beyond its own system. Further, the remaining 223 Protection System devices were maintained and tested within defined intervals. Per manufacturer guidelines, instrument transformers require minimal to no maintenance after operation. Also, DOPD did employ backup protection for all its Protection System devices. As a result, WECC determined that this issue poses a minimal risk to the BPS. WECC considered DOPD's relevant noncompliance with PRC-005 R2 NERC Violation ID WECC200800997 and determined it should not serve as a basis for applying a penalty. The cause of the prior instance DOPD incorrectly defining Bulk Electric System devices to only include its 230-kV facilities when it should have included devices associated with its 115kV facilities as well. In this instance, the cause of the violation was due to DOPD grouping together CTs and PTs into its maintenance management system. This prevented the summary report from specifying whether or not all CT’s and PT’s were being tested and maintained. So the mitigating activities from the prior instance of noncompliance would not have prevented the current issue from occurring. | To mitigate this issue, DOPD: 1. separated out instrument transformers as separate items in its maintenance management software, which will allow enhanced tracking of evidence documents for these devices. 2. added relay and CT/PT comparison testing documentation to the Douglas PUD Compliance Tracking SharePoint list to provide alarming and additional tracking for evidence. 3. updated its relay testing procedures to reinforce the importance of the CT/PT comparison testing. 4. provided additional training for its Technicians performing the tests to highlight the changes to the procedure and the importance of documenting the CT/PT comparison testing.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Alameda Municipal Power (APAT) | NCR10042 | WECC2014014422 | PRC-008-0 | R2 | On October 30, 2014 APAT submitted a Self-Report stating that, as a Distribution Provider (DP), it was in non-compliance with PRC-008-0 R2. The root cause of this issue was failure to execute existing controls. This issue began on July 1, 2014, when two relays were placed into the UFLS scheme without testing for UFLS function, and ended September 26, 2014, when APAT tested the relays. This issue was the entity's first noncompliance with this requirement; was identified and reported timely; was limited to two relays for a period of two months, both of which functioned as designed when tested; and posed minimal risk to the bulk power system (BPS). APAT identified this issue during an internal spot check for relay maintenance on September 23, 2014. APAT tested the relays on September 26, 2014, and both relays functioned as designed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. APAT implemented detective and compensating controls to mitigate the risk of Misoperation or functional failure of the untested relays. APAT’s controls include automated and escalated reminders for tasks, mandatory fields for collection of maintenance information, self-reviews, and administrator reviews. APAT utilizes SharePoint’s workflow management tool to promote timely, proactive, and thorough execution of these controls, as well as to ensure project visibility and accessibility for administrators. APAT also performs periodic spot checks to verify compliance for relay maintenance records. No harm is known to have occurred. Although the UFLS scheme was not used during the period in question, the relays would have activated as designed in that circumstance. The relays functioned as designed when tested for PRC-005-1b on June 19, 2014. The relays also functioned as designed when tested for UFLS function on September 26, 2014. The relays in question are also served out of a substation which is not connected to the Bulk Electric System. WECC considered APAT's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, APAT: 1) tested the relays for UFLS function; 2) performed a root cause analysis, determining the issue was the result of a failure to execute existing controls; 3) revised its UFLS program validation procedure to include more direction regarding new and/or changed equipment; and 4) provided training on this revision to requisite staff. WECC verified the completion of all mitigation activity.
2015-10-29 | Western Electricity Coordinating Council (WECC) | Platte River Power Authority (PRPA) | NCR05321 | WECC2015014674 | PRC-005-1.1b | R2; R2.1; R2.2 | On March 2, 2015, PRPA submitted a Self-Certification stating that, as a Transmission Owner (TO), Generator Owner (GO), and Distribution Provider (DP), it was in noncompliance with PRC-005-1.1b R2. The root cause of this issue was PRPA's failure to input six battery chargers into its automated maintenance management system. This issue began on April 2, 2014, when PRPA should have maintained and tested the battery chargers, and ended on November 18, 2014, when PRPA completed maintenance and testing on the battery chargers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PRPA implemented preventive, detective and compensating controls. As a preventive measure, PRPA uses daily operator checks of batteries and battery chargers for float voltage and current. As a detective measure, PRPA implements an annual review as part of the self-certification process to ensure that maintenance and testing had been performed as expected. Additionally, PRPA uses alarming to detect low voltage on the DC systems. As a compensating control, PRPA uses a battery system for each generator at the plant. Should the battery charger fail, the battery would provide DC power long enough to either fix the problem with the chargers, provide an alternate DC power source, or shutdown the generators in a controlled fashion. No harm is known to have occurred. WECC considered PRPA's compliance history and determined there were no relevant instances of noncompliance. In addition, PRPA has provided documentation of its internal compliance program to WECC. | To mitigate this issue, PRPA: 1) performed maintenance and testing on the six battery chargers; 2) updates its automated maintenance tracking software to include the battery chargers in scope; and 3) provided training to applicable employees on PRPA's transition to PRC-005-2. WECC has verified the completion of all mitigation activity.
2015-09-30 | Florida Reliability Coordinating Council (FRCC) | Duke Energy Florida, Inc. (DEF) | NCR00063 | FRCC2015015063 | PRC-005-1.1b | R2 | On April 13, 2015, DEF submitted a self-log stating that, as a Transmission Owner (TO), it had an issue of PRC-005-1.1b R2. On December 17, 2014, DEF self-logged that as a Transmission Owner (TO), it had an issue with PRC-005-1.1b R2. The Frequency Shift Keying (FSK) carrier units for Direct Transfer Trip (DTT) protection from Anclote to Seven Springs were found to be out of compliance. There are 2 carrier units at each end of the line, one for blocking (primary protection) and one for DTT (as secondary protection). Based upon information retrieved from DEF’s Maintenance Management System (MMS), on October 21, 2012 the primary blocking carrier was replaced. An Equipment Change Request (ECR) was submitted and processed for the primary blocking carrier replacement. As a result of the ECR, the primary blocking carrier was replaced in the MMS database, and the secondary protection DTT carriers were mistakenly removed from the MMS database. Once the DTT carriers were removed from the MMS database, it no longer generated preventative maintenance (PM) work orders for DEF to track maintenance activities on those carriers even though they were still in service. The maintenance interval for the carriers is 2yrs with a 25% grace period. The last maintenance completed on the secondary carriers at the Anclote end was September 23, 2011 and at the Seven Springs end was September 25, 2011, making them out of compliance as of March 22, 2014 and March 24, 2014 respectively. The tests were completed on December 30, 2014. The root cause of this issue is human error, in mistakenly removing the secondary carrier units from the MMS database. On March 22, 2014, DEF self-logged that as a Generator Owner, it had an issue of PRC-005-1b, R2. During a review of station battery maintenance documentation, it was discovered that four stations had incomplete records where data was not recorded correctly on evidentiary forms and checklists. 1. The station battery PM form was completed for Crystal River Units 4 and 5 each quarter of 2013 including the 3rd quarter, however an attached checklist was not completed. 2. Specific data was not recorded for Hines Units PB3A and 3B Annual PM battery charger output voltage and current readings. 3. Specific data was not recorded on Suwannee CT's P1, P2, and P3 2013 Quarterly PMs for 2nd, 3rd, and 4th quarters for "Internal Ohmic" readings for all battery cells. 4. Specific data was not recorded for for "AC Ripple Current for 125VDC West Bank and "Charger Ouput Voltage & Current" for 125VDC East Bank readings on Tiger Bay's 2013 Annual PM. The root cause is human error in not correctlly recording the required data readings. On March 3, 2014 DEF self-logged that, as a TO, it had an issue of PRC-005-1b, R2. Maintenance due dates had lasped for batteries located at DEF's Disston 230 kV Substation. DEF initiated a project to replace the existing batteries, and installed and tested the new batteries on November 30, 2012. DEF has a 1-year maintenance interval on these new batteries, with a 25% grace period. The next scheduled maintenance was due March 1, 2014. On March 31, 2014 DEF confirmed they had missed the maintenance. On April 2, 2014 DEF completed the required maintenance and made the necessary changes to its equipment database to correctly track the due dates for the new batteries. The battery maintenance was missed because two new battery banks at Disston were not correctly added to the DEF equipment data base for tracking maintenance due dates. The root cause is human error in not correctly adding the two new battery banks at Disston to the DEF equipment data base for tracking maintenance due dates. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The carrier units in question are designed for breaker failure, and will only be called upon to operate if there is a fault on the adjacent line or bus, and the breaker fails to clear it in time. Also, they are for secondary protection, and provide an alarm for loss of guard or a unit power failure. The blocking carrier is the primary protection and was in compliance. After maintenance was completed the maintenance results indicated that if called upon to operate, they would have operated as required. No harm is known to have occurred. A subsequent review revealed no sustained alarms, no corrective work orders, and no mis-operations on this line. The station battery PM form was completed for Crystal River Units 4 and 5 each quarter of 2013 including the 3rd quarter, however an attached checklist was not. The PM records for Crystal River were complete and the checklist was completed for the 4th quarter and annual preventative maintenance. Specific data was not recorded for Hines Units PB3A and 3B Annual PM battery charger output voltage and current readings. The rest of the PM form was complete, and this missing data had been previously documented a month prior on the November monthly inspection report. Specific data was not recorded on Suwannee CT's P1, P2, and P3 2013 Quarterly PMs for 2nd, 3rd, and 4th quarters for "Internal Ohmic" readings for all battery cells. However, DEF's Annual PM included these Internal Ohmic readings. Specific data was not recorded for for "AC Ripple Current for 125VDC West Bank and "Charger Ouput Voltage & Current" for 125VDC East Bank readings on Tiger Bay's 2013 Annual PM. However, this was due to a failure to document the readings, and readings taken since that time were found to be acceptable. No harm is known to have occurred. The batteries at Disston exceeded their maintenance interval by approximately 30 days. The risk to the BPS was minimized due to the following control measures that were in place during the 30 day lapse in maintenance: The Disston substation monitors low battery voltage on its batteries, with any existing alarms communicated automatically to the Energy Control Center (ECC). Also, communications between the ECC and the substation are monitored to identify any loss of communications. No call-out requests were initiated for battery alarms at Disston during the period of the lapsed maintenance. DEF also performs monthly visual substation inspections to identify issues. During these inspections field staff view conditions both in the switchyard and in the control house where batteries reside. No issues were identified with inspections with the Disston batteries during the period of the lapsed maintenance. No harm is known to have occurred. | To mitigate this issue, DEF: 1) completed the maintenance on both carrier units to bring them back into compliance; and 2) successfully added the secondary carriers to the DEF maintenance database; allowing the PMs to be generated and the prescribed maintenance to be accomplished within DEF's specified timeframe; 3) to prevent recurrence, added to the PRC-005 procedure inventorying 100% of substations every 5 years though the maintenance frequency is 6 years; 4) performed a cause analysis to determine the cause of these documentation issues. It was identified that there was unclear instruction in the procedure on using checklists and a failure to update the forms when a revision was issued; 5) developed required reading in Plantview for all DEF Maintenance Superintendents, Battery System Owners, and applicable maintenance supervisors on the new PRC-005-2 Battery Maintenance Procedure. Required reading was completed by the identified group related to the noncompliances; 6) ensured all sites have the current PM forms and that these forms are in the new tracking system. 7) completed the maintenance on Disston 230 kV Substation #1 Battery and #2 Battery; 8) issued & implemented the necessary Equipment Change Request to add the batteries to the DEF equipment data base, and removed details of the previously existing battery from the DEF equipment data base; and 9) developed a computer based required reading module on the equipment change request process. As of 12/27/2013 DEF maintenance supervisors, relay technicians and electricians completed the reading. In addition DEF performed an extent of condition review to determine if similar issues may exist elsewhere. Equipment maintenance on another line with the similar equipment configuration was in compliance.
2015-09-30 | Florida Reliability Coordinating Council (FRCC) | City of Homestead (HST) | NCR00037 | FRCC2015014727 | EOP-001-2.1b | R3; R3.1; R3.4 | On February 27, 2015, HST submitted a Self-Certification stating that as a BA and TOP, it had an issue of EOP-001-2.1b, R3.1 and R3.4. HST's Transmission Operator and Balancing Authority emergency plans did not include adequate communication protocols to be used during emergency situations; nor were staffing levels addressed with respect to emergency events. During the course of enforcement's determination review it was determined that HST should also better address EOP-001-2.1b R3.2 and R3.3, by including procedural references to "Transmission Operators" in its emergency communications, and resolving emergencies within "NERC-established timelines" as stated in the requirement. The root cause was determined to be human error in documenting HST's processes. The issue began in June 18, 2007, the date the Standard became mandatory and enforceable, and will end be when HST finishes its review process and signed-off as approved its new EOP-011 procedure, this step is anticipated to be completed on October 31, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. HST's emergency plans did not address communications, staffing levels, neighboring transmission operators, and NERC-established timelines. However, these issues were language specific problems related to the documentation of its plans, and not programmatic issues in meeting EOP-001 R3. Other HST plans directly related to the bulk power system, such as mitigating insufficient generating capacity, transmission emergencies, and load shedding were found to be adequate. Also, HST and its adjacent Balancing Authority were already part of a reserve sharing agreement that allows for external entities to provide assistance in emergency situations. No harm is known to have occurred FRCC determined that HST had no relevant compliance history. | To immediately mitigate this issue, HST sent memorandums to their System Operators to make them aware of immediate procedural changes to their EOP-001 Emergency Plan, addressing R3.1 thru R3.4: 1) Communications protocols to be used during emergencies; 2) Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines; 3) Tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities; and 4) Staffing levels for the emergency. To complete the final step of mitigation for this Self Certification, by October 31, 2015, HST will update its EOP Plans to reflect the changes outlined in the memorandum notifications.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Commonwealth Edison Company (ComEd) | NCR08013 | RFC2015015055 | EOP-004-2 | R2 | On June 24, 2015, ComEd submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue of EOP-004-2 R2. On Friday May 15, 2015 at approximately noon, a ComEd substation area operator, while performing a perimeter walk down, found a suspicious object on the ground inside the fence line of a 345kV to 138kV transmission substation. Following protocol, the area operator promptly reported the object to Transmission Operations, Corporate Security, and local police. ComEd notified PJM by phone of this possible EOP-004 reportable event on May 15, 2015. Approximately one hour after notifying local police, Corporate Security, Cook County Bomb and Arson Squad, local police, and fire personnel arrived at the station. The Bomb and Arson Squad determined that the object contained a transmitter, but not an explosive device. At approximately 3:45 PM, the suspicious object was turned over to the FBI for further analysis and the substation was given an “all clear.” On May 16, a joint investigation between ComEd corporate security and the FBI determined that the object may have been tied to a global space balloon challenge at a local middle school. On Monday May 18, the joint investigation confirmed that the suspicious object was part of a student’s space balloon that had inadvertently fallen into the substation yard with no nefarious intent. EOP-004 R2 and ComEd’s Operating Plan, OP-CE-1010, together require ComEd to report any EOP-004 reportable event within 24 hours, or by 4 PM on Monday if the event is not confirmed by the 4 PM Friday, to NERC, PJM, and ReliabilityFirst. ComEd notified NERC within 24 hours of the discovery of the reportable event, but did not notify PJM or ReliabilityFirst within 24 hours. The root cause of this noncompliance was ineffective training. The ComEd employees responsible for following the Operating Plan and making EOP-004 notifications to NERC, PJM, and ReliabilityFirst did not understand that the Operating Plan required them to notify PJM and ReliabilityFirst of the EOP-004 reportable event within 24 hours after the discovery of the event. The ComEd employees believed that they did not need to notify PJM or ReliabilityFirst because they had discovered that the suspicious object posed no risk within 24 hours of its identification. This belief is incorrect because the Operating Plan requires notifications to PJM and ReliabilityFirst within 24 hours with no exceptions. The duration of this noncompliance is from May 15, 2015, the date ComEd was required to comply with EOP-004-2 R2, to June 1, 2015, the date ComEd notified ReliabilityFirst of the reportable event. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. On May 15th, within three hours of discovering the suspicious object, ComEd Corporate Security determined the device was not explosive and posed minimal risk. EOP-004-2 R2 requirements and ComEd’s Corporate Security protocols required ComEd to report the event per its Operating Plan to NERC, PJM, and ReliabilityFirst by May 18th at noon. ComEd exceeded almost all of the requirements and protocols after identifying the issue by contacting ComEd Corporate Security, the Cook County Bomb and Arson Squad, the Cook County Fire Department, and having the FBI analyze the suspicious object. ComEd also contacted a local middle school to confirm that the suspicious object was part of a global space balloon challenge. ComEd made all of the contacts and confirmed that the suspicious object posed no threat and identified the source of the object all before May 18 at noon, the deadline by which ComEd was required to report that an event had occurred. No harm is known to have occurred. This is ComEd's first instance of noncompliance with EOP-004 R2. | To mitigate this issue, ComEd completed the following mitigation activities: 1) created two new email distribution lists to use when making notifications for reportable events. The first distribution list covers submission of EOP-004 Attachment 2 and includes all regulatory agencies required for EOP-004 reporting along with additional contacts in alignment with Operating Plan OP-CE-1010. The second distribution list covers submission of OE-417 forms (EOP-004 permits submission of OE-417 forms in lieu of EOP-004 Attachment 2). The second distribution list includes all regulatory agencies required for EOP-004/OE-417 reporting and additional contacts in alignment with Operating Plan OP-CE-1010; 2) clarified and improved its notification practices by revising its Operating Plan to add clarity regarding notifications; and 3) provided training to Transmission Operations Shift Managers on the applicable elements of the Operating Plan.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | EFS Parlin Holdings LLC (Parlin) | NCR10257 | RFC2014014484 | VAR-002-3 | R2 | On November 24, 2014, Parlin submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-3 R2. On October 9, 2014, the plant manager at Parlin observed that Parlin’s voltage was over the voltage scheduled provided to it by FirstEnergy, the Transmission Operator (TOP), on October 6, 2014 on the K1025 and G1047 transmission lines of the 230kV line. This observation occurred during routine monitoring of Parlin voltage metering versus metering in the FirstEnergy control building in the switchyard at the facility. After this observation on October 9, 2014, Parlin contacted FirstEnergy and informed them that Parlin was operating above its voltage schedule. After making this contact, Parlin reviewed voltage levels during other operating days during 2014 and discovered that it did not operate within its voltage schedule on 14 days between January 1, 2014 and October 16, 2014. Therefore, Parlin did not notify FirstEnergy that it was operating above its voltage schedule on those 14 days. These voltage excursions typically occurred during the late night and early morning hours. On October 20, 2014, Parlin received confirmation from FirstEnergy that Parlin had operated outside of its voltage schedule on October 9, 2014. The root cause of this noncompliance was poor workforce management due to ineffective training. Personnel at Parlin were not monitoring the generator’s voltage in comparison to its voltage schedule and not notifying FirstEnergy of deviations from the voltage schedule as VAR-002-3 R2 requires. The duration of this noncompliance is from January 1, 2014, the first date Parlin operated above its voltage schedule, to November 13, 2014, the date FirstEnergy granted Parlin’s request for an exemption from its voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Parlin is a small, 114 MW, generation facility. Voltage in the area is mostly controlled by larger generation units that are close to Parlin. Additionally, Parlin only operated at a maximum 2% deviation from its voltage schedule for a period of no more than two hours during any of its voltage excursions. The 2% deviation from the voltage schedule did not have a negative impact on generation and transmission equipment as neither the Transmission Owner nor TOP detected abnormal system voltage. Furthermore, PJM has since exempted Parlin form maintaining a voltage schedule. This is Parlin's first instance of noncompliance with VAR-002-3 R2. No harm is known to have occurred. | To mitigate this issue, Parlin: 1) Notified FirstEnergy of its deviation from its voltage schedule; 2) Reminded staff of the current voltage schedule and the requirement to notify the TOP, here FirstEnergy, any time Parlin cannot meets its voltage schedule; 3) Updated the VAR-002 procedures; 4) Conducted training for all operators on VAR-002-3 requirements, measures, and compliance protocols; 5) Requested an exemption from the voltage schedule from PJM; 6) Updated its VAR-002 compliance procedures to develop standard operation procedures for operating in power factor control and reporting deviations; 7) Trained employees on the new power factor schedule; 8) Updated the digital control system to perform a real-time power factor calculation to display to the screen with alarm points; and 9) Performed system recalibration at the direction of the manufacturer of the automatic voltage regulators to see if voltage control was possible. ReliabilityFirst has verified the completion of all mitigation activity.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | EFS Parlin Holdings LLC (Parlin) | NCR10257 | RFC2014014485 | VAR-002-3 | R1 | On November 24, 2014, Parlin submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-3 R1. On October 21, 2014, personnel at Parlin became aware for the first time that the generator’s automatic voltage regulators (AVRs) were not controlling for voltage. The AVRs were not controlling for voltage because they are not capable of voltage control due to technical limitations. The AVRs are only able to operate in a power factor control mode, controlling for reactive power, as the units were originally configured to go directly into power factor control upon breaker closure. Consequently, Parlin had not notified FirstEnergy, Parlin’s Transmission Operator (TOP), that its AVRs did not control voltage. Parlin does not presently have the physical equipment to control for voltage and operate in voltage control mode. The root cause of this noncompliance was poor workforce management, due to ineffective training and a failure to fully understand the requirements of the Standard. Personnel at Parlin did not know that the generator’s AVRs were not controlling for voltage, which shows ineffective training, and they did not fully understand that this inability to control for voltage was a violation, which shows personnel at Parlin did not fully understand the compliance obligations of VAR-002-3 R1. The duration of this noncompliance is from October 1, 2014, the enforcement date for VAR-002-3 R1, to February 26, 2015, the date Parlin completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Parlin is a small, 114 MW, generation facility. Voltage in the area is mostly controlled by larger generation units that are close to Parlin. VAR-002 mandates that each generator operate with its AVRs in-service and controlling voltage so that the generators can react accordingly to system events and prevent possible power collapse. Parlin’s AVRs that control for reactive power will provide voltage support to the Bulk Electric System during system events, however, more support would be provided by controlling voltage. Lastly, Parlin has not experienced an event where it was unable to support the system for a potential voltage collapse. This is Parlin's first instance of noncompliance with VAR-002-3 R1. No harm is known to have occurred. | To mitigate this issue, Parlin: 1) Notified FirstEnergy and PJM that when the Parlin generating units are operating, the generator’s automatic AVRs will not be in voltage control mode due to the technical limitation that the units can only operate in power factor control mode; 2) Updated its VAR-002 site compliance procedures; 3) Conducted training for all operators on the requirements, measures, and specific compliance protocols related to VAR-002-3; 4) Obtained a power factor schedule from FirstEnergy to replace its voltage schedule; 5) Updated its VAR-002-3 procedure to reflect this new power factor schedule and will create standard operating procedures for the power factor schedule; 6) Provided operator training on the power factor schedule and protocols; 7) Updated the digital control system to perform a real-time power factor calculation to display to the screen with alarm points to reflect the new power factor schedule; and 8) Performed system recalibration after having discussions with the original equipment manufacturer regarding the AVRs’ current voltage control limitations and other options. ReliabilityFirst has verified the completion of all mitigation activity.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power Rock Springs, LLC (EPRS) | NCR00251 | RFC2015014821 | PRC-005-1.1b | R2 | On March 31, 2015, EPRS submitted a Self-Certification stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. During a review of battery maintenance records for its April 1, 2015 Self-Certification, the Compliance Department at EPRS discovered that EPRS did not complete its monthly battery maintenance for October 2014 by the due date of November 5, 2014. EPRS defines monthly maintenance as a calendar month plus five days. EPRS completed its monthly battery maintenance for October 2014 on November 9, 2014. EPRS also discovered on January 13, 2015 that it failed to complete its fourth quarter battery maintenance for 2014 by the due date of January 1, 2015. EPRS defines quarterly maintenance as a calendar quarter plus ten days. EPRS completed its overdue quarterly maintenance on the same day it was discovered: January 13, 2015. The root cause of this noncompliance concerned the workforce management and verification management practices. Workforce management was implicated from personnel not being properly trained to ensure that maintenance was performed timely. Verification was implicated from not ensuring the battery maintenance was performed in accordance with EPRS’ testing procedures. The duration of this noncompliance is from November 5, 2014, the date EPRS was required to complete its monthly battery maintenance for October 2014, to January 13, 2015, the date EPRS completed all of its overdue maintenance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EPRS quickly discovered and remediated the overdue maintenance. EPRS discovered and completed the October monthly battery maintenance four days after its required due date and completed the fourth quarter battery maintenance for 2014 three days after its required due date. EPRS also completed its December 2014 monthly battery maintenance on time. EPRS successfully completed all other monthly and quarterly battery maintenance activities in 2014 on time. No harm is known to have occurred. EPRS has a prior violation of PRC-005-2, RFC2011001263. A Settlement Agreement covering violation of PRC-005 R2 was filed with FERC under NP13-12-000 on December 31, 2012. On January 30, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. EPRS’ prior violation and the instant noncompliance both share a similar root cause of ineffective training, but the instant violation is an isolated incident. The prior violation involved EPRS repeatedly not following maintenance and testing intervals for 23 relays, not testing certain devices that needed to be tested, and not providing evidence that maintenance and testing procedures were completed. In contrast, the instant noncompliance involves EPRS completing its October 2014 battery maintenance and testing four days late and its fourth quarter battery maintenance and testing for 2014 three days late. The instant noncompliance involved two isolated incidents of overdue testing that were promptly identified and remediated. As a result, ReliabilityFirst did not consider EPRS’ violation history as a factor warranting an alternative disposition method under the circumstances of the instant violation. | To mitigate this issue, EPRS: 1) Discussed the overdue maintenance and provided retraining on the importance of meeting the testing deadlines and the maintenance activities with the employee in charge of battery maintenance; 2) Changed the work order release date from 30 days after the completion of the previous months work order to every 30 days; and 3) Provided refresher training to EPRS staff on PRC-005 testing requirements and their intervals, including how EPRS defines monthly, quarterly, and annual.
2015-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power Rock Springs, LLC (EPRS) | NCR00251 | RFC2015014864 | VAR-002-2b | R2 | On April 9, 2015, EPRS submitted a Self-Report stating that, as a Generator Operator, it had an issue of VAR-002-2b R2. In preparation for its April 1, 2015 Self-Certification, EPRS identified that it failed to maintain its 500kV switchyard voltage within the target and associated bandwidth provided by its Transmission Owner (TOP), GridForce Management (then Constellation), 12 out of 15 times when EPRS’ generating units were online from January 25, 2014 to May 6, 2014. On all 12 of the occasions where EPRS did not maintain voltage within the bandwidth set out in EPRS’ voltage schedule, EPRS failed to notify its TOP of its voltage excursions as required by VAR-002. These voltage excursions occurred while the Plant Information (PI) voltage data point had locked up, was not updating its current status, and had not been identified by plant personnel. The PI data point is present and visible at the generation control room console to make monitoring voltage easier. Because the PI voltage data point had locked up and was not updating its current status, EPRS plant personnel would not have known they were exceeding their voltage schedule unless they were actively monitoring, which they were not, the switchyard voltage from the transmission control room terminal in the adjacent room. The root cause of this noncompliance concerned workforce management and verification. Workforce management was implicated because personnel at EPRS were not trained to understand if the PI voltage data point had locked up and was not updating its current status. Verification was implicated because EPRS did not confirm that that the PI voltage data point was working as designed by actively monitoring the switchyard voltage from the transmission control room terminal in the adjacent room. The duration of this noncompliance is from January 25, 2014, the date of EPRS’ first deviation from its voltage schedule, to April 30, 2015, the date EPRS notified its TOP of its voltage excursions and requested an expanded voltage schedule from the TOP to align with Peach Bottom’s voltage schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The voltage schedule for the EPRS 500 kV bus at the time was 533 kV with the voltage schedule at the Peach Bottom 500 kV bus at 538 kV. Peach Bottom consists of two large nuclear generating units directly connected to the EPRS substations by the 5014 500 kV line. The higher voltage schedule of 538 kV at Peach Bottom would impact EPRS’ ability to hold its voltage to 533kV. At the time of the violation, there was an inherent difference in the allowable high voltage threshold between the EPRS (533 kV) and Peach Bottom (538 kV) generating plants. In all cases where EPRS was above its bandwidth, the EPRS switchyard voltage was below the 538 kV Peach Bottom threshold. Since voltages in the immediate area of EPRS are driven largely by the 2 nuclear units at Peach Bottom, EPRS cannot significantly influence its voltage profile. In October 2014, EPRS received approval for an expanded voltage schedule and bandwidth that now provides the full 500 kV normal operating range (500-550 kV). Under the new expanded bandwidth, EPRS would never have been in violation. No harm is known to have occurred. This is EPRS' first instance of noncompliance with VAR-002 R2. | To mitigate this issue, EPRS will complete the following mitigation activities by March 1, 2016: 1) Request an expanded voltage schedule to align with Peach Bottoms’ voltage schedule, which is at the far end of one of the transmission lines leaving EPRS; 2) Add alarm points to the generation human-machine interface (“HMI”) to inform the operator that the generator unit is approaching the voltage schedule limit. These alarm points will ensure that EPRS operators are informed when the generator unit is approaching the voltage schedule limit even if there is an issue with the PI data; 3) Create a calculated point in the PI data that measures the 15 minute average voltages on the 500 kV switchyard buses and provides an alarm to the operator when the average approaches the voltage schedule limit; 4) Analyze how to prevent PI data from getting stale and not updating and to determine an effective method to alert EPRS operators of an alarm when the operators are outside of the control room; and 5) Conduct staff training to reinforce VAR-002 monitoring obligations. EPRS needs until March 1, 2016 to complete all of its mitigating activities because completing Milestones 4 and 5, prevent PI data from getting stale and not updating and training all relevant staff to reinforce VAR-002 monitoring, together will take an extended amount of time.
2015-09-30 | SERC Reliability Corporation (SERC) | The Dow Chemical Company (Dow) | NCR09037 | SERC2014013845 | PRC-005-1.1b | R2 | On February 3, 2014, SERC sent Dow a notice of a Compliance Audit scheduled for June 2, 2014. On May 14, 2014, Dow submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1.1b R2. Dow stated it was unable to produce evidence that battery maintenance had been performed in accordance with its Protection System maintenance and testing program. Dow schedules its Protection System maintenance and testing using its computer-based maintenance planning tool (CBE-PPM). CBE-PPM is used company-wide to establish the maintenance frequencies for electrical equipment. CBE-PPM populates a maintenance database that is used to create work orders and maintain documentation. While preparing documentation for its upcoming audit, Dow was not able to locate records for semi-annual and annual battery maintenance and testing that should have been performed in June and December of 2013. Dow believes that CBE-PPM did not create the expected work orders for battery maintenance in June and December of 2013. Dow has determined that all 32 station batteries were involved. SERC determined that Dow failed to provide evidence that 32 out of 32 (100%) batteries and 32 out of 836 (3.8%) total Protection System devices were maintained and tested within the defined intervals. This issue lasted from July 1, 2013, the first day after June 2013 when the six month battery maintenance and testing should have been performed, until July 31, 2014, when Dow completed its mitigation activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Dow employees perform twice-daily walk-by battery inspections and monthly inspections that should have detected battery problems. All batteries are equipped with ground detectors and some are equipped with low voltage alarms. Dow’s 12 generation units operate primarily for steam production and cogeneration of approximately 1,000 MW of electricity is available for sale to the local utility under a Public Utility Regulatory Policy Act contract, in which the output of the Dow units cannot be adjusted by the local utility. The generators interconnect to the transmission provider through a single ring bus. If a battery problem had developed, its impact would have been localized. Also, Dow did not identify any problems with the missed batteries while performing scheduled maintenance and testing for 2014. No harm is known to have occurred. SERC considered Dow’s PRC-005 R2 compliance history in determining the disposition track. Dow’s relevant prior noncompliance with PRC-005 R2 includes: NERC Violation ID SERC200700053. SERC determined that Dow’s compliance history should not serve as a basis for applying a penalty. The prior issue involving PRC-005 R2 involved a failure at the start of the mandatory and enforceable period of PRC-005 to include one of Dow’s units in its Protection System maintenance program after purchasing the unit in 2006. The current issue involved a failure to perform semi-annual and annual maintenance on batteries resulting from the failure of its CBE-PPM to create the expected work orders. Dow had alarms on some of the batteries that would alert in the event of low voltage and conducted twice-daily walk-by inspections and monthly inspections that would have identified problems with the batteries. The prior Mitigation Plan would not have prevented the current issue. Dow completed the missed maintenance activities within approximately two months of self-reporting the issue to SERC. Dow also has a compliance assurance system, conducts self-assessments and internal audits, and has tools to help ensure compliance. | To mitigate this issue, Dow: 1) labeled equipment IDs in global engineering and maintenance tracking system (GEMTS) as NERC registered equipment; 2) identified service schedules as compliance items; 3) created a new GEMTS NERC-specific report to enable responsible roles to schedule services; and 4) modified GEMTS service schedules to ensure a new service will come due annually on the same date.
2015-09-30 | SERC Reliability Corporation (SERC) | Virginia Electric and Power Company – Fossil and Hydro (GO, GOP) (VEP-FH) | NCR09028 | SERC2014014523 | PRC-005-1a | R2 | On December 17, 2014, VEP-FH submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-1b R2. VEP-FH failed to test and maintain all Protection System devices in accordance with its Protection System program. SERC later determined that the issue dated back to Version 1a of the Standard. While investigating the extent of condition for a unit trip that occurred on August 28, 2014, VEP-FH determined that it could not locate a complete set of maintenance and testing records for certain auxiliary relays installed on several units. VEP-FH had not included these relays in its PRC-005 Protection System maintenance and testing program, and as a result, VEP-FH could not locate complete records for these devices. VEP-FH had maintained these devices, but not according to the requirements of the VEP-FH Protection System maintenance and testing program. VEP-FH failed to include these relays in the program because when it established the program, it reviewed protective relay drawings to identify the devices that needed to be included, and the drawings did not include these specific relays. Instead, VEP-FH included these relays on drawings associated with the voltage regulator. VEP-FH used these trip relays to collect all trip signals that originated from the voltage regulator, its firing module (where applicable), and field overvoltage protection. In addition to collecting the trip signals, these trip relays served as an interposing relay between the excitation system controls and the main trip circuits for the generator breaker. SERC determined that these auxiliary relays did not function as Protection System devices and thus VEP-FH was not required to include the relays in its Protection System maintenance and testing program. While reviewing records to complete SERC’s request for information for the Self-Report, VEP-FH discovered that an additional three relays and three DC control circuits on two different generators were not maintained and tested within their defined intervals. VEP-FH scheduled testing for one relay and one DC circuit at one generator during a November 2008 outage along with other relays. The relay technician responsible for conducting the testing elected not to test the devices because VEP-FH previously tested them in December 2007. The technician generated a white sheet and noted on it that testing occurred in December 2007. VEP-FH failed to note that the testing was not conducted as scheduled. VEP-FH incorrectly indicated in its compliance tracking system that these devices had been maintained and tested as scheduled. As a result, VEP-FH missed the December 5, 2011 deadline for testing and maintaining these Protection System devices. VEP-FH scheduled the two relays and two DC circuits for the other generator to be tested during a fall 2013 outage. The relay technician responsible for the work was unfamiliar with the devices and failed to perform the scheduled testing. The relay technician generated white sheets for the devices and submitted these white sheets to VEP-FH for review and document storage. On these white sheets, the relay technician noted that the devices were not tested, but VEP-FH failed to notice these notations. VEP-FH incorrectly indicated in the compliance tracking system that these devices had been maintained and tested as scheduled. As a result, VEP-FH missed the April 16, 2014 deadline for testing and maintaining these devices. SERC reviewed an inventory spreadsheet compiled by VEP-FH which included a complete list of Protection System devices, the defined intervals, and most recent and prior maintenance and testing dates. SERC determined that VEP-FH did not perform maintenance and testing within the defined interval for three of 1,501 (0.2%) protective relays and three of 1,501 (0.2%) DC control circuitry devices. In total, VEP-FH could not provide evidence that six of 4,160 (0.14%) Protection System devices were maintained and tested within the defined intervals. This issue lasted from December 6, 2011, the first date of exceedance of an interval, through April 8, 2012, when VEP-FH performed testing and maintenance on the devices at the first generator, and from April 17, 2014, the second date of exceedance of an interval, through April 17, 2015, when VEP-FH completed its mitigation activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. VEP-FH’s failure to test and maintain relays and DC control circuits could lead to Protection System devices not operating as designed, which could cause a unit to trip unexpectedly or require reliance on the Transmission Owner’s Protection System devices to respond to a fault. A failure of one of the devices involved in this issue could potentially cause a loss of generation ranging from 234 MW to 580 MW. However, VEP-FH is a member of the PJM Regional Transmission Organization, which has a total installed generation capacity of 179,229 MW. Therefore, the loss of one of these generating units would represent no more than 0.32% of the generation capacity within PJM. VEP-FH did not experience any false trips or any other problems with the devices during this issue. No harm is known to have occurred. SERC considered VEP-FH’s PRC-005 R2 compliance history in determining the disposition track. VEP-FH’s relevant prior noncompliance with PRC-005 R2 includes: SERC200900270. SERC determined that VEP-FH’s compliance history should not serve as a basis for applying a penalty. The prior issue involved a failure to complete approximately 20 percent of VEP-FH’s total preventative maintenance activities on batteries in 2009, while the instant issue began more than two years after the mitigation of the prior issue and involves a failure to test and maintain 0.2 percent of VEP-FH’s relays and 0.2 percent of VEP-FH’s DC control circuits within the defined intervals. The instant issue occurred because of human error in documenting whether maintenance and testing occurred as scheduled and does not represent ongoing or repetitive noncompliance. | To mitigate this issue, VEP-FH: 1) added a layer of review and confirmation of all protection device testing and maintenance completion and evidence collection for all devices included in the PSMP. The process now consists of duel (two employees) redundant confirmation of completion. The final confirmation check will be conducted by an employee directly reporting to the Dominion manager of power generation regulatory compliance; 2) initiated the process change, communicated the change verbally, and distributed the revised compliance program guidance document on protection system maintenance and documentation; and 3) completed testing the devices involved. SERC has verified the completion of all mitigation activity.
2015-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2015015120 | VAR-002-4 | R2; R2.2 | On July 31, 2015, AECC submitted a Self-Certification stating that, as a Generator Operator, it had a minimal risk instance of noncompliance with VAR-002-4 R2; R2.2. On May 27, 2015, between 09:01 and 15:40, AECC did not maintain the generator voltage schedule provided by its Transmission Operator (TOP) at its Electric Cooperatives of Arkansas hydroelectric generating station (ECA station), nor did it notify its TOP of the deviation from the voltage schedule. AECC’s TOP required AECC to maintain a non-summer voltage schedule from September 16, 2014 – May 26, 2015. At 00:01 on May 27, 2015, AECC was scheduled to change to a summer voltage schedule. AECC’s plant operators did not transition from the non-summer voltage schedule to a summer voltage schedule. Nevertheless, the plant voltage was within the allowable voltage tolerance between 00:01 until 09:01. AECC plant operators implemented the summer voltage schedule at 15:40 that same day. The SPP RE determined that the minimal risk instance of noncompliance began on May 27, 2015 at 09:01, the time the plant voltage was outside the bandwidth provided by AECC’s TOP, through May 27, 2015 at 15:40, when AECC began maintaining the correct plant voltage. The root cause of the instance of noncompliance was failure to use existing controls. The ECA station does not have staff on-site. Instead, it is controlled from an off-site control center (McClellan). The schedule for the ECA station had not been physically posted in the McClellan plant, nor had the schedule been updated on AECC’s plant voltage webpage | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure of AECC to maintain its voltage schedule could have resulted in unacceptable bulk power system voltage in the vicinity of the ECA generating station. In this instance system voltage did not deviate from acceptable norms. AECC’s non-summer voltage and summer voltage schedules are similar and only differed by 3.45kV during on-peak hours. AECC deviated from its voltage schedule a total of 6.75 hours, and the issue was corrected the same day. Finally, no harm occurred as a result of this issue. A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including AECC’s noncompliance with VAR-002-1 R2; R2.2 (SPP2014013570) and VAR-002-2 R2; R2.2 (SPP2014014420) was posted on the NERC website on May 28, 2015. The 60-day review period passed on July 30, 2015. SPP RE considered this compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the VAR-002 issue was isolated and not systemic. The facts and circumstances of the prior issue of non-compliance did not mirror the circumstances that caused the current instance of non-compliance. | To mitigate this minimal risk instance of noncompliance, AECC: 1) Reviewed voltage web pages at each plant on May 27, 2015 to confirm the “Summer Schedule” schedules had been implemented at each plant in the Entergy control area. 2) Added a preventative maintenance task , on July 21, 2015, to the Computerized Maintenance Management System (CMMS) at each plant with a voltage schedule that changes seasonally to automatically email reminders when the schedule is about to change. The reminder emails are sent to the Plant Manager, the Assistant Plant Manager, and the plant operations email account at each facility two (2) days prior to the date that the voltage schedule changes. The Director Power Production is also copied on each notification email. The notification email reminds all parties that the voltage schedule is about to change and that the Plant Manager is responsible for making necessary changes to the AVR and ensuring plant operators are aware of the schedule change. The Plant Manager is responsible for updating the preventive maintenance task whenever he or she receives notification that the voltage schedule for the facility has changed. SPP RE has verified the completion of all mitigation activity.
2015-09-30 | Texas Reliability Entity (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT ISO) | NCR04056 | TRE2015014748 | PER-004-2 | R1 | On March 13, 2015, ERCOT ISO submitted a Self-Report stating that, as a Reliability Coordinator (RC), it had an issue with PER-004-2 R1. ERCOT ISO failed to ensure that it was staffed with NERC-certified RC operators, 24 hours per day, seven days per week. Specifically, a system operator had completed all required training but failed to meet his responsibility to submit the administrative fee to renew the NERC certification. The system operator continued to work 39 shifts over a three and a half month period without possessing a valid NERC certification as a result of the failure to submit the requisite certification renewal fee. The root cause was determined to be ERCOT ISO’s limited access to the NERC System Operator Certification and Continuing Education Database (SOCCED). While ERCOT ISO monitors the aspects of credentialing that could be monitored in SOCCED, ERCOT ISO does not have access to the SOCCED records associated with administrative fee payments. According to ERCOT ISO, the failure to remit payment was most likely an oversight. Texas RE determined the issue duration to be from September 6, 2014, the day after the NERC Certification expired, until December 22, 2014, when the system operator was removed from duty. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The system operator received all necessary training required to renew the NERC certification, but failed to submit the renewal fee. Additionally, the system operator had been certified for 11 years prior to the expiration of the certification. Furthermore, the operator earned a total of 228 Continuing Education Hours (CEHs) within the time period of February 2012 and July 2014, which exceeds the minimum number of CEHs necessary for Credential Maintenance/Certification. Lastly, ERCOT ISO asserts that the system operator was supervised at all times by the Shift Supervisor, who is a NERC Certified System Operator. No harm is known to have occurred. Texas RE considered ERCOT ISO’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ERCOT ISO: 1) removed the system operator from duty until the renewal payment was made; 2) verified that all other system operator certificates were current; 3) verified that all current system operators maintained the necessary NERC certification continuously for the past three years; and 4) enhanced the departmental process to monitor upcoming system operator NERC certification deadlines, including an automated monthly assessment in the AlertEnterprise GRC tool. Texas RE has verified the completion of all mitigation activity.
2015-09-30 | Texas Reliability Entity (Texas RE) | Electric Reliability Council of Texas, Inc. (ERCOT ISO) | NCR04056 | TRE2015014582 | COM-002-2 | R2 | On January 26, 2015, ERCOT ISO submitted a Self-Report stating that, as a Balancing Authority (BA), Reliability Coordinator (RC), and Transmission Operator (TOP), it had two issues with COM-002-2 R2. Specifically, ERCOT ISO explained that in issuing two directives, it failed to have the recipient of the directives repeat the information back correctly. In both instances, the recipient acknowledged the directive and the two communications resulted in the expected system and generation performance. The root cause for both non-compliance instances was human error by failing to ensure the recipient of the directives repeated the information back correctly. The issue duration was for approximately an hour on October 9, 2014, when the ERCOT ISO System Operator failed to have the recipient of a directive repeat the information back correctly during the first instance until the time the ERCOT ISO System Operator did not require a repeat back during the second instance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. Both ERCOT ISO directives were issued in a clear, concise, and definitive manner resulting in the expected system and generation performance. ERCOT ISO was also capable of easily contacting the GOP to remedy the situation if either of the directives had been implemented incorrectly or generation and system performance had deviated from expectations. No harm is known to have occurred. Texas RE considered ERCOT ISO’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ERCOT ISO: 1) ended the issuance of the directive of the second instance; and 2) developed an updated training module to provide to operators with lessons learned from this event. Attendees included all ERCOT ISO System Operators. Texas RE has verified the completion of all mitigation activity.
2015-09-30 | Texas Reliability Entity (Texas RE) | Texas Municipal Power Agency (TMPA) | NCR04141 | TRE2015015128 | PRC-005-2 | R1; R1.1; R1.2 | On August 5, 2015, TMPA submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue with PRC-005-2 R1. TMPA failed to establish a basis for testing its Protection Systems within its Protection System Maintenance Program (PSMP) for its Protection Systems. Specifically, TMPA’s PSMP did not address which maintenance method (time-based or performance-based) would be used for each Protection System Component Type. TMPA’s PSMP also did not include maintenance intervals consistent with the maintenance intervals specified in PRC-005-2, Tables 1-1 through 1-5 and Table 2 for the monitored Component attributes for each of its batteries. The root cause of the issue was the significant turnover of essential experienced personnel, including a vacancy in the Compliance Officer position and the retirement of the subject matter expert (SME) responsible for ensuring compliance with applicable maintenance standards for Protection Systems. Due to this break in staff continuity, there was a lapse in assigning and then providing adequate training for a new Compliance Officer and SME responsible for ensuring compliance with the applicable maintenance testing interval standards, including monitoring changes to those standards. Texas RE determined the issue duration to be from April 1, 2015, when PRC-005-2 became effective, until September 11, 2015, when TMPA revised its PSMP to align with PRC-005-2 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although TMPA failed to update its PSMP to include a time-based or performance-based maintenance method, in practice TMPA complied at all times with PRC-005-2’s time-based maintenance interval requirements. Specifically, TMPA’s existing Maintenance and Testing Program included time-based maintenance intervals for its equipment which, with the exception of the testing intervals for batteries, were shorter than required. With regard to battery maintenance intervals, TMPA stated that although its documented time-based battery maintenance intervals exceeded the corresponding PRC-005-2 intervals, TMPA actually implements maintenance and testing that complies with the required maintenance intervals. No harm is known to have occurred. Texas RE considered TMPA’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TMPA: 1) revised its PSMP document; 2) developed a new PSMP in accordance with the PRC-005-2 Standard; 3) added new personnel, including a Compliance Officer and an SME tasked with improving TMPA’s internal processes; 4) created a working group tasked with reviewing the status of all applicable NERC Standards; 5) implemented additional available features in an existing compliance database to ensure that review and improvement of internal processes are done in a timely manner; and 6) implemented additional available features in the Computerized Maintenance Management System to ensure compliance with TMPA’s Maintenance and Testing Program. Texas RE has verified the completion of all mitigation activity.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC2015014895 | PRC-005-1b | R2.1 | On March 2, 2015, PGAE submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it had an issue of PRC-005-1b R1. PGAE reported that it failed to complete maintenance and testing on batteries at the Spring Gap Power House due to a miscommunication after PGAE updated its Protection System Maintenance and Testing Plan (“PSMP”). WECC determined that the missed maintenance should have been reported under PRC-005-1b R2. PGAE’s PSMP requires that valve-regulated lead acid (“VRLA”) batteries be maintained using semi-annual resistance tests. The VRLA battery at the Spring Gap Power House was missed for several intervals between and including the first half of 2012 and the first half of 2014. WECC determined that PGAE’s failure to test one battery in accordance to its PSMP is a compliance exception of PRC-005-1b R2.1. The compliance exception began on July 2, 2012, when PGAE should have maintained and tested the battery in accordance with its PSMP, and is currently ongoing until its anticipated mitigation activity completion date of November 2, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PGAE failed to maintain one battery within the interval required by PGAE’s PSMP. The missed battery was the secondary source for DC power, and the battery charger was the primary. Also, PGAE’s PSMP had been updated to change the testing interval to semi-annual. While PGAE failed to meet this testing interval, PGAE had nonetheless continued to test and maintain the battery on an annual interval. Finally, PGAE failed to perform maintenance and testing on a single battery, out of 283 protection system batteries. WECC considered PGAE’s PRC-005 R2 compliance history in determining the disposition track. Previously, in Violation ID# WECC200901422, PGAE failed to maintain and test 92 protection system devices according to its PSMP interval, out of over 1200 devices. However, PGAE completed mitigating activities for the prior violation in 2009. Because of the age of the previous violation, WECC determined that PGAE’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, PGAE will complete the following mitigation activities by November 2, 2015: 1) review PGAE change management process, including communication methods, to ensure that updates specific to protective system maintenance are implemented effectively and timely; 2) Power Generation will review all station DC supplies to determine if other VRLA batteries require testing; and 3) Power Generation will conduct tailboards with all appropriate personnel to ensure that maintenance plans for batteries are accurate and up-to-date in SAP-WM, which is used to schedule and track maintenance work. PGAE's mitigation plan will require until November 2, 2015, because the review of all station DC supplies is time and personnel intensive.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Shiloh Wind Project 2, LLC (SWPII) | NCR10292 | WECC2015014574 | PRC-005-1.1b | R2 | During a Compliance Audit conducted from January 14 through January 15, 2015, WECC determined that SWPII, as a Generator Owner, was in non-compliance with PRC-001-1.1b R2. According to the Audit Team, SWPII provided documentation of its Protection System maintenance and testing program, and implementation of the program. However, the Audit Team determined that SWPII did not provide evidence that it had maintained and tested one communication system associated with a transfer trip scheme. The device is one of eighteen eligible devices in SWPII’s maintenance and testing program. SWPII recorded a prior test date for its SEL-2032 Communications Processor and associated communications circuit as of May 9, 2008. SWPII also provided evidence that the device was tested in 2013, as part of a neighboring entity’s transfer trip test that included SWPII’s fiber line. However, the documentation of that load check did not, in itself, demonstrate a successful test of the SEL-2032 Communications Processor and associated communications circuit; and, the document did not comply with the "Minimum Maintenance Activity" set out in SWPII’s maintenance and testing program. In addition, SWPII produced two one-line diagrams showing the communications paths in its system, but the Audit Team determined the diagrams and the neighboring entity’s load check together did not constitute a maintenance record, in compliance with PRC-001-1b R2. The root cause of SWPII’s compliance exception is a lack of compliance process to ensure that SWPII tests and maintains each protection system device according to SWPII’s maintenance and testing program, and that SWPII documents the results of that testing. The compliance exception started on May 10, 2014 (six years and one day after the Prior Test Date of the SEL-2032 communications system, which has a six year defined interval), and is ongoing until December 31, 2015, SWPII's anticipated mitigation activity completion date. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, SWPII did not maintain and test one communications system device. Although the testing was not complete, SWPII had evidence of some testing from 2008 and 2013. No harm is known to have occurred. WECC considered SWPII’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this compliance exception, by December 31, 2015, SWPII will: 1) Have the SEL-2032 Communications Processor and associated communications circuit tested; 2) Document the testing results according to SWPII’s maintenance and testing program; and 3) Modify SWPII’s Statement of Work (SOW) for 3rd party relay testing companies to include clear and concise testing results of Communications Processors associated with the facilities Protection Scheme.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Tri-State Generation and Transmission Association, Inc. - Reliability (TSGT) | NCR10030 | WECC2015014630 | PRC-001-1 | R3 | On February 11, 2015, TSGT submitted a Self-Report stating that, as a Generator Operator and a Transmission Operator (TOP), it was in possible non-compliance with PRC-001-1 R3. WECC reviewed the Self-Report, and conducted interviews with TSGT’s compliance staff, and determined that TSGT was in non-compliance with PRC-001-1 R3, because it had not coordinated its new protective systems and protective system changes with its neighboring Transmission Operators and Balancing Authorities, for three different generation plants, below. • Rifle Station. In May, 2012, TSGT installed new relays at the Rifle Generating Station (four units), but did not coordinate the changes with the TOP (Xcel Energy) or the Host Balancing Authority (BA) (Xcel Energy). TSGT notified the relevant personnel at Xcel Energy of the changes in December, 2012. • Craig Station. In May, 2012, TSGT installed a Unit 3 GSU neutral relay and the SEL-300G generator protection relay at the Craig Station, Unit 3; but did not coordinate the changes with the Host Balancing Authority (Western Area Power Administration). TSGT did coordinate the changes with the Transmission Operator (Tri-State), because the generation engineer overseeing the installation was working with transmission. • Nucla Generating Station. On September 27, 2014, a Generator Protection System Misoperation occurred at the Nucla Generating Station. While carrying out corrective actions in October and November of 2014, TSGT made changes to the 110% over voltage time delay setting, to implement changes that will be required by PRC-024. However, TSGT did not coordinate these changes in advance with the Transmission Operator (Tri-State) and Host Balancing Authority (Western Area Power Administration). The root cause for the instances of non-compliance at the Rifle and Craig Stations was the lack of an effective transition procedure when an employee changed jobs, and the following communication breakdown. TSGT did not have assigned ownership as to which department within the company is responsible for communicating with the TOP and BA. The root cause for the instance of non-compliance at the Nucla Generating Station was a lack of compliance understanding, because the engineer who implemented the protective system changes did not believe there would be an impact on transmission facilities, and therefore did not coordinate the changes with the Transmission Operator. The compliance exception started on May 31, 2012, the date Tri-State failed to coordinate nw protective systems and changes with the appropriate neighboring entities, and ended on July 31, 2015, when it completed its mitigation activities. | This compliance exception posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system. Specifically, TSGT failed to coordinate protection system relay settings at three generation plants with the applicable TOPs and BAs. TSGT implemented preventative and detective controls by conducting reviews of all capital projects in the year prior to implementation for any compliance impacts. Additionally, TSGT also assigns the standard owner as the project manager lead for projects involving relay setting changes. TSGT implemented other compensating controls. Specifically, TSGT implemented partial backup protection for two of the generation plants, with transmission-side distance relays looking back into the generation plant GSUs for possible faults, and one of the plants with a distance relay looking past the GSU and into part of the 220 kV bus. As a corrective control, TSGT sent email notifications to the appropriate entities identifying the relay settings changes shortly after it discovered its lack of coordination. No harm is known to have occurred. WECC considered TSGT’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, TSGT: 1) Made proper notifications to entities not initially informed per PRC-001-1.1 R3.1, 2) Streamlined internal process for coordinating with the Transmission Operator(s) and Host Balancing Authorities so that the Generation line of business will be responsible for performing this activity going forward, 3) Developed a protection system change control and coordination procedure to more clearly and effectively manage coordination. Procedure shall include internal notification process of protection system changes, but the external notification process as well, and 4) Provided training to ensure relevant generation personnel are aware of the new procedure and its location, as well as what is required of them.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2015014758 | EOP-001-2.1b | R5 | On March 19, 2015, EWEB submitted a Self-Report stating that, as a Transmission Operator, it was in possible non-compliance with EOP-001-2.1b R5. On April 13, 2015 through April 24, 2015, WECC conducted a Compliance Audit of EWEB’s facilities, where the WECC Audit Team reviewed the Self-Report and interviewed EWEB compliance staff. The WECC Audit Team determined that EWEB had a possible issue with EOP-001-2.1b R5, for its failure to provide its updated emergency plans to its Reliability Coordinator, neighboring Transmission Operators, and Balancing Authorities. Specifically, in calendar year 2013, although EWEB did provide its Restoration Plan to the Reliability Coordinator, it did not provide all applicable updated emergency plans to the Reliability Coordinator, Balancing Authority and adjacent Transmission Operators. WECC Enforcement reviewed the Self-Report and the Audit Team’s findings and confirmed that EWEB had a compliance exception with EOP-001-2.1b R5, for its failure to provide its updated emergency plans to its Reliability Coordinator, neighboring Transmission Operators and Balancing Authorities in calendar year 2013. The root cause of this compliance exception was EWEB's lack of a compliance process to ensure that its updated emergency plans were timely distributed to the applicable entities. The violation started on January 1, 2014, the first day after calendar year 2013, and ended on January 30, 2014. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, EWEB did not provide its updated emergency plans to its Reliability Coordinator, neighboring Transmission Operators and Balancing Authorities for calendar year 2013. EWEB distributed its updated emergency plans at least once per calendar year before and after the period of non-compliance in 2012, 2014, and 2015, to its Reliability Coordinator, neighboring Transmission Operators and Balancing Authorities. In addition, the compliance exception was limited to 29 days in 2014. No harm was known to have occurred. WECC considered EWEB's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this compliance exception, EWEB: 1) will reviewed and updated as appropriate its EOP-002 Capacity and Energy Emergencies procedure; 2) reevaluated its overall approach to compliance with EOP-001 R5 - the annual review, update and submittal of all EOP implementing documents; and 3) upon completion, established automated AssurX Tasks to ensure the execution of these new tasks each year.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2015014900 | PRC-004-2.1a | R1 | During a Compliance Audit conducted from April 13, 2015 through April 24, 2015, WECC determined that EWEB, as a Transmission Owner and Distribution Provider, had a compliance exception with PRC-004-2.1a R1, for its failure to implement a Corrective Action Plan to avoid future Misoperations for the Weyco 2 relay Misoperation that occurred on July 13, 2014. The WECC Audit Team conducted interviews with EWEB’s compliance staff to better understand the July 13, 2014 event. According to the Misoperations Report for 3Q 2014, EWEB reported that lightning caused a Ground Potential Rise (GPR) in the Pilot Wire circuit, opening the Pilot Wire Relay. EWEB stated that over the last several years, EWEB has replaced several high-risk older generation relay communication circuits with fiber, using a risk-based approach. Lightning has not been deemed to be an “essential risk” to pilot wire relays in this area of the EWEB Transmission System. EWEB’s Corrective Action Plan was to continue to monitor the pilot wire relay for lightning-caused Misoperations, and if it occurs again at this site, then EWEB would replace the HBC-1 pilot wire relays with fiber. EWEB timely submitted its 3Q 2014 Misoperations report for the Weyco 2 Substation incident; however, the WECC Audit Team determined that the Corrective Action Plan did not adequately address activities designed to avoid future Misoperations of a similar nature. Enforcement reviewed the Self-Certification and the Audit Team’s findings, and determined that although EWEB timely submitted a Misoperations Report for the Weyco incident, it did not develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature, and therefore, it had a compliance exception with PRC-004-2.1a R1. The root cause of this compliance exception was EWEB's lack of a compliance process to ensure that its Corrective Action Plan would prevent a possible recurrence of the applicable misoperation. No harm was known to have occurred from the original Corrective Action Plan. This violation started on December 1, 2014, the day the CAP was submitted, and will end when EWEB corrects the CAP, proposed completion date of December 31, 2015. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). EWEB failed to develop a Corrective Action Plan for a relay misoperation that opened a breaker on its 115 kV system. If EWEB does not develop and implement a corrective action plan to prevent recurrence, another misoperation of the same relay or similar relays with pilot wire connections could result in the opening of one or more 115 kV lines. However, based on the Audit Team’s analysis of Corrective Action Plans for prior EWEB misoperations, it is clear that EWEB has a robust process for analyzing and correcting Protection System misoperations. In this case, EWEB’s failure to develop a Corrective Action Plan was not based on a lack of institutional capability, but rather on the low risk of recurrence of the Misoperation. In addition, EWEB has only four lines using this protection system configuration. This limited number of lines, combined with the low risk of lightning in the area, reduces the potential impact even further. WECC considered EWEB's PRC-004-2a R1 complince history in determining the CE treatment. EWEB's relevant prior noncompliance with PRC-004-2a R1 includes Violation ID# WECC2013013129. WECC determined that the previous issue was distinguished from the current issue, because in the prior issue, EWEB developed an applicable Corrective Action Plan, but failed to provide one quarterly update to WECC on the progress of that plan. | To mitigate this compliance exception by 12/31/2015, EWEB will test the Pilot Wire relays,overall relaying scheme and communication system integrity; and further perform system studies on the Bulk Electric System to verify that this type of event would not cause a cascading outage or instability of the BPS. System studies will include transient stability analysis and steady state power flow.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC2015014690 | PRC-005-1b | R2 | On March 2, 2015, EWEB submitted a Self-Certification stating that, as a Transmission Owner, Generator Owner and Distribution Provider, it was in possible non-compliance with PRC-005-1b R2. On April 13, 2015 through April 24, 2015, WECC conducted a Compliance Audit of EWEB’s facilities, where the WECC Audit Team reviewed the Self-Certification and interviewed EWEB compliance staff. The WECC Audit Team determined that EWEB had a compliance exception with PRC-005-1b R2, for its failure test one breaker failure relay on one of its transmission protection systems, in accordance with its maintenance and testing plan. At EWEB, breaker failure relays are typically used in complex bus arrangements, and these relays are deployed using the same CT as the backup protective relay. Because of this configuration, EWEB does not perform individual load checks for breaker failure relays. Instead, EWEB performs a load check for each instrument transformer (CT and/or PT), but does not verify this signal is measured by each relay. If the instrument transformer secondary is proven to be accurate at one relay, EWEB assumes all other devices also measure the correct values. However, EWEB has one breaker failure relay that does not share a CT with another protective relay. In this case, EWEB failed to perform instrument transformer testing (load check) on this CT associated with one breaker failure relay on a BES transmission substation tie breaker. Enforcement reviewed the Self-Certification and the Audit Team’s findings, and determined that EWEB had a compliance exception with PRC-005-1b R2, for its failure to provide evidence that one breaker failure relay was maintained and tested within the intervals defined in its maintenance and testing program, and the date that device was last tested/maintained. The root cause of this compliance exception was EWEB's lack of a compliance process to ensure all current sensing devices were tested in accordance with its maintenance and testing program. This violation started on April 19, 2011, the date EWEB performed testing, but did not perform a load check, to February 28, 2015, the date EWEB performed a load check on the CT. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, EWEB failed to maintain and test a current sensing element and the associated breaker failure relay on one of its Transmission Protection Systems. However, this element is associated with a breaker failure relay which only operates if the primary interrupting device fails. Upon its discovery, as a compensating measure, EWEB tested the current sensing device and found that it was supplying the proper current to the relay. EWEB has two prior violations of this Standard and Requirement, given NERC Violation ID#’s WECC200801293 and WECC2011009026. In the first instance (WECC200801293), EWEB failed to maintain 40 relays in accordance with its maintenance and testing schedule. In the second instance (WECC2011009026), EWEB self-reported gaps in the maintenance and testing records at one EWEB plant. WECC considers the earlier issues as separate and distinct from the current compliance exception, because in this case, EWEB failed to test one current sensing device on one of its transmission protection systems in accordance with its maintenance and testing plan. No harm was known to have occurred. | To mitigate this compliance exception, EWEB: 1) performed instrument transformer testing (load check) on the current transformer associated with the deficient breaker failure relay, and 2) completed a revision to EWEB's Implementing Document, SESR.400.PRC.01-05 Relay Shop Procedure, to prevent this type of oversight from occuring again.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Imperial Irrigation District (IID) | NCR05195 | WECC2015014644 | MOD-001-1a | R4 | On February 19, 2015, IID submitted a Self-Report stating that, as a Transmission Service Provider, it was in possible non-compliance with MOD-001-1a R4. A WECC Subject Matter Expert (SME) reviewed the Self-Report and conducted interviews with IID’s compliance staff, and determined that IID had a compliance exception with MOD-001-1a R4. On December 29, 2014 IID revised its Available Transfer Capability Implementation Document (ATCID), to make some editorial changes and minor updates. However, IID did not notify each Planning Coordinator, Reliability Coordinator or Transmission Operator either adjacent to or associated with IID’s area until January 9, 2015, when IID notified the applicable entities. After IID implemented the revised ATCID, a copy was reviewed by IID’s Reliability Compliance Office. At that review, IID recognized that it was required to notify the required entities per MOD-001-1a R4.1 – R4.6, prior to implementing the revised ATCID. The root cause of this compliance exception was IID's lack of compliance process to ensure that revisions to its ATCID were distributed timely to the appropriate parties. No harm is known to have occurred. The violation started on December 29, 2014, the date IID revised its ATCID document, and on 1/9/2015, the date IID notified the required entities. | This compliance exception posed a minimal risk, and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, IID revised its ATCID as of December 29, 2014, but did not notify other applicable entities that the revised ATCID was being implemented, until January 9, 2015. Although a revised ATCID could affect other entities due to the many transfer capabilities specified in the ATCID procedure, IID’s revised ATCID did not in any way change how IID determines Available Transfer Capability; the only changes were formatting and editorial. IID implemented a detective control that required a review of the revised ATCID by IID’s Reliability Compliance Office, and identified IID’s obligation to notify certain entities per MOD-001-1a R4.1–R4.6 prior to implementing the revised ATCID. IID implemented compensating controls and revised its ATCID to require notification to certain entities before implementing a subsequent revised ATCID. No harm was known to have occurred. WECC considered IID's compliance history and determined there were no relevant instances of noncompliance. | IID notified the required entities via email 12 days after the date of implementation, to remediate this issue. To mitigate the compliance exception, IID: 1) revised its Available Transfer Capability Implementation Document to include a 5-day notification period; 2) emailed evidence of notification to Entities by March 15, 2015; and 3) and finalized the ATCID. WECC verified completion of IID’s mitigation plan.
2015-09-30 | Western Electricity Coordinating Council (WECC) | Idaho Power Company (IPCO) | NCR05191 | WECC2015014893 | TOP-007-0 | R1 | On March 2, 2015, IPCO submitted a Self-Report stating that, as a Transmission Operator, it had an issue with TOP-007-0 R1. On November 24, 2014, the entity’s Audit Services department issued a report for an internal assessment of TOP-007-0 that had been performed for the period of January 1, 2014 through August 31, 2014. The assessment team reviewed data for each of the entity’s Major WECC Transfer Paths for the assessment period and noted seven events in 2014, all on a single path, in which the SOL was exceeded, including four events on May 21, 2014, one event on July 3, 2014, and two events on July 14, 2014. During the first event on May 21, beginning at 9:10 and lasting through 9:12, the RC was contacted. For the three subsequent events on May 21, the exceeded SOL was not communicated to the RC. The July 3 event was the result of another entity’s 500 kV line being over its limit. The July 14 events also resulted from another entity’s 500 kV line tripping. At the time of both of these events, the other entity worked directly with the RC to bring the load back within the SOL. As a result, the current entity’s System Operator did not contact the RC. The entity’s internal procedures require the System Operator to contact the RC first, followed by corrective actions to mitigate the event. Per discussion with the operations group, the operators mistakenly interpreted this requirement to mean that if the event is short, then the RC does not need to be contacted since mitigation actions have already been taken. Additionally, since the RC is notified at the same time as the System Operators when an SOL is exceeded by an automatic notification provided by the Inter-control Center Communication Protocol (ICCP), the System Operators felt the phone calls were redundant to automated controls already in place to notify the RC. The duration of the noncompliance was from May 21, 2014, the first instance of noncompliance, through March 26, 2015, when IPCO completed its mitigation activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system. In this instance, the entity failed to inform its Reliability Coordinator (RC) when an IROL or SOL has been exceeded and the actions being taken to return the system to within limits. If the Transmission Operator does not inform the RC when an IROL or SOL has been exceeded it may delay event recovery, which may reduce system reliability. For the June and July instances, the other entity with the 500 kV line worked directly with the RC so although the entity as the Path Operator did not contact the RC , the RC was informed of the exceeded SOLs. For each of the three instances on May 21, the SOL was exceeded for about one minute in the first two events and less than five minutes in the third and measures were implemented before a call could be made. Additionally, the Reliability Coordinator was contacted as required by the standard when the initial event of the day occurred. In addition, the RC receives real-time information from the entity via ICCP data points and therefore was automatically notified at the same time as the entity’s System Operator when the SOL was exceeded and when the issue was resolved. No harm is known to have occurred. WECC considered IPCO's compliance history and determined there were no relevant instances of noncompliance. | To address the issue and ensure that the RC is aware of the conditions and the actions being taken by Idaho Power so the RC can help coordinate any other needed actions and maintain awareness of system conditions, Idaho Power has clarified its procedures in the following way for paths that are at or near the SOL: 1) When an SOL or IROL is at or near limits and expected to exceed this limit, the Idaho Power System Operator will place a single call to the RC communicating the system conditions along with the actions that are being taken or will be taken to return the system to within limits, if time permits. If the pre-emptive call cannot be completed due to System Operator work load a call will be made to the RC as soon as possible without jeopardizing personnel safety, equipment, or the reliability of the BES, if the system exceeds an SOL or IROL. 2) Any further limit violation for the related SOL will be considered as addressed by the initial communication to the RC unless the RC requests a follow up call, the system conditions change, or a new System Operator takes over the shift who has not been communicating with the RC regarding the SOL. 3) The System Operator will note on the operator log that the RC has been contacted concerning the SOL or IROL event. Idaho Power trained all System Operators on these clarifications to the procedures during Load Serving Operations Spring Training.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Exelon Generation Company, LLC (ExGen) | NCR04057 | RFC2015014802 | PRC-005-1.1b | R2 | On March 31, 2015, ExGen submitted a Self-Certification stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. During a quarterly internal compliance review, ExGen discovered multiple instances where ExGen personnel did not follow Exelon’s established battery maintenance intervals. Exelon Procedure ER-EP-405 is used to define the intervals and basis for Protection System maintenance and testing of Protection System components, including batteries. Exelon Procedure ER-EP-405 defines battery intervals as three months, four months, and no later than the last day of the fourth calendar month following the prior maintenance date depending on the particular battery at issue. Although the required activities for battery maintenance are included in Exelon Procedure ER-EP-153, the interval (90 or 120 days from the prior maintenance) for quarterly maintenance activities is not specified in this document. This lack of specificity created confusion among some ExGen personnel about how often battery maintenance needed to be performed on certain batteries and resulted in situations where battery maintenance was performed more than 90 days, as Exelon Procedure ER-EP-405 requires, but less than 120 days, after the prior maintenance had been performed. There were a total of 22 instances at four different ExGen facilities where maintenance was performed on battery banks, but not within the prescribed intervals. Of these 22 battery banks, five were in the ReliabilityFirst region, nine were in the Northeast Power Coordinating Council (NPCC) region, and eight were in the Texas Reliability Entity (TRE) region. ExGen has a total of 129 battery banks that require maintenance, meaning 5.86% of the battery banks were tested late. ExGen also discovered that a spreadsheet used to centrally track these maintenance activities on a quarterly basis included a formula that used a 180 day time frame, which matches a business quarter, rather than the correct 90/120 day time frame. The root cause of this noncompliance was inconsistently defined testing intervals for ExGen’s different maintenance, testing, and tracking procedures. The confusion among ExGen personnel in applying the different testing intervals and procedures also indicates a lack of effective training. Additionally, the inconsistent testing intervals and procedures reveal a lack of effective oversight of ExGen’s written maintenance and testing procedures as ExGen should not have allowed inconsistent testing intervals and procedures to remain in place. The duration of this noncompliance is from August 1, 2014, the date ExGen was required to comply with PRC-005-1.1b R2, to June 30, 2015, the date ExGen completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although ExGen performed all of its quarterly inspections, some of these quarterly inspections were late because they were outside of the required intervals of 90/120 days. However, the testing was only overdue by approximately one month. Additionally, the battery systems are continuously monitored via SCADA, with an annunciator in ExGen’s control room. This continuous monitoring at the time of the noncompliance minimizes the risk posed by this noncompliance because if an issue were to arise with a battery, ExGen would be notified by the SCADA monitoring system and the annunciator in the control room. Lastly, testing of the devices demonstrated that they were all operating within normal specifications, indicating that if ExGen had experienced any issues, its Protection System equipment would have functioned as intended. No harm is known to have occurred. This issue is ExGen’s first issue with PRC-005 R2, and as a result, ReliabilityFirst did not consider ExGen’s compliance history as a factor warranting an alternative disposition method. | To mitigate this issue, ExGen: 1) updated its timing mechanism in the tracking matrix to reflect the correct interval testing time period; 2) completed an extent of condition analysis on May 17, 2015 to identify any additional battery testing interval issues in ExGen’s fleet. That analysis revealed no further battery testing issues and that all quarterly battery inspections had been performed in accordance with the required intervals; 3) updated and improved Exelon Procedure ER-EP-405 and ER-EP-153 to account for the transition to PRC-005-2, which includes a maximum maintenance interval of four months for batteries in Table 1-4(a) through 1-4(f). Exelon Procedure ER-EP-153 was edited to add a declaration in the purpose section that the Exelon Maintenance Program is time based with a defined interval to match Exelon Procedure ER-EP-405 with minor maintenance intervals for batteries at 90 days and not more than 120 days; 4) distributed revised procedures and educated affected personnel on all of the changes to help prevent recurrence; and 5) corrected the centralized battery tracking matrix to properly calculate days between tests. ReliabilityFirst has verified the completion of all mitigation activity.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Susquehanna Nuclear, LLC (SUSQ) | NCR00889 | RFC2015014825 | VAR-002-2b | R2 | On March 27, 2015, SUSQ submitted a Self-Certification, and on March 31, 2015, SUSQ submitted a self-log stating that as a Generator Operator it had an issue of VAR-002-2b R2. When the generator voltage operates above the prescribed voltage schedule bandwidth limit of 543kV, it is required for the Control Room Operator to take action to reduce Mega Volt Ampere Reactive (MVARs) to attempt to lower the voltage back within the voltage schedule to the extent of the Unit’s capability (i.e. Facility Ratings aka PJM D-Curves). Operations did not take action to reduce MVARs to the unit capability limit of 54 MVARs. 54 MVARs was established as the temporary limit and the lowest MVARs achievable under PJM eDART ticket 968582 for Unit 2. Therefore, Operations did not take the necessary action to attempt to lower the voltage back within the voltage schedule with the maximum MVAR capability of the unit at that time per VAR-002 R2 and the voltage continued to operate above the high side of the voltage schedule bandwidth limit of 543kV. If MVAR, aux bus or other Unit limitations were a result of conditions at the time of the unit ramp/startup, then Operations did not make notification to the GCC/TCC (Generation Dispatch/Transmission Operator) that the voltage schedule cannot be maintained due to the Unit 2 MVAR capability limitations or other Unit limitations having been reached. This notification is specified in Susquehanna's operating procedures. Communication was established each night to discuss the PJM High System Voltage Action, but Control Room operator communication that the Unit was operating outside of the bandwidth due to MVAR limitations or other limitations being reached was not apparent from the voice recordings or control room logs. The requirement to notify PJM or the Transmission Owner (TO) is specified in PJM Manual 03, Section 3.3.3. Note 3 on page 35. The unit operated above the upper limit of the unit's voltage schedule during the following times: 20:00 on 9/16/2014 and 08:00 on 9/17/2014 00:00 on 9/18/2014 and 06:00 on 9/18/2014 There was a PJM High Voltage Action issued during the first instance that occured between 20:00 on 9/16/2014 and 08:00 on 9/17/2014. The unit has not operated outside of the voltage schedule without taking action or making the proper notification to the TO/Transmission Operator prior to this issue. The duration of this noncompliance is from September 16, 2014, the date SUSQ was subject to compliance with VAR-002-2b R2, to June 1, 2015, the date SUSQ completed its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. A PJM High Voltage Action, meaning voltage was high across the PJM footprint, was issued that covered part of the time that the unit did not meet its voltage schedule and the plant had no issues before or after this noncompliance where the unit operated outside of the voltage schedule without taking action or making the proper notice. The unit had control room alarming in place that notified operators when the limits of the voltage schedule were being approached at the time of the violation. Lastly, this deviation from the voltage schedule did not result in the loss of any BES equipment because the deviation was within the range at which there is no harm to equipment from having high voltage. No harm is known to have occurred. | To mitigate this issue, SUSQ: 1. generated a Condition Report (CR) on the potential violation to Operations. Susquehanna has a Correct Action program as a part of the nuclear requirements of the station. This corrective action program will assign the necessary actions to the various work groups at Susquehanna; 2. submitted Action Requests (ARs) for engineering and ops procedure group actions that are required to evaluate whether additional changes to programs and procedures are permitted; 3. issued a Ops Bulletin that communicates the need for Operations to maintain the prescribed Voltage Schedule and to communicate and log when the Unit is unable to do so; 4. performed evaluation for engineering changes; and 5. revised procedures OI-AD-029, OP-198-001 and OP-298-001 to provide direction for actions to take during a PJM High System Voltage Action (HSVA) when the generator is outside of the voltage bandwidth.
2015-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Talen Generation, LLC (TG) | NCR11362 | RFC2015015033 | VAR-002-3 | R1 | On March 31, 2015, TG submitted a self-log stating that as a Generator Operator it had an issue of VAR-002-3 R1. Martins Creek Unit 4 was started-up on the morning of 10/17/14. The automatic voltage regulator (AVR) was not put in service at the completion of startup. This condition was discovered through an existing process managed by Generation Power Dispatch (GPD). It was corrected approximately seven hours after the unit startup was completed. The Power Dispatcher discovered that the AVR position was in manual within 7 hours following startup of the unit. Also, the GPD shift turnover checklist includes an item for confirming the AVR position status. The root cause of this event was determined to be human performance error. Operating the plant with the AVR in manual would not directly cause the loss of any generation. While BES reliability issues can occur if the plant is operated outside the voltage schedule, the plant personnel monitors plant voltages and alarms would annunciate if voltages neared the schedule limits. The plant operators are trained to take appropriate actions if voltages exceed the published voltage limits. Even with the AVR in manual mode, the plant control room operators would have received indication that the plant voltages were at or outside the voltage schedule and they have been trained to take action to minimize Bulk Electric System (BES) reliability issues. During the seven hours when the AVR was in manual mode, the actual plant voltages remained within the published voltage schedule and bandwidth. The duration of this noncompliance is from October 17, 2014, the date TG was subject to compliance with VAR-002-3 R1, to July 31, 2015, the date TG committed to complete its mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Even with the AVR in manual mode, the plant control room operators would have received indication that the plant voltages were at or outside the voltage schedule and they have been trained to take action to minimize BES reliability issues. The plant operators continually monitor plant voltages and alarms, even with the AVR in manual mode, and alarms would sound if voltage levels reached the limits of the voltage schedule. Additionally, operating the plant with the AVR in manual would not directly cause the loss of any generation. Finally, plant voltages remained within the voltage schedule bandwidth throughout the entire period of the noncompliance. No harm is known to have occured. | To mitigate this issue, TG: 1. placed AVR in automatic service approximately seven hours after the unit startup was completed; 2. installed a DCS alarm to notify the PCO (Plant Control Room Operator) that the switch is in manual once the unit has synchronized and reached 50MW output; 3. issued a “PQS roster” (all-hands communication) after issuance of the root cause analysis report; and 4. reviewed the event as a Human Performance incident with site shifts and work groups. TG will also complete the following mitigation activities by 7/31/15: 1. Installation of an annunciator alarm to the local panel to provide a more visible and audible alarm for when the switch is in manual and the unit is operating above 50 MW. Wires will be run to make Item "2" an annunciator panel alarm, i.e. more highly visible, at the next outage opportunity (which is why additional time is necessary).
2015-08-31 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2014014140 | EOP-001-0.1b | R6 | On July 17, 2014, TVA submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue with EOP-001-0.1b R6. TVA failed to annually review and update its emergency plan for power system operations. On December 3, 2011, TVA revised an existing emergency assistance plan for power system operations. TVA did not review and update this emergency plan until March 15, 2013. On January 16, 2013, TVA issued an order to track the completion of the emergency plan by March 29, 2013. At that time, TVA assumed the calendar month of March 2013 fell within the three month grace period. Upon further review on July 14, 2014, TVA decided to evaluate this situation as a potential non-compliance issue. TVA’s procedure regarding the administration of processes and procedures defined “annual” as a rolling 12 months plus a 3 month grace period. NERC’s Compliance Application Notice-0010 (CAN-0010) provides guidance to the Compliance Enforcement Authority (CEA) on how to determine compliance for implementation of annual requirements. CAN-0010 states that “…CEAs are to verify that any alternative documented method demonstrates that the required activity was conducted at least once every Calendar Year.” The term “Calendar Year” is defined in CAN-0010 as within a calendar year, “beginning on January 1 and ending on December 31.” CAN-0010 also states that a CEA should find noncompliance if a registered entity did not adhere to its implementation of “annual”, “unless the entity conducts the annual activity at least once every Calendar Year.” (emphasis in original). TVA reviewed and implemented its emergency plan on December 3, 2011, and reviewed and updated it on March 15, 2013, a span of 15 months and 12 days. TVA did not adhere to its implementation of “annual” and it did not review and update its emergency plan during the 2012 calendar year as required. This issue lasted from January 1, 2013, when TVA failed to perform the annual review and update of its emergency plan for power system operations during the 2012 calendar year, through March 15, 2013, when TVA implemented the updated emergency plan for power system operations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TVA’s failure to update its emergency plan for power system operations annually could leave system operators without the most effective or up-to-date plan to respond to emergencies. However, the emergency plan at issue provided sufficient guidelines for TVA, as the BA, to request or provide emergency assistance. Although the updated procedure enhanced and clarified some of the processes, it did not significantly change the responsibilities of the system operators. The remainder of the revisions addressed title changes, the consolidation of neighboring utilities, and formatting changes. During the issue, no events occurred that required TVA to use this procedure. SERC considered TVA’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, TVA: 1) implemented the new revision on the effective date; 2) provided clarification regarding the grace period requirements for procedure revisions through internal TVA compliance groups such as the Reliability Standards oversight group and the Reliability Standards working group; 3) continued to use its problem evaluation report process to track procedures whose revision requires the use of the grace period; and 4) ensured the action due date aligns with the actual three month grace period and not the end of the month that the end of the grace period falls in, while ensuring that the annual review and update of the emergency plans occurs at least once every calendar year.
2015-08-31 | SERC Reliability Corporation (SERC) | Alcoa Power Generating Inc. – Yadkin Division (YAD) | NCR01169 | SERC2015014597 | MOD-030-2 | R3 | On January 22, 2015, YAD submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue with MOD-030-2 R3.2. YAD failed to perform the daily update of the Transmission model used to determine Available Flowgate Capability (AFC). YAD creates Automated Model Building (AMB) log files daily to show that YAD has uploaded the AFC data to the OATI secure site for posting to the Transmission model. On January 7, 2015, YAD discovered that it did not have AFC AMB log files for the period of November 20, 2014 through December 14, 2014. Although not required by YAD’s procedure, an employee checked the output of the AMB process to see if everything was working as expected and discovered the missing files. Upon discovering the absence of the log files, the employee contacted OATI to determine if OATI received the files. On January 8, 2015, OATI confirmed that there was a gap in the AFC data. OATI confirmed that the gap started on November 19, 2014 and lasted until December 15, 2014. The employee reported this issue to his or her immediate supervisor, the manager, and the chief compliance officer. The employee continued to investigate possible causes. After reviewing the issue with the OATI project manager, OATI technical support, and YAD computer support, YAD concluded that an interruption to the computer that runs the AFC AMB process likely caused this issue. On November 19, 2014, YAD ran a security patch update which forced an auto restart of the AFC AMB machine. The auto restart of the machine shut down the AFC update process. The program requires a login password, and therefore the program did not automatically restart when the machine did. This issue lasted from November 20, 2014, when YAD first failed to provide updated AFC information on a daily basis to the Transmission Service Providers (TSPs), through December 15, 2014, when YAD resumed providing updated AFC information on a daily basis to the TSPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. YAD’s failure to provide updated AFC calculations on a daily basis could result in the TSP making more or less transmission capacity available, possibly causing over- or under-subscription, respectively, on the transmission path. Over-subscription could lead to real-time overloading conditions on the system, which could cause a Reliability Coordinator to initiate a Transmission Loading Relief procedure. Alternatively, under-subscription creates a potential loss of revenue for the TSP. However, the TSP performs the AFC calculations regardless of whether the TOP updates the data. If the TOP data is not updated, the TSP calculates AFC using existing model data. Further, YAD’s 100 kV transmission system is only 19 miles, connecting Duke Energy Progress and Duke Energy Carolinas. YAD’s affiliated marketer uses the YAD transmission posted AFC to sell YAD generation into the market. YAD had approximately 200 MWs of generation during the issue and the transfer capacity of YAD’s line was approximately 363 MWs. No harm is known to have occurred. SERC considered YAD and its affiliates' compliance history in determining the disposition track. YAD and its affiliates' relevant prior noncompliance with MOD-030-3 R3 includes: NERC Violation IDs SERC2011008261 and SERC2011008265. SERC determined that YAD and its affiliates' compliance history should not serve as a basis for applying a penalty. In SERC2011008261, YAD failed to update daily values due to an issue with the software password. In SERC2011008265, YAD's affiliate Alcoa Power Generating, Inc.- Tapoco Division (APGI-Tapoco) also failed to update daily values due to an issue with the software password. Both prior violations occurred more than three years before the instant issue, indicating that this was not an ongoing or repetitive problem. The redundant systems installed by YAD and APGI-Tapoco as part of the Mitigation Plans for the previous issues provided back-up to the model actually calculating the AFC and did not address the failure presented in the instant issue, which involved an interruption in the submission of AFC data, not the creation of AFC data as occurred in the previous issues. As part of the previous Mitigation Plans, YAD and APGI-Tapoco each installed and maintained an alarm to indicate that the hourly runs failed to execute properly. In the instant issue, the process of pulling data into the AMB case and uploading the data to OATI was interrupted while the hourly runs creating the data were executing properly. | To mitigate this issue, YAD: 1) created an alert system to notify users when the log file fails to be created in the AMB process. This alert is in the form of an email, sent to at least two employees to notify of possible AMB log failure. The message goes to email and smart phone of the power system engineer and the local IT support; 2) performed manual checks on the data before the automated alert system was finalized; and 3) asked IT security to investigate if there is a process or method that IT can recommend to prevent another occurrence.
2015-08-31 | SERC Reliability Corporation (SERC) | Alcoa Power Generating Inc. – Yadkin Division (YAD) | NCR01169 | SERC2015014624 | BAL-002-1 | R4 | On February 6, 2015, YAD submitted a SERC-initiated Self-Report stating that, as a Balancing Authority (BA), it had an issue with BAL-002-1 R4.2. YAD failed to return Area Control Error (ACE) to its pre-Disturbance value within 15 minutes after the start of a Reportable Disturbance. While reviewing YAD’s BAL-002 quarterly report, SERC identified that YAD reported one Disturbance that was greater than the most severe single contingency loss, with a percent recovery of 0%. However, YAD had not submitted a Self-Report related to that event. After discussing the event and reviewing relevant information with SERC, YAD submitted a Self-Report for this issue. At 10:52 a.m. on October 20, 2014, Narrows unit #3 tripped. The YAD system operator reset the relay target and attempted to restart the unit. The unit restarted, but before going back online, the unit tripped again and locked out. The system operator attempted to balance the schedule and generation by curtailing an interchange tag. The system operator initiated a tag curtailment, but failed to approve the curtailment because he or she did not acknowledge the request to confirm the curtailment. By the time the system operator noticed the error and initiated and approved a second curtailment, the 15 minute time recovery period had passed. At 11:25 a.m., Narrows unit #3 returned to service and YAD returned ACE to its pre-Disturbance value. YAD’s largest single contingency is Narrows unit #3, at 29 MW. During this event, YAD also experienced SCADA communications and governor trouble on other units at Narrows, all contributing to reduced generation levels. YAD lost 43 MWs of total generation at Narrows. Because of the additional SCADA communications and governor trouble on the other units, YAD incorrectly determined that this event was multiple contingencies occurring within one minute or less of each other, and should therefore be excluded from compliance evaluation. As such, YAD did not submit a Self-Report at the time of the event. SERC reviewed the ACE records and did not identify multiple contingencies. This issue lasted from 11:08 a.m. on October 20, 2014, 16 minutes after the start of the Disturbance, through 11:25 a.m. on October 20, 2014, when YAD returned Narrows unit #3 to service and returned ACE to its pre-Disturbance value. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). YAD’s failure to return ACE to its pre-Disturbance level within 15 minutes of a reportable Disturbance could have resulted in inadvertent energy flows between the YAD system and neighboring BA areas during Disturbance recovery. However, YAD is located between two larger BA areas, thus reducing the potential impact. YAD has three interconnection points: two with Duke Energy Carolinas (DEC) at 100 kV and one with Duke Energy Progress (DEP) at 100 kV. DEC has approximately 20,600 MW of generation and DEP has approximately 13,500 MW of generation. Therefore, the impact of inadvertent flow in the YAD BA area, as YAD implemented tag curtailment and recovered generation from a 30 MW generator trip (0.09% of the total generation in the neighboring BA areas), had minimal effect on the BPS. No harm is known to have occurred. SERC considered YAD’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, YAD: 1) increased operating reserves for first quarter; 2) reduced maximum firm generation levels available to market to facilitate increased system disturbance recovery capability. Reduced generation to market will increase spinning reserves capacity; and 3) had its chief system operator discuss with each system operator the October 20, 2014 event, the requirements of the BAL-002-1 Standard, situational awareness, and the increased operating reserves.
2015-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Southwestern Public Service Company (Xcel Energy) | NCR01145 | SPP2015014847 | VAR-002-3 | R3 | On April 6, 2015, Xcel Energy submitted a self-report stating that, as a Generator Operator, it had a minimal risk instance of noncompliance with VAR-002-3 R3 because it did not notify its Transmission Operator (TOP) of a status change of the power system stabilizer (PSS) for Unit 3 at the Jones Station. On February 28, 2015, at approximately 8:30 a.m., the Jones Station control room operator brought Unit 3 and Unit 4 gas turbines online. Shortly thereafter, the control room operator, without visually confirming the status of the PSS for Unit 3 and Unit 4, notified the TOP that the PSS’ were active. Approximately eight hours later at 4:21 p.m., the evening control room operator noticed on the control screens that the Unit 3 PSS was inactive. The evening control room operator phoned the operator that was on duty at the time Unit 3 and Unit 4 were brought online and asked if the operator had deactivated the PSS on one of the units. The operator answered “no.” The evening control center operator immediately called Xcel Energy’s TOP to notify the TOP that the PSS was inactive. The evening control room operator then activated the PSS and notified the TOP of the status change. The PSS was inactive for approximately eight hours without Xcel Energy’s TOP being advised of the status change. The root cause of this instance of noncompliance was human error. Unit 3's PSS has an additional manual step to activate the PSS while Unit 4's PSS does this step automatically. In this instance, the control room operator did not manually activate the Unit 3 PSS and was unaware the PSS was not automatically activated. SPP RE determined the instance of noncompliance began on February 28, 2015, at 8:30 a.m., when Unit 3 was started with the PSS inactive and the TOP was incorrectly advised of the status, and ended on February 29, 2015, at 4:21 p.m., when the PSS was placed in service and the TOP was notified. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the short period of time the PSS for Unit 3 was inactive, the PSS for three of the four units at Jones Station were enabled and would have responded to a system disturbance. No emergency action was required during the time the Unit 3 PSS was inactive. Xcel Energy’s evening operator notified the TOP as soon as he realized the PSS on Unit 3 was inactive. No actual harm occurred. A Settlement Agreement covering violation of VAR-002-1.1b R3 for Xcel Energy (SPP2012011057) was filed with FERC under NP13-57-000 on September 30, 2013. On October 31, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE considered Xcel Energy's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the instances were of the same Standard and Requirement, the underlying conduct of the two instances was different. The prior violation involved a voltage regulator and occurred at a different Xcel Energy generation plant. The prior violation was also minimal risk, self-reported, and promptly mitigated. | To mitigate this minimal risk instance of noncompliance, Xcel Energy: 1) switched the PSS to “active” mode and notified the TOP; 2) added an alarm to the PSS that notifies the operators when the PSS becomes “inactive” upon startup, which will only clear after the unit reaches 20% of load capacity and the PSS becomes “active”; 3) met with affected shift supervisors and instructed them to be in the control room when the units were being brought online; 4) installed a temporary patch on the PSS software to automate the process; and, 5) retrained all operators and shift supervisors on the VAR-002-3 compliance requirements. SPP RE has verified the completion of all mitigation activity.
2015-08-31 | Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (EDE) | NCR01155 | SPP2014014398 | TOP-008-1 | R2 | During a Compliance Audit conducted from October 7, 2014, through October 9, 2014, the SPP RE determined that EDE, as a Transmission Operator, had two minimal risk instances of noncompliance with TOP-008-1 R2. On February 9, 2014, EDE’s Real Time Contingency Analysis (RTCA) identified three EDE transmission facilities with a post contingency flow of 103.82%, 103.45%, and 101.42% of the facilities’ emergency flow limit. Similarly, on February 13, 2014, EDE’s RTCA identified a flowgate with a post contingency flow of 100.15% of the emergency flow limit. EDE’s operating plan to mitigate exceeding the emergency flow limits for these facilities was to re-dispatch generation. However, on both occasions EDE’s system operators did not take action, pre-contingency, to mitigate the potential emergency flow limit violations. Because EDE did not re-dispatch its generation in response to the RTCA identification of potential emergency flow limit violations, the SPP RE Audit Team found that EDE did not operate to prevent the likelihood that a disturbance would result in a SOL violation. Additionally, these instances are illustrative that EDE operators were not documenting regular reviews of the RTCA to ensure that potential post-contingency flows exceeding the emergency limit had been mitigated. The SPP RE determined that the minimal risk instance of noncompliance began on February 9, 2013, the date the RTCA report showed EDE had a post-contingency flow exceeding 100% and EDE’s inaction to prevent the likelihood that a SOL would occur, through October 22, 2014, when the mitigation plan was completed. The root cause of the instance of noncompliance was human error. EDE’s system operators did not follow EDE’s plan to re-dispatch generation when EDE’s RTCA identified facilities that would exceed 100% of the emergency flow limit following a contingency. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EDE has established emergency ratings for its transmission facilities that are a continuous rating. Accordingly, EDE’s transmission facilities can operate indefinitely at the emergency limit without damage to its transmission facilities. The RTCA results on February 9, 2013 indicated that the monitored facilities would only exceed the emergency flow limit by 3.82%, 3.45% and 1.42% had the identified contingencies occur. The RTCA result on February 13, 2014, indicated that the monitored facility would only exceed the emergency flow limit by .15% had the contingency occurred. No post contingency voltage limit violations were identified on either occasion. Although no operator log entries were provided by EDE to demonstrate they were specifically monitoring the flows on these facilities, EDE’s SCADA system would have provided the system operators with an alarm at 95% and 100% of the normal rating and 95% and 100% of the emergency rating. EDE’s system operators were aware that to mitigate a high flow condition on the identified facilities they would have to dispatch generation and that the generation could be brought on line in 10 minutes. No actual harm occurred. EDE has no prior violations of this standard and requirement. | To mitigate this minimal risk instance of noncompliance, EDE: 1) instructed system operators to document reviews of RTCA studies in the operators’ log; 2) instructed system operators to coordinate with EDE’s Reliability Coordinator if the RTCA shows a post-contingency flow of 95% or higher than EDE’s emergency rating, the operators should develop a solution to bring the post-contingency limit below 95% of the emergency rating; and 3) instructed system operators to review subsequent RTCA studies to reaffirm that the potential post-contingency flow issue is mitigated and for the system operators to document the findings in the operators’ log. SPP RE has verified the completion of all mitigation activity.
2015-08-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE – Little Rock District (COELR) | NCR06037 | SPP2012011561 | PRC-005-1 | R2; R2.1, R2.2 | During a Compliance Audit conducted from December 10, 2012, through December 14, 2012, SPP RE determined that COELR, as a Generator Owner had an issue of noncompliance with PRC-005-1 R2; R2.1, R2.2 because COELR: (1) could not provide evidence of the annual load tests of the battery banks at two of its seven hydroelectric generating facilities and (2) in a sampling of 33 of COELR’s 59 generator protection systems, COELR could not provide evidence of the testing of its current transformers (CTs) and potential transformers (PTs). COELR’s Protection System Maintenance and Testing Program (PSMTP) states that the battery banks at is hydroelectric generating facilities will be load tested annually. During the Audit the COELR was unable to provide evidence to demonstrate that it had performed annual load tests on the battery banks at the Bull Shoals and Table Rock hydroelectric facilities. In addition to the visual inspection of CTs and PTs, COELR’s PSMTP includes a comparative test for instrument transformers that is performed concurrent with relay testing. For CTs not located in differential schemes, the COELR compares the output of the CT under test with the output of other CTs in series. Similarly, to test the output of PTs, the output of the PT under test is compared with the output of other PTs in parallel with the PT under test. SPP RE found that COELR had not documented any of the CT and PT comparative tests required by its PSMTP. This instance of non-compliance began on June 18, 2007, when PRC-005-1 R2 became mandatory and enforceable, and ended on August 1, 2013, when the COELR successfully mitigated the instance of noncompliance. The root cause of this issue was human error. COELR failed to fully comply with its PSMTP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the COELR did not perform annual battery load tests on two of its seven facilities, the COELR was performing a visual inspection and voltage check of its batter banks monthly. Additionally, the specific gravity of the battery bank cells was tested every quarter. Battery voltage is monitored continuously by the COELR area control center and alarms upon loss of tripping voltage. No actual harm occurred. Regarding COELR’s failure to perform comparative tests on its instrument transformers, instrument transformers have no moving parts and are extremely reliable. COELR was performing the visual inspections required in its PSMTP. Furthermore, the COELR was verifying current and voltage signals from the CTs and PTs during relay testing. | To mitigate this issue, the COELR: 1) revised its District Policy and testing procedures for PRC-005 R2 in order to provide documentation to validate compliance with the reliability requirements. 2) provided documentation for line relay and associated DC circuitry testing and voltage and current transformer inspections. 3) revised its battery load testing policy to remove annual load testing. SPP RE has verified the completion of all mitigation activity.
2015-08-31 | Texas Reliability Entity (Texas RE) | Sharyland Utilities, LP (SU) | NCR04119 | TRE2015014874 | PER-005-1 | R2; R2.1 | On April 20, 2015, SU submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue with PER-005-1 R2.1. On April 8, 2014, SU updated its BES company-specific reliability-related task list from four tasks to 18 critical operations tasks. The update was intended to more accurately reflect the work and tasks SU system operators were performing. As of October 5, 2014, SU verified capabilities to perform the new or modified tasks for seven of its eight system operators within the six month window. However, SU failed to verify one of its system operator's capabilities on all new or modified tasks until January 27, 2015, over nine months after the BES company-specific reliability-related task list was updated. The root cause of the issue was that the Transmission Operations Specialist tasked with training responsibility resigned from his position shortly after the updated task list was implemented. This position remained open until September 29, 2014, when a new Transmission Operations Specialist began work. Texas RE determined the issue duration to be from October 9, 2014, the day after the system operator was due to be trained, until January 27, 2015, when the System Operator was trained. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). According to SU, the task list revision in April 2014 only added tasks to the list that were already being performed by the system operators. In essence, the revision was to make the task list more comprehensive and accurate in its reflection of the work the system operators, including the system operator who was not verified by October 2014, were already performing. Additionally, the system operator in question has regularly attended training that covers many of the tasks listed in SU's task list. No harm is known to have occurred. Texas RE considered SU’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SU: 1) verified the system operator’s capabilities to perform the new and modified tasks; and 2) updated its system operator Training Manual to include provisions for ensuring that each System Operator’s capabilities are verified within six months of an update to its BES company-specific reliability-related task list. Texas RE has verified the completion of all mitigation activity.
2015-08-31 | Western Electricity Coordinating Council (WECC) | NorthWestern Corporation (NWC) | NCR05282 | WECC2015014865 | PRC-004-2a | R3 | From March 30, 2015 through April 10, 2015, WECC conducted an onsite Compliance Audit of NWC. During the Audit, the WECC Audit Team identified a possible issue of PRC-004-2.1a R3. The WECC Audit Team found that NWC experienced five (5) relay misoperations. NWC did not report quarterly updates for above misoperations as required by PRC-004-2 R3. The three misoperations at Cora, one relay misoperating three times on the same day, were remedied with replaced relays on July 30, 2013. However, NWC did not report this completion to WECC through the required quarterly updates. The remaining two misoperations at Colstrip and Broadview occurred on July 19, 2014; but NWC has not filed quarterly updates because it is waiting on its vendor, GE, for further information before completion. Enforcement reviewed the Audit Team’s findings and determined that NWC had a compliance exception with PRC-004-2.1a R3. Specifically, Enforcement determined NWC failed to provide quarterly updates for five Misoperations with open corrective action plans, according to the Regional Entity’s procedures, as required by PRC-004-2.1a R3. Enforcement further determined this issue began on April 1, 2013, the first quarter the update was due after the initial report. NWC reported it completed its mitigation activities on April 13, 2015. The root cause of this compliance exception was NWC's less than adequate communication with its vendor. NWC stated they did not file quarterly updates because they are waiting on the vendor for further information before completion. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NWC did not provide quarterly updates for five Misoperations with open corrective action plans as required by PRC-004-2a R3. As a compensating measure, NWC did provide WECC documentation of its Misoperations analysis and Corrective Actions Plans as required by the standard. NWC’s submittal of the Corrective Action Plan demonstrates that NWC reviewed, analyzed, and determined the root cause of the Misoperations. Furthermore, NWC’s submittal of the Misoperations incident report to WECC within the timeframe defined in WECC’s procedure minimized the possibility for the Misoperations to occur again. The submittal allowed WECC the ability to properly monitor and analyze the effect of the Misoperations and the remedial actions implemented. WECC reviewed NWC's compliance history and determined there were no relevant instances of noncompliance. No harm is known to have occurred. | To mitigate this issue, NWC: 1) Established a process for proper identification and reporting of Misoperations. Specifically, NWC will use the NERC Questions and Answers about Consistent Protection System Misoperation Reporting; as well as, ensuring a NWC Relay Engineer will identify and report Misoperations in webCDMS. 2) All quarterly updates will be tracked and reported in webCDMS by a Relay Engineer with an independent verification performed by the NERC Compliance Department using a separately maintained spreadsheet (Quarterly Misoperations Review); and 3) Created an alert in the compliance software program AssurX allowing for automated reminders to ensure timely reporting on a quarterly basis. The Mitigation Plan provides evidence that NWC submitted the quarterly updated information in webCDMS for the 5 Misoperations, as required by PRC-004-2.1a R3.
2015-08-31 | Western Electricity Coordinating Council (WECC) | NorthWestern Corporation (NWC) | NCR05282 | WECC2015014866 | PRC-008-0 | R2 | From March 30, 2015 through April 10, 2015, WECC conducted an onsite Compliance Audit of NWC. During the Audit, the WECC Audit Team identified a possible issue of PRC-008-0 R2. Based on NWC’s documentation and interviews with NWC, the WECC Audit Team determined that NWC had an issue with PRC-008-0 R2 for failing to maintain nine out of 62 PT devices associated with its Underfrequency Load Shedding (UFLS) systems. The start date of this issue is June 18, 2007, when the standard became mandatory and enforceable to NWC. NWC reported it completed its mitigation activities on April 14, 2015. The root cause of this compliance exception was NWC’s less than adequate understanding of the standard. NWC stated that it was unaware of what elements comprised of a UFLS system and that it assumed it had until the end of the first maintenance cycle to maintain these elements. For that reason, nine PTs were not tested and maintained within stated maintenance and testing intervals. | This compliance exception poses a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NWC failed to maintain 9 PT’s of its 62, as required by PRC-008-0 R2. This represents 15.5% of its total PT’s. Failure to maintain may cause UFLS devices to not operate as planned to help restore system frequency to the appropriate value. As a compensating measure, NWC’s relays associated with devices have alarming capability; therefore, if the device were to fail while in service a NWC dispatcher will be alerted to take action as needed to balance load to generation and control frequency in an islanded area. In addition, even with no maintenance or inspection there is a very low probability that enough undetected failures of UFLS sensing devices would significantly affect the overall operation and effectiveness of a distributed UFLS protection scheme during an actual UFLS event. For these reasons, WECC determined this compliance exception posed minimal risk to the reliability of the BPS. WECC reviewed NWC's compliance history and determined there were no relevant instances of noncompliance. No harm is known to have occurred. | To mitigate this issue, NWC: 1) Incorporated the nine devices into the PowerBase computer application for the nine devices. This will allow NWC’s computer automated tracking of testing to provide assurance that the testing will be on time and complete. 2) Added personnel to its Relay Substation group to provide oversight and tracking to the testing process. 3) Implemented an additional control process to its overall testing program. Specifically, NWC has quarterly meetings to review quarterly reports that track testing progress. The review is conducted by the NWC’s East/West supervisors, Manager, Director and Compliance Engineers. The Mitigation Plan provides evidence that NWC tested the nine voltage sensing devices, as required by PRC-008-0 R2.
2015-08-31 | Western Electricity Coordinating Council (WECC) | Salt River Project Agricultural Improvement and Power District (SRP) | NCR05372 | WECC2014014496 | PRC-005-1.1b | R2 | On December 11, 2014, SRP submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue with PRC-005-1.1 R2. SRP discovered a battery bank at a substation that was not tested in accordance with SRP’s Protection System Maintenance and Testing plan. SRP’s Protection System Maintenance and Testing Program (“PSMP”) requires Flooded Lead Acid battery banks to be load tested on a five year interval. The battery bank in scope was installed at the Agua Fria 230 kv substation on April 3, 2009. It was first tested on April 24, 2009, but was not tested again until September 19, 2014. SRP’s failure to test one battery bank within the defined interval stated in SRP’s PSMP is a compliance exception of PRC-005-1.1b R2.1. The compliance exception began on May 1, 2014, when SRP should have conducted the maintenance and testing, and continued through September 19, 2014, when SRP conducted the maintenance and testing of the battery bank. The root cause was a misconfiguration of SRP's maintenance tracking system. SRP’s maintenance management system input the next maintenance period based on the date of entry into the system rather than the date of previous maintenance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SRP failed to test one battery bank at an SRP substation. The test was completed 4 months and 14 days after the May 1, 2014 due date. This could potentially result in a failure to detect premature performance degradation of the batteries. Failure to detect premature performance degradation could lead the batteries to be unable to provide sufficient DC power for tripping transmission elements at the substation, if AC power to the substation were lost. However, SRP implemented compensating measures. Specifically, the battery bank was inspected and tested quarterly in addition to the five year performance test. This battery bank is also a secondary source for the protection systems at the substation. WECC reviewed SRP's compliance history and determined there were no relevant instances of noncompliance. No harm is known to have occurred. | To mitigate this issue, SRP completed maintenance and testing of the battery bank.
2015-08-31 | Western Electricity Coordinating Council (WECC) | Salt River Project Agricultural Improvement and Power District (SRP) | NCR05372 | WECC2014014495 | PRC-011-0 | R2 | On December 11, 2014, SRP submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue with PRC-011-0 R2. SRP discovered a battery bank at a substation that was not tested in accordance with SRP’s Undervoltage Load Shedding (“UVLS”) program. SRP's UVLS Maintenance and Testing Program requires Flooded Lead Acid battery banks to be load tested on a five year interval. The battery bank in scope was installed at the Agua Fria 230 kv substation on April 3, 2009. It was first tested on April 24, 2009, but was not tested again until September 19, 2014. SRP’s failure to test the battery bank within the defined interval stated in SRP’s UVLS program is a compliance exception of PRC-011-0 R2. The compliance exception began on May 1, 2014, when SRP should have conducted the maintenance and testing, and continued through September 19, 2014, when SRP conducted the maintenance and testing of the battery bank. The root cause was a misconfiguration of SRP's maintenance tracking system. SRP’s maintenance management system input the next maintenance period based on the date of entry into the system rather than the date of previous maintenance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SRP failed to test one battery bank at an SRP substation. The test was completed 4 months and 14 days after the May 1, 2014 due date. This could potentially result in a failure to detect premature performance degradation of the batteries. Failure to detect premature performance degradation could lead the batteries to be unable to provide sufficient DC power for tripping the undervoltage relay that implements part of the UVLS program. However, SRP implemented compensating measures. Specifically, the battery bank was inspected and tested quarterly in addition to the five year performance test. This battery bank is also a secondary source for the protection systems at the substation. WECC reviewed SRP's compliance history and determined there were no relevant instances of noncompliance. No harm is known to have occurred. | To mitigate this issue, SRP completed maintenance and testing on the battery bank.
2015-08-31 | Western Electricity Coordinating Council (WECC) | El Paso Electric Company (EPE) | NCR05140 | WECC2015014650 | VAR-002-2b | R3; R3.1 | On February 23, 2015, EPE submitted a Self-Report stating that, as a Generator Operator , it had an issue of VAR-002-2b R3. EPE reported that it failed to notify its associated Transmission Operator (TOP) within 30 minutes about a change in the status of its generator reactive power resources, including the status of each Automatic Voltage Regulator (AVR) and power system stabilizer and the expected duration of the change in status or capability. The first instance occurred on September 2, 2014, at 1:31 AM. EPE’s AVR at its Rio Grande Unit 8 moved from automatic mode to manual mode. EPE notified its TOP that the AVR was switched to manual mode on September 2, 2014 at 3:44 AM, 1 hour and 43 minutes after the required timeframe. The second instance occurred on September 3, 2014, at 3:31 AM. EPE’s AVR at the Rio Grande Unit 8 was fixed and brought back from manual mode into auto mode. EPE personnel notified the TOP on September 3, 2014, at 4:03 AM, two minutes after the required timeframe. On April 16, 2015, a WECC Subject Matter Expert (SME) began a review of EPE’s Self-Report, spoke with EPE personnel, and issued a data request. The SME determined that EPE had a possible issue with VAR-002-2b R3. Specifically, the SME determined that on two occasions, EPE failed to notify its TOP within 30 minutes about change in status of its generator reactive power resources and the expected duration of the change in status or capability. EPE failed to report the change in status within the timeframe due to the on duty shift supervisor’s attention being diverted to the issue of moving the AVR from manual to auto mode and securing technical assistance. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that EPE had a compliance exception of VAR-002-2b R3. Specifically, Enforcement determined that on two occasions, EPE failed to notify its TOP within 30 minutes about change in status of its generator reactive power resources and the expected duration of the change in status or capability as required by VAR-002-2b R3. Enforcement determined that the issue began September 2, 2014, the day that the operator did not notify the TOP that the AVR was in manual mode. Enforcement also determined that the issue ended on September 3, 2014, the day that EPE notified its TOP that its AVR was switched back into automatic mode. The Root Cause of this Compliance Exception was EPE’s shift supervisor’s attention being diverted to the issue of figuring out why the AVR changed, which resulted in the supervisor not contacting the TOP within the required time. Therefore, the shift supervisor committed an error in performance due to the distraction. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EPE implemented strong preventative controls by EPE implemented modern excitation systems with voltage limiters which would act to maintain generator output voltage within the capability curves of the generator preventing a generator trip. EPE also implemented strong detective controls by using a Disturbance Control Standard (DCS) to monitor generator status and metered quantities, which provide alarms for voltage levels. EPE also employs a generator start-up checklist that requires verification of AVR and power system stabilizers (PSS) in automatic control. As further compensation, EPE implemented compensating controls. Specifically, EPE implements multiple generators on the same 230kV bus which did provide voltage support in accordance with the voltage schedule. EPE’s generator is rated at 150 MW and integrated on a 115 kV bus with a similar generator. During the time Unit 8 was operating in manual mode, it did not operate above 56% of its rated capacity and the entity had generation totaling over 1779 MW (all with AVR in automatic mode) available to it. WECC reviewed EPE's compliance history and determined there were no relevant instances of noncompliance. No harm is known to have occurred. | To mitigate this issue, EPE: 1) EPE notified its TOP of the change in AVR on September 2, 2014 at 3:44 AM, when the AVR was switched from automatic mode to manual mode; 2) EPE notified its TOP of the change in AVR on September 3, 2014, at 4:03 AM, when the AVR was switched back to automatic mode; and 3) EPE also conducted a follow-up review of its existing controls and updated its written procedural document to reinforce existing hands-on reference aids within the control room.
2015-07-30 | Florida Reliability Coordinating Council (FRCC) | JEA (JEA) | NCR00040 | FRCC2015014664 | VAR-002-2b | R1 | On February 27, 2015, JEA submitted a Self-Certification stating that, as a Generator Operator, it had an issue of VAR-002-2b R1. JEA failed to notify its Transmission Operator that one of its generating units was not operating in automatic voltage regulation (AVR) mode while connected to the interconnected transmission system. In 2014, there were three instances in which JEA's Northside No. 3 unit was online and not in AVR mode, and no notification was given to the system operator that the AVR mode was not in automatic: 1) May 7, 2014 - unit reached minimum stable load (MSL) approximately 8:45 a.m. and was put in AVR at 1:15 p.m. 2) June 29, 2014 - unit reached MSL approximately 11:15 a.m. and was put in AVR at 12:54 p.m. 3) July 31, 2014 - unit reached MSL approximately 8:30 a.m. and was put in AVR at 10:20 a.m. The root cause in each instance has been determined to be human error by plant operators failing to follow the documented procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, JEA's failure to operate in AVR mode when connected to the interconnected transmission system on the three instances could have resulted in voltage instability. However, the time duration was 4 1/2 hours or less and the unit operated within its voltage schedule, and specified tolerances (239 KV +/- 3 KV), in all three instances. No actual harm was known to have occurred. | To mitigate this issue, JEA: 1) Placed the generating unit’s AVR operating mode to automatic; 2) Modified the generating unit’s startup procedure to ensure clarity for setting the AVR operating mode to automatic; and 3) Added energy management system alarms to detect and alert the system operators when the generating units’ AVR operating mode is set to manual. In addition, JEA provided its Generation Control Room Operators and System Operators with additional training on properly switching modes of operation for AVR; and necessary communications that accompany switching AVR modes. FRCC verified completion of the required mitigating activities and additional activities.
2015-07-30 | Midwest Reliability Organization (MRO) | Fibrominn, LLC (FBR) | NCR11300 | MRO2013013215 | FAC-008-3 | R6 | On December 6, 2013, FBR submitted a Self-Certification stating that as a GO, it had an issue of FAC-008-3 R6. Specifically, FBR failed to have Facility Ratings that were consistent with its documentation for determining its Facility Ratings because it did not have any documentation of its equipment ratings. FBR was involuntarily registered as a GO and GOP on December 20, 2012. FBR was not prepared for its compliance obligations when it was involuntarily registered. Since it was registered, FBR has been developing its NERC Compliance Program and has obtained the expertise of outside resources for the development of its Facility Ratings methodology and the verification of its determinations of the Facility Ratings. The instance of noncompliance began on January 1, 2013, when the standard became effective, and ended on December 1, 2013 when FBR obtained documentation of its equipment ratings and verified that there was no impact on the Facility Rating. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability to the bulk power system (BPS). This facility does not have significant impact on the BPS as it only produces a maximum output of 73.3 MVA, is not identified as a black start unit, and is not a base load unit. Additionally, FBR has no history of system events associated with Facility Ratings and was using good engineering judgment by focusing on its generator rating and step-up transformer rating for determining its Facility Rating. Finally, FBR's overall Facility Rating did not change as a result of receiving the equipment ratings documentation. No harm is known to have occurred. This is FBR's first instance of noncompliance with FAC-008-3. | To mitigate this issue, FBR: 1) Obtained documentation of its equipment ratings, and it verified on December 1, 2013, that the equipment ratings did not impact the Facility Rating.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Constellation Mystic Power, LLC (CMP) | NCR11088 | NPCC2015015081 | PRC-005-1.1b | R2; R2.1 | On April 6, 2015, Constellation Mystic Power, LLC submitted a self-report stating that as a GO, it had an issue of PRC-005-1.1b R2.1. Exelon Generation Co. LLC, CMP's parent company, discovered instances where field personnel did not strictly follow Exelon's established battery maintenance intervals. Exelon Procedure ER-EP-405 ("Exelon Power NERC Protective System Maintenance Program") defined battery maintenance intervals as "3 months, 4 months maximum" from the previous maintenance date. CMP completed 2nd quarter battery testing for its nine battery banks on June 17, 2014, and 3rd quarter battery testing on October 29, 2014, an interval of 134 days. According to the maintenance program, the 3rd quarter battery testing should have been completed by October 16, 2014, however CMP exceeded this date by 13 days. The root cause of this issue was conflicting information regarding testing intervals. Exelon has an additional Procedure ER-EP-153, titled "Quarterly Inspection and Maintenance of Station Batteries," which provides the required activities for battery maintenance, however does not specify a specific testing interval. The title of this Procedure created confusion among personnel, resulting in the 3rd quarter tests being completed during the 3rd quarter, but not within the 3-month, 4-month maximum interval defined in Procedure ER-EP-405. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the violation was minimal, as the batteries were tested only 13 days after the missed interval from the previous test. In addition, the batteries were in good working condition over the period in question, demonstrated by the completed inspection and maintenance on October 29, 2014 describing the batteries as having no deficiencies or corrective actions required. No harm is known to have occurred. NPCC considered Constellation Mystic Power, LLC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CMP: 1) Revised both ER-EP-405 and ER-EP-153 to define consistent intervals of 90 days, 120 days maximum, for battery maintenance activities; 2) Conducted personnel training on the revised procedures to prevent recurrence; and 3) Updated its centralized battery tracking matrix to properly calculate the 90/120 days between test dates. NPCC has verified the completion of all mitigation activity.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Granite Ridge Energy, LLC (GRE) | NCR07101 | NPCC2015015086 | PRC-005-1b | R2; R2.1 | Prior to an offsite Compliance Audit conducted from February 4, 2015 to April 9, 2015, GRE reported to the auditors that as a GO, it had an issue of PRC-005-1b R2.1. In 2008, GRE hired a contractor to develop a program to identify and track NERC required maintenance for devices required by PRC-005. GRE informed auditors that in preparation for the audit, they noticed that the CT11 and CT12 Generator Step Up Transformer primary and backup relays were not included in the maintenance and testing scheduling matrix, and therefore had missed their required testing interval. The relays were previously tested in 2006, and with a six year interval stated in GRE's maintenance and testing program, should have been tested again in 2012. The root cause of this issue was an inadvertent exclusion of the CT11 and CT12 GSU primary and backup relays from GRE's maintenance and testing matrix. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The relays in question are microprocessor relays that are thoroughly monitored devices and provide alarming through DCS into a 24x7 staffed control room. The missing relays make up 4 of 295 devices in GRE's protection system, or 1.4%. Under the requirements of the new PRC-005-2 standard, these devices would qualify for 12-year testing intervals. Once GRE discovered the discrepancy, they immediately worked with their contracting company to perform the maintenance on the relays at the earliest possible time. The maintenance and testing was completed on March 11, 2015. No issues were detected with the relays when the maintenance was performed, and the testing results were deemed satisfactory. No harm is known to have occurred. A NOCV covering violations of NPCC200900110 for GRE was filed with FERC under NP11-83-000 on January 31, 2011. On March 3, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. NPCC considered GRE's compliance history and determined that the instant issue was appropriate for a Compliance Exception because the underlying conduct of the two instances was different. In the previous violation, GRE did not perform DC circuit testing on devices that were listed on their testing schedule. In this instance, GRE performed maintenance and testing on all devices within the intervals listed in their maintenance and testing matrix, however the relays in question were inadvertently excluded from the matrix and therefore overlooked during maintenance scheduling. The risk of the violation was reduced because the relays were actively monitored devices in the control room and provided alarming in the event of any issue. | To mitigate this issue, GRE: 1) Performed the required maintenance on the CT11 and CT12 relays on March 11, 2015; 2) Updated maintenance tracking spreadsheet to include the CT11 and CT12 relays; and 3) Updated Preventative Maintenance tasks and job plans into the CMMS (computerized maintenance management system) to include CT11 and CT12 relays. NPCC has verified the completion of all mitigation activity.
2015-07-30 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2014014201 | PRC-023-2 | R1 | On August 7, 2014, Duke submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R1. Duke identified relays at seven terminals with setpoints that did not meet PRC-023-2 R1 Criterion 1, requiring transmission line relays to be set so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). Duke discovered the issue on June 10, 2014, while the Duke transmission planning department was performing an extent of condition assessment as a result of the discovery of an issue with PRC-023-2 R1 by an affiliate located and operating in the footprint of another Regional Entity. On June 10, 2014, the Duke protection and control engineering department ran a query in its relay loadability spreadsheet. The query compared Facility Ratings from the transmission planning department’s Facility Ratings database, with actual relay setpoints. Duke determined that the settings were accurate and met criterion 1. The Duke transmission planning department reviewed the database for accuracy and discovered that it did not include three Facility Rating changes, the first of which occurred on September 23, 2013. When Duke entered the correct Facility Ratings into the database, it found that relays at seven terminals were out of compliance with criterion 1. Specifically, both ends of Clingman black and Clingman white 230 kV lines were set at 143%, both ends of Akens white 230 kV line were set at 149%, and one end of the Dutchman white 230 kV line was set at 144%. This issue lasted from September 23, 2013, when the earliest Facility Rating change occurred and Duke failed to record it in the database, through June 20, 2014, when Duke adjusted the relay setpoints. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Duke’s failure to set transmission line relay trip setpoints in accordance with PRC-023-2 R1 criterion 1 could limit the transmission operators’ ability to take remedial action while protecting transmission equipment. However, Duke maintained the setpoints at greater than 142% of the Facility Rating, providing the operator substantial opportunities for remedial action. Further, results of Duke’s transmission planning contingency studies show that the maximum flow on any of the affected lines did not exceed 71% of the Facility Rating and would not approach the relay setpoints. Further, the results of the contingency studies show that loss of the lines would not cause instability. No harm is known to have occurred. SERC considered Duke and its affiliates’ PRC-023 R1 compliance history in determining the disposition track. Duke and its affiliates’ relevant prior noncompliance with PRC-023 R1 includes: NERC Violation IDs, SERC2011006476, FRCC2011008525, SERC2014013665, and FRCC2014014005. SERC determined that Duke and its affiliates’ compliance history should not serve as a basis for applying a penalty. In SERC2011006476, Duke failed to set 130 PRC-023 applicable relays to the appropriate setpoint, including 101 that Duke failed to set so that they did not operate at or below 150% of the highest seasonal Facility Rating of the circuit. Although the instant issue involves setting relays to the same setpoint, Duke identified the instant issue while performing an extent of condition assessment across its affiliates after self-reporting an issue to FRCC (see FRCC2014014005) and promptly mitigated the instant issue within 10 days of discovering it. In FRCC2011008525, Duke’s affiliate Progress Energy Florida (PEF), now Duke Energy Florida (DEF), failed to properly set relays to meet the PRC-023 R1 criteria because the relay settings were calculated between 1992 and 2002, a time prior to the mandatory and enforceable period for NERC Reliability Standards when PEF chose settings based on taps available in the installed electromechanical relays which provided coverage closest to 150% of the maximum transformer nameplate rating. The instant issue is substantially different from the prior issue because in the instant issue Duke determined that three prior Facility Rating changes were not incorporated into the relay setpoints, causing the relay setpoints to be set below 150% of the Facility Ratings. In SERC2014013665, Duke failed to establish a single relay setpoint within 24 months of being notified by its Planning Coordinator (PC) of a change to a facility in accordance with PRC-023-1 R3. The instant issue is substantially different from the prior issue because in the instant issue Duke failed to update relay setpoints that already existed instead of establishing a new relay setpoint after being notified by a PC that a facility should be addressed under PRC-023 R1. In FRCC2014014005, Duke’s affiliate DEF identified two transmission lines on which its relay setpoints were set such that they operated below 150% of the Facility Ratings. Duke and its affiliates performed an extent of condition review which identified the instant issue and led to the submission of the Self-Report to SERC. After discovering the instant issue, Duke promptly mitigated it within 10 days. | To mitigate this issue, Duke: 1) developed a procedure that details the transmission planning role and responsibility for complying with PRC-023-2; 2) gave training to transmission planning personnel directly responsible for Facility Ratings and made other personnel aware of the new procedure; 3) ran the Facility Ratings change report and Facility Rating database reports on a monthly basis and performed detail reviews; 4) migrated to one system for maintaining Facility Ratings – the Facility Ratings database; and 5) set up automatic reminders for monthly reviews of Facility Ratings change report and PRC-023 report reviews. SERC has verified the completion of all mitigation activity.
2015-07-30 | Southwest Power Pool Regional Entity (SPP RE) | Lea County Electric Cooperative, Inc. (LCEC) | NCR06047 | SPP2015014971 | PRC-005-1.1b | R2; R2.1 | During a Compliance Audit conducted on June 8, 2015, SPP RE determined that LCEC, as a Distribution Provider and Transmission Owner, had a minimal risk instance of noncompliance with PRC-005-1.1b R2; R2.1. LCEC’s relays were not tested or maintained within the defined intervals contained in its Protection System Maintenance and Testing Program (PSMTP). In its PSMTP, LCEC had relay testing intervals set at a maximum of fifty (50) months. However, 21 out of 37 LCEC’s current relay tests were conducted fifty-five months after the previous relay tests. This instance of non-compliance began in May 2014, the month the relays should have been tested, and ended in October 2015, when LCEC tested its relays. The root cause of this issue was LCEC’s inattention to adhere to the intervals defined in its PSMTP. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although LCEC tested its relays outside of their documented intervals, it did conduct tests soon after the interval (5 months after), and the relay test results demonstrated that all relays were in good working condition. Furthermore, the maximum interval for relays in PRC-005-2 is six (6) years for unmonitored relays, and twelve (12) years for monitored relays; therefore, LCEC’s relay tests that were conducted at 55 months were within a NERC acceptable interval. No Violation History. | To mitigate this minimal risk instance of noncompliance, LCEC: 1) Tested all of its relays; 2) Changed its PSMTP relay test intervals from fifty (50) to adopt the NERC intervals listed in Table 1 of PRC-005-2; and 3) Developed an automated system to provide notifications in advance of relay testing deadlines.
2015-07-30 | Southwest Power Pool Regional Entity (SPP RE) | The Empire District Electric Company (EDE) | NCR01155 | SPP2014014084 | PRC-005-1a | R2; R2.1 | On June 23, 2014, EDE submitted a Self-Report stating that, as a Transmission Owner and Distribution Provider, it had a minimal risk instance of noncompliance with PRC-005-1 R2.1 because it did not have evidence that all of its Protection System devices were maintained and tested within the defined intervals of its Protection System maintenance and testing program (Program). Specifically, EDE did not have documented battery test results from one battery bank at its Riverton plant, complete documented test results for two additional battery banks at the Riverton plant, and documented current transformer (CT) test results for one CT at one of its Energy Center generating units. The noncompliance affected less than 5% of EDE’s total protection system devices. The SPP RE determined that the minimal risk instance of noncompliance began on January 1, 2012, the date EDE did not have documented test results for the battery bank at its Riverton plant, through December 17, 2014, the date testing of all protection system devices subject to this noncompliance was completed. The root cause of the minimal risk instance of noncompliance was human error. EDE technicians did not adhere to EDE’s Program when scheduling and testing these protection system devices. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. EDE had testing records for two of the three Riverton battery banks, albeit incomplete per its Program. Although documentation could not be found for one of the Riverton battery banks, the Riverton plant batteries are continuously monitored and EDE operators will receive an alarm for voltage deviations. The lack of testing of the Energy Center CT also posed a minimal risk to the reliability of the bulk power system because the unit was a small peaking gas turbine that was not run regularly. Additionally, no issues were found with the CT when tested. No actual harm occurred as a result of this instance of noncompliance. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including EDE’s noncompliance with PRC-005-1 R2.1 was filed with FERC under RC12-16-000 on September 28, 2012. The 60-day review period passed on November 28, 2012. A Settlement Agreement covering violation of PRC-005-1 R2.1 for EDE (SPP201100632) was filed with FERC under NP14-4-000 on October 30, 2013. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SPP RE considered EDE's compliance history and determined that the instant issue is appropriate for Compliance Exception treatment because although the prior instances were of the same Standard and Requirement, the underlying conduct of the three instances was different. The prior violation and issue of noncompliance were related to a lack of testing due to conflict of staffing schedules (FFT) and a lack of documentation of testing due to a server error (SPP201100632) and were minimal risk issues. This minimal risk instance of noncompliance was self-reported and promptly mitigated by EDE. Additionally, the instant noncompliance, albeit a repeat, does not indicate a systemic issue of compliance for EDE. | To mitigate this minimal risk instance of noncompliance, EDE: 1) Implemented the standard battery inspection form at the Riverton plant to ensure proper battery inspection documentation; 2) Tested the Riverton plant batteries, including conductivity testing and string continuity testing; and 3) Tested the CT at the Energy Center. SPP RE has verified the completion of all mitigation activity.
2015-07-30 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Little Rock District (COE-LR) | NCR06037 | SPP201000209 | FAC-001-0 | R3 | On January 18, 2010, the United States Corps of Engineers-Little Rock District (COE-LR) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R3. Specifically, the COE-LR does not document, maintain, and publish facility connection requirements (FAC-001-0 R3). Therefore, the COE-LR could not make documentation of these requirements available to the users of the transmission system, the Regional Reliability Organization, and NERC. The root cause of the issue of noncompliance is that COE-LR has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE-LR does not believe it is a Transmission Owner, it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-LR does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-LR’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities an extensive evaluation and approval process would be necessary for any interconnection requests from outside entities. No actual harm has occurred due to this issue of noncompliance. The COE-LR has no relevant compliance history. | To mitigate this issue, COE-LR will: 1) develop facility connection requirements addressing all subrequirements and requirements of the standard; and, 2) publish these requirements. Mitigation activities are scheduled for completion on October 7, 2015.
2015-07-30 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Tulsa District (COE-Tulsa) | NCR06038 | SPP201000210 | FAC-001-0 | R3 | On January 18, 2010, the United States Corps of Engineers-Tulsa District (COE-Tulsa) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R3. Specifically, the COE-Tulsa does not document, maintain, and publish facility connection requirements (FAC-001-0 R3). Therefore, the COE-Tulsa could not make documentation of these requirements available to the users of the transmission system, the Regional Reliability Organization, and NERC. The root cause of the issue of noncompliance is that COE-Tulsa has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE-Tulsa does not believe it is a Transmission Owner, it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-Tulsa does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-Tulsa’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities an extensive evaluation and approval process would be necessary for any interconnection requests from outside entities. No actual harm has occurred due to this issue of noncompliance. The COE-Tulsa has no relevant compliance history. | To mitigate this issue, COE-Tulsa will: 1) develop facility connection requirements addressing all subrequirements and requirements of the standard; and, 2) publish these requirements. Mitigation activities are scheduled for completion on October 30, 2015.
2015-07-30 | Southwest Power Pool Regional Entity (SPP RE) | USACE – Kansas City District | NCR01357 | SPP2011008778 | PRC-005-1 | R1; R1.1, R1.2 | During a Compliance Audit conducted from December 14, 2011, through December 15, 2011, SPP RE determined that USACE Kansas City District, as a Generator Owner and Transmission Owner, had a minimal risk instance of noncompliance with PRC-005-1 R1; R1.1, R1.2. During a revision of its Protection System maintenance and testing procedure (PSMTP) performed on April 15, 2011, USACE Kansas City District inadvertently omitted the intervals, basis for intervals, and a summary of maintenance and testing procedures for its DC Circuitry from its PSMTP. The PSMTP stated that USACE Kansas City District would inspect DC Circuitry in the event of a wiring change or a major overhaul of the protection system (e.g. replacing relays); but did not include the specifics required for compliance with PRC-005-1. This instance of non-compliance began on April 15, 2011, the effective date of the revision of the PSMTP , and ended on April 1, 2013, when USACE Kansas City District successfully mitigated the instance of noncompliance. The root cause of this issue was an inadvertent omission during a document revision. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although USACE Kansas City District inadvertently omitted the intervals, basis for intervals, and a summary of maintenance and testing procedures for its DC Circuitry from its PSMTP on April 15, 2011, USACE Kansas City District had successfully tested its DC Circuitry under the prior version of its PSMTP in January 2011. Additionally, the maximum interval for DC Circuitry testing in PRC-005-2 is six (6) years; therefore, USACE Kansas City District’s DC Circuitry testing was within a NERC acceptable testing interval. USACE Kansas City District also uses microprocessor relays with trip coil monitors and circuit continuity checks, and its electromechanical relays are monitored 24/7. No actual harm occurred as a result of this instance. | To mitigate this minimal risk instance of noncompliance, USACE Kansas City District revised its PSMTP to incorporate intervals, basis for intervals, and a summary of maintenance and testing procedures for DC Circuitry to comply with the current version of PRC-005-2. SPP RE has verified the completion of all mitigation activity.
2015-07-30 | Western Electricity Coordinating Council (WECC) | Pend Oreille County Public Utility District No. 1 (POPD) | NCR05315 | WECC2015014642 | TOP-002-2b | R11 | On February 18, 2014, POPD self-certified that, as a Transmission Operator, it was compliant with TOP-002-2b R11 for calendar year 2013. On June 30, 2014, WECC notified POPD that it was conducting a validation of “Compliant” self-certifications submitted by U.S. Registered Entities for calendar year 2013. As part of the validation review process, WECC issued data requests for certain evidence to validate POPD’s compliance. Then, a WECC SME conducted interviews with POPD compliance staff, and determined that POPD had a compliance exception of TOP-002-2b R11, for its failure to demonstrate through documentation that it determined its Transmission Planning Study performed in 2012, remained valid for use in current day, next-day, and seasonal planning activities for the period January 1, 2013 through April 18, 2014. On February 18, 2015, because of the discussions between WECC and POPD, POPD submitted a Self-Report stating that, as a Transmission Operator, it was in possible non-compliance with TOP-002-2b R11. The root cause of this compliance exception was POPD’s lack of compliance understanding and the lack of an administrative compliance process to ensure that the review of its 2012 Transmission Planning Study was documented and used to determine SOLs. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, POPD failed to document its review of seasonal studies. POPD was conducting reviews of its studies related to current system conditions, but could not provide documentation of those reviews. This compliance exception is primarily a documentation error, because for the duration of this compliance exception, POPD’s system was planned through undocumented discussions between POPD engineering and system operating personnel, and POPD has operating procedures in place for response and coordination of unanticipated events on its system. POPD is relatively small, with very little change in its footprint since the last WECC Compliance Audit. The POPD system contains a small inventory of BES facilities and elements, with limited connectivity to the BES. WECC considered POPD's compliance history in determining the disposition track and determined there were no relevant instances of noncompliance. No harm is known to have occurred. | To mitigate this issue, POPD conducted a review to evaluate its 2011 Transmission Study for applicability to the 2014 winter season.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | American Bituminous Power Partners, L.P. (ABPP) | NCR00680 | RFC2015014731 | FAC-008-3 | R6 | During the Compliance Audit conducted from February 9, 2015 through February 18, 2015, ReliabilityFirst determined that ABPP, as a Generator Owner, had an issue with FAC-008-3 R6. During the Compliance Audit, ReliabilityFirst reviewed a total of nine of ABPP’s Facility Ratings, and could not confirm the accuracy of three of them: (1) the maximum design limit MW rating for its generator at lagging power factor, (2) the maximum design limit MW rating for its generator at leading power factor, and (3) the maximum design limit for its manual disconnect switch. ReliabilityFirst determined that these three Facility Ratings and the calculations supporting them were incorrect and required modification. The root cause of this violation was human error resulting from miscalculations by a single individual. The maximum design limit MW ratings for the generator at both lagging and leading power factor and the maximum design limit of the manual disconnect switch were all incorrect because the individual making the ratings calculation multiplied the wrong numbers to get the rating. For the generator ratings, ABPP was not using the correct numbers per the generator specifications. For the switch, ABPP incorrectly used the rating of the breaker instead of the rating for the manual disconnect switch. These were mistakes made by an individual who is no longer employed by ABPP. Furthermore, as part of its Mitigating Activities discussed in detail below, ABPP took measures to reduce the likelihood that a single employee could cause similar errors in the future. The duration of this noncompliance is from January 1, 2013, the date ABPP was required to comply with FAC-008-3 R6, to February 17, 2015, the date ABPP completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The new and correct values for the maximum design limit MW ratings for the generator at both lagging and leading power factor and the maximum design limit for the manual disconnect switch did not impact the conclusion that ABPP’s generator is the most limiting component. At all times before, during, and after the noncompliance, ABBP’s generator was the most limiting component and there were no devices in danger of overloading. ABPP did not have to de-rate or ramp down the generator to protect any equipment. At all times, ABPP could run its generator at full output up to its maximum rating and no facility device would overload. No harm is known to have occurred. ReliabilityFirst determined that ABPP's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, ABPP: 1) committed to document and correct the three incorrect values and the Facility Ratings table; 2) corrected the maximum design limit of the generator for leading and lagging power factor of 0.9 from 99.75 MW to 95.004 MW; 3) corrected the rating for the manual disconnect switch from 190.992 MVA to 143 MVA; 4) ensured that the numbers used for calculating the Facility Ratings were correct through an additional review by the Senior Plant Engineer and Plant Manager before submitting the revised numbers to ReliabilityFirst; and 5) submitted a revised Facility Ratings table with the correct Facility Ratings on February 17, 2015, prior to the close of the Compliance Audit on February 18, 2015. ABPP’s Mitigating Activities will prevent further violations by ensuring that the Facility Ratings table is aligned with the requirements of the FAC-008 and that all Facility Ratings are properly calculated and documented. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | AES Beaver Valley L.L.C. (AESBV) | NCR00663 | RFC2014013635 | FAC-008-3 | R6 | During a Compliance Audit conducted from February 17, 2014 to February 26, 2014, ReliabilityFirst determined that AESBV, as a Generator Owner, was noncompliant with FAC-008-3 R6. AESBV failed to provide evidence that it established Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology. AESBV’s documentation concluded that Generator #3 (114 MVA) was the most limiting equipment of the AESBV Facility, when in fact Generator #2 and the Generator Step-Up Transformer MAX01 were the most limiting equipment (110 MVA) of the Facility. Per AESBV’s Facility Ratings methodology, the overall Rating for the Facility should have been 145 MVA, but AESBV established an overall Rating of 149 MVA. Therefore, AESBV did not have Facility Ratings for its solely and jointly owned Facilities that were consistent with the associated Facility Ratings methodology. The root cause of this noncompliance was human error via an isolated miscalculation. In calculating the overall rating for the facility, AESBV should have used the MVA value from its most limiting equipment. However, based on its previous misidentification of the most limiting equipment, AESBV used an incorrect MVA value and calculated an incorrect overall rating for the facility. The duration of this issue is from January 1, 2013, the date by which AESBV should have established Facility Ratings consistent with the associated Facility Ratings methodology, to February 22, 2014, the date AESBV provided evidence to ReliabilityFirst that it revised its procedure and documentation to establish an overall Facility Rating consistent with the associated Facility Ratings methodology. | ReliabilityFirst determined that the subject noncompliance posed a minimal risk to the reliability of the bulk power system based on the following factors. AESBV has not been synchronized to the grid since July 20, 2013 because AESBV is a coal fired plant that AES determined is no longer economical to operate, so for most of the duration of this noncompliance, AESBV could not have had any impact on the BES. AESBV is currently in the process of deregistering as a Registered Entity. No harm is know to have occurred. ReliabilityFirst determined that AESBV’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, AESBV revised its Facility Rating and Methodology Procedure to include Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology. This resulted in changing the Facility Rating from 149 MVA to 145 MVA. AESBV’s Facility Ratings Methodology now states that Generator #2 and Generator Step-Up Transformer MAX01 are the most limiting equipment of the AESBV Facility. ReliabilityFirst concluded that these revisions, implemented by AESBV during the course of the Compliance Audit, demonstrate compliance with FAC-008-3 R6. Although AESBV’s mitigation does not fully prevent recurrence of the noncompliance, since AESBV is deregistering, recurrence is not a concern. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | AES Beaver Valley L.L.C. (AESBV) | NCR00663 | RFC2014013636 | PRC-005-1.1b | R2 R2.1 R2.2 | During a Compliance Audit conducted from February 17, 2014 to February 26, 2014, ReliabilityFirst determined that AESBV, as a Generator Owner, had an issue of PRC-005-1.1b R2. AESBV failed to provide evidence of current maintenance and/or testing of DC control circuitry for 3 13.8 kV bus differential relays, and the dates when the DC control circuitry for the 3 13.8 kV bus differential relays were last maintained and tested. The number of applicable devices that AESBV did not maintain and test within the defined intervals (R2.1 and R2.2) was less than 5% of AESBV’s total Protection System devices. The root cause of this noncompliance was AESBV’s misunderstanding of the requirements of PRC-005-1.1b R2. AESBV did not understand that maintenance and testing of the DC control circuitry associated with the 13.8 kV bus differential relays was required by PRC-005-1.1b R2 because it did not consider the 13.8 kV buses generator interconnection Facilities. AESBV also provided a letter from the contractor it had used to conduct its maintenance and testing in 2011 which stated that DC control circuitry tests were not performed on the relays because it was not possible to safely conduct the tests without an outage. AESBV incorrectly believed that this letter provided additional and sufficient justification for failing to conduct certain maintenance and testing required by PRC-005. ReliabilityFirst, however, concluded that the DC control circuity associated with the 13.8 kV bus differential requires maintenance and testing under PRC-005 even if the only way to safely isolate and conduct the testing is to schedule outages to the Nova Chemical Plant and other relevant loads and equipment. The duration of this noncompliance is from November 25, 2013, the date AESBV was required to comply with PRC-005-1.1b R2, to May 6, 2015, the date AESBV completed its mitigating activities. | ReliabilityFirst determined that the subject noncompliance posed a minimal risk to the reliability of the bulk power system based on the following factors. AESBV has not been synchronized to the grid since July 20, 2013 because AESBV is a coal fired plant that AES determined is no longer economical to operate, so for most of the duration of this noncompliance, AESBV could not have had any impact on the Bulk Electric System (BES). AESBV is currently in the process of deregistering as a Registered Entity. No harm is know to have occurred. ReliabilityFirst determined that AESBV's compliance history should not serve as a basis for applying a penalty. | In the Mitigating Activities, AESBV committed to take the following actions. AESBV agrees that, if it resynchronizes the facility to the grid, it will bring the facility into full compliance with the version of PRC-005 in effect at that time by the time AESBV resynchronizes the facility to the grid. Since AESBV is not operational and is in the process of deregistering, there is no need to test or maintain the subject devices unless it becomes operational, which is what AESBV has agreed to do.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Alcoa Power Generating Inc. (Alcoa) | NCR00667 | RFC2015014608 | VAR-002-3 | R3 | On January 23, 2015, Alcoa submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-3 R3. The Alcoa facility at issue has four generator units, which produce approximately 750 MW of generation that function primarily to serve Alcoa Inc.’s internal load related to aluminum production. The units at issue, Generator Units 1 and 2, connect directly to a 15 kV distribution station to supply power to the smelting and rolling loads. On January 6, 2015, Alcoa brought Generator Unit 2 online after it had been offline for a tube leak repair. Shortly thereafter, the voltage began to swing. To steady the voltage and reduce the swing, Alcoa determined it was necessary to switch Generator Unit 1 AVR from automatic mode into manual mode. When Generator Unit 1 AVR was placed in manual mode, the on-shift operator timely notified the Transmission Operator, Vectren Transmission System Operations (Vectren), of the status change. Subsequently, on Friday January 16, 2015, Alcoa determined that it was appropriate to return Generator Unit 1 AVR back to automatic mode. The operators notified the shift supervisor, who noted the status change in the supervisor log and the abnormal operations log. However, there is no communication log entry indicating that the operator contacted Vectren to report the status change within 30 minutes. On the following business day, Monday, January 19, 2015, Alcoa performed its regularly scheduled audit of communication logs and discovered the communication failure. Alcoa performed this audit pursuant to its procedure (WAR-VAR-002-3 Instruction Generator Operation for Maintaining Network Voltage) for meeting the requirements of VAR-002-3 and its capacitor agreement with Vectren for maintaining VAR. This procedure dictates that operations communications logs must be audited every business day to verify that all NERC required communications are properly made. After Alcoa discovered this communication failure, it immediately notified Vectren of the status change. The root cause for this noncompliance was an isolated human performance issue caused by time pressures associated with abnormal conditions related to Alcoa Inc.’s other internal, industrial activities, including high pressure steam, rolling mill hot water, and potline arrangement. When Generator Unit 1 AVR was placed back into automatic mode, the operators were also communicating status and redirecting plant personnel to address the abnormal conditions.. For example, two potline interruptions occurred in the smelter at this time, which the operators were required to address and correct. These abnormal conditions and associated time pressures resulted in the operators failing to follow Alcoa’s procedure and notify Vectren of the status change related to Generator Unit 1 AVR. The duration of this noncompliance is from January 16, 2015, the date Alcoa returned Generator Unit 1 AVR to automatic mode, to January 19, 2015, the date Alcoa notified Vectren of the status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, Alcoa’s VAR agreement with Vectren was, and is currently, suspended. As a result, Vectren, as the LBA, has Alcoa running at VARs lower than the agreement to meet Vectren’s needs and gives Alcoa leeway to manage the voltage to meet Alcoa’s 15 kV needs. Second, Alcoa continues to monitor and communicate conditions real time to Vectren. Communication logs provide supporting evidence that Alcoa contacts Vectren twice per day to verify that the VAR agreement is suspended and that the VARs are meeting Vectren’s expectations. Considering these factors, Vectren would have been made aware of any VAR-related issues during the period of this noncompliance and would have been able to take appropriate mitigating actions. ReliabilityFirst determined that Alcoa’s compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, Alcoa: 1) reviewed operating procedure WAR-VAR-002-3 with the control room operators on duty during the noncompliance and reemphasized the requirement to contact Vectren of a change in status of the AVR; 2) reviewed the requirements of VAR-002-3 with all plant personnel and retrained the control room operators on these requirements during Alcoa’s first quarter Town Hall training sessions; and 3) conducted refresher training on human performance error trap recognition and recommended practices. Alcoa’s mitigation actions help prevent future violations by ensuring that all plant personnel, and control room operators in particular, are fully aware of and retrained on Alcoa’s WAR-VAR-002-3. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTEE) | NCR00753 | RFC2014014524 | PER-005-1 | R2 | On December 5, 2014, DTEE submitted a Self-Report stating that, as a Balancing Authority, it had an issue with PER-005-1 R2. DTEE determined that a decertified employee worked several shifts prior to completing the Training Performance Evaluation as required. DTEE modified training for EOP-004-2, and a System Operation Center (SOC) employee completed the web-based training, but prior to completing the Training Performance Evaluation for the training, the employee went on an extended medical leave of absence. On October 1, 2014, while on medical leave, DTEE changed the status of the employee to decertified because the employee had not completed the Training Performance Evaluation, which is a post-training test to evaluate whether the employee is competent to perform the subject task(s). DTEE notified the employee via email, but the employee did not view the email. DTEE, during its root cause analysis, determined that the number of email messages that the employee received while on medical leave reduced the likelihood of the employee viewing the email notification. On November 11 and 12, 2014, the employee came back to work to acclimate himself and prepare for a meeting, but DTEE did not give the employee a second notification about his decertification at that time. On November 13, 2015, the employee reported to work as scheduled for a nightshift. While working the first nightshift, the employee sent an email to an SOC training staff employee inquiring what training needed to be completed prior to year end. The training staff employee did not view the email until he returned to work on Monday, November 17, 2014. In the meantime, the SOC employee finished the first nightshift and returned to work the following three nightshifts on November 14-16, 2014. Upon viewing the email, the training staff employee notified management of the issue. On November 17, 2014, the employee completed the required Training Performance Evaluation and was recertified. The duration of this noncompliance is from November 13, 2014, the date the employee began working (despite DTEE having decertified him), to November 17, 2014, the date the employee completed the Training Performance Evaluation and DTEE recertified him. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the employee did not complete the Training Performance Evaluation, he did complete the training itself, including questions following the training relating to the content of the training. Additionally, the employee is an experienced system supervisor, and the training in question related to event reporting. The employee is aware of his responsibilities for event reporting and has performed the subject tasks numerous times. Additionally, the issue was short in duration because the employee proactively inquired as to what additional training he needed to complete before the end of the year, and the SOC training staff promptly notified management of the employee’s incomplete training. No harm is known to have occurred. ReliabilityFirst considered DTEE's compliance history and determined there was no relevant history of noncompliance. ReliabilityFirst determined that DTEE's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, DTEE: 1) revised the MOC ADM-001 Training Program document to implement required communication when an employee is decertified, and include this revision in training documents; 2) revised the DO-SOC-TRNG-0001 SOC Training Program document to implement required communication when an employee is decertified, and include this revision in training documents; 3) revised the MOC work schedule to indicate if an employee is not certified or not qualified in order to provide a visual indication of the change in status; 4) revised the SOC work schedule to indicate if an employee is not certified or not qualified in order to provide a visual indication of the change in status; 5) provided visual control room qualification status indication for the control room; and 6) revised the training program documentation to explain decertification and certification requirements and expectations. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Essential Power OPP, LLC (EPOPP) | NCR00212 | RFC2014014278 | PRC-005-1.1b | R2 | On September 2, 2014, EPOPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1.1b R2. EPOPP determined that seven solid state relays in the switchyard were misclassified as microprocessor relays. Specifically, EPOPP discovered the misclassifications during a review of EPOPP’s Program. In a compliance review following the discovery of these misclassifications, EPOPP determined that these seven solid state relays were last tested in 2009. EPOPP’s Program requires all solid state relays to be tested every four years, while microprocessor relays must be tested every six years. Therefore, these seven solid state relays should have been retested in 2013 and testing was overdue. While performing mitigation for the above noncompliance, EPOPP discovered another noncompliance with PRC-005-1.1b R2. EPOPP reported the discovery of this additional noncompliance to ReliabilityFirst on February 18, 2015. During mitigation, EPOPP reviewed its 2009 testing records and could not locate the 2009 testing records for the GT2 LPSO microprocessor relay. EPOPP claims it tested the GT2 LPSO microprocessor relay in 2009 along with the rest of EPOPP’s generation station relays, but does not have documentation to substantiate its claim. The two noncompliances are both isolated instances of missing testing or documentation out of a five year period of time that involved hundreds of tests. The root cause for both noncompliances was human error. The relays were classified by an individual via visual inspection and recorded in a spreadsheet. In the spreadsheet, the individual meant to mark the seven solid state relays as such, but mistakenly marked the seven solid state relays as microprocessor relays. The test records for one GT2 LPSO microprocessor relay were also inadvertently misplaced as a result of human error. The duration of this noncompliance is from December 31, 2013, the start date of the Compliance Audit assessment period, to April 30, 2015, the date EPOPP proposed to complete its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. EPOPP conducted an in-depth assessment of how each of the seven solid state relays would affect the BPS. The assessment revealed that none of the seven relays have direct transfer trips affecting the First Energy Yard breakers. All of the seven relays would remove one or both EPOPP Units from the BPS, but none of the relays would remove or trip any other systems or breakers from the BPS outside the EPOPP switchyard. Additionally, the GT2 LPSO relay does not trip anything outside of the EPOPP generation facility. Finally, in 2013, the testing for the associated CTs and PTs and trip checks in the switchyard was completed with no reported problems. No harm is known to have occurred. EPOPP has one prior violation of PRC-005 R2 and it is distinguishable from the current noncompliance. The prior violation stemmed primarily from EPOPP’s protection system maintenance and testing program’s failure to include maintenance and testing intervals for associated communication systems or voltage and current sensing devices, which was caused by a lack of understanding the Reliability Standard at issue. In contrast, the instant noncompliance involved isolated, inadvertent human error in misclassifying solid state relays as microprocessor relays, which resulted in seven solid state relays getting tested late, and one missing test record for one microprocessor relay. Therefore, although EPOPP has a prior violation of PRC-005 R2, ReliabilityFirst did not consider EPOPP’s violation history as a factor warranting an alternative disposition method. | To mitigate this issue, EPOPP: 1) performed a review of PRC-005-1.1b R1 and R2 and the current state of EPOPP’s compliance which it completed on September 30, 2014; 2) determined which equipment was missing from or misidentified in EPOPP’s protective system maintenance and testing program, which was also completed on September 30, 2014. During this review, EPOPP discovered that documentation was missing for the 2009 test of its GT2 LPSO microprocessor relay and subsequently reported that additional noncompliance to ReliabilityFirst; 3) performed testing on all missing elements of the EPOPP Protection System and completed all testing on December 26, 2014; 4) reviewed the Essential Power PRC-005 program documents and made all necessary revisions, which it completed on February 28, 2015; and 5) trained all relevant EPOPP staff on the PRC-005 procedure and testing tracking method. This tranining was completed on March 16, 2015. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | PJM Interconnection, LLC (PJM) | NCR00879 | RFC2015014776 | COM-001-1.1 | R5 | PJM oversees and ensures the performance of assigned or shared Transmission Operator (TOP) tasks by its Member Transmission Owners (TOs), also referred to as Local Control Centers, by certain established controls (PJM and TOP controls). For example, PJM has established its PJM TO/TOP Matrix, a document that provides a clear delineation of responsibility for each assigned or shared TOP task. PJM has assigned and shares TOP tasks in the PJM TO/TOP Matrix with Duke Energy Corporation (NCR00761). Duke Energy Corporation is registered via a JRO with Duke Energy Ohio, Inc. for the TO functions (and other functions). During a Spot Check of PJM and Duke Energy Ohio, Inc. and Duke Energy Kentucky, Inc. (collectively, Duke) conducted from March 10, 2015 through March 11, 2015, ReliabilityFirst determined that, as a TOP, PJM had an issue with COM-001-1.1 R5. Duke did not provide evidence of written operating instructions and procedures to enable continued operation of its system during the loss of telecommunications facilities as required by COM-001-1.1 R5. PJM requires its Members, including Duke, to have written operating instructions and procedures to enable continued operation of the Member’s system during the loss of energy management system (EMS) data exchange that specifically address sending data to PJM. Duke provided ReliabilityFirst PJM’s manual and Duke’s procedures that address actions to take during the loss of EMS data exchange and notifications required during loss of data communication. However, Duke’s procedures did not specifically address sending data to PJM and PJM did not otherwise provide evidence specifically addressing written operating instructions and procedures to enable continued operation of its system during the loss of telecommunications facilities. The root cause of the noncompliance was Duke’s misunderstanding of what was required for COM-001-1.1 R5. The duration of this noncompliance is from April 12, 2013, which is the start date of the compliance period for the Spot Check, to March 31, 2015, the date Duke updated its procedures to address continued operation of its system during the loss of telecommunications facilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. COM-001-1.1 R5 calls for documentation and not specific actions in real time to address a loss of telecommunications/EMS data exchange. PJM and Duke had procedures in place to restore telecommunication facilities that were lost, but did not have procedures to enable continued operations during the loss of the telecommunications/EMS data exchange facilities. Furthermore, Duke does in fact have robust data communications facilities (with data available at three different control centers), and thus a complete loss of data communications is less likely. No harm is known to have occurred. ReliabilityFirst determined that PJM's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, PJM required Duke to update its procedures to document the requirement for Duke to send data to PJM as required in PJM Manual 1, Section 3.2.3 during the loss of EMS data exchange. Specifically, Duke’s updated procedures provide that for a planned or unplanned outage of data communications, the TOP will dispatch the appropriate field personnel to substations and tie line substations that have experienced a data communications outage and the field personnel will manually record megawatt flow and voltage data from data worksheets and will communicate that information to PJM. Additionally, to prevent recurrence of the same or similar noncompliance with other PJM members, PJM communicated the expectation to all of its member Transmission Owners that they review their written operating procedures to ensure that they include an explicit procedure addressing the requirements specified in the PJM Manual 1, Section 3.2.3 during the loss of EMS data exchange. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | SERC Reliability Corporation (SERC) | Citizens Electric Corporation (CITZ) | NCR01192 | SERC2015014623 | PRC-005-1b | R1 | On February 6, 2015, CITZ submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-005-1.1b R1. CITZ failed to include activities specifically addressing the maintenance and testing of station battery chargers in its Protection System maintenance and testing program. SERC later determined that the issue extended back to Version 1b of the Standard. NERC revised the definition of Protection System to include battery chargers. The revised definition became effective April 1, 2013. CITZ believed the practices it had in place at that time met the requirements of PRC-005 and the revised definition of Protection System. However, following a regularly scheduled mock audit, CITZ’s consultant suggested that CITZ include language specifically for maintenance and testing of battery chargers in CITZ’s operational policy and lineman technician work plan. SERC reviewed the Protection System maintenance and testing program CITZ had in place at the time of the definition revision, and confirmed that the program did not include the required information for battery chargers. This issue lasted from April 1, 2013, when the revised Protection System definition became enforceable, through September 8, 2014, when CITZ added battery chargers to its Protection System maintenance and testing program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. CITZ’s failure to include battery chargers in its maintenance and testing program could lead to the battery chargers being excluded from maintenance and testing, which could lead to inadequate charging of batteries and possibly the associated inability to operate Protection System relays to prevent transmission equipment damage and personnel injury. However, CITZ continuously monitored each battery and battery charger pair through a Supervisory Control and Data Acquisition (SCADA) system. Alarms would have alerted operators to low battery voltage and other charger malfunctions. The CITZ transmission system consisted of 69 miles of a 138 kV transmission line through three substations. There was one battery charger at each substation. A battery charger malfunction would not cause a relay to trip, but it could prevent a relay from tripping if the battery was allowed to discharge. The Protection System at each substation was backed up by protection features such as “fail to trip” logic at adjacent substations that would have cleared transmission faults if the primary protection failed. CITZ did not experience battery charger-related failures or misoperations. CITZ verified the battery chargers worked properly. No harm is known to have occurred. SERC considered CITZ’s PRC-005-1 R1 compliance history in determining the disposition track. CITZ’s relevant prior noncompliance with PRC-005-1b R1 includes: NERC Violation ID SERC200700015. SERC determined that CITZ's compliance history should not serve as a basis for applying a penalty. The instant issue occurred because CITZ failed to make changes to its program consistent with changes to the definition of Protection System that became effective on April 1, 2013. Since the prior violation occurred in 2007 through 2008, the Mitigation Plan for the prior violation did not address the definition change. | To mitigate this issue, CITZ modified its maintenance and test procedures and lineman technician workplan to specifically include battery chargers and associated maintenance tasks to be performed.
2015-06-30 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014192 | MOD-008-1 | R5 | On July 28, 2014, DEP submitted a Self-Certification stating that, as a Transmission Operator (TOP), it had an issue with MOD-008-1 R5. DEP failed to report changes of its Transmission Reliability Margin (TRM) to its Transmission Service Provider (TSP) and Transmission Planner(s) (TP) within seven days of the change. DEP posts TRM values for each of its interfaces on open access same-time information system (OASIS). That document includes 13 months of import and export values of TRM, reserves, and network reservations for each of DEP’s six interfaces. The interface TRM values are a composite of the TRM values for the Flowgates along each interface. The Flowgate TRM values are used in the calculation of Available Transmission Capacity (ATC). When the ATC values are posted on OASIS, they do not show the individual Flowgate TRM that had been used in the calculation of ATC. The Interface TRM is calculated and posted separately from the ATC. On July 24, 2014, during a review of its MOD-008-1 R5 compliance evidence, DEP determined that it established and utilized the then-current Flowgate TRM values to calculate and post the ATC values on the DEP OASIS on June 18, 2014. However, DEP did not post the then-current Interface TRM values on the DEP OASIS until July 18, 2014, 30 days after the TRM values were changed. DEP further investigated historical ATC changes on OASIS and the posting of Interface TRM values on OASIS which revealed six additional events where the time between the posting of updated ATC values and updated TRM values exceeded seven days. In those cases, the resulting periods of noncompliance ranged from 1 to 211 days, with an average of 77 days for all seven instances. According to DEP, its personnel were confused regarding the relationship between the posting of ATC values in OASIS and posting the Interface TRM values. This issue lasted from March 9, 2011, eight days after DEP’s first change to TRM values without providing updated values to its TSPs and TPs, through July 18, 2014, when DEP posted the current TRM file on OASIS. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEP’s failure to provide updated TRM values to its TSPs and TPs within seven days of a change could have caused TSPs or TPs to incorrectly analyze the impacts and timing of service requests. However, despite this failure, DEP posted the correct ATC values on OASIS, providing that information to neighboring systems in a timely manner. When the DEP TRM values changed and were different from the posted values, the difference between the stale TRM values and the updated TRM values was between 1 and 6%, resulting in small analytical errors. In addition, DEP calculated TRM values in accordance with its documented methodology and performed the TRM calculations at least once every 13 months. No harm is known to have occurred. SERC considered DEP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DEP: 1) provided Transmission Planning notification of the change in process for providing Transmission Planning TRM; 2) provided Transmission Planning with Flowgate TRM; and 3) modified its TRM implementation document on the DEP OASIS to document the process for providing Flowgate TRM to Transmission Planning per the time requirements of MOD-008-1 R5.
2015-06-30 | SERC Reliability Corporation (SERC) | Sam Rayburn G&T Electric Cooperative Inc. (SRG&T) | NCR01307 | SERC2015014733 | FAC-003-1 | R1 | On February 26, 2015, SRG&T submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue with FAC-003-1 R1. SRG&T failed to have a formal transmission vegetation management program (TVMP) for a 0.24 mile 230 kV transmission line that went in service on May 11, 2013. SRG&T identified the issue through a self-assessment that it conducted on its TO function. The SRG&T internal compliance program (ICP) requires a self-assessment each year. The ICP allows for the self-assessment to be based on risk or function. In the past, SRG&T conducted the Self-Assessments by Function spread out over three years, ensuring every function is reviewed twice in the 6-year audit period. Prior to May 11, 2013, the SRG&T member at issue did not have any transmission facilities 200 kV or above, and therefore, did not have FAC-003 compliance obligations. On May 11, 2013, the SRG&T member put a 230 kV line into service that connected a substation to an Entergy line. The SRG&T member failed to have a formal TVMP due to a misunderstanding of the Standard and how it applies to the length of the transmission line. The SRG&T member misinterpreted the line length exemption for generator leads and thought that the line length exemption applied to all lines. This issue lasted from May 11, 2013, when the line went into service, until May 1, 2015, when mitigation was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SRG&T’s failure to officially enact a TVMP could have resulted in miscommunication, confusion, or late communication of imminent vegetation threats, potentially leading to flashover between vegetation and overhead supply conductors. However, the SRG&T member put the 0.24 mile long line into service on May 11, 2013. SRG&T subsequently inspected the line in April, July, and October of 2014 and January 2015, and cut 12 trees near the substation in January 2015. In addition, Entergy removed 22 trees from one right of way that terminated at the SRG&T member substation in August 2014, applied herbicide treatment in September 2014 to two rights of way that terminated at the SRG&T member substation, and conducted aerial vegetation inspections in April, July, and December of 2014. SRG&T had scheduled herbicide treatment for the right of way for October 2014, but did not apply herbicide after determining that Entergy had already applied herbicide the previous month. Although not part of a documented TVMP, SRG&T’s actions indicate that it was regularly inspecting the line and aware of the importance of vegetation management. The line is not part of a designated Interconnection Reliability Operating Limit. No harm is known to have occurred. SERC considered SRG&T’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SRG&T: 1) developed a formal TVMP for the 0.24 mile long 230 kV transmission line and inspected the line based on the TVMP; 2) implemented a formal TVMP with scheduled inspections of the 230 kV transmission line on an annual basis; and 3) set reminders for the inspection in a compliance management and tracking tool.
2015-06-30 | SERC Reliability Corporation (SERC) | Sam Rayburn G&T Electric Cooperative Inc. (SRG&T) | NCR01307 | SERC2015014734 | FAC-003-1 | R2 | On February 26, 2015, SRG&T submitted a Self-Report stating that, as a Transmission Owner (TO), it had an issue with FAC-003-1 R2. SRG&T failed to have an annual plan for vegetation management work to ensure the reliability of the system for a 0.24 mile 230 kV transmission line that went into service on May 11, 2013. SRG&T identified the issue through a self-assessment that it conducted on its TO function. The SRG&T internal compliance program (ICP) requires a self-assessment each year. The ICP allows for the self-assessment to be based on risk or function. In the past, SRG&T conducted the Self-Assessments by Function spread out over three years, ensuring every function is reviewed twice in the 6-year audit period. Prior to May 11, 2013, the SRG&T member at issue did not have any transmission facilities 200 kV or above, and therefore, did not have FAC-003 compliance obligations. On May 11, 2013, the SRG&T member put a 230kV line into service that connected a substation to an Entergy line. The SRG&T member failed to have an annual plan for vegetation management work due to a misunderstanding of the Standard and how it applies to the length of the transmission line. The SRG&T member misinterpreted the line length exemption for generator leads and thought that the line length exemption applied to all lines. This issue lasted from May 11, 2013, when the line went into service, until May 1, 2015, when mitigation was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SRG&T’s failure to officially enact an annual plan for vegetation management work could have resulted in miscommunication, confusion, or late communication of imminent vegetation threats, potentially leading to flashover between vegetation and overhead supply conductors. However, the SRG&T member put the 0.24 mile long line into service on May 11, 2013. SRG&T subsequently inspected the line in April, July, and October of 2014 and in January of 2015, and cut 12 trees near the substation in January 2015. In addition, Entergy removed 22 trees from one right of way that terminated at the SRG&T member substation in August 2014, applied herbicide treatment in September 2014 to two rights of way that terminated at the SRG&T member substation, and conducted aerial vegetation inspections in April, July, and December of 2014. SRG&T had scheduled herbicide treatment for the right of way for October 2014, but did not apply herbicide after determining that Entergy had already applied herbicide the previous month. Although not part of a documented annual plan for vegetation management, SRG&T’s actions indicate that it was regularly inspecting the line and aware of the importance of vegetation management. The line is not part of a designated Interconnection Reliability Operating Limits. No harm is known to have occurred. SERC considered SRG&T’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, SRG&T: 1) developed a formal TVMP for the 0.24 mile long 230 kV transmission line and inspected the line based on the TVMP; 2) implemented a formal TVMP with scheduled inspections of the 230 kV transmission line on an annual basis; and 3) set reminders for the inspection in a compliance management and tracking tool.
2015-06-30 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2014014314 | PER-005-1 | R2 | On September 8, 2014, TVA submitted a Self-Report stating that, as a Balancing Authority (BA), it had an issue with PER-005-1 R2. TVA failed to verify each of its System Operator’s capabilities to perform each assigned task identified in R1.1 at least one time within six months of a modification of the Bulk Electric System (BES) company-specific reliability-related tasks. Prior to April 1, 2013, the date PER-005-1 became mandatory and enforceable, TVA had identified reliability-related tasks specific to the participant scheduling function, which included certain parts of TVA’s BA responsibilities. On February 12, 2014, a NERC-certified System Operator performed the shift duties of the participant scheduling function. This shift occurred more than six months after TVA identified the reliability-related tasks. Prior to the System Operator working the shift, TVA had not verified the capability of this System Operator to perform the identified reliability-related tasks specific to the participant scheduling function. TVA determined that the root cause of this issue was its inability to easily track in its database whether it had verified that System Operators were capable of performing specific reliability-related tasks. TVA’s database only allowed one job function to be tracked per System Operator, making it difficult to determine if a System Operator had been deemed capable of performing specific reliability-related tasks. Prior to the implementation of PER-005-1, the System Operator at issue had completed a technical qualifications checklist for the participant scheduling position and had performed the job for approximately two years. The technical qualifications checklist was similar to the company-specific reliability-related task list, but the technical qualifications checklist did not contain the level of detail required by PER-005-1. When working the participant scheduling position shift, the System Operator was unaware that TVA had not verified his or her capabilities to perform the reliability-related tasks identified for the position. Several weeks later, during a discussion between the System Operator and a member of the technical training staff, the technical training staff member learned that the System Operator had covered the shift. The trainer raised a concern as to whether TVA had verified the System Operator’s capabilities for the participant scheduling function. TVA had documented verification of the System Operator’s capabilities in the training system for the other BA desks, but not the participant scheduling desk. This issue lasted from February 12, 2014, when the System Operator worked a shift prior to TVA completing the required verification, through February 13, 2014, when the System Operator’s shift ended. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TVA’s failure to confirm that the System Operator met the specific training requirements could have resulted in delayed or less effective execution of the duties of that role. However, the System Operator at issue was NERC-certified and had previously performed the duties of the participant scheduling position for almost two years before moving to another BA role. In addition, the System Operator had also developed training for the participant scheduling specialist position. Prior to the implementation of PER-005-1, the System Operator had completed a technical qualifications checklist for this position which, although less detailed, was similar to the current verification requirements for the position. The System Operator had sufficient knowledge and experience to perform the duties of the participant scheduling position. No harm is known to have occurred. SERC considered TVA’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, TVA: 1) reviewed training records to ensure that verification of the capability to perform the identified reliability-related tasks for any System Operator that may be required to cover shift has been performed at least once; 2) updated training records so that the list of System Operators that have been verified on the reliability-related tasks can be easily accessible; 3) developed an enhancement that will allow the database to track more than one job function for each System Operator; and 4) performed an extent of condition review for the other operating functions (Reliability Coordinator and Transmission Operator) to ensure there had been no similar instances in those TVA groups.
2015-06-30 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (Chisholm) | NCR11291 | SPP2015014829 | VAR-002-3 | R1 | On April 2, 2015, Chisholm submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it had a minimal risk instance of noncompliance with VAR-002-3 R1. Specifically, on March 10, 2015, Chisholm took its Automatic Voltage Regulator (AVR) out of service so that a third-party vendor could test a Chisholm SCADA upgrade. Chisholm’s operators did not notify its Transmission Operator that the AVR was out of service. Chisholm’s AVR remained out of service for ten (10) days. On March 20, 2015, Chisholm discovered the error, placed the AVR back in service, and resumed its operations in automatic voltage control mode. This instance of non-compliance began on March 10, 2015, when Chisholm took its AVR out of service for testing, and ended on March 20, 2015, when Chisholm put its AVR back into service. The root cause of this issue was human error. Additionally, Chisholm did not have internal controls in place to ensure the AVR was placed in service once the third-party vendor completed testing. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to operate its AVR in automatic voltage control mode, and failure to communicate the status to its Transmission Operator would cause the Chisholm facility not to respond to system voltage excursions and could impair the TO’s ability to respond to system voltage problems. However, Chisholm is a 235 MW variable generation wind farm that does not provide reactive power support. No actual harm occurred as a result of this issue. A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including Smoky Hills Wind Farm, LLC’s, (an affiliate of Chisholm), noncompliance with VAR-002-1.1b R3 was posted on the NERC website on September 30, 2014. The 60-day review period passed on November 29, 2014. SPP RE considered this compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the VAR-002 issue was isolated and not systemic. The facts and circumstances of the prior issue of non-compliance did not mirror the circumstances that caused the current instance of non-compliance. | To mitigate this minimal risk instance of noncompliance, Chisholm implemented the following precautions: 1) Processes to ensure communication to the TOP when starting any testing, even if the testing is not expected to impact normal operations. 2) An alarm that is set to go off if the Voltage Control Mode is disabled. 3) Added processes to the Chisholm View Operational Manual to ensure more frequent checks on the status of the Voltage Control Mode, particularly after system testing and upgrades.
2015-06-30 | Southwest Power Pool Regional Entity (SPP RE) | Chisholm View Wind Project, LLC (Chisholm) | NCR11291 | SPP2015014830 | VAR-002-3 | R3 | On April 2, 2015, Chisholm submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it had a minimal risk instance of noncompliance with VAR-002-3 R3. Specifically, on March 10, 2015, Chisholm took its Automatic Voltage Regulator (AVR) out of service so that a third-party vendor could test a Chisholm SCADA upgrade. Chisholm’s operators did not notify its Transmission Operator that the AVR was out of service within 30 minutes of the AVR’s status change. Chisholm’s AVR remained out of service for ten (10) days. On March 20, 2015, Chisholm discovered the error, placed the AVR back in service, and resumed its operations in automatic voltage control mode. This instance of non-compliance began on March 10, 2015, when Chisholm took its AVR out of service for testing, and ended on March 20, 2015, when Chisholm put its AVR back into service. The root cause of this issue was human error. Additionally, Chisholm did not have internal controls in place to ensure the AVR was placed in service once the third-party vendor completed testing. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to operate its AVR in automatic voltage control mode, and failure to communicate the status to its Transmission Operator within a timely manner would cause the Chisholm facility not to respond to system voltage excursions and could impair the TO’s ability to respond to system voltage problems. However, Chisholm is a 235 MW variable generation wind farm that does not provide reactive power support. No actual harm occurred as a result of this issue. A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including Smoky Hills Wind Farm, LLC’s, (an affiliate of Chisholm), noncompliance with VAR-002-1.1b R3 was posted on the NERC website on September 30, 2014. The 60-day review period passed on November 29, 2014. SPP RE considered this compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because the VAR-002 issue was isolated and not systemic. The facts and circumstances of the prior issue of non-compliance did not mirror the circumstances that caused the current instance of non-compliance. | To mitigate this minimal risk instance of noncompliance, Chisholm implemented the following precautions: 1) Processes to ensure communication to the TOP when starting any testing, even if the testing is not expected to impact normal operations. 2) An alarm that is set to go off if the Voltage Control Mode is disabled. 3) Added processes to the Chisholm View Operational Manual to ensure more frequent checks on the status of the Voltage Control Mode, particularly after system testing and upgrades.
2015-06-30 | Texas Reliability Entity (Texas RE) | CER-Colorado Bend Energy Partners LP (CBEC) | NCR11067 | TRE2015014835 | PRC-005-1.1b | R2; R2.1 | On April 6, 2015, CBEC submitted a Self-Report to Texas RE, NPCC, and RF stating that, as a Generator Owner, it had an issue with PRC-005-1.1b R2.1. CBEC failed to provide evidence that 8 station batteries were maintained and tested within the defined intervals provided by CBEC’s parent company, Exelon Generation Company, LLC. This failure represents 3.7% of its applicable devices (8 of 211 total devices). The root cause of the missed testing was inconsistent defined testing intervals between its different procedures and tracking methods. In one instance, battery testing intervals were listed as 90-120 days. In another instance, battery testing intervals were defined as “3 Months, 4 Months Maximum,” based on the last day of the 4th calendar month following prior maintenance. In yet another instance, these intervals were defined as 180 days, matching the business quarter. Texas RE determined the issue duration to be from August 23, 2014, the day after the first battery testing was due, until September 29, 2014, when CBEC performed all applicable battery testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although CBEC has a maximum capability of 498 MW, the issue duration lasted a short period of time, approximately one month. Also, even though CBEC did not meet the 120 day requirement detailed in one of its procedures, CBEC indicated that it did meet the “quarterly” requirement listed in another document. Furthermore, CBEC confirmed that the battery systems are continuously monitored via SCADA, with an annunciator in its control room. Lastly, when the devices were tested, all were shown to be operating within normal specifications, indicating that if CBEC had experienced any issues, its Protection System equipment would have functioned as intended. No harm is known to have occurred. A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R1 and PRC-005-1 R2 for CBEC was filed with FERC under RC13-10-000 on June 27, 2013. The 60-day review period passed on August 26, 2013. A FFT informational posting addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R1 for CBEC’s affiliate, Exelon Generation Company, LLC was posted on the NERC website on February 27, 2014. The 60-day review period passed on April 28, 2014. A FFT informational posting addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R1 and PRC-005-1 R2 for CBEC’s affiliate, CER Quail Run Energy Partners LP (NCR11068) was filed with FERC under RC13-10-000 on June 27, 2013. The 60-day review period passed on August 26, 2013. A FFT informational posting addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 for CBEC’s affiliate, Exelon Wind 4, LLC (NCR10122) was filed with FERC under RC13-3-000 on December 31, 2012. The 60-day review period passed on March 1, 2013. Although CBEC and its affiliates have previous violations involving failure to maintain and test Protection System devices within the defined intervals, Texas RE determined that this instance does not warrant an alternative disposition method because this minimal risk occurred over a short duration (one month) and involved a small number of affected devices. Furthermore, several measures have been implemented to prevent future recurrence. | To mitigate this issue, CBEC: 1) performed and documented all applicable battery testing; 2) updated all documents to reflect 90 -120 day testing intervals (instead of the prior 3-4 month internals; 3) updated and improved its procedures ER-EP-405 and ER-EP-153 to account for the transition to PRC-005 Version 2; and 4) corrected centralized battery tracking matrix to properly calculate days between tests. The spreadsheet also indicates when battery maintenance is almost due and when it is past due. Additionally, CBEC will complete the following mitigation activities by June 30, 2015: 1) confirm any extent of condition to identify any additional battery testing interval issues in ExGen's fleet; and 2) distribute procedures and educate affected personnel on changes to help prevent reoccurrence.
2015-06-30 | Texas Reliability Entity (Texas RE) | Mesquite Wind LLC (MQWF) | NCR04097 | TRE2015014652 | VAR-002-3 | R3 | On February 23, 2015, MQWF submitted a Self-Report stating that, as a Generator Operator owned by Lone Star I, it had an issue with VAR-002-3 R3. Specifically, POW failed to notify its Transmission Operator within 30 minutes of the Master VAR Controller (MVC) being returned to automatic control. On February 2, 2015, MQWF placed its MVC into manual control at 16:50 to facilitate a maintenance need at the facility and notified Oncor, the Transmission Operator, within 30 minutes of this change. However, following the completion of the maintenance, Power Engineers, a third party maintenance vendor, returned the MVC to automatic control at 18:41 and notified the Remote Operations Control Center (ROCC), MQWF’s VAR-002 communication liaison, that the maintenance was complete. According to the ROCC log notes, the ROCC Operator did not initially understand that the MVC was changed back to automatic at the conclusion of the maintenance. Therefore, it was not until the ROCC Operator observed the MVC was back in automatic control, that it notified the Transmission Operator at 20:22 of the change from manual to automatic, 68 minutes after the required 30 minute notification window. The root cause was determined to be a gap in communication regarding the VAR status change post maintenance between Power Engineers and EDPR NA’s ROCC, which resulted in a delayed status change notification to the Transmission Operator. The issue duration of this issue was determined to be approximately 68 minutes on February 2, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to timely report changes in VAR statuses could have resulted in the Transmission Operator not being readily notified about weakness or strengths in a particular area and making operational decisions based on incomplete data. The risk to the BPS was reduced due to the following factors. First, MQWF maintained its voltage profile during the issue duration, based on a review of the PI data. Second, this single instance of non-compliance was only 68 minutes in duration. Third, the capacitor banks were the only reactive resources at issue and were under automatic control during the issue period. Fourth, the subject 200 MW wind power plant is connected to the BES via a 345 kv transmission line, and the peak and average output during the issue duration period were 47.44 MW and 30.89 MW, respectively. Further mitigating the risk is MQWF having an e-mail and audible alarm notifying the ROCC Operator when the voltage controller has been switched from Automatic to Manual control mode, which is considered much less desirable state of the system. No harm is known to have occurred. MQWF has no prior violations of VAR-002 R3. However, MQWF’s affiliate has one previous noncompliance of VAR-002 R3. Compliance History of Affiliate – Blue Canyon II Windpower, LLC (NCR06040) A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including noncompliance with VAR-002-1.1b R3 (SPP2014013698) for Blue Canyon II was posted on the NERC website on June 26, 2014. The 60-day review period passed on August 25, 2014. While the instances were of the same Standard and Requirement, the circumstances were different. In the previous instance, the Entity mistakenly notified its generator dispatcher, instead of its Transmission Operator, that Blue Canyon II’s two 6 MVAR capacitor banks tripped offline. In this instance, the ROCC Operator did not realize that the MVC was changed back to automatic control by a third party vendor. Therefore, the ROCC Operator failed to inform the Transmission Operator of the status change within 30 minutes. | To mitigate this issue, MQWF has taken the following actions: 1) MQWF notified the Transmission Operator and QSE of the status change in the Master VAR Controller from manual to automatic; 2) EDPR NA, on behalf of Lone Star I, contacted Power Engineers to discuss the correct protocol to be observed when a change in status occurs. This communication served two purposes. First, it reminded Power Engineers of the notification responsibilities concerning the change in status. Second, the verbal review was conducted promptly following the event; 3) EDPR NA and Power Engineers contractually agreed that, in foreseeable normal operating conditions, EDPR NA’s ROCC will make all future status changes. In the event Power Engineers believes that personal injury or equipment damage is imminent, Power Engineers may change a system’s state without prior approval from the ROCC but will notify the ROCC as soon as possible thereafter; and 4) EDPR NA informed Power Engineers of the following new requirements: • any changes made to the control mode by its representatives should be communicated to the respective EDPR ROCC Operator within 15 minutes of the change; and • Power Engineers must contact the ROCC before making any changes if system conditions allow. Texas RE has verified the completion of all mitigation activity.
2015-06-30 | Texas Reliability Entity (Texas RE) | Notrees Windpower, LP (Notrees) | NCR10276 | TRE2015014756 | PRC-005-1.1b | R2; R2.1 | On March 18, 2015, Notrees submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1.1b R2.1. Notrees failed to test 5 relays within the 5-year (+12 month) intervals it had defined in its maintenance and testing program. The 5 relays represent 2.67% of its applicable devices (5 of 187 total devices). The root causes are related to a change in site management in 2013, the need for process improvements for scheduling outages and determining work scope, and a misunderstanding of whether the commercial operation date or the initial test date should be used to set the due date of the maintenance interval. Texas RE determined the issue duration to be from September 11, 2014, the day after testing was due for the first set of relays, until November 10, 2014, when Notrees updated its Maintenance and Testing Program to allow testing intervals of 12 calendar years for microprocessor relays. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). According to Notrees, the protective relays in question are monitored microprocessor relays that send alarms to a 24/7 monitoring center that can initiate corrective action when needed. Furthermore, the new NERC Reliability Standard, PRC-005-2, allows a maximum maintenance interval of 12 calendar years for protective relays with these attributes. Although the relays at issue were tested outside of Notrees’ defined intervals, testing was completed approximately 6 years from its initial test date, which is within the PRC-005-2 maximum interval. Additionally, the issue period lasted a short time, 2 months, and when the devices were tested, all were shown to be operating within normal specifications. Finally, if a protective device were to have misoperated, the maximum loss in generation that would have affected the ERCOT interconnection would have been 153 MW. No harm is known to have occurred. A Settlement Agreement covering a violation of PRC-005-1 R2 for Duke Energy Florida, Inc. was filed with FERC under NP14-27-000 on January 30, 2014. On February 28, 2014, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for Progress Energy Florida was filed with FERC under NP13-29-000 on March 27, 2013. On April 26, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for Duke Energy Carolinas was filed with FERC under NP13-8-000 on November 30, 2012. On December 28, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2 for Duke Energy Corporation was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although Notrees’ affiliates have previous violations involving failure to maintain and test Protection System devices within the defined intervals, Texas RE determined that this instance does not warrant an alternative disposition method because this minimal risk occurred over a short duration (2 months) and involved a small number of affected devices. Furthermore, Notrees has implemented several measures to prevent future recurrence. | To mitigate this issue, Notrees: 1) updated its maintenance and testing manual to include a 12-year maximum testing interval for microprocessor relays on November 10, 2014; 2) performed and documented relay testing for the applicable protective relays; 3) added an internal High Voltage Maintenance Team that includes a supervisor and three technicians, whose responsibility includes the planning and oversight of protection system maintenance and testing; 4) replaced its maintenance and testing manual with a protection system maintenance program (PSMP) for compliance with PRC-005-2 on April 1, 2015; and 5) implemented outage management procedures and a work management tool to ensure equipment is maintained within maintenance intervals. Texas RE has verified the completion of all mitigation activity.
2015-06-30 | Texas Reliability Entity (Texas RE) | Post Oak Wind, LLC (Post Oak) | NCR10167 | TRE2015014653 | VAR-002-3 | R3 | On February 23, 2015, Post Oak submitted a Self-Report stating that, as a Generator Operator owned by Lone Star II, it had an issue with VAR-002-3 R3. Specifically, Post Oak failed to notify its Transmission Operator within 30 minutes of the Master VAR Controller (MVC) being returned to automatic control. On February 2, 2015, Post Oak placed its MVC into manual control at 16:50 to facilitate a maintenance need at the facility and notified Oncor, the Transmission Operator, within 30 minutes of this change. However, following the completion of the maintenance, Power Engineers, a third party maintenance vendor, returned the MVC to automatic control at 18:41 and notified the Remote Operations Control Center (ROCC), Post Oak’s VAR-002 communication liaison, that the maintenance was complete. According to the ROCC log notes, the ROCC Operator did not initially understand that the MVC was changed back to automatic at the conclusion of the maintenance. Therefore, it was not until the ROCC Operator observed the MVC was back in automatic control, that it notified the Transmission Operator at 20:22 of the change from manual to automatic, 68 minutes after the required 30 minute notification window. The root cause was determined to be a gap in communication regarding the VAR status change post maintenance between Power Engineers and EDPR NA’s ROCC, which resulted in a delayed status change notification to the Transmission Operator. The issue duration of this issue was determined to be approximately 68 minutes on February 2, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to timely report changes in VAR statuses could have resulted in the Transmission Operator not being readily notified about weakness or strengths in a particular area and making operational decisions based on incomplete data. The risk to the BPS was reduced due to the following factors. First, Post Oak maintained its voltage profile during the issue duration, based on a review of the PI data. Second, this single instance of non-compliance was only 68 minutes in duration. Third, the capacitor banks were the only reactive resources at issue and were under automatic control during the issue period. Fourth, the subject 200 MW wind power plant is connected to the BES via a 345 kv transmission line, and the peak and average output during the issue duration period were 71.25 MW and 46.18 MW, respectively. Further mitigating the risk is Post Oak having an e-mail and audible alarm notifying the ROCC Operator when the voltage controller has been switched from Automatic to Manual control mode, which is considered much less desirable state of the system. No harm is known to have occurred. Post Oak has no prior violations of VAR-002 R3. However, Post Oak’s affiliate has one previous noncompliance of VAR-002 R3. Compliance History of Affiliate – Blue Canyon II Windpower, LLC (NCR06040) A Find, Fix, Track and Report (FFT) informational posting addressing remediated issues for certain registered entities including noncompliance with VAR-002-1.1b R3 (SPP2014013698) for Blue Canyon II was posted on the NERC website on June 26, 2014. The 60-day review period passed on August 25, 2014. While the instances were of the same Standard and Requirement, the circumstances were different. In the previous instance, the Entity mistakenly notified its generator dispatcher, instead of its Transmission Operator, that Blue Canyon II’s two 6 MVAR capacitor banks tripped offline. In this instance, the ROCC Operator did not realize that the MVC was changed back to automatic control by a third party vendor. Therefore, the ROCC Operator failed to inform the Transmission Operator of the status change within 30 minutes. | To mitigate this issue, Post Oak has taken the following actions: 1) Post Oak notified the Transmission Operator and QSE of the status change in the Master VAR Controller from manual to automatic; 2) EDPR NA, on behalf of Lone Star II, contacted Power Engineers to discuss the correct protocol to be observed when a change in status occurs. This communication served two purposes. First, it reminded Power Engineers of the notification responsibilities concerning the change in status. Second, the verbal review was conducted promptly following the event; 3) EDPR NA and Power Engineers contractually agreed that, in foreseeable normal operating conditions, EDPR NA’s ROCC will make all future status changes. In the event Power Engineers believes that personal injury or equipment damage is imminent, Power Engineers may change a system’s state without prior approval from the ROCC but will notify the ROCC as soon as possible thereafter; and 4) EDPR NA informed Power Engineers of the following new requirements: • any changes made to the control mode by its representatives should be communicated to the respective EDPR ROCC Operator within 15 minutes of the change; and • Power Engineers must contact the ROCC before making any changes if system conditions allow. Texas RE has verified the completion of all mitigation activity.
2015-05-28 | Florida Reliability Coordinating Council (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2015014693 | TOP-004-2 | R6 | On March 2, 2015, VERO submitted a Self-Report stating that, as a Transmission Operator, it had an issue of TOP-004-2 R6.2. Vero failed to implement its defined procedure requiring three-part communications when switching transmission elements. In an effort to prevent miscommunications while switching transmission elements, VERO requires three-part communications in its switching procedure. However, on three separate occasions while issuing switching orders (January 4, 2013, March 11, 2013 and March 14, 2013), VERO's system operator failed to provide acknowledgement that the switchman in the field correctly understood the instructions (third step of three-part communication). While the requirement does not specifically require the use of three=part communications for normal switching operating instructions, VERO decided to implement this best practice in order to aid in preventing switching communication errors by providing a communication practice for operators to follow in all cases where instructions and directives are exchanged. The root cause for this issue was human error in failing to acknowledge the communication reply, which could have resulted from lack of training reinforcement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, VERO's failure to use the three-part communication, as required by its procedure, could have resulted in the wrong element being switched. However, this risk was reduced because: 1) Two steps of the three-step communication practice were performed (the recipient repeated the instruction back correctly) in all three instances; and 2) All three instances involved switching on 138 kV elements that feed into a 69 kV system only affecting VERO loads. No harm was known to have occurred. | To mitigate this issue, VERO re-trained its system operators and sub-station personnel in three-part communication and added three-part communication training to its annual training requirements. FRCC has verified the completion of all mitigation activity.
2015-05-28 | Florida Reliability Coordinating Council (FRCC) | Vero Beach, City of (VERO) | NCR00079 | FRCC2015014774 | PRC-005-1 | R2; R2.1 | On March 18, 2015, VERO submitted a Self-Report stating that, as a Transmission Owner (TO) and Distribution Provider, it had an issue of PRC-005-1 R2. VERO did not perform required maintenance (per its Protection System Maintenance Program) on two relays that failed their performance testing (one distance relay and one directional ground overcurrent relay). VERO tested its relays at Substation 7 on March 16, 2011. However, due to an oversight, the tester did not notify engineering and operations personnel of the failed tests, and therefore no actions were taken to perform maintenance activities that needed to be addressed. Two zone 3 relays (1) distance relay and (1) directional ground overcurrent relay failed their tests. The distance relay, B phase, max torque angle test has a tolerance +/- 2.00 deg. and the actual test results indicated a 5.90 deg., which produced a failed test. The directional ground overcurrent relay, directional pickup test has a tolerance +/- 10% and the actual test results revealed a 11.43% tolerance which produced a failed test. VERO replaced the relays on March 11, 2015. The root cause of this issue was human error in failing to notify appropriate personnel of the failed tests in order to have the required maintenance performed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to properly maintain these relays could have caused over reaching relaying from the neighboring TO. The risk was reduced, however, because the neighboring TO has Zone 5 relaying in place that covers VERO's Zone 3 relaying. In the event that VERO's Zone 3 relays had failed to function, the neighboring TO's Zone 5 relays would have still protected the line. No harm was known to have occurred. | To mitigate this issue, VERO: 1) contacted the relay testing firm, tested the failed relays, confirmed the relays were out of tolerance, and replaced the relays; and 2) included in its testing activities, a form for the testing firm to fill out in the event a relay is found out of manufacturer tolerances. The form is to be signed by the testing technician and a VERO representative. A member of VERO management will review each day’s activity and formulate a plan of action in the event a relay is found out of manufacturer tolerances. FRCC has verified the completion of all mitigation activity.
2015-05-28 | Midwest Reliability Organization (MRO) | Lakefield Wind Project, LLC (LWP) | NCR11180 | MRO2015014773 | VAR-002-2b | R1 | On January 30, 2015, Lakefield Wind Project, LLC (LWP), submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue of VAR-002-3 R3. Upon review by LWP and MRO, it was determined that the issue directly related to R1, rather than R3. Additionally, LWP and MRO determined that the issue began on September 24, 2014 when VAR-002-2b was in effect. Therefore, MRO determined that VAR-002-2b R1 is the applicable Standard Requirement at issue. LWP reported that it failed to operate its generator in the automatic voltage control mode and did not notify its Transmission Operator (TOP) of the voltage control status and the reason for not operating in the automatic voltage control mode. LWP's voltage control was disabled on September 24, 2014 when a disturbance cause an outage of the wind farm control system. After the control system was restored, LWP operators failed to notice that the voltage control function was disabled and did not take action to restore it or to notify the TOP of the status change. Upon receiving an updated voltage schedule from its TOP on September 30, 2014, LWP discovered that the voltage control function was disabled. LWP immediately enabled the voltage control upon discovery and notified its TOP of the status change. The issue began on September 24, 2014 and ended on September 30, 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). This issue posed a potential risk primarily due to the fact that neither LWP, as the GOP, nor its TOP was aware that the facility was operating without automatic voltage control. However, due to the small size of the facility (206 MW), LWP’s contribution to voltage regulation in its area is small and would not have a great impact on the ability of the system to respond to reactive power demands. Furthermore, this is a wind generation facility and is inherently variable and non-dispatchable and would, therefore, not be heavily relied upon by system operators. As such, the risk to the BES is minimal. No harm is known to have occurred. This is LWP’s first instance of noncompliance with VAR-002. | To mitigate this issue, LWP: 1) enabled the automatic voltage control function; 2) notified ITC of the automatic voltage control status change; 3) held a meeting to discuss this issue and to correct operator behavior by verbally explaining the requirement, Lakefield’s Procedure, and the requirement to notify the Transmission Operator within 30 minutes of a change in status of the Voltage Controller; 4) developed training to cover Lakefield’s internal procedure for VAR-002-3 and the Standard; and 5) provided training to all Lakefield personnel who have responsibility for monitoring the facility and notifying the Transmission Operator. The mitigating activities were completed by January 29, 2015.
2015-05-28 | Midwest Reliability Organization (MRO) | Otter Tail Power Company (OTP) | NCR01023 | MRO2014013880 | VAR-002-2b | R3 | On May 27, 2014, Otter Tail Power (OTP), submitted a Self-Report stating that as a Generator Operator (GOP), it had an issue with VAR-002-2b R3. At 8:56 a.m. on March 27, 2014 the automatic voltage regulator (AVR) and power system stabilizer (PSS) tripped from automatic to manual mode at the entity’s Big Stone plant. This change was not communicated to the Transmission Operator (TOP) until 9:32 a.m., 36 minutes later (R3.1 requires this communication to occur within 30 minutes). An adjacent transmission line (Blair-Granite Falls 230kV), owned by another entity, tripped which caused the AVR at Big Stone to switch from automatic to manual voltage control mode. This occurred because the relay controlling the AVR sensed momentary low voltage on the Big Stone 24kV bus. The entity’s generation personnel began working with the AVR manufacturer immediately to determine the appropriateness of the AVR response. This effort to understand the problem delayed the notification to the TOP past the required 30 minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The duration of the issue was 6 minutes and was self reported by OTP. OTP is vertically integrated and performs both the GOP and TOP functions and was able to maintain its voltage schedule during the period of noncompliance. No harm is known to have occurred. This is OTP’s first instance of noncompliance with VAR-002-2b. | To mitigate this issue, OTP: 1) notified the TOP of the change in AVR; and 2) provided additional training regarding the corporate VAR-002 policy for all operators at Big Stone. OTP will also complete the following mitigation activities by May 29, 2015: 1) automate its notification of AVR/PSS status by creating a telemetry point to be monitored by the entity's EMS, which will provide the TOP with real-time notification of voltage control mode status changes; 2) implement modified settings for the relay associated with the AVR that will make it less sensitive; and 3) enable event capturing capability on the relay associated with the AVR, in order to provide forensic information related to future operations. OTP needs to coordinate the change with a generator outage.
2015-05-28 | Northeast Power Coordinating Council (NPCC) | Green Mountain Power Corporation (GMP) | NCR07103 | NPCC2015014915 | PRC-005.1.1b | R2; R2.1; R2.2 | On February 17, 2015, GMP submitted a self-report stating that as a GO, it had an issue of PRC-005.1.1b, R2. During GMP's 2014 self-certification assessment for PRC-005-1.1b, it was discovered that at the Ascutney generation site, three microprocesser relays and the associated control circuitry were not tested according to the time interval stated in GMP's generation protection system maintenance and testing program. The maintenance and testing program calls for both protective relays and control circuitry to be tested on six year intervals. The protective relays and the control circuitry were both due for testing in 2014, however the testing was not completed. The testing was missed due to overlapping events at the end of 2014, including multiple storms during late 2014, deadlines for several distributed generation interconnection projects, and completion of capital projects. The root cause of the violation was GMP's failure to schedule the device testing with enough extra time to account for delays. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential impact to the bulk power system was minimal because the Ascutney 4GT generation unit is a small 14.4 MVA generator used as a blackstart resource in ISO-NE's System Restoration Plan, and is only run on an as-needed basis at ISO-NE's request. The unit was available for all requests in 2014, with a total runtime of 79.8 hours (these requests were not for system restoration, but for peak period requests). The duration of the violation was short, as the missed testing was detected quickly, with the testing completed only 38 days after the violation had begun. The generation protection system components performed as expected during testing, with the exception of one field ground relay that was immediately replaced. All three relays and the control circuitry were in working order prior to and immediately following the missed test interval. No harm is known to have occurred as a result of this violation. NPCC considered GMP's compliance history and determined there were no relevant instances of noncompliance related to PRC-005 R2. | To mitigate this issue, GMP: 1) Completed testing of the necessary relays on 02/07/2015; 2) Completed testing of the necessary control circuitry on 02/07/2015; and 3) Established electronic reminders for protection system maintenance activities. NPCC has verified the completion of all mitigation activity.
2015-05-28 | Northeast Power Coordinating Council (NPCC) | Mass. Municipal Wholesale Electric Company (MMWEC) | NCR07136 | NPCC2014014411 | PRC-005-1 | R2; R2.1 | On October 16, 2014, MMWEC submitted a self-report stating that as GO and TO, it had an issue with PRC-005-1 R2. During a self audit of its protection system maintenance and testing program for the 3rd quarter of 2014, MMWEC discovered that they had deficiencies related to in services testing of current transformers (CTs) and coupling capacitor voltage transformers (CCVTs) providing input to four protective relays. MMEC did not test 15 of 486 protection system devices. In service testing of inputs from six CTs (one CT per phase at two locations) to a differential relay that detects faults on a generator step up (GSU) transformer were not performed in accordance with MMWEC’s maintenance and testing program. This GSU transformer is for the 100 MW capacity steam turbine generator associated with pseudo-combined cycle units. The root cause of the failure to test was that the list of devices that MMWEC provided to the testing vendor was incomplete and the omission was not identified until MMWEC cross-referenced the one-line diagram with past test reports during this self-audit. In service testing of inputs from three CTs (one per phase) to a line differential relay and from three CTs (one per phase) to a breaker failure relay were omitted during in service testing in 2009 and 2011. Line 1, which connects the steam turbine generator to the switchyard bus, has two breakers. Standard operating procedure specifies that only one of the two breakers be closed during operation of the steam turbine generator in order to reduce the individual breaker operations and the associated wear and tear of breaker cycling on both OCBs. The one open breaker isolated these CTs and prevented testing of current inputs to two protective relays. Normal operation of the switchyard alternates which breaker is closed when the steam turbine generator is synchronized to the grid. MMWEC did not identify that the same breaker was open during two successive testing cycles, resulting in the omission of the same CTs in successive tests. In service testing of inputs from three CCVTs (one per phase) to an AC directional overcurrent relay was not performed since 2009. MMWEC’s maintenance and testing schedule specifies that in service testing of CTs and PTs be performed every four years. Testing was due in 2013. MMWEC scheduled testing of all applicable CTs, PTs and CCVTs in 2011. However, MMWEC discovered, during the self-audit, that no record exists for testing these CCVTs for the 2011 tests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk of potential impact to the BPS due to the discovered deficiencies in testing of the CTs and CCVTs affects an increased risk of misoperation of four protective relays. These protective relays are part of Protection Systems for the Stony Brook steam turbine generator GSU and the 345 KV line that is the radial generator lead for the Stony Brook plant. In each case the potential impact to the BPS is minimal. The potential loss of generation ranges from 100 MW in the case of tripping of the steam turbine generator to a loss of 526 MW capability in the tripping of the 345 KV line. 526 MW is typically less than one-third of the ISO-NE ten minute reserve requirement, which is 125% of the largest single contingency for the system. The Stony Brook plant is located in the Western-Central Massachusetts zone, which ISO-NE (the Reliability Coordinator) has determined is not an import constrained area. Two of the Stony Brook gas turbine units in simple cycle mode are black start units in the regional restoration program. The steam turbine generator is not a part of the black start capability of the Stony Brook plant. MMWEC’s four year testing cycle for CTs and PTs is conservative compared to the 12 calendar year interval for testing within PRC-005-2. MWECC completed the testing of the aforementioned CTs and CCVTs and verified that all inputs to protective relays were correct and the CTs and CCVTs were operating as designed. NPCC considered MMWEC's compliance history and determined there were no relevant instances of noncompliance related to PRC-005 R2. | To mitigate this issue, MMWEC: 1) reviewed the as-built drawings and updated the in service testing list to include the relay associated with the omitted CTs 2) completed the in service testing of CTs and CCVTs that were omitted in the previous testing 3) implemented new internal controls to improve communications with testing vendor and provide for better oversight of the testing process 4) revised MMWEC's maintenance and testing program document to ensure new internal controls are followed for future testing in order to prevent recurrence. NPCC has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2014013982 | VAR-002-2b | R3.1 | On May 28, 2014, AEP submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-2b R3.1. AEP determined that it did not notify the Transmission Operator (TOP) of a Power System Stabilizer (PSS) status change within the required 30 minutes following a planned outage. Specifically, during a planned outage, the exciter on a generator unit went through a control upgrade and, over the course of the project, the PSS was manually disabled. To certify the generator’s exciter following the control upgrade, the PSS was not enabled. When the generator paralleled to the grid on November 24, 2013, at 1947 hours, the plant operator stated that the PSS was in service. While monitoring the generator, 43 minutes following parallel, the plant operator realized that the PSS was disabled. Upon this realization, the plant operator communicated the revised status to generation dispatch with an estimated return time of noon the following day. AEP notified PJM and AEP TOP of the revised status via telephone at 2108 hours, which was 121 minutes following parallel. AEP determined that the root cause of the noncompliance was the plant operator’s oversight in not verifying that the PSS was in service during start up due to past routine sequence. Normal procedure is that the PSS is enabled at all times and becomes active during startup from an automatic control loop. Thus, the operator assumed the PSS was enabled. The duration of this noncompliance is for 91 minutes on November 24, 2013, which is 30 minutes following PSS’s change in status to the time AEP notified the TOP of the change in status. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the plant operator discovered the violation within a short period of time as a result of monitoring the system. Additionally, three other generators at the generating station were running with Automatic Voltage Regulator (AVR) and the PSS was enabled on the three generators at the time of the noncompliance, which minimizes any effect on the system of operating the one generating unit with the PSS disabled by helping to control the total voltage. No harm is known to have occurred. AEP has previously violated VAR-002 R3. The facts and circumstances of AEP’s prior violations of VAR-002 R3 are distinguishable from the facts and circumstances of the present noncompliance. First, during startup of a unit in 2011, an AEP operator unsuccessfully attempted to switch the AVR from manual control mode to automatic control mode. The issue occurred for almost seven hours before an operator noticed the alarm indicating the AVR was operating in manual control mode. Unlike the previous violation where the operator unsuccessfully tried to change the status of the AVR, the operator involved in the current noncompliance incorrectly assumed the PSS was already enabled and thus did not attempt to change its status. Regardless, here, the operator realized his mistake within 43 minutes. AEP’s only other violation of VAR-002 R3 is arguably similar to the instant noncompliance in that the operators did not realize that the PSS did not automatically enable when the unit was restored. However, in the previous situation, AEP did not discover that the PSS was not enabled for ten days because no alarms were associated with the condition. Conversely, here, the operator discovered the issue within 43 minutes, which demonstrates an improvement in AEP’s detective controls, which ReliabilityFirst seeks to encourage by treating the instant issue as a Compliance Exception. ReliabilityFirst therefore determined that AEP’s violation history relative to VAR-002 R3 does not warrant an alternative disposition method. ReliabilityFirst determined that AEP's compliance history should not serve as a basis for applying a penalty. | To mitigate this issue, AEP: 1) AEP updated the control system screens to more prominently indicate the status of the AVR and PSS systems in multiple locations. This will allow operators to view the status from whichever screen they may be utilizing during a start-up; 2) AEP added more alarms to the control system. Specifically, if a breaker is closed and the PSS is disabled, an alarm is triggered that states PSS disabled with BKR Closed – Notify Dispatch ASAP; 3) AEP amended the start-up checklist to better document the status of the AVR/PSS function; and 4) AEP provided refresher training to plant operators to discuss the importance of the AVR and PSS reporting requirement. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | American Electric Power Service Corporation as agent for Appalachian Power Company, Indiana Michigan Power Company, Kentucky Power Company, Kingsport Power Company, Ohio Power Company, Wheeling Power Company, AEP Ohio Transmission Company, AEP Appalachian Transmission Company, AEP West Virginia Transmission Company, AEP Indiana Michigan Transmission Company and AEP Kentucky Transmission Company, Inc. (AEP) | NCR00682 | RFC2014014024 | PRC-001-1.1 | R2 R2.2 | On June 20, 2014, AEP submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue with PRC-001-1.1 R2. AEP did not notify its Reliability Coordinator and affected TOPs and Balancing Authorities of a relay failure or take corrective action as soon as possible. On April 2, 2014, AEP performed trip testing on a 138 kV circuit breaker and determined that the 21 relay mho element contacts were not mechanically functional and thus would not issue a trip. On April 14, 2014, AEP reviewed the situation and determined that the relay provided inadequate protection. AEP took the circuit breaker out of service that same day and, on April 15, 2014, replaced the relay and placed the circuit breaker back in service. Upon determining that the relay provided inadequate protection, AEP made the proper notifications. AEP determined that the root cause of the noncompliance was that although AEP personnel were trained on AEP’s Failure or Disabling of Protection Systems Procedure, in this case, they did not recognize the relay failure as inadequate protection. This relay protection design is rare in that it does not have two redundant systems, which is the current design standard on the AEP system. The duration of this noncompliance is from April 2, 2014, the date AEP determined that the relay was not functional, to April 14, 2015, the date AEP made proper notifications and took corrective action. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. From April 2, 2014 through April 14, 2014, while the circuit breaker remained in service, the only protection that was not available was phase 1 to phase 3 impedance relays, and adjacent zone phase 1 to phase 3 impedance relays would have operated as designed and properly isolated any phase 1 to phase 3 fault within the relevant zone of protection within expected clearing times. Thus, the line was still protected. No harm is known to have occurred. ReliabilityFirst considered AEP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, AEP: 1) AEP conducted a meeting with the department responsible for the noncompliance to review the noncompliance; 2) developed face-to-face training and identified a target audience for the training to provide heightened awareness regarding relay failures. In the training, AEP addressed specific examples of failed relaying and how the failures are handled in AEP's documented processes; and 3) AEP delivered training to the target audience. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Baltimore Gas and Electric Company (BGE) | NCR00689 | RFC2014014269 | FAC-008-3 | R6 | On August 13, 2014, BGE submitted a Self-Report stating that, as a Transmission Owner, it had an issue of FAC-008-3 R6. BGE identified four Bulk Electric System (BES) facilities that had incorrect Facility Ratings. Specifically, in February 2014, an operations computer specialist reviewed a recently completed project at a substation and identified that Facility Ratings may not have been updated after the completion of the project. Subsequent review confirmed the suspicion and BGE conducted a review of all recent projects to determine the extent of condition. This extent of condition review revealed a total of four Facility Ratings discrepancies. In each case the out-of-date Facility Ratings were conservative, meaning the facilities were operating below equipment capacity. The two projects that resulted in Facility Ratings discrepancies included a 115 kV transmission reconductoring effort at one substation (Lipins Project) and a project to replace disconnect switches at another substation (Windy Edge Project). The Lipins Project involved a two day delay based in part on the project being completed earlier than anticipated, but the facility ratings engineer was not aware of the early completion and thus did not complete the review of the Facility Ratings until after the project was complete and the circuit was energized. BGE failed to communicate two BES Facility Ratings increases of an 89% to 109% change (approximately 200-250 MVA) in all normal, four-hour, and load dump ratings for all temperature sets. The Windy Edge Project involved an approximately nine month delay based on a project manager’s incorrect belief that Facility Ratings changes should be communicated at the end of a multi-facility project rather than on a per-facility basis. For the Windy Edge Project, BGE failed to communicate two Facility Ratings increases of 1% or less (2 to 4 MVA) for a four-hour night rating at three temperatures and 22% to 42% (60 to 150 MVA) in all normal, four-hour, and load dump ratings across all temperature sets. The duration of this noncompliance is from June 7, 2013, the start date of the earliest out-of-date Facility Rating, to January 30, 2015, the date BGE completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, one of the circuits at issue supplies only non-BES radial distribution facilities. Second, all prior Facility Ratings were more conservative than the correct Facility Ratings thus diminishing the effect of the error. Third, BGE discovered the issues relatively quickly considering the unique circumstances of the human performance root causes and through the effective implementation of an internal control to review projects post-completion. ReliabilityFirst considered BGE's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, BGE: 1) corrected and communicated all affected Facility Ratings; 2) conducted a root cause investigation, which resulted in actions to improve its Energizing New Electrical Equipment Procedure; 3) reviewed the Facility Ratings process with project management personnel; 4) provided refresher training to project management personnel; and 5) conducted a review of all Facility Ratings to verify accuracy by creating a comprehensive set of facility drawings, which ultimately resulted in the discovery and correction of one additional discrepancy related to the Windy Edge Project. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Delmarva Power & Light Company (DPL) | NCR00752 | RFC2015014809 | PRC-008-0 | R2 | On March 26, 2015, DPL submitted a Self-Certification, and on February 1, 2015, DPL submitted a self-log stating that, as a Transmission Owner it had an issue of PRC-008-0 R2. On September 15, 2014, having completed an internal compliance investigation of the issue, DPL determined that a possible violation had occurred involving PRC-008-0 R2. Specifically, DPL had failed to perform certain calibration and trip tests in a timely manner as required under its underfrequency load shedding (UFLS) equipment maintenance and testing program. Three (3) UF relays (Harmony P10, Harmony P11, and Naamans P3) for which calibrations were overdue, and two (2) circuits (Harmony 603 and 606) for which trip tests were overdue, were identified when an SME was reviewing their UFLS equipment maintenance spreadsheet. In this instance, the tab on which the above identified relays and circuits are tracked was inadvertently overlooked, thus resulting in the maintenance delay. Immediately upon identifying these issues, the calibrations were scheduled for the following day and completed on August 20, 2014, and the circuit trip tests were scheduled for the day after and completed on August 21, 2014. As of August 20, 2014, the Harmony P10 calibration was 45 calendar days overdue, the Harmony P11 calibration was 23 calendar days overdue, and the Naamans P3 calibration was 23 calendar days overdue. As of August 21, 2014, the Harmony 603 circuit trip test was 62 calendar days overdue, and the Harmony 606 circuit trip test was 68 calendar days overdue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. In all instances, the calibration and trip tests (while delayed) determined the relays and circuits to be in good operational order. Should there have been a load shed incident during this time period, the relays and circuits at issue would have performed as intended. Moreover, immediately upon identifying the issue, the calibration and trip tests were scheduled and completed, thus eliminating any on-going risk. Finally, DPL requires regular reviews of the UFLS maintenance schedule to identify upcoming tests and ensure timely completion. In the vast majority of cases, DPL’s relays and circuits are tested in a timely manner. This particular instance represents only a small number of DPL’s UFLS equipment for which regular maintenance is required, tracked and executed in a timely manner. Additionally, The distribution feeders related to the DPL UFLS equipment have been re-arranged, so that all relaying associated with UFLS is now microprocessor, which eliminates the need for calibration moving forward. No harm is known to have occurred. | To mitigate this issue, DPL: 1) completed the three (3) UF relay calibrations on August 20, 2014; 2) completed the two (2) circuit trip tests on August 21, 2014. With these calibrations and circuit trip tests complete, the UFLS equipment maintenance and test schedule was brought back into compliance and is currently up-to-date; and 3) developed a maintenance report and guideline to strengthen the UFLS maintenance schedule review process to prevent future SME oversight in the UFLS maintenance schedule review process. Collectively, the maintenance report and guideline will establish: (i) the frequency by which such reviews must be conducted, (ii) personnel roles and responsibilities, and (iii) requirements for scheduling and completion of UFLS maintenance items.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Utilities (FE Utilities) | NCR11315 | RFC2013012950 | PRC-023-2 | R2 | On September 18, 2013, FE Utilities submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-023-2 R2. FE Utilities reported that three out-of-step blocking (OSB) elements were not set to allow tripping of phase protective relays for three-phase faults that may occur during the loading conditions used to verify transmission line relay loadability. Specifically, during the testing phase of new OSB functionality being added to its circuit rating program (Circuit Loadability Program), FE Utilities discovered that certain OSB relays were inconsistent with the original OSB relay loadability spreadsheet results. Upon further investigation, FE Utilities determined that an inadvertent error in the formula within the original OSB relay loadability spreadsheet impacted these OSB relays. Because of the error in the original OSB loadability spreadsheet, the settings for three OSB relays did not meet the requirements of PRC-023-2 R2. The three 345 kV transmission lines involved in the noncompliance are each protected by three separate and independent protection schemes: 1) an electromechanical step distance scheme with no OSB, 2) a communications-assisted scheme with OSB (electromechanical relay), and 3) a microprocessor-based relay scheme (communications-assisted and step distance) with OSB (microprocessor relay elements). The duration of this noncompliance is from July 1, 2012, the date the faulty OSB spreadsheet was first used, to November 14, 2013, the date FE Utilities completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Only one of the protection schemes on each transmission line was impacted by the OSB calculation error discovered. Relay settings on the other two protection schemes for each transmission line were not impacted and acceptable fault clearing would have occurred even if the loading conditions specified in PRC-023-2 R1 were to occur simultaneously with a three-phase fault on the line. Second, FE Utilities self-identified the noncompliance and promptly mitigated the issue with both corrective and preventive actions. No harm is known to have occurred. ReliabilityFirst considered FE Utilities's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FE Utilities: 1) confirmed that the OSB relay settings are correct in both its circuit loadability program and its revised OSB relay loadability spreadsheet; 2) corrected relay settings for the three line terminals; 3) corrected the formula in the spreadsheet; 4) confirmed the relay settings for all OSB relays in service; and 5) implemented the revised relay settings on the three electromechanical OSB relays. ReliabilityFirst has verified the completion of all mitigation activity
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | GenPower Services LLC/Longview Power LLC (GPSLP) | NCR11208 | RFC2014014408 | VAR-002-1.1b | R2 | During the Compliance Audit conducted from September 22, 2014 to October 3, 2014, ReliabilityFirst determined that GPSLP, as a Generator Operator (GOP), had an issue with VAR-002-1.1b R2. Specifically, GPSLP was not operating its unit within the voltage schedule of 520+/-4 kV. GPSLP was operating with the Automatic Voltage Regulator (AVR) controlling Power Factor, not controlling voltage. While operating within this mode, GPSLP was not staying within its voltage bandwidth. GPSLP was frequently operating outside of its voltage schedule, typically fewer than 5kV over its schedule, and not at the plant’s applicable capabilities, meaning the plant could have absorbed or emitted more VARs. During the commissioning of the plant, plant operators were taught by the Original Equipment Manufacturer (OEM) to operate with the AVR in automatic with the Power Stabilization System on and with MVAR control selected, thereby controlling Power Factor. After commissioning of the plant, plant operators continued to operate the plant in this mode. By operating with AVR controlling Power Factor, GPSLP did not take action to control voltage within its voltage schedule as the Reliability Standard requires. GPSLP only provided additional MVAR support, and took action to control its voltage when requested to do so by its Transmission Operator (TOP). With AVR controlling Power Factor, the AVR tried to keep the plant at unity. By operating its plant at unity, GPSLP was not able to meet its assigned voltage schedule, as the plant was not absorbing in VARs when the voltage went too high or pushing out VARs when the voltage went too low. The main reason GPSLP operated its plant at unity is because that is how GPSLP plant operators were instructed to operate the plant by the OEM. ReliabilityFirst determined that the root cause of this violation was that GPSLP did not fully understand the requirements of the Reliability Standard at issue. The duration of this noncompliance is from January 24, 2012, the date GPSLP registered with NERC as a Generator Owner (GO)/GOP, to October 9, 2014, the date GPSLP completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. GPSLP has limited impact on the 500 kV transmission system, and the North Longview high-voltage interconnection line specifically, because the voltage typically operates at or above the voltage schedule of 525 kV. Due to these higher voltages, the Transmission Owner (TO)/TOP rarely contacted GPSLP to adjust voltage. On rare occurrences where specifically requested by the TO and/or TOP to adjust voltage, GPSLP adjusted reactive power output to absorb more VARs. There is no apparent basis for the TO’s more restrictive voltage schedule as compared to the default voltage schedule allowed by the TOP. No harm is known to have occurred. ReliabilityFirst considered GPSLP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GPSLP: 1) evaluated all of the possible ways in which it could place the AVR in automatic where it is controlling voltage rather than controlling Power Factor; 2) contacted Siemens, the OEM, for information on how to place the AVR in automatic where it is controlling voltage; 3) developed a procedure for how to place the AVR in automatic where it is controlling voltage and contacted Siemens for confirmation; 4) after receiving confirmation from Siemens, GPSLP placed the AVR into automatic where it is controlling voltage on October 9, 2014; 5) committed to provide training to the Control Room Operators and Shift Supervisors on using AVR in automatic where it is controlling voltage and on the Requirements of the VAR-002 Reliability Standard; and 5) committed to continue to contact its TOP to confirm that GPSLP is in compliance with the voltage schedule and providing the necessary grid support. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | GenPower Services LLC/Longview Power LLC (GPSLP) | NCR11208 | RFC2014014408 | VAR-002-1.1b | R2 | During the Compliance Audit conducted from September 22, 2014 to October 3, 2014, ReliabilityFirst determined that GPSLP, as a Generator Operator (GOP), had an issue with VAR-002-1.1b R2. Specifically, GPSLP was not operating its unit within the voltage schedule of 520+/-4 kV. GPSLP was operating with the Automatic Voltage Regulator (AVR) controlling Power Factor, not controlling voltage. While operating within this mode, GPSLP was not staying within its voltage bandwidth. GPSLP was frequently operating outside of its voltage schedule, typically fewer than 5kV over its schedule, and not at the plant’s applicable capabilities, meaning the plant could have absorbed or emitted more VARs. During the commissioning of the plant, plant operators were taught by the Original Equipment Manufacturer (OEM) to operate with the AVR in automatic with the Power Stabilization System on and with MVAR control selected, thereby controlling Power Factor. After commissioning of the plant, plant operators continued to operate the plant in this mode. By operating with AVR controlling Power Factor, GPSLP did not take action to control voltage within its voltage schedule as the Reliability Standard requires. GPSLP only provided additional MVAR support, and took action to control its voltage when requested to do so by its Transmission Operator (TOP). With AVR controlling Power Factor, the AVR tried to keep the plant at unity. By operating its plant at unity, GPSLP was not able to meet its assigned voltage schedule, as the plant was not absorbing in VARs when the voltage went too high or pushing out VARs when the voltage went too low. The main reason GPSLP operated its plant at unity is because that is how GPSLP plant operators were instructed to operate the plant by the OEM. ReliabilityFirst determined that the root cause of this violation was that GPSLP did not fully understand the requirements of the Reliability Standard at issue. The duration of this noncompliance is from January 24, 2012, the date GPSLP registered with NERC as a Generator Owner (GO)/GOP, to October 9, 2014, the date GPSLP completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. GPSLP has limited impact on the 500kV transmission system, and the North Longview high-voltage interconnection line specifically, because the voltage typically operates at or above the voltage schedule of 525kV. Due to these higher voltages, the Transmission Owner (TO)/TOP rarely contacted GPSLP to adjust voltage. On rare occurrences where specifically requested by the TO and/or TOP to adjust voltage, GPSLP adjusted reactive power output to absorb more VARs. There is no apparent basis for the TO’s more restrictive voltage schedule as compared to the default voltage schedule allowed by the TOP. No harm is known to have occurred. ReliabilityFirst considered GPSLP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, GPSLP: 1) evaluated all of the possible ways in which it could place the AVR in automatic where it is controlling voltage rather than controlling Power Factor; 2) contacted Siemens, the OEM, for information on how to place the AVR in automatic where it is controlling voltage; 3) developed a procedure for how to place the AVR in automatic where it is controlling voltage and contacted Siemens for confirmation; 4) after receiving confirmation from Siemens, GPSLP placed the AVR into automatic where it is controlling voltage on October 9, 2014; 5) committed to provide training to the Control Room Operators and Shift Supervisors on using AVR in automatic where it is controlling voltage and on the Requirements of the VAR-002 Reliability Standard; and 5) committed to continue to contact its TOP to confirm that GPSLP is in compliance with the voltage schedule and providing the necessary grid support. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | ITC Transmission | NCR00803 | RFC2014013846 | EOP-005-2 | R1 R1.4 | On May 7, 2014, the ITC Transmission, METC, and ITC Midwest (NCR10192) (ITCM) (collectively, the ITC Companies) submitted Self-Reports to ReliabilityFirst and MRO stating that, as Transmission Operators (TOPs), they had an issue of EOP-005-2 R1. MRO administratively dismissed the Alleged Violation with Violation ID MRO2014013955 and tranferred enforcement responsibility to ReliabilityFirst. The Regions determined that the ITC Companies violated EOP-005-2 R1 by not including megavar capacity for their Blackstart Resources in their restoration plan, a single plan shared by the ITC Companies. EOP-005-2 went into effect on July 1, 2013, and included an additional requirement (beyond what was required for EOP-005-1) for explicit documentation of various characteristics of the Blackstart Resources (including the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit) in restoration plans. All of these characteristics, with the exception of the megavar capacity, was included in the ITC System Restoration Plan under EOP-005-1. The ITC System Restoration Plan failed to include the megavar capacity of the Blackstart Resources as required by EOP-005-2 R.1.4. In reviewing ITC’s System Restoration Plan in preparation for initial compliance with EOP-005-2, the ITC Companies inadvertently failed to recognize that they did not explicitly identify the megavar capacity for their Blackstart Resources in their System Restoration Plan. The duration of this noncompliance is from July 1, 2013, the date the ITC Companies were required to comply with EOP-005-2 R1, to May 1, 2014, the date the ITC Companies updated the ITC System Restoration Plan to include the megavar capacity of the Blackstart Resources. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The lack of identification in ITC’s System Restoration Plan of megavar capacity represented an administrative oversight that would have had little or no impact on the plan’s effectiveness. First, the System Restoration Plan had all other required information, including a description of the priority for establishing off-site power to nuclear plants; procedures for restoring interconnections with other TOPs; identification of Blackstart Resource characteristics including Blackstart Resource name, location, megawatt capacity, and type of unit; identification of cranking paths and initial switching requirements between each Blackstart Resource and the unit to be started; identification of acceptable voltage and frequency limits during restoration; Operating Processes to re-establish connections within the TOP system; Operating Processes to restore load required to restore the system; and Operating Processes for transferring authority back to the Balancing Authority (BA). Second, operating personnel can obtain megavar capacity information outside of the System Restoration Plan. In this case, for the ITCT system and one of the islands in the ITCM systems, the Blackstart Resources are diesel generators located at the site of the target unit where the initial cranking path is internal to the plant. The loading of these Blackstart Resources will be performed using plant processes by plant personnel familiar with the capability of the Blackstart Resources. For METC and the other island in the ITCM systems where the Blackstart Resources will be used in initial cranking paths controlled by the ITC system operator, the megavar capacity is readily available to the ITC system operators via the Transmission Management System, which is used to implement the restoration procedures. Thus, not explicitly having the megavar capacity in the System Restoration Plan would have had little or no impact on ITC carrying out the System Restoration Plan. No harm is known to have occurred. ReliabilityFirst considered ITC Companies' compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ITC Companies will complete the following mitigation activities by June 30, 2015: 1) update the System Restoration Plan to include megavar capacity 2) committed to meet with subject matter experts about the Alleged Violation and the ramifications that it had on the Bulk Electric System (BES), if any; 3) committed to have root cause analysis work completed by its Reliability Compliance personnel and a subject matter expert; and 4) committed to build an internal control for a subject matter expert to review any initiated changes and update the System Restoration Plan semi-annually as necessary.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | METC (ITC Companies) | NCR00820 | RFC2014013847 | EOP-005-2 | R1 R1.4 | On May 7, 2014, the ITC Transmission, METC, and ITC Midwest (NCR10192) (ITCM) (collectively, the ITC Companies) submitted Self-Reports to ReliabilityFirst and MRO stating that, as Transmission Operators (TOPs), they had an issue of EOP-005-2 R1. MRO administratively dismissed the Alleged Violation with Violation ID MRO2014013955 and tranferred enforcement responsibility to ReliabilityFirst. The Regions determined that the ITC Companies violated EOP-005-2 R1 by not including megavar capacity for their Blackstart Resources in their restoration plan, a single plan shared by the ITC Companies. EOP-005-2 went into effect on July 1, 2013, and included an additional requirement (beyond what was required for EOP-005-1) for explicit documentation of various characteristics of the Blackstart Resources (including the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit) in restoration plans. All of these characteristics, with the exception of the megavar capacity, was included in the ITC System Restoration Plan under EOP-005-1. The ITC System Restoration Plan failed to include the megavar capacity of the Blackstart Resources as required by EOP-005-2 R.1.4. In reviewing ITC’s System Restoration Plan in preparation for initial compliance with EOP-005-2, the ITC Companies inadvertently failed to recognize that they did not explicitly identify the megavar capacity for their Blackstart Resources in their System Restoration Plan. The duration of this noncompliance is from July 1, 2013, the date the ITC Companies were required to comply with EOP-005-2 R1, to May 1, 2014, the date the ITC Companies updated the ITC System Restoration Plan to include the megavar capacity of the Blackstart Resources. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The lack of identification in ITC’s System Restoration Plan of megavar capacity represented an administrative oversight that would have had little or no impact on the plan’s effectiveness. First, the System Restoration Plan had all other required information, including a description of the priority for establishing off-site power to nuclear plants; procedures for restoring interconnections with other TOPs; identification of Blackstart Resource characteristics including Blackstart Resource name, location, megawatt capacity, and type of unit; identification of cranking paths and initial switching requirements between each Blackstart Resource and the unit to be started; identification of acceptable voltage and frequency limits during restoration; Operating Processes to re-establish connections within the TOP system; Operating Processes to restore load required to restore the system; and Operating Processes for transferring authority back to the Balancing Authority (BA). Second, operating personnel can obtain megavar capacity information outside of the System Restoration Plan. In this case, for the ITCT system and one of the islands in the ITCM systems, the Blackstart Resources are diesel generators located at the site of the target unit where the initial cranking path is internal to the plant. The loading of these Blackstart Resources will be performed using plant processes by plant personnel familiar with the capability of the Blackstart Resources. For METC and the other island in the ITCM systems where the Blackstart Resources will be used in initial cranking paths controlled by the ITC system operator, the megavar capacity is readily available to the ITC system operators via the Transmission Management System, which is used to implement the restoration procedures. Thus, not explicitly having the megavar capacity in the System Restoration Plan would have had little or no impact on ITC carrying out the System Restoration Plan. No harm is known to have occurred. ReliabilityFirst considered ITC Companies' compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ITC Companies will complete the following mitigation activities by June 30, 2015: 1) update the System Restoration Plan to include megavar capacity 2) committed to meet with subject matter experts about the Alleged Violation and the ramifications that it had on the Bulk Electric System (BES), if any; 3) committed to have root cause analysis work completed by its Reliability Compliance personnel and a subject matter expert; and 4) committed to build an internal control for a subject matter expert to review any initiated changes and update the System Restoration Plan semi-annually as necessary.
2015-05-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Northern Indiana Public Service Company (NIPSCO) | NCR02611 | RFC2014014190 | PRC-005-1b | R2.1 | On July 10, 2014, NIPSCO submitted a Self-Report stating that, as a Generator Owner, it was noncompliant with PRC-005-1b R2.1. NIPSCO determined it could not provide evidence that it completed calibration maintenance and testing on certain relays in accordance with the four year testing interval outlined in NIPSCO’s Program. Specifically, NIPSCO’s Program contained a conservative, four year schedule for periodic testing of the subject relays. In April 2014, NIPSCO completed calibration tests on 17 relays at the Sugar Creek Generating Plant. On or around June 16, 2014, however, NIPSCO discovered through an internal review of Protection System device maintenance/testing dates, that there was no evidence documenting the performance of calibration tests on those 17 relays at the Sugar Creek Generating Plant from April 2010 to April 2014, as required by NIPSCO’s Program. Testing should have occurred in April 2010 according to NIPSCO’s Program, but the last documented testing for the relays occurred in April 2009. The root cause of this violation was ineffective use of software to track the required testing dates. Specifically, NIPSCO had software in place that could have automatically and effectively tracked the required testing dates, yet the NIPSCO personnel responsible for tracking testing dates were unnecessarily doing so manually. The duration of this noncompliance is from April 20, 2013, the date NIPSCO was required to test the subject relays per its Program, to April 15, 2014, the date NIPSCO completed its Mitigating Activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The four year interval under the current NIPSCO Program is conservative by industry standards. Importantly, these relays would be subject to a six year interval under PRC-005-2. In this case, NIPSCO provided evidence that the relays were tested five years earlier with no issues. When the relays were tested in April 2014, NIPSCO found that no re-calibration was necessary and that there were no other issues with the relays. Additionally, all of the subject relays are microprocessor-type relays which are often specified by the manufacturer as not requiring regular calibration tests because they are digital machines that generally cannot fall out of alignment. No harm is known to have occurred. ReliabiltyFirst considered NIPSCO's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because NIPSCO’s prior violations of PRC-005-1b R2.1, are distinguishable from the instant noncompliance. The prior violations involved inadequate and missing documentation of test and inspection records and missing some relay and battery tests. In contrast, the instant noncompliance involved certain relay tests being performed one year later than NIPSCO’s conservative Program required (but in a manner that would have been compliant with a subsequent version of PRC-005). There were no documentation issues, as all of the tests were properly documented. Therefore, although NIPSCO has prior violations of PRC-005-1b R2.1, ReliabilityFirst did not consider NIPSCO’s violation history as a factor warranting an alternative disposition method. | To mitigate this issue, NIPSCO: 1) committed to and provided evidence of testing all of the subject relays as of April 2014; 2) personnel began to use its Cascade software to monitor the maintenance and testing intervals for relays (instead of the manual monitoring that resulted in the instant noncompliance); and 3) provided evidence that its Compliance Engineers are monitoring the Cascade software and database in order to ensure that maintenance and testing intervals are followed. ReliabilityFirst has verified the completion of all mitigation activity.
2015-05-28 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2015014709 | VAR-001-4 | R5 | On February 27, 2015, Duke submitted a Self-Certification reporting that, as a Transmission Operator (TOP), it had an issue with VAR-001-4 R5. Duke found two occurrences where it did not provide the Generator Operator (GOP) with the notification requirements for deviations from the voltage or Reactive Power schedule. Duke discovered the issue on February 13, 2015 while performing an extent of condition review prompted by a similar issue found at an affiliate. For Duke Energy-owned GOP facilities in the Duke TOP area, Duke issues a document that includes language to notify the Duke System Operating Center (SOC), as the TOP, of deviations from its issued voltage or Reactive Power schedule. Duke does not issue the document to Independent Power Producers (IPP) on the Duke system because it contains specific proprietary information that is not suitable for sharing with IPPs. Instead, Duke issues each IPP a separate voltage or Reactive Schedule. However, these separate voltage or Reactive Power schedules do not include the notification requirements for deviations from the voltage or Reactive Power schedules because Duke believed there was language in each Interconnection Agreement that addressed the required notifications. During its review, Duke discovered there was no such language in the Interconnection Agreement for the two IPPs to promptly notify the Duke SOC, as the TOP, if the GOP was unable to maintain the specified voltage or Reactive Power schedule. The root cause of this issue was that Duke incorrectly believed there was language in each Interconnection Agreement that addressed the required notifications. This issue lasted from October 1, 2014, when the Reliability Standard became mandatory and enforceable, through March 9, 2015, when Duke provided reporting requirements to the GOPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Duke’s failure to provide notification requirements for deviations from the voltage or Reactive Power schedules could have caused the two GOPs to fail to notify Duke of deviations from its voltage or Reactive Power schedule. However, the Duke TOP monitors voltage across its entire footprint through its Energy Management System and a voltage monitoring tool. The output from one of the GOPs is included on the voltage monitoring tool that specifically monitors the voltage on the GOP’s bus lines where they interconnect with Duke, allowing Duke to detect deviations from the GOP’s schedule. This GOP’s operators were aware of the voltage control requirements imposed by the interconnection agreement. The second GOP is not included in the voltage monitoring tool because it is not a GOP in the Duke TOP Area. Instead, the second GOP is in a neighboring TOP Area and is under the neighboring TOP’s authority. The second GOP is normally not connected to only Duke and had not been connected to only Duke during this issue. In the event that the second GOP was under Duke’s authority, the Duke SCADA continuously monitors the point of interconnection with the second GOP, allowing Duke to detect deviations from the second GOP’s schedule. Duke verified that all of the voltage and Reactive Power schedules it submitted to all other GOPs provided notification requirements for deviations from the specified schedules or that the requirements were included in the interconnection agreements. No harm is known to have occurred. SERC considered Duke’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, Duke: 1) issued a letter to each of the GOPs involved outlining the TOP notification requirements for deviations from their respective voltage schedules; and 2) issued the spring voltage schedules to each GOP in the Duke TOP Area, which included the TOP notification requirements.
2015-05-28 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2015014625 | VAR-001-4 | R5 | On February 9, 2015, DEP submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue with VAR-001-4 R5. DEP reported that it did not provide the Generator Operator (GOP) with the notification requirements for deviations from the voltage or Reactive Power schedule. On September 25, 2014, DEP sent all of the interconnected GOPs a voltage or Reactive Power schedule in preparation for the October 1, 2014 implementation of VAR-001-4. DEP issued the same Reactive Power schedule to one GOP that it had previously issued on May 23, 2013. The re-issuance specified the Reactive Power schedule to be maintained by the plant in question but did not contain notification requirements for deviations from the Reactive Power schedule. DEP identified the oversight on January 30, 2015 during a review of compliance evidence in preparation for annual SERC Self-Certifications. DEP attributed the oversight to human error because personnel failed to include the notification requirements in the Reactive Power schedule for a single GOP. DEP reviewed all of the voltage and Reactive Power schedules it submitted and found that it provided notification requirements for deviations from voltage or Reactive Power schedules to all other GOPs. This issue lasted from October 1, 2014, when the Standard became mandatory and enforceable, until February 2, 2015, when DEP provided the GOP with the notification requirements for deviations from the Reactive Power schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEP’s failure to provide notification requirements for deviations from the Reactive Power schedule could have caused the GOP to fail to notify DEP of deviations from its Reactive Power schedule. However, the plant in question is a single 35 MVA generator connected to a system of approximately 12,000 MVA of available generation. Because of its size, DEP does not rely on Reactive Power from the plant in question as an essential element of its Reactive Power reserve. The Reactive Power schedule instructs the plant in question to maintain only 4 MVA when operating and it has not produced any generation to the DEP system since December 12, 2014. DEP has not experienced any operational issues associated with the plant in question related to Reactive Power or voltage support. DEP does not have any voltage issues in this area of the system, and has additional reactive resources in the area if they are needed. DEP verified that all of the voltage and Reactive Power schedules it submitted to all other GOPs provided notification requirements for deviations from the specified schedules. No harm is known to have occurred. SERC considered DEP’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, DEP re-issued the Reactive Power schedule to the plant in question with clear language that provided notification requirements for when the GOP cannot meet the Reactive Power schedule.
2015-05-28 | SERC Reliability Corporation (SERC) | Florida Reliability Coordinating Council, Inc. (FRCC) | NCR00026 | SERC2014013681 | EOP-006-2 | R5 | On April 2, 2014, FRCC submitted a Self-Report to SERC stating that, as a Reliability Coordinator (RC), it had an issue with EOP-006-2 R5. FRCC failed to approve or disapprove the Transmission Operator’s (TOP) submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the TOP. On December 6, 2013, a TOP submitted a restoration plan to FRCC via email to the administrative RC mailbox for its annual review. On the same day, FRCC migrated its e-mail to new servers. Technical issues with accessing and monitoring the mailbox that arose due to this migration prevented FRCC operations staff from identifying new receipts to the administrative RC mailbox from December 6, 2013 through January 9, 2014. As a result, the submitted TOP restoration plan was not approved or disapproved by FRCC within 30 calendar days following the receipt of the restoration plan from the TOP. SERC reviewed FRCC’s procedure for TOP restoration plan submittal, review, and approval, effective November 1, 2013. Section 5.2.1 of the procedure indicated that FRCC staff would be notified on their individual email accounts when a TOP restoration plan was submitted to the administrative RC mailbox. FRCC later determined that this process was not implemented until January 2014. On January 9, 2014, a FRCC staff member attempted to review emails in the RC mailbox during an operations staff meeting and found that the mailbox was inaccessible. The IT department was immediately notified and fixed the issue. It was at this time that FRCC operations staff discovered the TOP restoration plan that was submitted on December 6, 2013. On January 14, 2014, FRCC’s Regional Operations Coordinator (ROC), who is responsible for developing the annual review schedule and ensuring that the schedule is followed, notified the FRCC’s Member Services Regulatory Director of the potential RC compliance issue. This resulted in a discussion about how to best move forward to get the RC’s review back on track, a decision to start gathering evidence to determine if a possible noncompliance had occurred, and discussion of any mitigating steps to put into place immediately to prevent recurrence. Following the discussion, the ROC contacted the TOP and suggested that the TOP withdraw its December 6, 2013 submission. FRCC’s process for reviewing restoration plans does not have a specific step in which it can request resubmission of a TOP’s restoration plan. No FRCC officers were involved in the discussion or the suggestion that the TOP withdraw its December 6, 2013 submission. On January 14, 2014, the TOP withdrew its restoration plan submission. On the same day, the TOP resubmitted its restoration plan for approval, which FRCC approved on February 6, 2014, 62 days after the TOP’s restoration plan was first submitted. There were no changes in the TOP’s resubmitted restoration plan from its December 6, 2013 submission. This issue lasted from January 6, 2014, 31 days after the TOP submitted its restoration plan to FRCC, through February 6, 2014, when FRCC approved the TOP's restoration plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC’s failure to approve or disapprove the TOP’s restoration plan within 30 days of its receipt could have resulted in the use of an outdated or unapproved TOP restoration plan that may not have been coordinated and compatible with the RC’s restoration plan and other TOP’s restoration plans within the RC area. However, the TOP’s restoration plan was submitted for annual review and had no revisions to the previously approved restoration plan. The use of the restoration plan was not required during the issue. No harm is known to have occurred. SERC considered FRCC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, FRCC: 1) restored operation staff's access to the administrative RC mailbox; and 2) created an auto-forward feature that automatically forwards copies of all incoming submissions to the RC mailbox to the personal mailbox of four FRCC operations staff personnel.
2015-05-28 | SERC Reliability Corporation (SERC) | Florida Reliability Coordinating Council, Inc. (FRCC) | NCR00026 | SERC2014014407 | IRO-005-1 | R1 | On October 22, 2014, FRCC submitted a Self-Report stating that, as a Reliability Coordinator (RC), it had an issue with IRO-005-3.1a R1.6. FRCC failed to monitor the current Area Control Error (ACE) for all of its Balancing Authorities (BAs). SERC later determined that the issue extended back to Version 1 of the Standard. There are ten BAs within FRCC’s footprint. FRCC has the capability to directly monitor nine of the BA ACE values. New Smyrna Beach (NSB) is the tenth BA and its ACE is not directly monitored by the RC. Its ACE value was incorporated into Duke Energy Florida’s (DEF) BA values. DEF had been providing supplemental regulation service to NSB since 1992 under a FERC filed Interchange Agreement. On May 6, 2014, the NSB remote terminal unit (RTU) used to transmit the ACE value to DEF failed, preventing the ACE BA monitoring process from occurring. Although DEF continued to provide its ACE value to FRCC, the equation used to generate this ACE value did not include NSB’s data. Therefore, this RTU failure prevented FRCC from monitoring current ACE values for NSB. In addition, on September 30, 2014, DEF notified FRCC that it was ending t the regulation service. According to DEF, the RTU failure interrupted the regulation service on May 6, 2014 and DEF did not restore the service during the remaining term of the contract. FRCC discovered this issue on October 3, 2014 when DEF notified FRCC of the NSB RTU issue and contract termination. FRCC stated that the primary cause of the issue was that FRCC did not have adequate controls in place to directly monitor NSB’s ACE if an issue occurred with the DEF and NSB process that was in place. Also, FRCC did not have sufficient knowledge of the NSB and DEF contract terms, specifically the expiration date. SERC determined that because FRCC did not have the ability to monitor the NSB ACE at any time during the enforceable period of IRO-005, the issue began on June 18, 2007 instead of at the time of the RTU failed. This issue lasted from June 18, 2007, when the Standard became mandatory and enforceable, through October 6, 2014, the date FRCC implemented a process to calculate the NSB real time ACE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC’s failure to directly monitor the NSB ACE for more than seven years could have resulted in FRCC being unaware of ACE deviations on a real time basis that could produce reliability impacts. However FRCC received ACE information from DEF that incorporated the ACE information of NSB for slightly less than seven years. During the time period for which DEF did not provide regulation service to NSB and thus did not include the NSB ACE information in its ACE information, FRCC continued to monitor the aggregate FRCC ACE Area parameter and the other BAs' respective ACE information, which would have allow FRCC to identify any reliability impacts to the RC Area that were attributable to NSB BA ACE deviations. The NSB BA’s peak system load during the summer of 2014 was 91 MW out of FRCCs peak load of 45,221 MW (0.2%) and would produce minimal impact on the ACE of the FRCC Region as a whole. Any significant changes in NSB ACE values would also have been detected by FRCC as unscheduled flows on the NSB’s three tie-lines with its two interconnected Transmission Operators. In addition, as part of normal operations, FRCC monitored transmission elements and potential contingencies in and around the NSB system to ensure that it would have identified and mitigated reliability issues related to transmission loading in the area. No harm is known to have occurred. SERC considered FRCC’s compliance history and determined that there were no relevant instances of noncompliance. | To mitigate this issue, FRCC: 1) implemented a calculation on their EMS which calculates the NSB ACE using real-time input data available to the RC; 2) modified and distributed the FRCC member services data modeling specification and collection procedure to address the requirement for the RC to receive ACE values directly from all BAs; 3) reviewed the implementation status for the NSB Inter-Control Center Communications Protocol (ICCP) link; and 4) confirmed that NSB configured their ICCP link to the RC and is transmitting their ACE value directly to the RC’s EMS.
2015-05-28 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority - TVAM (TVAM) | NCR01341 | SERC2014014313 | INT-004-2 | R2 | On September 8, 2014, TVAM submitted a Self-Report stating that, as a Purchasing-Selling Entity, it had an issue with INT-004-2 R2. TVAM failed to ensure a tag was updated for the next available scheduling hour and future hours as required by INT-004-2 R2.2. This issue is a result of a power trader unintentionally creating two different tags for the same dynamic load for the same time. Further, the hourly values were incorrectly calculated and displayed as an average rather than a sum on the Dynamic Schedule Monitor, resulting in an indication of within bounds schedule deviations on the trader’s monitor. The schedule for the tags were 60 MW and 45 MW, resulting in total of 105 MW scheduled for an actual load that varied from 50 MW to 58 MW during the three hour period of the issue. On June 20, 2014, TVAM’s estimated average hourly energy profile (e-tag) for a dynamically scheduled load served in the Southern Company Balancing Authority Area deviated from the actual hourly integrated energy by more than 47 to 55 MWs for hours ending (HE) 1 through HE 3. The normal practice is to have one active tag for a dynamic schedule at any given time. TVA traders created the dynamic tags each Thursday for the upcoming Friday through Thursday. Tag #1 was scheduled to expire at HE 24 on June 19, 2014. However, on June 19, 2014, the trader made a tag update at 9:15 p.m., which extended the tag expiration to HE 7 on June 20, 2014. This extension created an overlap with tag #2, the new weekly tag. Even though the previous hour’s deviation was only 20 MWs, the trader made this adjustment to the tag to keep the deviations below the +25 MW limit. However, the trader forgot about the new tag. The trader’s Dynamic Schedule Monitor tool, used to alert the trader when deviations approached or exceeded the requirement limits, gave erroneous ‘in bounds’ readings because it averaged rather than summed the MWs on the two tags due to a programming error. Even though the trader received no alarms, the trader was monitoring the data and identified that the tool did not display the last adjustment made. The trader reviewed tag #1 and verified that it reflected the latest actual schedule data for the next few hours, and therefore made no further adjustments for those hours. During HE 3, the trader realized that there were two tags. The trader made adjustments to both tags effective at HE 3. The trader zeroed out the MWs on Tag #1 and changed the start time of Tag #2. The deviation returned within bounds for HE 4. SERC determined that TVAM had an issue with INT-004-2 R2 because TVAM failed to ensure a tag was updated for the next available scheduling hour and future hours as required to ensure the hourly average energy profile indicated on the tag did not deviate by more than +25 megawatt-hours. Specifically, TVAM unintentionally created two different tags for the same dynamic load for the same time. The schedules for these tags were 60 MW and 45 MW, resulting in a total of 105 MW scheduled for an actual load that varied from 50 MW to 58 MW during the issue. This issue lasted from HE 1 on June 20, 2014, when TVAM created two tags for the same dynamic load, resulting in deviation of greater than 25 MW from the hourly average energy profile, through HE 3 on June 30, 2014, when TVAM zeroed out one of the tags, bringing the any deviation within 25 MW of the hourly average energy profile. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TVAM’s failure to update the tag to stay within the 25 MW band could cause the Interchange Distribution Calculator tool used for congestion management in the Eastern Interconnection to overestimate or underestimate the impact of the dynamic tag on one or more flowgates, which could result in inefficient curtailment actions to relieve any excessive flowgate loading. However, TVAM reviewed NERC TLR logs for June 20, 2014, HE 1 through HE 3 and found no curtailments of the dynamic tags in question during the issue, indicating that loading on these active flowgates was not significantly impacted by this dynamic schedule issue. In addition, the issue resulted in a difference of only a maximum of 55 MW of scheduled load verses 17,690 MW of actual load on the system at the time of the issue. No harm is known to have occured. SERC considered TVAM's INT-004-2 R2 compliance history in determining the disposition track. TVAM'’s relevant prior noncompliance with INT-004-2 R2 include(s): NERC Violation IDs SERC2012010846 and SERC2013012788. SERC determined that TVAM's compliance history should not serve as a basis for applying a penalty. The underlying conduct of the instant issue and the previous issues were different. The first prior issue involved a failure to update dynamic tags because of inaccurate information on display screens resulting from a software configuration change that led to a source code error. The second prior issue involved a failure to adjust the tagged schedule because an alarm did not issue due to a coding error made for the spring time change. The instant issue resulted from having two tags for the same dynamic load for the same time, the hourly values of which were incorrectly calculated and displayed as an average rather than a sum on the Dynamic Schedule Monitor, which resulted in a false indication of within bounds schedule deviations. The actions taken to prevent recurrence for the previous violations would not have prevented this occurrence. In addition, on March 19, 2015, FERC approved the removal of the PSE function from the NERC Compliance Registry, noting that the PSE function is “primarily market-driven and has minimal reliability impacts.” | To mitigate this issue, TVAM: 1) scheduled a reminder to review tags on each trader’s calendar two hours before the start of the new weekly dynamic tags; and 2) developed a solution for the Dynamic Schedule Monitor tool to correctly calculate the MWs when there are multiple tags.
2015-05-28 | SERC Reliability Corporation (SERC) | Virginia Electric and Power Company (DP, LSE, TO) (VEP-Trans) | NCR01214 | SERC2014014177 | PRC-023-2 | R1 | On July 28, 2014, VEP-Trans submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R1. VEP-Trans failed to use any one of the Requirement R1 criteria for certain specific circuit terminals to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the Bulk Electric System (BES) for all fault conditions. VEP-Trans should have set the non-compliant relays to meet criterion 1. In preparation for the PRC-023-2 R1 switch-on-to-fault (SOTF) loadability requirement becoming effective on October 1, 2013, VEP-Trans conducted a review to identify relays having applicable SOTF functionality. VEP-Trans identified 137 relays, 48 of which would not have met the future SOTF loadability requirement. VEP-Trans created work orders to reset each of these 48 relays prior to October 1, 2013. VEP-Trans creates, manages, and administers all relay reset work through its Systems, Applications, and Products work management program (SAP). On July 10, 2014, as part of an annual review, VEP-Trans checked to verify that the relay resets issued for the 48 relays with applicable SOTF functionality had been completed. VEP-Trans found nine locations, each including redundant digital relays, for a total of 18 digital relays, with applicable SOTF functionality, where VEP-Trans had not reset the relays by the effective date of October 1, 2013 for SOTF schemes. VEP-Trans reset 12 relays in the interim, from October 1, 2013 through July 10, 2014. As of July 10, 2014, VEP-Trans had not reset relays at three locations involving six relays. On July 10, 2014, VEP-Trans requested expedited completion of the relay resets for the remaining six relays. On July 18, 2014, VEP-Trans completed resetting these relays. VEP-Trans determined that the cause of the issue was a human performance failure. Specifically, VEP-Trans’ engineers and relay technical supervision failed to adequately follow-up on and communicate SAP work orders, identify this work as necessary for compliance with a NERC Reliability Standard, and communicate the importance of meeting the required project completion date. This issue lasted from October 1, 2013, when the Standard became mandatory and enforceable for SOTF schemes, through July 18, 2014, when VEP-Trans finished resetting the relays using criterion 1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. VEP-Trans’ failure to correctly set the relays with SOTF functionality by October 1, 2013 raised the risk that the breaker would not reclose, resulting in a lockout instead of a momentary interruption. However, VEP-Trans reset four of the 18 relays within a month of the October 1, 2013 enforceable date, and the remaining relays had SOTF limits set between 93% and 119% of the respective lines’ highest seasonal Facility Rating until they were reset. During the issue, the highest peak load recorded on the lines associated with the nine affected locations did not exceed 60% of the respective SOTF limit. SOTF protection schemes are designed to provide backup protection for a brief period following a breaker closure when the primary protection is unavailable. SOTF relays do not affect normal breaker operation because SOTF protection is designed to operate only during a breaker reclosure following a fault or disturbance. No harm is known to have occurred. SERC considered VEP-Trans’ PRC-023-1 R1 compliance history in determining the disposition track. VEP-Trans’ relevant prior noncompliance with PRC-023-1 R1 includes: NERC Violation ID SERC2012011535. SERC determined that VEP-Trans' compliance history should not serve as a basis for applying a penalty. The underlying conduct of the instant issue and the prior issue was different. In the prior issue, VEP-Trans had a discrepancy between the relay control drawings and the relay setting documentation, resulting in a single three-phase set of relays not being set to operate above 150% of the highest seasonal Facility Rating of a circuit. In the current issue, relays with SOTF functionality were not set to the appropriate level prior to the effective date of PRC-023-2 R1 for SOTF schemes because VEP-Trans did not clearly communicate the need to reset the relays prior to the effective date and did not verify the completion of that work until after the effective date. | To mitigate this issue, VEP-Trans: 1) reset the relays at the three locations at issue (six relays); 2) implemented using a SAP work order type titled, “Grayland Avenue Corrective Maintenance” (GRCM) for NERC compliance driven relay resets, which allows for the creation of grace periods and compliance dates within a work order for tracking, monitoring, and notification purposes; 3) initiated flagging GRCM work orders as “NERC”. Work orders flagged as NERC are included on VEP-Trans' executive compliance scoreboard, where open NERC compliance related work is continuously monitored to ensure compliance dates are met; 4) implemented standard “work order long text” language during the creation of SAP work orders that includes: a) work order type and location; b) detailed description of work to be performed; c) target date of resets (if not project resets); d) compliance dates (where applicable); and e) engineer’s name and phone number; 5) implemented a standard email template from VEP-Trans engineers to relay technical supervision following SAP work order creation that includes all information stated in the work order long text; and 6) conducted targeted training on the template language and the use of the GRCM work order and “NERC” flag by all applicable engineers.
2015-05-28 | Texas Reliability Entity (Texas RE) | ExxonMobil Refining and Supply Company (ExxonMobil) | NCR04058 | TRE2014014486 | VAR-002-3 | R1 | On December 8, 2014, ExxonMobil submitted a Self-Report stating that, as a Generator Operator (GOP), it had an issue with VAR-002-3 R1. Specifically, ExxonMobil was operating with the AVR in service and controlling power factor, not voltage, and was not exempted from operating with the AVR in service and controlling voltage by the TOP, ERCOT ISO. The root cause of the issue is that ExxonMobil failed to make timely technical changes to its equipment in order to meet compliance with VAR-002-3. The noncompliance is ongoing and will continue until the AVR-voltage equipment is installed and functional by March 15, 2016. The extended time frame is due to the following three actions that ExxonMobil must complete to become compliant and to prevent recurrence: 1) ExxonMobil will make hardware and software modifications to five generators in the complex. There is considerable complexity in terms of implementing the technical requirements and components as well as coordinating staff and equipment outages in order to facilitate the work; 2) staff will be trained to implement the changeover; and 3) procedures will be updated and manpower expended to stay abreast of the latest developments in new Standards. Texas RE determined the issue duration to be from October 1, 2014, when VAR-002-3 R1 became mandatory and enforceable, through present. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ExxonMobil is a petrochemical refinery that houses private load and generation which interconnects to the ERCOT grid at 138 kV. A failure to operate with the AVR in service could possibly result in voltage instability. However, the risk to the reliability of the BPS was reduced by the following factors. On average, the facility injects 50 MW into the ERCOT grid. The facility has been operating with the AVR in service controlling power factor with automatic step-changing voltage control on the generator step-up transformer for several years. Lastly, the local transmission operator and ERCOT ISO were aware of the AVR equipment limitations. No harm is known to have occurred. Texas RE considered ExxonMobil’s compliance history and determined there were no relevant instances of noncompliance. | ExxonMobil will complete the following mitigation activities by March 15, 2016: 1) update the ExxonMobil internal notification procedure for new standards; 2) update procedures and operator manuals and develop required pre-outage mechanical work scope for facilities; 3) complete required pre-outage mechanical work scope for facilities; and 4) complete mechanical work, complete updating procedures and training, and transition to voltage control.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Avista Corporation (AVA) | NCR05020 | WECC2014014518 | BAL-005-0.2b | R17 | On December 15, 2014, AVA submitted a Self Report to WECC stating that, as a Balancing Authority, it had an issue with BAL-005-0.2b R17. Specifically, the AVA business unit responsible for the annual inspections kept the reminder to check and calibrate the two devices in MS Outlook, but the AVA personnel responsible for the annual inspection overlooked the Outlook reminder notice to perform the work. As a result, AVA did not timely perform the required inspections and calibrations. However, AVA provided evidence showing that it had checked and calibrated each applicable time error and frequency device in October 2014. The root cause of this compliance exception is human error and a lack of an internal control to ensure AVA timely performed annual maintenance activities. This issue started from September 13, 2012, the date the standard was enforceable for AVA, and ended October 29, 2014, when AVA inspected and calibrated its time error and frequency devices for calendar year 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. Specifically, AVA failed to document the devices which could potentially affect the frequency bias component of Area Control Error (ACE). If the time error and frequency devices are out of calibration, the frequency bias component of ACE could be calculated incorrectly. The effect of an inaccurate ACE value could result in over or under generation. As a preventative control, AVA implemented a reminder to check and calibrate the two time error and frequency devices in MS Outlook. The Outlook reminder notice was only on one computer, operated by the business unit technician. However, if the technician was distracted or called to do other duties, the technical might overlook or dismiss the reminder. As a detective control, AVA implemented a review of the records from the prior year. The review was not a documented procedure but was an ad hoc event. In this review, the technician discovered the missing documentation and contacted the AVA Compliance staff. AVA then conducted the required inspections and calibrations. As a compensating control, AVA inspected and calibrated the two time error and frequency devices in 2014. No harm is known to have occured. In consideration of AVA’s compliance history, WECC notes that AVA does not have previous violations of this Standard and requirement. | To mitigate this issue, AVA: 1) implemented the CATSWeb compliance tracking system and used the system successfully to alert operators, and to track maintenance work for other processes.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Bonneville Power Administration (BPA) | NCR05032 | WECC2014014494 | MOD-001-1a | R3 | On December 10, 2014, BPA submitted a Self Report to WECC stating that, as a Transmission Service Provider, it had an issue with MOD-001-1a R3. Specifically, BPA reported that its ATCID contains language stating that “BPA can simulate a reliability-based flow in the direction counter to prevailing flows on all of its ATC Paths. Therefore, BPA calculates reliability-based TTCs for all of its ATC Paths.” However, for two of BPA’s ATC Paths, BPA does not calculate TTCs. For two BPA ATC Paths, BPA does not generate TTC values in the counter-prevailing direction. Those paths are the West of Hatwai (west to east) and the Montana Intertie (west to east). Because BPA’s actual practices were different from what was documented, BPA failed to keep its ATCID current, thereby preventing validation for two ATC paths, given the same information. The root cause for this issue is lack of knowledge and information management. Specifically, due to an oversight by a BPA Subject Matter Expert, BPA included an incorrect statement in its ATCID regarding the method used to calculate TTC in the direction counter to prevailing flows for two of its ATC paths. This issue began from October 17, 2014, when BPA’s ATCID was placed into effect with the incorrect information, and ended December 5, 2014 when mitigation was complete. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BPA failed to include information in its ATCID describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC calculations can be validated for two of its ATC paths, which could potentially result in a customer's inability to validate the results of BPA's ATC calculations. The inability to validate BPA’s ATC might impact a customer's ability to most economically purchase and dispatch power. However, As a compensating measure, the two ATC Paths in question do not have reliability based concerns in the non-prevailing direction. As such, the likelihood of a customer needing to validate ATC on these two Paths in the non-prevailing direction is extremely low. No harm is known to have occured. In consideration of BPA’s compliance history, WECC notes that BPA does not have previous violations of this Standard and requirement. | To mitigate this issue, BPA: 1) updated its ATCID to have accurate language that reflects current practice.
2015-05-28 | Western Electricity Coordinating Council (WECC) | City of Riverside Public Utilities (CYRS) | NCR05093 | WECC2014014202 | PRC-007-0 | R1 | On August 8, 2014, CYRS submitted a Self Report stating that, as a Distribution Provider, it had an issue with PRC-007-0 R1. CYRS reported that since calendar year 2010, CYRS had not armed sufficient load to be restored as required by the WECC UFLS program. Specifically, during an internal compliance review, CYRS identified two discrepancies in its UFLS program from the WECC UFLS Program requirements. First, for an approximately one-year period from June 2010 through May 2011, CYRS did not arm sufficient load at the initial frequency set point of 59.1/59.5 Hz to comply with the WECC UFLS Program and the Southern Island Load-Tripping Plan (SILTP). Second, for the period of June 2010 through June 2014, CYRS did not provide enough frequency overshoot to meet the requirements in the WECC UFLS Program. The root cause of CYRS’s compliance exception is a lack of compliance understanding and compliance processes to develop and implement a UFLS program consistent with WECC’s UFLS program requirements. The compliance exception start date was May 31, 2010, when CYRS did not arm sufficient load to comply with the WECC UFLS Program and the SILTP. The compliance exception end date was October 1, 2013; the date PRC-007 was no longer in effect. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). In this instance, CYRS failed to ensure that its UFLS program was consistent with the WECC UFLS program requirements. In 2010, CYRS would not have shed sufficient load as required by the WECC program by 1.6MW in the first frequency band. Additionally, for each year from 2010 through 2013, the entity would not have restored sufficient load in case of a frequency overshoot, by as much as 2MW. This compliance exception posed minimal risk to the BPS, because not tripping sufficient load is that the frequency may not be restored to the level expected under normal implementation of the WECC UFLS plan, leading to further load shedding. Likewise, in the case of not restoring load when expected, the BES frequency may overshoot the allowable tolerance, causing more load to be restored earlier than anticipated. However, CYRS represents only a fraction of the shared load shedding responsibilities, and CYRS would have theoretically shed load according to the WECC UFLS in the lower frequency bands. CYRS implemented detective controls by conducting an annual review and revision of its UFLS program, as required by the standard. No harm is known to have occured. In consideration of CYRS’s compliance history, WECC notes that CYRS does not have previous violations of this Standard and requirement. | To mitigate this issue, CYRS: 1) implemented the 2011/2012 UFLS program changes which corrected the amount of load to be shed at the initial frequency set point, and eliminated the 1.6 MW deficiency; 2) determined that its UFLS program was configured and its relays armed to supply at least the required quantities of automated load shed at the initial frequency set points. 3) on approximately May 2014, Riverside took prompt corrective action by modifying the necessary relay settings in the field. The setting changes were completed on June 29, 2014. Riverside's 2014 SILTP report reflects relay settings that are also fully compliant with the WECC UFLS Program.
2015-05-28 | Western Electricity Coordinating Council (WECC) | City of Tacoma, Department of Public Utilities, Light Division (TPWR) | NCR05097 | WECC2015014859 | PER-003-1 | R3 | On January 12, 2015, TPWR submitted a Self-Certification stating that, as a Balancing Authority, it was in possible non-compliance with PER-003-1 R3. A WECC SME reviewed the Self-Certification and conducted interviews with TPWR’s compliance staff, and determined that one of TPWR’s Real Time Energy Traders (RTET) did not timely pay the renewal fees for his NERC Balancing and Interchange Operator certificate. According to the SME, the payment was due on August 31, 2014 and was renewed on September 12, 2014. Between the date of expiration and the date the expiration was discovered, the RTET worked two shifts, performing balancing and interchange functions. The RTET was current on all necessary training to renew the certificate, and was qualified to sit at the trading desk. The employee’s NERC Certified System Operator Certificate is in effect from August 31, 2011 until August 31, 2017. The root cause of this compliance exception was human error, and the lack of an administrative process to ensure that TPWR’s NERC operator certificates are renewed on time. The violation start date was September 1, 2014, one day after the renewal payment was due. The violation end date was September 12, 2014 (12 days), the date the RTET paid the renewal for his NERC certificate. | This compliance exception posed minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, a TPWR trader forgot to renew his NERC certificate before it expired. The certificate expired on August 31, 2014 and was renewed on September 12, 2014. TPWR’s System Operators are not permitted to perform reliability-related tasks without a valid NERC Certificate and without direct supervision. TPWR implemented preventative controls. Specifically, TPWR follows industry procedure for certificate reminders of renewal. NERC tracks renewal dates and sends emails to the individual traders. The individual traders are responsible to log into NERC's system and pay the fees. The RTET training coordinator tracks renewal dates, associated requirements, and provides a reminder for each trader to pay the fee for their certificate. TPWR implemented compensating controls by ensuring the RTET was current on all necessary training and satisfied all his NERC CE requirements, meaning he was qualified to sit at the trading desk between September 1, 2014 and September 12, 2014. Also, the NERC Certified System Operator Certificate is in effect from August 31, 2011 until August 31, 2017. No harm is known to have occured. In consideration of TPWR’s compliance history, WECC notes that TPWR does not have previous violations of this Standard and requirement, and has provided documentation of its internal compliance program. | To mitigate this issue, TPWR: 1) entered automatic reminders into the Outlook calendars of the training coordinator and RTET Supervisor; 2) posted physical copies of NERC Certificate numbers and expiration dates at the training coordinator work station, the RTET Supervisor work station, and the RTET desk; and 3) completed work towards incorporating NERC Certification Renewal into the 2015 RTET annual training plan.
2015-04-30 | Florida Reliability Coordinating Council (FRCC) | Florida Municipal Power Agency (FMPA) | NCR00022 | FRCC2015014639 | FAC-008-3 | R6 | On February 6, 2015, FMPA Self-Reported that, as a Generator Owner it had an issue of FAC-008-3 R6. A new auxiliary Current Transformer was installed at Cane Island Unit 1, due to a breaker replacement project at the Cane Island substation, on October 21, 2010. Ownership structure changed at the Cane Island plant site, effective on February 14, 2013, causing the new current transformer to be the responsibility of FMPA, and under FMPA's Facility Ratings Program. FMPA became aware of the new current transformer in January 2014 and updated the inventory used in its Protection System Maintenance Program accordingly, but failed to update the FMPA Facility Ratings in accordance with its Facility Rating methodology until January 28, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was greatly limited due to the fact that the new current transformer is not the limiting element of the Cane Island Unit 1 Facility. The Facility is limited by the generator step-up transformer which is rated at 1,916 Amps, while the new current transformer is rated at 3,000 Amps. Cane Island Unit 1 is a 40 MW reserve/peaking unit with an annual capacity factor typically less than 10%. In the event one of the auxiliary current transformers sustained damage due to overloading, the worst case impact would be loss of the 40 MW output of the unit. Planning studies have shown that a single contingency loss of even the largest unit at Cane Island (300 MW) would not cause a risk to the BPS. FMPA provided FRCC with its 2014 Ten-Year Transmission Plan of two transient stability simulations involving the loss of Cane Island Unit 4 (300 MW) with faults on the system, both simulations of which show no risk to BPS reliability. The loss of Cane Island Unit 1 (40 MW) due to an auxiliary current transformer damaged from loading above its continuous rating, which does not involve a fault on the system, is a much less severe scenario than described above and would also have no risk. No harm is known to have occurred. | To mitigate this noncompliance, FMPA: 1. made some organizational changes after transitioning to the registered Generator Owner for the Cane Island units and since the new current transformer was installed. In early 2014, FMPA hired a new Transmission Planning Manager and has been migrating certain oversight responsibilities over to him, Facility Ratings being one of those responsibilities. 2. Over the last year, the new Transmission Planning Manager has been holding routine conference calls with FMPA's Generation Fleet O&M department, plant site personnel, and agents to discuss any changes taking place and to ensure that appropriate documentation is updated. Additionally, FMPA held Subject Matter Expert training on February 9, 2015 to go over change management and notification procedures with appropriate personnel.
2015-04-30 | Midwest Reliability Organization (MRO) | Iberdrola Renewables (IR) | NCR10259 | MRO2015014771 | PRC-005-1b | R2 | During a Compliance Audit conducted from October 24, 2014, MRO determined that Iberdrola Renewables (IR), as a GO, had an issue of PRC-005-1 R2. IR did not have evidence that it conducted certain of the current transformer (CT) maintenance and testing work that should have been performed according to its maintenance program. IR provided evidence that it conducted the required ratio tests and burden tests but could not produce any evidence of the other tests required by its maintenance program including: saturation, insulation, and polarity tests. IR's maintenance program required electrical tests that were appropriate for commissioning, but that were more extensive than necessary for periodic maintenance and testing. This issue began on August 1, 2013 (when IR’s oldest facility, Elm Creek, reached its first five-year maintenance interval) and ended on February 28, 2015 (completed mitigating activities). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. IR implements continuous monitoring of the values measured by protection system instrument transformers with various alarms enabled that would notify operators of any problems. They also implement a heartbeat monitoring scheme for the alarming paths. MRO staff reviewed evidence of continuous monitoring implementation. The extensive electrical tests that IR has included in its program are appropriate for commissioning but there is no technical justification for repeating these tests on a periodic basis. Because any unacceptable error or failure of IR’s CTs would be detected promptly through continuous monitoring, the risk to the BES posed by the lapse of maintenance records is minimal. Furthermore, PRC-005-2 (effective on April 1, 2015) does not require that any periodic maintenance of Voltage and Current Sensing devices be performed if they are continuously monitored in accordance with the standard. This is IR’s first issue with PRC-005. No harm is known to have occurred. | To mitigate this issue, IR will revise its Electrical Maintenance Program Scope of Work, modifying the instrument transformer maintenance tasks such that they will include signal verification on a twelve-year interval in accordance with PRC-005-2. Mitigating activities were completed by February 28, 2015.
2015-04-30 | Midwest Reliability Organization (MRO) | Iberdrola Renewables (IR) | NCR10259 | MRO2015014772 | FAC-009-1 | R1 | During a Compliance Audit conducted from October 24, 2014, MRO determined that Iberdrola Renewables (IR), as a GO, had an issue of FAC-009-1 R1. IR incorrectly documented the Rating of the New Harvest Facility. One low voltage wire bus conductor was documented incorrectly in IR's ratings database. The generator step-up transformer rating had been documented as 115 MVA, but the nameplate rating was 100 MVA. This issue began on December 30, 2011 (when New Harvest was commissioned) and ended on August 29, 2014 (when IR completed mitigating activities). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Out of IR’s eight facilities in the MRO footprint, only New Harvest’s overall facility rating was affected. MRO reviewed three years of historical loading data provided by IR in order to determine whether the New Harvest wind farm had been operated above the nameplate rating of its GSU. The highest output of the plant during the three year period was 100.9 MVA and was sustained for less than one minute. The rating was also exceeded to lesser degrees in other instances within the three-year period, however, the average loading of the facility over 30 minutes was always less than 100 MVA. New Harvest is an intermittent wind generation resource, with an aggregate capability of 100MW which is delivered through a single point of interconnection at a substation which is not owned by IR. As such, the impact to the BES due to an overloading of the GSU would be minimal and the potential risk to the BES posed by this issue is also minimal. For radial generation that is not a blackstart unit and is not associated with an IROL or SPS, the only risks posed by Facility Rating errors are the possible impacts to the BES from an unplanned outage of the generation. The primary concern related to the loss of a large generating facility is the impact on system frequency. Based on historical data, an outage of 100 MW of generation (the size of New Harvest) in the Eastern Interconnection would cause a temporary system frequency decline of less than 0.02 Hz, given the worst-case system conditions. Frequency excursions of this small magnitude occur regularly and the system is designed to tolerate them. Furthermore, system operators do not rely on non-dispatchable energy resources such as wind generation to the same degree that they rely on dispatchable generation. This is IR’s first issue with FAC-009. No harm is known to have occurred. | To mitigate this issue, IR: 1) performed a review of all of its equipment and facility rating documentation; 2) updated the documentation with missing or corrected ratings; and 3) provided the updated ratings to the GOP for its facilities. Mitigating activities were completed by August 29, 2014.
2015-04-30 | Midwest Reliability Organization (MRO) | Minnesota Power (Allete, Inc.) | NCR00674 | MRO2015014554 | VAR-002-2b | R3 | On January 9, 2015, Minnesota Power (MP), submitted a Self-Report stating that as a GOP, it had an issue of VAR-002-2b R3. MP’s Generator Operators failed to notify MP’s Transmission Operators of a change in the AVR (Automatic Voltage Regulator) status associated with one of MP’s generating units. On March 21, 2014 at 9:23AM, MP’s Laskin Unit 2 tripped due to a fault. The unit was placed back in service at 10:26 AM, but the AVR did not come back online. At 8:05 PM, the Generator Operators re-enabled the AVR and notified the Transmission Operator. Not all of the entity’s personnel were aware of the requirement to report outages of the AVR to the entity’s System Operator. The issue began on March 31, 2014 and ended on March 31, 2015. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk to the BPS of this finding is reduced as a result of: The generator associated with this issue is only 64.5 MW, incapable of causing a serious risk to the BPS, and interconnects to the BPS at 115kV. The generator is not associated with an IROL, and is not blackstart capable. The duration of the issue was less than 10 hours. This is MP’s first instance of non-compliance with VAR-002 No harm is known to have occurred. | To mitigate this issue, MP: 1) The entity verified, prior to January 9, 2015, that this was an isolated incident and that all other unplanned AVR outages have been reported to the entity’s System Operators. 2) Generator Operators communicated the AVR status to the entity’s Transmission Operators on March 21, 2014. 3) On January 7, 2015, clarified its “Guideline for Voltage and Reactive Power Control” to emphasize that a change in status of an AVR must be reported to Transmission Operators within 30 minutes. 4) On March 31, 2015, MP trained its personnel to ensure that all are aware of the need to report changes in AVR status.
2015-04-30 | Midwest Reliability Organization (MRO) | Western Area Power Administration - Upper Great Plains East (WAPA) | NCR01036 | MRO2013012705 | EOP-008-1 | R6 | On July 1, 2013, Western Area Power Administration (WAPA), submitted a Self-Report stating that as a BA and TOP, it had an issue of EOP-008-1 R6. WAPA did not have sufficient communications pathways available to comply with EOP-008-1 R6 at the time the Standard Requirement became mandatory and enforceable. As of July 1, 2013, the enforcement date for EOP‐008‐1, WAPA’s backup control center functionality was dependent on the primary control center’s functionality. The issue began on July 1, 2013 and will end on March 31, 2016. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The data points in question were considered to be non-critical by the WAUE and included such information as customer substations and load data, tapped substation data, and silent switch data. While this information is good for the RC to have for reliability purposes, these data points were not required to support WAPA’s real time monitoring and assessment of their respective balancing areas or their TOP functionality. WAUE’s Control Center functionality as a TOP and its ability to monitor and control facilities within its TOP footprint was not compromised during the 2013 EOP-008-1 drill. A number of the missing data points are also monitored by neighboring TOPs. In preparation for the drill, the RCs were contacted concerning the issue and how WAPA would monitor or control these data points during the drill. The risk posed to the Bulk Electric System by this issue was minimal because the problematic data points were of low importance for TOP and RC reliability purposes. Furthermore, WAPA was capable of implementing appropriate data failure procedures upon deployment to the BUCC. This is WAPA’s first instance of noncompliance with EOP-008-1 R6. No harm is known to have occurred. | To mitigate this issue, WAPA: 1) Established access to all but 84 of the approximately 700 missing data points at WAO by January 6, 2015. 2) WAPA-UGPR will establish the capability to independently send all of the data points to the Reliability Coordinators from the Watertown Alternate Control Center in order to support real-time monitoring and assessment of the Reliability Coordinator Areas. Mitigating activities will be completed by March 1, 2016
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | MEG Generating Company, LLC (MEG) | NCR00838 | RFC2014014488 | MOD-010-0 | R2 | On December 2, 2014, MEG submitted a Self-Report stating that, as a GO, it had an issue with MOD-010-0 R2. On March 21, 2014, MEG received a MOD-010 data request from ReliabilityFirst. MEG mistakenly believed that the data request only required a response if the requested data had changed from 2013. Because the requested information had not changed, MEG did not submit responses. However, MEG subsequently conducted a re-examination of the data request after some staffing turnover and realized that responses were required. MEG then promptly submitted the requested data, albeit beyond the deadline established by the applicable Reliability Standards. The root cause of this noncompliance was human error. The responsible individuals misunderstood what the data request required of them. The duration of this noncompliance is from April 25, 2014, the deadline for MEG to respond to the data request, to August 28, 2014, the date on which MEG submitted the requested information to ReliabilityFirst. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the Transmission Owners already possessed the information requested from MEG and had already submitted it to ReliabilityFirst. Consequently, the late response from MEG was merely informative that nothing had changed. Second, the requested information had not changed from 2013, so it did not affect the actual BES modeling. ReliabilityFirst considered MEG's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MEG: 1) submitted the requested data to ReliabilityFirst in accordance with the data request; and 2) committed to have at least two staff members review each data request from ReliabilityFirst.
2015-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | MEG Generating Company, LLC (MEG) | NCR00838 | RFC2014014489 | MOD-012-0 | R2 | On December 2, 2014, MEG submitted a Self-Report stating that, as a GO, it had an issue with MOD-012-0 R2. On June 13, 2014, MEG received a MOD-012 data request from ReliabilityFirst. MEG mistakenly believed that the data request only required a response if the requested data had changed from 2013. Because the requested information had not changed, MEG did not submit responses. However, MEG subsequently conducted a re-examination of the data request after some staffing turnover and realized that responses were required. MEG then promptly submitted the requested data, albeit beyond the deadline established by the applicable Reliability Standards. The root cause of this noncompliance was human error. The responsible individuals misunderstood what the data request required of them. The duration of this noncompliance is from July 25, 2014, the deadline for MEG to respond to the data request, to August 28, 2014, the date on which MEG submitted the requested information to ReliabilityFirst. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the Transmission Owners already possessed the information requested from MEG and had already submitted it to ReliabilityFirst. Consequently, the late response from MEG was merely informative that nothing had changed. Second, the requested information had not changed from 2013, so it did not affect the actual BES modeling. ReliabilityFirst considered MEG's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, MEG: 1) submitted the requested data to ReliabilityFirst in accordance with the data request; and 2) committed to have at least two staff members review each data request from ReliabilityFirst.
2015-04-30 | SERC Reliability Corporation (SERC) | Virginia Electric and Power Company – Fossil and Hydro (GO, GOP) (VEP-FH) | NCR09028 | SERC2014014341 | VAR-002-2b | R1 | On September 17, 2014, VEP-FH submitted a Self-Report stating that, as a Generator Operator, it had an issue with VAR-002-2b R3. VEP-FH failed to notify the Transmission Operator (TOP) that it was operating a generator in a mode other than automatic voltage control mode. SERC later determined that the issue was more appropriately addressed under VAR-002-2b R1. On June 26, 2014 at 10:32 a.m., a VEP-FH station control room operator requested and received permission from the VEP Market Operations Center (MOC) to briefly place the automatic voltage regulator (AVR) into manual mode to test the AVR alarm. Accordingly, the VEP-FH station control room operator switched the AVR status from automatic to manual, and then back to automatic, in less than 40 seconds. Later, VEP-FH conducted an internal review of its electronic notification tickets for the associated AVR alarm testing schedule and determined that the MOC had not notified the TOP of the AVR status change from automatic to manual and back to automatic. The MOC failed to notify the TOP by voice notification or electronic notification ticket. Prior to this issue, the TOP had verbally indicated that an electronic notification ticket was unnecessary for this type of alarm testing, in an effort to eliminate possible nuisance notifications. Based on this discussion with the TOP, the MOC personnel decided not to notify the TOP of the change in AVR status for the alarm test. After the instant issue occurred, VEP-FH requested and received written guidance from the TOP regarding notification of AVR status change during alarm tests. The TOP’s written guidance was that a phone call to the TOP Generation Dispatch is sufficient for the AVR alarm test and that an electronic notification ticket is not required. SERC determined that VEP-FH had an issue with VAR-002-2b R1 because VEP-FH failed to notify that TOP that it was operating a generator in a mode other than automatic voltage control mode. This issue lasted from June 26, 2014 at 10:32 a.m., when VEP-FH switched the AVR from automatic to manual without prior notification to the TOP, through approximately 40 seconds later, when VEP-FH switched the AVR back to automatic. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. VEP-FH’s failure to notify the TOP that it was operating a generator with the AVR in manual mode increased the risk that the TOP would assume that the generator would respond as if the AVR was in automatic voltage control mode. However, in this instance, the AVR was in manual for less than 40 seconds on a single unit with 57 MWs of generation. VEP-FH maintained the voltage schedule while the AVR was in manual control. No harm is known to have occurred. SERC considered VEP-FH compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, VEP-FH: 1) provided a notification to the MOC operations staff on July 2, 2014. Anytime a station notifies the MOC of a status change for an AVR or Power System Stabilizer (PSS), to include testing or short term switching from automatic to manual, the MOC must immediately notify PJM Interconnection, LLC prior to the change. In addition, the MOC must create an eDART ticket.; and 2) provided the following guidance to the power station operating management teams and to power station compliance personnel on July 2, 2014: (a) AVR and/or PSS maintenance and/or testing should be scheduled as far in advance as possible; (b) maintenance and/or testing includes, but is not limited to, changing the voltage regulator status from automatic to manual control mode and changing the PSS operational modes; (c) changing the AVR and/or PSS status to perform testing must also be scheduled in advance; (d) all AVR and/or PSS maintenance and/or testing shall be scheduled through the manager of power generation operations support or his or her designee; and (e) this scheduling must be completed before the maintenance and testing is performed.
2015-04-30 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014451 | MOD-030-2 | R2; R2.5.1 | On August 5, 2014, SERC sent DEP an initial notice of a Compliance Audit scheduled for November 3, 2014 through November 21, 2014. On November 14, 2014, DEP submitted a Self-Report stating that, as a Transmission Operator (TOP), it had an issue with MOD-030-2 R2.5.1. Following notification of a modification that affected the Total Flowgate Capability (TFC) of a flowgate used in the Available Flowgate Capacity (AFC) process, DEP did not update the TFC within seven days. On October 28, 2014, while locating information to respond to a request from the SERC audit team, DEP determined that a Facility Rating change occurred on May 1, 2014, and that DEP did not incorporate the change in the AFC/Available Transmission Capacity (ATC) database within seven calendar days. DEP’s Transmission Planning Department maintains a Transmission Facility Ratings database and an AFC/ATC database. The data sets in both databases include normal and emergency ratings. DEP includes the emergency ratings as alternate ratings that are used for contingency planning only. DEP maintains its Transmission Facility Ratings database within a SharePoint site. DEP flags changes to the Transmission Facility Ratings database with a comment in the “Updates” field, to alert stakeholders to update the AFC/ATC database. The SharePoint workflow sends an automated email notice to engineers in the System Operations Department who make the required changes to the AFC/ATC database. Recipients of the email refer to the “Updates” section to determine the specifics of the Facility Rating changes. DEP’s 2014 transmission projects included a project where a neighboring Transmission Owner (TO) planned to re-conductor a portion of the Person-Halifax 230 kV line. Prior to the line project, DEP engineers had determined that the project would increase the emergency ratings of the facility to 712/756 MVA (summer/winter) but would not change the normal ratings. During the line project, DEP changed the Transmission Facility Ratings database to include the predicted increase. However, DEP did not flag the changes to be made in the AFC/ATC database until the TO completed the project. On May 1, 2014, DEP and its neighboring TO returned the Person-Halifax 230 kV line to service and DEP put the revised emergency ratings into effect. However, DEP’s engineers had recalculated the emergency ratings during the line project, and DEP updated the Transmission Facility Ratings database to reflect the adjusted emergency ratings of 713/765 MVA (summer/winter). The adjusted emergency ratings reflected an increase of one MVA and nine MVA respectively from what DEP predicted before the project. SharePoint distributed the automated email notification. However, due to human error, when DEP entered the change into the Transmission Facility Ratings database, DEP did not modify the “Updates” section to include any information about the emergency rating adjustment. Specifically, DEP did not include a description in the “Updates” section explaining that the Person-Halifax 230 kV line rating was modified. Instead, DEP included this description in a separate “Version History” field in the database. Because DEP documented the change in the wrong field, the change went unnoticed by the email recipients. Therefore, the email recipients did not make the change to the AFC/ATC database. On July 18, 2014, while performing an AFC/ATC database update, DEP changed the Person-Halifax 230 kV emergency rating to 713/765 MVA, consistent with the Transmission Facility Ratings database. At that time, DEP did not recognize this delay in performing the update as an issue. SERC determined that DEP had an issue with MOD-030-2 R2 because DEP failed to update the TFC within seven calendar days of DEP being notified of a change in a rating by the TO that would affect the TFC of a flowgate used in the AFC process. This issue lasted from May 8, 2014, when DEP failed to update the TFC within seven calendar days following the notification, through July 18, 2014, when DEP updated the database. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because of the failure to update the AFC/ATC database, DEP transmission planning could have achieved incorrect results when determining the margin of ATC remaining. However, the delay affected only an emergency rating, which DEP would use for contingency planning purposes under a specific contingency. The modification that DEP failed to make to the AFC/ATC database was a less than 2% adjustment of the planned emergency rating and the change would have increased the emergency rating. DEP operations used a more conservative rating because DEP had not entered the increased rating into the database. No specific contingency occurred. No harm is known to have occurred. SERC considered DEP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DEP: 1) updated the rating of the Person-Halifax 230 kV line to 713/765 MVA in its AFC/ATC process; and 2) updated the process control document to clarify the process surrounding Facility Rating database changes, revision history, and implementation. SERC has verified the completion of all mitigation activity.
2015-04-30 | Western Electricity Coordinating Council (WECC) | Tri-State Generation and Transmission Association, Inc. - Reliability (TSGT) | NCR10030 | WECC2015014619 | PRC-004-2.1a | R3 | On February 9, 2015 (during the Self-Certification period for 2014), TSGT submitted a Self-Report stating that, as a Generator Owner, it was in possible noncompliance with PRC-004-2.1a R3. WECC reviewed the Self-Report and conducted interviews with TSGT’s compliance staff, and determined that TSGT was in noncompliance with the Standard, because it had not provided documentation of its Misoperations Analyses and Corrective Action Plans according to WECC’s procedures. On April 21, 2014, a Misoperation occurred on the Generator Protection System for Unit 2 of TSGT’s Craig generating plant. Consistent with TSGT’s procedures, the Line of Business group reported the Craig plant Misoperation to the Reliability Compliance group on May 21, 2014. While preparing its third quarter Misoperation report in November 2014, the Reliability Compliance group discovered that it had failed to include the Craig plant Misoperation report in the second quarter submission to WECC. The Line of Business group had submitted the Craig plant Misoperation report early in the quarter, before the deadline, but the Reliability Compliance group missed the email when the other Misoperation reports came in later for that quarter. TSGT contacted WECC in December 2014, in order to remedy the situation. WECC instructed TSGT that the 2nd quarter Misoperation report for 2014 would be opened up for TSGT to amend the additional Misoperation report, and on February 5, 2015, TSGT corrected that report. The root cause for this instance of non-compliance is TSGT’s lack of a strong compliance process for coordination between its Line of Business and Reliability Compliance groups. The compliance exception started on September 1, 2014, the date TSGT was supposed to provide documentation of its Misoperations, and was remediated on February 5, 2015, when TSGT corrected the report. | This issue posed a minimal risk, and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, TSGT failed to timely provide a Misoperation report and its respective corrective action plan to WECC. TSGT appropriately analyzed the Misoperation and implemented its corrective action plan. No harm is known to have occurred. WECC considered TSGT's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TSGT: 1) implemented preventative controls requiring email reminders to the business units in order to trigger timely submissions of Misoperation reports; and 2) TSGT implemented corrective controls, because TSGT contacted WECC in late December in order to determine how to best remedy the missed Misoperation report.
2015-04-30 | Western Electricity Coordinating Council (WECC) | Arlington Wind Power Project, LLC (AWPP) | NCR10279 | WECC2014014246 | PRC-005-1 | R2 | On August 18, 2014, AWPP submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1 R2. In the Self-Report, AWPP reported that it failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1 R2. Specifically, there were two instances of noncompliance reported by AWPP. In the first instance, AWPP’s Protection System maintenance and testing program in effect during December 2010 required that visual substation inspections were to be conducted monthly. AWPP failed to conduct the monthly inspection for December 2010 as required in its maintenance and testing program. In the second instance, AWPP’s Protection System maintenance and testing program in effect during June 2014 required that visual substation inspections were to be conducted monthly. AWPP conducted the monthly inspection for June 2014 nine days outside of the interval described in its maintenance and testing program. As a result, AWPP reported that it had a possible issue with PRC-005-1 R2. An audit was conducted at AWPP concluding on November 19, 2014. This issue was reviewed by the auditors. The auditors found that AWPP failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program. The auditors also confirmed that the mitigating activities were completed by AWPP. The auditors forwarded their findings to a WECC Subject Matter Expert (SME) for review. An SME then reviewed the issue. As a result of the examination, the SME determined that AWPP had an issue with PRC-005-1 R2. Specifically, the SME confirmed that AWPP failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report, Audit Team, and SME findings. Based on this review, Enforcement determined that AWPP had an issue with PRC-005-1 R2. Specifically, Enforcement determined that AWPP failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1 R2. Enforcement determined that the issue began on January 1, 2011, the day that the monthly requirement to perform the visual substation inspection for December 2010 expired. Enforcement also notes that the issues ended on July 7, 2014, the date that the entity adopted version 2 of the standard and that AWPP performed the inspection on July 9, 2014. Enforcement determined that the root cause of the first instance was a lack of implementing adequate systems and that the root cause of the second instance was human error in that the maintenance was simply performed late. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AWPP failed to provide evidence that Protection System devices were maintained and tested within the defined intervals of its Protection System maintenance and testing program. Specifically, the monthly visual substation inspection for December 2010 was not performed and the June 2014 monthly visual substation inspection was conducted nine days late. If devices are not tested per the program defined by the entity, the devices cannot be certified to operate as planned to interrupt disturbances that may damage the transmission system or generating units. AWPP is a 102.9 MW facility, limiting the effect that it has on the BPS. Additionally, in the first instance, AWPP only missed the inspection for one month and, in the second instance, AWPP conducted the testing only nine days after the interval described in its maintenance and testing program. All other required monthly substation inspections were conducted and documented at the correct intervals, limiting the probability of any risk to the BPS. AWPP also developed and implemented a plan to transition to PRC-005 version 2 on July 7, 2014, only seven days after the missed maintenance occurred. In both instances, the intervals of the maintenance performed by AWPP would have been compliant under the new PRC-005 version 2 maintenance and testing plan. No harm is known to have occurred. For these reasons, WECC determined this noncompliance posed minimal risk to the reliability of the BPS. WECC considered AWPP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, AWPP: 1) implemented a new work management system that creates work orders for performing maintenance activities in accordance with the AWPP maintenance and testing procedure; 2) reviewed the maintenance and testing procedures with operations personnel; and 3) adopted version 2 of PRC-005 for the battery permitting up to four months for the battery inspection to be completed. WECC has verified the completion of all mitigation activity.
2015-04-30 | Western Electricity Coordinating Council (WECC) | Sagebrush Power Partners LLC (SAGB) | NCR11123 | WECC2014014247 | PRC-005-1 | R2 | On August 18, 2014, SAGB submitted a Self-Report stating that, as a Generator Owner, it had an issue of PRC-005-1 R2. In the Self-Report, SAGB reported that it failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1 R2. Specifically, SAGB reported two instances of noncompliance. In the first instance, SAGB’s Protection System maintenance and testing program in effect during the period from November 2010 through April 2011 required that visual substation inspections were to be conducted monthly. SAGB failed to conduct the monthly inspections for November 2010, December 2010, and April 2011 as required in its maintenance and testing program. In the second instance, SAGB’s Protection System maintenance and testing program in effect during November 2013 required that visual substation inspections were to be conducted monthly. SAGB conducted the monthly inspection for November 2013 nine days outside of the interval described in its maintenance and testing program. This was due to a planned outage occurring during this period to perform annual maintenance activities. As a result, SAGB reported that it had a possible issue with PRC-005-1 R2. An audit was conducted at SAGB concluding on November 20, 2014. This issue was reviewed by the auditors. The auditors found that SAGB failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program. The auditors also confirmed that the mitigating activities were completed by SAGB. The auditors forwarded their findings to a WECC Subject Matter Expert (SME) for review. An SME then reviewed the issue. As a result of the examination, the SME determined that SAGB had a possible issue with PRC-005-1 R2. Specifically, the SME confirmed that SAGB failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report, Audit Team, and SME findings. Based on this review, Enforcement determined that SAGB had an issue with PRC-005-1 R2. Specifically, Enforcement determined that SAGB failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1 R2. Enforcement determined that the issues began on December 1, 2010, the day that the monthly requirement to perform the visual substation inspection for November 2010 expired. Enforcement also notes that the issue ended on December 9, 2013, the date that the late visual substation inspections were completed. Enforcement determined that the root cause of the first instance was a lack of implementing adequate systems in place and that the root cause of the second instance was a lack of adequate planning for the inspection missed due to the outage. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SAGB failed to provide evidence that Protection System devices were maintained and tested within the defined intervals of its Protection System maintenance and testing program. Specifically, the monthly visual substation inspections for November 2010, December 2010, and April 2011 were not performed and the November 2013 monthly visual substation inspection was conducted nine days late. If devices are not tested per the program defined by the entity, the devices cannot be certified to operate as planned to interrupt disturbances that may damage the transmission system or generating units. SAGB is a 100MW wind power facility, limiting the effect that it has on the BPS. Additionally, in the first instance, SAGB missed the inspection for three months and, in the second instance, SAGB conducted the testing only nine days after the interval described in its maintenance and testing program. All other required monthly substation inspections were conducted and documented at the correct intervals, limiting the probability of any risk to the BPS. No harm is known to have occurred. For these reasons, WECC determined this noncompliance posed minimal risk to the reliability of the BPS. WECC considered SAGB compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SAGB: 1) implemented a new work management system that creates work orders for performing maintenance activities in accordance with the SAGB maintenance and testing procedure; and 2) reviewed the maintenance and testing procedures with operations personnel. WECC has verified the completion of all mitigation activity.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | Covanta Niagara LP | NCR10009 | NPCC2015014745 | FAC-008-3 | R2 | During a Compliance Audit conducted from July 25, 2014 through December 16, 2014, NPCC determined that Covanta Niagara LP, as a GO, had an issue of FAC-008-3 R2. Covanta Niagara failed to include the ratings of their in-line breakers, 701A and 701B (located just before the final Niagara owned equipment, disconnects 711 and 712), as part of their equipment ratings for each generator facility. The root cause was Covanta Niagara's misconception of who owned the equipment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The audit team reviewed the corrected rating summaries that included the missing in-line breakers 701A and 701B and noted that the addition of the ratings for these breakers do not change the overall conclusions of Niagara’s analysis that show the most restrictive and second most restrictive equipment at the Covanta Niagara facility. NPCC considered Covanta Niagara's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Covanta Niagara 1) provided ratings of in-line breakers 701A and 701B and added the ratings to their rating summary sheets. NPCC has verified the completion of all mitigation activity.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | Orange and Rockland Utilities, Inc. (O&R) | NCR07186 | NPCC2015014729 | PRC-002-NPCC-01 | R14 | On October 30, 2014 O&R submitted a Self-Report stating that, as a TO, it had issues related to standard PRC-002-NPCC-01 [Requirement R14]. Specifically, a maintenance and testing program was not established until October 3, 2014 for stand-alone Disturbance Monitoring Equipment (DME). Per PRC-018-1 (the companion standard to PRC-002-NPCC-01 that specifies the phase-in schedule for DMEs), an entity is to be 100% compliant with maintenance requirements for DMEs six months after the required installation date for the DME equipment. Therefore, the duration of the issue was from April 20, 2014 through October 2, 2014. The root cause of the issues was a less than adequate internal control process to ensure compliance with the above requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This is due to the fact that stand-alone DMEs are not utilized for the actual operation of the system. Rather, these devices are utilized to monitor key electrical quantities (e.g. currents, voltages, frequencies), following system disturbances. If the DMEs malfunction, then the data they generate simply cannot be used to analyze system events, and no operational issue will be experienced as a results of this. However, in this particular case, a maintenance program was put in place on 10/03/2014, and actual testing of the DME equipment followed after that date, in accordance with the schedule prescribed in the aforementioned maintenance program. In conclusion, no harm is known to have occurred as a result of the violation. NPCC considered O&R's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, O&R.: 1) has put in place a Maintenance and testing Program for stand-alone Disturbance Monitoring Equipment, effective10/03/2014; and 2) has periodically performed required verification tests for DME equipment, in accordance with the schedule prescribed in their maintenance program. NPCC has verified the completion of all mitigation activity.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | New York Power Authority (NYPA) | NCR07161 | NPCC2015014746 | PRC-001-1 | R3. | On July 1, 2014, NYPA submitted a self-report stating that as a GOP, it had an issue of PRC-001-1 R3. NYPA discovered the issue through the self-logging program. NYPA did not coordinate all of its protection system changes to the New York System Operator (NYISO) as required by the NYISO's System Protection Manual for Special Protection System (SPS) data updates. The manual directs facility equipment owners to prepare and submit SPS descriptions that include the "initiating incident (SPS trigger or triggers)." Each year, the NYISO’s system protection data coordinator emails the SPS data to the facility’s equipment owners for review and revision. In response to those emails, during the initial PRC-001 enforcement date through 2012, NYPA affirmed the Niagara 230 kV Generation Rejection SPS description information that included five initiating incident triggering conditions. However, NYPA had previously determined that there was no operational need for two of the SPS’s initiating triggering conditions and were operationally disabled prior to 2007. The root cause was a documentation issue that stemmed into an oversight in communications between the NYISO and NYPA. The Niagara 230 kV Generation Rejection SPS description information was updated as part of the NYISO’s 2013 annual SPS data update on March 26, 2013. | There was minimal risk to the Bulk Power System (BPS) as a result of the oversight in reporting the removal of two initiating triggering conditions included in Niagara’s 230 kV Generation Rejection SPS (PA-3) description information to the NYISO. If the NYISO Shift Supervisor had requested Niagara’s 230 kV Generation Rejection SPS to be activated with either of the two initiating triggering conditions due to a BPS system condition, NYPA would have informed the NYISO Shift Supervisor that these initiating triggering conditions were not available. At this point, the NYISO Shift Supervisor would take other necessary actions to ensure that the BPS remained in secure state. The Niagara’s 230 kV Generation Rejection SPS (PA-3) was originally installed in the 1960’s to protect for a number of Western New York and Eastern Ontario system contingencies that includes dynamic stability and thermal overload conditions. At the time of installation these initiating conditions were required to reject Niagara generation following the loss of the cross-state 345kv lines to avoid overloading the underlying 115kV and 230kV systems. Since that time, improvements in the BPS have alleviated the majority of the conditions to point where this SPS is rarely activated. In 2004, NYPA conducted studies and determined that two of the initiating triggering conditions were no longer operationally required and were functionally disabled. NPCC considered NYPA's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, NYPA: 1) submitted the updated SPS memo to the NYISO that corrected the initiating triggers for their SPS 2) implemented a new process identifying the responsibilities of the PCE group and the System Planning groups and the reporting of changes and performance to the NYISO. 3) completed a review of all NYPA’s Special Protection Memos, SPS descriptions, initiating conditions and other related information. 4) reviewed the existing process to ensure a full understanding of their responsibilities regarding the coordination and reporting responsibilities of changes in NYPA’s special Protection Systems to the NYISO. 5) revised and reissued their generation and transmission SPS support document and reissued NPCC has verified the completion of all mitigation activity.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | Public Service Company of New Hampshire (PSNH) | NCR07203 | NPCC2015014641 | PRC-005-1.1b | R2; R2.1 | On October 16, 2014, PSNH submitted a self-report stating that as a Transmission Operator, it had an issue of PRC-005-1.1b R2. During a review of their maintenance work order system, it was discovered that four DC control circuits missed their 4-year testing frequency, which were required during the 2013 calendar year. The root cause was due to PSNH failing to follow procedure in updating their maintenance work order system. PSNH did not ensure correct testing frequencies were consistent with their BPS list changes. PSNH reviewed 3600 devices on their system and confirmed that these four DC control circuits were the only devices that missed the required testing cycle. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Two of the DC control circuits are associated to relays that have redundant systems which would have provided fault clearing in the event of disturbances. The potential impact to the transmission system would have been a delayed clearing by remote terminals if the respective redundant system had failed or was out of service for maintenance. The two remaining DC control circuits are associated to breaker failure relays. The primary protection is the breaker operating as designed while breaker failure (stuck breaker) relays are the secondary system. The potential impact to the transmission system would have been delayed clearing by remote terminals to clear the fault. Additionally, there were no issues with reclosing during the period testing was not performed. PSNH operational records indicate that the breakers and reclosing function of these relays did initiate and close properly. NPCC considered PSNH's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, PSNH: 1) performed a review of all the PSNH maintenance database triggers and listings. The review resulted in PSNH including a peer check and caution note within their procedure to ensure changes to the BPS list are also updated correctly in their work order system. 2) tested the four DC control circuits. The tests found no problems. 3) developed and rolled out a lessons learned regarding the need to update the work management system to ensure correct testing frequencies are updated when the BPS list is changed. NPCC has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | American Bituminous Power Partners, LP (ABPP) | NCR00680 | RFC2014014452 | PRC-005-1 | R2 | On October 31, 2014, ABPP submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-005-1 R2. ABPP determined that it did not keep complete evidence of maintenance and testing within defined intervals for its batteries and battery chargers. Specifically, ABPP did not keep complete evidence of maintenance and testing within defined intervals for its batteries and battery chargers at its Grant Town Power Plant. ABPP discovered this missing evidence during an internal assessment of compliance as part of ABPP’s ongoing operation of its internal compliance program. This internal assessment reviewed battery and battery charger maintenance documentation stored in ABPP’s facility maintenance management database. Testing evidence was either missing or incomplete for monthly, quarterly, and annual activities. ABPP’s discovery of the missing and incomplete evidence prompted it to further investigate the issue. As part of this investigation, ABPP conducted interviews with site personnel and hired a third party NERC consultant (ICF International) which led ABPP to the conclusion that its PRC-005 compliance program needed revision and improvement. ABPP determined that the root cause of the issue was that ABPP maintenance personnel did not fully understand the PRC-005 documentation requirements related to maintenance and testing and that site plant procedure, controls, and training related to PRC-005 compliance needed improvement. The duration of this noncompliance is from September 1, 2011, the date ABPP was required to comply with PRC-005-1 R2, to October 21, 2014, the date ABPP completed its Mitigation Plan. During mitigation, ABPP discovered another noncompliance with PRC-005-1 R2. On December 29, 2014, ABPP sent an email to ReliabilityFirst stating that, as a GO, it had found another issue with PRC-005-1 R2. Specifically, ABPP found that prior to ABPP’s November 8-9, 2014 testing of its current transformers (CTs) and potential transformers (PTs), ABPP had not been testing its CTs and PTs and therefore was not keeping evidence of that testing. ABPP, in its capacity as a GO is subject to compliance with PRC-005-1 R2 and ABPP registered as a GO on May 30, 2007. From May 30, 2007 through November 8, 2014, ABPP did not test, and therefore did not keep records of testing, its CTs and PTs. The root cause of this noncompliance was the same as the self-reported issue described above: ABPP maintenance personnel did not understand and were not properly trained on the documentation requirements related to maintenance and testing of CTs and PTs. The duration of this second noncompliance is from September 1, 2011, the date ABPP was required to comply with PRC-005-1 R2, to November 9, 2014, the date ABPP completed its testing of its CTs and PTs with proper documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. ABPP checks its battery systems, batteries, and chargers every day as part of daily inspections. There were no misoperations during the noncompliance period related to battery systems or CTs and PTs. All devices with missing or incomplete testing were subsequently tested and ABPP found no issues with any of the tested devices. Also, ABPP identified no issues with the supporting testing documentation of the battery systems, CTs, and PTs. Additionally, all other components of ABPP’s protection system maintenance and testing program were tested in accordance with defined intervals and with properly maintained evidence to support that testing. Finally, ABPP is an 80 megawatt waste coal power facility that has a minimal impact on the Bulk Electric System. ReliabilityFirst considered ABPP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ABPP: 1) revised the site plant procedure to more clearly define inspection intervals and data recording requirements; 2) retrained applicable site personnel, including management and technicians, on Reliability Standard Requirements and documentation protocols to remind them of the importance of keeping accurate and timely records of testing; 3) installed additional site controls to ensure timely completion of testing through the use of the Microsoft Outlook program that allows the manager to record and assign tasks to subordinates; 4) revised its inspection data sheets to more clearly define inspection protocols to match the recommendations of the Original Equipment Manufacturer; and 5) implemented a six month period of additional data review and evidence sign off by the Plant Manager to ensure technicians are following the correct inspection recording protocol. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE East China, LLC (DTEEC) | NCR08048 | RFC2014014016 | PRC-005-1 | R1 | During a Compliance Audit conducted from May 8, 2014 through May 23, 2014, ReliabilityFirst determined that DTEEC, as a Generator Owner (GO), had an issue of PRC-005-1 R1. DTEEC’s Protection System maintenance and testing program did not include testing and maintenance intervals for DC battery chargers. Although DTEEC’s Protection System maintenance and testing program did not include battery chargers, DTEEC did provide evidence that it had actually been testing the devices. In addition, DTEEC’s DC control circuitry interval of seven years was based on the NERC Protection System Maintenance Technical Reference, which requires partial monitoring to qualify for the less frequent seven-year interval. DTEEC did not meet all the requirements for partial monitoring of DC control circuitry. Although DTEEC met the interval requirements for partially monitoring for notes 1a, 1d, 1e, and 1f, it failed to meet note 1b (monitoring of trip coil continuity and trip voltage by periodic checking of a monitoring light or by an automatic continuity monitoring means such as the trip coil monitor of the microprocessor relay). Because DTEEC did not satisfy all requirements of the NERC Protection System Maintenance Technical Reference, DTEEC did not qualify for the longer, seven-year interval and instead should have used a five-year interval. The duration of this noncompliance is from April 1, 2013, when battery chargers were added to the definition of Protection System and therefore were subject to the Requirements of PRC-005, to May 16, 2014, the date DTEEC remediated this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Although DTEEC’s Protection System maintenance and testing program did not specify maintenance and testing intervals for one device type, DTEEC was actually performing testing on those devices, significantly reducing risk to the BES. In addition, although DTEEC failed to meet one requirement to qualify for the longer, seven-year interval for DC control circuitry testing, it did have monitoring lights of trip coil continuity and trip voltage, but lacked a formal procedure for personnel to monitor them. Furthermore, DTEEC was performing all necessary maintenance and testing on the incorrectly-determined seven-year maintenance and testing interval. ReliabilityFirst considered DTEEC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DTEEC: 1) revised its Protection System maintenance and testing program to incorporate DC battery charger maintenance and testing requirements; and 2) changed the DC control circuitry testing intervals to every five years. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE Electric) | NCR00753 | RFC2014013448 | VAR-002-2b | R3 | On February 21, 2014, DTE Electric submitted a Self-Report to ReliabilityFirst stating that as a Generator Owner (GO) and Generator Operator (GOP), it had an issue with VAR-002-2b R3. The noncompliance occurred at the St. Clair Power Plant on Unit #1. At 1331 EST, the St. Clair Power Plant Unit #1 automatic voltage regulator (AVR) unexpectedly changed from automatic mode to manual mode. Although AVR status change alarming was installed and operational on the Energy Management System (EMS), there was no audible alarming in the control room itself. The alarming was designed to alert the Central System Supervisor and the Merchant Operation Controller in case the operator failed to make the required call after manually changing AVR status, which was the anticipated course of action. The EMS alarm was identified by DTE Electric Merchant Operation personnel at 1402 EST, who then called the St. Clair Power Plant operator to question this change in state. Once notified, the St. Clair Power Plant operator inspected the AVR status and returned the AVR to Auto at 1404 EST. The St. Clair Power Plant Unit #1 AVR was in manual mode for a total of 33 minutes. After the AVR was returned to automatic mode, the plant operator notified the TOP of the change in AVR from automatic mode to manual mode and the subsequent return to automatic voltage control mode. The duration of the issue with VAR-002-2b R3 is less than one day, January 27, 2014, the date DTE Electric failed to notify its Transmission Operator within thirty minutes of a change in status of an automatic voltage regulator. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. DTE Electric was cooperative throughout the enforcement process for this issue, DTE Electric’s mitigation was effective and comprehensive. ReliabilityFirst considered DTE Electric's compliance history and determined there were no relevant instances of noncompliance or ReliabiltyFirst considered DTE Electric's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because ReliabilityFirst determined that the conduct of DTE Electric’s personnel was ideal under circumstances that they could not control, the issue was promptly detected, the mitigation was robust and effective, and its reporting of the issue was timely. | To mitigate this issue, DTE Electric: 1) inspected the St. Clair Power Plant Unit #1 AVR relay contacts; 2) created a corrective action report on AVR signage and unit control room alarms; and 3) installed AVR control room alarming at the St. Clair Power Plant. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Generation and Marketing (FE Generation) | NCR11317 | RFC2013012499 | PRC-001-1 | R3 | On May 31, 2013, FE Generation submitted a Self-Certification to ReliabilityFirst stating that as a Generator Operator (GOP) it had an issue with PRC-001-1 R3. FE Generation reported that, during an internal review, it discovered that it failed to coordinate a change on a single protective relay with its Transmission Operator (TOP) and Host Balancing Authority. Specifically, FE Generation discovered that a generator protective relay upgrade conducted in 2011 was not on an internal PRC-001 relay project list. Upon discovery, FE Generation conducted an investigation to determine the level of coordination that occurred during the upgrade. FE Generation determined that it had no documentation available to support that coordination was conducted with the locally interconnected Transmission Owner. FE Generation determined that although it has a detailed procedure in place for coordinating changes to protective systems, the relay design engineer did not follow it. The duration of this noncompliance is from May 2, 2011, the date FE Generation failed to coordinate a change to a protective system, to October 31, 2013, the date FE Generation completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the noncompliance was not discovered for two years, the duration also supports the conclusion that the noncompliance was an isolated occurrence of a single employee not following the procedure. Second, FE Generation made only one functional change to the relay that required coordination. ReliabilityFirst considered FE Generation's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FE Generation: 1) removed the additional protective relay functionality that was not coordinated; and 2) developed and presented re-training on the requirements of coordination.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Generation and Marketing (FE Generation) | NCR11317 | RFC2013012757 | PRC-001-1 | R1 | During the FE Generation Compliance Audit conducted from June 17, 2013 through June 28, 2013, ReliabilityFirst determined that FE Generation, as a Generator Operator (GOP) had an issue of PRC-001-1 R1. ReliabilityFirst discovered that FE Generation did not designate operating personnel as the individuals who are familiar with the purpose and limitation of Protection System schemes. Furthermore, of those non-operating personnel, one of eight individuals was not familiar with certain Protection System schemes applied in FE Generation’s area, affecting two of the 18 generation facilities. The duration of this noncompliance is from June 18, 2007, the date FE Generation was required to comply with PRC-001, to December 31, 2014, the date FE Generation completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the personnel identified by FE Generation who were familiar with Protection System schemes are technical personnel who support operations at the facilities. Second, FEGM personnel unfamiliarity was limited to stability limitations and Special Protection schemes, not owned by FE Generation, at two generating facilities. ReliabityFirst considered FE Generation's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue FE Generation: 1) developed standardized PRC-001 training to include the purpose and limitations of Protection System schemes in its area; 2) revised a procedure to designate operations personnel to have familiarity with the purpose and limitations of Protection System schemes; and 3) administered training to those designated operations personnel, with future training to occur on a three-year cycle.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Nuclear (FE Nuclear) | NCR11316 | RFC2013012170 | VAR-002-1.1b | R2 | On March 18, 2013, FE Nuclear submitted a Self-Report to ReliabilityFirst stating that as a Generator Owner (GO) and Generator Operator (GOP) it had and issue with VAR-002-1.1b R2. FE Nuclear reported that during a review of operating data at all nuclear sites, it discovered three voltage schedule excursions during off-peak hours at its Beaver Valley facility. In each case, there was no record of having contacted the local control center. The greatest excursion was 2.6 kV. FE Nuclear’s root cause analysis of the excursions revealed that a small difference in exciter voltage, such as the small difference present in the instant noncompliance, when displayed on an analog meter, did not appear different enough for an operator to identify that the voltage schedule was not being followed. The duration of this noncompliance is from March 18, 2011, the date of the first occurrence of the noncompliance, to September 12, 2013, the date FE Nuclear completed its remediation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the noncompliance was not identified for a period of two years, the root cause was related to human error in reading imprecise instrumentation, which has a limited likelihood of recurrence even during the period in which the problem was unknown to FE Nuclear. Second, the Beaver Valley facility is located in a geographic area of significant generation such that other units could compensate for the error. Third, the failure to identify the small voltage excursions was not due to a failure to monitor voltage. ReliabilityFirst considered FE Nuclear's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FE Nuclear: 1) supplemented metering with a computer dedicated to monitoring station voltage with alarms for voltage excursions; 2) improved a procedure to require twice-daily review of automatic voltage regulator set-point adjustments to maintain voltage during the change from on-peak to off-peak voltage schedules; and 3) conducted training on the revised procedure. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Nuclear (FE Nuclear) | NCR11316 | RFC2013012759 | FAC-008-1 | R2 | During the FE Nuclear Compliance Audit conducted from June 17, 2013 through June 28, 2013, ReliabilityFirst determined that FE Nuclear, as Generator Owner (GO) had an issue of FAC-008-1 R2. FE Nuclear failed to provide a method of inspection and review of Facility Ratings Methodologies for three nuclear generating facilities. The duration of this noncompliance is from February 23, 2009, the start date of the Compliance Audit period, to June 28, 2013, the date FE Nuclear implemented its mitigating actions. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, FE Nuclear’s generating facilities have a normal band of operation between the normal operating point (applicable alarm or trip value) and the operating limit (maximum operating value) imposed on the system, so the inherent value in this Requirement is diminished for the operating conditions of these particular facilities. Second, FE Nuclear promptly resolved the noncompliance during the audit. ReliabityFirst considered FE Nuclear's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue FE Nuclear revised its Facility Ratings Methodology to apply to FE Generation and FE Nuclear, thus providing all Facility Ratings Methodologies in one document. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Pleasants Energy, LLC (Pleasants Energy) | NCR00294 | RFC2014013916 | VAR-002-1.1b | R2 | ReliabilityFirst conducted a compliance audit of Pleasants Energy on August 14, 2013, during which ReliabilityFirst determined that Pleasants Energy, as a Generator Operator (GOP) had an issue of VAR-002-1.1b R2. Pleasants Energy did not maintain the generator voltage or Reactive Power output (within applicable Facility Ratings) as directed by the Transmission Operator (TOP). Specifically, Pleasants Energy did not maintain the generator voltage or Reactive Power output (within applicable Facility Ratings) as directed by the TOP at various times from April 12, 2012 to August 30, 2013. At various points during this time period, Pleasants Energy did not maintain voltage levels within the TOP’s default voltage schedule. Also, Pleasants Energy did not notify the TOP when it was not maintaining proper voltage levels and did not request any exemptions or modifications to its voltage schedule from the TOP. The operators on shift were unaware that they were required to notify the TOP if they were operating outside of the voltage schedule. The root cause of this noncompliance was that Pleasants Energy plant operators did not understand that VAR-002-1.1b requires notification to the TOP, and exemption or modification (where applicable), when Pleasants Energy is unable to maintain voltage levels within its schedule. This was the only audit finding at the Operations and Planning Compliance Audit of Pleasants Energy, and there was no indication that plant operators lacked an understanding of compliance responsibilities with respect to other Reliability Standards. The duration of this noncompliance is from August 3, 2012, the date by which Pleasants Energy was required to comply with VAR-002-1.1b, to May 30, 2013, the date Pleasants Energy completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. At all relevant times, voltage was regulated by Pleasants Energy’s Automatic Voltage Regulator (AVR). From April 12, 2012 to August 30, 2013, the plant had a total operating time of 969 hours and 7 minutes. For 840 hours and 16 minutes, the plant operated within its voltage schedule. For 128 hours and 51 minutes, Pleasants Energy operated outside of its voltage schedule (138kv +/- 2kV). During those 128 hours and 51 minutes, Pleasants Energy was always within 1.98% of the TOP’s voltage schedule (138kv +/- 2kV). Throughout the entire period of the noncompliance, the AVR continued to maintain system voltage and Pleasants Energy was not contacted by the TOP about operating outside of the low end of the voltage schedule. The size, type, location, and electrical connections of the units at the plant made it impossible at times for the plant to meet its voltage schedule, even when the plant was providing maximum MVARs to the electrical system. During the entire period of noncompliance, Pleasants Energy did not notify or request an exemption from the TOP when it was outside of its voltage schedule. Although Pleasants Energy’s mitigation plan was completed on May 30, 2013, Pleasants Energy did not request a modified voltage schedule until July 1, 2013. As of July 1, 2013, Pleasants Energy had put in place a procedure to notify the TOP when it is unable to meet the voltage schedule and to obtain an exemption in such cases, thereby decreasing risk to the Bulk Electric System (BES). ReliabilityFirst considered Pleasants Energy's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Pleasants Energy: 1) developed and presented training to plant personnel on the TOP voltage schedule that Pleasants Energy must follow; 2) added a red flashing alert to the operator screen in the control room which alerts the operators if the TOP voltage level is not being met; and 3) revised its plant procedure to state that after synchronizing to the grid and reaching base/preselected load, the net system voltage must be monitored to ensure compliance with the TOP voltage schedule. If the net system voltage is outside of the TOP voltage schedule, the control room operator must raise or lower the voltage accordingly or notify the TOP requesting an exemption or modification to the voltage schedule. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | U.S. Department of Energy (DOE) | NCR04167 | RFC2013013004 | PRC-005-1b | R2.1 | On September 20, 2013, DOE submitted a Self-Report stating that, as a Distribution Provider (DP) and Transmission Owner (TO), it had an issue of PRC-005-1b R2.1 During a review of Preventive Maintenance activity for Bulk Electric System (BES) related equipment, DOE discovered that two items associated with the BES had exceeded their Preventive Maintenance delinquent dates. Delinquent dates are maintenance due dates. Exceeding an item’s Preventive Maintenance delinquent date means the item is overdue for maintenance according to DOE’s Preventive Maintenance Program (Program). One of these two items, the Bus 22 Potential Transformer (PT), is part of the Protection System for the site and falls under the Transmission Owners requirement of PRC-005-R1b R2.1. The other item, Oil Circuit Breaker (OCB) 258, is part of the BES and is included in the Site’s Program but does not fall under the NERC definition of a Protection System. Procedure FBP-SM-PRO-00384 of the Program requires that when a Preventive Maintenance task cannot be completed by the delinquent date, then either (a) a Preventive Maintenance deferral must be processed or (b) the equipment must be taken out of service. DOE initially planned, scheduled, and attempted Preventive Maintenance testing for the Bus 22 PT at the X-530 Switchyard within its defined interval. During the first and subsequent maintenance attempts, DOE encountered recurring problems while switching the PT out of service, which caused a loss of metering to the plant side. While the DOE further evaluated these switching out of service issues, the maintenance task exceeded the May 30, 2013 delinquent date without the required Preventive Maintenance deferral. Additionally, power operations could not take the Bus 22 PT out of service prior to its delinquent date because it would have impacted revenue metering for the plant site. OCB 258 became delinquent on June 15, 2013 and a request was made to Ohio Valley Electric Corporation (OVEC) and the Midcontinent Independent System Operator, Inc. (MISO) to take the OCB out of service on June 18, 2013. MISO approved the removal of OCB on June 24, 2013 and it was taken out of service on that same day. The duration of this noncompliance is from May 30, 2013, the date by which DOE was required to comply with PRC-005, to October 31, 2013, the date DOE completed its Mitigation Plan to remediate its noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The Bus 22 PTs remained in service and the protective relays were not impacted. If a fault were to occur on the Bus 22 PT, the system would switch to the Bus 21 PT and thus the relay potential would remain in service while metering for the site might be lost. Additionally, OCB 258 is only one of 20 OCBs in a seven bay breaker-and-a-half scheme (meaning the system has adequate alternate ties to the BES in case of the failure of OCB 258). ReliabiltyFirst considered DOE's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because although DOE had two prior violations of PRC-005, ReliabilityFirst did not consider DOE’s violation history as a factor warranting an alternative disposition method. The two prior violations are distinguishable as both prior violations involved a failure to provide evidence of any maintenance and testing for required Protection System devices. In contrast, the instant noncompliance stems from DOE attempting to implement its Program for the devices at issue, but encountering unexpected problems while implementing it, which caused DOE to violate the Reliability Standard at issue while addressing those problems. As a result, ReliabilityFirst did not consider the prior conduct of DOE an aggravating factor warranting a non-monetary sanction since ReliabilityFirst does not have the authority to assess a monetary sanction against the DOE. | To mitigate this issue, DOE: 1) generated and processed Preventive Maintenance deferrals to evaluate the impact of their continued operation and to allow time for proper planning and scheduling of the overdue maintenance; 2) expedited the maintenance on the overdue items within its work control process and either processed Preventive Maintenance deferrals or removed the equipment from service; 3) completed an extent of condition analysis to determine if any other maintenance tasks were overdue for other DOE items; 4) processed and completed tasks related to three additional items revealed as a result of the condition analysis; 5) made switchyard preventative maintenance a higher priority in its work control process; and 6) made the identification and processing of NERC related maintenance tasks a higher priority in its work control process. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014141 | PRC-005-1b | R2 | On July 17, 2014, DEP submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1b R2. DEP reported that it was missing a quarterly battery inspection report for the 4th quarter of 2013 at the Mayo Plant. As part of a self-assessment, DEP generation compliance requested a review of the quarterly and annual maintenance inspection records for each of the Fossil and Hydro plants for DEP. DEP discovered that a quarterly inspection report for the Mayo Plant was missing for the fourth quarter of 2013. DEP completed the preventative maintenance (PM) record on November 21, 2013 for this fourth quarter inspection. However, DEP could not locate the completed inspection report. This inspection report is required to demonstrate DEP’s compliance with its PRC-005 program. Two batteries were affected at the Mayo Plant. While SERC was performing its assessment and determining the scope of the issue, DEP found an additional issue. In 2012, DEP’s PRC-005 program for battery maintenance required it to perform maintenance quarterly and annually. The program defines quarterly as every three months and the system used to schedule maintenance establishes target dates based on the previous completion date. The program also allows a three week grace period before and after the target date. The system generates work orders 30 days prior to the target date to allow scheduling of the maintenance to occur within the grace period. DEP discovered a second issue with the Protection System maintenance program during an internal review of records in preparation for the upcoming DEP audit. On January 25, 2012, DEP performed fourth quarter battery maintenance at the Smith Energy Complex Combined Cycle Steam Unit. Based on that completion date, the maintenance management system generated a work order 30 days prior to the target date for the next quarter which was April 25, 2012. To comply with the maintenance program, the earliest the maintenance should have been performed was April 4, 2012. However, the maintenance was immediately scheduled and performed on March 27, 2012, one week earlier than allowed by the DEP program. DEP’s work management system did not have logic to prevent the early scheduling and completion of periodic maintenance and testing. This issue affected one battery at the Smith Energy Complex. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. DEP’s failure to maintain adequate inspection records and to maintain its batteries within the intervals defined in its program could have resulted in inadequate maintenance of the batteries, which could result in unnecessary and unplanned plant outages or the inability to respond to disturbances or both. However, the batteries at both locations had low voltage alarms, allowing DEP to investigate if a battery had a problem. In addition, DEP’s other monthly and weekly preventative maintenance records show the batteries were in good operating condition. The quarterly maintenance records for subsequent quarters also indicate that the batteries were in good operating condition. No harm is known to have occurred. A Settlement Agreement covering violations of PRC-005 R2 for DEP was filed with FERC under NP12-12-000 on December 30, 2011. On January 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered DEP's compliance history and determined that the instant issue was appropriate for compliance exception treatment because the causes of the extant issues were not addressed by the previous Mitigation Plan. The prior violation involved a failure by DEP to conduct maintenance on Coupling Capacitive Voltage Transformers as called for in its Protection System maintenance and testing program. DEP determined that the root cause of the violation was database corruption and as part of its Mitigation Plan, DEP undertook an inventory of its substations and reconciled the remainder of the field inventory with its database. A Settlement Agreement covering violations of PRC-005 R2 for DEP was filed with FERC under NP13-476-000 on July 31 2013. On January 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered DEP's compliance history and determined that the instant issue was appropriate for compliance exception treatment because the causes of the extant issues were not addressed by the previous Mitigation Plan. DEP missed or had incomplete maintenance or testing records for less than 5 percent of the Protection System devices. Mitigation included performing maintenance and testing on those devices and revising their record keeping methods for those, but not all, devices. A Find, Fix, Track and Report informational posting addressing remediated issues for certain registered entities including noncompliance with PRC-005 R2 for DEP was posted on the NERC website on January 30, 2014. The 60-day review period passed on March 31, 2014. SERC considered DEP's compliance history and determined that the instant issue was appropriate for compliance exception treatment because the causes of the extant issues were not addressed by the previous Mitigation Plan. For this prior issue DEP had inadvertently closed a work order before testing on a single line trap had been successfully completed. DEP identified the root cause was the failure to require evidence of work completion to be attached to the work order prior to closing the order. The requirement to do so was added to the work order process for all Protection System devices. | To mitigate this issue, DEP: 1) issued a plant standing order to properly document the reports per the Fossil/Hydro Organization procedure with the plant Instrument & Control personnel; 2) established a procedure to ensure that staff will verify once a quarter that the inspection reports are properly recorded in addition to the existing checks already in place; 3) documented lessons learned to ensure all parties involved with quarterly battery PM are aware of the requirement to complete the PM during the specified quarter, and not prior to the start date; 4) ensured that all applicable staff signed off that they had read the document containing the lessons learned; and 5) sent a memo to DEP plant managers and superintendents informing each plan of the quarterly PM review and expectations.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014176 | PRC-023-2 | R5 | On July 22, 2014, DEP submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R5. DEP failed to submit a list of circuits using PRC-023 Criterion 12 to the Regional Entity within 15 months. On June 5, 2014, during an internal periodic review of PRC-023-2 compliance, DEP determined that it had exceeded the 15 month period since it last reported on PRC-023-2 R5. DEP reported its updated list to SERC on June 17, 2014. Before that, DEP last reported its updated list to SERC on February 6, 2013. During the approximate 16.5 months between reports, on May 13, 2013, DEP replaced the relays on one 500kV terminal at its Wake substation with microprocessor relays with load encroachment capability. This left only one 230kV line on the DEP criterion 12 list. DEP stated that the apparent cause of this issue was that it had no mechanism in place to remind it to report criterion 12 data to SERC. This issue lasted from May 6, 2014, when DEP failed to submit its updated list within 15 months of its last report through June 17, 2014, when DEP submitted its updated list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEP’s failure to provide an updated list of its criterion 12 circuits to SERC within 15 months left SERC and NERC unaware for approximately 1.5 months that DEP removed one circuit from its criterion 12 list and could have affected long term planning. However, the relaying change DEP made increased the loadability of the transmission line and DEP used the correct setpoints in its contingency planning models. No harm is known to have occurred. SERC considered DEP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DEP: 1) reported its Criterion 12 facility list to SERC via email on June 17, 2014; and 2) established a recurring internal reminder to the responsible DEP business units for completing a review and submitting the report. SERC has verified the completion of all mitigation activity.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014017 | INT-001-3 | R1 | On June 23, 2014, DEP submitted a Self-Report stating that, as a Purchasing-Selling Entity (PSE), it had an issue with INT-001-3 R1. DEP failed to ensure that Arranged Interchange was submitted to the Interchange Authority for all Dynamic Schedules at the expected average MW profile for each hour. The joint dispatch dynamic schedule is referenced as Dynamic Transfer East to Duke (DTRED). Duke Energy Power Trading is responsible for purchasing transmission service reservations (TSRs). On May 8, 2014, Duke Energy Power Trading reserved a TSR on the DEP system to flow power into the Duke Energy Carolinas (DEC) system, but because DTRED was not expected to flow in this direction, a TSR was not established on the DEC system. A tag was not needed because power was not flowing at the time. For Hour Ending (HE) 20:00, conditions changed anticipating DTRED would flow from DEC to DEP. Therefore, Duke Energy Power Trading established a TSR on the DEC system for flow into DEP. No actual flow was taking place and no tag was in place for this anticipated flow. However, TSRs were in place and ready if economics were satisfied for actual flow. Earlier that day, DEP system operators substituted 0 MW for the DEP TSR values to avoid an unexpected flow without the necessary tagging in place. However, this entry was made in the incorrect data field in the DEP system that provides data for the automation. Due to this incorrect entry, from 19:00 to 19:07 the dynamic schedule DTRED flowed eight MWh of energy without a tag in place because TSRs had been established and economic conditions had been satisfied. During the seven minutes, the DTRED schedule ramped up to reach a peak of 100 MW and integrated a total of eight MWh. At 19:28, the DEP system operator discovered the issue and terminated the DTRED schedule for the remainder of the hour. This issue occurred because the DEP system operators failed to adhere to DEP’s established procedures. This issue lasted from May 8, 2014 at 19:00, when the schedule began to flow without a tag, to May 8, 2014 at 19:07, when the DEP system operator terminated the schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For a period of 28 minutes, when the inputs in the automated system would have allowed flows if then economic conditions were met, DEP’s Interchange Authority and Reliability Coordinator would not have been aware of the DTRED transaction because DEP failed to properly tag this data. However, the transaction flowed for seven minutes with an integrated total of eight MWh. After the seven minutes, the transaction stopped flowing because economic conditions were no longer met and the system operator later terminated the flow for the remainder of the hour. At the time of the issue, the DEC Balancing Authoritie's (BA’s) instantaneous load was approximately 14,660 MW and the DEP East BA’s instantaneous load was approximately 8,922 MW for a total of 23,582 MW instantaneous load between the two BAs. The peak of 100 MW that flowed during these seven minutes represented approximately 0.4% of the combined BA load at that time. In addition, there were no Transmission Loading Reliefs for the flowgates that this transaction would impact. No harm is known to have occurred. A Notice of Confirmed Violation covering violations of INT-001 R1 for DEP was filed with FERC under NP11-266-000 on August 31, 2011. On September 30, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with INT-001 R1 for DEP was filed with FERC under RC14-14-000 on July 31, 2012. The 60-day review period passed on September 29, 2012. SERC considered DEP's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the instances were of the same Standard and Requirement, the underlying conduct of the instances was different. The prior violations were related to failure to create and submit tags while the instant issue was related to failure of DEP System Operators to adhere to established procedures. A System Operator had inadvertently replaced the DTRED schedule in the Energy Management System tabular incorrectly and this allowed the DTRED to flow without a tag on May 8, 2014 from 19:00 to 19:07 when other criteria were satisfied. System Operators had current approved procedures providing guidance on the correct process to substitute the DTRED schedule to a certain MW value, which, if adhered to, would have prevented the DTRED from flowing without a tag. | To mitigate this issue, DEP: 1) notified system operator supervisors that effective immediately, the Transmission Services Desk will generate a tag as soon as transmission for the DTRED is purchased with no delay; 2) sent an email to system operators advising them of the event and the correct and incorrect ways to substitute the DTRED schedule to a certain value; 3) deployed an “interlock” to the DEP energy management system such that the DTRED will not be allowed to flow energy without a Confirmed Interchange tag for DTRED; and 4) required system operators to read and sign off on their understanding of the existing procedure SORMC-GOP-150 "Joint Dispatch Dynamic Schedule" which contains guidance on how to manually substitute values for DTRED. SERC has verified the completion of all mitigation activity.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2014014200 | PRC-023-2 | R5 | On August 6, 2014, Duke submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R5. Duke reported that it had not submitted a list of facilities using PRC-023-1 R1 Criterion 12 to its Regional Entity. An affiliate’s discovery of an issue with PRC-023-2 R5 prompted Duke to review its records related to PRC-023. On July 7, 2014, that review led Duke to discover that it had not reported its one facility that had relay trip setpoints established in accordance with PRC-023-2 R1 Criterion 12. Duke should have submitted the initial list to SERC in 2013, the year that PRC-023-2 went into effect. In 2013, SERC conducted a survey to determine how many circuits in the SERC Region were set according to Criterion 12. SERC confirmed that Duke did not submit a list to SERC including the Asbury 500kV line in the 2013 calendar year. Duke stated that the primary cause of the issue was an administrative oversight. SERC determined that Duke had an issue with PRC-023-2 R5 because it failed to provide an updated list of the circuits associated with relays set in accordance with Requirement 1 Criterion 12 to its Regional Entity at least once each calendar year. This issue lasted from January 1, 2014, when Duke failed to submit its updated list within the 2013 calendar year through July 11, 2014, when Duke reported the facility to SERC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Duke’s failure to provide a list of its criterion 12 circuits to SERC within the 2013 calendar year left SERC and NERC unaware that Duke had one facility with relay trip setpoints established in accordance with criterion 12. However, Duke used the correct Facility Ratings in its contingency planning models. No harm is known to have occurred. SERC considered Duke's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Duke: 1) reported its Criteria 12 facilities to SERC via email on July 11, 2014; 2) implemented a new Standards implementation procedure to ensure the proper implementation of new NERC Standards prior to the Standards becoming effective; and 3) setup automated reminders in CATSWeb to assist with meeting compliance submittal deadlines.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014385 | EOP-005-2 | R5 | On August 5, 2014, SERC sent DEP a notice of a Compliance Audit scheduled for November 3, 2014 through November 21, 2014. On October 7, 2014, DEP submitted a Self-Report stating that, as a Transmission Operator, it had an issue with EOP-005-2 R5. DEP did not provide the latest Reliability Coordinator (RC) approved restoration plan to all of its system operators prior to its effective date. DEP’s restoration plans are made available to system operators as hard copies and are also uploaded electronically to its energy control center SharePoint site. DEP utilizes its SharePoint site as evidence of the date it made restoration plan available to system operators in the primary control room. On July 9, 2014, during a review of the EOP-005-2 R5 compliance evidence, DEP discovered that the May 27, 2014 RC-approved restoration plan was posted to the SharePoint site on May 30, 2014, which was three days after the effective date. DEP determined that the issue was caused by process flaws associated with the revision and posting process of the RC-approved versions of the restoration plan. This issue lasted from May 26, 2014, the last day that DEP could have made its restoration plan available to all of its system operators prior to its effective date, through May 30, 2014, when DEP made its restoration plan available to all of its system operators. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. DEP’s failure to post the approved version of the restoration plan prior to its effective date could have led system operators to use restoration plans that do not correctly reflect current system configurations, appropriate blackstart units and cranking paths, and other vital information. However, the previous version of the restoration plan was available in the control room and the five changes to the restoration plan would not have affected the essential steps of a system restoration event if one had occurred prior to posting the revised version of the restoration plan on the SharePoint site. DEP posted the revised restoration plan within three days of its approval. No harm is known to have occurred. SERC considered DEP's compliance history and determined there were no relevant instances of non-compliance. | To mitigate this issue, DEP: 1) posted the current version of the RC-approved DEP restoration plan to the DEP energy control center SharePoint site for availability to system operators; 2) held a meeting in which relevant staff discussed the issue and possible solutions; 3) modified the SharePoint Library to include effective dates for all system operator reference manuals; 4) revised the “Administration of the System Operations Reference Manual Carolinas" to incorporate the effective date into the procedure process and to modify the procedure process so that the procedure is available in the SharePoint Library before the effective date; and 5) created an extra step in the approval process to address the use of effective dates.
2015-03-31 | SERC Reliability Corporation (SERC) | Fayetteville Public Works Commission (FPWC) | NCR01240 | SERC2014014194 | PRC-005-1.1b | R2 | On July 31, 2014, FPWC submitted a Self-Report stating that, as a Transmission Owner and a Distribution Provider that owns a transmission Protection System, it had an issue with PRC-005-1.1b R2. FPWC reported that it could not produce evidence of annual testing of station batteries during calendar year 2013. FPWC could not provide data to demonstrate that it performed impedance testing on station batteries at its Points of Delivery (POD) during calendar year 2013, as required by its program. FPWC downloads test data reports from the battery testing device into a database for permanent retention. The last recorded test date for annual impedance testing of the POD batteries in the database was July 25, 2012. Sometime around August 2013, during FPWC’s performance of its yearly battery testing program, the battery tester failed. FPWC did not download the data from testing completed prior to the tester failure into the database. Therefore, FPWC does not have documentation that it completed the required POD testing prior to the failure. FPWC personnel verified that yearly battery testing was being done when the tester failed, but cannot confirm whether all POD battery testing was completed prior to the failure. The cause of the issue was FPWC staff’s failure to promptly download data from the testing device to verify that the required testing had been satisfactorily completed. Timely verification of the satisfactory testing would have provided the opportunity to expedite repair of the tester or to acquire another tester to complete the testing, prior to the end of calendar year 2013. SERC reviewed FPWC’s Protection System program documents and an inventory spreadsheet compiled by FPWC, which included a complete listing of Protection System devices, the defined intervals, and most recent and prior maintenance and testing dates. SERC determined that FPWC had an issue with PRC-005-1.1b R2 because it could not provide documentation that seven out of seven batteries (100%) were maintained and tested within the defined annual interval. In total, FPWC could not provide documentation that seven out of 87 Protection System devices (8%) were maintained and tested within the defined intervals. This issue lasted from January 1, 2014, when FPWC could not provide evidence of annual impedance testing for 2013 through July 31, 2014, when FPWC completed and documented battery testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A station battery failure could trip a FPWC unit offline or prevent a trip when necessary. However, FPWC physically inspected the batteries twice each month for parameters such as voltage, physical appearance, charger output voltage and current, and electrolyte levels. The results of these other tests did not indicate any issues with the batteries. In addition, FPWC displays the battery voltage at its dispatch operations center, and receives an alarm there if voltage drops below a prescribed value. FPWC had directed its dispatchers to send out FPWC personnel to respond in the event of battery voltage alarms and received no battery alarms during the period. FPWC had redundant battery banks in order to provide battery capacity to cycle the breaker. No harm is known to have occurred. SERC considered FPWC compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FPWC: 1) obtained a replacement impedence tester, completed the required impedance testing on the POD batteries, and found all battery tests satisfactory; 2) downloaded test data into the database; 3) revised procedure to require data to be downloaded into permanent repository within 30 days of completing testing; 4) trained personnel on procedure changes and required status reports; 5) established a designated storage area in a well-traveled location for equipment that needs to be tested or repaired; and 6) began monthly reporting of compliance status of protection system testing.
2015-03-31 | SERC Reliability Corporation (SERC) | Grand Tower Energy Center, LLC (GTEC) | NCR11435 | SERC2014014384 | PRC-005-1.1b | R2 | On October 7, 2014, GTEC submitted a Self-Report stating that, as a Generation Owner, it had an issue with PRC-005-1.1b R2. GTEC cannot provide evidence that the voltage and current sensing devices were maintained or tested. On January 31, 2014, GTEC purchased a generating plant from another utility. Following the purchase of the plant, GTEC conducted a review of maintenance and testing records provided by the utility. GTEC could not find maintenance or testing records associated with voltage and current sensing devices in the documentation provided. SERC reviewed the Protection System program document and an inventory spreadsheet compiled by GTEC which included a complete listing of Protection System devices, the defined intervals, and most recent and prior maintenance and testing dates. Based on this review, SERC determined that GTEC had an issue with PRC-005-1.1b R2 for failing to have documentation that its Protection System devices were maintained and tested for all 141 of its voltage and current sensing devices. In total, GTEC lacked documentation showing maintenance or testing of 141 out of 302 (47%) total Protection System devices. The root cause of the issue was that GTEC could not locate maintenance and testing records for the voltage and current sensing devices in the documentation that the selling utility provided to GTEC. This issue lasted from January 31, 2014, GTEC’s registration date, through May 16, 2014, when GTEC completed maintenance and testing of the voltage and current sensing devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GTEC’s lack of maintenance and testing records could have led to inadequate or late maintenance or testing, which could result in the loss of a generating unit or reliance on the Transmission Owner’s Protection System devices to respond to a fault if GTEC’s Protection System devices failed to operate as designed. However, GTEC’s plant is manned by a control operator and monitored by an outside operator twenty-four hours a day, seven days a week. The readings from the voltage and current sensing devices lead to a microprocessor relay that would show a failure reading from the voltage and current sensing devices and personnel would be dispatched to determine the cause of the signal. GTEC is a combined cycle power plant with a total summer output of 478 MW interconnected by a single 138 KV interconnection in the MISO footprint, which has 137,232 MW of summer generation capacity. Therefore, GTEC represents less than 0.3% of the generation in the MISO footprint. GTEC is an independent power producer and is bid into MISO for the day-ahead market. Therefore, the generation is not used for generation planning purposes. GTEC completed all testing by May 16, 2014 and did not identify any issues with the voltage and current sensing devices. No harm is known to have occurred. | To mitigate this issue, GTEC: 1) updated the maintenance and testing program per PRC-005-2 requirements; and 2) completed the first round of potential and current transformer testing per the PRC-005-2 requirements.
2015-03-31 | SERC Reliability Corporation (SERC) | South Carolina Electric & Gas Company (SCEG) | NCR00915 | SERC2014014125 | PRC-005-1b | R2 | On June 10, 2014, SERC sent SCEG a notice of a compliance audit scheduled to begin on September 8, 2014. On July 10, 2014, SCEG submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-005-1b R2. SCEG could not provide evidence that all Protection System devices were maintained within the defined intervals. On March 27, 2014, as part of a normal self-audit, SCEG compared a list of known PRC-005 applicable substations to the list used in SCEG’s substation inspection management software (SIMS) program. SCEG identified two substation batteries and two battery chargers that were not listed in SIMS. Although SCEG management met with and confirmed that the responsible technician performed the required maintenance, SIMS did not contain evidence that SCEG performed maintenance on the two batteries and two battery chargers. SCEG installed the batteries and chargers on March 1, 2013, and performed acceptance testing on the devices prior to installation. As such, SCEG should have conducted maintenance on these devices once in each remaining quarter in 2013 and once in the first quarter of 2014. SCEG could not produce a record of the two batteries and two chargers being maintained in the last two quarters of 2013 and in the first quarter of 2014. SCEG submitted evidence that it conducted maintenance on these devices on May 29, 2014. After the July 10, 2014 Self-Report, SCEG conducted a thorough review of all other substation inspection and maintenance documentation and discovered one additional issue. SCEG built a new substation in 2012 and placed it into service on May 23, 2012. The substation had one battery and one battery charger but these Protection System devices were not added to SIMS. SCEG has documentation that the inspector was in the substation doing inspections from June 2012 through February 2013, but SCEG did not document any maintenance of the battery or battery charger during this period. SCEG first recorded battery maintenance for this new substation on April 5, 2013. According to SCEG, its current Protection System consists of the following: 2,707 relays, 156 associated communication systems, 2,519 PT/CTs (V/I Verifications), 103 station batteries, 103 station battery chargers, and 2,707 DC control circuitry devices. Therefore, SCEG’s current Protection System consists of 8,295 total devices. SCEG could not provide evidence that 3 of 103 station batteries (2.9%) and 3 of 103 station battery chargers (2.9%) were maintained within the defined intervals. In total, SCEG could not provide evidence that 6 of 8,295 Protection System devices (0.072%) were maintained within the defined intervals. This issue lasted from October 1, 2012, when SCEG could not provide evidence of maintenance within the defined interval, through May 29, 2014, when SCEG conducted and documented maintenance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCEG’s failure to record the maintenance of batteries and battery chargers created a risk that SCEG might not discover problems with those devices, which could lead to Protection System devices not operating as expected, thus affecting neighboring Transmission Operators. However, SCEG conducted acceptance testing prior to installation. The batteries also had low voltage alarms that were monitored 24 hours a day, 7 days a week, which would have alerted SCEG personnel to problems with those devices. Even though SCEG could not produce evidence of the maintenance, SCEG provided an attestation that it maintained the three batteries and three chargers as required by its PRC-005 maintenance and testing program. No harm is known to have occurred. A Find, Fix, Track and Report informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 for SCEG was filed with FERC under RC13-7-000 on March 27, 2013. The 60-day review period passed on May 26, 2013. SERC considered SCEG’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment. The prior issue involved a failure to provide maintenance and testing dates for relays, associated communication devices, voltage and current sensing devices, and DC control circuitry. The current issue involves a small number of batteries and battery chargers that were not added to the software program for maintenance and testing after the Protection System devices were installed, resulting in inadequate documentation of maintenance activities. As a result, the mitigating actions from the prior issue did not address the root cause of the instant issue. | To mitigate this issue, SCEG: 1) performed and documented maintenance activities on the batteries, as described in SCEG’s PRC-005 maintenance and testing program; 2) developed and conducted training to remind technicians of proper testing, maintenance, and documentation processes and to help ensure that similar future issues are quickly identified and corrected; 3) conducted periodic management reviews of PRC-005 applicable substations. This periodic review compares two different data sets to ensure SCEG accounts for all batteries; 4) enhanced automated quarterly battery reports to identify documentation errors; 5) focused training on reinforcing documentation processes such that inspectors have a clearly defined path for reporting erroneous or missing data discovered in the field; and 6) developed a workflow process to ensure uniformity across both regions, define roles and responsibilities, and to serve as a permanent reference document.
2015-03-31 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2014014106 | PRC-005-1.1b | R2 | On July 7, 2014, TVA submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1.1b R2. TVA could not provide evidence that all Protection System devices were maintained and tested within the defined intervals. On April 15, 2014, during a review of performance dates for preventive maintenance activities, TVA Browns Ferry Nuclear (BFN) personnel identified a missed maintenance interval of 26 weeks plus a 45 day grace period for a battery and charger. The scheduler mishandled a change in the scheduled maintenance, which resulted in TVA performing its maintenance and testing late. The scheduler set the date without regard to the previous preventative maintenance performance date, and therefore, had no logical basis for the date set. TVA performed the preventative maintenance nine days after required by the defined interval. TVA performed the preventative maintenance activities on April 15, 2014, immediately upon discovering the missed interval. Before that, TVA last performed the activities on August 21, 2013. TVA reported owning the following Protective System devices: 20,906 protective relays, 1,374 associated communication systems, 28,259 voltage and current sensing devices, 446 station batteries, 541 station battery chargers, and 20,906 DC control circuits. Of these devices, TVA maintained or tested one out of 446 station batteries (0.22%) and one out of 541 station battery chargers (0.18%) outside of the defined intervals. In total, TVA maintained or tested two out of 72,432 Protection System devices (0.0028%) outside of the defined intervals. This issue lasted from April 6, 2014, when TVA failed to maintain Protection System devices within the defined interval through April 15, 2014, when TVA completed preventative maintenance on the missed Protection System devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TVA’s failure to maintain the station battery and battery charger within the defined intervals could lead to the equipment malfunctioning. However, the 24VDC bus is equipped with a low-voltage alarm in a control room that TVA manned on a 24-hour basis. The appropriate procedural response to this alarm would have been to dispatch personnel to the communications battery room to investigate the cause. No voltage alarms associated with the missed battery went off for the duration of the issue. TVA completed the annual preventative maintenance on November 8, 2013, which was in the interim between its quarterly preventative maintenance. On April 15, 2014, TVA completed the quarterly preventative maintenance. On both occasions TVA did not discover any maintenance or operability issues with the station battery or charger. The involved devices did not experience any failures during the issue period, which lasted a total of nine days. No harm is known to have occurred. A Notice of Confirmed Violation covering violations of PRC-005-1 R2 for TVA was filed with FERC under NP09-36-000 on September 25, 2009. On October 23, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering two violations of PRC-005-1 R2.1 for TVA was filed with FERC under NP10-180-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2; R2.1 for TVA was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1b R2 for TVA was filed with FERC under NP14-4-000 on October 30, 2013. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered TVA’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the instances were of the same Standard and Requirement, TVA’s internal controls limited the scope of and duration of the issue. TVA had implemented a regular review of performance dates for preventive maintenance activities, which allowed TVA to detect the issue within nine days of missing the interval, and immediately implemented corrective actions by performing the required maintenance activities on the two devices. TVA had a low voltage alarm for the battery at issue, which would have alerted it to any problems with the battery. TVA's prior violations involved significantly more Protection System devices and the duration of those violations were significantly longer. | To mitigate this issue, TVA: 1) removed the individual who processed the subject preventative maintenance change request (PMCR) from PMCR duties; 2) performed an extent of condition review of PMCRs performed by the same individual, and identified no additional occurrences; 3) briefed all BFN work management personnel responsible for scheduling preventative maintenance and implementing PMCRs; 4) revised descriptions for all applicable BFN NERC preventative maintenances to start with "FERC" to ensure personnel are aware when they are dealing with a NERC regulated preventative maintenance; 5) regularly completed compliance verifications since they were resumed for March 2014; 6) shared lessons learned with Nuclear Power Group peers and made lessons learned available to all TVA NERC compliance program managers; 7) revised PRC-005 preventative maintenance compliance verification process to require: (a) initiation of corrective actions when issues are identified; and (b) that dated documentation of each completed verification is provided; 8) revised its compliance program document to include performance of compliance verifications of PRC-005; and 9) performed communication and training required by an approved change management plan.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2013012620 | PRC-008-0 | R2 | On July 11, 2013, AECC submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue of noncompliance with PRC-008-0 R2 because it did not test two of its 64 (3.1%) UFLS relays within the five year interval defined in its Protection System Maintenance and Testing Program (Program). The root cause of the issue of noncompliance was AECC‘s lack of employee oversight of the UFLS equipment testing schedule reviews. The issue of noncompliance began July 31, 2009, when the first UFLS relay should have been tested to fall within the defined interval and ended October 8, 2012, the date of the last UFLS relay test. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Only two of AECC’s 64 (3.1%) UFLS relays, at two substations, were not tested within the five year interval. Subsequent testing of the two UFLS relays found the relays to be fully operational and would have functioned as expected if a load shedding event had occurred. The load under UFLS control at the two substations is approximately 16.5 MW on peak and represents only 2.0% of the designated load shed of AECC’s UFLS program. No actual harm occurred. AECC does not have prior violation history. | To mitigate this issue of noncompliance, AECC: 1. revised the Program to improve the process of reviewing the UFLS test schedule; and, 2. confirmed both relays had been properly tested. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Grand River Dam Authority (GRDA) | NCR01101 | SPP2014013865 | TOP-002-2.1b | R11 | During a Compliance Audit conducted from May 12, 2014, through May 15, 2014, SPP RE determined that GRDA, as a Generator Operator, Load-Serving Entity, and Transmission Operator, had an issue of noncompliance with TOP-002-2.1b R11 because it did not use identical seasonal System Operating Limits (SOLs) for common facilities with neighboring Transmission Operators. GRDA determined its seasonal SOLs based on its Facility Ratings, which are based upon the most limiting element of the facility. GRDA kept the most limiting elements of its facilities on a spreadsheet. GRDA provided its neighboring Transmission Operators with its SOLs on a different spreadsheet. During the audit, SPP RE noticed discrepancies between the two spreadsheets (8 out of 17 sampled facilities had mismatched SOLs). Therefore, GRDA could not demonstrate that it was using identical SOLs with its neighboring Transmission Operators. The root cause of the issue of noncompliance was a lack of documentation consistency. The issue began on March 11, 2014, and ended on December 22, 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although wrongly reported SOLs can lead to facilities being operated above their actual ratings, most of the SOLs GRDA provided its neighboring TOPs were below the facilities’ actual ratings. Only two of the wrongly reported SOLs exceeded the actual rating. Furthermore, of the SOLs that exceeded the actual facility rating, the largest discrepancy was 15 MVA. Upon a subsequent inquiry by SPP RE, GRDA attested that historical SCADA data showed that none of its facilities experienced operations that exceeded their actual ratings. No actual harm occurred as a result of this issue of non-compliance. No violation history. | To mitigate this issue, GRDA: 1. Verified current GRDA SOLs on common facilities with SPP, as its Balancing Authority and Reliability Coordinator, and affected neighboring TOPs; 2. Updated the GRDA’s document # 6200Facility Ratings Process document to clarify steps for the coordination with neighboring TOPs of identical SOLs for common facilities; and 3. Documented that the responsible engineering staff have read and understand the updated GRDA’s document # 6200 Facility Ratings Process procedural steps. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Grand River Dam Authority (GRDA) | NCR01101 | SPP2014013874 | TOP-008-1 | R2 | During a Compliance Audit conducted from May 12, 2014, through May 15, 2014, SPP RE determined that GRDA, as a Transmission Operator, had an issue of noncompliance with TOP-008-1 R2 because it did not operate to prevent the likelihood that a disturbance, i.e., loss of a Catoosa autotransformer would result in a System Operating Limit (SOL) violation. On December 3, 2013, GRDA became aware that the autotransformers at its Catoosa substation would exceed their emergency ratings (188 MVA) should loss of the other autotransformer occur (only two of the three autotransformers were in service). GRDA’s Reliability Coordinator (RC) contacted GRDA regarding the potential SOL violation and suggested that GRDA place a third autotransformer at the Catoosa substation in service. GRDA notified the RC that it had an operating directive in place to open a power circuit breaker at the Claremore substation to prevent the SOL violation, should it lose one of the autotransformers. The December 3, 2013 RTCA provided by GRDA showed that the post contingency loading on the autotransformers (207.9 MVA) was in excess of the emergency rating of the autotransformers (188 MVA) for loss of one of the two autotransformers in service. GRDA’s operating directive did not indicate that it was safe to exceed the autotransformer emergency rating for any length of time. The root cause of the issue of noncompliance was a lack of a fully vetted procedure. The issue began on December 3, 2013, and ended on September 15, 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). GRDA did have an operating directive in place to prevent the likelihood of an SOL violation caused by loss of a Catoosa autotransformer. However, the operating directive was ineffective in preventing an immediate SOL violation, i.e., the remaining Catoosa autotransformer exceeding its emergency rating by 10%. GRDA has since indicated that the autotransformers at Catoosa can exceed their Emergency rating by 111% for two (2) hours before being damaged. Additionally, SCADA alarms (Level 1 = 135 MVA, Level 2 = 150 MVA, Level 3 = 165 MVA, Level 4 = 188 MVA) are in place that would provide notification to system operators in the event of an impending transformer overload. GRDA system operators would under most overload conditions have sufficient time to implement mitigating measures. No Violation History. | To mitigate this minimal risk instance of noncompliance, GRDA: 1. Updated its SOL Process to address how System Operators are to handle N-1 SOL violations in real-time; 2. Updated its Operations Planning Process to include Next-day system studies performed by System Operators and procedural steps associated with the study. 3. Updated its GRDA Facility Rating Methodology to include time limit for exceeding emergency limits. 4. Trained responsible system operation staff on updated processes. 5. Trained responsible engineering staff on updated processes. 6. Updated Transmission Operating Directive TOD or operating guide for exceeding the Catoosa Autotransformers emergency rating that includes three limits, (Normal, emergency and short term emergency) and time limits for exceeding emergency limits. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Tulsa District (COE-Tulsa) | NCR06038 | SPP201000204 | FAC-001-0 | R1; R1.1, R1.2, R1.3 | On January 13, 2010, United States Corps of Engineers-Tulsa District (COE-Tulsa) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R1, R1.1, R1.2, R1.3, (SPP201000204). Specifically, the COE-Tulsa does not document, maintain, and publish facility connection requirements (FAC-001-0 R1). The root cause of the issue of noncompliance is because COE-Tulsa has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE- Tulsa does not believe it is a Transmission Owner, it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-Tulsa does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-Tulsa’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities, an extensive evaluation and approval process would be necessary for any interconnection requests from outside entities. No actual harm has occurred since the issue of noncompliance start date. The COE-Tulsa has no relevant compliance history. | To mitigate this issue, COE-Tulsa will complete the following mitigation activities by October 30, 2015: 1) develop facility connection requirements addressing all requirements and subrequirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Tulsa District (COE-Tulsa) | NCR06038 | SPP201000205 | FAC-001-0 | R2; R2.1, R2.1.1, R2.1.2, R2.1.3, R2.1.4, R2.1.5, R2.1.6, R2.1.7, R2.1.8, R2.1.9, R2.1.10, R2.1.11, R2.1.12, R2.1.13, R2.1.14, R2.1.15, R2.1.16 | On January 13, 2010, United States Corps of Engineers-Tulsa District (COE-Tulsa) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R2, et seq. (SPP201000205). Specifically, the COE-Tulsa does not document, maintain, and publish facility connection requirements (FAC-001-0 R2, et. seq). The root cause of the issue of noncompliance is that COE-Tulsa has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE- Tulsa does not believe it is a Transmission Owner and it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-Tulsa does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-Tulsa’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities an extensive evaluation, and approval would be necessary for any interconnection requests from outside entities. No actual harm has occurred due to this issue of noncompliance. The COE-Tulsa has no relevant compliance history. | To mitigate this issue, COE-Tulsa will complete the following mitigation activities by October 30, 2015: 1) develop facility connection requirements addressing all subrequirements and requirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Little Rock District (COE-LR) | NCR06037 | SPP201000202 | FAC-001-0 | R1; R1.1, R1.2, R1.3 | On January 18, 2010, United States Corps of Engineers-Little Rock District (COE-LR) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R1, R1.1, R1.2, R1.3, (SPP201000202). Specifically, the COE-LR does not document, maintain, and publish facility connection requirements (FAC-001-0 R1). The root cause of the issue of noncompliance is because COE-LR has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE-LR does not believe it is a Transmission Owner, it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-LR does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-LR’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities, an extensive evaluation and approval process would be necessary for any interconnection requests from outside entities. No actual harm has occurred since the issue of noncompliance start date. The COE-LR has no relevant compliance history. | To mitigate this issue, COE-LR will complete the following mitigation activities by October 7, 2015: 1) develop facility connection requirements addressing all requirements and subrequirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Tulsa District (COE-LR) | NCR06037 | SPP201000203 | FAC-001-0 | R2; R2.1, R2.1.1, R2.1.2, R2.1.3, R2.1.4, R2.1.5, R2.1.6, R2.1.7, R2.1.8, R2.1.9, R2.1.10, R2.1.11, R2.1.12, R2.1.13, R2.1.14, R2.1.15, R2.1.16 | On January 18, 2010, United States Corps of Engineers-Little Rock District (COE-LR) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R2, et seq. (SPP201000203). Specifically, the COE-LR does not document, maintain, and publish facility connection requirements (FAC-001-0 R2, et. seq). The root cause of the issue of noncompliance is that COE-LR has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE-LR does not believe it is a Transmission Owner and it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-LR does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-LR’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities an extensive evaluation, and approval would be necessary for any interconnection requests from outside entities. No actual harm has occurred due to this issue of noncompliance. The COE-LR has no relevant compliance history. | To mitigate this issue, COE-LR will complete the following mitigation activities by October 7, 2015: 1) develop facility connection requirements addressing all subrequirements and requirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE-Kansas City District | NCR01357 | SPP201100459 | PRC-005-1 | R2; R2.1 | On January 18, 2011, USACE-Kansas City submitted a Self-Report stating that, as a Generator Owner and Transmission Owner, it had an issue of noncompliance with PRC-005-1 R2, inclusive of R2.1 because it did not have evidence that some Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing program (Program) (Version 2, dated 08/04/10). Specifically, USACE-Kansas City did not have evidence of performing its yearly microprocessor based relays tests on 27 of its 93 relays for the year of 2010. USACE-Kansas City’s Program requires USACE-Kansas City to perform yearly 1) microprocessor relay self-tests; 2) meter accuracy verification; and 3) output trip circuit verifications to ensure D.C. circuitry connectivity with its breakers. USACE-Kansas was not able to provide evidence that it had performed these tests on 27 of its 93 relays for the year 2010. The root cause of the issue of noncompliance was USACE-Kansas City’s employees’ inattention to ensure the microprocessor based relays were tested according to USACE-Kansas City’s Program. The issue of noncompliance began on January 1, 2010, and lasted until July 18, 2011 (the date of completion of testing and verification of the microprocessor based relays). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Of the 93 total relays located at USACE Kansas City’s two substations, only 27 were implicated in the self-report. When USACE-Kansas City tested the microprocessor relays to mitigate the issue of noncompliance, it verified that all 27 relays were in proper working order. Additionally, these microprocessor relays were commissioned in 2007 and installed with back-up relays. These microprocessor relays are monitored by a USACE-Kansas City operator in the operations center 24x7 and there are alarms if the relays become inoperable. Although USACE-Kansas City’s testing interval for its microprocessor relays is yearly, Table 1 of the NERC Technical Reference, applicable at the time of the issue of non-compliance, proposed a maximum verification interval of ten (10) years for thoroughly monitored relays. No actual harm is known to have occurred. No Violation History. | To mitigate this issue and prevent recurrence, USACE-Kansas City: 1) Completed relay self-tests and output trip circuit verification on all the relays; 2) Performed relay meter accuracy verification tests (04/18/2011); 3) Evaluated its Program and revised the intervals; 4) Developed a revised testing schedule for the two facilities in accordance with its revised Program; and, 5) Completed relay tests within the frequency required by the new Program. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE-Kansas City District | NCR01357 | SPP2011008131 | VAR-002-1.1b | R3; R3.1 | On September 19, 2011, USACE-Kansas City submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it had an issue of noncompliance with VAR-002-1.1b R3, inclusive of R3.1 because it did not notify its Transmission Operator (TOP) within 30 minutes of the status change of a power system stabilizer (PSS) at the Stockton hydro facility. On February 10, 2011, USACE-Kansas City staff reported to its TOP that the status of the PSS at Stockton was “off.” During an August 3, 2011, Power Operations and Maintenance review at Stockton, USACE-Kansas City staff noticed that the Stockton PSS was in the “on” position. USACE-Kansas City staff could not establish when the PSS was switched on and could not confirm that its TOP had been notified of the change in status. On August 3, 2011, at 15:15, USACE-Kansas City changed the status of the Stockton PSS to “off,” and notified its TOP. The root cause of this issue of noncompliance was the failure of the Stockton operators to verify the status of the PSS during plant operations, and notify the TOP of a status change. This issue of noncompliance began sometime after February 10, 2011, when USACE-Kansas City failed to report to its TOP that the Stockton PSS was on and ended August 3, 2011, when USACE-Kansas City switched the Stockton PSS to the off position and informed its TOP of the status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. USACE-Kansas City’s TOP had previously provided the USACE-Kansas City’s Stockton facility with an exemption from its PSS requirements; was not relying on the Stockton PSS for voltage support; and was not expecting any notifications regarding the status of the Stockton PSS. Furthermore, USACE-Kansas City’s Stockton facility is a small hydroelectric power plant (50 MW) capable of providing minimal reactive support to the BES. No actual harm is occurred while the PSS was switch in the “on” position. No Violation History. | To mitigate this issue, USACE-Kansas City: 1) determined required PSS settings and applied the correct setting; 2) informed the TOP of the PSS status change; 3) provided information tags on the PSS to indicate the required position; and, 4) informed plant staff of the appropriate PSS status and reporting requirements. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | South Houston Green Power, LLC (SHGP) | NCR11310 | TRE2014014440 | PRC-005-1b | R1; R1.1 | During a Compliance Audit conducted from October 28, 2014 through November 5, 2014, Texas RE determined that SHGP, as a Generator Owner (GO), had an issue with PRC-005-1b R1 and R1.1. Specifically, SHGP’s Maintenance and Testing Program did not have a defined interval or basis for testing Instrument Transformers from February 1, 2013 to April 29, 2014. Following the Compliance Audit, Texas RE also determined that while SHGP did define test intervals for its Instrument Transformers on April 29, 2014, SHGP did not define a basis for these test intervals until December 1, 2014. After the plant was acquired under new ownership in February 2013, SHGP revised the Protection System Maintenance Program; however, it did not make any adjustments to the interval and basis for testing instrument transformers in the revision. The root cause was determined to be a failure to make these adjustments. Texas RE determined the duration of the issue to be from February 1, 2013, when SHGP registered as a GO, through December 1, 2014, when SHGP defined an interval and basis for its test intervals. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This issue is documentation-based, and did not pose any Operational risk to the BPS. During the Audit, Texas RE found that the Instrument Transformers had been tested in 2008. According to SHGP’s current testing intervals, these Instrument Transformers were not due for testing again until 2020. Additionally, while SHGP’s generation totals at approximately 1100 MW, throughout the issue period, SHGP only exported a maximum of 485 MW from its Private Use Network. No actual harm is known to have occurred. SHGP asserts that it has not experienced any trips or mis-operations due to the Instrument Transformers over the duration period. Texas RE considered SHGP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SHGP has taken the following actions: 1) updated its Maintenance and Testing Program to include defined testing intervals for its Instrument Transformers; and 2) updated its Maintenance and Testing Program to include a defined basis for the testing intervals of its Instrument Transformers. SHGP will complete the following mitigating activity by April 1, 2015: 3) develop and implement a new Maintenance and Testing Program, designed to address the requirements set forth in the upcoming NERC Reliability Standard, PRC-005-2. The new Standard defines set intervals for Protection System equipment and serves as an industry basis.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2014014406 | INT-004-2 | R2 | On October 24, 2014, AZPS submitted a Self-Report stating that, as a Balancing Authority (BA), Transmission Operator (TOP), and Purchase-Selling Entity (PSE) it had an issue of INT-004-2 R2.. During an internal compliance review, AZPS found that it had an inconsistent interpretation of the requirements of INT-004-2. Operators would make adjustments to dynamic interchange schedules for the next available scheduling hour and future hours when a generator would trip and the energy profile would go to zero. Similarly, when the generator would return to service, the next available scheduling hour and the future hours would be adjusted to reflect the schedule returning to full. However, when the average energy profile in an hour was greater than 250 MW and in that hour the actual hourly integrated energy deviated from the hourly average energy profile indicated on the tag by more than +/- 10%, the required adjustments were not always performed. Similarly, when the average energy profile in an hour was less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +/- 25 megawatt-hours, the required adjustments were not always performed. A WECC Subject Matter Expert (SME) review the information provided by AZPS and found that AZPS provided updates for electronic tags for Dynamic Interchange Scheduling (tags) for instances of generator loss or reductions, it failed to update the tags when certain outside Load Serving Entity’s (LSEs) executed energy purchases and/or sales when the average energy profile in an hour was greater than 250 MW and in that hour the actual hourly integrated energy deviated from the hourly average energy profile indicated on the tag by more than +/- 10%. Likewise, when the average energy profile in an hour was less than 250 MW and in that hour the actual hourly average profile indicated on the tag deviated by more than +/- 25%, the entity did not update the tag. Therefore the SME determined AZPS had a possible issue with INT-004 R2. The SME forwarded this information to Enforcement. Enforcement reviewed the information provided by AZPS and the SME. Enforcement determined that AZPS failed to ensure that the tag for the Dynamic Interchange Schedule was updated for the next available scheduling hour and future hours when the average energy profile in an hour was greater than 250 MW and in that hour the actual hourly integrated energy deviated from the hourly average energy profile indicated on the tag by more than +/- 10%. Likewise, when the average energy profile in an hour was less than 250 MW and in that hour the actual hourly average profile indicated on the tag deviated by more than +/- 25%, the entity did not update the tag. As a result, AZPS has an issue with INT-004-2 R2. AZPS has had multiple instances of noncompliance of this standard beginning August 27, 2008, the effective date of this standard and is ongoing . AZPS does not have a history of violations for INT-004-2. The root cause of this issue was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. AZPS failed to ensure that the tag for a Dynamic Interchange Schedule was updated for the next available scheduling hour and future hours which could potentially result in transmission congestion within the BA area and/or across interconnections with neighboring entities. The amount of congestion that could occur is not possible to calculate given the lack of data and the limitless scenarios that could be played out. Additionally, AZPS has had numerous instances in which the tags were not updated when required and is not able to catalog all of the events or their severity. For these reasons, the impact severity is based upon a cascading loss of more than three BES elements of >200kV. The root cause of this issue was lack of compliance understanding. AZPS implemented strong preventative and detective controls to prevent a cascading loss of more than three BES elements of >200kV. Specifically, AZPS implemented real time monitoring of its transmission system via an energy management system (EMS) by NERC certified system operators on a continuous basis. Should transmission congestion begin to occur, the EMS will provide indication by real time quantities and, potentially, alarms for the operators. The operators will then act to mitigate congestion by reducing generation. This is further bolstered by the entity’s training programs and procedures for mitigating transmission congestion. Further, AZPS implemented strong detective controls to detect if a cascading loss of more than three BES elements of >200kV occured. Specifically, it implemented real time monitoring of its transmission system via an energy management system (EMS) by NERC certified system operators on a continuous basis. Additionally, its operators are positioned and trained to immediately respond to any directive issued by the Reliability Coordinator (RC) upon notification of a potential contingency scenario. Furthermore, AZPS implemented procedures for its operators to mitigate any transmission congestion issues by reducing generation and provided training to its NERC certified system operators on the procedures as well as monitoring and alarming tools. As generation is reduced, AZPS’ operators are trained to update the electronic tags relative to the generation reduction amount. For these reasons, and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the reliability of the BPS. | To mitigate this issue, AZPS completed the follow mitigation activities: 1) developed an automated process that accesses future hour forecasted schedule values and automatically updates the dynamic tags every hour. This automation is monitored and alarmed if it should fail; and 2) Developed a training module to instruct the staff on these requirements; the automated process and the manual process to follow should the automation fail. This training module was delivered to all Real-time Traders.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Public Utility District No.1 of Clark County (CKPD) | NCR05334 | WECC2014014463 | PER 005-1 | R1 | During a Compliance Audit conducted from November 3, 2014 through November 14, 2014, WECC determined that CKPD, as a Transmission Operator (TOP) , had an issue of PER-005-1 R1. The audit period for this audit was October 28, 2011 to August 1, 2014. During the onsite audit, the WECC Auditors found a possible issue of PER-005-1 R1. Specifically, PER-005-1 R1 requires CKPD to use a “Systematic Approach to Training (SAT) to establish a training program for the BES company-specific reliability-related tasks performed by its system operators and to implement the program” and R1.1 requires CKPD to “create a list of BES company-specific reliability related tasks performed by its System Operators.” After several data requests and interviews, the WECC Auditors determined that the documentation of CKPD’s SAT is insufficient to meet the intended requirements of PER-005 R1. Firstly, because it does not include documentation of CKPD’s analysis of its training needs, which pursuant to FERC Order 742 is considered the foundational element of a SAT. Secondly, the SAT does not include a documented method for evaluating the program and making improvements as a result of this evaluation. Other than a single sentence at the end of the program document, there was no evidence that this evaluation was performed. The lack of these two things led the audit team to conclude that CKPD did not use a SAT to establish its training program during the audit period. Furthermore, the audit team found that CKPD’s list of 21 Reliability Related Tasks (RRTs) was insufficient as a list of RRTs as required by the PER-005-1 R1. This is because many of the elements in the RRT list are not tasks at all, but internal procedures. Such procedure-based tasks could possibly be viewed as RRTs if they were broken down into constituent tasks, but CKPD provided no evidence of such an approach. Also, 17 of the 21 RRTs are solely related to emergency response. Limiting the tasks to emergency actions excludes a significant number of key tasks that CKPD should consider as reliability related item to be performed during normal operations. As a result, the audit team found that CKPD did not use a SAT to establish its training program and did not create an adequate list of BES company-specific reliability related tasks performed by its System Operators. This information was forwarded to Enforcement for review. Enforcement reviewed the information provided by CKPD and the audit team. Per PER-005 R1 CKPD is required to use a “Systematic Approach to training to establish a training program for the BES Company-specific reliability related tasks performed by its System Operators”. Although CKPD has a documented Training Program, the program’s design and implementation do not rise to the level of a SAT. Specifically, CKPD could not produce documentation to demonstrate how the process was designed and developed. Further. CKPD’s RRTs cannot be described as “tasks”, but consist of general procedures. Therefore, CKPD failed to use a Systematic Approach to Training to establish its training program and has an issue with PER-005-1 R1. This issue began April1, 2013, the date PER-005-1 R1 became enforceable and is ongoing. The root cause is lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CKPD failed to use a Systematic Approach to Training to establish its training program and failed to create a list of BES company-specific reliability related tasks performed by its System Operators. The lack of sufficiently documented process for establishing, implementing, and evaluating its program indicates that its training program is not based on an organized and methodical system. As a result, it seems probable that CKPD’s System Operators do not have the level of training required to maintain BES reliability under all conditions. If the lack of a Systematic Approach to Training persists, the risk to the BES is that human error performed by CKPD’s System Operators will cause, contribute to, or exacerbate a system event. Further, failing to create an adequate list of BES company specific reliability related tasks for its System Operators could lead to the System Operators not receiving regular training on tasks necessary for the reliable operation of the BES. The root cause of this issue was lack of compliance understanding. Although CKPD’s documentation of its SAT is insufficient to meet the intended requirements of PER-005-1 R1, CKPD does employ outside vendors for the provision of the bulk of their System Operator training in addition to participation in annual RC restoration drills and some in-house training. Further, CKPD is relatively small in size. Its service territory covers a single county. CKPD owns 120 miles of 115kV transmission lines and less than ten miles at 69kV with an all-time system peak of 1000 MW. A system failure brought on by a lack of sufficient training would be contained within CKPD’s immediate service area and would be unlikely to have cascading effects that would impact the large interconnecting entities. For these reasons and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the BES. WECC considered CKPD's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CKPD will complete the following mitigation activities by May 15, 2015: 1) amend its Operating Personnel Training Program to ensure that the program's design and implementation rise to the level of a Systematic Approach to Training. Specifically, CKPD will produce documentation that demonstrates how the process was designed and developed (based on a SAT); 2) CKPD will produce a list of its utility specific BES Real-Time Reliability Related Tasks that provide detail regarding activities that its System Operators would be expected to complete (instead of a list of general procedures); and 3) activities will include both emergency activities as well as normal activities expected to be performed regularly as part of the BES operations.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Seattle City Light (SCL) | NCR05382 | WECC2014014497 | INT-009-2 | R1 | On December 11, 2014, SCL submitted a Self-Report stating that, as a balancing authority (BA), it had an issue of INT-009-2 R1. On November 2, 2014, SCL experienced an internet outage. During this internet outage, SCL failed to implement a 1 MW reliability curtailment for eTag SCL PWX01Z507113 CISO. The curtailment was to begin on November 2, 2014 at 1900 and was requested at 1841. The internet provider continued to accept outbound internet traffic from SCL but SCL was not able to receive inbound data. Because of the internet outage, SCL had no visibility of the eTag adjustment at the time, but was automatically approved at 1849 by an Open Access Technology International, Inc., (OATI) “Backstop” service but not actually implemented by SCL until 1940. As a result, SCL did not comply with INT-009-2 R1 for 40 minutes. The WECC Subject Matter Expert (SME) reviewed the information provided by SCL. SCL, as the sending BA, did not agree as to the magnitude of Interchange with the receiving BA for 40 minutes. The actual curtailment of energy (from 150MW to 149MW) was not implemented until internet connectivity was restored around 1940. The SME found that due to the interruption of internet service and the loss of the computer applications that depended on it, SCL failed to have its Composite Confirmed Interchange identical in magnitude to that of the Adjacent Balancing Authority. The SME forwarded this information to Enforcement for review. Enforcement reviewed the information provided by the WECC SME and SCL. Enforcement determined that per INT-009 R1, SCL failed to have its Composite Confirmed Interchange identical in magnitude to that of the Adjacent Balancing Authority. SCL did not agree to the magnitude of interchange with the receiving BA from 1900 to 1940, 40 minutes on November 2, 2014. The root cause of this issue was lack of technology management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SCL failed to have its Composite Confirmed Interchange identical in magnitude to that of the Adjacent Balancing Authority due to a loss of internet communications. SCL, as the sending BA, did not agree to the magnitude of interchange with the receiving BA for 40 minutes. Disagreement in the magnitude of Interchange between adjacent BAs causes the accumulation of inadvertent interchange and incorrect calculation of Net Scheduled Interchange for use in the Area Control Error (ACE) equation or in the worst cause the interconnection facilities could become overloaded. However, the amount of any overload that could occur is not possible to calculate. For these reasons, the impact severity is based upon a loss of a single BES element of >200kV. SCL implemented detective controls. Specifically, SCL implemented 24/7 hour staffing of its System Operations Control Center and Power Marketing operation, which allowed it to quickly notice degradation of certain computer applications and commence alternative actions. It leveraged its Energy Management System (EMS), which is independent of the Internet and provides SCL System Operators full situational awareness of real-time transmission limits, loadings, and alarming during this type of event. Further, SCL implemented strong compensating controls. Specifically, it implemented a redundant Internet Service Provider; however, some manual intervention was required to switch applications between internet systems. SCL had a documented emergency backup procedure, which addressed this type of event. As part of this procedure, SCL sent a WECCNet message informing the region and other BAs of SCL's internet failure requiring manual exchange of information. The backup procedure was implemented, allowing SCL's System Operators to control interchange quantities to the last known good WIT number, then manually exchange and confirm changes with neighboring BAs and PEAK RC. Additionally SCL's NERC certified System Operators are fully-trained to implement the emergency procedure. These measures and the functioning EMS allowed SCL to be aware of any significant curtailments, equipment outages, or large power flow changes occurring during an internet incident so that it could respond timely and accordingly. Based on this information and the fact that no harm was caused, this issue poses a minimal risk to the reliability of the BES. WECC considered SCL's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SCL will complete the following mitigation activities by May 15, 2015: 1) Install additional workstation at System Operations Center connected to alternate ISP (Comcast guest network) as backup internet access point to log into OATI and WIT in the event of a primary or secondary ISP internet outage; System Operators review process for loss of internet and use of alternate connection, and individually log in using backup workstation to test functionality; 2) Install additional workstation at the Power Operations & Marketing (Power Marketing) floor connected to alternate ISP (Comcast guest network) as backup internet access point to log into OATI and WIT in the event of a primary or secondary ISP internet outage; Power Marketing revises its Emergency Preparedness Standard Operating Procedure (Procedure) for loss of internet and use of alternate connection; Real-Time Power Marketers review Procedure, and individually log in using backup workstation to test functionality; and 3) Implement monitoring of OATI on direct T-1 line by Uniform Resource Locator (URL) rather by Internet Protocol (IP) address to allow better monitoring of internet-based connectivity to OATI.
2015-02-26 | Florida Reliability Coordinating Council (FRCC) | Gainesville Regional Utilities (GRU) | NCR00032 | FRCC2014014491 | EOP-004-2 | R2 | During a Compliance Audit conducted from December 1, 2014 through December 3, 2014, FRCC determined that GRU, as a BA, DP, GO, GOP, TO and TOP, had a non-compliance of EOP-004-2, R2. GRU experienced an event which required its primary control center to evacuate and resume operations at its backup facility. However, GRU did not report the event (per their Operating Plan) within 24 hours of recognition of meeting an event type threshold for reporting required per Standard EOP-004-2, R2. GRU's evacuation occured on February 25, 2014, however GRU did not report that the evacuation had occurred until March 12, 2014. The root cause is that GRU failed to recognize that the evacuation of its primary control center required reporting in 24 hours The violation severity level for this noncompliance was determined to be Severe because GRU submitted the event report more than 60 hours after meeting an event threshold for reporting. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. GRU notified the Reliability Coordinator upon evacuating, and arrived at its back up control center within 19 minutes, and were operational at the backup control center within 23 minutes. Additionally, GRU's system only comprises approximately one percent of FRCC Regional transmission, and approximately one percent of the Regional load. No harm is known to have occurred. This is a case by case Compliance Exception and is not related to the Self Logging process. | To mitigate this issue, GRU: 1) GRU reported the event, although the timing was beyond the standard's requirements. 2) GRU provided additional training to its operating personnel on the recognition of reportable events and the timing requirements for reporting such events.
2015-02-26 | Midwest Reliability Organization (MRO) | City of Ames Electric Services (AMES) | NCR00972 | MRO2015014558 | EOP-004-2 | R1 | On November 25, 2014, City of Ames Electric Services (AMES), submitted a Self-Report stating that as a DP and TO, it had an issue of EOP-004-2 R1. AMES failed to update its Event Reporting procedures to include changes made to the new version of the EOP-004 Standard when it became effective on January 1, 2014. The issue began on January 1, 2014 and ended on November 25, 2014 | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk to the BPS of this finding is reduced as a result of: AMES was registered only for the DP and LSE functions until April 1, 2014 when it added the TO function for two 161kV substations. AMES has a peak load of 130MW and less than 35MW of UFLS, which means the only EOP-004-2 “Event Types” that are applicable are Damage or Destruction of a Facility and Physical Threats to a Facility, both of which were covered by AMES’s “Sabotage Reporting Procedure” and included contact information for the entity’s RC and TOP, local police, and the FBI. They were just missing updated contact information for NERC and MRO. AMES had no reportable events, and based upon its size and location, it is very unlikely that AMES could contribute to an event that would have an impact on BES reliability. There is no relevant compliance/violation history for this entity. | To mitigate this issue, AMES developed a new “Event Reporting Plan” which complies with EOP-004-2 R1 on November 25, 2014.
2015-02-26 | Midwest Reliability Organization (MRO) | ITC Midwest (ITCM) | NCR10192 | MRO2013013184 | FAC-008-3 | R6 | On August 28, 2013, ITC Midwest (ITCM) submitted a Self-Certification stating that, as a TO, it had an issue of FAC-008-3 R6. ITCM identified two equipment ratings that were incorrectly documented in its facility rating database. No incorrect facility ratings were identified. The issue began on January 1, 2013 (effective date of standard) and ended on January 15, 2014 (date facility rating database was revised). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The facts and circumstances of this case are consistent with the use of good engineering judgment on behalf of ITCM to focus on the types of equipment, which are predominately the most limiting when calculating facility ratings. This is demonstrated by the fact that the pieces of equipment with rating documentation errors were not the most limiting elements in their facilities. It is also a reasonable assumption that relays and bus conductor would not be the most limiting equipment associated with a facility. ITCM has had no relevant prior violations. | To mitigate this issue, ITCM: 1) updated its facility ratings database to represent existing equipment; and 2) confirmed no facility ratings were impacted. To complete mitigation of this issue, ITCM will perform a comprehensive review of its equipment ratings by December 11, 2015.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Lansing By Its Board of Water and Light (LBWL) | NCR00718 | RFC2014013622 | PRC-005-1 | R2 | On March 4, 2014, LBWL submitted a Self-Report stating that as a Distribution Provider (DP), Generator Owner (GO), and Transmission Owner (TO), it had an issue of PRC-005-1a R2. While gathering evidence for an upcoming NERC audit, LBWL discovered gaps in evidence associated with the implementation of its Protection System Maintenance and Testing Program (Program). These gaps included the completion of only some inconsistent testing of the Instrument Transformers and DC Control Circuity. Out of 735 total tests required by PRC-005-1a R2, 356 were either late or missed. Many of these tests lacked proper documentation and methodology, contained inadequately documented results, and revealed a lack of consistency in interpretation of the testing procedures. In 2011, LBWL revised its Maintenance Practices to require testing of its protective relay systems, communication systems, battery systems, and associated DC circuity and instrument transformers. Following these revisions, LBWL experienced several changes in leadership and key technical positions. This high turnover among the individuals responsible for implementing the revised Maintenance Practices led to inconsistent implementation of the Maintenance Practices and the required testing and documentation. The duration of this noncompliance is from June 9, 2011, the date by which LBWL should have performed its testing, to July 3, 2015, the date LBWL will complete its mitigating activities to remediate this noncompliance by performing the required testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. LBWL employs a comprehensive backup program. This backup program includes primary and back-up phase distance relaying. The primary relays are on one set of current transformers (CTs) and the backup relays are on a different set of CTs. The 138 kV circuit breakers are equipped with dual trip coils. Both the primary and secondary relays initiate the tripping of both breaker trip coils. Having the primary and backup relays on a different set of CTs reduces the likelihood of a Misoperation because if one set of CTs goes down, the relays can still get through on the other set of CTs. In addition, LBWL employs breaker-and-a-half and ring-bus configurations for its 138 kV system, which provides additional reliability and security as those reduce the likelihood of tripping and a Misoperation. LBWL also has a SCADA/EMS system with EMS alarming which monitors station DC battery potential as well as currents and voltages at all 138 kV busses and transmission lines. This monitoring system allows for quick detection and remediation of a potential Misoperation. Finally, LBWL’s entire Bulk Electric System (BES) only consists of a 138 kV loop feeding approximately 300 MW of load that has a minimal impact on the BES. Although LBWL has a prior violation of PRC-005-1 R2, that violation is distinguishable from the instant noncompliance. LBWL’s prior violation occurred in 2008 and arose from an inadvertent scheduling error in testing its relays. The scheduling was in error by a calendar quarter and put the testing out of sync such that 15% of LBWL’s relays were not tested on time. In contrast, this noncompliance stemmed from improper implementation of LBWL’s revised Maintenance Practices and resulted from a combination of leadership changes, changes in testing methodology, and the unavailability of key employees. As a result of the differences in facts and circumstances, ReliabilityFirst did not consider LBWL’s violation history as a factor warranting an alternative disposition method or a monetary penalty. | To mitigate this issue, LBWL will complete the following mitigation activities by July 3, 2015: 1) hired a maintenance engineer with responsibility for reliability compliance to work with LBWL’s Electrical Test Group (ETG); 2) the maintenance engineer worked with the ETG to set up a schedule of tests to bring each facility in violation back into compliance; 3) committed to test any Relays, Communications Systems, Voltage and Current Sensing Devices, Batteries and Chargers, and DC Control Circuitry in violation; 4) the maintenance engineer is responsible for confirmation and review of all tests and filing of all test results; and 5) the maintenance engineer is also responsible for overseeing all LBWL BES facilities’ maintenance responsibilities and ensuring that ETG staff comply with all testing requirements. Mitigation will take until July 2015 because of the number of tests LBWL must conduct and because LBWL is avoiding testing during periods of peak demand.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Ebensburg Power Company (Ebensburg) | NCR08051 | RFC2014014206 | PRC-005-1b | R2 R2.1 | During the Compliance Audit conducted July 16, 2014 through July 24, 2014, ReliabilityFirst determined that Ebensburg, as a Generator Owner (GO) had an issue of PRC-005-1b R2 and R2.1. Ebensburg could not provide evidence that it completed maintenance and testing for its current transformers (CTs) and potential transformers (PTs) from 1990 until 2013. Specifically, Ebensburg had tested its plant’s CTs and PTs during the commissioning of the plant in 1990. After those tests in 1990, Ebensburg did not test its CTs and PTs again until 2013. From 1990 to 2012, Ebensburg’s Maintenance and Testing Program only required testing of CTs and PTs during installation of equipment and when problems were identified with the equipment. Ebensburg’s CTs and PTs did not experience any problems from 1990 to 2012 and therefore were not tested. On April 18, 2012, Ebensburg revised its Program, implemented the Revised Program and changed the testing frequency of the plant’s CTs and PTs to a ten year interval in accordance with NERC requirements. Ebensburg performed the required testing of all CTs and PTs during Ebensburg’s scheduled spring outage from April 21 to April 27, 2013. The duration of this noncompliance is from April 18, 2012, the date Ebensburg revised its Program to change the testing procedures and frequency of the plant’s CTs and PTs, to May 30, 2013, the date Ebensburg completed the testing of all CTs and PTs with supporting documentation to remediate this noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Throughout the duration of the noncompliance, Ebensburg maintained and tested various components of CTs and PTs as part of the routine maintenance and testing of the plant’s electrical systems, particularly the generation protective systems. Although Ebensburg did not conduct the specific CTs and PTs testing on time, the routine maintenance tests and checks Ebensburg conducted decreased the risk posed by the instant noncompliance. Also, the failure rate of CTs and PTs is generally very low. Moreover, the tests, when performed, demonstrated that the CTs and PTs were operating properly. Finally, Ebensburg is a 50 MW generating unit that has a minimal impact on the Bulk Electric System (BES). Although Ebensburg has a prior violation of PRC-005 R2 (See Violation ID No. RFC200800094), that violation is distinguishable from the instant noncompliance. Ebensburg’s prior violation of PRC-005 R2 occurred in 2008, involved Ebensburg missing six months of battery tests, and occurred because of a breakdown in the facility’s preventative maintenance system process which is used to issue work orders for the monthly tests. In contrast, this noncompliance arose because Ebensburg’s Preventative Maintenance and Testing Program in place from 1990 to 2012 did not require interval testing of Ebensburg’s CTs and PTs. As a result of the differences in facts and circumstances, ReliabilityFirst did not consider Ebensburg’s violation history as a factor warranting an alternative disposition method or a monetary penalty. | To mitigate this issue, Ebensburg: 1) performed the required testing of all CTs and PTs, with supporting documentation, during Ebensburg’s scheduled spring outage from April 21 to April 27, 2013; 2) started work on establishing a monthly system to review the latest versions of NERC Standards that apply to Ebensburg as a GO and a Generator Operator. These monthly reviews will identify any changes that may need to be made to keep Ebensburg in compliance with the updated procedures and requirements; and 3) implemented this new monthly check system in October 2014. This system will ensure that Ebensburg continues to test in accordance with testing intervals listed in Ebensburg’s Revised Program and in accordance with the relevant Reliability Standards.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Wheat Field Wind Power Project, LLC (WFWP) | NCR10318 | WECC2014014376 | PRC-005-1.1b | R2 | On October 6, 2014, WFWP submitted a Self-Report stating that as a, Generator Operator and Generator Owner, it had an issue with PRC-005-1.1b R2. In the Self-Report, WFWP reported that it failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1.1b R2. Specifically, WFWP’s Protection System maintenance and testing program in effect during June 2014 required that visual substation inspections were to be conducted monthly. WFWP conducted the monthly inspection for June 2014 nine days outside of the interval described in its maintenance and testing program. As a result, WFWP reported that it had a possible issue with PRC-005-1.1b R2. An audit was conducted WFWP concluding on November 19, 2014. This issue was reviewed by the auditors and was initially dismissed due to WFWP's adoption of PRC-005 version 2 on July 7, 2014, which allows up to four months for battery inspections. As part of NERC’s review of the dismissal, NERC officially rejected the dismissal on December 29, 2014. NERC’s rejection of the dismissal is based on the timeline of the issue. WFWP failed to perform the monthly inspection in June and did not adopt version two until July 7, 2014 or perform the inspection until July 9, 2014. In January 2015, a WECC Subject Matter Expert (SME) began a review of WFWP’s Self-Report. As a result of the examination, the SME determined that WFWP had a possible issue with PRC-005-1.1b R2. Specifically, the SME determined that WFWP failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program. WFWP identified that the root cause of the issue was human error in that the maintenance was simply performed late. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WFWP had an issue with PRC-005-1.1b R2. Specifically, Enforcement determined that WFWP failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1.1b R2. Enforcement determined that the issue began on July 1, 2014, the day that the monthly requirement to perform the visual substation inspection for June expired. Enforcement also notes that the issue ended on July 7, 2014, the date that the entity adopted version 2 of the standard and that WFWP performed the inspection on July 9, 2014. | WFWP failed to provide evidence that Protection System devices were maintained and tested within the defined intervals of its Protection System maintenance and testing program. Specifically, the monthly visual substation inspection for June 2014 was conducted nine days late. If devices are not tested per the program defined by the entity, the devices cannot be certified to operate as planned to interrupt disturbances that may damage the transmission system or generating units. However, WFWP is only a 96.6 MW wind power facility, limiting the effect that it has on the BPS. Additionally, in this instance, WFWP conducted the testing only nine days after the interval described in its maintenance and testing program and this was a single occurrence of missed maintenance. All other required monthly substation inspections were conducted and documented at the correct intervals, limiting the probability of any potential harm to the BPS. WFWP also developed and implemented a plan to transition to PRC-005 version 2 on July 7, 2014, only seven days after the missed maintenance occurred. The intervals of the maintenance performed by WFWP would have been compliant under the new PRC-005 version 2 maintenance and testing plan. For these reasons, WECC determined this issue posed minimal risk to the reliability of the BPS. | To mitigate this issue, WFWP: 1) adopted version 2 of PRC-005 for the battery permitting up to four months for the battery inspection to be completed.
2015-02-26 | Western Electricity Coordinating Council (WECC) | California Independent System Operator (CISO) | NCR05048 | WECC2014014368 | EOP-001-2.1b | R5 | On September 25, 2014, CISO submitted a Self-Report citing possible noncompliance with EOP-001-2.1b R5. Specifically, CISO reported that when it performed its annual review and update of emergency plan, two of CISO’s twenty-two neighboring entities were inadvertently omitted from the distribution list, resulting in those entities not receiving updated copies of CISO’s emergency plans. On November 6, 2014, a WECC SME reviewed the Self-Report and discussed the possible noncompliance with CISO. The SME determined that CISO updated its emergency plans in January, February and December of 2013. After the December update, CISO failed to distribute its new plan to Hetch Hetchy Water and Power (“HHWP”) and Western Area Power Administration–Desert Southwest Region (“WALC”), two neighboring entities that CISO was required to distribute the updated plan to. The SME further determined that the changes made in the December revision were minor. The SME found that CISO had a possible noncompliance with EOP-001-2.1b R5, and forwarded the findings to Enforcement for review. Enforcement reviewed the Self-Report and the SME’s findings and determined that CISO failed to provide a copy of its updated emergency plans to its neighboring Transmission Operators (“TOPs”) and Balancing Authorities (“BAs”). Such failure is a noncompliance with EOP-001-2.1b R5. Enforcement further determined that this issue began on December 23, 2013, the date CISO should have provided its emergency plans to HHWP and WALC, and continued through September 4, 2014, the date that CISO did provide the update to these neighboring entities. | CISO failed to provide a copy of its updated emergency plans to its neighboring BAs/TOPs which could potentially result in a miscommunication between the entities with regard to emergencies. Given that the types of emergencies addressed by the plans are numerous and vary in scope and magnitude, it is impossible to assess the exact impact to the BES. However, given that all neighboring BAs and TOPs did receive previous copies of the emergency plans, and due to the nature of the minor changes in the December revision, the impact to the BES would be limited to misunderstandings of small details associated with emergency response. The root cause of this issue was a failure of controls management. Specifically, as a preventive control, CISO implemented a list of entity names required to receive a copy of the plans within the header of the document. However, the person sending the document did not use the proper email information. As a compensating measure, CISO distributed earlier revisions of its emergency plans to all of the required entities as part of its January and February 2013 revisions. Also, the revisions made in the December 2013 version were minor and non-substantive. For these reasons, and because this issue caused no actual harm, WECC determined this issue posed minimal risk to the reliability of the BES. | To mitigate this issue, CISO: a. created a check sheet that ensures a correlation between email addresses and entity names that will be used to verify each entity is included in the distribution prior to the plan being distributed; b. added a second review, prior to publishing, to ensure that the Reliability Coordinator (“RC”) and all adjacent BAs/TOPs are included on Operating Procedure update email notifications; and c. provided training to the Procedure Control team regarding sharing and coordination practices with the RC and adjacent BAs/TOPs. WECC accepted CISO’s Mitigation Plan on January 29, 2015. CISO completed its Mitigation Plan on October 22, 2014. WECC verified completion of the Mitigation Plan on February 2, 2015.