2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014684 | CIP-002-3 | R3 | SPPRE_URE1 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE1 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE1’s misinterpretation of CIP-002-3. SPPRE_URE1’s Planning Coordinator had informed SPPRE_URE1 that it did not consider SPPRE_URE1, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE1 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE1 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE1 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014699 | CIP-002-3 | R4 | SPPRE_URE1 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE1’s senior manager did not annually approve SPPRE_URE1’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE1 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE1’s misinterpretation of CIP-002-3. SPPRE_URE1’s Planning Coordinator had informed SPPRE_URE1 that it did not consider SPPRE_URE1, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE1 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE1 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE1 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014669 | CIP-002-3 | R1 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE2 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014682 | CIP-002-3 | R2 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE2 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE2 does not own any Critical Assets. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014687 | CIP-002-3 | R3 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE2 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE2 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2015014694 | CIP-002-3 | R4 | SPPRE_URE2 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE2’s senior manager did not annually approve SPPRE_URE2’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE2 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE2 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE2’s misinterpretation of CIP-002-3. SPPRE_URE2’s Planning Coordinator had informed SPPRE_URE2 that it did not consider SPPRE_URE2, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE2 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, because SPPRE_URE2 does not own any Critical Assets, this issue of noncompliance was a documentation deficiency only and no actual harm occurred. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE2 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014670 | CIP-002-3 | R1 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE3 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014683 | CIP-002-3 | R2 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE3 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE3 does not own any Critical Assets. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014688 | CIP-002-3 | R3 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE3 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE3 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2015014696 | CIP-002-3 | R4 | SPPRE_URE3 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE3’s senior manager did not annually approve SPPRE_URE3’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE3 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE3 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE3’s misinterpretation of CIP-002-3. SPPRE_URE3’s Planning Coordinator had informed SPPRE_URE3 that it did not consider SPPRE_URE3, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE3 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM and null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE3 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE3 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014667 | CIP-002-3 | R1 | SPPRE_URE4 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE4 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014680 | CIP-002-3 | R2 | SPPRE_URE4 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE4 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE4 does not own any Critical Assets. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014685 | CIP-002-3 | R3 | SPPRE_URE4 submitted a Self-Certification stating that, as a Generator Owner and Generator Operator, it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE4 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE4 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2015014700 | CIP-002-3 | R4 | SPPRE_URE4 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE4’s senior manager did not annually approve SPPRE_URE4’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE4 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE4 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE4’s misinterpretation of CIP-002-3. SPPRE_URE4’s Planning Coordinator had informed SPPRE_URE4 that it did not consider SPPRE_URE4, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE4 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE4 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE4 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014668 | CIP-002-3 | R1 | SPPRE_URE5 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R1. Specifically, SPPRE_URE5 did not identify or document a risk-based assessment methodology (RBAM) used to identify Critical Assets. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014681 | CIP-002-3 | R2 | SPPRE_URE5 submitted a Self-Certification stating that, as a Generator Owner and Generator Operator, it had a minimal risk instance of noncompliance with CIP-002-3 R2. Specifically, SPPRE_URE5 did not develop a list of its identified Critical Assets determined by its application of a risk-based assessment methodology (RBAM), even though the list would have been a null list as SPPRE_URE5 does not own any Critical Assets. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014686 | CIP-002-3 | R3 | SPPRE_URE5 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R3. Specifically, SPPRE_URE5 did not develop a list of its identified Critical Cyber Assets determined by its application of a risk-based assessment methodology (RBAM) and list of Critical Assets, even though the list would have been a null list as SPPRE_URE5 does not own any Critical Assets or Critical Cyber Assets. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2015014695 | CIP-002-3 | R4 | SPPRE_URE5 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE5’s senior manager did not annually approve SPPRE_URE5’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. SPPRE_URE5 did not have a documented RBAM, and had not developed lists for its Critical Assets or Critical Cyber Assets, even though the lists would have been null lists as SPPRE_URE5 does not own any Critical Assets or Critical Cyber Assets. Therefore, the senior manager had no documents in which to approve annually. The root cause of this issue was SPPRE_URE5’s misinterpretation of CIP-002-3. SPPRE_URE5’s Planning Coordinator had informed SPPRE_URE5 that it did not consider SPPRE_URE5, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE5 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to maintain an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to identify and document an RBAM could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE5 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate the issue of noncompliance, SPPRE_URE5 will: 1) Execute a Memorandum of Understanding, with its parent company whereby it will have RBAM documentation for CIP-002-3 based on the bright line criteria used in CIP-002-5; 2) Review and apply the bright line criteria used in CIP-002-5; 3) Document a critical asset null list that is approved and signed by a Company Officer; 4) Document a critical cyber asset null list that is approved and signed by a Company Officer; and 5) Ensure that it enters a notification for 2016 that activities 2-4 need to be repeated once it implements a document management (Sharepoint) and calendar notification tool (Archer) later in 2015 to prevent recurrence.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 6 (SPPRE_URE6) | NCRXXXXX | SPP2015014697 | CIP-002-3 | R4 | SPPRE_URE6 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE6’s senior manager did not annually approve SPPRE_URE6’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. The root cause of this issue was SPPRE_URE6’s misinterpretation of CIP-002-3. SPPRE_URE6’s Planning Coordinator had informed SPPRE_URE6 that it did not consider SPPRE_URE6, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE6 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to continue maintaining an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to review an RBAM and Critical Asset and Critical Cyber Asset lists could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE6 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE6 will: 1.) Review RBAM and apply methodology. 2.) Have Company Officer sign list of critical assets (should be a null list). 3.) Have Company Officer sign list of critical cyber assets (should be a null list). 4.) Repeat above 1 to 3 for February 2016. In preparation for CIP version 5, a document management tool (Sharepoint) and calendar notification tool (Archer) is being implemented. A notification that this process will need to be repeated in 2016 will be entered into both of these tools.
2015-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 7 (SPPRE_URE7) | NCRXXXXX | SPP2015014698 | CIP-002-3 | R4 | SPPRE_URE7 submitted a Self-Certification stating that it had a minimal risk instance of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE7’s senior manager did not annually approve SPPRE_URE7’s risk-based assessment methodology (RBAM), list of Critical Assets, and list of Critical Cyber Assets. The root cause of this issue was SPPRE_URE7’s misinterpretation of CIP-002-3. SPPRE_URE7’s Planning Coordinator had informed SPPRE_URE7 that it did not consider SPPRE_URE7, a variable generation wind farm, to be critical for purposes of the Planning Coordinator’s Steady State Planning study. SPPRE_URE7 misinterpreted that determination to mean that it did not own any Critical Assets and, therefore, did not need to continue maintaining an RBAM or null lists of its Critical Assets and Critical Cyber Assets. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to review an RBAM and Critical Asset and Critical Cyber Asset lists could result in failing to identify and protect Critical Assets, which could allow such assets to be compromised, leading to the potential loss of Critical Cyber Asset functionality or a complete system failure. However, SPPRE_URE7 does not own any Critical Assets. Therefore, this was merely a documentation deficiency and no actual harm occurred as a result of this instance of non-compliance. No violation history relevant to this issue of noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE7 will: 1.) Review RBAM and apply methodology. 2.) Have Company Officer sign list of critical assets (should be a null list). 3.) Have Company Officer sign list of critical cyber assets (should be a null list). 4.) Repeat above 1 to 3 for February 2016. In preparation for CIP version 5, a document management tool (Sharepoint) and calendar notification tool (Archer) is being implemented. A notification that this process will need to be repeated in 2016 will be entered into both of these tools.
2015-04-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014107 | CIP-007-3a | R5; R5.2.1 | TRE_URE1 submitted a Self-Report to Texas RE and SPP RE stating that it had an issue with CIP-007-3a R5.2.1. Specifically, TRE_URE1 did not change shared account passwords for 17 of its machines prior to placing the machines into service. The root cause of the issue was that TRE_URE1 did not have a documented process to check for a password change before deployment of a computer that was newly imaged. TRE_URE1 had an issue with CIP-007-3a R5.2.1 for approximately nine months. | This issue posed a minimal risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE1’s failure to change passwords on the accounts of the 17 computers prior to deployment could have resulted in a vulnerability that may be exploited to access any part of the system and compromise the reliability of the BPS. However, the risk was mitigated due to the following factors. First, TRE_URE1 has multiple layers of physical security in place to prevent unauthorized access. Second, the systems involved were non-administrator accounts, and the local accounts require direct local access. Also, the shared accounts did not include administrator access. Furthermore, the passwords for the shared accounts are secured and provided to authorized personnel. No actual harm is known to have occurred. Although TRE_URE1 has had previous noncompliance for failing to change passwords on systems before deployment, the instances involved different systems that were deployed by different groups. While the circumstances of the issues are similar, Texas RE and SPP RE determined that it does not warrant an alternative disposition method because TRE_URE1 has implemented measures to prevent future recurrence of this specific issue. | To mitigate this issue, TRE_URE1: 1) changed passwords on the affected machines; 2) updated the procedure and deployment checklist to include a step that confirms passwords have the current year date; and 3) provided refresher training in processes and procedures regarding deploying devices to the ESP. Texas RE has verified the completion of all mitigation activity.
2015-04-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014306 | CIP-007-3a | R5 | TRE_URE2 submitted a Self-Report stating that it had identified two instances of noncompliance with CIP-004-3a R4. Texas RE subsequently determined that the instances of noncompliance should have been submitted as instances of noncompliance with CIP-007-3a R5 rather than CIP-004-3a R4. As a result, Texas RE dismissed the CIP-004-3a R4 issue and a new Self-Report identifying the noncompliance with CIP-007-3a R5 was submitted. TRE_URE2 failed to ensure that shared user accounts and authorized access permissions were implemented consistent with the concept of “need to know” with respect to work functions performed. In addition, TRE_URE2 failed to limit access to systems to those with authorization. The Self-Report contained two instances. With regard to the first incident, TRE_URE2 discovered that an employee shared the password list to all of its Critical Cyber Assets (CCAs) with two individuals who had not been granted authorized electronic access. One of the individuals was a TRE_URE2 employee, and the other individual was a TRE_URE2 contractor. The issue was initially discovered via a software reporting tool on the same day that the TRE_URE2 employee copied the password list from a company laptop to an unencrypted USB drive and provided the passwords list to the two individuals. At the time of the noncompliance, neither co-worker had an active request for this access. Since this instance of noncompliance, TRE_URE2 has authorized the employee’s cyber access but not the contractor’s cyber access. However, the contractor attested that he deleted the password list from his electronic devices. In addition, TRE_URE2 has since changed all the passwords. The TRE_URE2 employee was granted authorized electronic access. TRE_URE2 changed the affected passwords during its normal annual password change process. Regarding the second incident, TRE_URE2 discovered that an employee shared the password list to all of its CCAs with a TRE_URE2 employee who had not been granted authorized electronic access. The issue was initially discovered via a software reporting tool on the same day that a TRE_URE2 employee authorized to access the document provided the USB thumb drive to a co-worker who then copied the list to the co-worker’s computer. The co-worker, who is a TRE_URE2 employee, did not have authorized cyber access at the time of the incident. The TRE_URE2 employee was granted authorized electronic access. TRE_URE2 had an issue with CIP-007-3a R5 for approximately five months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. TRE_URE2 failed to minimize the risk of unauthorized system access which could lead to the introduction of exploitable vulnerabilities in TRE_URE2’s Cyber Assets without its knowledge. TRE_URE2 employees on two different occasions shared passwords to all CCAs with individuals that had not been granted electronic access to CCAs. In addition, the passwords were copied onto an unencrypted USB drive which increased the risk because the data was not protected, and TRE_URE2 would not have been able to track the information in the event it was further copied or shared. Although TRE_URE2 was alerted immediately of the noncompliance, at least in the first instance TRE_URE2 failed to change the affected passwords for almost two months. Furthermore, while TRE_URE2 indicated on the self-report that after the incident it obtained the contractor’s verbal confirmation that he deleted the passwords, TRE_URE2 waited nine months to obtain a formal attestation from the contractor confirming that the password list was deleted from any devices. However, the risk was mitigated by the following factors. First, TRE_URE2 immediately discovered the noncompliances through its Data Loss Prevention tool. Second, the employees and contractor to whom the other TRE_URE2 employees gave the protected information had properly authorized access to the PSP, and they had the same job duties and responsibilities as the authorized employees. Thus, it was less likely that the unauthorized employees and contractor would use the information in a way that would put the BES at risk. Third, in the first instance of noncompliance, it took TRE_URE2 only eight days from the date of the incident to grant the employee authorized access to the CCAs. In the second instance of noncompliance, it took TRE_URE2 only two days to grant the employee authorized access to the CCAs. Finally, the contractor attested that the password list was deleted from all devices, acknowledging that there were no attempts to gain access to CCAs. No harm is known to have occurred. The compliance history for CIP-007 R5 is distinguishable from the noncompliance here. However, unlike the subject noncompliances, most of the previous violations related to failure to change passwords under CIP-007 R5.2 and 5.3. Several issues in one of the previous violations related to TRE_URE2’s failure to conduct reviews of access privileges to local user accounts, but those issues are distinguishable from the instant noncompliances, which relate to individuals improperly sharing information with unauthorized individuals. As a result, Texas RE did not consider TRE_URE2’s CIP-007 R5 violation history as a factor warranting an alternative disposition method. | To mitigate this issue, TRE_URE2: 1) had its supervisors review their employees’ access for protection and control personnel, which is the group involved in the instances of noncompliance, and request access where necessary; 2) updated its current field training relating to the appropriate access that supervisors must request; and 3) had its protection and control employees take the updated training, which includes a complete review of the basic responsibilities relating to CIP processes and procedures. Texas RE has verified the completion of all mitigation activity.
2015-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014263 | CIP-006-3c | R1; R1.1 | WECC_URE1 submitted a Self-Certification stating that, it had a possible instance of noncompliance with CIP-006-3c R1.1. Later, WECC_URE1 reported an additional instance of noncompliance with CIP-006-3c R1.1. The first instance of noncompliance occurred in early 2013, when WECC_URE1 remodeled a Physical Security Perimeter (PSP). During the remodel, WECC_URE1 omitted from the six-wall border two rectangular sections in the north wall mesh above the drop ceiling. The omitted sections measure 16.5” by 7.5” and 16” by 6.5”. The PSP contains non-critical Cyber Assets, consisting of energy management system (EMS) workstations and desk phones. The PSP does not contain Critical Cyber Assets (CCAs). WECC_URE1 discovered the two omitted sections of the PSP. Regarding the other instance of noncompliance, WECC_URE1 added a new PSP. While implementing the six-wall border, WECC_URE1 omitted one rectangular section of the PSP where the ceiling meets the wall. Within this PSP, an iron beam runs along the ceiling 18” away from the wall. The iron beam obstructed the view behind the beam, leading to WECC_URE1’s omission of the rectangular section from the six-wall border. The omitted section measured 18” by 48”. The PSP contains over non-critical Cyber Assets, consisting of EMS workstations and desk phones. The PSP does not contain CCAs. WECC_URE1 discovered the omitted section from the PSP. The root cause of this instance of noncompliance was WECC_URE1's failure to thoroughly inspect before remodeling or building PSPs. | This instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to ensure that all Cyber Assets within an Electronic Security Perimeter resided within an identified PSP. This occurred because WECC_URE1 implemented six-wall borders, but omitted two sections from the six-wall border in one PSP and one section from the six-wall border in a second PSP. This could have allowed malicious individuals to gain physical access to non-critical Cyber Assets. However, WECC_URE1 implemented internal controls to prevent a malicious individual from gaining access and causing damage. The devices in scope were protected by username and password authentication and a separate level of authentication for the EMS application used to view the real-time information. Access points were used to restrict communication into and out of the ESPs. WECC_URE1 also implemented antivirus that likely would have prevented malicious code from being installed. WECC_URE1’s internal controls also included software designed to detect and alert to any changes in the configuration of the devices. Additionally, the devices in scope were not used to give directives to other entities, but were only used for application and tech support. In order to gain physical access to either of the PSPs in scope, a malicious individual would need to enter the main entrance of the building, access the ceiling space through a ceiling hatch in the hall, crawl in the ceiling to the PSP, enter the PSP through one of the holes in the six-wall border, and then drop nine feet from the ceiling to the ground. WECC_URE1 did not discover any access attempts through the PSP holes. As a result, no harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) Updated the physical security plan to require approval of a PSP boundary change prior to the PSP effective date; and 2) Patched the PSP holes.
2015-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013902 | CIP-004-3a | R4.1, R4.2 | WECC_URE2 submitted a Self-Certification stating that, as a Responsible Entity, it had noncompliance of CIP-004-3a R4. WECC_URE2 transitioned to a new contract security service company. As part of the transition, WECC_URE2 compiled a roster of existing contract security officers with access rights to WECC_URE2’s Critical Cyber Assets (CCAs). WECC_URE2 provided the roster to the new contract security company to validate that all security officers on the roster had been hired by the new security company and thus would require continued access to WECC_URE2’s CCAs. If security officers appeared on the roster, but were not hired by the new security provider, WECC_URE2 would remove their physical access rights to WECC_URE2’s CCAs. While compiling the roster of existing contract security officers, WECC_URE2 omitted the name of one security officer. The security officer had physical access rights to Physical Security Perimeters (PSPs). The one security officer in scope was not hired by the new security company and no longer required physical access to WECC_URE2’s CCAs. However, because the name of the security officer in scope was omitted from the roster, the new security company was unable to inform WECC_URE2 that the security officer had not been hired and that their physical access rights should be removed. The new contract security company began providing security for WECC_URE2 and as a result, the security officer in scope no longer required physical access to WECC_URE2’s CCAs. Later, WECC_URE2 conducted a quality control review of its security officer roster and discovered the name of the security officer in scope was omitted from the roster WECC_URE2 sent to the new contract security company. WECC_URE2 revoked the security officer’s physical access rights and updated the CCA physical access list. The root cause of this noncompliance was an individual oversight during the original roster compilation. The noncompliance start date was the eighth calendar day after the change of personnel with access to WECC_URE2’s CCAs. The noncompliance end date was when WECC_URE2 revoked the physical access rights and updated the CCA physical access list. | This compliance exception posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE2 did not revoke access and update its list of personnel who have access to CCAs within seven calendar days of a change in personnel. This noncompliance involved one security officer who was not retained by WECC_URE2’s new contract security company. This noncompliance could have resulted in the individual in scope gaining physical access to CCAs and non-CCAs. The individual in scope could have used physical access to the PSPs to cause damage to the devices or install malicious software. However, the noncompliance and associated potential consequences were limited due to the controls implemented by WECC_URE2. WECC_URE2 did not grant electronic access to the personnel in scope. The devices in the PSPs in scope each had its own username and password. The personnel in scope did not have access to any of the device’s usernames or passwords. The PSPs are monitored twenty-four hours a day seven days a week by the other WECC_URE2 personnel working at the PSPs. This reduces the likelihood that an unauthorized individual would be able to successfully gain logical access and cause damage to the devices within the PSPs. For these reasons, and because no harm is known to have occurred from this compliance exception, WECC determined this noncompliance poses a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE2 revoked the security officer's physical access rights and updated the list of personnel who have access to the CCAs.
2015-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015014547 | CIP-007-3a | R4. | FRCC_URE1 submitted a Self-Report stating that it had an issue applicable to CIP-007-3a R4. Specifically, FRCC_URE1 failed to file a required TFE for three Cyber Assets prior to putting them in-service. Three PLC bridge controllers that are used to collect pressure and temperature data from the turbines went in-service approximately three months before the TFE was submitted. The Cyber Assets are not architected to run antivirus software and were therefore required to be added to a TFE. The original plan was to add the Cyber Assets to the antivirus TFE because the technology, basis and compensating measures are the same. Based on previous FRCC guidance and internal discussions, there was confusion about whether or not there needed to be a separate TFE for these Cyber Assets because one device configuration is different from the other devices, which added to the delayed submittal. The TFE was submitted approximately three months after the Cyber Assets went in-service. The TFE was approved by FRCC one month later. The root cause for this issue was that FRCC_URE1 had an incomplete on-boarding process which would provide ample time for applicable personnel to properly assess the need for the TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Risk was minimized because the Cyber Assets were afforded the appropriate protective compensating and mitigating measures prior to going in-service. The Cyber Assets are not designed to run antivirus software. The Cyber Assets reside in a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP), and do not have access to the Internet. They are protected by access point firewalls with an intrusion detection system (IDS), and electronic access to the Cyber Assets is authenticated by the user’s logged active directory (AD) credentials. Furthermore, the PLC cards have no control function of the Bulk Electric System (BES) and therefore no impact on operations. The PLCs provide data collection of temperature and pressure output of the turbines. If the compensating measures failed the operators would have 15 minutes to respond to the event, thereby minimizing any impact to the BES. Upon the implementation of version 5 of the CIP standards, this TFE will no longer be required because malicious code prevention exists at the system level, active directory (AD), at which there is the ability to deter, detect, or prevent malicious code. No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) Submitted required TFE; 2) Created a checklist of steps for use in onboarding of new Cyber Assets for use in projects.
2015-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015014548 | CIP-007-3a | R6. | FRCC_URE1 submitted a Self-Report stating that it had an issue applicable to CIP-007-3a R6. Specifically, FRCC_URE1 failed to file a required TFE for three Cyber Assets prior to putting them in-service. Three PLC bridge controllers that are used to collect pressure and temperature data from the turbines went in-service approximately three months before the TFE was submitted. The Cyber Assets are not designed to produce security event logs and were therefore required to be added to a TFE. The TFE was submitted approximately three months after the Cyber Asset went in-service. The TFE was approved by FRCC one month later. The root cause for this issue was that FRCC_URE1 had an incomplete on-boarding process which would provide ample time for applicable personnel to properly assess the need for the TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Risk was minimized because the Cyber Assets were afforded the appropriate protective compensating and mitigating measures prior to going in-service. The Cyber Assets are not designed to produce security event logs. The Cyber Assets reside in a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP), do not have access to the Internet, are protected by access point firewalls with an intrusion detection system (IDS), and electronic access to the Cyber Assets is authenticated by the user’s logged active directory (AD) credentials. Furthermore, the PLC cards have no control function of the BES and therefore no impact on operations. The PLCs provide data collection of temperature and pressure output of the turbines. If the compensating measures failed the operators would have 15 minutes to respond to the event, thereby minimizing any impact to the BES. Upon the implementation of version 5 of the CIP standards, this TFE will no longer be required because Security Event Monitoring (logging) exists at the system level, active directory (AD). No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) Submitted required TFE; 2) Created a checklist of steps for use in onboarding of new Cyber Assets for use in projects.
2015-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2015014549 | CIP-007-3a | R5. | FRCC_URE1 submitted a Self-Report stating that it had an issue applicable to CIP-007-3a R5.3. Specifically, FRCC_URE1 failed to file a required TFE for three Cyber Assets prior to putting them in-service. Three PLC bridge controllers that are used to collect pressure and temperature data from the turbines went in-service approximately three months before a TFE was filed. These Cyber Assets do not have accounts in which to change passwords and were therefore required to be added to a TFE. The TFE was submitted approximately three months after the Cyber Asset went in-service. The TFE was approved by FRCC one month later. The root cause for this issue was that FRCC_URE1 had an incomplete on-boarding process which would provide ample time for applicable personnel to properly assess the need for the TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Risk was minimized because the Cyber Assets were afforded the appropriate protective compensating and mitigating measures prior to going in-service. The Cyber Assets do not have accounts in which to change passwords. However, the Cyber Assets reside in a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP), do not have access to the Internet, are protected by access point firewalls with an intrusion detection system (IDS), and electronic access to the Cyber Assets is authenticated by the user’s logged active directory (AD) credentials. Furthermore, the PLC cards have no control function of the BES and therefore no impact on operations. The PLCs provide data collection of temperature and pressure output of the turbines. If the compensating measures failed the operators would have 15 minutes to respond to the event, thereby minimizing any impact to the BES. Upon the implementation of version 5 of the CIP standards, this TFE will no longer be required because System Access Control exists at the system level, active directory (AD). No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) Submitted required TFE; 2) Created a checklist of steps for use in onboarding of new Cyber Assets for use in projects.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014744 | CIP-007-3a | R2; R2.1; R2.2 | NPCC_URE1 submitted a self-report stating that it had an issue with CIP-007-3a R2. Two devices had documentation that indicated associated ports and services should be closed. NPCC_URE1 devices do not have the functionality that allows its services to be disabled. The root cause of the non-compliance was NPCC_URE1's failure to submit a Technical Feasibility Exception for the devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). NPCC_URE1 has a number of mitigation measures to reduce exploitation that include the following; firewalls, host-based firewalls, physical security, local syslogging and intrusion detection. E-Mail and internet access by CCAs (including protected cyber assets) is not permitted by firewall rules, minimizing compromise opportunity. In addition, NPCC_URE1 contracts with a third-party to log and monitor access to the Electronic Security Perimeter (ESP) and provides alerting 24 hours a day, 7 days a week. In addition to the managed monitoring service, NPCC_URE1 employs an intrusion detection system. This system passively monitor NPCC_URE1 network traffic and generate alerts on suspicious activity. The Security Event Manager (SEM) monitors activity and protects from threats and vulnerabilities by collecting and correlating event logs. The SEM provides a console for viewing alerts by the NPCC_URE1 staff. | To mitigate this issue, NPCC_URE1: 1) completed a verification of all ports and services on all Protected Cyber Assets. The current running configuration was compared against the baseline documented in CIP-007 R2 Ports and Services documentation. 2) filed a TFE describing and justifying why NPCC_URE1 cannot achieve strict compliance with the applicable requirement. NPCC has verified the completion of all mitigation activity.
2015-03-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2015014747 | CIP-002-3 | R4 | NPCC_URE2 submitted a self-report stating that it had an issue of CIP-002-3 R4. NPCC_URE2 failed to have their senior manager approve their documentation for CIP-002-3 R4. NPCC_URE2 prepared the documents for signature in but the senior manager was unavailable for signature and the documents were left in a file ready for signature. During the course of the end of the year responsibilities, the documents were misplaced and the senior manager was unable to sign before the end of the year. The root cause of the violation was due to human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The failure to develop a list of Critical Assets and CCAs and have it approved by senior management could potentially result in non-identification and protection of Critical Assets and CCAs. Therefore, critical systems may not be afforded all the CIP protections. NPCC_URE2 is a Generator Owner and based on its RBAM does not have any Critical Assets or CCAs, therefore the entity has no impact to the BPS based upon the application of their RBAM to its assets. NPCC_URE2 has documented and updated their RBAM annually. It has also identified its potential assets and demonstrated its application of the RBAM against all of NPCC_URE2’s assets. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) provided a signed and dated record of senior manager or delegate approval of the necessary documents NPCC has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014370 | CIP-004-3a | R4 | RF_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. RF_URE1 failed to revoke access to Critical Cyber Assets for two students who worked as summer interns within seven days of the end of their internships. RF_URE1 did not submit Out of Service Notification forms and revoke access for these students until 11 days after each of the student’s internships ended. Upon investigation, RF_URE1 determined that there were no access attempts made by either student, or anyone else using their credentials, during the time that the students’ access badges were still active. The root cause of this noncompliance was the failure to follow established company procedures for revoking access to Critical Cyber Assets. The duration of the first instance of noncompliance is from the seventh day following the end of the first student’s internship, to the date on which RF_URE1 revoked that student’s access to the Critical Cyber Assets. The duration of the second instance of noncompliance is from the seventh day following the end of the second student’s internship, to the date on which RF_URE1 revoked that student’s access to the Critical Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the two students had physical access only to a small subset of areas containing Critical Cyber Assets, and never had electronic access to them. Furthermore, the areas in which the student interns were assigned are occupied 24 hours a day by operations personnel. Second, neither of the student’s departures was for cause and each had undergone personnel risk assessments and cyber security training in accordance with the CIP Reliability Standards. | To mitigate this issue, RF_URE1: 1) Counseled the two submitters of the Out of Service Notification requests on the importance of initiating the employee Out of Service request as soon as a firm date is determined so that access can be cancelled within seven calendar days for access to NERC assets; 2) Counseled Corporate Security’s contract security officer on the importance of properly and promptly handing ID cards requiring deactivation; 3) Updated its Out of Service Checklist form to emphasize that Corporate Security should be contacted in addition to sending the employee’s ID card to Corporate Security on the same day the employee separation occurs; and, 4) Issued an awareness notification to all Company supervisors of employees with access to NERC assets reminding them of their responsibility to coordinate with Corporate Security to ensure timely cancellation of access, within 24 hours for personnel terminated for cause and within seven calendar days for any other changes. RF_URE1 also issued similar informational notifications to the employees themselves as well as the supervisory chain of command up through and including Directors. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014345 | CIP-004-3a | R4 | RF_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R4. RF_URE2 indicated that a RF_URE2 supervisor failed to remove physical access for a staff augmentation contractor to two Physical Security Perimeters (PSPs) after the contractor changed job functions within the same Responsibility Center. The supervisor failed to review the contractor’s NERC CIP accesses and revoke those that did not apply to the new job function. The contractor’s new supervisor learned that the contractor’s access to two PSPs was still active during RF_URE2’s access validation review. The contractor’s change in job function did not trigger the automated controls which are in place for access removal when individuals transfer to different Responsibility Centers within RF_URE2. The contractor’s new job responsibilities also required NERC CIP access but to different assets than those protected by the two affected PSPs. The duration of this noncompliance is from the date RF_URE2 was required to comply with CIP-004-3a R4 to the date RF_URE2 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The contractor only had access to two PSPs that were not necessary for his job function. Additionally, the contractor was NERC CIP cleared and did not access the PSPs after the change in job function. The contractor also had a current Personnel Risk Assessment and NERC cybersecurity training at all relevant times: before the job change, during the one month period when he inadvertently retained authorized access rights to the subject PSPs, and after the unauthorized access was revoked. RF_URE2 Corporate Security also reviewed the log files to confirm that the contractor did not access either of the PSPs after his job function changed. ReliabilityFirst considered RF_URE2's compliance history and determined there were no relevant instances of noncompliance | To mitigate this issue, RF_URE2: 1) submitted an SRS ticket to remove the contractor’s access that was no longer required. This request was processed and completed on that same day, thereby removing the contractor’s access to both affected PSPs; 2) counseled both the old supervisor and the contractor’s on-site representative on the importance of checking on an individual’s NERC CIP access when contemplating reassignments; 3) took measures to prevent future recurrences of this issue. These measures included adding a standing agenda item to the weekly status meeting between the staff augmentation contract firm and RF_URE2 supervisors to review any proposed role changes of contractor resources. Any identified planned role changes will trigger review of physical and logical access to better assure unneeded access in the new role is revoked in a timelier manner; and 4) created a daily automatically generated report that is auto-emailed each day to the contract representative and relevant RF_URE2 supervisor. This report shows any person that has a supervisor change. The report is sent out immediately after the Personnel Action Notice process has recorded a change in supervisors and allows for review of physical and logical access and submission of appropriate and timely tickets. Both the daily report and the weekly meeting agenda item will increase awareness of job changes that require changes in NERC access. ReliabilityFirst has verified the completion of all mitigtion activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014348 | CIP-006-3c | R7 | RF_URE2 submitted a Self-Report stating that it had an issue of CIP-006-3c R7. RF_URE2 stated that, on three different dates, the Physical Access Control System hard drive experienced disk errors that resulted in partial file corruption of the logs recording PSP access. On each of these three dates, journal files that were produced in accordance with CIP-006-3c R6 were inadvertently corrupted and only partially recoverable. Therefore, RF_URE2 failed to meet the retention requirement of CIP-006-3c R7 for these three dates. RF_URE2 believes the loss of the journal files is related to disk errors or locked record/delayed writes associated with anti-virus scanning. The duration of this noncompliance is from the date RF_URE2 was required to comply with CIP-006-3c R7, to the date RF_URE2 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The scope of the noncompliance was limited to the damaged journal files on the three specified dates. RF_URE2 was able to partially recover readable information for logging physical access to the various PSPs during the second occurrence. Physical security measures such as monitoring by RF_URE2 Corporate Security Command Center personnel, door locks and alarms, and access card readers remained active during these periods when the files were damaged and thus the PSPs remained protected. ReliabilityFirst considered RF_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE2: 1) ran programs on the affected servers to fix disk errors; 2) increased the memory on the affected servers from 1 gigabyte to 4 gigabytes; 3) modified how antivirus scans were performed on specific folders; 4) replaced the hard drives on both affected servers; and 5) implemented hardware changes to allow the Support Team to perform “Emergency Reboots” of the servers. This ability to reboot will decrease the lead time to troubleshoot technology issues because system reboots can be performed in the event of memory issues or system unresponsiveness; resulting in improved issue resolution time. ReliabilityFirst has verified the completion of all mitigtion activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2014013993 | CIP-003-3 | R6 | RF_URE3 submitted a Self-Report stating that it had an issue with CIP-003-3 R6. RF_URE3 determined that patches were automatically installed without approved change control requests or cyber security testing being completed between two devices. Specifically, a machine reboot was initiated on a device while the device was being fixed. When the device restarted, device patches began automatically installing on that device. On six different dates in 2014, patches were automatically installed without proper change control between the two devices. The patches were supposed to be installed on the devices, but were installed prematurely via an automated process that should have been disabled prior to the device being used. When the patches were installed, neither the approved change control request nor cyber security testing for the patches had been completed. The devices were configured without effective group policy controls that traditionally prevent automated patching. The root cause of this noncompliance was ineffective controls. The duration of this noncompliance is from the date RF_URE3 was required to comply with CIP-003-3 R6, to the date RF_URE3 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. RF_URE3 has been highly cooperative throughout the enforcement process and has been proactive in ensuring future compliance and reliability; and RF_URE3’s mitigation was effective and comprehensive. RF_URE3’s mitigation actions will prevent further issues by ensuring updated processes are in place that prevent automatic patching without proper authorization. Appropriate RF_URE3 staff have been trained on these updated processes to prevent recurrence. ReliabilityFirst considered RF_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE3: 1) disabled Windows Update Service, the process that caused the automated patching to prevent any additional patches from being installed without proper change control. The patches were also removed; 2) ran a vulnerability scan as part of cyber security testing and revalidation to assess whether the installation adversely impacted the devices in any way. The scan showed that all patches, except one, were successfully uninstalled. Per Microsoft, there is no mechanism to remove the remaining patch; 3) researched other technical controls, such as whether a group policy object can be applied to the vendor supplied Windows workstations, in an attempt to prevent recurrence; 4) updated process documentation to ensure the process reflects the necessary steps to properly patch a RF_URE3 device; and 5) conducted reeducation and reinforcement training of the roles, responsibilities, and processes for updating patches for the individuals at RF_URE3 that support these devices. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014013789 | CIP-002-3 | R4 | RF_URE4 submitted a Self-Report stating that it had an issue with CIP-002-3 R4. RF_URE4 failed to keep a signed and dated record of the senior manager or delegate’s approval of its risk-based assessment methodology (RBAM). RF_URE4 performed its RBAM, however, the senior manager did not approve the RBAM, the list of Critical Assets (null), and the list of Critical Cyber Assets (null) until a later date. The duration of this noncompliance is from the earliest date the senior manager could have approved the RBAM, to the date RF_URE4 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. This issue was purely a documentation issue, as RF_URE4 timely completed its RBAM, but failed only to create and retain a written record of its approval. In addition, both the lists of Critical Assets and Critical Cyber Assets were null, reducing the potential harm from a delayed approval of the RBAM. ReliabilityFirst considered RF_URE4's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE4: 1) approved the RBAM, the null list of Critical Assets, and the null list of Critical Cyber Assets; 2) implemented a second tier of internal controls to ensure that plant personnel will be able to maintain and demonstrate compliance with all CIP-002 requirements; and 3) implemented compliance tracking system software that provides notifications to plant personnel to perform annual reviews and complete signatures for CIP-002. If the tasks are not completed and entered into the system by a programmed date, the tasks are escalated to compliance personnel.
2015-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013985 | CIP-002-3 | R1; R1.2 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-002-3 R1.2. SERC_URE1 did not correctly follow its risk-based assessment methodology (RBAM) that is used to identify its Critical Assets. Some of SERC_URE1’s control centers contained assets with the capability to manipulate breakers within two substations through relaying software. SERC_URE1 had relay specific software loaded onto control room workstations designed to provide remote support to the substations at issue. This relay software allowed manipulation of breakers in the substations. SERC_URE1 failed to accurately consider these control centers within its RBAM for multiple years because it incorrectly believed it had removed all control capabilities of all breakers greater than 200kV from its control centers. In reality, some of the control centers retained the ability to manipulate breakers at several substations greater than 200 kV. SERC reviewed SERC_URE1’s RBAMs from the period and found that in each year, the first question of each RBAM was whether the control center controlled any breakers of 100 kV or higher. SERC_URE1 answered ‘no’ to this first question because it believed it had eliminated the ability to control breakers at the affected substations from the control centers. SERC_URE1’s RBAM only required it to further analyze the control centers for Critical Asset consideration if it answered this first question in the affirmative. As such, SERC_URE1 incorrectly excluded the control centers from further Critical Asset consideration after answering ‘no’ to the first question. Because the affected control centers had the ability to manipulate breakers of 100 kV or above, SERC_URE1 should have answered ‘yes’ to the first question of its RBAM for the control centers that contained assets with this relay software. Despite this failure, SERC_URE1’s responses to the remaining questions in its RBAM posed for control centers would not have changed, resulting in the determination that the control centers were not Critical Assets. Thus, the final Critical Asset list would not have changed. SERC determined that SERC_URE1 has an issue with CIP-002-3 R1.2 because it did not correctly follow its RBAM as written. This issue lasted from the day after SERC_URE1 failed to follow its RBAM correctly in one year through when SERC_URE1 completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to follow its RBAM as written could lead it to overlook or fail to properly consider some assets for inclusion as Critical Assets, which could lead to a failure to identify and protect associated Critical Cyber Assets. However, if SERC_URE1 had considered the control centers beyond the first question, SERC_URE1 would have determined that they were not Critical Assets and the list of Critical Assets would not have changed. SERC_URE1 had conducted planning studies in which it removed all 100 kV and above transmission and those studies determined that the bulk electric system would remain stable. The software within the control centers that could be used to manipulate the relays at the affected substations was used by SERC_URE1 for remote engineering support purposes and not for control purposes. The software could only be used to manipulate three total breakers. Lastly, the software resided within control centers that SERC_URE1 staffed with trained system operators 24 hours a day, seven days a week. No harm is known to have occurred. SERC considered SERC_URE1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) removed the ability to manipulate breakers at several substations from within one of the control centers at issue; and 2) formally transitioned to the CIP-002 version 5 standard. As a result the RBAM assessment is no longer completed.
2015-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2014014546 | CIP-002-3 | R4 | SERC_URE2 submitted a Self-Report stating that it had an issue with CIP-002-3 R4. SERC_URE2 reported that the senior manager failed to approve annually the risk-based assessment methodology (RBAM), the list of Critical Assets, and the list of Critical Cyber Assets (CCAs) in one year. During an internal audit conducted as part of its Internal Compliance Program, SERC_URE2 determined that it had not conducted its annual review and approval of the RBAM and null list of Critical Assets and CCAs in one year. SERC_URE2 conducted its prior annual review and approval, but did not conduct the next review and approval until a month after the next annual review and approval should have been conducted, which is outside of both a rolling twelve month period and a calendar year period. The primary cause of this issue was a turnover in personnel responsible for ensuring the annual reviews and approvals occur and a lack of internal controls. When the employee who was responsible for ensuring the annual review and approval changed roles at the company, that employee cancelled the annual calendar reminder that was part of the previous mitigation plan actions and sent the cancellation to the employee who would be taking over that role. The incoming employee failed to create a calendar reminder for the annual review. This issue lasted from the day after SERC_URE2 failed to conduct the annual review and approval, through when SERC_URE2 reviewed and approved the RBAM, Critical Asset list, and CCA list. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to conduct its annual review and approval of the RBAM could have led to recent changes in the entities asset list to be overlooked or omitted from consideration. However, SERC_URE2 does not have Critical Assets. It applied its RBAM in the years prior to and after the missed year, resulting in null lists for Critical Assets. In addition, SERC_URE2 is a minimal size utility that owns a co-generation plant. No harm is known to have occurred. SERC considered SERC_URE2's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the prior and instant issues were of the same Standard and Requirement, SERC_URE2 discovered the instant issue during an internal audit, whereas the prior issue was discovered by a SERC audit team, indicating that SERC_URE2 has strengthened its detective internal controls. In addition, SERC_URE2 was approximately one month late in approving the necessary documents, whereas in the prior issue, SERC_URE2 took over a year to fully resolve the issue. SERC also considered that SERC_URE2 has implemented preventative internal controls as part of its mitigating activities when determining that Compliance Exception treatment was appropriate. | To mitigate this issue, SERC_URE2: 1) had its designated CIP senior manager sign its RBAM, Critical Asset, and Critical Cyber Asset list; and 2) set its annual calendar reminders through the next decade for two separate dates (November and December) for the Primary Compliance Officer, Primary Compliance Contact and Alternate Compliance Contact.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014465 | CIP-004-3a | R4; R4.1 | TRE_URE1 submitted a Self-Log to Texas RE stating that it had an issue with CIP-004-3a R4.1. TRE_URE1 failed to update the list(s) for a single contractor within seven days of a change in personnel with unescorted physical access to two Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs). The issue was discovered as part of a routine quarterly access review conducted by TRE_URE1 pursuant to CIP-004-3a R4.1. A segment of that review compares records in the TRE_URE1 corporate badging system for authorized unescorted physical access to the records in the internal list of personnel for authorized unescorted physical access and identifies discrepancies. Specifically, a contractor was granted physical access in the corporate badging system to two PSPs; however, the list of personnel who have authorized cyber or authorized unescorted physical access rights to CCAs was not updated until eleven days after access was granted. When examining the root cause of this issue, TRE_URE1 identified that the CIP administrator who granted authorized unescorted physical access in the corporate badging system did not recall the seven-day internal list update requirement and made an incorrect decision about how to complete the internal list record upon encountering an atypical issue in the internal list record entry process. TRE_URE1 had an issue with CIP-004-3a R4.1 for three days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. • The contractor had been properly approved by the contractor's management and a TRE_URE1 CIP administrator for the unescorted physical access to the two PSPs. o The Personal Risk Assessment (PRA) for the contractor was recently cleared. o The contractor had recently completed both the CIP training and policy acknowledgement. • This incident is not indicative of a systemic flaw in the TRE_URE1 CIP access granting process. • As part of the Risk Assessment, TRE_URE1 identified what threat could occur as a result of not updating the internal list as necessary. • Such access would pose a very minimal threat because of the following mitigating factors: o The CCAs in the Control Center are in an open office environment and an attempt by an unknown individual to access any of those assets during normal business hours would quickly be noted, challenged and curtailed. o In the unlikely event such activity was not noted or such activity occurred outside normal business hours, the electronic defense-in-depth deployed to protect CCAs has multiple mechanisms by which inappropriate activity would be detected and notifications would be automatically sent to the support team. o The above defense-in-depth mechanisms would also mitigate any comparable access attempts from the Control Center. Texas determined that the instant issue was appropriate for CE treatment. Although TRE_URE1 and its affiliates had prior noncompliance issues with CIP-004, the root causes were different. Additionally, TRE_URE1 has implemented several measures to address the root cause and to prevent recurrence of this specific issue. | To mitigate this issue, TRE_URE1: 1) updated the list of personnel who have authorized cyber or authorized unescorted physical access rights to CCAs; 2) retrained the individual who delayed the internal list update; 3) added an additional flag drop-down box to the internal list in order to prevent delays in completing the process; 4) added a new required comment field to the internal list to allow the entry of follow-up notes or other specifics around access; 5) modified the process document for access additions to add the following: a. On any occasion where the new flag option is selected, the responsible CIP administrator shall create a task reminder in the applicable mailbox for all CIP administrators so follow-up can be pursued if needed; that task reminder is to be set 5 days after the internal list entry was created or modified. b. Once the circumstances are resolved, the flag will be adjusted accordingly; and 6) revised the access request checklist to include setting up the reminder noted above. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2015014648 | CIP-002-3 | R4 | TRE_URE2 submitted a Self-Report to Texas RE stating that it had an issue with CIP-002-3 R4. Specifically, TRE_URE2 cannot produce documentation that the senior manager or delegate approved the risk-based assessment methodology (RBAM), the list of Critical Assets (CAs) and the list of Critical Cyber Assets (CCAs). The root cause was the lack of a backup that assured that the annual approval and documentation preservation was completed. Texas RE determined that TRE_URE2 had an issue with CIP-002-3 R4 for approximately one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to produce a document showing and approving the RBAM, list of Critical Assets, and CCAs could potentially result in a lack of identification and protection of Critical Assets and CCAs. Therefore, critical systems would not be afforded all the CIP protections and could have allowed TRE_URE2’s peak load to be lost or misused. The risk to the reliability of the BPS was reduced by the following four mitigating factors. First, in the prior year, TRE_URE2 identified and documented that they had no Critical Assets or CCAs. Second, TRE_URE2 applied and approved its risk-based assessment methodology, ending the issue period, and stated that it did not have any Critical Assets or CCAs during the issue period. Third, TRE_URE2’s smaller size minimizes the risk to the BES. Specifically, TRE_URE2’s peak demand was less than 140 MW. Fourth, TRE_URE2 had no Special Protection Systems. No actual harm is known to have occurred due to this noncompliance. Texas RE considered TRE_URE2’S compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) approved its RBAM and null CA/CCA lists; 2) instituted a three step process that occurs annually in Outlook directing the delegated person to complete the following actions: • perform annual standard requirements; • obtain annual signatures; • save/file signature pages electronically; and 3) included the above steps in its plans for its new work order system. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012558 | CIP-006-3a | R2 | During a Compliance Audit, WECC determined that WECC_URE1 had an issue with CIP-006-3a R2. During the audit, the WECC Auditors discovered eight (8) Physical Access Control System (PACS) devices or Intelligent Controller (IC) Board Controllers that were incapable of logging system events related to Cyber Security. The auditors verified that there WECC_URE1 did not file Technical Feasibility Exceptions (TFEs) for these 8 Cyber Assets (CAs). Per CIP-006 R2, CAs that authorize and/or log access to the Physical Security Perimeter must be protected from unauthorized physical access and shall be afforded the protective measures specified in CIP-007-3. WECC_URE1 failed to file TFEs per CIP-007 R6.3 for the eight PACS devices. The auditor forwarded this information to Enforcement for review. Enforcement reviewed the information provided by the WECC Auditor. Enforcement determined that WECC_URE1 failed to file TFE’s for 8 PACS devices which were incapable of logging system events related to Cyber Security. This issue began January 31, 2010, the date which WECC_URE1 should have filed its initial TFE for those 8 devices and ended on July 8, 2013, the date WECC_URE1’s TFE’s for those 8 devices were approved. The root cause was lack of internal controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to file TFE’s for 8 Cyber Assets which were incapable of logging system events related to Cyber Security. Failing to file a TFE report for devices that are incapable of monitoring system events related to cyber security implies that WECC_URE1 is unaware of a technical deficiency of these 8 CAs. WECC_URE1 has compensating measures in place to prevent the compromise of the ESP. Specifically, WECC_URE1 implemented a defense-in-depth architecture of physical and logical Cyber Security controls, including internal and external physical security mechanisms with guards, special locks, Close Circuit Television (CCTV), and logical network perimeter and internal Cyber Security control including firewalls, vulnerability scanning tools, Intrusion Detection Systems and a Security Events Management (SEM) system. Thus, even if a potential attacker obtained information from the devices in scope, the attacker would still have to penetrate WECC_URE1’s defenses to utilize the information gained. For these reasons, and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the reliability of the BPS. | To mitigate this issue, WECC_URE1: 1) WECC_URE1 submitted TFE # 2013-WECC-TFE02330 for the 8 PACS devices in scope that are technically infeasible of logging system events related to cyber security. The TFE was approved July 8, 2013; WECC has verified the completion of all mitigation activity.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014454 | CIP-004-3 | R3 | WECC_URE2 submitted a Self-Report stating that it was in possible non-compliance with CIP-004-3a R3. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE2 compliance staff, and determined that WECC_URE2 granted unescorted physical access to an employee without first performing and documenting the results of a PRA for that employee. WECC_URE2 performed a PRA for one employee (“first employee”). Subsequently, WECC_URE2 granted physical access to CCAs, and used the PRA information for another employee (“second employee”) with a similar name as the first employee. When access was granted, WECC_URE2 performed a name search to verify the PRA status, but did not check the unique ID number for a match. At the time, WECC_URE2 did not have a full step-by-step procedure to grant access and verify that the PRA information matched the employee getting access. WECC_URE2 subsequently finished this procedure, but did not discover this issue until later, when WECC_URE2 reviewed the PRA history for the first employee for renewal after seven years. After discovering the error, WECC_URE2 revoked access for the second employee with the similar name. The root cause of this issue of non-compliance is WECC_URE2’s lack of a compliance process, leading to its failure to verify that PRA information matched the employee. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to perform a PRA and document the results for one employee prior to granting that employee unescorted physical access to WECC_URE2 Critical Cyber Assets. The employee had access to various CCAs. This issue of non-compliance posed potential harm to WECC_URE2, because failing to perform a PRA prior to granting unescorted physical access could lead to WECC_URE2 failing to know of an employee's criminal or malicious history. If WECC_URE2 granted physical access to CCAs to an employee with malicious intentions, he/she could physically damage the devices, unplug cables, or attempt to use malware on a USB stick or other device to attempt to gain logical access and control of the devices. WECC_URE2 implements preventative controls that require a user name and password for logical access to the devices, which only employees with authorized logical access would know. The person in this case was only granted physical access. Without logical access, a person with physical access only would require a certain amount of time to gain logical access, if at all. WECC_URE2’s facilities are staffed with authorized personnel 24/7, who would most likely know which employees had authorized physical and/or logical access, and could possibly prevent an unauthorized person from gaining logical access, once inside the facility. WECC_URE2 also uses a subnet system for its devices, separating devices into distinct groups, which would require someone who wanted to inflict maximum damage to compromise multiple devices in order to affect all subnets. WECC_URE2 also uses port plugs on its devices, which could delay/prevent a malware attack using a USB device. WECC_URE2 implements detective controls that would alert WECC_URE2's transmission control center (via alarms) if load changed. Also, if there were any unauthorized logical access attempts into the ESP, an email would be sent to alert personnel, and personnel could have corrected a problem. These alarm controls are tested on a bi-monthly basis to ensure that they are working properly, alerting WECC_URE2 of any unauthorized logical access attempts. As further compensation, WECC_URE2 implements compensating controls, because thefacilities in question are logically separated from one another, so if a malicious person wanted to affect load, it would require compromising either the Control Center, to which the employee in this case did not have access, or each facility individually, which takes time; allowing WECC_URE2 to discover the attack. | To mitigate this compliance exception, WECC_URE2: 1) Revoked unescorted physical access to its Critical Cyber Assets for one employee; 2) Defined steps for reviewing, conducting and reporting CIP PRAs. The steps include searching the human resources database to confirm identity and employment status and also the security screening database, as well as historical files to confirm the CIP PRA elements are complete; and 3) implemented a two-step review process for CIP PRAs. When there are two Personnel Security Consultants (PSC) present, both will review the CIP PRA to ensure it meets the standard requirement and sign off on the file. In the event both PSCs are not available, the Sr. Manager, EEO & Employee Relations will provide the secondary review. The new process has been instituted and documented.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014325 | CIP-006-3c | R7 | WECC_URE3 submitted a Self-Report stating that it had an issue of CIP-006-3c R7. In the Self-Report, WECC_URE3 reported that it failed to retain physical access logs for at least 90 days. Specifically, WECC_URE3’s hard drive experienced disk errors that resulted in partial file corruption of the logs recording Physical Security Perimeter (“PSP”) access on three different dates. In each of these instances, the journal files that were produced in accordance with CIP-006-3c R6 were inadvertently corrupted and only partially recoverable resulting in WECC_URE3 failing to meet the retention requirements of CIP-006-3c R7 for the corrupted logs on these three dates. WECC_URE3 believes the loss of the files is related to disk errors or locked record/delayed writes associated with anti-virus scanning. As a result, WECC_URE3 reported that it had a possible issue with CIP-006-3c R7. A WECC Subject Matter Expert (SME) began a review of WECC_URE3’s Self-Report and spoke with WECC_URE3 personnel. As a result of the examination, the SME determined that WECC_URE3 had an issue with CIP-006-3c R7. Specifically, the SME determined that WECC_URE3 failed to retain physical access logs for at least 90 days, as required by CIP-006-3c R7. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE3 had an issue with CIP-006-3c R7 for failing to retain physical access logs for at least 90 days. Enforcement determined that the issue began the first day that it failed to retain logs for at least 90 days. Enforcement also determined that the issue ended on the date that WECC_URE3 completed its Mitigating Activities. Additionally, Enforcement determined that the root cause of this noncompliance was hardware failure. WECC_URE3 failed to retain physical access logs that recorded the PSP access on three different dates due to the system experiencing hard drive disk errors. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to retain physical access logs for at least 90 days. Failure to retain physical access logs for the required time could potentially result in WECC_URE3 not having an accurate account of who accessed the Electronic Security Perimeters (ESP) via the PSPs during the three occurrences of lost data. This could assist unauthorized personnel in gaining unauthorized access to the PSPs and the ESPs. This could lead to an individual being able to physically damage the EMS workstations and other hardware equipment. WECC_URE3 implemented strong preventative controls to prevent any unauthorized access. Specifically, WECC_URE3 implemented independent local control panels to manage the local doors and badge access readers whether the systems are fully functional or not. This maintained the physical access control list even during the three instances where the hard drives experienced disk errors. Additionally, the scope of the issue was limited to the damaged journal files on the three specified dates. WECC_URE3 was also able to partially recover readable information for logging physical access to the various PSPs during the second occurrence. No harm is known to have occurred. For these reasons, WECC determined this issue posed minimal risk to the reliability of the BPS. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE3: 1) personnel ran programs on the affected servers to fix disk errors; 2) increased the memory on the affected servers; 3) modified how antivirus scans were performed on specific folders; 4) replaced the hard drives on both affected servers; and 5) implemented hardware changes to allow the Support Team to perform “Emergency Reboots” of the servers. WECC has verified the completion of all mitigation activity.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014180 | CIP-002-3 | R4 | WECC_URE4 submitted a Self-Report stating that its CIP senior manager did not sign and date its Risk-Based Assessment Methodology (RBAM) for calendar year 2013. WECC_URE4 had records for two approval dates for its RBAM; one for 2012 and one for 2014, but no review date or approval document for 2013. WECC_URE4’s lists for its Critical Assets (CA) and Critical Cyber Assets (CCAs) are null lists, and have been approved by WECC_URE4’s CIP senior manager. According to WECC_URE4, it applied the procedures set forth in its RBAM when its new Backup Control Center was commissioned in 2013, but failed to conduct a review and acquire approval for the RBAM at that time. The root cause of this compliance exception was human error, and WECC_URE4’s failure to review its RBAM and have it approved by WECC_URE4’s CIP senior manager for calendar year 2013. | This compliance exeption posed a minimal risk, but did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to ensure that its risk-based assessment methodology (RBAM) was approved by its CIP senior manager for calendar year 2013. This instance of non-compliance could have posed a potential risk to WECC_URE4 because failing to approve its RBAM during the 2013 calendar year could potentially result in an RBAM that may not accurately identify facilities, Critical Assets, or Critical Cyber Assets. However, in this case, WECC_URE4’s lists of CAs and CCAs are null, and were appropriately approved by a CIP senior manager for 2012, 2013, and 2014. WECC_URE4 implemented compensating controls, because WECC_URE4 reviewed and approved the Critical Asset (CA) and CCA lists and verified that each list was null. Since the lists of CAs and CCAs did not identify any assets as critical,WECC_URE4 would likely know that it had no CCAs and therefore no devices needed to be protected. | WECC_URE4 remediated this compliance exception when its CIP senior manager approved its RBAM for calendar year 2014. WECC will not require further mitigation activities for this instance of non-compliance.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014527 | CIP-006-2 | R2 | WECC Compliance Auditors conducted an onsite audit of WECC_URE5 to determine WECC_URE5’s compliance with the Standard. The Audit Team reviewed submitted evidence, conducted on-site audit tours, interviews, and data request submittals. The Audit Team submitted a Data Request to obtain a list of WECC_URE5’s approved ports and services on its Physical Access Control System (“PACS”), as well as a list of currently enabled ports and services on those devices. WECC_URE5 responded that its PACS devices do not have any open ports and services, and as such, WECC_URE5 did not have a baseline list. However, while doing site tours the auditors observed a PACS control panel that was connected using an Ethernet LAN connection. To verify that the PACs panel was not using any TCP/IP ports in its communication to the server, the auditors reviewed the device configuration instructions. The auditors found that the PACS type used by WECC_URE5 are configured by default to use a port when using the LAN interface. The Audit Team then issued another Data Request, inquiring into whether WECC_URE5 was aware of the open port, and to provide the business justification for the open port. WECC_URE5 responded to the Data Request and stated the devices do not communicate via the identified port and that the manufacturer had configured the device on site to use a different port. WECC_URE5 provided evidence that the devices were communicating using a routable protocol over the different port. Because WECC_URE5 did not have a baseline of open ports and services for their PACS devices, the Audit Team determined WECC_URE5 had a possible issue with CIP-006-3c R2.2, and forwarded the findings to Enforcement for review. Enforcement reviewed the Audit Teams findings, the audit report, and Data Request responses. Enforcement determined that WECC_URE5 had an open port on certain PACS devices protecting Critical Cyber Assets that was not listed on its baseline. As such, WECC_URE5 has an issue of noncompliance with CIP-006-3c R2.2. | WECC_URE5 failed to properly enumerate and document open ports or services for certain PACS devices protecting CCAs. The root cause of the issue of noncompliance was a failure of technology management. Such failure could result in the improper or lack of protection to those devices not properly documented. Further, having undocumented ports or services results in an inadequate annual cyber vulnerability assessment. However, WECC_URE5 implemented several compensating measures. First, WECC_URE5 implemented an “Electronic Security Perimeter (“ESP”) like” environment that restricts user access to Cyber Assets. WECC_URE5 also implemented an anti-malware product to monitor and protect PACS Cyber assets. Finally, due to the nature of the devices themselves, the likelihood a malicious user having the ability to alter the devices is very low. For these reasons, and because no harm is known to have occurred, WECC determined this issue posed minimal risk to the reliability of the BES. | To mitigate this violation, WECC_URE5 will complete by April 30, 2015: 1) Review its PACS documentation to identify the scope of the existing references to the ACUs within the PACS, as well the existing identification of ACUs on PACS diagrams; 2) Draft additional text for inclusion within its physical security documentation; 3) Identify the ACUs within WECC_URE5s Cyber Vulnerability Assessment documentation; 4) Create a new document focused exclusively on the identification of ACUs and their associated port, so that ACUs benefit from their own separate listing; and 5) Review other relevant documents that support the PACS to confirm that no additional modifications were warranted.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013297 | CIP-004-1 | R3 | During the Compliance Audit, ReliabilityFirst determined that RF_URE1, had an issue of CIP-004-1 R3. RF_URE1 failed to provide evidence of complete personnel risk assessments (PRAs), including seven year background checks and identity verifications for three contractors. Specifically, although RF_URE1 provided redacted PRAs for all sampled vendors and contractors, the records for three contractors failed to show either a seven year criminal check or identity verification. One contractor only showed records going back five years for the criminal check, another had a PRA without an identity check, and the last was believed to have been completed, but the vendor was not able to provide the 2009 records. The duration of this noncompliance is from the start date of the Compliance Audit assessment period, to the date RF_URE1 remediated the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. All three contractors had a lengthy work history with RF_URE1, and RF_URE1 took immediate action, removing access for all contractors involved in the noncompliance until new PRAs or additional evidence could be provided to RF_URE1 by the vendor, to mitigate the risk of the noncompliance and prevent recurrence. ReliabilityFirst considered RF_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE1: 1) provided evidence that it had removed all access for all contractors involved in the noncompliance until new PRAs or additional evidence could be provided to RF_URE1 by the vendor; and 2) revised its PRA process to require that any contractors and vendors provide redacted PRA results before access is granted, a requirement that did not exist prior to the Compliance Audit. ReliabilityFirst verified that these mitigating actions were complete during the Compliance Audit.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013303 | CIP-006-1 | R6 | During the Compliance Audit, ReliabilityFirst determined that RF_URE1, had an issue of CIP-006-1 R6. ReliabilityFirst discovered that several Manual Log Books used as Visitor Logs for access to Physical Security Perimeters (PSPs) contained incomplete information regarding escort and/or visitor names. Specifically, although RF_URE1 provided manual visitor logging records from PSP access points, some of the entries in those logs were missing either the escorting personnels’ signatures or the visitors’ names. The duration of this noncompliance is from the start date of the Compliance Audit assessment period, to the date RF_URE1 remediated the noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the manual logs were incomplete, they were in place and being used. Second, RF_URE1 was able to view video of the PSP access points to confirm the visitors and escorts in question on the incomplete logs, reducing uncertainty about the security of those physical access points even without proper logging. Third, RF_URE1 took immediate action, described in detail in the following paragraph, to mitigate the noncompliance when it was discovered. During the Compliance Audit, RF_URE1 provided evidence demonstrating it identified all missing log information through camera footage at each access point, and provided re-training through emails, meeting, and reminder posters to make employees aware of the importance of completing visitor logs and escorting visitors at all times. ReliabilityFirst considered RF_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE1: 1) provided evidence demonstrating it identified all missing log information through camera footage at each access point; and 2) provided re-training through emails, meeting, and reminder posters to make employees aware of the importance of completing visitor logs and escorting visitors at all times. ReliabilityFirst verified these mitigating activities during the Compliance Audit, including a review of the current manual visitor logs.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013304 | CIP-007-1 | R2 | During the Compliance Audit, ReliabilityFirst determined that RF_URE1 had an issue of CIP-007-1 R2. RF_URE1 provided only a high-level process to ensure only those ports and services required for normal and emergency operations are enabled. Although RF_URE1 provided additional detail to the audit team for the purposes of explanation, its internal process document failed to provide sufficient detail to ensure only needed ports and services are enabled. In addition, RF_URE1 failed to provide sufficient evidence that only needed ports and services are enabled for all Cyber Assets inside Electronic Security Perimeters (ESPs). Although RF_URE1 provided evidence demonstrating that it uses ports and services baseline documents to compare against configuration files, baselines were not available for all Cyber Assets until the second quarter. The duration of this noncompliance is from the start date of the Compliance Audit period, to the date RF_URE1 completed mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although RF_URE1 failed to provide sufficient evidence of its ports and services processes to demonstrate compliance with CIP-007 R2, RF_URE1 did maintain some documentation of configurations and ports and services, and provided sufficient detail to the audit team, although this detail was not documented for the use of RF_URE1 personnel. Second, RF_URE1 had remediated the noncompliance prior to the Compliance Audit, based on results of its Cyber Vulnerability Assessment, indicating that some internal controls are in place to identify and manage risks related to ports and services. ReliabilityFirst considered RF_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, RF_URE1: 1) provided greater detail of how it ensures only needed ports and services are enabled, and committed to revise its process to include these additional details; 2) created ports and services baselines for all Cyber Assets prior to the Compliance Audit; and 3) formed a Configuration Management Working Group to facilitate the development of more comprehensive baseline documentation with enhanced descriptions of the operational need for an open port or service.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014377 | CIP-006-3c | R2.2 | RF_URE2 submitted a Log stating it had an issue of CIP-006-3c R2.2. An internal audit indicated that micro panels (to which card readers, doors, inputs and outputs are physically wired) and workstations should be considered part of the Physical Access Control System (PACS). RF_URE2 has not considered micros or workstations as part of PACS and therefore have not afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3 as defined in CIP-006 R2.2 for workstations, and have not afforded the protective measures specified above excluding CIP-006-3 R4 and R5 for micros. PACS are defined as Cyber Assets that control, alert, or log access to the Physical Security Perimeter(s), exclusive of locally mounted hardware or devices at the Physical Security Perimeter such as motion sensors, electronic lock control mechanisms, and badge readers. RF_URE2's sever has been identified as PACS, but RF_URE2 has not included micros and workstations as PACS. Workstations were not considered PACS because the workstation itself does not control, alert or log access but is a means to access a web-based application that has the ability to remote unlock doors. Because it is a web-based application, every workstation on the wide area network (WAN) could access the application if the user is able to get through the following layers of security: 1. Must be on the RF_URE2 network (If not, must have two-factor authentication) 2. Two-factor authentication to access the firewall 3. Must have an account on the application 4. Must have a specific role within the application to perform remote control. The servers on which the application is hosted follow all requirements detailed in CIP-006-3 R2.2. Micros were not considered PACS because although they have the ability to store logs, there is no mechanism or interface to change badge holder permissions or pull badge access logs directly from a micro panel. The only way to communicate card holder permissions from server-to-micro-to reader is with the corresponding application system. All changes to access permissions must be initiated in the application database. For the micros, there are offices/service centers and substations. For the workstations, the issue implicated all workstations (since the application is web-based). | RF_URE2 determined that this issue posed a minimal risk to Bulk Power System reliability based on the following factors. First, the web-based application can only be accessed through the following layers of security: (1) Must be on the RF_URE2 network (If not, must have two-factor authentication); (2) Two-factor authentication to access the firewall ; (3) Must have an account on the application; (4) Must have a specific role within the application to perform remote control. Second, the only way to communicate card holder permissions from server-to-micro-to reader is with the corresponding application system. All changes to access permissions must be initiated in the application database. As a result of the foregoing, RF_URE2 determined that while the potential existed for compromise to its system, the likelihood of compromise through the micros or workstations was low. | For the workstations, RF_URE2 implemented remote desktop access to the application, changed firewall access rules to only allow virtual machines to connect to server, changed firewall authentication of all users to require SecurID for everyone, and remove request and workflow system from the PACS server. For the substation micros, RF_URE2 put them on the current critical network or collaborated with the group for a separate solution. For the control centers and data centers, RF_URE2 ran ethernet cable from each panel to the server. RF_URE2 will complete the following mitigation activities by December 31, 2015.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012422 | CIP-007-3a | R5 | RF_URE3 submitted a Self-Report stating that it had an issue of CIP-007-3a R5. Specifically, RF_URE3 failed to develop and manage five shared accounts that monitor their system in accordance with CIP-007-3a R.5.1.3, 5.2 and 5.2.2. The shared accounts provide logging functions within the RF_URE3 CIP environment. Internal review of the issue that a change management checklist completed during system implementation identified three (3) accounts and personnel with access, but in a subsequent review, RF_URE3 discovered that there were five (5) accounts not listed. This issue was identified as a result of continued extent-of-condition analysis associated with affiliate entity reported issues and mitigation. The duration of this issue is from the date by which RF_URE3 had five shared accounts for which it failed to comply with CIP-007-3a R5, to the date by which RF_URE3 will complete the Mitigation Plan that will remedy this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The implicated accounts are shared accounts utilized for support to the logging program. Access to the account does not allow for access to the actual assets being logged; the account only provides access to the logs for review of unusual activity. ReliabilityFirst discovered that RF_URE3’s current corporate affiliates, have violations of CIP-007-3a R5. However, the start date for each of the violations began when RF_URE3 was not a corporate affiliate. RF_URE3 has not previously violated CIP-007-3a R5 and therefore ReliabilityFirst did not consider RF_URE3’s violation history to constitute an aggravating factor for penalty and disposition determination. | To mitigate this issue, RF_URE3 will complete the following mitigation activities by June 29, 2015: 1) enable logging on the shared accounts; 2) define process improvements: 3) conduct training on revised processes; and 4) transition to corporate affiliate’s significant change testing program. Mitigtion will take until June 2015 to accommodate quality assurance assessments of the change testing program and conduct training and awareness activities.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014264 | CIP-004-3a | R4 | WECC_URE1 submitted a Self-Report stating that it had an issue of non-compliance with CIP-004-3a R4. For three separate individuals, WECC_URE1 did not revoke access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. WECC_URE1 terminated the first individual and the supervisor locked the identification badge, electronic physical access key card key card and keys in his desk. WECC_URE1 disabled physical access permissions to WECC_URE1’s general office buildings on the key card. WECC_URE1 discovered that physical access permissions to WECC_URE1’s Physical Security Perimeter (PSP) and an additional PSP, both of which are controlled by the the security management system, were still enabled on the key card, and WECC_URE1 disabled the access on the key card. WECC_URE1 updated the list of personnel who have authorized unescorted access to generation CCAs, and removed the individual from the list. WECC_URE1 terminated a second individual, but did not revoke the associated electronic access card until 53 days later. WECC_URE1 removed the physical access permissions to WECC_URE1’s headquarters for a third individual who was an employee of an WECC_URE1 subsidiary, but the physical access permission to the Data Center was not revoked until 24 days later. (However, it should be noted that when WECC_URE1 revoked physical access to the WECC_URE1 headquarters, access was also revoked to the access doors to the Data Center). The root cause of these issues was a lack of compliance understanding, leading to WECC_URE1’s failure to timely revoke access and update its access lists. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to update the access list to the PSP within seven calendar days of a change in personnel per CIP-004 R4.1 and R4.2, for three separate individuals. This issue poses potential harm to WECC_URE1, because failing to revoke access promptly increases the likelihood of a malicious person utilizing the inaccurate access list to gain physical access to CCAs. Specifically an outside individual could steal or gain the WECC_URE1 employee's access badge and use it to gain unauthorized access. Additionally, the formal employee in scope could have used the inaccurate list to lie to the appropriate personnel (Security Guard or HR) and state that the badge was lost to gain a duplicate temporary badge and gain access to the two PSPs. WECC_URE1 implemented preventative controls. Specifically, the individual’s supervisor collected and locked in his desk the identification badge, electronic physical access key card and keys, which would reduce the likelihood of any employee or an outside malicious individual using the former employee's badge to gain access to the two PSPs. In addition, WECC_URE1 also has operators within each PSP who operate the Management System and could have stopped the former employee, or other unauthorized individuals. No harm is known to have occurred from WECC_URE1's failure to control access to its PSPs. | To mitigate this issue, WECC_URE1: (1) revoked access for the first individual, (2) revoked access for the second individual; and (3) revoked access for the third individual.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013489 | CIP-004-1 R3 | R3 | WECC_URE2 submitted a Self-Certification stating that it was in possible non-compliance with CIP-004-3 R3. A WECC SME reviewed the Self-Certification and conducted interviews with WECC_URE2 compliance staff, and determined that WECC_URE2 failed to accurately verify the identity of one janitorial contractor, prior to granting access for that individual to one WECC_URE2 Physical Security Perimeter (PSP). Specifically, the contractor worked for a vendor that conducted an initial clearance for the contractor, and WECC_URE2 granted CIP access to that contractor to WECC_URE2’s PSP. WECC_URE2 compliance staff identified the issue when the individual's existing PRA was nearing expiration and required an update. As part of the update, WECC_URE2 staff noticed a discrepancy between the existing Social Security number and the updated Social Security number for the contractor. After further investigation,WECC_URE2 discovered the contractor intentionally gave a false Social Security number, and immediately revoked access. The root cause of this issue is WECC_URE2’s lack of a compliance process for verifying the accuracy of personnel risk assessment information from its contractors and vendors. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE2 failed to accurately identify the identity of one contractor prior to granting the contractor access to one PSP. Specifically, the contractor fraudulently submitted an incorrect Social Security number when hired, and was then granted physical access to WECC_URE2's primary transmission control center. This issue of non-compliance posed potential harm to WECC_URE2, because failing to accurately verify a contractor’s identity prior to granting access could lead to WECC_URE2 being unaware of the contractor’s actual identity and criminal background history. However, WECC_URE2 implemented controls to prevent an unverified contractor from causing actual harm to WECC_URE2’s CCAs in the PSP. Specifically, the WECC_URE2 PSP in question is staffed 24 hours a day 7 days a week and thus personnel would have likely detected any attempted logical and physical malicious activity. Also, the contractor did not have logical access to CCAs or any devices within the ESP, thus making it difficult to compromise the CCAs or the associated Critical Asset since user credentials are required to gain access. And, WECC_URE2 implemented AV and malware prevention tools on the devices to mitigate the likelihood of a contractor implanting a virus to gain control of or harm the CCAs. WECC_URE2 implemented detective controls for logging and alerting for detected bad password attempts on the assets within the ESP. Thus, if the contractor attempted to gain logical access to the CCA by guessing passwords, WECC_URE2's logging would have detected it and alerted personnel responsible for responding to the alert. | To mitigate this issue of non-compliance, WECC_URE2: (1) revoked the contractor’s access to its PSP, and (2) worked with the contractor to review its corrective action plan related to Social Security re-verification and criminal background checks. WECC verified WECC_URE2’s mitigation plan was complete.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013992 | CIP-005-3a R1 | R1 | WECC_URE2 submitted a Self-Report stating that it was not compliant with CIP-005-3a R1. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE2's compliance staff and determined that WECC_URE2 had failed to follow its change control process for four rule set changes (all unauthorized changes) on one logical access point (two redundant devices) that control logical access into WECC_URE2's control center ESP. The ESP contains approximately 50 to 60 cyber assets of which 20 to 30 are classified as CCAs, including SCADA workstations, operator consoles, test workstations, primary SCADA servers, and AGC and training simulator devices. The rule set changes did not follow the WECC_URE2 change management process nor have proper approval for implementation. An EMS infrastructure firewall administrator enabled changes to a firewall rule set on a ESP electronic access control point, to work around a non-emergency issue on an interface on the firewall. The firewall administrator needed the rule enabled to correct an issue with his VPN profile in order to support on-call remote access into the ESP. The VPN connection allowed remote users to gain remote access into the corporate network and gain access into the ESP after two-factor authentication was performed. WECC_URE2 enabled two more rules. These rule sets only impacted interfaces that do not have interactive access to any ESP and only impacted traffic between DMZs. WECC_URE2 enable a rule on the same ESP access point that controls the DMZ between the WECC cloud access to WECC_URE2, only impacting traffic between the DMZ and the WECC cloud. The root cause of this issue was WECC_URE2’s lack of a compliance process, and its failure to timely implement its access management procedures. | This instance of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE2 failed to follow its change control process for four rule set changes for one access point that controls logical access into WECC_URE2's control center ESP. This non-compliance poses potential harm to WECC_URE2, because its failure to follow established change control procedures on an access point to the primary control center ESP could allow unauthorized, inappropriate, and incorrect changes, introducing vulnerabilities and unrestricted access into the ESP. WECC_URE2 implemented preventative controls, using two-factor authentication at the access point, for any communication from the corporate network into the ESP, preventing an unauthorized user from gaining access into the ESP. WECC_URE2 implemented user credential controls on the devices within the ESP and an additional layer of credentials to access the EMS application on the SCADA devices. It is unlikely that an unauthorized user would know both layers of credentials, and therefore, would not be able to access the CCAs and EMS application within the ESP. WECC_URE2 implemented detective controls, using an IDS sensor on the access point which would detect anomalous activity, and scans originating from the cooperate side of the access point going into the ESP interface of the access point. Also, WECC_URE2's control center is manned 24 hours a day 7 days a week by operators who are stationed on the SCADA devices, and has 24 hours a day 7 days a week logging and monitoring of the access point and devices within the ESP. The operators would likely detect any generation or transmission value changes and would be able to react to and correct changes. The devices would also detect login attempts and generate invalid login attempt alerts to EMS support personnel 24 hours a day 7 days a week. | To mitigate this issue of non-compliance, WECC_URE2 will: (1) review CIP-005 with its EMS personnel; (2) reviewing the current WECC_URE2 Change Control Process for all EMS CIP Cyber Assets; and (3) identify improvements to the current EMS Change Control Process.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013990 | CIP-006-3c R1 | R1 | WECC_URE2 submitted a Self-Report stating that it was in possible non-compliance with CIP-006 R1. A WECC SME reviewed the Self-Report and conducted interviews with WECC_URE2 compliance personnel, and determined that WECC_URE2 failed to ensure that one janitorial contractor was provided unauthorized access by a second janitorial contractor, and did not sign the manual log for entry and exit into one PSP in the control center. Upon discovery of the issue, both janitorial contractors were terminated from the WECC_URE2 account, and all access was revoked. In addition, WECC_URE2 identified another issue of CIP-006 R1. A janitorial contractor entered a WECC_URE2 control center, but did not sign in. A review of the door force alarms via camera showed that the contractor was provided access by a second contractor. Upon discovery of the issue, both janitorial contractors were terminated from the WECC_URE2 account, and all access was revoked. The root cause of this issue is human error, and a lack of understanding by WECC_URE2’s janitorial contractors of WECC_URE2’s security processes at physical access points. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In two instances, janitorial contractors did not comply with WECC_URE2’s physical security plan, did not sign in, and allowed unauthorized access for other janitorial contractors. This issue of non-compliance poses potential harm to WECC_URE2 because failing to follow log-in procedures to the WECC_URE2 control center could potentially result in WECC_URE2 being unaware for a short period of time when contractors are entering and leaving the control center containing WECC_URE2's most important CCAs. WECC_URE2 implemented preventive and detective controls, because the control center was staffed 24 hours a day 7 days a week, and in each case, the contractor was in the line of sight of WECC_URE2 personnel the entire time. Additionally, the CCAs were password-protected and WECC_URE2 had trained the contractors in the proper way to handle CCAs. These controls would likely prevent the visitor from physically damaging the CCAs and also prevent the visitor from gaining logical access and thereby preventing misuse of the AGC. | To mitigate this issue of non-compliance, WECC_URE2: (1) revoked access and terminated the contractors involved; and (2) worked with its janitorial contractor to remove PAC access for the contractors in question; (3) updated the PAC master list; (4) provided compliance training; and (5) submitted a compliance training sign-in sheet as proof of training.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014405 | CIP-004-3a | R4 | WECC_URE3 submitted a Self-Report stating that it was in possible non-compliance with CIP-004-3a R4. The WECC Enforcement Department (Enforcement) determined that on WECC_URE3 granted physical access to one individual, but did not update the access list, as required by the Standard. WECC_URE3 discovered the oversight during a quarterly review of the Physical Access Rights List (who should have access), and the PACS list (who currently has access in the system). WECC_URE3 revoked access for the individual in question, and updated the list. The root cause of these issues of CIP-004-3a R4 is access management, leading to WECC_URE3’s failure to monitor and control access to its Critical Cyber Assets. | This issue posed a minimal risk, and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to maintain its access lists to reflect a change in access for two personnel. Specifically, for one individual, WECC_URE3 failed to update the access list(s) within seven days; and for the second individual, WECC_URE3 failed to revoke physical access within seven days after such access was no longer required. These individuals had access to 3 PSPs, 20 ESPs, 55 CCAs, 16 ACMs, 22 PACs devices, and 2 Cyber Assets. This issue poses potential harm to WECC_URE3, because failing to revoke physical access when such access is no longer necessary could lead to unauthorized use of devices to cause harm to the BES. In this instance, the individuals had physical access to devices in the EMS ESP. With physical access to the EMS devices, a malicious person could plug a USB or CD containing malicious software (malware) into an EMS device that controls WECC_URE3's transmission to attempt to gain logical control of the device. WECC_URE3 implemented preventative controls. Specifically, an individual needs to pass a guard with the access list at the gate, before gaining access to the PSP that contains the EMS ESP. Although one individual still had physical access on his card, he was not on the access list and could not have been able to get past the guard. WECC_URE3 also uses anti-virus software on its devices, which could prevent a malware attack. WECC_URE3 implemented detective controls. Specifically, WECC_URE3 has personnel on site 24 hours a day 7 days a week, and the personnel would detect a malicious attempt to gain logical access to an EMS device through a malware attack. WECC_URE3 also uses anti-virus software to detect a malware attack. Further, WECC_URE3 has video surveillance, which could also detect an attempt to gain unauthorized logical access to an EMS device. Finally, WECC_URE3 uses an Intrusion Detection System (IDS), which, like the anti-virus, could detect a malware attack. WECC_URE3 implemented compensating controls. Specifically, both individuals in question were in good standing at WECC_URE3. WECC_URE3 also has a policy in place that employees cannot plug in any removable media (i.e., USB or CD) to any device. Both employees were up-to-date on training, and as they were both in good standing, there is a low likelihood that either would attempt any malicious activity. | To mitigate this issue, WECC_URE; 1) revoked access for both individuals; and 2) implemented a process to have one person make access right change and a different person to validate changes. WECC has verified the completion of all mitigation activity.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013591 | CIP-003-3 | R4 | WECC issued an Annual Notice of Requirement to Self-Certify. WECC_URE4 self-certified its possible non-compliance with CIP-003-3 R4. A WECC SME reviewed the Self-Certification, issued data requests, and conducted an interview with WECC_URE4 personnel. According to the SME findings, WECC_URE4 failed to assess its adherence to its Critical Cyber Asset (CCA) information protection program, document the results, and implement an action plan to remediate deficiencies identified during the assessment, as required by CIP-003-3 R4. Specifically, WECC_URE4 did not have sufficient evidence to show it had performed a review of its adherence to its CCA information protection program for the 2012 calendar year. WECC_URE4 stated that it had appropriate evidence for all other calendar years including 2013. WECC_URE4 stated that the possible cause of the issue was confusion about responsibilities resulting from a new manager over CIP-003. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the self-certification information and the SME’s findings and determined that WECC_URE4 had an issue with CIP-003-3 R4 for its failure to assess its adherence to its CCA information protection program, document the results, and implement an action plan to remediate deficiencies identified during the assessment. Enforcement determined that the issue began the first day of the year that WECC_URE4 did not have sufficient evidence to show it had performed a review of its adherence to its Critical Cyber Asset information protection program. Enforcement also notes that WECC_URE4 submitted a mitigation plan for this issue and WECC_URE4 completed the mitigating activities. WECC verified completion of mitigating activities. | In this instance, WECC_URE4 failed to assess its adherence to its CCA information protection program during the calendar year. WECC_URE4’s failure to assess its adherence to its CCA information protection program could lead to WECC_URE4 not knowing if its personnel understood and were following its program to protect sensitive information associated with CCAs. If WECC_URE4 personnel were not following its program, unauthorized individuals would have the potential to gain access to sensitive information and could use that information to attack WECC_URE4's controls. WECC_URE4 implemented good preventive controls to prevent unauthorized individuals from gaining access. Specifically, WECC_URE4 stated that its process ensures sensitive information is classified and has the confidential watermarking. WECC_URE4 also stated that its process ensures that all hard copy sensitive data is stored under lock and key. WECC_URE4’s process ensures that all soft copy sensitive data is stored on secure drives, for which access is only given to individuals with proper approval. Additionally, WECC_URE4 requires that a written form be filled out and approved if an individual needs to gain access to sensitive information. WECC_URE4 also requires individuals to meet PRA and CIP Training requirements prior to gaining access to sensitive information and for contractors to have a non-disclosure agreement. WECC_URE4 also implemented good detective controls to detect unauthorized individuals from gaining access. Specifically, WECC_URE4 tracks individuals that have access to sensitive information in its CIP PI Database. WECC_URE4 generates quarterly reports from its CIP PI Database and reviews the information to ensure that only necessary individuals maintain access. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 completed the following mitigating activities: Establishment of a notification to the Process Owner of the Standard, reminding them of the requirement to document the adherence to the CCA information protection program. This was done using task management software. Notification will be recurring and has an attached escalation feature to notify others if not completed in advance end of the year. Review of adherence to the program will be integrated into WECC_URE4's routine CIP Process Owner meetings that occur monthly throughout the year. WECC has verified completion of WECC_URE4’s mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014121 | CIP-006-3c | R1 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-006-3c Requirement 1. In the Self-Report, WECC_URE4 reported that it failed to prohibit inappropriate use of physical access as required by CIP-006-3c R1.4. Specifically, WECC_URE4 granted physical access to the Backup Control Center (BUCC) that contained ten Energy Management System (EMS) workstations to four contractors. The individual granting access to this Physical Security Perimeter (PSP) accidentally gave physical access to an entire group instead of only the appropriate individuals within the group. This allowed four unauthorized contractors to have unescorted physical access to the BUCC. As a result, WECC_URE4 reported that it had a possible issue with CIP-006-3c R1. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-006-3c R1.4. Specifically, the SME determined that WECC_URE4 failed to prohibit inappropriate use of physical access as required by CIP-006-3c R1.4. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-006-3c R1.4. Specifically, Enforcement determined that WECC_URE4 failed to prohibit inappropriate use of physical access as required by CIP-006-3c R1.4. Enforcement also notes that WECC_URE4 submitted a mitigation plan and WECC_URE4 completed the mitigating activities. | WECC_URE4 failed to grant access to only authorized individuals. Specifically, WECC_URE4 granted four contractors physical access to the BUCC that contained ten EMS workstations. The unauthorized access of the four contractors had the potential to be used to gain physical access to the BUCC and damage or destroy the 10 EMS workstations. The unauthorized access could also allow the four contractors to log into the EMS workstations and attempt to insert a worm or virus that could impact the network or functionality of the workstations. The four contractors also could potentially work with a disgruntled employee who had access to the BUCC and was willing to share his or her account information to gain logical access and attempt to remotely access the EMS workstations within the Primary Control Center (PCC). WECC_URE4 implemented good preventative controls to prevent the physical access from occurring. Specifically, WECC_URE4 never granted logical user access to the ten EMS workstations within the BUCC to the four contractors. WECC_URE4 also implemented redundant EMS workstations in the PCC to reduce the negative impact of one or all of the EMS workstations being damaged or destroyed within the BUCC. Additionally, WECC_URE4 also maintains the PCC and BUCC in an active and passive state respectively, meaning the BUCC could not become the PCC until the PCC was either shut down or unavailable. WECC_URE4 disabled the ability to run mass storage devices on the EMS workstations to prevent the installation of malicious software. WECC_URE4 also implemented detective controls to detect the unauthorized physical access from occurring. Specifically, WECC_URE4 implemented processes to investigate suspicious activity on the EMS workstations. If a contractor was given a valid user account and password, the account logs would track the valid user's activity on a daily basis. WECC_URE4 also implemented anti-virus software that would send an alert message to the appropriate personnel if malicious software was detected. Additionally, WECC_URE4 has quarterly reviews of employees and contractors that have full access to the BUCC to limit the likelihood that unauthorized access to the EMS workstations is undetected. WECC_URE4 discovered this issue during one of these quarterly reviews. As another detective control, WECC_URE4's badges are color coded based on several factors, including whether the individual is an employee or contractor and whether the individual has full or restricted access. Employees can detect whether someone should be in the BUCC based on the color code. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 completed the following mitigating activities: WECC_URE4 removed the PSP doors from the four contractor’s access profile. WECC_URE4 parsed the existing physical control system into two separate physical systems, one for CIP (PACM) operation and the other for business operation. This will in turn separate the administrative tasks/entries which will prevent or minimize the potential for future access modification errors. WECC has verified completion of WECC_URE4's mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014391 | CIP-006-3c | R2 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-006-3c R2. In the Self-Report, WECC_URE4 reported that it failed to use passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Specifically, WECC_URE4 failed to file a Technical Feasibility Exception (TFE) for three PACS devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3 under CIP-006-3c R2. As a result, WECC_URE4 reported that it had a possible issue with CIP-006-3C R2. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-006-3c R2. Specifically, this possible issue was originally part of NERC Violation ID WECC2014013931. The original scope of NERC Violation ID WECC2014013931 consisted of 27 devices: 24 EACM devices and 3 PACS devices. The WECC SME determined that the PACS devices should be removed from the scope of NERC Violation ID WECC2014013931 and should be a separate possible issue under CIP-006-3C R2. The SME determined that WECC_URE4 failed file a TFE for three PACS devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3 under CIP-006-3c R2. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-006-3c R2. Specifically, Enforcement determined that WECC_URE4 failed to file TFEs for three PACS devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3 under CIP-006-3c R2. Enforcement determined that the issue began on the day that CAN-0017 was issued, verifying that a TFE needs to be filed to show compliance in enforcing password complexity for devices that cannot fully meet all requirements. WECC_URE4 is currently in the process of submitting a Mitigation Plan; however, prior to creating the new possible issue, WECC_URE4 had submitted a Mitigation Plan for NERC Violation ID WECC2014013931, stating mitigation was completed on or before September 30, 2014. The mitigation plan was accepted. At the time the Mitigation Plan was submitted, the three PACS devices were still within scope of NERC Violation ID WECC2014013931. | In this instance, WECC_URE4 failed to use passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Specifically, WECC_URE4 failed to file a TFE for three PACS servers that are incapable of enforcing the password complexity requirements. The servers manage door operations. Failing to file a TFE for devices not technically capable of enforcing password complexity requirements could lead to WECC_URE4 not knowing of vulnerabilities on those devices. As compensation for any vulnerability with these devices, WECC_URE4 implemented strong compensating controls. Specifically, WECC_URE4 has a manual procedure by which the changing and validation of password complexity is observed and signed off on by the appropriate supervisor. WECC_URE4 also has a procedure written that defines the requirement of CIP-007 R5.3.1 and CIP-007 R5.3.2. Utilizing the Vendor Firmware, and HP iLo to proctor the requirements with the manual procedure ensures compliance. In addition, WECC_URE4 has logging, monitoring, and alarming on all account activity within the systems affected. WECC_URE4 also controls access through authorization and accounting and provide appropriate ports and services controls, patch management, and malicious software prevention tools. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 has not yet submitted a Mitigation Plan to address this issue. WECC_URE4 is required to submit a plan for mitigating this issue. However, prior to creating the current possible issue, WECC_URE4 had submitted a Mitigation Plan for NERC Violation ID WECC2014013931 and at the time the Mitigation Plan was submitted, the three PACS devices were still within scope of NERC Violation ID WECC2014013931. In that mitigation plan, WECC_URE4 stated it completed the following mitigating activities: WECC_URE4 submitted evidence of the performance of the CAN-0017 TFE submitted to cover the assets not capable of the Technical Controls. WECC_URE4 also submitted evidence of password change and account renaming where applicable. WECC verified completion of the mitigating activities associated with WECC2014013931.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013935 | CIP-007-3a | R4 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-007-3a R4. In the Self-Report, WECC_URE4 reported that it failed to use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter (ESP) by failing to file Technical Feasibility Exceptions (TFEs) on or before the date the devices were installed. Specifically, WECC_URE4 failed to amend its original TFEs when adding three new devices to an ESP. The three devices that WECC_URE4 failed to file TFEs for are Cisco switches that are used to manage WECC_URE4’s ESP. As a result, WECC_URE4 reported that it had a possible issue with CIP-007-3a R4. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-007-3a R4. Specifically, the SME determined that WECC_URE4 failed to use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the ESP by failing to file TFEs on or before the date the devices were installed. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-007-3a R4. Specifically, Enforcement determined that WECC_URE4 failed to use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the ESP by failing to file TFEs on or before the date the devices were installed. Enforcement determined that the issue began the day that WECC_URE4 installed the switches without filing the TFEs. | WECC_URE4 failed to amend its original TFEs when adding three new Cisco switches to an ESP. Failing to submit TFEs for new devices could result in misidentifying the critical role or function that these devices serve to the ESP. The two ESPs in scope contain devices that are essential for WECC_URE4 to reliably operate its EMS, which manages WECC_URE4's area load peaking, with 19 interconnections to neighboring BAs. WECC_URE4 implemented strong preventative controls to prevent the weakening of the ESP security. Specifically, WECC_URE4 implemented two primary and one backup Cisco switches that have an embedded layer of security within the operating system (IOS). The Cisco switches also have intelligence within the IOS to prevent unknown Media Access Control (MAC) addresses from connecting to the network preventing an unauthorized user with a laptop to connect to the switches. WECC_URE4 also implemented strong detective controls to detect the weakening of the ESP security. Specifically, WECC_URE4 implemented a Security Information and Event Management (SIEM) that is used to monitor various network devices, such as firewalls, switches, and routers within the ESP. If an unauthorized user installed a virus into the ESP, the current detective and preventive measures would likely block the virus or other malicious code from causing harm. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 stated that it completed the following mitigating activities: WECC_URE4 submitted evidence of the performance of the vulnerability assessment in 2013 as well as provided a current “baseline” of authorized ports and services for the three switches. WECC_URE4 staggered deployment by using standby/testing systems for testing of new AV signatures. WECC has verified completion of this mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013931 | CIP-007-3a | R5 | WECC_URE4 submitted a Self-Report identifying a possible issue with CIP-007-3a R5. In the Self-Report, WECC_URE4 reported that it failed to file a Technical Feasibility Exception (TFE) for devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters, as required by CIP-007 R5.3. As a result, WECC_URE4 reported that it had a possible issue with CIP-007-3a R5. A WECC Subject Matter Expert (SME) began a review of WECC_URE4’s Self-Report, spoke with WECC_URE4 personnel, and issued data requests. As a result of the examination, the SME determined that WECC_URE4 had a possible issue with CIP-007 R5.3. Specifically, the SME determined that WECC_URE4 failed to file a TFE for devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. WECC_URE4 failed to file the TFEs for 24 Electronic Access Control and Monitoring (EACM) devices that are incapable of enforcing the password complexity requirements required by CIP-007 R5.3. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WECC_URE4 had an issue with CIP-007 R5.3. Specifically, Enforcement determined that WECC_URE4 failed to file a TFE for devices that are technically incapable of using passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Enforcement determined that the issue began on the day that WECC_URE4 failed to file a TFE to show compliance in enforcing password complexity for devices that cannot fully meet all requirements. | WECC_URE4 failed to use passwords that are at least six characters long and consist of alpha, numeric, and "special" characters. Specifically, WECC_URE4 failed to file a TFE for 24 EACM devices that are incapable of enforcing the password complexity requirements. Failing to file a TFE for devices not technically capable of enforcing password complexity requirements could lead to WECC_URE4 not knowing about vulnerabilities on those devices. WECC_URE4 implemented strong compensating controls to compensate for these devices. Specifically, WECC_URE4 has a manual procedure to observe and obtain approval by the appropriate supervisor the change and validation of password complexity. WECC_URE4 also has a procedure that defines the requirement of CIP-007 R5.3.1 and R5.3.2. Utilizing the vendor firmware to proctor the requirements with the manual procedure ensures compliance. WECC_URE4 also has logging, monitoring, and alarming on all account activity within the systems affected. Additionally, WECC_URE4 controls access through authorization, accounting, providing appropriate ports and service controls, patch management, and malicious software prevention tools. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 stated that it completed the following mitigating activities: WECC_URE4 submitted evidence of the performance of the CAN-0017 TFE submitted to cover the assets not capable of the Technical Controls. WECC_URE4 also submitted evidence of password change and account renaming where applicable. WECC has verified completion of this mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014000 | CIP-009-3 | R1 | WECC conducted on Combo On-site Audit of WECC_URE4’s facilities. At the Audit, the WECC Audit Team identified a possible issue of CIP 009-3 R1. The WECC Audit Team determined that WECC_URE4 failed to annually review the recovery plan. Specifically, WECC_URE4 created a recovery plan for Critical Cyber Assets. The recovery plan addressed the minimum criteria outlined in each sub-requirement of Requirement 1, but WECC_URE4 did not review the plan. WECC_URE4 changed its process from including annual reviews in the revision history to using the DocMinder system. WECC_URE4 had one DocMinder task for both annual review of the plan and annual exercise of the plan. WECC_URE4 separated those processes into two separate tasks within DocMinder. Based on a review of an audio file of the exercise of the plan and the DocMinder output, the WECC audit team determined that there is no evidence that the plan was appropriately reviewed. This resulted in WECC_URE4 having a possible issue of CIP 009-3 R1 for failing to annually review the recovery plan. The Audit Team forwarded its findings to Enforcement for review. Enforcement reviewed the Audit Team’s findings and determined that WECC_URE4 had an issue with CIP 009-3 R1. Specifically, Enforcement determined that WECC_URE4 failed to annually review the recovery plan. Enforcement determined that the issue began the day that after one year from the last review of the plan. Enforcement also determined that the issue ended the date that WECC_URE4 annually reviewed the plan. | WECC_URE4 failed to annually review the recovery plan. Specifically, WECC_URE4 created a recovery plan for Critical Cyber Assets. The recovery plan addressed the minimum criteria outlined in each sub-requirement of Requirement 1, but WECC_URE4 did not review the plan. WECC_URE4 owns and operates two Hydro Electric facilities with 10 generators at each facility, with an aggregate capacity of about 2000 MW. Additionally, WECC_URE4 operates two hydro units off irrigation canals. Despite WECC_URE4’s failure to review the recovery plan, WECC_URE4’s recovery plan is well documented and there were no substantial changes impacting the plan during the noncompliance time frame. Annual exercises of the plan were also conducted each year, even though the plan was not reviewed. The issue caused no actual harm. For these reasons, WECC determined this issue posed a Minimal risk to the reliability of the BES. | WECC_URE4 completed the following mitigating activities on: A task notification that details the recovery plan sections under review and confirms the performance of the review will be dispatched as a recurring reminder on an annual basis. A Review block will be incorporated to the Recovery Plan showing the date of annual review. WECC has verified completion of this mitigation plan.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014097 | CIP 007-1 | R2 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R2. During this time,WECC Auditors were conducting a review of WECC_URE5’s compliance with CIP-007-1 R2. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert also reviewed WECC_URE5’s self-report and found that it failed to enable only those ports and services required for normal and emergency operations. Specifically, WECC_URE5 failed to submit a complete list of TFE’s for 5 devices in scope. These devices are SCADA workstations and logical controllers. The WECC SME forwarded this information to Enforcement for review. Enforcement reviewed the self-report and the SME findings. Enforcement determined WECC_URE5 failed to enable only those ports and services necessary for normal and emergency operations. Further, WECC_URE5 failed to submit a complete list of TFE’s that include the 5 devices in scope. The root cause was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to enable only those ports and services necessary for normal and emergency operations. Specifically, WECC_URE5 failed to submit a complete list of TFE’s for 5 devices in scope. Failing to submit TFEs in a timely manner could result in the proper compensating measures not being applied to the SCADA system. Since these devices cannot disable unnecessary ports, WECC_URE5 may be unaware of all the ports the devices use and which ports may be vulnerable to attack. Also, the access point may not be setup correctly to compensate for the unnecessary ports and allow unnecessary communication into the Electronic Security Perimeter (ESP). On the other hand, WECC_URE5 implemented some compensation controls such as placing these devices in a physically secure location. Only authorized personnel have access. The network containing these devices is monitored by the WECC_URE5 IDS system and network services provided to these devices are controlled by a role-based policy system. Further, WECC_URE5 developed, documented, and implemented procedures to address ports and services from both a physical network port perspective and from a TCP and UDP ports and services perspective. This procedure is contained in the “CIP-007 System Security Management Program” document, Section 8.2. It is WECC_URE5’s commitment to ensure that only those ports and services required for normal and emergency operations are enabled when an asset is in service within the Electronic Security Perimeter. The procedures contained in Section 8.2 is provided to WECC_URE5 staff to guide their actions based on a “locked-down” approach that does not compromise necessary functionality or system availability. Also, per CIP-007 R2.1, it is WECC_URE5’s intent that all Secure Networks role assignments be made in such a way that they deny access by default, so that explicit permissions must be specified. The default role for each physical port in WECC_URE5’s network shall be “New User Lockdown”, unless it is a purpose-specific port (not a regular user port) and authentication must be enabled. To the extent that it is technically feasible, the assignment of default roles for ports shall be made prior to the deployment of the equipment for production use. When setting up new Critical Cyber Asset software or hardware at WECC_URE5, it is required that all unused services and ports are disabled. Starting from a complete locked-down approach allows for only the required services and ports to be enabled. For computer-based assets, WECC_URE5 personnel evaluate the necessary ports and services required for operations (with Vendor input), and disable those who do not meet criteria for the application. For non-computer-based assets, staff assesses what ports and services must remain enabled based on their review of the configuration screens on the device. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) submitted a request for TFE #2014-WECC-TFE02513 on 6/26/2014 to cover three devices and 2014-WECC-TFE02507 on 6/25/2014 to cover two devices; 2) implemented a tracking spreadsheet showing all requirements for which a device might have a technical infeasibility, and all devices will be evaluated before deployment, and; 3) involved more of its personnel in the compliance procedure development process to further enhance a culture of compliance. WECC has verified the completion of all mitigation activity.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014013956 | CIP 007-1 | R3 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R3. During this time, WECC Auditors were conducting a review of WECC_URE5’s compliance with CIP-007-1 R3. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert (SME) also reviewed WECC_URE5’s self-report and issued a data request to further clarify information about the devices in scope. The WECC SME found that WECC_URE5 failed to file a TFE for (4) devices consisting of an RTU, two plant voltage control and monitor devices, and a workstation that can control the total plant load. The entity also failed to document applicability of security patches for six devices, consisting of two control room interface devices for plant status, control, and alarming; one interface development device, one PACS server, and two PACS workstations. The entity also failed to check for security patches for 17 devices, consisting of two control room interface devices for plant status, control, and alarming; one interface development device, one PACS server, two PACS workstations, nine PACS panels, one device that controls breaker status, relay alarms, and other plant statuses; and one device that controls transformer status and alarms, station service status and alarms, and other plant statuses. As a result of these findings, the WECC SME found that WECC_URE5 failed to document and implement a security path management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter (ESP). The WECC SME forwarded these findings to Enforcement for review. Enforcement reviewed the information provided in the self-report and from the WECC SME and determined that WECC_URE5 failed to document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESP either separately or as a component of the documented configuration management process specified in CIP 006 R6. Further, WECC_URE5 failed to file a TFE for four devices, failed to document applicability of security patches for 6 devices, and failed to check for security patches for 17 devices. The root cause of this issue was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESP either separately or as a component of the documented configuration management process specified in CIP 006 R6. Failing to document and implement a security patch management program could lead to vulnerabilities on devices because patches were not applied. If a malicious person knew of new patches that fixed vulnerabilities (something that can be deduced by looking at the patch information), he or she could scan devices on the network in order to obtain information about the device, specifically the version of software on the device (what is updated by a patch or upgrade). If the person is able to obtain this information, he or she could know if a patch or upgrade has been applied. If a scanned device is discovered to not have had the latest patch or upgrade applied, the person could use malicious software to exploit that vulnerability in attempt to take control of the device. In this case, two of the devices in scope are sources for the Plant Load Set Point. WECC_URE5 implemented strong preventative controls to prevent the above consequence from occurring. Specifically, it implemented MAC-based authentication, where any device with an unknown MAC address is locked down to prevent it from communicating with any of the devices on the network until the MAC address is authenticated. This would prevent someone from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which would help prevent someone from remotely attempting to send attack packets through to the devices on the network. Furthermore, WECC_URE5 also implemented strong detective controls to detect the above consequence. Specifically,WECC_URE5 has operators manning the PSPs 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, WECC_URE5 would likely correct the condition as WECC_URE5 implemented strong corrective controls. Specifically, WECC_URE5 operators have the ability to switch the plant into 'Manual' mode, which prevents any control from cyber devices. WECC_URE5 also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, WECC_URE5 set up the two Plant Load Set Point sources (see above) to be independent of one another. Therefore, if one device were to be compromised, WECC_URE5 could switch to the other device to manage the set point. WECC_URE5 can also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) submitted the following TFE's 2014-WECC-TFE02514 and 2014-WECC-TFE02512 to cover the four (4) devices consisting of an RTU, two plant voltage control and monitor devices, and a workstation that can control the total plant load; 2) created documentation to track assessment of patch for IBM compatible devices and train employees on compliance standards and what is expected of them; 3) used a third-party software to track patch assessment tracks to remind technicians when to assess patches, which paperwork is required, and what approval is needed; and 4) trained its personnel to address the root cause of lack of compliance understanding.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014098 | CIP 007-1 | R4 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R4. During this time, WECC Auditors were conducting a review of WECC_URE5’s compliance with CIP-007-1 R4. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert discussed this possible noncompliance with WECC_URE5. WECC_URE5 stated that it had 29 devices that were technically not capable of implementing AV/malware prevention tool and were not included in a TFE. After reviewing the self-report and speaking with WECC_URE5, the WECC SME found that WECC_URE5 failed to submit a complete list of TFEs that included 29 devices in scope. The WECC SME forwarded this information to Enforcement for review. Enforcement reviewed the information from the self-report and the WECC SME and determined that WECC_URE5 failed to submit a complete list of TFEs per CIP 007-1 R4 for 29 devices which included GMS workstations, PLCs, PACM control panels, firewalls, and a Firewall Management server. Therefore, WECC_URE5 has an issue with CIP 007-1 R4. This issue began the initial date when the TFE’s were supposed to be filed to the day WECC_URE5 completed its filing for the 29 devices. The root cause was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to submit a complete list of TFEs per CIP 007-1 R4 for 29 devices which included GMS workstations, PLCs, PACM control panels, firewalls, and a Firewall Management server. Failing to submit a complete list of TFEs that included the 29 devices in scope could result in misidentifying the critical role or function that devices serve in the ESP. Mis-identifying the role or function of these devices could result in adding incorrect compensating measures that would adequately address the weakness posed by the device not being technically capable of implementing malware prevention tools. The 29 devices in scope are CCAs that are vital for the management of the SCADA systems. WECC_URE5 implemented strong preventative controls to prevent consequence from occurring. Specifically, WECC_URE5 implemented MAC-based authentication, which prevents any unauthorized device with an unrecognized MAC address from communicating with any of the devices on the network. This would prevent personnel from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which would help prevent someone from remotely attempting to send attack packets through to the devices on the network. WECC_URE5 implemented strong detective controls to detect the above consequence. Specifically, the entity has operators manning the PSPs 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, the entity would have likely corrected the condition as the entity implemented strong corrective controls. Specifically, the entity's operators have the ability to switch the plant into 'Manual' mode, which prevents any control from cyber devices. The entity also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, WECC_URE5 set up the two Plant Load Set point sources to be independent of one another. Therefore, if one device were to be compromised, the entity could switch to the other device to manage the set point. WECC_URE5 can also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1);submitted TFEs for the 29 devices in scope under the following ID’s: 2010-WECC-TFE00694-4, 2014-WECC-TFE02506, 2014-WECC-TFE02511, 2014-WECC-TFE02516, 2014-WECC-TFE02517, and 2014-WECC-TFE02518 WECC has verified completion.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014099 | CIP 007-1 | R5 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R5. During this time, WECC Auditors were conducting a review of WECC_URE5's compliance with CIP-007-1 R5. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. A WECC Subject Matter Expert (SME) reviewed WECC_URE5's self-report and discussed this possible noncompliance with WECC_URE5. WECC_URE5 stated that it had 9 Critical Cyber Assets (CCAs) that were technically not capable of implementing technical and procedural controls that enforce access authentication of, and accountability for, all user activity and were not included in the original Technically Feasible Exceptions (TFEs) filed. Therefore WECC_URE5 failed to use passwords that are at least six characters long and consist of a combination of alpha, numeric, and “special” characters as required by CIP 007 R5. The WECC SME forwarded this information to Enforcement. Enforcement reviewed the SME’s and WECC_URE5's information and determined that WECC_URE5 failed to implement and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. Further, WECC_URE5 failed to use passwords that are at least six characters long and consist of a combination of alpha, numeric, and “special” characters. Specifically, WECC_URE5 did not file TFEs for 9 devices incapable of enforcing the password complexity requirements of CIP-007 R5. The root cause of this issue was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to use passwords that are at least six characters long and consist of a combination of alpha, numeric, and “special” characters. Specifically, WECC_URE5 did not file TFEs for 9 devices incapable of enforcing the password complexity requirements of CIP-007 R5. Failing to submit a complete list of TFEs could result in misidentifying the critical role or function that devices serve within the Electronic Security Perimeter (ESP). Misidentifying the role or function of these devices could result in adding incorrect compensating measures such as basic input and output system (BIOS) updates then the Kernel of the Operating System (OS) may become corrupted or incompatible, thus rendering the OS incapable of booting. On the other hand, WECC_URE5 did implement strong preventative controls to prevent the above consequence from occurring. Specifically, WECC_URE5 implemented MAC-based authentication, which prevents any unauthorized device with an unrecognized MAC address from communicating with any of the devices on the network. This could prevent personnel from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which could help prevent someone from remotely attempting to send attack packets through to the devices on the network. WECC_URE5 also implemented strong detective controls to detect the above consequence. Specifically, WECC_URE5 has operators inside the Physical Security Perimeters (PSPs) 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, WECC_URE5 could have likely corrected the condition as it implemented strong corrective controls. Specifically, WECC_URE5's operators have the ability to switch the plant into 'Manual' mode, which could prevent any control from cyber devices. WECC_URE5 also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, it set up the two Plant Load Set point sources to be independent of one another. Therefore, if one device were to be compromised, WECC_URE5 could switch to the other device to manage the set point. WECC_URE5 can also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons, and the fact that no harm was caused WECC determined this issue posed a minimal risk to the reliability of the BES. | To mitigate this issue, WECC_URE5: 1) submitted requests for TFEs #2014-WECC-TFE02506 and TFE02511. WECC has verified completion.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014014006 | CIP 007-1 | R6 | WECC_URE5 submitted a Self-Report stating that it had an issue of CIP 007-1 R6. During this time, WECC Auditors were conducting a review of WECC_URE5's compliance with CIP-007-1 R6. The WECC Auditors found no further instances of possible non-compliance during their audit other than what WECC_URE5 had submitted in its self-report. Further, a WECC Subject Matter Expert (SME) also reviewed WECC_URE5's self-report and found that it failed to fully implement automated tools or organizational controls to monitor system events related to cyber security, as technically feasible. Specifically, WECC_URE5 failed to file a TFE for 16 devices consisting of, nine (9) PACS panels, three PACS interfaces, two controllers that provide breaker status, relay alarms, and other plant statuses; one device that provides communication between the SCADA master and substation end point-devices, and a RTU. WECC_URE5 also failed to review logs for nine (9) devices, consisting of two interface devices for plant status, control, and alarming; one interface development station, one PACS server, two PACS workstations, and three workstations that can control plant load. The WECC SME forwarded these findings to Enforcement for review. Enforcement reviewed the self-report and the SME’s findings and determined that WECC_URE5 failed to ensure that all Cyber Assets within the ESP implement tools or process controls for monitoring cyber security-related system events. Specifically, WECC_URE5 failed to file a TFE for 16 devices consisting of, nine (9) PACS panels, three PACS interfaces, two controllers that provide breaker status, relay alarms, and other plant statuses; one device that provides communication between the SCADA master and substation end point-devices, and a RTU. WECC_URE5 also failed to review logs for nine (9) devices, consisting of two interface devices for plant status, control, and alarming; one interface development station, one PACS server, two PACS workstations, and three workstations that can control plant load. The root cause was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to ensure that all Cyber Assets within the ESP implement tools or process controls for monitoring cyber security-related system events, as technically feasible. Specifically, WECC_URE5 failed to file TFE for 16 devices. The root cause of the TFE portion of the issue was a lack of communication between those that file the TFEs and those that work with the devices requiring the TFEs. WECC_URE5 also stated that there was not one person designated to see the TFE-filing process from start to finish, adding to the lack of communication. For the log review portion of the issue, the entity stated that the root cause was a lack of compliance understanding due to a lack of training. Failing to ensure that, where technically feasible, CAs in the ESP has tools or processes to monitor cyber security-related system events and review these logs could lead to malicious activity on the network being undetected. Someone could scan devices on the network to look for vulnerabilities on the device. If vulnerabilities are discovered, the person could use malware to launch an attack and possibly exploit the vulnerability. If the attack succeeds, the person could take control of the devices. This unknown person could also scan other devices in scope to look for vulnerabilities and launch an attack with malware to attempt to take control of the device. If the attack was successful and the person able to take control of the device, he/she could use the device to scan other devices connected to it to look for vulnerabilities. If vulnerabilities are discovered, the person could launch an attack to try to get control of the device. If successful, the person could repeat the process of scanning for vulnerabilities, launching an attack against the device, and taking control of the device until a device controlling the generation is compromised. WECC_URE5 implemented strong preventative controls to prevent the above consequence from occurring. Specifically, WECC_URE5 implemented MAC-based authentication. With this authentication, any device with an unknown MAC address is locked down to prevent it from communicating with any of the devices on the network until the MAC address is authenticated. This would prevent someone from attempting to scan the network, either remotely or on-site. WECC_URE5 also restricts traffic flow into the network, locking down ports and services to only those required for operations, then sending the remaining traffic through multiple firewalls for inspection before going to the devices in the network. The firewalls include application blocking/filtering and IP address filtering, which would help prevent someone from remotely attempting to send attack packets through to the devices on the network. WECC_URE5 also implemented strong detective controls to detect the above consequence. Specifically, the entity has operators at the PSPs 24 hours a day 7 days a week. These operators could detect if a malicious person was on-site attempting to disrupt load and/or transmission. If operators suspect a cyber-attack due to erratic behavior of the devices being detected, WECC_URE5 would likely correct the condition as WECC_URE5 implemented strong corrective controls. Specifically, WECC_URE5's operators have the ability to switch the plant into 'Manual' mode, which prevents any control from cyber devices. WECC_URE5 also has multiple metering devices which are not connected to the network that could be relied on in the event that an attack succeeds and the devices in scope show incorrect information as to the status of the plant's operations. As further compensation, WECC_URE5 implemented strong compensating controls. Specifically, WECC_URE5 set up the two Plant Load Set Point sources to be independent of one another. Therefore, if one device were to be compromised, WECC_URE5 could switch to the other device to manage the set point. WECC_URE5 could also switch the Plant Load Control to 'Local Control', which would no longer rely on these devices for the set point. For these reasons and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the reliability of the BES. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) filed TFEs for the 16 devices in scope under TFE Requests 2014-WECC-TFE02503, 2014-WECC-TFE02504 and 2014-WECC-TFE02505 and on June 26, 2014 under TFE Requests 2014-WECC-TFE02508 and 2014-WECC-TFE02515; 2) installed Adaptive Log Exporter on devices in scope that are capable using automated logging, configured SIEM to accept logs from these devices in scope, developed processes for manually reviewing logs for devices not capable of using automated logging, and trained staff on changes.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012480 | CIP-002-3 | R1 | During a Compliance Audit, WECC determined that WECC_URE6 was in non-compliance with CIP-002-3 R1, because WECC_URE6 failed to consider all asset types listed in R1.2.1 through R1.2.7 in its risk-based assessment of Critical Asset Identification. According to the Audit Team, WECC_URE6 changed its Critical Asset identification methodology from a risk-based assessment methodology (“RBAM”) consistent with Version 3 of the Standard, to the bright line criteria methodology set out in Version 4, while Version 3 was still in effect. Specifically, WECC_URE6 changed its criteria in section 5.1.1.2 of its RBAM from a threshold of 300 MW to 1500 MV or 1000 MVAR. Both methodologies determined that WECC_URE6 did not have any Critical Assets. Enforcement reviewed the Audit Team’s findings and the evidence WECC_URE6 produced at the Audit, and determined that WECC_URE6 had an issue with CIP-002-3 R1 for failing to identify and document a risk-based assessment methodology to identify its Critical Assets, compliant with Version 3 of the CIP Standards. However, because WECC_URE6'S generation capacity is 56 MW, the criteria adjustment did not change the determination that WECC_URE6 did not have any Critical Assets. The root cause of the non-compliance was WECC_URE6's lack of compliance understanding leading to its failure to monitor the CIP Version changes through the NERC and FERC processes. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. When WECC_URE6 changed its methodology from its initial Critical Asset Identification Procedure approach to a methodology based on CIP-002-4 Attachment 1 criteria, it failed to identify its Cyber Assets, as required by Version 3 of the Standard. This issue of non-compliance posed potential harm to WECC_URE6, because if its Cyber Assets were not correctly identified, they may not be protected. However, the WECC Audit Team confirmed that either methodology returned null lists for Cyber Assets and associated Critical Cyber Assets. | WECC_URE6 submitted a mitigation plan addressing this issue of non-compliance. To mitigate this issue, WECC_URE6 revised its RBAM to reflect the 300 MW threshold referenced in CIP-002-3 R1.2.5 (Version 3). By revising its RBAM, WECC_URE6 is minimizing the probability of further violations of CIP-002-3 R1.