2012-03-30 | FERC | NP12-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Grand Ridge Energy III LLC (Grand Ridge Energy III) | NCR11030 | RFC2011001257 | Settlement Agreement | From May 2, 2011 through May 13, 2011, ReliabilityFirst conducted a Compliance Audit of Grand Ridge Energy LLC, a corporate affiliate of Grand Ridge Energy III. During the Audit, ReliabilityFirst discovered a violation of PRC-005-1 R2. ReliabilityFirst determined that Grand Ridge Energy III, as a Generator Owner (GO), failed to provide: (1) evidence that it maintained and tested certain Protection System devices within the defined intervals; and (2) the date it last tested and maintained certain Protection System devices. Grand Ridge Energy LLC and Grand Ridge Energy III share the Protection System devices at issue. Grand Ridge Energy III has primary as well as backup fiber optic communications devices associated with Protection Systems. Grand Ridge Energy III's communications systems consist of a single optical ground wire with multiple pairs of fibers, which serve both the primary and secondary line Protection System relays. The relays have different pairs of fiber from the same cable. Grand Ridge Energy III failed to provide (1) evidence that it maintained and tested its backup communications systems within the defined intervals, as required by R2.1, and (2) the date that it last tested and maintained the backup associated communications systems, as required by R2.2. The violation implicated both of Grand Ridge Energy III's two associated communications systems which are two of its 37 (5.4%) total Protection System devices. Grand Ridge Energy III comprises a portion of Grand Ridge Wind Farm, and consists of 33 wind turbines with a total generating capacity of 49.5 MW. Grand Ridge Energy III utilizes the compliance program developed by its affiliate, Invenergy LLC. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. Grand Ridge Energy III's primary and secondary fiber optic communications systems are monitored within the operations center as two separate alarms. The communications systems at issue were operating properly when tested at the time of commissioning in 2008. In addition, the communication system for one set of relays was continuously monitored at the Transmission Owner's control center. Furthermore, Grand Ridge Energy III's Protection System devices alarm upon actuation. The alarms occur locally on the substation alarm panel and alarm at Grand Ridge Energy III's control center. In addition, an alarm for the primary Protection System occurs on the interconnecting utility's Supervisory Control and Data Acquisition (SCADA) system. Grand Ridge Energy III's Protection Systems have backup and redundant protection in place, and Grand Ridge Energy III has experienced no misoperations since registration. | 5/21/2010 (when Grand Ridge Energy III registered as a GO and was required to comply with the Standard) | 10/28/2011 (when Grand Ridge Energy III ensured that all Protection System maintenance and testing was up to date) | $3,700 Settlement of (RFC2011001256 and RFC2011001257) | Audit | On June 2, 2011, Grand Ridge Energy LLC submitted to ReliabilityFirst a Mitigation Plan to address its separate violation of PRC-005-1 R2. This Mitigation Plan addressed Grand Ridge Energy III's violation of PRC-005-1 R2 as well, so Grand Ridge Energy III did not submit a separate Mitigation Plan for the instant violation. In accordance with the Mitigation Plan, Grand Ridge Energy verified that it tested the communications circuits at commissioning. Grand Ridge Energy also established constant monitoring on backup relay protection circuits. Finally, Grand Ridge Energy obtained an explanation and evidence to support "constant monitoring" of one of two fiber communication circuits. Constant monitoring means that (a) loss of communications result in an alarm to the SCADA alarm panel monitor in the control center, and (b) connected backup communication system to the ComEd SCADA system alarms if the communication system is lost. | 2011-10-28 | 2012-02-13 | Agrees/ Stipulates | ReliabilityFirst considered certain aspects of Grand Ridge Energy III's compliance program, which was in place at the time of the violation, to be mitigating factors when determining the penalty amount. Grand Ridge Energy III utilizes the compliance program provided by its corporate affiliate, Invenergy, though Grand Ridge Energy III is responsible for its own compliance with the Reliability Standards. The Compliance Manager reports directly to the Vice President, Asset Management and Operations, and may interface with the executive management as necessary. The Compliance Manager conducts monthly compliance webex and conference calls with the facility operations and maintenance managers as well as support staff to inform them of compliance issues. In addition, the Plant Manager conducts training for facility staff. The Compliance Manager periodically assesses compliance using an internal compliance questionnaire and an independent review of the evidence demonstrating compliance. Furthermore, personnel report any violation of the Reliability Standards to the Compliance Manager for thorough Corporate Management review of the violation. ReliabilityFirst considered the fact that it discovered the violations during the Compliance Audit and subsequent review, rather than through self-reports, and did not apply mitigating credit for self-reporting. ReliabilityFirst considered as a mitigating factor the degree and quality of Grand Ridge Energy III's cooperation in connection with the violations and the prompt submittal of effective mitigation plans to remediate the violations. ReliabilityFirst considered the violations to be repetitive conduct in light of Grand Ridge Energy III's affiliates' previous violations of PRC-005-1, and as such considered Grand Ridge Energy III's compliance history to be an aggravating factor in determining the penalty determination. Grand Ridge Energy III corporate affiliate Invenergy Cannon Falls LLC (NCR10244) previously violated PRC-005-1 R1 and R2 in the Midwest Reliability Organization. These violations were filed with FERC on June 30, 2011 under NP11-228-000. Grand Ridge Energy III corporate affiliate Hardee Power Partners Limited (NCR00035) previously violated PRC-005-1 R1 and R2 in the Florida Reliability Coordinating Council. These violations were filed with FERC on October 14, 2009 under NP10-2-000 and on November 30, 2011 under NP11-23-000.
2012-03-30 | FERC | NP12-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Grand Ridge Energy IV LLC (Grand Ridge Energy IV) | NCR11031 | RFC2011001258 | Settlement Agreement | From May 2, 2011 through May 13, 2011, ReliabilityFirst conducted a Compliance Audit of Grand Ridge Energy LLC, a corporate affiliate of Grand Ridge Energy IV. During the Audit, ReliabilityFirst discovered a violation of PRC-005-1 R1. ReliabilityFirst determined that Grand Ridge Energy IV, as a Generator Owner (GO), failed to have a Protection System maintenance and testing program (Program) in place, as required by the Standard. Specifically, Grand Ridge Energy IV did not have a Program until October 8, 2010, when Grand Ridge Energy IV put in place its Substation Maintenance Plan, which is a Microsoft Excel document containing maintenance and testing intervals and a basis for each interval for each Protection System device. Prior to October 8, 2010, Grand Ridge Energy LLC had contracted with a vendor in order to establish adequate coverage for the facility equipment, but the vendor's testing plan did not meet the criteria of the Standard due to inadequate knowledge of the detailed requirements of what constituted a Plan. Grand Ridge Energy LLC and Grand Ridge Energy IV share a Protection System maintenance and testing program. Grand Ridge Energy IV comprises a portion of Grand Ridge Wind Farm, and consists of seven wind turbines with a total generating capacity of 10.5 MW. Grand Ridge Energy IV utilizes the compliance program developed by its affiliate, Invenergy LLC. | PRC-005-1 | R1 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. With the exception of its backup communications systems, Grand Ridge Energy IV maintained and tested its Protection System devices on regular intervals. In addition, Grand Ridge Energy IV fully tested all of its relays, direct current control circuitry, and voltage and current sensing devices upon commissioning the Grand Ridge facility in 2008. Grand Ridge conducted sporadic battery testing throughout the period. Furthermore, Grand Ridge Energy IV's Protection System devices alarm upon actuation (when the protection systems trip or upon loss of communication). The alarms occur locally on the substation alarm panel and alarm at Grand Ridge Energy IV's control center. An alarm for the primary Protection System occurs on the interconnecting utility's Supervisory Control and Data Acquisition (SCADA) system. Grand Ridge Energy IV's Protection Systems have backup and redundant protection in place, and Grand Ridge Energy IV has experienced no misoperations since registration. | 5/21/2010 (when Grand Ridge Energy IV registered as a GO and was required to comply with the Standard) | 10/8/2010 (when Grand Ridge Energy IV implemented its Substation Maintenance Plan) | $800 (for RFC2011001258 and RFC2011001259) | Audit | On June 2, 2011, Grand Ridge Energy LLC submitted to ReliabilityFirst a Mitigation Plan to address its own violation of PRC-005-1 R1. This Mitigation Plan revised Grand Ridge Energy IV's Program as well, so Grand Ridge Energy IV did not submit a Mitigation Plan. In accordance with the Mitigation Plan, Grand Ridge Energy implemented a Protection System maintenance and testing program, the Substation Maintenance Plan. In addition, subsequent to the Audit, Grand Ridge Energy implemented a revised Program in order to improve the document's clarity. The Program was revised from an Excel format to a narrative format. | 2011-10-28 | 2012-02-13 | Agrees/ Stipulates | ReliabilityFirst considered certain aspects of Grand Ridge Energy IV's compliance program, which was in place at the time of the violation, to be mitigating factors when determining the penalty amount. Grand Ridge Energy IV utilizes the compliance program provided by its corporate affiliate, Invenergy, though Grand Ridge Energy IV is responsible for its own compliance with the Reliability Standards. The Compliance Manager reports directly to the Vice President, Asset Management and Operations, and may interface with the executive management as necessary. The Compliance Manager conducts monthly compliance webex and conference calls with the facility operations and maintenance managers as well as support staff to inform them of compliance issues. In addition, the Plant Manager conducts training for facility staff. The Compliance Manager periodically assesses compliance using an internal compliance questionnaire and an independent review of the evidence demonstrating compliance. Furthermore, personnel report any violation of the Reliability Standards to the Compliance Manager for thorough Corporate Management review of the violation. ReliabilityFirst considered the fact that it discovered the violations during the Compliance Audit and subsequent review, rather than through self-reports, and did not apply mitigating credit. ReliabilityFirst considered as a mitigating factor the positive degree and quality of Grand Ridge Energy IV's cooperation in connection with the violations and the prompt submittal of effective mitigation plans to remediate the violations. ReliabilityFirst considered the violations to be repetitive conduct in light of Grand Ridge Energy IV's affiliates' previous violations of PRC-005-1, and as such considered Grand Ridge Energy IV's compliance history to be an aggravating factor in the penalty determination. Grand Ridge Energy IV corporate affiliate Invenergy Cannon Falls LLC (NCR10244) previously violated PRC-005-1 R1 and R2 in the Midwest Reliability Organization. These violations were filed with FERC on June 30, 2011 under NP11-228-000. Grand Ridge Energy IV corporate affiliate Hardee Power Partners Limited (NCR00035) previously violated PRC-005-1 R1 and R2 in the Florida Reliability Coordinating Council. These violations were filed with FERC on October 14, 2009 under NP10-2-000 and on November 30, 2011 under NP11-23-000.
2012-03-30 | FERC | NP12-22-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Grand Ridge Energy IV LLC (Grand Ridge Energy IV) | NCR11031 | RFC2011001259 | Settlement Agreement | From May 2, 2011 through May 13, 2011, ReliabilityFirst conducted a Compliance Audit of Grand Ridge Energy LLC, a corporate affiliate of Grand Ridge Energy IV. During the Audit, ReliabilityFirst discovered a violation of PRC-005-1 R2. ReliabilityFirst determined that Grand Ridge Energy IV, as a Generator Owner (GO), failed to provide: (1) evidence that it maintained and tested certain Protection System devices within the defined intervals; and (2) the date it last tested and maintained certain Protection System devices. Grand Ridge Energy LLC and Grand Ridge Energy IV share the Protection System devices at issue. Grand Ridge Energy IV has primary as well as backup fiber optic communications devices associated with Protection Systems. Grand Ridge Energy IV's communications systems consist of a single optical ground wire with multiple pairs of fibers, which serve both the primary and secondary line Protection System relays. The relays have different pairs of fiber from the same cable. Grand Ridge Energy IV failed to provide (1) evidence that it maintained and tested its backup communications systems within the defined intervals, as required by R2.1, and (2) the date that it last tested and maintained the backup associated communications systems, as required by R2.2. The violation implicated both of Grand Ridge Energy IV's two associated communications systems which are two of its 37 (5.4%) total Protection System devices. Grand Ridge Energy IV comprises a portion of Grand Ridge Wind Farm, and consists of seven wind turbines with a total generating capacity of 10.5 MW. Grand Ridge Energy IV utilizes the compliance program developed by its affiliate, Invenergy, LLC. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. Grand Ridge Energy IV's primary and secondary fiber optic communications systems are monitored and alarmed to the operations center as two separate alarms. The communications systems at issue were operating properly when tested at the time of commissioning in 2008. In addition, the communication system for one set of relays was continuously monitored at the Transmission Owner's control center. Furthermore, Grand Ridge Energy IV's Protection System devices alarm upon actuation. The alarms occur locally on the substation alarm panel and alarm at Grand Ridge Energy IV's control center. In addition, an alarm for the primary Protection System occurs on the interconnecting utility's Supervisory Control and Data Acquisition (SCADA) system. Grand Ridge Energy IV's Protection Systems have backup and redundant protection in place, and Grand Ridge Energy IV has experienced no misoperations since registration. | 5/21/2010 (when Grand Ridge Energy IV registered as a GO and was required to comply with the Standard) | 10/28/2011 (when Grand Ridge Energy IV ensured that all Protection System maintenance and testing was up to date) | $800 (for RFC2011001258 and RFC2011001259) | Audit | On June 2, 2011, Grand Ridge Energy LLC submitted to ReliabilityFirst a Mitigation Plan to address its separate violation of PRC-005-1 R2. This Mitigation Plan addressed Grand Ridge Energy IV's violation of PRC-005-1 R2 as well, so Grand Ridge Energy IV did not submit a separate Mitigation Plan. In accordance with the Mitigation Plan, Grand Ridge Energy verified that it tested the communications circuits at commissioning. Grand Ridge Energy also established constant monitoring on backup relay protection circuits. Finally, Grand Ridge Energy obtained an explanation and evidence to support "constant monitoring" of one of two fiber communication circuits. Constant monitoring means that (a) loss of communications result in an alarm to the SCADA alarm panel monitor in the control center, and (b) connected backup communication system to the ComEd SCADA system alarms if the communication system is lost. | 2011-10-28 | 2012-02-13 | Agrees/ Stipulates | ReliabilityFirst considered certain aspects of Grand Ridge Energy IV's compliance program, which was in place at the time of the violation, to be mitigating factors when determining the penalty amount. Grand Ridge Energy IV utilizes the compliance program provided by its corporate affiliate, Invenergy, though Grand Ridge Energy IV is responsible for its own compliance with the Reliability Standards. The Compliance Manager reports directly to the Vice President, Asset Management and Operations, and may interface with the executive management as necessary. The Compliance Manager conducts monthly compliance webex and conference calls with the facility operations and maintenance managers as well as support staff to inform them of compliance issues. In addition, the Plant Manager conducts training for facility staff. The Compliance Manager periodically assesses compliance using an internal compliance questionnaire and an independent review of the evidence demonstrating compliance. Furthermore, personnel report any violation of the Reliability Standards to the Compliance Manager for thorough Corporate Management review of the violation. ReliabilityFirst considered the fact that it discovered the violations during the compliance audit and subsequent review, rather than through self-reports, and did not apply mitigating credit. ReliabilityFirst considered as a mitigating factor the positive degree and quality of Grand Ridge Energy IV's cooperation in connection with the violations and the prompt submittal of effective mitigation plans to remediate the violations. ReliabilityFirst considered the violations to be repetitive conduct in light of Grand Ridge Energy IV's affiliates' previous violations of PRC-005-1, and as such considered Grand Ridge Energy IV's compliance history to be an aggravating factor in the penalty determination. Grand Ridge Energy IV corporate affiliate Invenergy Cannon Falls LLC (NCR10244) previously violated PRC-005-1 R1 and R2 in the Midwest Reliability Organization. These violations were filed with FERC on June 30, 2011 under NP11-228-000. Grand Ridge Energy IV corporate affiliate Hardee Power Partners Limited (NCR00035) previously violated PRC-005-1 R1 and R2 in the Florida Reliability Coordinating Council. These violations were filed with FERC on October 14, 2009 under NP10-2-000 and on November 30, 2011 under NP11-23-000.
2012-03-30 | FERC | NP12-22-000 | SERC Reliability Corporation (SERC) | Sabine River Authority of TX/LA (Sabine) | NCR01305 | SERC201000588 | Settlement Agreement | On August 5, 2010, Sabine self-reported a violation of FAC-008-1 R1 after discovering that its generation Facility Ratings Methodology (FRM) did not address the entire scope of equipment required by the Standard. On August 24, 2010, a SERC audit team reported an additional violation of FAC-008-1 R1 after finding that Sabine was unable to provide evidence of a documented generation FRM from June 18, 2007 through August 27, 2007. The SERC audit team also found that Sabine's generation FRM in place after August 27, 2007 failed to address relay protective devices, terminal equipment, and series and shunt compensation devices. SERC staff determined that Sabine, as a Generator Owner (GO), was in violation of FAC-008-1 R1 because Sabine did not have an FRM prior to August 27, 2007, and once it adopted an FRM, did not address all necessary equipment. On May 28, 2010, Sabine registered as a Transmission Owner (TO). During its review of Sabine's Self-Report and the findings of the SERC audit team, SERC staff requested Sabine's transmission FRM. Sabine stated that it believed its generation FRM was sufficient for both functions. SERC staff reviewed Sabine's generation FRM and found it did not address Facility Ratings for the TO function and solely addressed Facility Ratings for the GO function. SERC staff determined that Sabine, as a TO, was in violation of FAC-008-1 R1 for not having an FRM that covered its transmission equipment. | FAC-008-1 | R1; R1.2.1 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. Sabine's FRM was designed to reflect the most limiting element, the generator; 2. The revised Facility Rating did not change; and 3. Sabine attested that the Facilities were rated based on manufacturer's ratings and the units had been operated in accordance with those Ratings. | 6/18/2007 (when the Standard became mandatory and enforceable for Sabine's GO function) and 5/28/2010 (when the Standard became mandatory and enforceable for Sabine's TO function) | 7/29/2011 (Mitigation Plan completion) | $7,500 (for SERC201000588 and SERC201000602) | Self-Report | Sabine completed the following actions: 1. Revised and consolidated its procedures for FAC-008 and FAC-009 into one procedure to address both generation and transmission facilities and to include all equipment listed in FAC-008-1 R1.2.1; and 2. Updated its FRM to include all relevant generation and transmission equipment, a description of how all such equipment is rated, and its Rating. | 2011-07-29 | 2011-08-03 | Admits | Sabine did not have a documented internal compliance program (ICP) in place at the time of this violation. Sabine provided the following information regarding its ICP which was later implemented and which was considered a neutral factor by SERC in its penalty determination: Sabine implemented an ICP through a compliance policy dated October 20, 2010. The compliance policy outlines key compliance program elements, including direction and oversight, policies and procedures, training and communications, monitoring and evaluation, promotion and enforcement, and records. The NERC compliance officer has direct access to the general manager as well as members of the operating board. SERC did not apply mitigating self-reporting credit for this violation because SERC staff determined the violation was discovered as a result of audit preparation.
2012-03-30 | FERC | NP12-22-000 | SERC Reliability Corporation (SERC) | Sabine River Authority of TX/LA (Sabine) | NCR01305 | SERC201000602 | Settlement Agreement | On August 24, 2010, a SERC audit team reported a violation of FAC-009-1 R1 after determining that it was unable to verify that Sabine had established Facility Ratings for its facilities that were consistent with the associated generation Facility Ratings Methodology (FRM) prior to August 28, 2007. On August 28, 2007, Sabine established Facility Ratings that were consistent with the associated generation FRM as of that date. SERC staff determined that Sabine, as a Generator Owner (GO), was in violation of FAC-009-1 R1 for not establishing Facility Ratings consistent with its FRM. On May 28, 2010, Sabine registered as a Transmission Owner (TO) and was required to have established Facility Ratings for its transmission facilities consistent with an associated FRM. SERC staff found that Sabine did not have an FRM for its TO function and was therefore unable to demonstrate that it had developed Facility Ratings consistent with an associated transmission FRM. SERC staff determined that Sabine, as a TO, was in violation of FAC-009-1 R1 for not establishing Facility Ratings consistent with its FRM. | FAC-009-1 | R1 | Medium | Severe | SERC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. Sabine's FRM was designed to reflect the most limiting element, the generator; 2. The revised Facility Rating did not change; and 3. Sabine attested that the Facilities were rated based on manufacturer's ratings and the units had been operated in accordance with those Ratings. | 6/18/2007 (when the Standard became mandatory and enforceable for Sabine's GO function) and 5/28/2010 (when the Standard became mandatory and enforceable for Sabine's TO function) | 7/29/2011 (Mitigation Plan completion) | $7,500 (for SERC201000588 and SERC201000602) | Compliance Audit | Sabine completed the following actions: 1. Revised and consolidated its procedures for FAC-008 and FAC-009 into one procedure to address both generation and transmission facilities and to include all equipment listed in FAC-008-1 R1.2.1; and 2. Established Facility Ratings for all relevant generation and transmission equipment consistent with the associated FRM. | 2011-07-29 | 2011-08-30 | Admits | Sabine did not have a documented internal compliance program (ICP) in place at the time of this violation. Sabine provided the following information regarding its ICP which was later implemented and which was considered a neutral factor by SERC in its penalty determination: Sabine implemented an ICP through a compliance policy dated October 20, 2010. The compliance policy outlines key compliance program elements, including direction and oversight, policies and procedures, training and communications, monitoring and evaluation, promotion and enforcement, and records. The NERC compliance officer has direct access to the general manager as well as members of the operating board.
2012-03-30 | FERC | NP12-22-000 | Texas Reliability Entity (Texas RE) | Silver Star I Power Partners, LLC (Silver Star) | NCR10235 | TRE201000275 | Settlement Agreement | On July 21, 2010, Silver Star self-reported a violation of PRC-005-1 R2 to Texas RE. Silver Star, as a Generator Owner, failed to perform a test on some of its total generation Protection System devices (3 out of 54 total devices) within the intervals required by its Protection System maintenance and testing program. The tests that were not performed were the infrared checks of capacitor coupled voltage transformers (CCVTs), as defined in Silver Star’s maintenance and testing program, which were required every six months. The three CCVTs whose tests were missed comprised 5.6% of Silver Star’s total Protection System devices and 100% of the CCVTs. These devices were last tested in April 2009. The entity missed the next test date due October 2009. Specifically, these tests were performed in July 2010, which was 15 months after the previous test and nine months late. The required six-month inspection for the three CCVTs was missed because of the lack of automatic work orders that would have ensured that testing was performed within defined intervals. | PRC-005-1 | R2 | Lower | Lower | The violation posed a minimal and did not pose a serious or substantial risk to the bulk power system because the three CCVTs comprised a small part, 5.6%, of Silver Star's total Protection System devices. The CCVT infrared checks that were done at the end of the violation period showed that the CCVTs were in satisfactory operation condition. Furthermore, the Silver Star plant consists of a 60 MW portion of the ERCOT region generation. | 10/1/2009 (date the missed maintenance/testing should have occurred) | 7/1/2010 (date the maintenance/testing was completed) | 2000 | Self-Report | Silver Star completed the maintenance/testing on the three CCVTs (on July 1, 2010) and further mitigated the violation by implementing a maintenance scheduling system (on January 28, 2011) that generates reminders and alarms that ensure that maintenance and testing is performed on a timely basis. The maintenance tracking software generates automatic work orders, reminders and alarms based upon the due dates of maintenance and testing and will ensure that maintenance and testing will be performed within required intervals. Moreover, new Protection System maintenance and testing procedures were developed and implemented at Silver Star on October 11, 2010 that clarified and streamlined the maintenance and testing protocols applicable to Silver Star's generation Protection System equipment. The new procedures strengthen the overall compliance program at Silver Star. | 2011-01-28 | 2011-07-07 | Neither Admits nor Denies | Texas RE noted Silver Star's internal compliance program, in effect at the time of the violation, as a mitigating factor in the penalty determination. The program also has a named and staffed reliability compliance manager who has independent access to the CEO and work independent of operation and management. The program is sufficiently resourced, fully supported and participated in by senior management and included disciplinary action for employees involved in violations. Silver Star’s internal compliance program is managed and maintained by its parent company, BP Wind Energy North America, Inc. (BPWENA).
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901611 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to provide adequate and reliable telecommunications facilities for the exchange of Interconnection and operating information, in violation of COM-001-1 R1. | COM-001-1 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to provide adequate and reliable telecommunications facilities for the exchange of interconnection and operating information, the interim risk to the BPS was mitigated because the basic lines of communication (voice and data) between the Reliability Coordinator (RC) and BPA that met this Standard were already in place and functioning, while EWEB completed its documentation to comply with the Standard. BPA is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities during the period of the violation. The lines of communication were installed by BPA, the former TOP responsible for these communication facilities and functions, and continued to perform adequately during the short period of time while EWEB developed appropriate documentation, procedures and instructions. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB identified telecommunications resources used to communicate with its TOPs and BA (BPA). EWEB implemented a new system operating procedure defining how EWEB personnel are expected to plan and operate the EWEB electric system in accordance with each NERC Reliability Standard. EWEB provided evidence of completion in a document titled Telecommunications Maintenance and Testing Program, dated June 9, 2010. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901612 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB did not manage, alarm, test and/or actively monitor vital telecommunications facilities, in violation of COM-001-1 R2. | COM-001-1 | R2 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to manage, alarm, test and/or actively monitor vital telecommunications facilities, the interim risk to the BPS was mitigated because the basic lines of communication (voice and data) with the Reliability Coordinator (RC) and BPA that addressed this Standard were already in place and functioning, while EWEB completed its documentation to comply with the Standard. The basic lines of communication were installed with alarms by BPA, the former TOP responsible for these communication facilities and functions. BPA is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities during the period of the violation. EWEB actively managed and monitored the communication facilities during the short interim period required to develop appropriate documentation, procedures and testing plans, minimizing the risk to the BPS. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB identified telecommunications resources used to communicate with its TOPs and BA (BPA). EWEB implemented a new telecommunications system operating procedures defining how EWEB personnel are expected to plan and operate the EWEB electric system in accordance with each NERC Reliability Standard. EWEB developed procedures and guidance for alarming and testing vital communications in its document titled Telecommunications Maintenance and Testing Program, dated June 9, 2010. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901613 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to provide a means to coordinate telecommunications among its area and the respective areas of other Reliability Coordinators (RCs), Transmission Operators (TOPs) and Balancing Authorities (BAs), in violation of COM-001-1 R3. EWEB's telecommunications coordination did not include the ability to investigate and recommend solutions to telecommunications problems within its area and with other areas. | COM-001-1 | R3 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to provide a means to coordinate telecommunications among its area and the respective areas of other RCs, TOPs and BAs, the interim risk to the BPS was mitigated because the basic lines of communication (voice and data) with the RC and BPA were already in place and functioning while EWEB completed its documentation to comply with the Standard. BPA is EWEB's surrounding BA and acted as the TOP for EWEB's facilities during the period of the violation. Sufficient coordination occurred under BPA during the violation period to ensure the continued ability to investigate and recommend solutions to telecommunications problems, while EWEB developed guidelines for coordination. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB identified telecommunications resources used to communicate with its TOPs and BA (BPA). EWEB implemented a new telecommunications system operating procedures defining how EWEB personnel are expected to plan and operate the EWEB electric system in accordance with each NERC Reliability Standard. EWEB developed a written plan to address system operation with the ability to investigate and recommend solutions to telecommunications problems in its document titled Telecommunications Maintenance and Testing Program, dated June 9, 2010. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901614 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities, in violation of COM-001-1 R5. | COM-001-1 | R5 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to have written operating instructions and procedures to enable continued operation of the system during the loss of telecommunications facilities, the interim risk to the BPS was mitigated because the basic lines of communication (voice and data) with the Reliability Coordinator (RC) and BPA that met this standard were in place and functioning while EWEB completed its documentation to comply with the Standard. The basic lines of communication were installed with alarms by BPA, the former TOP responsible for these communication facilities and functions. BPA is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities during the period of the violation. EWEB actively managed and monitored the communication facilities during the short interim period required to develop operating instructions and procedures to enable continued operation of the system, minimizing risk to the BPS. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB identified telecommunications resources used to communicate with its TOPs and BA (BPA). EWEB implemented a new telecommunications system operating procedures defining how EWEB personnel are expected to plan and operate the EWEB electric system in accordance with each NERC Reliability Standard. EWEB developed a written plan to address system operation with loss of vital communications in its document titled Telecommunications Maintenance and Testing Program, dated June 9, 2010. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901615 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to develop, maintain and implement a set of plans to mitigate operating emergencies on the transmission system, in violation of EOP-001-0 R3. | EOP-001-0 | R3 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to develop, maintain and implement a set of plans to mitigate operating emergencies on the transmission system, the interim risk to the BPS was mitigated because the requirements of EOP-001-0 were included as elements of EWEB’s Emergency Operations Planning: System Operating Procedure, dated February 10, 2010. Prior to this plan, the plan developed by BPA would have been sufficient to ensure adequate mitigation of any operating emergencies while EWEB completed its documentation to comply with the Standard. BPA is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities during the period of the violation. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provided the EWEB Emergency Operations Planning: System Operating Procedure (the Procedure) that addressed insufficient generating capacity for mitigating operating emergencies on the transmission system and or load shedding. The Procedure was developed in coordination with BPA, which provided comments before the Procedure was approved. In addition, EWEB provided training and fully implemented the Procedure. | 2010-06-09 | 2010-10-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901616 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to have emergency plans that would enable it to mitigate operating emergencies, in violation of EOP-001-0 R4. | EOP-001-0 | R4 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to have emergency plans that would enable it to mitigate operating emergencies, the interim risk to the BPS was mitigated because the applicable requirements of 1-EOP-001-0 were also elements of the emergency operations provided for in BPA's document, Technical Requirements for Interconnection with Bonneville Power Administration. The plans provided in this document were developed by BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, and were sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for EWEB to restate the agreements' provisions and incorporate them into its own plan addressing the requirements of EOP-001-0 R3. Because EWEB was previously located entirely within the footprint of BPA (through an Interconnection Agreement with BPA) which has full visibility of EWEB, there has been no increased risk to the BPS due to an administrative change in functional registration while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provided the EWEB Emergency Operations Planning: System Operating Procedure (the Procedure) that addressed insufficient generating capacity for mitigating operating emergencies on the transmission system and or load shedding. The Procedure was developed in coordination with BPA, which provided comments before the Procedure was approved. In addition, EWEB provided training and fully implemented the Procedure. | 2010-06-09 | 2010-10-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901617 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan, in violation of EOP-001-0 R5. | EOP-001-0 | R5 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to include the applicable elements in Attachment 1-EOP-001-0 when developing its emergency plan, the interim risk to the BPS was mitigated because EWEB has existing practices for mitigating operating emergencies sufficiently and timely with other TOPs and BAs. However, these practices have not been documented in a comprehensive plan that demonstrates how they address all elements of Attachment 1 of EOP-001-0. WECC reviewed EWEB's existing practices and determined that they are sufficient to minimize the risk to BPS reliability while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB implemented its Emergency Operations Planning: System Operating Procedure that includes an emergency operation section (R5.2.3). This section adopts the elements of Attachment 1-EOP-001-0 as a list of additional elements to be considered as potential mitigating responses during any emergency condition. | 2010-06-09 | 2010-10-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901618 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to annually review and update its emergency plan, and to provide a copy of its updated emergency plans to its Reliability Coordinator (RC) and to neighboring TOPs and Balancing Authorities (BAs), in violation of EOP-001-0 R6. | EOP-001-0 | R6 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to annually review and update its emergency plan, and provide a copy of its updated emergency plans to its RC and to neighboring TOPs and BAs, the interim risk to the BPS was mitigated because the applicable requirements of this Standard were addressed in the emergency operations provided for in BPA's document: Technical Requirements for Interconnection with Bonneville Power Administration. BPA is EWEB's surrounding BA and acted as the TOP for EWEB's facilities during the period of the violation. Therefore, WECC determined that the necessarily coordination between BPA and EWEB occurred. According to EWEB, the existing practices between BPA and EWEB were sufficient to minimize the risk to BPS reliability while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB annually reviews and updates its emergency plan and provides a copy of its updated emergency plans to its RC through its BA. The plan is coordinated with EWEB's neighboring entities. | 2010-06-09 | 2010-10-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901660 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to have a restoration plan to reestablish its electrical system in a stable and orderly manner in the event of a partial or total shutdown of its system, and was lacking the necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels, in violation of EOP-005-1 R1. | EOP-005-1 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to have a restoration plan to reestablish its electrical system in a stable and orderly manner in the event of a partial or total shutdown of its system, and was lacking the necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels, the interim risk to the BPS was mitigated because BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, maintained plans and facilities for system restoration while EWEB completed its documentation to comply with the Standard. The plans addressed the requirements of EOP-005-1 R1, and continued to be adequate for restoration during the short period of time until EWEB plans were completed. EWEB could call on BPA, under the terms of their Emergency Assistance Agreement, for assistance with emergency response and system restoration in the interim period of time until EWEB was prepared to assume its new function. WECC determined that this fact minimized the possibility of inappropriate or non-timely emergency response by EWEB. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB secured the services of a third party, GDS Associates, to assist in the development of an integrated system restoration plan. EWEB provided its system restoration plan to its BA to show that it addressed the requirements of this Standard. | 2010-06-09 | 2011-02-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901661 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to develop restoration plans with a priority of restoring the integrity of the interconnection, in violation of EOP-005-1 R3. | EOP-005-1 | R3 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to develop restoration plans with a priority of restoring the integrity of the interconnection, the interim risk to the BPS was mitigated because BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, maintained plans and facilities for system restoration while EWEB completed its documentation to comply with the Standard. Further, EWEB could call on BPA, under the terms of their Emergency Assistance Agreement, for assistance with emergency response and system restoration in the interim period of time until EWEB was prepared to assume its new function. WECC determined that this fact minimized the possibility of inappropriate or non-timely emergency response by EWEB. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB secured the services of a third party, GDS Associates, to assist in the development of an integrated system restoration plan. EWEB provided its system restoration plan to its BA to show that it has addressed mitigated the requirements of the Standard. | 2010-06-09 | 2011-02-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901662 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to coordinate its restoration plans with the Generator Owners (GOs) and Balancing Authorities (BAs) within its area, its Reliability Coordinator, and neighboring TOPs and BAs, in violation of EOP-005-1 R4. | EOP-005-1 | R4 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to coordinate its restoration plans with the GOs and BAs within its area, the interim risk to the BPS was mitigated because BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities, maintained plans and facilities for system restoration while EWEB completed its documentation to comply with the Standard. The plans addressed the requirements of EOP-005-1 R1, and continued to be adequate for restoration during the short period of time until EWEB plans were completed. EWEB could call on BPA, under the terms of their Emergency Assistance Agreement, for assistance with emergency response and system restoration in the interim period of time until EWEB was prepared to assume its new function. WECC determined that this fact minimized the possibility of inappropriate or non-timely emergency response by EWEB. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), GO and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB secured the services of a third party, GDS Associates, to assist in the development of an integrated system restoration plan. EWEB provided its system restoration plan to its BA to show that it has addressed mitigated the requirements of the Standard. | 2010-06-09 | 2011-02-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901663 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to periodically test its telecommunications facilities needed to implement the restoration plan, in violation of EOP-005-1 R5. | EOP-005-1 | R5 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to periodically test its telecommunications facilities needed to implement the restoration plan, the interim risk to the BPS was mitigated because BPA, EWEB's surrounding Balancing Authority (BA), acted as the TOP for EWEB's facilities and maintained plans and facilities for system restoration while EWEB completed its documentation to comply with the Standard. The plans addressed the requirements of EOP-005-1 R1, and continued to be adequate for restoration during the short period of time until EWEB plans were completed. Required telecommunication facilities were in place and would have been tested within the previous year by BPA. EWEB could call on BPA, under the terms of their Emergency Assistance Agreement, for assistance with emergency response and system restoration in the interim period of time until EWEB was prepared to assume its new function. WECC determined that this fact minimized the possibility of inappropriate or non-timely emergency response by EWEB. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB secured the services of a third party, GDS Associates, to assist in the development of an integrated system restoration plan. EWEB provided its system restoration plan to its BA to show that it has addressed mitigated the requirements of the Standard. | 2010-06-09 | 2011-02-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901664 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to train its operating personnel in the implementation of its restoration plan, in violation of EOP-005-1 R6. | EOP-005-1 | R6 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to train its operating personnel in the implementation of its restoration plan, the interim risk to the BPS was mitigated because BPA, which is EWEB's surrounding Balancing Authority (BA), acted as the TOP for EWEB's facilities and maintained plans and facilities for system restoration while EWEB completed its documentation to comply with the Standard. The plans addressed the requirements of EOP-005-1 R1, and continued to be adequate for restoration during the short period of time until EWEB plans were completed. EWEB could call on BPA, under the terms of their Emergency Assistance Agreement, for assistance with emergency response and system restoration in the interim, minimizing the possibility of inappropriate or non-timely emergency response by EWEB. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB secured the services of a third party, GDS Associates, to assist in the development of an integrated system restoration plan. EWEB provided its system restoration plan to its BA to show that it’s mitigated the requirements of the Standard. | 2010-06-09 | 2011-02-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901665 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to verify the restoration procedure by actual testing or by simulation, in violation of EOP-005-1 R7. | EOP-005-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to verify the restoration procedure by actual testing or by simulation, the interim risk to the BPS was mitigated because BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities and maintained plans and facilities for system restoration while EWEB completed its documentation to comply with the Standard. The plans addressed the requirements of EOP-005-1 R1, and continued to be adequate for restoration during the short period of time until EWEB plans were completed. EWEB could call on BPA, under the terms of their Emergency Assistance Agreement, for assistance with emergency response and system restoration, minimizing the possibility of inappropriate or non-timely response by EWEB. WECC reviewed EWEB's operating staff credentials and determined they were adequately trained to ensure reliable operations in the event of a partial or total shut down of the system. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB secured the services of a third party, GDS Associates, to assist in the development of an integrated system restoration plan. EWEB provided its system restoration plan to its BA to verify its restoration procedure by actual testing or simulation. | 2010-06-09 | 2011-02-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901657 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to have a plan to continue reliability operations in the event its control center becomes inoperable, in violation of EOP-008-0 R1. | EOP-008-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to have a plan to continue reliability operations in the event its control center becomes inoperable, the interim risk to the BPS was mitigated because EWEB had existing, proven practices for continuing reliable system operations following the loss of the main control center. EWEB’s dispatchers are experienced and know the system and the actions necessary to ensure continued reliable operations of the BPS in the event that its control center becomes inoperable. WECC determined that EWEB only lacked documentation, test records and training records that met the requirements of this Standard. After reviewing EWEB's operating staffs credentials, WECC determined they are adequately trained to ensure reliable operations in the event that its control center becomes inoperable. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 12/15/2009 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its loss of control center functionality plan on December 15, 2009. The plan contains a procedure for continued monitoring and operation of the electrical equipment under EWEB's control and addresses all the requirements set forth in EOP-008-0. EWEB trained its dispatchers on the updated plan. | 2009-12-15 | 2009-12-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901765 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB was not staffed with adequately trained operating personnel, in violation of PER-002-0 R1. | PER-002-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB was not staffed with adequately trained operating personnel, the interim risk to the BPS was mitigated because EWEB owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. EWEB's network is designed to receive power from BPA and serves EWEB's load. Disturbances of EWEB's facilities do not have a significant impact on the reliability of the surrounding Balancing Authorities (BAs) and TOPs. EWEB coordinated operations with BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities. EWEB’s operating staff had the knowledge, experience and training to maintain system reliability while further training required by this Standard was being obtained. WECC reviewed EWEB's operating staffs credentials and determined they were adequately trained to ensure reliable system operations. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its system operator training curriculum and credential maintenance reports as specified by the EWEB training program. Further, EWEB adequately trained its operating personnel as specified by the EWEB training program. | 2010-06-09 | 2010-08-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901766 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to have a training program for all operating personnel that are in positions directly responsible for complying with NERC standards and positions that have the primary responsibility, either directly or through communications with others, for real-time operation of the interconnected Bulk Electric System, in violation of PER-002-0 R2. | PER-002-0 | R2 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to have a training program for all operating personnel that are in positions directly responsible for complying with NERC standards and positions that have the primary responsibility, either directly or through communications with others, for real-time operation of the interconnected Bulk Electric System, the interim risk to the BPS was mitigated because EWEB owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. EWEB's network is designed to receive power from BPA and serves EWEB's load. Disturbances of EWEB's facilities do not have a significant impact on the reliability of the surrounding Balancing Authorities (BAs) and TOPs. EWEB coordinated operations with BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities. EWEB’s operating staff had the knowledge, experience and training to maintain system reliability while further training required by this Standard was being obtained. WECC reviewed EWEB's operating staff's credentials and determined they were adequately trained to ensure reliable system operations. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its system operator training curriculum and credential maintenance reports as specified by the EWEB training program. Further, EWEB adequately trained its operating personnel as specified by the EWEB training program. | 2010-06-09 | 2010-08-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901767 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB did not have a training program with training objectives and did not document initial and continuing training that addressed competencies and knowledge. The training staff was not identified, and their competencies in both knowledge of system operations and instructional capabilities was not identified, in violation of PER-002-0 R3. | PER-002-0 | R3 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB did not have a training program with staff training objectives and did not document initial and continuing training that addressed competencies and knowledge of its staff, the interim risk to the BPS was mitigated because EWEB owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. EWEB's network is designed to receive power from BPA and serves EWEB's load. Disturbances of EWEB's facilities do not have a significant impact on the reliability of the surrounding Balancing Authorities (BAs) and TOPs. EWEB coordinated operations with BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities. EWEB’s operating staff had the knowledge, experience and training to maintain system reliability while further training required by this Standard was being obtained. WECC reviewed EWEB's operating staff's credentials and determined they were adequately trained to ensure reliable system operations. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its system operator training curriculum and credential maintenance reports as specified by the EWEB training program. Further, EWEB adequately trained its operating personnel as specified by the EWEB training program. | 2010-06-09 | 2010-08-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901768 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel, in violation of PER-002-0 R4. | PER-002-0 | R4 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel, the interim risk to the BPS was mitigated because EWEB owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. EWEB's network is designed to receive power from BPA and serves EWEB's load. Disturbances of EWEB's facilities do not have a significant impact on the reliability of the surrounding Balancing Authorities (BAs) and TOPs. EWEB coordinated operations with BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities. EWEB’s operating staff had the knowledge, experience and training to maintain system reliability while further training required by this Standard was being obtained. WECC reviewed EWEB's operating staff's credentials and determined they were adequately trained to ensure reliable system operations. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its system operator training curriculum and credential maintenance reports as specified by the EWEB training program. Further, EWEB adequately trained its operating personnel as specified by the EWEB training program. | 2010-09-10 | 2012-03-02 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901536 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to staff all operating positions that have the primary responsibility, either directly or through communications with others, with personnel that are NERC-certified for the applicable functions for the real-time operation of the interconnected Bulk Electric System (BES), as well as for positions directly responsible for complying with NERC standards, in violation of PER-003-0 R1. | PER-003-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to staff all operating positions that have the primary responsibility, either directly or through communications with others, with personnel that are NERC-certified for the applicable functions for the real-time operation of the interconnected BES, as well as for positions directly responsible for complying with NERC standards, the interim risk to the BPS was mitigated because EWEB owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. EWEB's network is designed to receive power from BPA and serves EWEB's load. Disturbances of EWEB's facilities do not have a significant impact on the reliability of the surrounding Balancing Authorities (BAs) and TOPs. EWEB coordinated operations with BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities. EWEB’s operating staff had the knowledge, experience and training to maintain system reliability while EWEB's existing training program is upgraded and their operations staff becomes certified. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provided an email verifying completion of NERC certification for all applicable positions. EWEB also implemented a coordinated a training program for operating personnel, designed to promote reliable system operations. EWEB also requires the credential of NERC-certification for personnel that have primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected BPS and for positions directly responsible for complying with NERC standards. | 2010-06-09 | 2010-07-28 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901540 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period, in violation of TOP-002-1 R1. | TOP-002-2 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to maintain a set of current plans that are designed to evaluate options and set procedures for reliable operation through a reasonable future time period, the interim risk to the BPS was mitigated because the development of plans to evaluate options and set procedures for reliable operations through a reasonable future time period are long term planning activities that are normally performed on an annual basis. Thus, the most recent plans created by BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, were entirely adequate for ensuring BPS and EWEB system reliability during the short period of time until EWEB’s planning function became operational and EWEB completed its documentation to comply with the Standard. Further, EWEB's violation presented a primarily documentation issue because EWEB's planning guidelines for expected normal operations existed but needed to be extended into the future to address the requirements of TOP-002-2 R1. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its normal operations planning system operating procedure plan that is designed to evaluate reliable operations annually. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901541 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose, in violation of TOP-002-2 R2. | TOP-002-2 | R2 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose, the interim risk to the BPS was mitigated because system planning and design study functions are long-term activities that are normally performed on an annual basis. The most recent plans created by BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, were adequate for ensuring BPS and EWEB reliability during the short period of time until EWEB’s planning function became operational and the perspective of its operating personnel incorporated into the system planning. WECC also determined that long-term activities, while performed on an annual basis, are not critical for the reliability of the BPS. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its normal operations planning system operating procedure plan that is designed to evaluate reliable operations annually. Operating personnel participated in the implementation of this plan. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901542 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to coordinate its current day, next day, and seasonal planning and operations with the neighboring Balancing Authorities (BAs) and TOP and with its Reliability Coordinator (RC), so that normal Interconnection operation will proceed in an orderly and consistent manner, in violation of TOP-002-2 R4. | TOP-002-2 | R4 | Medium | Moderate | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to coordinate its current day, next day, and seasonal planning and operations with the neighboring BAs and TOP and with its RC, so that normal Interconnection operation will proceed in an orderly and consistent manner, the interim risk to the BPS was mitigated because current-day, next-day, and seasonal planning are operations planning activities that are normally performed on a long-term or annual basis. Thus, the most recent plans completed by BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities, were adequate to ensure that normal interconnection operations would proceed in an orderly and consistent manner during the short period of time until EWEB's planning function became operational and EWEB completed its documentation to comply with the Standard. The larger encompassing BA, which previously coordinated these activities, would be fully aware of EWEB planning and operations. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB completed its normal operations planning system operating procedure plan that is designed to evaluate reliable operations in an orderly and consistent manner with its neighbors. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901543 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns, in violation of TOP-002-2 R5. | TOP-002-2 | R5 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns, the interim risk to the BPS was mitigated because system planning to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns is an operational planning activity that is normally performed on a long-term or annual basis. The most recent plans created by BPA, which is EWEB's surrounding Balancing Authority and acted as the TOP for EWEB's facilities, were adequate for ensuring the reliability of the BPS and EWEB's system during the short period of time until EWEB’s planning function became operational and EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB developed winter and summer studies, on an annual basis to meet scheduled system configuration, generation dispatch and interchange scheduling and demand patterns. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901544 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to meet unscheduled changes in system configuration and generation dispatch, in violation of TOP-002-2 R6. | TOP-002-2 | R6 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to meet unscheduled changes in system configuration and generation dispatch, the interim risk to the BPS was mitigated because systems planning to meet the conditions listed in this requirement are operational planning activities that are normally performed on a long-term or annual basis. The most recent plans created by BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, were adequate for ensuring the reliability of the BPS and EWEB's system during the short period of time until EWEB’s planning function became operational and the perspective of its operating personnel incorporated, and EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB's winter and summer operating studies were performed to determine the response of the EWEB transmission and sub-transmission systems to single or multiple contingencies during peak load conditions with planned line outages. According to its Mitigation Plan, EWEB, developed and implemented procedures for conducting routine operational plans for its system. The procedures provide for active participation by operating personnel in the study processes. The procedures also include a method of coordinating and communicating current-day, next-day and seasonal operations with other entities within the interconnection. EWEB's operational plans are designed to meet scheduled, and unscheduled (N-1) system configuration, generation dispatch, interchange scheduling and demand patterns. The procedures also include methods for determining SOLs and, if necessary, for communicating such limits to other entities that share common facilities. The procedures include a protocol for communicating changes in system capabilities and characteristics to the BA or RC, if warranted. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901545 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to meet all System Operating Limits (SOLs) and Interconnection Reliability Operating Limits (IROLs), in violation of TOP-002-2 R10. | TOP-002-2 | R10 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to meet all SOLs and IROLs, the interim risk to the BPS was mitigated because SOLs and IROLs are operational planning activities that are normally performed on a long-term or annual basis. The most recent plans created by BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, were adequate for ensuring the reliability of the BPS and EWEB's system during the short period of time until EWEB’s planning function became operational and the perspective of its operating personnel incorporated into the system planning, and while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provided to WECC an email defining EWEB’s SOL methodology, its annual assessment of SOLs, and facility rating, on August 12, 2010. According to its Mitigation Plan, EWEB, developed and implemented procedures for conducting routine operational plans for its system. The procedures provide for active participation by operating personnel in the study processes. The procedures also include a method of coordinating and communicating current-day, next-day and seasonal operations with other entities within the interconnection. EWEB's operational plans are designed to meet scheduled, and unscheduled (N-1) system configuration, generation dispatch, interchange scheduling and demand patterns. The procedures also include methods for determining SOLs and, if necessary, for communicating such limits to other entities that share common facilities. The procedures include a protocol for communicating changes in system capabilities and characteristics to the BA or RC, if warranted. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901546 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to perform seasonal, next-day, and current-day Bulk Electric System (BES) studies to determine System Operating Limits (SOLs), in violation of TOP-002-2 R11. | TOP-002-2 | R11 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to perform seasonal, next-day, and current-day BES studies to determine SOLs, the interim risk to the BPS was mitigated because seasonal, next day, and current day studies are operational planning activities that are normally performed on a long-term annual basis. The most recent plans created by BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, were adequate for ensuring the reliability of the BPS and EWEB's system during the short period of time until EWEB’s planning function became operational and the perspective of its operating personnel incorporated into the system planning, and while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provided an email to WECC defining EWEB’s SOL methodology, its annual assessment of SOLs, and facility rating, on August 12, 2010. According to its Mitigation Plan, EWEB, developed and implemented procedures for conducting routine operational plans for its system. The procedures provide for active participation by operating personnel in the study processes. The procedures also include a method of coordinating and communicating current-day, next-day and seasonal operations with other entities within the interconnection. EWEB's operational plans are designed to meet scheduled, and unscheduled (N-1) system configuration, generation dispatch, interchange scheduling and demand patterns. The procedures also include methods for determining SOLs and, if necessary, for communicating such limits to other entities that share common facilities. The procedures include a protocol for communicating changes in system capabilities and characteristics to the BA or RC, if warranted. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901547 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to notify its Reliability Coordinator (RC) and Balancing Authority (BA) of changes in capabilities and characteristics in its transmission facility status and rating, in violation of TOP-002-2 R16. | TOP-002-2 | R16 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to notify its RC and BA of changes in capabilities and characteristics in its transmission facility status and rating, the interim risk to the BPS was mitigated because EWEB owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. EWEB coordinated operations with BPA, which is EWEB's surrounding BA and acted as the TOP for EWEB's facilities. EWEB’s operating staff had the knowledge, experience and training to adequately communicate changes in facility status or rating with its RC and BA during the short period of time while it upgrades its documentation to include this communication procedure. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB implemented a process to notify the RC of changes in capabilities and characteristics including transmission facility status and changes in transmission facility ratings via the Inter-Control Center Communications Protocol (ICCP). According to its Mitigation Plan, EWEB, developed and implemented procedures for conducting routine operational plans for its system. The procedures provide for active participation by operating personnel in the study processes. The procedures also include a method of coordinating and communicating current-day, next-day and seasonal operations with other entities within the interconnection. EWEB's operational plans are designed to meet scheduled, and unscheduled (N-1) system configuration, generation dispatch, interchange scheduling and demand patterns. The procedures also include methods for determining SOLs and, if necessary, for communicating such limits to other entities that share common facilities. The procedures include a protocol for communicating changes in system capabilities and characteristics to the BA or RC, if warranted. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901548 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB failed to communicate without any intentional time delay the information described in R1 through R16 to its Reliability Coordinator (RC), in violation of TOP-002-2 R17. | TOP-002-2 | R17 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to communicate without any intentional time delay the information described in TOP-002-2 R1 through R16 to its RC, the interim risk to the BPS was mitigated because EWEB owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. During the time of the violation, EWEB coordinated operations with BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities. EWEB’s operating staff had the knowledge, experience and training to adequately communicate changes in facility status or rating with its RC and BA during the short period of time while it upgraded its documentation to include the required communication procedure, and while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB began communicating the information described in R1 through R16 to its RC. According to its Mitigation Plan, EWEB, developed and implemented procedures for conducting routine operational plans for its system. The procedures provide for active participation by operating personnel in the study processes. The procedures also include a method of coordinating and communicating current-day, next-day and seasonal operations with other entities within the interconnection. EWEB's operational plans are designed to meet scheduled, and unscheduled (N-1) system configuration, generation dispatch, interchange scheduling and demand patterns. The procedures also include methods for determining SOLs and, if necessary, for communicating such limits to other entities that share common facilities. The procedures include a protocol for communicating changes in system capabilities and characteristics to the BA or RC, if warranted. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901549 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to maintain accurate computer models utilized for analyzing and planning system operations, in violation of TOP-002-2 R19. | TOP-002-2 | R19 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to maintain accurate computer models utilized for analyzing and planning system operations, the interim risk to the BPS was mitigated because at the time the violation occurred, BPA was maintaining accurate computer models utilized for analyzing and planning system operations. BPA is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities prior to EWEB's TOP registration. The most recent plans created by BPA were adequate for ensuring the reliability of the BPS and EWEB's system during the short period of time until EWEB’s planning function became operational, and EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB implemented a process to maintain accurate computer models utilized for analyzing and planning system operations. According to its Mitigation Plan, EWEB, developed and implemented procedures for conducting routine operational plans for its system. The procedures provide for active participation by operating personnel in the study processes. The procedures also include a method of coordinating and communicating current-day, next-day and seasonal operations with other entities within the interconnection. EWEB's operational plans are designed to meet scheduled, and unscheduled (N-1) system configuration, generation dispatch, interchange scheduling and demand patterns. The procedures also include methods for determining SOLs and, if necessary, for communicating such limits to other entities that share common facilities. The procedures include a protocol for communicating changes in system capabilities and characteristics to the BA or RC, if warranted. | 2010-06-09 | 2010-09-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901537 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to provide planned outage information daily to its TOP, Balancing Authority (BA) and Reliability Coordinator (RC) for scheduled generator outages planned for the day, in violation of TOP-003-0 R1. | TOP-003-0 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to provide planned outage information daily to its TOP, BA and RC for scheduled generator outages planned for the day, the interim risk to the BPS was mitigated because at the time of the violation, EWEB was communicating the required outage information to its adjacent entities and its BA. EWEB’s operating staff had the knowledge, experience and training to adequately provide planned outage information meeting this requirement during the short period of time while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the RC that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 3/16/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provides generator data hourly to BPA’s Ancillary Services webpage and daily to its RC via a PNSC Generation Availability Report. These reports provide planned outage information as required in the Standard. | 2010-03-16 | 2010-03-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901539 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas, in violation of TOP-003-0 R3. | TOP-003-0 | R3 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas, the interim risk to the BPS was mitigated because at the time of the violation, EWEB communicated the required outage information to its adjacent entities and Balancing Authority (BA). EWEB’s operating staff had the knowledge, experience and training to adequately plan and coordinate scheduled outages of telemetering, and control equipment and associated communication channels between the affected areas during the short period of time while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 3/16/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provides generator data hourly to BPA’s Ancillary Services webpage and daily to the Reliability Coordinator via a PNSC Generation Availability Report. These reports provide planned outage information as required in the Standard. | 2010-03-16 | 2010-03-24 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901441 | Settlement Agreement | On June 12, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to develop, maintain and implement formal policies and procedures to provide for transmission reliability, in violation of TOP-004-2 R6. | TOP-004-2 | R6 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to develop, maintain, and implement formal policies and procedures to provide for transmission reliability, the interim risk to the BPS was mitigated because EWEB operated its system in accordance with the requirements of the Standard, but was only lacking formal policies and procedures. At the time of the violation, EWEB’s operating staff had the knowledge, experience and training to adequately coordinate activities that impact reliability with adjacent TOP's and BPA, which is EWEB's surrounding Balancing Authority (BA) and acted as the TOP for EWEB's facilities, during the short period of time while EWEB completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB, jointly and individually, developed and maintained policies and procedures for its TOPs that address the execution and coordination of the requirements specified in R6 and its subrequirements. | 2010-06-09 | 2010-07-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901770 | Settlement Agreement | On May 5, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to specify a criterion that exempts generators from compliance with respect to maintaining a list of generators in its area that are exempt from following a voltage or Reactive Power schedule as described in R4 and R6.1, in violation of VAR-001-1 R3. | VAR-001-1 | R3 | Lower | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to specify a criterion that exempts generators from compliance with respect to maintaining a list of generators in its area that are exempt from following a voltage or Reactive Power schedule as described in VAR-001-1 R4 and R6.1, the interim risk to the BPS was mitigated because EWEB’s Balancing Authority (BA) and former TOP (BPA), had primary responsibility for voltage and reactive control, and EWEB had limited ability to influence these voltage parameters. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB provided its voltage and Reactive Power control system operating procedure that indicates a list of EWEB’s generators on its transmission system that are exempt from following a voltage or Reactive Power schedule. This is referenced in EWEB Dispatch Standing Order #1004. Further, EWEB notified the GO of all exempt generators on the EWEB transmission system by letter. This letter is sent to the GO annually. | 2010-06-09 | 2010-06-23 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901771 | Settlement Agreement | On May 5, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers, in violation of VAR-001-1 R6. | VAR-001-1 | R6 | Medium | Moderate | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers, the interim risk to the BPS was mitigated because EWEB's Balancing Authority (BA) and former TOP (BPA), had primary responsibility for voltage and reactive control while EWEB completed its documentation to comply with the Standard. Further, EWEB stated its reactive resources currently have very little effect on the BPS because EWEB is dependent on its BA to provide reactive supply and voltage control services on behalf of EWEB under a contract. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB and BPA implemented a process to monitor the status of the transmission reactive power resources within their respective areas. EWEB’s automatic voltage regulators and power system stabilizers are operated in service at all times that a unit is connected to the system. Further, the EWEB transmission and distribution dispatcher will direct the GOP to maintain the voltage schedule that it was given or remove the unit from service. | 2010-06-09 | 2010-06-23 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Eugene Water & Electric Board (EWEB) | NCR05153 | WECC200901772 | Settlement Agreement | On May 5, 2009, EWEB, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to EWEB upon its registration for the TOP function. EWEB was registered on the NERC Compliance Registry for the TOP function on May 8, 2009. EWEB submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. EWEB is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised EWEB that it was not required to register when asked by EWEB. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for EWEB. As a result, BPA formally informed EWEB on April 6, 2009 that it would not serve as EWEB's TOP. Therefore, EWEB had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective May 8, 2009, EWEB had failed to provide documentation to the Generator Owner (GO) specifying the required tap changes, a timeframe for making the change, and technical justification for these changes, in violation of VAR-001-1 R11. | VAR-001-1 | R11 | Lower | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that EWEB was assuming a new TOP function, which was a one-time registration issue. Although EWEB failed to provide documentation to the GO specifying the required tap changes, a timeframe for making the change, and technical justification for these changes, the interim risk to the BPS was mitigated because EWEB’s Balancing Authority (BA) and former TOP (BPA), had primary responsibility for voltage and reactive control while EWEB completed its documentation to comply with the Standard. EWEB had limited ability to influence these parameters. At the time of the violation, EWEB was purchasing voltage control and reactive support services through a contract with BPA. WECC determined that the issue with the violation was not related to the act that the system operators did not have documentation specifying tap changes, but was related to the fact that the documentation indicating tap changes and justification status had to be acknowledged and owned by EWEB, as a TOP. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of EWEB’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for EWEB's facility and that BPA did not need control for system reliability. EWEB resides in BPA's BA footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which EWEB was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as EWEB completing its TOP certification. BPA offered and provided other assistance to EWEB to ensure it had all the BPA resources and experience in helping EWEB obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. In addition, at the time of its registration for the TOP function, EWEB was addressing the requirements for its other functions as a Transmission Owner (TO), Transmission Provider (TP), Purchasing-Selling Entity (PSE), Load Serving Entity (LSE), Distribution Provider (DP), GO and Generator Operator (GOP). | 5/8/2009 (when EWEB registered as a TOP) | 6/9/2010 (Mitigation Plan Completion) | 0 | Self-Report | To mitigate this violation, EWEB engineering will determine the needed taps settings and communicate those to the GOs through a letter that includes the timeframe for making the changes and the technical justification for the changes. A copy of this letter has been provided to the EWEB dispatch office. | 2010-06-09 | 2010-06-23 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, BPA unexpectedly notified EWEB that BPA would no longer be acting as the TOP for EWEB. This notice was effective immediately. Consequently, EWEB was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) EWEB self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) EWEB did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102913 | Settlement Agreement | On August 19, 2011, NCPA, as a Generator Operator, submitted a Self-Report identifying a possible violation of VAR-002-1.1b R2. During an internal review of its procedures and data, NCPA discovered that the published generator voltage schedule was being exceeded on two units. Specifically, the actual voltages on NCPA's Collierville 230 kV units were running 1-2 kV higher than the published schedule with its Transmission Operator, Pacific Gas and Electric Company (PGAE). NCPA's failure to maintain the published generator voltage without an exemption from PGAE resulted in NCPA not meeting the defined voltage schedules for the Collierville generating facility. | VAR-002-1.1b | R2 | Medium | Moderate | WECC determined this issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because although the actual voltage was higher than the published voltage, on August 19, 2011, PGAE was made aware of the inconsistency and immediately determined the generator voltage needed to be reissued to match the higher voltage. In addition, during the periods of time in which the deviations from the schedule occurred, NCPA did not receive any notifications from the Transmission Operator indicating any area voltage concerns. | 8/2/2007 (when the Standard became mandatory and enforceable) | 11/18/2011 (Mitigation Plan completion) | 500 | Self-Report | On August 29, 2011, NCPA submitted a Mitigation Plan to WECC addressing the violation of VAR-002-1.1b R2. In accordance with the Mitigation Plan, NCPA met with PGAE to discuss analysis of the current voltage schedule. NCPA met with PGAE and reviewed data pertaining to the voltage schedule. As a result, PGAE agreed with NCPA's finding that the then current Collierville voltage schedule at that time was not feasible. PGAE requested additional information on the Collierville units, and NCPA supplied it to them. PGAE issued a new formal voltage schedule that NCPA is implementing and monitoring. NCPA also revised existing operating procedures to reflect the new voltage schedule and conducted refresher training with dispatchers on the new voltage schedule. | 2011-11-18 | 2012-02-22 | Does Not Contest | The approved Mitigation Plan completion date was extended by 57 days due to NCPA having to wait for PGAE's new voltage schedule. The receiving and implementing of the schedule took longer than anticipated. WECC determined that no adjustments to the penalty were warranted. There were no additional factors that warranted penalty adjustments.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901338 | Settlement Agreement | On March 20, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration effective February 6, 2009, SNPD did not manage, alarm, test, and/or actively monitor vital telecommunications facilities, in violation of COM-001-1 R2. | COM-001-1 | R2 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD did not manage, alarm, test, and/or actively monitor vital telecommunications facilities, the interim risk to the BPS was mitigated by the fact that SNPD telecommunication circuits were alarmed and monitored, while SNPD completed its documentation to comply with the Standard. SNPD operators had been trained on how to respond to alarms, and SNPD actively monitored all telecommunications facilities and was able to troubleshoot and repair any system that needed repairs. The interim risk to the BPS has been abated by the fact that SNPD had backup systems in place and its operators were always able to communicate with the entities involved in an event. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 1/8/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD completed the implementation of its capital asset management system which schedules and tracks completion of maintenance and testing of its telecommunication systems. | 2010-01-08 | 2010-04-01 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901339 | Settlement Agreement | On March 20, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD failed to have written operating instructions and procedures to enable continued operation during the loss of telecommunications facilities, in violation of COM-001-1 R5. | COM-001-1 | R5 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to have written operating instructions and procedures to enable continued operation during the loss of telecommunications facilities, the interim risk to the BPS was mitigated by the fact that SNPD had backup systems in place in case of the loss of primary telecommunications facilities. SNPD operators had been trained on how to respond to alarms, and SNPD actively monitored all telecommunications facilities and was able to troubleshoot and repair any system that needed repairs. The interim risk to the BPS has been abated by the fact that SNPD had backup systems in place and its operators were always able to communicate with the entities involved in an event. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 1/8/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD completed the implementation of its capital asset management system which schedules and tracks completion of maintenance and testing of its telecommunication systems. SNPD also prepared a document for the Operators that will describe the specific steps to take in case of a telecommunications failure. | 2010-01-08 | 2010-04-01 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901340 | Settlement Agreement | On March 20, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD failed to develop, maintain, and implement a set of plans to mitigate operating emergencies for (1) insufficient generating capacity; (2) on the transmission system; (3) load shedding; and (4) system restorations, in violation of EOP-001-0 R3. | EOP-001-0 | R3 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to develop, maintain, and implement a set of plans to mitigate operating emergencies for (1) insufficient generating capacity; (2) on the transmission system; (3) load shedding; and (4) system restorations, the interim risk to the BPS was mitigated by the fact that all of the requirements of EOP-001-0 were elements of emergency operations provided for in SNPD's transmission service agreement, Network Operating Agreement, and Technical Requirements for Interconnection with BPA. The plans contained in these documents were developed by BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, and were sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for SNPD to restate the agreements' provisions and incorporate them into its own plan addressing the requirements of EOP-001-0 R3. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was fully compliant with the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD developed and implemented an Emergency Operations Plan that addresses insufficient generation capacity and comprehensive load shedding plans. These plans entail extensive power flow studies to determine what actions system operators need to implement in the event of an emergency on SNPD's transmission system. Also, SNPD developed a detailed system restoration plan in the event of a partial or complete system black out from BPA, SNPD's TSP. SNPD needs to coordinate all emergency action plans with its BA and annually review and update as necessary. | 2010-04-28 | 2010-05-17 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901341 | Settlement Agreement | On March 20, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD failed to annually review and update its emergency plan, and to provide a copy of its updated emergency plans to its Reliability Coordinator (RC) and neighboring TOPs and Balancing Authorities (BAs), in violation of EOP-001-0 R6. | EOP-001-0 | R6 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to annually review and update its emergency plan, and to provide a copy of its updated emergency plans to its Reliability Coordinator (RC) and neighboring TOPs and Balancing Authorities (BAs), the interim risk to the BPS was mitigated by the fact that all of the requirements of EOP-001-0 were elements of emergency operations provided for in SNPD's transmission service agreement, Network Operating Agreement, and Technical Requirements for Interconnection with BPA. The plans contained in these documents were developed by BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, and were sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for SNPD to restate the agreements' provisions and incorporate them into its own plan addressing the requirements of EOP-001-0 R6. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD provided a copy of its updated emergency plans to its RC and neighboring entities. SNPD needs to annually review and update as necessary. | 2010-04-28 | 2010-05-17 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901342 | Settlement Agreement | On March 20, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to coordinate its emergency plans with the neighboring TOPs and Balancing Authorities (BAs) as appropriate, in violation of EOP-001-1 R7. | EOP-001-0 | R7 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to coordinate its emergency plans with the neighboring TOPs and Balancing Authorities (BAs) as appropriate, the interim risk to the BPS was mitigated by the fact that all of the requirements of EOP-001-0 were elements of emergency operations provided for in SNPD's transmission service agreement, Network Operating Agreement, and Technical Requirements for Interconnection with BPA. The plans contained in these documents were developed by BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, and were sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for SNPD to complete its emergency plans and coordinate them with the neighboring TOPs and BAs as appropriate. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD has established and maintained reliable communications between interconnected systems. | 2010-04-28 | 2010-05-17 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901384 | Settlement Agreement | On March 26, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD failed to have a restoration plan to reestablish its electrical system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels, in violation of EOP-005-1 R1. | EOP-005-1 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to have a restoration plan to reestablish its electrical system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels, the interim risk to the BPS was mitigated by the fact that the SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. The 115 kV local network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. As an acting TOP for SNPD's facilities, BPA maintained plans for system restoration, which met the requirements of EOP-005-1 and continued to be adequate for restoration during the short period of time until SNPD's plans were completed. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD implemented a restoration plan to reestablish its electric system in a stable and orderly manner in the event of a partial or total shutdown of the system. The plan includes all necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels. | 2010-04-28 | 2010-06-10 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901385 | Settlement Agreement | On March 26, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to develop restoration plans with a priority of restoring the integrity of the Interconnection, in violation of EOP-005-1 R3. | EOP-005-1 | R3 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to develop restoration plans with a priority of restoring the integrity of the Interconnection, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. The 115 kV local network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. As an acting TOP for SNPD's facilities, BPA maintained plans for system restoration, which addressed the requirements of EOP-005-1 and continued to be adequate for restoration during the short period of time until SNPD's plans were completed. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD developed its restoration plans with a priority of restoring the integrity of the Interconnection. | 2010-04-28 | 2010-06-10 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901386 | Settlement Agreement | On March 26, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to coordinate its restoration plans with the Generator Owners (GOs) and Balancing Authorities (BAs) within its area, its Reliability Coordinator (RC), and neighboring TOPs and BAs. | EOP-005-1 | R4 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to coordinate its restoration plans with the Generator Owners (GOs) and Balancing Authorities (BAs) within its area, its Reliability Coordinator (RC), and neighboring TOPs and BAs, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. The 115 kV local network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. As an acting TOP for SNPD's facilities, BPA maintained plans for system restoration, which met the requirements of EOP-005-1 and continued to be adequate for restoration during the short period of time until SNPD's plans were completed. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD coordinated its restoration plans with the GO and BA within its area, its RC, and neighboring TOs and BAs. | 2010-04-28 | 2010-06-10 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901387 | Settlement Agreement | On March 26, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to periodically test its telecommunications facilities needed to implement the restoration plan, in violation of EOP-005-1 R5. | EOP-005-1 | R5 | Medium | High | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to periodically test its telecommunications facilities needed to implement the restoration plan, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. The 115 kV local network is designed to receive power from BPA and serves SNPD’s load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. As an acting TOP for SNPD's facilities, BPA maintained plans for system restoration, which addressed the requirements of EOP-005 and continued to be adequate for restoration during the short period of time until SNPD's plans were completed. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD started periodic testing of its telecommunication facilities needed to implement the restoration plan. | 2010-04-28 | 2010-06-10 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901388 | Settlement Agreement | On March 26, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to train its operating personnel in the implementation of the restoration plan, in violation of EOP-005-1 R6. | EOP-005-1 | R6 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to train its operating personnel in the implementation of the restoration plan, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. The 115 kV local network is designed to receive power from BPA and serves SNPD’s load. The 115 kV local network is designed to receive power from BPA and serves SNPD’s load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. As an acting TOP for SNPD's facilities, BPA maintained plans for system restoration, which addressed the requirements of EOP-005-1 and continued to be adequate for restoration during the short period of time until SNPD's plans were completed. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD has trained its operating personnel in the implementation of the restoration plan, such training included simulated exercises where practicable. | 2010-04-28 | 2010-06-10 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901389 | Settlement Agreement | On March 26, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to verify the restoration procedure by actual testing or by simulation, in violation of EOP-005-1 R7. | EOP-005-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to verify the restoration procedure by actual testing or by simulation, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. The 115 kV local network is designed to receive power from BPA and serves SNPD’s load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. As an acting TOP for SNPD's facilities, BPA maintained plans for system restoration, which met the requirements of EOP-005-1 and continued to be adequate for restoration during the short period of time until SNPD's plans were completed. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD verified the restoration procedure by simulation. | 2010-04-28 | 2010-06-10 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901390 | Settlement Agreement | On March 26, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to have a plan to continue reliability operations in the event its control center becomes inoperable, in violation of EOP-008-0 R1. | EOP-008-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to have a plan to continue reliability operations in the event its control center becomes inoperable, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. SNPD's 115 kV local network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. This coordination would have allowed SNPD to continue reliable operations in the event its control center became inoperable. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD documented a plan to continue reliable operations of its system in the event SNPD's primary control center become inoperable. SNPD established a backup control center that allows continued reliability operations the event the main center inoperable. SNPD established a contingency plan where the backup control center shall not rely on data or voice communication from the main control facility. The contingency plan will include written procedures for all applicable requirements of the Standard. | 2010-04-28 | 2010-05-26 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901391 | Settlement Agreement | On March 31, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD was not staffed with adequately trained operating personnel, in violation of PER-002-0 R1. | PER-002-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD was not staffed with adequately trained operating personnel, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. SNPD's network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. This coordination would have allowed SNPD to provide reliable operation even without being staffed with adequately trained operating personnel because BPA had trained personnel available during the time of the violation. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD made sure that it was staffed with adequately trained operating personnel. SNPD provided its Operating Personnel Training Program, dated April 28, 2010, as evidence of compliance to WECC. | 2010-04-28 | 2010-05-17 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901392 | Settlement Agreement | On March 31, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to have a training program for all operating personnel that are in positions directly responsible for complying with NERC Reliability Standards and positions that have the primary responsibility, either directly or through communications with others, for real-time operation of the interconnected Bulk Electric System (BES), in violation of PER-002-0 R2. | PER-002-0 | R2 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to have a training program for all operating personnel that are in positions directly responsible for complying with NERC Reliability Standards and positions that have the primary responsibility, either directly or through communications with others, for real-time operation of the interconnected Bulk Electric System (BES), the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. SNPD's network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. This coordination would have allowed SNPD to provide reliable operation even in the absence of a training program, as required by this Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD implemented an Operating Personnel Training Program, dated April 28, 2010. SNPD's training program for operating personnel includes job descriptions, operating polices, regulatory requirements, training staff credentials and course outlines. The program also includes positions that require operations training, program criteria, and a process for training documentation. | 2010-04-28 | 2010-05-17 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901393 | Settlement Agreement | On March 31, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD did not have a training program with training objectives and did not document initial and continuing training that addressed competencies and knowledge. The training staff was not identified, and their competencies in both knowledge of system operations and instructional capabilities was not identified, in violation of PER-002-0 R3. | PER-002-0 | R3 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD did not have a training program with training objectives and did not document initial and continuing training that addressed competencies and knowledge. The training staff was not identified, and their competencies in both knowledge of system operations and instructional capabilities was not identified, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. SNPD's network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. This coordination would have allowed SNPD to provide reliable operation even in the absence of a training program addressing the requirements of PER-002-0 R3. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD provided its Operating Personnel Training Program, dated April 28, 2010, as evidence of compliance. SNPD's training program includes training objectives, a plan for initial and continuing training, dedicated training time, and is staffed with a qualified trainer. | 2010-04-28 | 2010-05-17 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901394 | Settlement Agreement | On March 31, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel, in violation of PER-002-0 R4. | PER-002-0 | R4 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel, the interim risk to the BPS was mitigated by the fact that SNPD owns and operates a 115 kV local network that contains no critical facilities identified under the critical facilities list with WECC. SNPD's network is designed to receive power from BPA and serves SNPD's load. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. This coordination would have allowed SNPD to provide reliable operation even in the absence of training involving at least five days per year of training drills using realistic simulations, as required by PER-002-0 R4. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD provided its Operating Personnel Training Program, dated April 28, 2010, as evidence of compliance. SNPD provides its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. | 2010-04-28 | 2010-05-17 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901325 | Settlement Agreement | On March 10, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to staff all operating positions that have the primary responsibility, either directly or through communications with others, with personnel that are NERC-certified for the applicable functions for the real-time operation of the interconnected BES, and positions directly responsible for complying with NERC standards, in violation of PER-003-0 R1. | PER-003-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to staff all operating positions that have the primary responsibility, either directly or through communications with others, with personnel that are NERC-certified for the applicable functions for the real-time operation of the interconnected BES, and positions directly responsible for complying with NERC standards, the interim risk to the BPS was mitigated by the fact that SNPD is imbedded within the BPA Balancing Area and has limited transmission connections to the Western Interconnection at 115 kV, thus reducing the risk to the BPS. SNPD currently coordinates operations with BPA. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. This coordination would have allowed SNPD to provide reliable operation although it failed to staff all operating positions that have the primary responsibility with personnel that are NERC-certified, as required by PER-003-0 R1. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 4/28/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD staffs operating positions with NERC-certified operators that have the primary responsibility for the real-time operation of the interconnected BES and complying with NERC reliability standards. SNPD provided a list of its transmission operators who had completed certificate training. | 2010-04-28 | 2010-05-26 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901533 | Settlement Agreement | On June 25, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose, in violation of TOP-002-2 R2. | TOP-002-2 | R2 | Medium | Moderate | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to ensure its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose, the interim risk to the BPS was mitigated by the fact that the development of plans to evaluate options and set procedures for reliable operation through a reasonable future time period are long-term planning activities that are normally performed on an annual basis. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. Thus, the most recent plans completed by BPA were entirely adequate for ensuring BES and SNPD system reliability during the short period of time until SNPD's planning function became operational. Further, SNPD operating personnel participated in the system planning and design study processes. However, the SNPD did not have a formal policy and/or procedure for verifying this coordination to provide compliance with TOP-002-2 R2. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 7/22/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD ensures that its operating personnel participate in the system planning and design study processes, so that these studies contain the operating personnel perspective and system operating personnel are aware of the planning purpose. SNPD provided its Electric Reliability Operations Procedure dated July 22, 2010 as proof of compliance. | 2010-07-22 | 2011-01-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901534 | Settlement Agreement | On June 25, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns, in violation of TOP-002-2 R5. | TOP-002-2 | R5 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns, the interim risk to the BPS was mitigated by the fact that system planning to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns is an operational planning activity that is normally performed on a long-term or annual basis. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities, while SNPD completed its documentation to comply with the Standard. Thus, the most recent plans completed by BPA were adequate for ensuring BES and SNPD system reliability during the short period of time until SNPD's planning function became operational. Further, SNPD could produce generation and load schedule information, but it did not have documentation to demonstrate how it uses this capability to meet system configurations and demand patterns. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 7/22/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD met all scheduled system configuration, generation dispatch and demand patterns. SNPD provided its Electric Reliability Operations Procedure dated July 22, 2010 as proof of compliance. | 2010-07-22 | 2011-01-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901535 | Settlement Agreement | On June 25, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to document its policy related to using uniform line identifiers when referring to transmission facilities of an interconnected network, in violation of TOP-002-2 R18. | TOP-002-2 | R18 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to document its policy related to using uniform line identifiers when referring to transmission facilities of an interconnected network, the interim risk to the BPS was mitigated by the fact that SNPD used uniform line identifiers when referring to its transmission facilities based on its historical communications with the BPA and neighboring TOPs. However, SNPD did not have a documented policy that addressed uniform nomenclature when referring to transmission equipment. Also, during the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 7/22/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD uses uniform line identifiers when referring to transmission facilities of an interconnected network. SNPD provided its Electric Reliability Operations Procedure dated July 22, 2010 as proof of compliance. | 2010-07-22 | 2011-01-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901530 | Settlement Agreement | On June 25, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD did not routinely perform comprehensive transient stability analysis to ensure that instability, uncontrolled separation, or cascading outages would not occur as a result of the most severe single contingency, in violation of TOP-004-2 R2. | TOP-004-2 | R2 | High | High | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD did not routinely perform comprehensive transient stability analysis to ensure that instability, uncontrolled separation, or cascading outages would not occur as a result of the most severe single contingency, the interim risk to the BPS was mitigated by the fact that operational planning to prevent instability, uncontrolled separation, or cascading outages due to the most severe single contingency is normally performed on a long-term basis. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities. Thus, the most recent stability analysis completed by BPA were adequate for ensuring BES and SNPD system reliability during the short period of time until SNPD could routinely perform its own comprehensive transient stability analyses. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 7/22/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD operates so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single contingency. SNPD provided its Electric Reliability Operations Procedure dated July 22, 2010 as proof of compliance. | 2010-07-22 | 2011-01-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901531 | Settlement Agreement | On June 25, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD did not routinely perform comprehensive transient stability analysis to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator, in violation of TOP-004-2 R3. | TOP-004-2 | R3 | High | High | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD did not routinely perform comprehensive transient stability analysis to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by its Reliability Coordinator, the interim risk to the BPS was mitigated by the fact that operational planning to prevent instability, uncontrolled separation, or cascading outages due to multiple outages as specified by its Reliability Coordinator is normally performed on a long-term basis. During the period of this violation, SNPD coordinated operations with BPA, which is SNPD's surrounding Balancing Authority and acted as the TOP for SNPD's facilities. Thus, the recent stability analysis completed by BPA was adequate for ensuring BES and SNPD system reliability during the short period of time until SNPD can routinely perform its own comprehensive transient stability analyses. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 7/22/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD committed to operate in a manner to protect against instability, uncontrolled separation, or cascading outages resulting from multiple outages, as specified by the WECC Reliability Coordinator. SNPD provided its Electric Reliability Operations Procedure dated July 22, 2010 as proof of compliance. | 2010-07-22 | 2011-01-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901532 | Settlement Agreement | On June 25, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to develop, maintain, and implement formal policies and procedures to provide for transmission reliability, in violation of TOP-004-2 R6. | TOP-004-2 | R6 | Medium | Moderate | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to develop, maintain, and implement formal policies and procedures to provide for transmission reliability, the interim risk to the BPS was mitigated by the fact that up until its registration became effective on February 6, 2009, SNPD relied on BPA as the Control Area operator and since then, coordination between BPA and SNPD related to planned outages, system switching, system facilities limits, and system operations to address voltage schedules and real and reactive power flow issues, while SNPD completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 7/22/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD individually and jointly with other TOPs, developed, maintained, and implemented formal policies and procedures to provide for transmission reliability. SNPD provided its Electric Reliability Operations Procedure dated July 22, 2010 as proof of compliance. | 2010-07-22 | 2011-01-31 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Snohomish County (SNPD) | NCR05335 | WECC200901529 | Settlement Agreement | On June 25, 2009, SNPD, in connection with its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with the Standards newly applicable to SNPD upon its registration for the TOP function. SNPD was registered on the NERC Compliance Registry for the TOP function on February 6, 2009. SNPD submitted Self-Reports and accompanying Mitigation Plans in a timely manner and completed the Mitigation Plans as anticipated. Additionally, WECC audited SNPD from January 17 through January 26, 2012 and found no compliance violations at the audit. SNPD is in the Bonneville Power Administration (BPA) Control Area. As the Control Area operator, BPA had registered as a TOP. Based on discussions with WECC, BPA believed that only it was required to register as a TOP and so advised SNPD that it was not required to register when asked by SNPD. After issuance of an unrelated registration decision in which FERC upheld the registration of an entity as a TOP and clarified TOP compliance responsibilities, BPA undertook an assessment to determine if it would serve as the TOP for SNPD. As a result, BPA formally notified SNPD on December 24, 2008 that it would not serve as SNPD's TOP. Therefore, SNPD had to register as a TOP and report itself as noncompliant with the applicable NERC Standards. Beginning on the date of its TOP registration, effective February 6, 2009, SNPD had failed to document its process for providing appropriate technical information concerning protective relay information to its operating personnel, in violation of TOP-006-1 R3. | TOP-006-1 | R3 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that SNPD was assuming a new TOP function, which was a one-time registration issue. Although, SNPD failed to document its process for providing appropriate technical information concerning protective relay information to its operating personnel, the interim risk was mitigated by the fact that SNPD provides protective relay information to its operating personnel, while SNPD completed its documentation to comply with the Standard. Also, the interim risk to the BPS was abated because BPA conducted a technical assessment of SNPD’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for SNPD's facility and that BPA did not need control for system reliability. SNPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA had the responsibility to ensure reliability within its BA footprint. During the period during which SNPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine real-time communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA did not believe that any additional risk to the BPS was experienced as SNPD completing its TOP certification. BPA offered and provided other assistance to SNPD to ensure it had all the BPA resources and experience in helping SNPD obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. WECC determined that SNPD used reasonable efforts upon learning of its newly assumed TOP function to ensure that no additional risk to the BPS was experienced as SNPD completed its TOP certification by fully engaging and coordinating with BPA. In addition, at the time of its registration for the TOP function, SNPD was addressing the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). | 2/6/2009 (when SNPD registered as a TOP) | 1/27/2010 (when Mitigation Plan was completed) | 0 | Self-Report | To mitigate this violation, SNPD provided its System Operations Policy dated January 27, 2010 to provide system operators protection system technical information and established a process to meet with system operators when protection systems change significantly. | 2010-01-27 | 2010-02-09 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on December 24, 2008, BPA unexpectedly notified SNPD that BPA would no longer be acting as the TOP for SNPD. This notice was effective immediately. Consequently, SNPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) SNPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) SNPD did not contest the violations.
2012-02-29 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC200900260 | Settlement Agreement | The entity as a Balancing Authority self-reported on September 22, 2009, that thirty (30) of the entity's Interchange Transaction Tags (tags), between June 14, 2009 and August 11, 2009, did not identify the ramp rates or start/stop times (Null tags). The entity reported that its default ramp rate for a Null tag in its Energy Management System (EMS) or interchange scheduler is 20 minutes for schedules inside or outside of the FRCC footprint. As evidenced in the tags, the default used by the entity and the other party for these Null tags was not the 20 minute ramp rate. The Null tags did not accurately include the effects of the varying ramp rates in its Schedule Interchange value to calculate Area Control Error (ACE). | BAL-005-0.1b | R11 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. The mismatch was only between a 10 or 20 minute ramp rate in the Scheduled Interchange between affected Balancing Authorities and there were no subsequent violations reported for Control Performance Standards (CPS1 and CPS2) for BAL-001-0a by the affected entities. 2. The only potential effect to the BPS has been a temporary increase in inadvertent energy during the ramp times. 3. The impact is also minimized due to the small number of the tags which had this mismatch in ramp times, and the ramp was only between a rate of ten minutes at one Balancing Authority and twenty minutes at the other Balancing Authority. 4. The MW profile ranged from 1 to 129 MW but the effect of mismatch of the ramp rates between the Balancing Authorities would have varied from 0 to 32 MW maximum depending on the MW size. | 6/14/2009 (Start date of first non-compliant tag) | 11/23/2009 (Mitigation Plan Completion) | $12,000 (for FRCC200900260, FRCC200900275 and FRCC200900276) | Self-Report | SEC submitted a Mitigation Plan on October 22, 2009 and further revised it on November 23, 2009 to include steps for modifying the electronic tag approval process to only approve tags that have defined ramp times. In addition to process modifications, SEC also changed the OATI webScheduler default ramp duration to 10 minutes to be consistent with the eastern interconnection; SEC also instituted a formal system operations practice addressing operator actions related to interchange schedule ramping and associated electronic tag processing. Institution of this practice also included the training of all system coordinators and associate system coordinators on the required information. | 2009-11-23 | 2010-09-10 | Neither Admits nor Denies | FRCC noted the strength of SEC's internal compliance program (ICP), in effect at the time of the violation and awarded mitigating credit because of it. The entity has a documented ICP that was recently reviewed by FRCC to verify the program included violation mitigation, corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP.
2012-02-29 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC200900275 | Settlement Agreement | From September 28, 2009 to October 2, 2009 FRCC performed an audit on SEC and discovered that on August 11, 2008, the entity disabled the Special Protection System (SPS), Black Creek Out Step Tripping (OST) Scheme, for the purpose of performing relay maintenance for approximately one hour. The entity failed to notify the entity's Energy Management Control Center (EMCC) of planned maintenance activity that would produce a temporary status change in the SPS. As a result, the entity, as a Balancing Authority and Transmission Operator, did not notify the affected Transmission Operators and Balancing Authorities of a change in status when one of its SPS was removed from service for approximately one hour on August 11, 2008. | PRC-001-1 | R6 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the SPS was out of service for one hour while the entity’s maintenance personnel were performing maintenance on the SPS. During the one hour, FRCC reviewed the system conditions and data and confirmed that no such condition existed that required the SPS to be armed or triggered. | 8/11/2008 (When the entity failed to notify the appropriate parties of the change in status of the SPS) | 8/11/2008 (When the SPS returned to service) | $12,000 (for FRCC200900260, FRCC200900275 and FRCC200900276) | Compliance Audit | SEC submitted a Mitigation Plan on November 9, 2009 for this violation. In accordance with the plan, SEC revised and put into effect a relay coordination practice which clearly identifies communication requirements associated with notification of affected Transmission Operators and Balancing Authorities of each change in SPS status to comply with NERC Reliability Standard PRC-001 R6. SEC also installed signs at SEC’s SPS facilities warning transmission services field personnel to contact SEC’s EMCC prior to removing SPS equipment from service. In addition, SEC provided awareness training for all applicable staff. | 2009-11-06 | 2009-12-21 | Neither Admits nor Denies | FRCC noted the strength of SEC's internal compliance program (ICP), in effect at the time of the violation and awarded mitigating credit because of it. The entity has a documented ICP that was recently reviewed by FRCC to verify the program included violation mitigation, corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP.
2012-02-29 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Seminole Electric Cooperative (SEC) | NCR00068 | FRCC200900276 | Settlement Agreement | From September 28, 2009 to October 2, 2009 FRCC performed an audit on SEC and discovered that SEC, as a Transmission Owner and Generator Owner, owns Special Protections Systems (SPS) and has a system maintenance and testing program. The program did not include the following: relays (R1.1.1), instrument transformers (R1.1.2) and communication systems (R1.1.3). In addition, the program did not include documentation the maintenance testing interval basis (R1.2) nor a summary of the testing procedure (R1.3) for all of the elements identified from June 18, 2007 until August 26, 2009. The entity’s current SPS maintenance and testing program has included these elements from August 27, 2009 to present. | PRC-017-0 | R1.1; R1.2; R1.3 | High | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity was performing the maintenance on the SPS relays and its associated components within the defined interval though they did not have a defined documented maintenance program. | 6/18/2007 (When the Standard became enforceable) | 8/27/2009 (Mitigation Plan completion) | $12,000 (for FRCC200900260, FRCC200900275 and FRCC200900276) | Compliance Audit | SEC submitted a Mitigation Plan on November 4, 2009 for this violation. In accordance with the plan, SEC revised and put into effect an SPS practice which clearly includes all SPS maintenance and testing program requirements, identification of SPS relays, instrument transformers, communications systems and batteries as outlined by the Standard. | 2009-08-27 | 2009-12-21 | Neither Admits nor Denies | FRCC noted the strength of SEC's internal compliance program (ICP), in effect at the time of the violation and awarded mitigating credit because of it. The entity has a documented ICP that was recently reviewed by FRCC to verify the program included violation mitigation, corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP.
2012-02-29 | FERC | NP12-18-000 | Midwest Reliability Organization (MRO) | Otter Tail Power Company (OTP) | NCR01023 | MRO201000152 | Settlement Agreement | During a regularly scheduled compliance audit conducted by MRO from February 15, 2010 through February 25, 2010, MRO discovered that OTP was in violation of PRC-005-1 R2. OTP had provided a list of all relays associated with the bulk electric system at randomly selected stations, and MRO then requested maintenance and testing records for each of 65 randomly selected relays and associated components at each station. MRO found that OTP lacked certain testing records in accordance with its Protection System maintenance and testing program, and therefore requested a full inventory of Protection System maintenance and testing records. MRO determined that OTP, as a Transmission Owner and Distribution Provider, failed to document all required evidence of equipment maintenance and testing, as required by the Standard. Specifically, MRO determined that OTP failed to maintain evidence for maintenance and testing of thirty protective microprocessor and solid state relays at seven transmission substations, as well as two station batteries at two generation stations. Per OTP's Protection System maintenance and testing program document for generation, OTP failed to provide 2009 testing records for the BITE test (cell impedance and strap resistance) of the station batteries at Big Stone Generating Station. At Coyote Generating Station, OTP failed to provide test records from 2007 to 2009. The plant computerized maintenance management systems generate recurring preventive maintenance work orders (PMs) to maintain and test station batteries but did not specify that cell impedance and strap resistance testing was required on these two stations. OTP has 781 Protection System devices subject to the Standard and failed to provide evidence of testing for approximately 4% of the devices. OTP has a total of 265 transmission protective relays, 27 generation protective relays, 28 transmission station batteries and 5 generation station batteries in its system. | PRC-005-1 | R2 (R2.1, R2.2) | High | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because although OTP failed to provide maintenance and testing records for thirty relays at seven substations and two station batteries at two generation stations, OTP provided records of specific gravity, temperature testing, and annual battery inspections during the entire period of the violation. Additionally, OTP monitored battery voltage continuously on the plant control system at both plants and the system would have alarmed the control room in the event of a low voltage condition. Half of the relays were identified as back-up relays and all but one of the relays were associated with 115 kV substations. On January 24, 2011, shortly after discovery of the violation, battery impedance and strap resistance testing was performed at Big Stone and Coyote Station. Furthermore, there were no relay misoperations on the 30 relay devices in question. | 6/18/2007 (when the Standard became mandatory and enforceable) | 01/24/2011 (when OTP completed mitigation activity) | 0 | Compliance Audit | On October 8, 2010, OTP submitted a Mitigation Plan to MRO to address the violation of PRC-005-1 R2. In accordance with the Mitigation Plan, OTP: (1) performed impedance testing and strap resistance testing on station batteries; (2) trained electricians on the requirements of OTP's Standard Operating Procedure related to PRC-005-1 for maintenance and testing of generation protection equipment, including training on impedance and strap resistance testing; (3) performed a full review of all bulk electric system (BES) assets to create an inventory list of all protection relays and associated protection system equipment; (4) reviewed all technician test reports for BES transmission and BES generation to ensure that there were no additional protection system elements that missed their maintenance and testing interval due date; and (5) performed maintenance and testing on any devices missing records identified during the inventory review. | 2011-01-24 | 2011-07-01 | Admits | OTP's internal compliance program (ICP), in place at the time of the violation, was considered by MRO to be a mitigating factor in the penalty determination. OTP's ICP is distributed to employees through a NERC Reliability Standards Compliance Policy (Policy) that is available to all employees through the company's intranet. Employees have also been informed of the Policy through OTP's employee newsletter and live communications and training. Several departments have added NERC Compliance key performance indicators (KPIs) to help emphasize compliance standards within the department’s responsibility. The Policy, the communications, and the KPIs have been used to educate employees on the OTP ICP and how OTP’s mission of reliable service shall be demonstrated through a commitment to compliance with all NERC Reliability Standards. The OTP Policy expressly states that its purpose is “To foster and sustain a culture of compliance that supports reliability of the Bulk Power System and strives to minimize the potential for violations of applicable requirements.” OTP’s Compliance Officer is a senior executive who reports directly to OTP’s President and CEO. The Compliance Officer is also authorized with independent access to the OTP Board of Directors and Audit Committee. OTP also has an Alternate Compliance Officer to provide additional senior executive support to the management of NERC compliance and reliability activities. To further support senior executive involvement in NERC compliance and reliability activities, the NERC Compliance Steering Committee includes several OTP senior-level executives, each of whom report directly to OTP’s President and CEO. In addition to the Mitigation Activity already completed, OTP will purchase a Power Communications Analyzer (Analyzer). The Analyzer will be used to test relay communications between substations, which will enhance reliability by ensuring that the protective relays are communicating. The Analyzer will be purchased within 60 days of approval of this Settlement Agreement by the Commission. OTP will also train its employees on how to use the Analyzer within 120 days of purchasing the Analyzer. The estimated cost of the Analyzer is approximately $13,500.
2012-02-29 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Covanta Mid-Conn Inc. (Covanta) | NCR10008 | NPCC201000217 | Settlement Agreement | On December 6, 2010, Covanta self-reported a violation of VAR-002-1 R1. NPCC determined that Covanta, as a Generator Operator, did not operate its Unit #5 Automatic Voltage Regulator (AVR) in automatic voltage control mode and failed to notify the Transmission Operator (TOP), CONVEX, as required by the Standard. The Unit #5 AVR was instead being operated in DC control mode. Covanta employees were operating under the assumption that the DC control mode automatically controlled voltage. However, after the manufacturer of the AVR performed an assessment and made minor repairs to the unit, an internal investigation concluded that the AVR DC mode only controlled field voltage and not terminal voltage. The site also houses a second generator, which was operated correctly. | VAR-002-1 | R1 | Medium | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because although the unit was not operated in automatic voltage control mode, voltage was maintained within an acceptable range during the period that the unit was operated in DC control mode. The South Meadow 5 unit had its AVR placed into automatic one day after having the manufacturer, GE, perform an assessment and make minor repairs to the affected unit. These repairs eliminated any risk associated with this violation and there have been no further violations of this standard on the South Meadow 5 unit. Additionally, Unit #5 is a 45 MVA unit, connected to the 115 kV system and has minimal impact on voltage control in the area. | 8/2/2007 (When the Standard became enforceable and mandatory) | 12/6/2010 (When the generator was placed in the correct mode and the TOP was notified) | $4,000 (for NPCC201000217 and NPCC201000218) | Self-Report | On December 21, 2010, Covanta submitted to NPCC a Mitigation Plan to address the violation of VAR-002-1 R1. In accordance with the Mitigation Plan, Covanta has: (1) placed the Unit #5 AVR in automatic voltage control mode and notified the TOP; (2) administered training to supervisors, other management and operators on VAR-002 requirements; (3) placed placards on AVR control switches as a reminder of the notification requirement; (4) updated start-up procedures and created checklists to include notification and status of AVR changes; and (5) installed an AVR alarming system. | 2011-03-07 | 2011-05-05 | Does Not Contest | Covanta had a documented internal compliance program in place at the time of the violation that NPCC considered neutral as a mitigating factor in determining the penalty.
2012-02-29 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Covanta Mid-Conn Inc. (Covanta) | NCR10008 | NPCC201000218 | Settlement Agreement | On December 6, 2010, Covanta self-reported a violation of VAR-002-1 R3. NPCC determined that Covanta, as a Generator Operator, did not operate its Unit #5 Automatic Voltage Regulator (AVR) in automatic voltage control mode and failed to notify the Transmission Operator (TOP), CONVEX, within 30 minutes as required by the Standard. The Unit #5 AVR was instead being operated in DC control mode. Covanta employees were operating under the assumption that the DC control mode automatically controlled voltage. However, after the manufacturer of the AVR performed an assessment and made minor repairs to the unit, an internal investigation concluded that the AVR DC mode only controlled field voltage and not terminal voltage. | VAR-002-1 | R3 | Medium | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because although the unit was not operated in automatic voltage control mode, voltage was maintained within an acceptable range during the period that the unit was operated in DC control mode. The South Meadow 5 unit had its AVR placed into automatic one day after having the manufacturer, GE, perform an assessment and make minor repairs to the affected unit. These repairs eliminated any risk associated with this violation and there have been no further violations of this standard on the South Meadow 5 unit. Additionally, Unit #5 is a 45 MVA unit, connected to the 115 kV system and has minimal impact on voltage control in the area. | 8/2/2007 (When the Standard became enforceable and mandatory) | 12/6/2010 (When the generator was placed in the correct mode and the TOP was notified) | $4,000 (for NPCC201000217 and NPCC201000218) | Self-Report | On December 21, 2010, Covanta submitted to NPCC a Mitigation Plan to address the violation of VAR-002-1 R3. In accordance with the Mitigation Plan, Covanta has: (1) placed the Unit #5 AVR in automatic voltage control mode and notified the TOP; (2) administered training to supervisors, other management and operators on VAR-002 requirements; (3) placed placards on AVR control switches as a reminder of the notification requirement; (4) updated start-up procedures and created checklists to include notification and status of AVR changes; and (5) installed an AVR alarming system. | 2011-03-07 | 2011-05-05 | Does Not Contest | Covanta had a documented internal compliance program in place at the time of the violation that NPCC considered neutral as a mitigating factor in determining the penalty.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC201000724 | Settlement Agreement | On August 14, 2009, a static wire (an overhead ground wire that functions to protect the conductor from lightning) on Tower 3478 separated and fell across several of IPL's transmission lines, causing various problems including a high impedance phase-to-ground fault, loss of distribution transformers and a boiler trip (Event). IPL believes the static line was previously damaged during a severe thunderstorm on August 4, 2009 when lightning struck four spans west of Tower 3478. From October 5, 2009 through November 15, 2010, ReliabilityFirst initiated and led a Compliance Investigation (CI) to determine the causes of this Event. As part of the CI, ReliabilityFirst investigated IPL and discovered a possible violation of COM-002-2 R2. Specifically, ReliabilityFirst discovered two occasions in which IPL, as a Balancing Authority (BA) and Transmission Operator (TOP), issued directives, but did not follow the communications protocol described in the Standard, known as three-part communications. In the first instance, the IPL system operator, as the TOP, issued a directive to the plant operator directing him to reset and close two breakers. The plant operator replied, "okay," rather than repeating the directive back as required by the Standard. In the second instance, the IPL system operator, as the TOP, issued a directive to the plant operator directing him to bring a unit back online. The plant operator replied, "okay," rather than repeating the directive back as required by the Standard. | COM-002-2 | R2 | Medium | High | ReliabilityFirst determined this violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors: (1) IPL operators issued the directives in a clear manner, as evidenced by the fact that IPL correctly implemented both directives; (2) IPL monitors all points of its system in real time through the IPL SCADA system; (3) the IPL TOP constantly monitors the actions of the IPL Generator Operators, and in this case, verified both directives; and (4) of the several hundred recordings that ReliabilityFirst analyzed, IPL failed to utilize three-part communications in only two instances. | 8/14/2009 (When the first instance occurred of failing to use three-part communication) | 8/14/2009 (When the last instance occurred of failing to use three-part communication) | $15,000 (for RFC201000724 and RFC201000725) | Compliance Investigation | On June 10, 2011, IPL submitted a Mitigation Plan to address the violation. In accordance with the Mitigation Plan, IPL (1) communicated to all Transmission and Generator Operators the importance of three-part communication; and (2) retrained all operating personnel with a third-party-supplied COM-002 training program. | 2011-08-30 | 2011-09-28 | Agrees/ Stipulates | ReliabilityFirst considered the following mitigating factors when determining the penalty amount: (1) certain aspects of IPL's compliance program, in effect at the time of the violation, including the fact that IPL's senior management is active in compliance and the emphasis on compliance training and self-assessments; and (2) IPL was proactive in reporting the Event on August 20, 2009, six days after it occurred. Although IPL is a subsidiary of AES Corporation (AES), ReliabilityFirst concluded that this is an attenuated connection and that other AES affiliates' prior conduct should not be considered in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Indianapolis Power & Light Company (IPL) | NCR00798 | RFC201000725 | Settlement Agreement | On August 14, 2009, a static wire (an overhead ground wire that functions to protect the conductor from lightning) on Tower 3478 separated and fell across several of IPL's transmission lines, causing various problems including a high impedance phase-to-ground fault, loss of distribution transformers and a boiler trip (Event). IPL believes the static line was previously damaged during a severe thunderstorm on August 4, 2009 when lightning struck four spans west of Tower 3478. From October 5, 2009 through November 15, 2010, ReliabilityFirst initiated and led a Compliance Investigation (CI) to determine the causes of this Event. As part of the CI, ReliabilityFirst investigated IPL and discovered a possible violation of PRC-004-1 R1. During the Event, IPL experienced three Misoperations. One Misoperation occurred when a breaker at the Hanna substation opened because the line relay did not receive the carrier blocking signal. This constituted a Misoperation because the relay operated for a fault not within a zone of protection. In addition, two Misoperations occurred when the Petersburg-Thompson 345 kV line primary ground relay and backup ground relay both failed to trip. The Protection System elements failed to operate within the specified time when a fault or abnormal condition occurred within their zone of protection. The relays determine fault direction from the polarizing current. During the Event, the currents from two of the generator step up transformers providing this polarizing current were out of phase with the other sources of polarizing current, effectively neutralizing the current. Thus, the relays did not receive the polarizing current required to operate. The Standard requires that if and to the extent that IPL recognized these Misoperations, IPL, as a Transmission Owner (TO), should have reported them to IPL on March 31, 2010. IPL failed to recognize these Misoperations until May 5, 2010 and reported them on May 12, 2010. Further, IPL's initial Corrective Action Plans did not clearly state the plans to correct the cause of the Misoperations. Thus, IPL failed to submit appropriate Corrective Action Plans for the Misoperations and therefore failed to analyze these Misoperations, as required by the Standard. | PRC-004-1 | R1 | High | Severe | ReliabilityFirst determined this violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors: (1) IPL utilizes the current polarizing circuit that caused the Misoperations in all of its primary and backup protection system schemes for its Petersburg-Thompson 345 kV line as well as the protection schemes of four other lines associated with the Petersburg substation; (2) IPL utilizes similar current polarizing circuit schemes at four other substations, but they are only similar in that autotransformer tertiary windings are used for ground relay polarizing sources; and (3) no other IPL substations use the summing logic or combination of multiple sources that was used at Petersburg. However, given that the current polarizing circuits are prevalent throughout IPL's substations, and that the current polarizing circuit was at issue during the Event, this violation could implicate additional problems with the polarizing current scheme. | 8/14/2009 (The day of the Misoperations) | 8/27/2011 (When IPL submitted its acceptable Corrective Action Plans) | $15,000 (for RFC201000724 and RFC201000725) | Compliance Investigation | On May 26, 2011, IPL submitted a Mitigation Plan to address the violation. In accordance with the Mitigation Plan, IPL (1) developed and implemented a Corrective Action Plan for the Hanna substation Misoperation whereby IPL replaced the spark gap tub and retuned the traps and tuning units; (2) developed and implemented a Corrective Action Plan for the Petersburg substation Misoperations whereby it will replace electro-mechanical line relays with microprocessor relays and add bi-directional direct transfer trip to the Protection System; (3) corrected the ground polarizing circuit issue by verifying primary current injection, visually inspecting the polarizing circuit path by a point-to-point physical verification of the wiring and analyzing digital fault recorder information and relay event data; (4) removed its generator step up transformer for Petersburg generating Unit 4 from the circuit until it inspects the current polarization for that unit; (5) made temporary changes to increase the sensitivity to the type of fault at issue in this incident including taking the out-of-step relay at the Petersburg substation out of service and moving the Petersburg-Thompson line fault detector from the individual breaker currents to the transmission line current; and (6) completely replaced the relay equipment at both ends of the Petersburg-Thompson transmission line. | 2011-12-31 | 2012-02-07 | Agrees/ Stipulates | ReliabilityFirst considered the following mitigating factors when determining the penalty amount: (1) certain aspects of IPL's compliance program, in effect at the time of the violation, including the fact that IPL's senior management is active in compliance and the emphasis on compliance training and self-assessments; and (2) IPL was proactive in reporting the Event on August 20, 2009, six days after it occurred. IPL has previously violated PRC-005-1 R1 and R2.1, which ReliabilityFirst treated as a closely related standard. ReliabilityFirst determined this was repetitive conduct and an aggravating factor. However, the aggravation is limited by the fact that PRC-005-1 addresses proactive maintenance and testing for Protection Systems, while PRC-004-1 addresses the corrective actions to take in response to a Misoperation. Further, IPL could not feasibly have tested the functionality of the corrective actions undertaken because that would require the outage of all four of its Petersburg units. Although IPL is a subsidiary of AES Corporation (AES), ReliabilityFirst concluded that this is an attenuated connection and that other AES affiliates' prior conduct should not be considered in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | AES Shady Point, LLC (AES Shady Point) | NCR01055 | SPP201000408 | Settlement Agreement | On August 16, 2010, AES Shady Point self-reported a violation of PRC-005-1 R1. AES Shady Point, as a Generator Owner, failed to include, in its generation Protection System maintenance and testing program, a description of the basis for its three-year relay testing interval, in violation of R1.1. Additionally, AES Shady Point had not documented testing intervals, or a basis for such intervals, for its station batteries, associated communication systems, DC control circuitry, and instrument transformers. Further, in violation of R1.2, AES Shady Point did not include, in its generation Protection System maintenance and testing program, a summary of maintenance and testing procedures for station batteries, associated communication systems, DC control circuitry, and instrument transformers. This violation affected 153 (100%) of AES Shady Point's Protection System devices: 85 relays, 2 associated communication systems, 45 instrument transformers, 1 station battery bank and 20 DC control circuits. This violation was the result of a lack of a comprehensive formal program for the scheduling and documentation of all the Protection System maintenance and testing at the AES Shady Point facility and instead, reliance on informal and undocumented program activity. | PRC-005-1 | R1; R1.1; R1.2 | High | Severe | SPP RE determined that AES Shady Point's violation of PRC-005-1 R1 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because it related to the failure to identify a basis for its three-year testing interval for its relays. The three-year interval was reasonable for the identified relays based on AES Shady Point's Transmission Operator (TOP)/Generator Operator (GOP)'s PRC-005-1 maintenance and testing procedures and did not materially affect the reliability of relay operation. For its batteries, AES Shady Point provided a manufacturer's maintenance document supporting its battery maintenance and testing procedures and intervals. AES Shady Point substantiated monthly visual inspections and voltage checks for its batteries from 2010 forward and substantiated battery load tests occurring on a six-year interval. For its instrument transformers, AES Shady Point stated it conducted visual inspections during outages and switch-yard walk throughs where accessible and provided documentation of commissioning tests. AES Shady Point's affected communication systems had been tested by its TOP/GOP in 1999 and 2011. AES Shady Point's control room operators continuously monitor 23 of its 85 station relays, its battery bank, its 161 kV station bus, its two associated communication paths, and multiple alarm points for its five station breakers. Finally, AES Shady Point's facility represents only 5% of its interconnected TOP's generating resources, and its generation plant is connected to the BPS at 161 kV with a maximum output of 320 MW. | 6/18/2007 (Date the Standard became mandatory and enforceable) | 4/8/2011 (Mitigation Plan completion) | $15,000 (for SPP201000408; SPP201000409; SPP201000410; and SPP201000411) | Self-Report | AES Shady Point developed a detailed PRC-005 maintenance and testing procedure which sets out the maintenance and testing intervals, as well as the basis for those intervals, for all of its PRC-005 Protection System devices. AES Shady Point reviewed and revised its existing Protection System maintenance and testing documents per PRC-005-1 R1 program requirements and implemented policy revisions. In addition, AES Shady Point set up the existing plant work management system to play a key role in documenting and reporting all activities related to the maintenance and testing of Protection System devices. Further, AES Shady Point will run initial quarterly reports of all Protection System maintenance and testing activities and recalibrate and correct as necessary. | 2011-04-08 | 2011-04-25 | Neither Admits nor Denies | AES Shady Point is a member of the AES corporate family of companies, which includes a total of 17 NERC registered affiliates. Although the AES Corporation itself is not a NERC registered entity, the NERC registered AES affiliates participate in an AES Corporate Compliance Program. Through its Compliance Program, the AES Corporation provides compliance oversight and support to its affiliates. When assessing the penalty, SPP RE considered AES Shady Point and its affiliates’ violation history and found that AES Shady Point’s affiliates had the following prior violations of the same standards and requirements as the instant violations. In the ReliabilityFirst Corporation region: AES Beaver Valley L.L.C. had a violation of PRC-005-1 R2, FAC-008-1 R1 and FAC-009-1 R1; AES Ironwood LLC had a violation of FAC-008-1 R1 and FAC-009-1 R1; AES Red Oak, L.L.C. had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2; and AES Warrior Run had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2. In the Texas Reliability Entity, Inc. region, AES Deepwater, Inc. had a previous violation of PRC-005-1 R1. As a result of these findings, SPP RE considered the instant violations as repeat violations and applied them as an aggravating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | AES Shady Point, LLC (AES Shady Point) | NCR01055 | SPP201000409 | Settlement Agreement | On August 16, 2010, AES Shady Point self-reported a violation of PRC-005-1 R2. AES Shady Point, as a Generator Owner, had failed to implement, per the Standard, its Protection System maintenance and testing programs as follows: 1) for its relay devices, AES Shady Point could not substantiate testing within a three-year interval for four (of 85) relays; 2) for its station batteries, AES Shady Point could not provide documentation of monthly battery maintenance and testing; 3) for its 20 DC control circuits, AES Shady Point could not provide documentation of the last test date; and 4) for its instrument transformers, AES Shady Point could not provide testing data after initial commission testing. This violation affected 72 (47%) out of 153 of AES Shady Point's Protection System devices. AES Shady Point failed to document testing as required by the Standard for 4 relays, 2 associated communication systems, 45 instrument transformers, 1 battery bank, and 20 DC control circuits. This violation was the result of a lack of a comprehensive formal program for the scheduling and documentation of all the Protection System maintenance and testing at the AES Shady Point facility and instead, reliance on informal and undocumented program activity. | PRC-005-1 | R2; R2.1; R2.2 | High | Moderate | SPP RE determined that AES Shady Point's violation of PRC-005-1 R1 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because it related to the failure to identify a basis for its three-year testing interval for its relays. The three-year interval was reasonable for the identified relays based on AES Shady Point's Transmission Operator (TOP)/Generator Operator (GOP)'s PRC-005-1 maintenance and testing procedures and did not materially affect the reliability of relay operation. For its batteries, AES Shady Point provided the manufacturer's battery maintenance document supporting its battery maintenance and testing procedures and intervals. AES Shady Point substantiated monthly visual inspections and voltage checks for its batteries from 2010 forward and substantiated battery load tests occurring on a six-year interval. For its instrument transformers, AES Shady Point stated it conducted visual inspections during outages and switch-yard walk throughs where accessible and provided documentation of commissioning tests. AES Shady Point's affected communication systems had been tested by its TOP/GOP in 1999 and 2011. AES Shady Point's control room operators continuously monitor 23 of its 85 station relays, its battery bank, its 161 kV station bus, its two associated communication paths, and multiple alarm points for its five station breakers. Finally, AES Shady Point's facility represents only 5% of its interconnected TOP's generating resources, and its generation plant is connected to the BPS at 161 kV with a maximum output of 320 MW. | 6/18/2007 (Date the Standard became mandatory and enforceable) | 6/3/2011 (Mitigation Plan completion) | $15,000 (for SPP201000408; SPP201000409; SPP201000410; and SPP201000411) | Self-Report | AES Shady Point provided current testing and maintenance results for all of its PRC-005 Protection Systems. This included: communication system carrier tests, monthly station and switchyard inspections, DC trip tests, monthly potential transformer and current transformer (CT) visual inspections, CT commissioning tests, relay tests, and weekly and monthly battery inspections and testing. Additionally, AES Shady Point provided evidence of staff training in NERC Standards and awareness and PRC-005 generation and Protection Systems. Appropriate staff and management personnel were tasked and trained to monitor the performance of maintenance and testing activity, and will be granted any authority needed to ensure the timely performance of the activities. AES Shady Point automated the scheduling and the documentation of all maintenance and testing activities to coincide with the schedules as developed and documented by the program. | 2011-06-03 | 2011-07-05 | Neither Admits nor Denies | AES Shady Point is a member of the AES corporate family of companies, which includes a total of 17 NERC registered affiliates. Although the AES Corporation itself is not a NERC registered entity, the NERC registered AES affiliates participate in an AES Corporate Compliance Program. Through its Compliance Program, the AES Corporation provides compliance oversight and support to its affiliates. When assessing the penalty, SPP RE considered AES Shady Point and its affiliates’ violation history and found that AES Shady Point’s affiliates had the following prior violations of the same standards and requirements as the instant violations. In the ReliabilityFirst Corporation region: AES Beaver Valley L.L.C. had a violation of PRC-005-1 R2, FAC-008-1 R1 and FAC-009-1 R1; AES Ironwood LLC had a violation of FAC-008-1 R1 and FAC-009-1 R1; AES Red Oak, L.L.C. had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2; and AES Warrior Run had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2. In the Texas Reliability Entity, Inc. region, AES Deepwater, Inc. had a previous violation of PRC-005-1 R1. As a result of these findings, SPP RE considered the instant violations as repeat violations and applied them as an aggravating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | AES Shady Point, LLC (AES Shady Point) | NCR01055 | SPP201000410 | Settlement Agreement | On August 13, 2010, AES Shady Point self-reported a violation of FAC-008-1 R1.2.1. As a Generator Owner, AES Shady Point had failed to include in its Facility Ratings Methodology all equipment required by FAC-008-1 R1.2.1. Specifically, the Ratings Methodology did not include transmission conductors and series and shunt compensation devices. Although the Facility Ratings Methodology addressed terminal equipment specific to each of AES Shady Point's generating units, it did not include other terminal equipment in the plant switchyard. The excluded switchyard equipment included: tubular bus conductors, circuit breakers, air disconnect switches and current transformers. | FAC-008-1 | R1; R1.2.1 | Medium | Severe | SPP RE determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AES Shady Point's Facility Ratings Methodology did not include series and shunt compensation devices because AES Shady Point does not have any such devices. Although AES Shady Point did not include a portion of its terminal equipment in its Facility Ratings Methodology, it did include the terminal equipment that was specific to each generation train, and neither the excluded terminal equipment nor transmission conductor represented a limiting factor in the rating of its generating facility. As a result, AES Shady Point's Facility Rating and the identification of the most limiting element was not altered by the inclusion of the omitted terminal equipment. Finally, AES Shady Point's facility represents only 5% of its interconnected Transmission Operator's generating resources, and its generation plant is connected to the BPS at 161 kV with a maximum output of 320 MW. | 6/18/2007 (Date the Standard became mandatory and enforceable) | 1/11/2011 (Mitigation Plan completion) | $15,000 (for SPP201000408; SPP201000409; SPP201000410; and SPP201000411) | Self-Report | AES Shady Point engaged an independent consulting firm to review and revise its Facilities Ratings Methodology to include all equipment specified in FAC-008-1. The Methodology was revised to include all of AES Shady Point's equipment required by FAC-008-1 R1.2.1. Appropriate staff and management personnel were tasked and trained to monitor any changes in the equipment that may affect the Facility Ratings Methodology or changes in ambient or operating conditions that could affect the resulting ratings. In addition, AES Shady Point will continue to monitor the NERC and/or SPP RE Standards that may require revisions of the methodology or the ratings. | 2011-01-11 | 2011-02-24 | Neither Admits nor Denies | AES Shady Point is a member of the AES corporate family of companies, which includes a total of 17 NERC registered affiliates. Although the AES Corporation itself is not a NERC registered entity, the NERC registered AES affiliates participate in an AES Corporate Compliance Program. Through its Compliance Program, the AES Corporation provides compliance oversight and support to its affiliates. When assessing the penalty, SPP RE considered AES Shady Point and its affiliates’ violation history and found that AES Shady Point’s affiliates had the following prior violations of the same standards and requirements as the instant violations. In the ReliabilityFirst Corporation region: AES Beaver Valley L.L.C. had a violation of PRC-005-1 R2, FAC-008-1 R1 and FAC-009-1 R1; AES Ironwood LLC had a violation of FAC-008-1 R1 and FAC-009-1 R1; AES Red Oak, L.L.C. had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2; and AES Warrior Run had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2. In the Texas Reliability Entity, Inc. region, AES Deepwater, Inc. had a previous violation of PRC-005-1 R1. As a result of these findings, SPP RE considered the instant violations as repeat violations and applied them as an aggravating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | AES Shady Point, LLC (AES Shady Point) | NCR01055 | SPP201000411 | Settlement Agreement | On August 13, 2010, AES Shady Point self-reported a violation of FAC-009-1 R1. As a Generator Owner, AES Shady Point had not established Facility Ratings inclusive of equipment ratings for all of its terminal equipment (tubular bus conductors, circuit breakers, air disconnect switches and current transformers) as it had not included these devices in its Facility Rating Methodology. Additionally, it failed to provide ratings for transmission conductors and series and shunt compensation devices. | FAC-009-1 | R1 | Medium | Severe | SPP RE determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). AES Shady Point's Facility Ratings Methodology did not include series and shunt compensation devices because AES Shady Point does not have any such devices. Although AES Shady Point did not include a portion of its terminal equipment in its Facility Ratings Methodology, it did include the terminal equipment that was specific to each generation train, and neither the excluded terminal equipment nor transmission conductor represented a limiting factor in the rating of its generating facility. As a result, AES Shady Point's Facility Rating and the identification of the most limiting element was not altered by the inclusion of the omitted terminal equipment. Finally, AES Shady Point's facility represents only 5% of its interconnected Transmission Operator's generating resources, and its generation plant is connected to the BPS at 161 kV with a maximum output of 320 MW. | 6/18/2007 (Date the Standard became mandatory and enforceable) | 1/11/2011 (Mitigation Plan completion) | $15,000 (for SPP201000408; SPP201000409; SPP201000410; and SPP201000411) | Self-Report | AES Shady Point engaged an independent consulting firm to review existing procedures, records, and other information to revise its Facilities Rating to become consistent with its revised Rating Methodology. AES Shady Point produced a spreadsheet containing a listing of all its FAC-008-1 R1.2.1 designated equipment along with the ratings of such equipment. These ratings were found to be consistent with AES Shady Point's revised methodology. Appropriate staff and management personnel were tasked and trained to monitor any changes in equipment, changes in ambient conditions and operating conditions that could affect the Facility Ratings. In addition, AES Shady Point will continue to monitor the NERC and/or SPP RE Standards that may require revisions of the methodology that may possible effect rating. | 2011-01-11 | 2011-02-24 | Neither Admits nor Denies | AES Shady Point is a member of the AES corporate family of companies, which includes a total of 17 NERC registered affiliates. Although the AES Corporation itself is not a NERC registered entity, the NERC registered AES affiliates participate in an AES Corporate Compliance Program. Through its Compliance Program, the AES Corporation provides compliance oversight and support to its affiliates. When assessing the penalty, SPP RE considered AES Shady Point and its affiliates’ violation history and found that AES Shady Point’s affiliates had the following prior violations of the same standards and requirements as the instant violations. In the ReliabilityFirst Corporation region: AES Beaver Valley L.L.C. had a violation of PRC-005-1 R2, FAC-008-1 R1 and FAC-009-1 R1; AES Ironwood LLC had a violation of FAC-008-1 R1 and FAC-009-1 R1; AES Red Oak, L.L.C. had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2; and AES Warrior Run had a violation of FAC-008-1 R1, FAC-009-1 R1, and PRC-005-1 R1 and R2. In the Texas Reliability Entity, Inc. region, AES Deepwater, Inc. had a previous violation of PRC-005-1 R1. As a result of these findings, SPP RE considered the instant violations as repeat violations and applied them as an aggravating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Texas Reliability Entity (Texas RE) | Buffalo Gap Wind Farm, LLC (Buffalo Gap) | NCR04025 | TRE201000118 | Settlement Agreement | During a compliance audit from March 9, 2010 through March 11, 2010, Texas RE determined that Buffalo Gap, as a Generator Owner, failed to produce any evidence of a documented Facility Ratings Methodology for the period prior to April 30, 2009, in violation of this Standard. | FAC-008-1 | R1 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because during the period of noncompliance, Buffalo Gap developed and submitted its Facility Ratings to the Reliability Coordinator and Transmission Operator in the form of a Resource Asset Registration Form/Generation Asset Registration Form since 2008. These forms included protection, transformer, breaker, reactive capability and operational related information. After Buffalo Gap documented its Facility Ratings Methodology, the Facility Ratings established from this methodology were consistent with the Facility Ratings developed and submitted to the Reliability Coordinator and Transmission Operator previously. Buffalo Gap owns one wind plant comprised of 3 units. | 6/28/2007 (When the Standard became enforceable and mandatory for Buffalo Gap) | 4/30/2009 (Mitigation Plan completion) | $30,000 (for TRE201000118 and TRE201000120) | Compliance Audit | Buffalo Gap employed a consulting firm to develop an entire compliance program including the development and documentation of a Facility Ratings Methodology. Buffalo Gap reviewed with a third-party engineering firm its Facility Ratings, to verify that all equipment and their ratings has been documented properly. Also, the AES Corporation, which is the parent company of Buffalo Gap, hired a full time NERC compliance manager to oversee AES's North American generation, transmission and distribution facilities. As part of Buffalo Gap's above and beyond actions, Buffalo Gap added spacers to 138 kV transmission lines and cleared out vegetation below 139 kV and overhead collection lines. Buffalo Gap estimates that the costs to implement the agreed to actions beyond those necessary to come into compliance with the FAC-008, PRC-005 and other Standards as discussed here and below, including (1) developing corporate key performance indicators related to NERC reliability compliance and (2) developing online NERC reliability standard training system for management and operators, are $275,101. | 2009-04-30 | 2011-05-02 | Neither Admits nor Denies | Texas RE considered the following factors when determining the penalty amount: 1. Aggravating factor: Texas RE determined that this was a repeat violation of FAC-008-1 R1 because four of Buffalo Gap's affiliates (AES Warrior Run, AES Red Oak, AES Ironwood and AES Beaver Valley) had previously violated this Standard. 2. Mitigating factors: Buffalo Gap has an established internal compliance program (ICP) that is widely disseminated throughout the company and is closely monitored by several tiers. Buffalo Gap’s operations manager serves as the company’s reliability compliance manager, and along with all other employees, has direct access to the CEO and board of directors. Buffalo Gap also participates in an AES Corporate Compliance Committee, where members meet with other AES entities to discuss compliance matters throughout each region. Additionally, Buffalo Gap’s senior management provides its full support and participation. Buffalo Gap states that it is sufficiently staffed and funded to maintain its compliance program. Furthermore, the Corporate Compliance Committee meets with AES senior management to provide an annual report regarding compliance matters.
2012-02-29 | FERC | NP12-18-000 | Texas Reliability Entity (Texas RE) | Buffalo Gap Wind Farm, LLC (Buffalo Gap) | NCR04025 | TRE201000120 | Settlement Agreement | During a compliance audit from March 9, 2010 through March 11, 2010, Texas RE discovered that Buffalo Gap, as a Generator Owner, did not have a generation Protection System maintenance and testing program (Program) in place prior to July 22, 2009 and as a result Buffalo Gap's did not have a Program addressing testing of its voltage and current sensing devices, in violation of PRC-005-1 R1. Buffalo Gap's July 22, 2009 maintenance and testing program document did not address in its scope, voltage and current sensing devices. Texas RE determined that the violation period should begin on Buffalo Gap’s Generator Owner NERC registration date of June 28, 2007. Buffalo Gap stated that although it did not have a Program addressing this Standard, its equipment was properly tested during the violation period because the equipment is new and its testing schedule for most of the devices will not begin for several years. Buffalo Gap's Protection System includes 98 current sensing devices and 15 voltage sensing devices, totaling 113 devices. These 113 devices represent 38.1% of Buffalo Gap's total 296 Protection System devices. | PRC-005-1 | R1 | High | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because Buffalo Gap did not exceed industry-accepted testing intervals for the devices in question and testing/maintenance on other protected devices had been properly performed. Buffalo Gap’s facilities' commercial operations began recently, with the first generation facility being commissioned in 2006, the second in June 2007, and third in July 2008. As a result, the testing schedule for most of the devices will not begin for several years. | 6/28/2007 (When the Standard became enforceable and mandatory for Buffalo Gap) | 11/15/2010 (Mitigation Plan completion) | $30,000 (for TRE201000118 and TRE201000120 ) | Compliance Audit | Buffalo Gap researched the manufacturer's recommendation and industry best practices to determine what the appropriate maintenance and testing scope should be for the voltage and current sensing devices that are used in the facilities' protection scheme. Once this was determined, Buffalo Gap’s Program was revised (effective November 15, 2010) to include maintenance and testing intervals and procedures for these devices. In addition, Buffalo Gap stated that it had performed an aerial inspection of its overhead electrical lines to verify that the actual installation matches the design. Also, Buffalo Gap showed through the audit that the devices in question were kept up with actual testing at the time of the audit. As part of Buffalo Gap's above and beyond actions, Buffalo Gap upgraded its physical security to its equipment buildings that house breaker, protective and communication devices for substations, to include changing out door locks and installed 24/7 monitored security systems. Last, a third party engineer consultant was hired to develop a new Program for PRC-005-2. Buffalo Gap estimates that the costs to implement the agreed to actions beyond those necessary to come into compliance with the FAC-008, PRC-005 and other Standards as discussed here and above, including (1) developing corporate key performance indicators related to NERC reliability compliance and (2) developing online NERC reliability standard training system for management and operators, are $275,101. | 2010-11-15 | 2011-05-02 | Neither Admits nor Denies | Texas RE considered the following factors when determining the penalty amount: 1. Aggravating factor: Texas RE determined that this was a repeat violation of PRC-005-1 R1 because three of Buffalo Gap's affiliates (AES Warrior Run, AES Red Oak and AES Beaver Valley) had previously violated this Standard. 2. Mitigating factors: Buffalo Gap has an established internal compliance program (ICP) that is widely disseminated throughout the company and is closely monitored by several tiers. Buffalo Gap’s operations manager serves as the company’s reliability compliance manager, and along with all other employees, has direct access to the CEO and board of directors. Buffalo Gap also participates in an AES Corporate Compliance Committee, where members meet with other AES entities to discuss compliance matters throughout each region. Additionally, Buffalo Gap’s senior management provides its full support and participation. Buffalo Gap states that it is sufficiently staffed and funded to maintain its compliance program. Furthermore, the Corporate Compliance Committee meets with AES senior management to provide an annual report regarding compliance matters.
2012-02-29 | FERC | NP12-18-000 | Texas Reliability Entity (Texas RE) | City of Austin dba Austin Energy (Austin Energy) | NCR04029 | TRE201000147 | Settlement Agreement | During a compliance audit on August 24, 2010 through August 26, 2010 (Audit), Austin Energy, as a Transmission Owner (TO) and a Distribution Provider (DP), failed to provide time-relevant documentation related to the basis for increasing the maintenance and testing intervals from four to five years for 301 of its electromechanical relays, and from four to six years for 61 of its microprocessor-based relays. The change of the maintenance intervals occurred in January 2009, while the documents provided during the audit that showed the basis for this change were created after the fact, on July 21, 2010 and August 26, 2010, respectively. The revised, signed Protection System Maintenance Program (PSMP) version 2, effective July 27, 2010, does contain the basis for maintenance intervals. Based on these facts, Texas RE determined that Austin Energy violated PRC-005-1 R1.1. Shortly before the start of the Audit, Austin Energy self-reported that Austin Energy’s version 1 of its PSMP failed to contain a summary of maintenance and testing procedures for associated communication systems. However, Austin Energy’s PSMP version 2 contains a summary of test procedures for associated communications. Based on these facts, Texas RE determined that Austin Energy violated PRC-005-1 R1.2. | PRC-005-1 | R1; R1.1; R1.2 | High | Lower | This violation posed a moderate risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the BPS because the reliability impact of failing to provide documentation in its PSMP of the basis (R1.1) for increasing the maintenance and testing intervals was for approximately 9% of the devices. 89.9% of the devices were maintained and tested. Also, increasing the intervals to five or six years is within the maximum intervals allowed, as referenced in PRC-005-2 Protection System Maintenance Supplementary Reference dated July 2009. In addition, Austin Energy's reliability report, which tracks relay failure rates, showed that the failure rates did not appear to be affected as a result of the change in periods. The total number of relays at issue (348) represents 9.1% of the total number of Protection System devices. Furthermore, relay technicians determined that only four relays were outside t+K2he acceptable testing period tolerances. Texas RE determined that the reliability impact of failing to provide documentation of summary of maintenance and testing procedures for associated communication systems (R1.2) presents a moderate risk to the BPS. Austin Energy was actually performing testing and maintenance on the communications associated with its Protection Systems and was following a maintenance and testing procedure but the maintenance and testing procedure was not documented. Austin Energy’s Mitigation Plan states that operations personnel generally followed historical, orally communicated procedures when performing tests of associated communication systems. Therefore, Texas RE determined that the violation of R1.2 posed a moderate risk to the BPS. | R1.1: 1/1/2009 (When the change in the maintenance intervals occurred ) R.1.2: 6/28/2007 (When Austin Energy was registered as a TO and DP) | 7/27/2010 (When PSMP version 2 took effect) | $40,000 (for TRE201000147, TRE201000148 and TRE201000149) | Compliance Audit (Austin Energy self-reported the violation after receiving an audit notification and after the auditors discovered a violation of PRC-008-0) | Effective July 27, 2010, Austin Energy consolidated and compiled all of its individual equipment/system Protection System maintenance processes and documentation into a single process document. Additionally, Austin Energy revised some specific equipment/system maintenance and testing requirements to improve the effectiveness of the program and reflect current NERC and industry information. Many of the maintenance and testing intervals and their basis and procedures have been updated. | 2011-08-19 | 2011-11-04 | Neither Admits nor Denies | Austin Energy had a transmission compliance program in effect at the time of the violation. The scope of this program includes all aspects of the organization that have any influence on the reliability of Austin Energy's transmission system and compliance with the NERC Reliability Standards and the Electric Reliability Council of Texas' (ERCOT) Protocols and Operating Guides. The program addresses such topics as a policy statement, organization structure, Austin Energy's registrations, a compliance plan process, how to draft compliance documents, Austin Energy self-compliance audit, responding to areas of non-compliance, compliance awareness and compliance training. Austin Energy annually reviews and modifies its compliance program. NERC compliance training is administered to employees on a regular basis. NERC compliance is included as part of the performance review of affected staff. Austin Energy’s compliance program is operated and managed independently of operations and consists of six full-time employees. Austin Energy has a named director of reliability compliance who has a direct reporting relationship to the deputy general manager/chief operating officer and an indirect reporting relationship to the general manager. Austin Energy has engaged the services of a consultant to provide support and guidance. Texas RE considered one prior violation by Austin Energy of IRO-001-1 R8 but did not apply it as an aggravating factor when determining the penalty amount because it involved a Standard that is not the same or similar to the instant violation. Texas RE gave a limited amount of mitigating credit to Austin Energy taking into account Austin Energy self-reported the violations of PRC-005-1 R1 and R2 shortly before the compliance audit.
2012-02-29 | FERC | NP12-18-000 | Texas Reliability Entity (Texas RE) | City of Austin dba Austin Energy (Austin Energy) | NCR04029 | TRE201000148 | Settlement Agreement | After receiving an audit notice and shortly before the start of Texas RE's compliance audit on August 24, 2010 through August 26, 2010, Austin Energy, as a Transmission Owner (TO) and a Distribution Provider (DP), self-reported a violation of PRC-005-1 R2.1. Austin Energy reported that it failed to test 348 electromechanical relays in accordance with the intervals defined in the previous version of its Protection System Maintenance Program (PSMP). This represents 9.1% of the total number (3,837) of Protection System devices. The amount of months past due for testing varied from a maximum of 39 months (six relays) to a minimum of less than one month (51 relays). Austin Energy stated that it tested 71 relays within the established four-year timeframe but could not provide documents to support its statement. | PRC-005-1 | R2; R2.1 | High | Lower | This violation posed a moderate risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the BPS because 4 relays out of 348, or 1.1%, were found to be outside tolerance. The total number of relays without documented maintenance and testing was 348 (9.1%) out of 3,837 total Protection System devices. In addition, Austin Energy was in fact performing testing and maintenance on the communications associated with its Protection Systems and thus was following a maintenance and testing procedure but the maintenance and testing procedure was not documented. Austin Energy’s Mitigation Plan states that its operations personnel generally followed historical, orally communicated procedures when performing tests of associated communication systems. | 6/28/2007 (When Austin Energy was registered as a TO and DP) | 3/3/2010 (When testing of all relays was completed) | $40,000 (for TRE201000147, TRE201000148 and TRE201000149) | Compliance Audit (Austin Energy self-reported the violation after receiving an audit notification and after the auditors discovered a violation of PRC-008-0) | According to its Mitigation Plan, Austin Energy completed the following actions: (1) For electromechanical protective relays – All of the electromechanical protective relays identified as being past due for testing have since been tested and maintained and are current per the effective maintenance intervals. (2) For microprocessor protective relays – Based on the revised process (PSMP version 2), Austin Energy completed all maintenance by August 19, 2011. The change in the process resulted in additional devices requiring maintenance/testing. For example, Austin Energy’s previous PSMP did not require testing of microprocessor-based relays because they are self-monitored and remotely alarmed. To enhance reliability, Austin Energy’s PSMP version 2 includes a twelve-year interval for such relays. (3) For associated communication systems – Based on PSMP version 2, Austin Energy completed all outstanding maintenance by August 2011. | 2011-08-19 | 2011-11-04 | Neither Admits nor Denies | Austin Energy had a transmission compliance program in effect at the time of the violation. The scope of this program includes all aspects of the organization that have any influence on the reliability of Austin Energy's transmission system and compliance with the NERC Reliability Standards and the Electric Reliability Council of Texas' (ERCOT) Protocols and Operating Guides. The program addresses such topics as a policy statement, organization structure, Austin Energy's registrations, a compliance plan process, how to draft compliance documents, Austin Energy self-compliance audit, responding to areas of non-compliance, compliance awareness and compliance training. Austin Energy annually reviews and modifies its compliance program. NERC compliance training is administered to employees on a regular basis. NERC compliance is included as part of the performance review of affected staff. Austin Energy’s compliance program is operated and managed independently of operations and consists of six full-time employees. Austin Energy has a named director of reliability compliance who has a direct reporting relationship to the deputy general manager/chief operating officer and an indirect reporting relationship to the general manager. Austin Energy has engaged the services of a consultant to provide support and guidance. Texas RE considered one prior violation by Austin Energy of IRO-001-1 R8 but did not apply it as an aggravating factor when determining the penalty amount because it involved a Standard that is not the same or similar to the instant violation. Texas RE gave a limited amount of mitigating credit to Austin Energy taking into account Austin Energy self-reported the violations of PRC-005-1 R1 and R2 shortly before the compliance audit.
2012-02-29 | FERC | NP12-18-000 | Texas Reliability Entity (Texas RE) | City of Austin dba Austin Energy (Austin Energy) | NCR04029 | TRE201000149 | Settlement Agreement | During a compliance audit of Austin Energy on August 24, 2010 through August 26, 2010 (Audit), Texas RE's Audit team found that Austin Energy, as a Transmission Owner and a Distribution Provider, failed to test seven Under Frequency Load Shedding (UFLS) relays in accordance with the intervals defined in the previous version of its Protection System Maintenance Program (PSMP). This represents 7.8% of the total 90 UFLS relays. The number of months past due for testing varied from a maximum of four months (for two relays) to less than a month (for one relay). Relays were overdue during ten of the fifteen months of this violation, from November 17, 2007 through January 28, 2009. | PRC-008-0 | R2 | Medium | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the BPS because the actual reliability impact of failing to test these seven relays within the defined four-year interval is minimal for the following reasons: 1. The seven relays represent 7.8% of the total of 90 UFLS relays. 2. The amount of months past due for testing varied from a maximum of four months (for two relays) to a minimum of less than one month (for one relay), with the weighted average for all seven past due relays being 2.7 months. 3. The testing for all UFLS relays is currently up-to-date. 4. Austin Energy performed the maintenance and testing on all of the UFLS equipment except for seven and none of the relays were attributed to a misoperation. 5. Austin Energy's relay technicians determined that no relays were outside of acceptable tolerances. | 11/17/2007 (When testing became overdue) | 1/28/2009 (When testing of the relays was completed) | $40,000 (for TRE201000147, TRE201000148 and TRE201000149) | Compliance Audit | All the UFLS relays identified as past due were tested and maintained per the currently effective maintenance intervals. The date on which the last relay test was completed was January 28, 2009. To ensure that this violation would not occur again, Austin Energy updated its processes to ensure that maintenance/testing of UFLS relays will be performed within prescribed intervals. Austin Energy also defined the method for reporting maintenance issues to the Reliability Coordinator. Austin Energy also implemented spot checks of its PSMP to ensure compliance. | 2009-01-28 | 2011-11-04 | Neither Admits nor Denies | Austin Energy had a transmission compliance program in effect at the time of the violation. The scope of this program includes all aspects of the organization that have any influence on the reliability of Austin Energy's transmission system and compliance with the NERC Reliability Standards and the Electric Reliability Council of Texas' (ERCOT) Protocols and Operating Guides. The program addresses such topics as a policy statement, organization structure, Austin Energy's registrations, a compliance plan process, how to draft compliance documents, Austin Energy self-compliance audit, responding to areas of non-compliance, compliance awareness and compliance training. Austin Energy annually reviews and modifies its compliance program. NERC compliance training is administered to employees on a regular basis. NERC compliance is included as part of the performance review of affected staff. Austin Energy’s compliance program is operated and managed independently of operations and consists of six full-time employees. Austin Energy has a named director of reliability compliance who has a direct reporting relationship to the deputy general manager/chief operating officer and an indirect reporting relationship to the general manager. Austin Energy has engaged the services of a consultant to provide support and guidance. Texas RE considered one prior violation by Austin Energy of IRO-001-1 R8 but did not apply it as an aggravating factor when determining the penalty amount because it involved a Standard that is not the same or similar to the instant violation.
2012-02-29 | FERC | NP12-18-000 | Texas Reliability Entity (Texas RE) | Loraine Windpark Project LLC (Loraine Windpark) | NCR11075 | TRE201000239 | Settlement Agreement | On February 14, 2011, Texas RE conducted a spot check of Loraine Windpark relating to IRO-001-1.1 R8 and TOP-001-1 R3, based on an incident report received by Texas RE from the Electric Reliability Council of Texas (ERCOT). On November 11, 2010, from 13:47 (all times CPT) until 16:30, Loraine Windpark, as a Generator Operator, failed to comply with a directive issued by ERCOT, the Reliability Coordinator and Transmission Operator, as required by IRO-001-1.1 R8. At the time of the directive, ERCOT was conducting a nodal market readiness test (Nodal LFC Test). ERCOT's directive was associated with the directed generation output levels for facilities within its control (Lone Wolf I and Lone Wolf II), as described below. At no time did Loraine Windpark notify ERCOT that complying with the directive would violate safety, equipment, or regulatory or statutory requirements. Tenaska Power Services (TPS) was under contract with Morgan Stanley SQ3 to provide Qualified Scheduling Entity (QSE) services for Loraine Windpark; Morgan Stanley SQ3 is the QSE for Loraine Windpark and the scheduling representative for Lone Wolf Wind Generator Resource (Lone Wolf). During the Nodal LFC Test on November 11, 2010 at 13:47:06, TPS was instructed by ERCOT to follow the nodal base points for Lone Wolf. At the time, Lone Wolf Unit 1 was over-generating by 37 MW and Lone Wolf Unit 2 was over-generating by 38 MW. The West-North stability limit was 1,691 MW with actual flow of 1,828 MW. The ERCOT System Operator did not reference the West-North stability limit during his call to the QSE scheduling representative for Lone Wolf. At 14:27:20, TPS called the ERCOT Operator and stated that the reason Lone Wolf was unable to follow its base points, as instructed by ERCOT, was due to Supervisory Control and Data Acquisition (SCADA) system control issues and that these issues were being investigated. Technicians for Lone Wolf discovered that a hardware failure was preventing the SCADA system from properly curtailing Lone Wolf Units 1 and 2. Lone Wolf had installed and successfully tested the SCADA system in advance of the Nodal LFC Test. Once the owners of Loraine Windpark became aware that ERCOT issued a directive (through ERCOT's instructions to TPS), they immediately responded to the curtailment directive by instructing the plant operators at the Lone Wolf facility to manually follow all requests to curtail while Loraine Windpark worked to correct the technical issues related to its SCADA system. The ERCOT Operator clarified that the instruction was considered to be a directive by ERCOT at 14:27:20, when Morgan Stanley SQ3 called the ERCOT Operator to explain the technical issues Lone Wolf was encountering with its SCADA system. Beginning approximately 16:30, Loraine Windpark began to manually follow its nodal base points as directed by ERCOT. | IRO-001-1.1 | R8 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because ERCOT ISO exercised mitigating alternatives (i.e. other generator reductions) to reduce flow on the West-North Stability Limit. However, the failure of Loraine Windpark to follow its base point (by dropping generation to 0 MW) contributed to the power flow exceeding, by approximately 137 MW, the West-North Stability Limit (consisting of six 345 kV lines). The West-North Stability Limit is a result of studies regarding the possible oscillations between generation in west Texas and generation in the rest of ERCOT due to various changes in topology and generation pattern. | 11/11/2010 at 13:47 (When Loraine Windpark should have complied with ERCOT's directive) | 11/11/2010 (When Loraine Windpark complied with ERCOT's directive, 163 minutes later) | $32,500 (for TRE201000239 and TRE201000240) | Spot Check | On March 9, 2011, Loraine Windpark submitted to Texas RE a Mitigation Plan to address the violations of IRO-001-1.1 R8 and TOP-001-1 R3. In accordance with the Mitigation Plan, Loraine Windpark has completed the following: (1) Immediately upon learning that Loraine Windpark had been directed to follow its nodal base points, and that plant operators had not yet curtailed the facility, Loraine Windpark instructed its plant operators to manually follow all TPS curtailment requests. Loraine Windpark instructed its plant operators, consistent with existing procedures, to give absolute priority to verbal curtailment requests. This manual curtailment process was continued for the remainder of the LFC Test and procedures allowing for manual curtailment are now in place. (2) Loraine Windpark established new procedures that detail the steps it and its service providers are required to take in the event that the ability to automatically follow the nodal base points is lost or compromised and also require Loraine Windpark operational personnel to respond manually to the nodal base points until such time as the ability to automatically curtail has been restored. (3) Loraine Windpark has implemented an automatic alert within its software which notifies if the SCADA communication signal is not operating and/or when there is a mismatch between its output and the corresponding nodal base point. TPS, at Loraine Windpark's request, also has implemented a backup alert that notifies Loraine Windpark of a mismatch between its output and the corresponding nodal base point. (4) Loraine Windpark has discussed the circumstances that occurred on November 11, 2010 and reviewed the communications from that day in detail with both TPS and plant operators. This process has allowed Loraine Windpark and its service providers to identify gaps in their communications protocols and to ensure better communication in the future. | 2011-03-03 | 2011-09-01 | Neither Admits nor Denies | In addition to the mitigation activity described herein, Loraine Windpark engaged a consultant shortly after the November 11, 2010 event to further strengthen its compliance program. Loraine Windpark has also actively informed other market participants with wind generation assets that ERCOT views its nodal basepoints as directives and not simply market signals. Texas RE considered these above and beyond measures as mitigating factors in the penalty determination. Loraine's internal compliance program was not a mitigating or aggravating factor in determining a penalty.
2012-02-29 | FERC | NP12-18-000 | Texas Reliability Entity (Texas RE) | Loraine Windpark Project LLC (Loraine Windpark) | NCR11075 | TRE201000240 | Settlement Agreement | On February 14, 2011, Texas RE conducted a spot check of Loraine Windpark relating to IRO-001-1.1 R8 and TOP-001-1 R3, based on an incident report received by Texas RE from the Electric Reliability Council of Texas (ERCOT). On November 11, 2010, from 13:47 (all times CPT) until 16:30, Loraine Windpark, as a Generator Operator, failed to comply with a directive issued by ERCOT, the Reliability Coordinator and Transmission Operator, as required by TOP-001-1 R3. At the time of the directive, ERCOT was conducting a nodal market readiness test (Nodal LFC Test). ERCOT's directive was associated with the directed generation output levels for facilities within its control (Lone Wolf I and Lone Wolf II), as described below. At no time did Loraine Windpark notify ERCOT that complying with the directive would violate safety, equipment, or regulatory or statutory requirements. Tenaska Power Services (TPS) was under contract with Morgan Stanley SQ3 to provide Qualified Scheduling Entity (QSE) services for Loraine Windpark; Morgan Stanley SQ3 is the QSE for Loraine Windpark and the scheduling representative for Lone Wolf Wind Generator Resource (Lone Wolf). During the Nodal LFC Test on November 11, 2010 at 13:47:06, TPS was instructed by ERCOT to follow the nodal base points for Lone Wolf. At the time, Lone Wolf Unit 1 was over-generating by 37 MW and Lone Wolf Unit 2 was over-generating by 38 MW. The West-North stability limit was 1,691 MW with actual flow of 1,828 MW. The ERCOT System Operator did not reference the West-North stability limit during his call to the QSE scheduling representative for Lone Wolf. At 14:27:20, TPS called the ERCOT Operator and stated that the reason Lone Wolf was unable to follow its base points, as instructed by ERCOT, was due to Supervisory Control and Data Acquisition (SCADA) system control issues and that these issues were being investigated. Technicians for Lone Wolf discovered that a hardware failure was preventing the SCADA system from properly curtailing Lone Wolf Units 1 and 2. Lone Wolf had installed and successfully tested the SCADA system in advance of the Nodal LFC Test. Once the owners of Loraine Windpark became aware that ERCOT issued a directive (through ERCOT's instructions to TPS), they immediately responded to the curtailment directive by instructing the plant operators at the Lone Wolf facility to manually follow all requests to curtail while Loraine Windpark worked to correct the technical issues related to its SCADA system. The ERCOT Operator clarified that the instruction was considered to be a directive by ERCOT at 14:27:20, when Morgan Stanley SQ3 called the ERCOT Operator to explain the technical issues Lone Wolf was encountering with its SCADA system. Beginning approximately 16:30, Loraine Windpark began to manually follow its nodal base points as directed by ERCOT. | TOP-001-1 | R3 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because ERCOT ISO exercised mitigating alternatives (i.e. other generator reductions) to reduce flow on the West-North Stability Limit. However, the failure of Loraine Windpark to follow its base point (by dropping generation to 0 MW) contributed to the power flow exceeding, by approximately 137 MW, the West-North Stability Limit (consisting of six 345 kV lines). The West-North Stability Limit is a result of studies regarding the possible oscillations between generation in west Texas and generation in the rest of ERCOT due to various changes in topology and generation pattern. | 11/11/2010 at 13:47 (When Loraine Windpark should have complied with ERCOT's directive) | 11/11/2010 (When Loraine Windpark complied with ERCOT's directive, 163 minutes later) | $32,500 (for TRE201000239 and TRE201000240) | Spot Check | On March 9, 2011, Loraine Windpark submitted to Texas RE a Mitigation Plan to address the violations of IRO-001-1.1 R8 and TOP-001-1 R3. In accordance with the Mitigation Plan, Loraine Windpark has completed the following: (1) Immediately upon learning that Loraine Windpark had been directed to follow its nodal base points, and that plant operators had not yet curtailed the facility, Loraine Windpark instructed its plant operators to manually follow all TPS curtailment requests. Loraine Windpark instructed its plant operators, consistent with existing procedures, to give absolute priority to verbal curtailment requests. This manual curtailment process was continued for the remainder of the LFC Test and procedures allowing for manual curtailment are now in place. (2) Loraine Windpark established new procedures that detail the steps it and its service providers are required to take in the event that the ability to automatically follow the nodal base points is lost or compromised and also require Loraine Windpark operational personnel to respond manually to the nodal base points until such time as the ability to automatically curtail has been restored. (3) Loraine Windpark has implemented an automatic alert within its software which notifies if the SCADA communication signal is not operating and/or when there is a mismatch between its output and the corresponding nodal base point. TPS, at Loraine Windpark's request, also has implemented a backup alert that notifies Loraine Windpark of a mismatch between its output and the corresponding nodal base point. (4) Loraine Windpark has discussed the circumstances that occurred on November 11, 2010 and reviewed the communications from that day in detail with both TPS and plant operators. This process has allowed Loraine Windpark and its service providers to identify gaps in their communications protocols and to ensure better communication in the future. | 2011-03-03 | 2011-09-01 | Neither Admits nor Denies | In addition to the mitigation activity described herein, Loraine Windpark engaged a consultant shortly after the November 11, 2010 event to further strengthen its compliance program. Loraine Windpark has also actively informed other market participants with wind generation assets that ERCOT views its nodal basepoints as directives and not simply market signals. Texas RE considered these above and beyond measures as mitigating factors in the penalty determination. Loraine's internal compliance program was not a mitigating or aggravating factor in determining a penalty.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Central Lincoln People's Utility District (CLPD) | NCR05062 | WECC201002251 | Settlement Agreement | On October 6, 2010, CLPD self-reported a violation of PRC-005-1 R2.1. CLPD, as a Distribution Provider, failed to test the DC circuitry of five circuit breakers located at its Florence Substation within the defined time intervals specified in its PRC-005 Protection System Maintenance and Testing plan (Plan). Although it could provide maintenance and testing records for DC circuitry testing and maintenance at its Florence substation between April 17, 2008 and November 4, 2010, records for these devices were not consistent with the intervals prescribed under its Plan. CLPD failed to provide evidence that it maintained and tested 100% of its DC circuitry at the Florence substation within defined intervals. | PRC-005-1 | R2.1 | High | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the BPS equipment was backed up by redundant CLPD Protection System equipment and Bonneville Power Administration Protection System equipment. | 04/09/2008 (date after CLPD had mitigated its previous PRC-005-1 R2 violation) | 11/4/2010 (date Mitigation Plan was completed) | 20000 | Self-Report | On December 2, 2010, CLPD submitted a revised Completed Mitigation Plan outlining the following actions undertaken to mitigate the violation: 1. CLPD updated inspections forms to include recorded battery charger amperage and voltage testing; 2. CLPD updated breaker trip checks (including DC control circuitry), procedure and documentation; and 3. CLPD implemented an annual PRC-005 training program to ensure the Maintenance and Testing Plan is followed. | 2010-11-04 | 2011-02-08 | Neither Admits nor Denies | This violation was CLPD's second violation of PRC-005-1 R2. WECC had previously determined that CLPD violated the Standard from June 18, 2007 to April 8, 2008, because CLPD did not have a maintenance and testing program pursuant to PRC-005-1 R1 and because CLPD failed to provide evidence of maintenance and testing pursuant to R2. In the instant case, although CLPD did have a maintenance and testing program in place, and CLPD could provide some evidence of DC circuitry maintenance and testing, CLPD did not adhere to maintenance and testing intervals prescribed by its program. WECC determined that the instant violation is a separate instance of noncompliance and considered the prior violation to be an aggravating factor in assessing the penalty.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Clatskanie People's Utility District (CPUD) | NCR05100 | WECC201102369 | Settlement Agreement | On January 13, 2011 WECC performed an Off-Site Audit. CPUD maintained the position that it was not subject to PRC-005-1 because its distribution facilities were radial. However, based on CPUD's one-line diagrams, WECC determined that CPUD's Wauna Substation was not radial because it was connected to the distribution side of the station. CPUD provided as evidence of compliance its Transmission Protection System Maintenance and Testing Program dated August 19, 2008, which addressed the requirements of PRC-005-1 R1. Accordingly, WECC determined that CPUD violated this Standard because it did not have a maintenance and testing program from June 18, 2007 until August 19, 2008. This Standard applies to CPUD's Distribution Provider function. | PRC-005-1 | R1 | High | Severe | WECC determined that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because the protection devices involved in the violation are located at a single 230 kV/13.8 kV station connected the BPS, with a limited generation output of 52 MW. | 2007-06-18 | 2008-08-19 | $25,000 (Settlement of WECC201002369 and WECC201002370) | Off-Site Audit | On January 13, 2011, CPUD submitted a Mitigation Plan, stating that it had a Protection System Maintenance and Testing program in place since August 19, 2008 and therefore had mitigated the violation as of this date. | 2010-12-16 | 2012-02-23 | Agrees/ Stipulates | WECC determined that there were no aggravating factors to be considered when determining the penalty amount. Mitigating factors considered by WECC: (1) CPUD took voluntary corrective actions to remediate both violations; (2) This is CPUD's first violation of this Standard; (3) CPUD was cooperative with WECC; (4) There was no evidence that CPUD tried to conceal the violations; and (5) WECC found no evidence that the violations were intentional.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Clatskanie People's Utility District (CPUD) | NCR05100 | WECC201102370 | Settlement Agreement | On January 13, 2011 WECC performed an Off-Site Audit and discovered that CPUD had failed to maintain 7 of its 8 relays (87.5%) within the four-year interval defined in its Maintenance and Testing Program and had not maintained any of its current transformers (100%) within the same four-year interval. WECC determined that according to four-year intervals specified in its Maintenance and Testing Program, CPUD should have tested its current transformers in 2005 and 2009 but failed to do so. WECC determined that CPUD has not tested some of its Protection System devices since June 18, 2007, when this Standard went into effect. This Standard applies to CPUD's Distribution Provider function. | PRC-005-1 | R2.1 | High | Severe | WECC determined that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because the protection devices involved in the violation are located at a single 230 kV/13.8 kV station connected the BPS, with a limited generation output of 52 MW. In addition, CPUD is taking interim measures to reduce the risk to the BPS by having an officer monitor testing cycles and report through the Internal Compliance Committee to the General Manager, who is in charge of assuring that maintenance and testing cycles are met. | 2007-06-18 | 2013-06-30 | $25,000 (Settlement of WECC201002369 and WECC201002370) | Off-Site Audit | On January 13, 2011, CPUD submitted a Mitigation Plan, which requires it to identify its protection equipment and develop a firm schedule for maintenance and testing and perform maintenance and testing on that equipment. CPUD plans to test its protection equipment no later than June 30, 2013, when the paper mill associated with its facility is scheduled for a cold outage. Absent an outage of the paper mill, CPUD cannot safely and reliably perform the necessary maintenance and testing. CPUD stated that it would perform the maintenance and testing earlier if the paper mill goes into an outage. In addition, CPUD adopted an updated maintenance and testing program that calls for ten-year testing cycles for solid state relays and associated equipment and as needed testing of Current Transformers and Potential Transformers based on periodic visual inspections or any anomalous readings from continuous electronic monitoring. CPUD stated that according to industry standards, ten-year cycles are a reasonable time frame for solid state relays. | 6/30/2013 (expected) | TBD | Neither Admits nor Denies | WECC determined that there were no aggravating factors to be considered when determining the penalty amount. Mitigating factors considered by WECC: (1) CPUD took voluntary corrective actions to remediate both violations; (2) This is CPUD's first violation of this Standard; (3) CPUD was cooperative with WECC; (4) There was no evidence that CPUD tried to conceal the violations; and (5) WECC found no evidence that the violations were intentional.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Modesto Irrigation District (MID) | NCR05244 | WECC201102390 | Settlement Agreement | From February 7, 2011 to February 18, 2011, WECC performed an on-site audit of MID's compliance with various Reliability Standards. The Audit Team requested that MID provide maintenance and testing records for its transmission protection equipment. After reviewing these records, WECC determined that MID, as a Generator Owner and Transmission Owner, failed to provide documentation that Protection System devices were maintained and tested within the defined intervals. Specifically, three of MID's protective relays located on the transmission systems at MID's Claus and Santa Cruz substations were not maintained or tested within the intervals defined in MID's Protection System Maintenance and Testing Program (Program). MID had previously never considered its internal 115 kV system as part of the bulk electric system (BES) because the 115 kV lines in question are radial lines and are looped into a common bus. Because of this, the relays on MID's 115 kV system were not included in the BES test database. The device with the longest missed testing interval was Clau115N_87Babc. According to the Program, this device has a four year maintenance and testing interval and can be tested up to one year after the interval. The device was last tested on March 10, 2004; thus, it should have been tested on March 10, 2009. MID failed to test and maintain 3 of 503 of the relays on its system within the intervals defined in its Program, accounting for approximately 0.6% of its relay devices. | PRC-005-1 | R2 | High | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because only a small number of MID's total protection devices (3 out of 503) were not tested within the proper intervals. Additionally, two of the relays had been previously tested in 2006 and the third in 2004. Moreover, the configuration of the 115 kV lines further reduced the risk. The transmission protection systems involved are on 115 kV transmission lines. The electric utility side of MID serves approximately 112,000 customers with a peak summer load of 697 MW (2006). Finally, WECC is not aware of any misoperation attributed to these relays during the period in which they were not tested. | 3/10/2009 (when MID should have tested the Clau115N_87Babc transmission protection device) | 4/6/2011 (when MID completed mitigation activities) | 3600 | Audit | On March 29, 2011, MID submitted to WECC a Mitigation Plan to address the violation of PRC-005-1 R2.1. In accordance with the Mitigation Plan, MID has maintained and tested the protective equipment at issue. The associated 115 kV loop protective devices have been included in MID's BES relay database for scheduled testing. | 2011-03-24 | 2011-04-20 | Agrees/ Stipulates | WECC determined that there were no aggravating factors affecting the penalty.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | PacifiCorp (PAC) | NCR05304 | WECC201103051 | Settlement Agreement | On October 25, 2011, PAC self-reported a violation of VAR-002-1.1b R3. PAC reported that on July 6, 2011, PAC was in the five day process of commissioning a new Power System Stabilizer (PSS) on its Jim Bridger "Unit 3." During commissioning, the PSS status was changed to "off" on two occasions to facilitate testing. Unit 3 experienced 7 startups and shutdowns before the new PSS was fully tuned, commissioned and released for service. During the 5 startups, Unit 3 never reached the load point threshold (90 MW) that would have required PAC to place the PSS in service. However, during two startups, Unit 3 exceeded the 90 MW threshold but PAC failed to notify its Grid Operations of this status change (i.e. that the device was not in service). WECC determined that during the commissioning, in these two occasions, PAC failed to notify its associated Transmission Operator (TOP) within thirty minutes of a PSS status change. Therefore, WECC determined that PAC, as a Generator Operator, was in violation of VAR-002-1.1b R3 for its failure to notify its TOP within thirty minutes of the PSS status change. | VAR-002-1.1b | R3 | Medium | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because although PAC failed to notify its TOP of the PSS status change, potential impacts from the violation are limited. The PSS system on Unit 3 was temporarily turned off. During PSS commissioning, PAC continued to run its automatic voltage regulator (AVR) systems. Further, PSS systems on the remaining units at Jim Bridger did not experience a status change triggering VAR-002-1.1b R3 reporting. Given the brief duration of the violation and compensating measures in place during the violation period, WECC determined that this violation posed a minimal risk to the reliability of the BPS. | 07/06/2011 (date PAC failed to notify its TOP of PSS status change) | 12/09/2011 (date Mitigation Plan was completed) | 2500 | Self-Report | On October 25, 2011 PAC submitted a Mitigation Plan addressing the violation of VAR-002-1.1b R3. In its Mitigation Plan PAC outlined the following actions: 1) PAC provided refresher training to plant operators; 2) PAC revised its "Energy Generation Engineering reporting procedures, Automatic Voltage Regulator and Power System Stabilizer Status Reporting" to clarify the reporting requirements during maintenance, testing, tuning and commissioning of AVR and PSS systems; and 3) PAC distributed the revised operating procedures to Managing Directors for each of PAC's generation facilities and obtained written confirmation from Managing Directors that all Control Operators and Operations Supervisors have reviewed and acknowledged the procedure. | 2011-12-09 | 2012-01-18 | Does Not Contest | WECC considered PAC’s Internal Compliance Program as a mitigating factor in determining violation disposition and penalty. Specifically, WECC found that PAC's ICP is documented and disseminated throughout its operations staff; PAC has ICP oversight staff and the ICP oversight staff is supervised at a high level in the organization.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Chelan County (CHPD) | NCR05338 | WECC201103040 | Notice of Confirmed Violation | On October 7, 2011, CHPD, as a Generator Operator and Generator Owner, self-reported a violation of VAR-002-1.1b R3. CHPD stated that on September 30, 2011 at 14:00, a technician and plant operator were testing the reactive power instability on the 25 MW, B10 Unit at CHPD’s Rock Island Powerhouse No. 1 facility. While administering the test, the Power System Stabilizer (PSS) was switched off for ten minutes. After completion of the test, the plant operator switched the PSS back online at 14:10. On October 3, 2011, during a weekly review of operator logs, CHPD discovered that the plant operator at the Rock Island Powerhouse plant failed to make the required notifications to the Transmission Operator (TOP) regarding the PSS change in status. WECC determined that the PSS was out of service for ten minutes and that the operator notified the TOP upon discovery of change of service the following Monday. By the time CHPD was aware of the change in status, the 30-minute window to notify the TOP had elapsed; thus, CHPD did not notify the TOP within 30 minutes of the change in PSS status, as required by VAR-002-1.1b R3. | VAR-002-1.1b | R3 | Medium | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the PSS on all other CHPD units remained in service when the Rock Island B10 Units PSS was offline for ten minutes. Therefore, WECC determined that if the B10 Unit started to swing, the PSS on the remaining units, which represent 98.75 percent of the CHPD system, would protect the CHPD system and the BPS. Further, CHPD’s B10 Unit at the Rock Island Powerhouse facility has a total capacity of approximately 25 MW, while CHPD’s total generating capacity is approximately 2,000 MW. Therefore, the violation is limited to a generating unit that represents approximately 1.25 percent of the generation available to CHPD. Further, for these reasons, WECC determined this violation posed minimal risk to the reliability of the BPS. | 9/30/2011 (when the PSS was switched off and the TOP was not notified) | 9/30/2011 (when the PSS was switched back in service) | 8000 | Self-Report | On November 3, 2011, CHPD submitted as complete a Mitigation Plan, stating that the following steps to reinforce the PSS notification requirement were taken: 1) Disciplinary action for the Plant Operator who failed to make the notification; 2) Memo to all plant operations personnel (for all CHPD generation facilities) describing the event and reiterating the importance of proper notification and requesting that staff review the notification procedure which was attached to the memo; 3) Increased the training frequency for the notification procedure from biannual to annual; and 4) Installed alarms for PSS status in the plant control room with an associated alarm at the Transmission Operators' dispatch center (CHPD System Operations) with the System Operations Instruction requiring the System Operator to call the Plant Operator when the alarm is received. | 2011-10-28 | 2012-01-18 | Accepts | WECC applied the following aggravating factor when determining the penalty amount: This violation was CHPD’s second assessed violation of this Standard. CHPD had previously violated the Standard between March 31, 2009 and May 28, 2009 (NP10-56-000) because CHPD had an Automatic Voltage Regulator (AVR) out of service at its Rock Island Generating Plant and failed to notify its TOP that the AVR was out of service within 30 minutes of the change of status. In this case, CHPD discovered that the plant operator at the Rock Island Powerhouse plant failed to make the required notifications to the TOP regarding the PSS change in status within the 30-minute requirement. Therefore, WECC determined that the violation alleged herein is a repeat instance of noncompliance. WECC applied the following mitigating factor when determining the penalty amount: WECC reviewed CHPD’s Internal Compliance Program (ICP) and found among other things that: CHPD’s ICP is documented; the ICP is disseminated throughout its operations staff; CHPD has ICP oversight staff, which is supervised at a high level in the organization and has and independent access to the CEO and/or board of directors. Also, CHPD has allocated sufficient resources to its ICP; the ICP has the support and participation of senior management; CHPD reviews and modifies its ICP regularly; and CHPD’s ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis.
2012-01-31 | FERC | NP12-12-000 | Florida Reliability Coordinating Council (FRCC) | JEA | NCR00040 | FRCC201100422 | Settlement Agreement | On March 8, 2011, JEA submitted a Self-Report to FRCC that as a Transmission Operator, it was in violation of TOP-004-2 R1 because during a one-day event on January 13, 2011, a failed static wire resulted in the outage of two 138 kV transmission lines. These outages led to what appeared to be MVA limit conditions on a 230/138 kV autotransformer. Although the System Operating Limit (SOL) was exceeded because the autotransformer had been rated conservatively, there was no Interconnection Reliability Operating Limit (IROL) exceedance. The system operator initiated a load shed of the entity's local load (approximately 135 MW) for approximately one hour to resolve what appeared to be a transformer overload. There was no instability, uncontrolled separation, or cascading outages that did occur or would have resulted from the loss of the transformer. Tests performed after the event indicated that the autotransformer in question had been rated conservatively and was not overloaded, had not been damaged and was not at risk of failure. Moreover, because the entity had an existing rating methodology under FAC-008 and followed it pursuant to FAC-009, FRCC concluded that there were no other related violations. | TOP-004-2 | R1 | High | High | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the outage of the two 138 kV circuits, led to indicated MVA limit conditions on the Hartley 230/138 kV autotransformer, even if the transformer had tripped, the result would have been limited to loss of local entity internal load. In fact, the manual load shed performed to correct the exceedance affected only local load. There would not be any instability, uncontrolled separation, or cascading outages resulting from the loss of the Hartley 230/138 kV autotransformer because the transformer would have only affected loss of local entity internal load. Also, although there appeared to be an overload on the autotransformer, due primarily to cold weather, the autotransformer was never actually overloaded because it had been rated conservatively. This was confirmed by subsequent review of industry standards, dissolved gas analysis and electrical testing of the autotransformer which showed the transformer was actually under rated. | 1/13/2011 (start date of event) | 1/13/2011 (end date of event) | 0 | Self- Report | The entity mitigated the issue by performing the following activities: (1) The entity enhanced its Facility Rating Methodology to include flexibility to account for cold weather conditions and the specific characteristics of autotransformers and other power system equipment to address real-time conditions. A new Methodology was developed by entity operations to include normal and emergency winter Ratings; (2) The entity also updated its operations procedures to include actions to take in cold weather conditions as they relate to the enhanced Rating Methodology. System operations procedures were updated to include a specific list of actions to take in anticipation of and during cold weather conditions. The procedures include a process for utilizing winter Ratings including but not limited with respect to the autotransformer in question. The procedures also include a process where the system operator can review and modify as appropriate, specific emergency limits based on real-time information; (3) Furthermore, the entity provided training to operators, which included a review of the following: (a) the January 13, 2011 event in detail; (b) its new Rating Methodology with operators, especially cold weather normal and emergency Ratings; (c) the modified operations procedures; (d) appropriate standards, responsibilities and expectations of transmission operators for SOLs and other equipment overloads, with emphasis on cold weather operations; and (e) remedial action plans with emphasis on actions during cold weather operations. | 2011-06-01 | 2011-10-24 | Neither Admits nor Denies | The entity has a documented internal compliance program (ICP) which was in place at the time of the violation, which was considered a mitigating factor in the penalty determination, that was recently reviewed by FRCC to verify the program included violation mitigation, corrective action processes, internal controls, upper management involvement and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust internal compliance program. FRCC also took into account as a mitigating factor the fact that the registered entity also undertook voluntary and appropriate measures pursuant to the NERC Event Analysis program to address the related event. The registered entity performed all of the steps in the program including an internal compliance evaluation and a self-report. In addition, FRCC considered the fact that there was controlled manual load shed (to bring loading below the then established SOL) which was considered in the penalty determination.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Allegheny Energy Supply Company, L.L.C. [GO, GOP] (AE Supply) | NCR02600 | RFC2011001050 | Settlement Agreement | On June 16, 2011, AE Supply submitted a Self-Report to ReliabilityFirst reporting a violation of VAR-002-1.1a. AE Supply initially self-reported six occasions on which it failed to notify its Transmission Operator (TOP) of an unexpected change in the status of a generator reactive power resource, however, after further investigation, AE Supply discovered three additional occasions when it did not notify its TOP of an unexpected change in the status of a generator reactive power resource. The changes in status involved placing the Automatic Voltage Regulator (AVR) into manual mode for each occasion. For six of the nine occasions, AE Supply exceeded the 30-minute notification requirement by a range of six minutes to 104 hours and 52 minutes. The remaining three occasions involved instances in which the change in status lasted fewer than 30 minutes and AE Supply did not inform its TOP of the change. ReliabilityFirst determined that AE Supply, as a Generator Operator (GOP), failed to notify its TOP within 30 minutes of a change in the status of a generator reactive power resource on nine separate occasions. | VAR-002-1.1a | R3 | Medium | High | This violation posed a moderate risk to the reliability of the bulk power system (BPS) because generators provide reactive and voltage control necessary to ensure voltage levels, reactive flows, and reactive resources are maintained within applicable Facility Ratings to protect equipment and the reliable operation of the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because during each of the nine occasions, AE Supply manually controlled voltage, and maintained the generator voltage or reactive power output as directed by the TOP. | 5/27/2010 (Date of the first occasion on which AE Supply exceeded the 30-minute notification requirement contained within the Standard) | 6/6/2011 (Date of the last occasion on which AE Supply exceeded the 30-minute notification requirement contained within the Standard) | 15000 | Self-Report | AE Supply will reinforce the importance of timely reporting of changes in AVR status to all AE Supply power station management. Additionally, AE Supply will develop and conduct AVR status training for AE Supply power station personnel, emphasizing the process and procedures to follow in the event of a status or capability change on any generator reactive power resource. AE Supply also will conduct training on reporting AVR status for real-time operating personnel responsible for notifying the TOP. Finally, AE Supply will revise its power station outage startup procedures to include verification that the AVR is in automatic before startup begins. | 3/31/2012 (Approved Date) | TBD | Agrees/Stipulates | AE Supply is a wholly-owned, indirect subsidiary of FirstEnergy Corp. (FirstEnergy). Prior to February 25, 2011, AE Supply was a wholly-owned subsidiary of Allegheny Energy, Inc. (Allegheny), a public utility company. On February 25, 2011, FirstEnergy acquired Allegheny and its affiliates, including AE Supply. Of the nine occasions constituting the violation of VAR-002-1.1a R3, five occurred prior to FirstEnergy’s February 25, 2011 acquisition of Allegheny and its registered affiliates. Therefore, ReliabilityFirst considered both FirstEnergy’s and Allegheny’s respective compliance programs and cultures of compliance as mitigating factors in determining the penalty amount. Allegheny had a documented internal compliance program, in effect at the time of the violation which established the goals, structure, responsibilities and processes for achieving full compliance with Reliability Standards. Allegheny distributed its compliance program on the internal Allegheny website. Allegheny continually reviewed its compliance program, and conducted training, as required, to introduce new compliance requirements or to reinforce existing requirements. AE Supply conducted an internal review of 50% of all applicable standards on a biennial schedule. FirstEnergy’s FERC Reliability and Compliance Policy addresses all Reliability Standards. FirstEnergy updates the policy and procedures as necessary and distributes the policy to FirstEnergy and affiliate employees. The compliance program includes engagement and support of senior management.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Big Sandy Peaker Plant, LLC (BSPP) | NCR00690 | RFC201100944 | Settlement Agreement | On May 26, 2011, BSPP, as a Generator Owner (GO), self-reported noncompliance with FAC-008-1 R1 prior to a scheduled compliance audit. In May, 2007, BSPP identified its gas turbine generators as the most limiting equipment, but did not conduct a review of the associated electrical systems. On April 22, 2008, BSPP documented its Facility Ratings Methodology; however, ReliabilityFirst determined in a July 2011 Compliance Audit that this 2008 Methodology did not address terminal equipment, as required by the Standard. As a result, ReliabilityFirst determined that from June 18, 2007, when BSPP was required to comply with the Standard, through April 22, 2008, BSPP did not have a documented Methodology that included terminal equipment pursuant to R1 of the Standard. During the July 2011 Compliance Audit, ReliabilityFirst also determined that BSPP's most recent April 19, 2011 Methodology document did properly address terminal equipment. Thus, from April 22, 2008, when BSPP first documented its Methodology, through April 19, 2011, the date the latest Methodology came into effect, BSPP failed to have a Methodology that included terminal equipment, as required by R1.2.1 of the Standard. | FAC-008-1 | R1 | Medium | Severe | This violation posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by two factors. First, although prior to April 22, 2008, BSPP did not have a documented Methodology, BSPP had identified its gas turbine generators as the most limiting piece of equipment in its facility. Since documenting its Methodology on April 22, 2008 and revising it on April 19, 2011, BSPP confirmed that it correctly listed the gas turbine generators as the most limiting piece of equipment. Second, the rating for the gas turbine generators remains unchanged from the one produced by the 2008 Methodology. | 6/18/2007 (when BSPP became subject to compliance with FAC-008-1 R1) | 4/19/2011 (when BSPP revised its Methodology to include terminal equipment) | $20,000 (for RFC201100944, RFC201100945, RFC201100946, and RFC201100947) | Self-Report | On June 27, 2011, BSPP submitted to ReliabilityFirst a Mitigation Plan addressing the alleged violation of FAC-008-1 R1. In accordance with the Mitigation Plan, BSPP (1) documented its formal rating Methodology pursuant to the requirements of the standard and (2) included terminal equipment in its Methodology and all of the factors listed in Requirements R1.1 - R1.3.5. | 2011-04-19 | 2011-11-28 | Neither Admits nor Denies | ReliabilityFirst considered the following mitigating factors when determining the penalty amount. First, certain aspects of BSPP's compliance program were determined by ReliabilityFirst to be mitigating factors. BSPP distributes its compliance program to employees who have direct or indirect responsibility for compliance. BSP employees and corporate team members regularly attend NERC and regional workshops and conferences. BSPP's reliability compliance officer, the Vice President, Operations, reports to the President and CEO, Operations. The President and CEO, Operations, has direct access to both the Chairman and CEO of Tenaska, Inc. Additionally, the Vice President, Operations, attends regular meetings with the President and CEO, Operations, as well as the Board of Stakeholders and is encouraged to discuss reliability and compliance matters with them. BSPP assigned the responsibility for ensuring independent program management to the Vice President, Transmission. The Vice President, Transmission, does not report to the President and CEO, Operations, which enhances the independence in managing the compliance program. BSPP conducts internal audits as well as reviews and authorizes the compliance program semi-annually. ReliabilityFirst determined that there were no aggravating factors in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Big Sandy Peaker Plant, LLC (BSPP) | NCR00690 | RFC201100945 | Settlement Agreement | On May 26, 2011, BSPP, as a Generator Owner (GO), self-reported noncompliance with FAC-009-1 R1 prior to a scheduled compliance audit. Prior to April 22, 2008, BSPP did not have a documented Methodology and therefore could not have Facility Ratings that were consistent with its Methodology, as required by FAC-009-1, R1. Additionally, during the compliance audit, ReliabilityFirst determined that BSPP's Methodology, dated April 22, 2008, was not sufficient to demonstrate compliance with FAC-009-1, RI. Specifically, ReliabilityFirst was unable to determine the limiting element of the facility according to the scope of equipment listed under FAC-008, R 1.2.1 due to different units of measure (MVA/Amps). ReliabilityFirst also could not locate ratings for relay Protection System devices and series and shunt compensation devices based on the April 22. 2008 Methodology. From June 18, 2007, when BSPP was required to comply with the Standard, through April 22, 2008, BSPP did not have an adequately documented Methodology and therefore could not have Facility Ratings that are consistent with its Methodology, as required by the Standard. From April 22, 2008, when BSPP first documented its methodology, through April 19, 2011, BSPP failed to establish Facility Ratings that were consistent with its Methodology, as required by the Standard. | FAC-009-1 | R1 | Medium | Severe | This violation posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by two factors. First, although prior to April 22, 2008, BSPP did not have a documented Methodology, BSPP had identified its gas turbine generators as the most limiting piece of equipment in its facility. Since documenting its Methodology on April 22, 2008 and revising it on April 19, 2011, BSPP confirmed that it correctly listed the gas turbine generators as the most limiting piece of equipment. Second, the rating for the gas turbine generators remains unchanged from the one produced by the 2008 Methodology. | 6/18/2007 (when BSPP became subject to compliance with FAC-009-1 R1) | 4/19/2011 (when BSPP utilized its revised Methodology to develop Facility Ratings pursuant to FAC-009-1 R1) | $20,000 (for RFC201100944, RFC201100945, RFC201100946, and RFC201100947) | Self-Report | On June 27, 2011, BSPP submitted to ReliabilityFirst a Mitigation Plan addressing the alleged violation of FAC-009-1 R1. In accordance with the Mitigation Plan, BSPP utilized its updated Methodology to develop Facility Ratings pursuant to the Standard. | 2011-04-19 | 2011-11-28 | Neither Admits nor Denies | ReliabilityFirst considered the following mitigating factors when determining the penalty amount. First, certain aspects of BSPP's compliance program were determined by ReliabilityFirst to be mitigating factors. BSPP distributes its compliance program to employees who have direct or indirect responsibility for compliance. BSP employees and corporate team members regularly attend NERC and regional workshops and conferences. BSPP's reliability compliance officer, the Vice President, Operations, reports to the President and CEO, Operations. The President and CEO, Operations, has direct access to both the Chairman and CEO of Tenaska, Inc. Additionally, the Vice President, Operations, attends regular meetings with the President and CEO, Operations, as well as the Board of Stakeholders and is encouraged to discuss reliability and compliance matters with them. BSPP assigned the responsibility for ensuring independent program management to the Vice President, Transmission. The Vice President, Transmission, does not report to the President and CEO, Operations, which enhances the independence in managing the compliance program. BSPP conducts internal audits as well as reviews and authorizes the compliance program semi-annually. ReliabilityFirst determined that there were no aggravating factors in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Big Sandy Peaker Plant, LLC (BSPP) | NCR00690 | RFC201100946 | Settlement Agreement | On May 26, 2011, BSPP, as a Generator Owner (GO), self-reported noncompliance with PRC-005-1 R1 prior to a scheduled compliance audit. From June 18, 2007, when BSPP was required to comply with the Standard, through April 22, 2008, BSPP did not have a documented Protection System maintenance and testing program (Program), as required by the Standard. ReliabilityFirst further concluded during a July 2011 compliance audit that BSPP's April 22, 2008 documented Program did not satisfy the requirements of the Standard. Specifically, ReliabilityFirst determined that the April 22, 2008 Program "only provides the compliance framework for BSPP and basically repeats the standard." On May 6, 2011, BSPP revised its Program to include a basis for all Protection System devices. Upon further review, ReliabilityFirst determined the basis for BSPP's voltage and current sensing devices which BSPP based on a draft version of Reliability Standard PRC-005-2 was not an acceptable basis as the draft standard has not been approved. On July 14, 2011, BSPP revised its Program to include an acceptable basis for maintenance and testing of voltage and current sensing devices. Thus, from June 18, 2007 through May 6, 2011, BSPP failed to adequately document its Program, as required by the Standard. From May 6, 2011, through July 18, 2011, BSPP did not have an acceptable basis in its Program for maintenance and testing of voltage and current sensing devices. BSPP's Program includes a total of 163 Protection System devices, consisting of 44 relays, 52 CTs/PTs, 4 Battery Banks and 63 DC Control Circuits. | PRC-005-1 | R1 | High | Severe | This violation posed a moderate risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following: BSPP (1) performed routine maintenance on relays and batteries during the duration of the alleged violation, (2) conducted maintenance and testing on its Protection System relays on a four year interval, (3) conducted maintenance and testing on its batteries on annual and quarterly intervals, and (4) reviewed all plant events and has had no Protection System misoperations. | 6/18/2007 (when BSPP became subject to compliance with PRC-005-1 R1) | 7/18/2011 (when BSPP included an acceptable basis for maintenance and testing of voltage and current sensing devices in its Program) | $20,000 (for RFC201100944, RFC201100945, RFC201100946, and RFC201100947) | Self-Report | On June 27, 2011, BSPP submitted to ReliabilityFirst a Mitigation Plan addressing the alleged violation of PRC-005-1 R1. In accordance with the Mitigation Plan, BSPP included in its documented Program (1) maintenance and testing intervals and the basis for those intervals, (2) a summary of maintenance and testing procedures for its Protection System devices, and (3) a new basis for maintenance and testing of its voltage and current sensing devices. The updated program has clearly defined procedures for the maintenance and testing of DC Control Circuitry, CTs and PTs. | 2011-09-26 | 2012-01-31 | Neither Admits nor Denies | ReliabilityFirst considered the following mitigating factors when determining the penalty amount. First, certain aspects of BSPP's compliance program were determined by ReliabilityFirst to be mitigating factors. BSPP distributes its compliance program to employees who have direct or indirect responsibility for compliance. BSP employees and corporate team members regularly attend NERC and regional workshops and conferences. BSPP's reliability compliance officer, the Vice President, Operations, reports to the President and CEO, Operations. The President and CEO, Operations, has direct access to both the Chairman and CEO of Tenaska, Inc. Additionally, the Vice President, Operations, attends regular meetings with the President and CEO, Operations, as well as the Board of Stakeholders and is encouraged to discuss reliability and compliance matters with them. BSPP assigned the responsibility for ensuring independent program management to the Vice President, Transmission. The Vice President, Transmission, does not report to the President and CEO, Operations, which enhances the independence in managing the compliance program. BSPP conducts internal audits as well as reviews and authorizes the compliance program semi-annually. ReliabilityFirst determined that there were no aggravating factors in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Big Sandy Peaker Plant, LLC (BSPP) | NCR00690 | RFC201100947 | Settlement Agreement | On May 26, 2011, BSPP, as a Generator Owner (GO), self-reported noncompliance with PRC-005-1 R.2.1 prior to a scheduled compliance audit. ReliabilityFirst determined that BSPP could not provide evidence that it maintained its DC Control Circuits within defined intervals, in violation of this Standard. The DC Control Circuits were included in the May 6, 2011 Maintenance and Testing program. | PRC-005-1 | R2.1 | High | Severe | This violation posed a moderate risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by two factors. First, as part of the start-up process, each generating unit has various system health checks, including checks of DC Control Circuits. For example, a health monitoring circuit which monitors the lockout relay trip circuit is in effect on approximately 50% of BSPP's Protection System DC Control Circuits. BSPP used successful equipment starts to monitor the proper functioning of the DC Control Circuits. Second, BSPP reviewed all plant events and has had no Protection System misoperations. | 6/18/2007 (when BSPP became subject to compliance with PRC-005-1 R2) | 9/26/2011 (when BSPP completed its maintenance and testing) | $20,000 (for RFC201100944, RFC201100945, RFC201100946, and RFC201100947) | Self-Report | On June 27, 2011, BSPP submitted to ReliabilityFirst a Mitigation Plan addressing the alleged violation of PRC-005-1 R2. In accordance with the Mitigation Plan, BSPP (1) updated its Program to include defined procedures for maintenance and testing of its DC Control Circuits and (2) conducted maintenance and testing of its DC Control Circuits pursuant to its Program. | 2011-09-26 | 2012-01-31 | Neither Admits nor Denies | ReliabilityFirst considered the following mitigating factors when determining the penalty amount. First, certain aspects of BSPP's compliance program were determined by ReliabilityFirst to be mitigating factors. BSPP distributes its compliance program to employees who have direct or indirect responsibility for compliance. BSP employees and corporate team members regularly attend NERC and regional workshops and conferences. BSPP's reliability compliance officer, the Vice President, Operations, reports to the President and CEO, Operations. The President and CEO, Operations, has direct access to both the Chairman and CEO of Tenaska, Inc. Additionally, the Vice President, Operations, attends regular meetings with the President and CEO, Operations, as well as the Board of Stakeholders and is encouraged to discuss reliability and compliance matters with them. BSPP assigned the responsibility for ensuring independent program management to the Vice President, Transmission. The Vice President, Transmission, does not report to the President and CEO, Operations, which enhances the independence in managing the compliance program. BSPP conducts internal audits as well as reviews and authorizes the compliance program semi-annually. ReliabilityFirst determined that there were no aggravating factors in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Buckeye Power, Inc. (Buckeye Power) | NCR00700 | RFC201000653 | Settlement Agreement | During a Compliance Audit, conducted from September 13, 2010 through September 28, 2010, ReliabilityFirst discovered a violation of FAC-008-1 R1.2.1. Buckeye Power, as a Generator Owner, failed to include the ratings methodology for its transmission conductors, relay protective devices and terminal equipment in earlier versions of its Facility Ratings Methodology. Specifically, ReliabilityFirst reviewed Revisions 0 through 3 of the Facility Ratings Methodology utilized by Buckeye Power. Revision 0 is dated September 13, 2007; Revision 1 is dated June 15, 2009; Revision 2 is dated August 6, 2009; and Revision 3 is dated December 18, 2009. ReliabilityFirst determined that Revisions 0, 1 and 2 of Buckeye Power’s Facility Ratings Methodology did not include transmission conductors, relay protective devices and terminal equipment. The current version of Buckeye Power’s Facility Ratings Methodology, Revision 3, effective on December 18, 2009, included transmission conductors, relay protective devices and terminal equipment. ReliabilityFirst determined that Buckeye Power violated the Standard by failing to include transmission conductors, relay protective devices and terminal equipment in the scope of equipment addressed within the Facility Ratings Methodology in prior versions of the document. | FAC-008-1 | R1; R1.2.1 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a minimal, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated because Buckeye Power’s Facility Ratings were based upon its most limiting element being, by design, its generators. In Revision 0, Buckeye Power included generators in the scope of equipment addressed in its Facility Ratings Methodology. As a result, generators are, and have always been, the most limiting element of Buckeye Power’s facility. Buckeye Power's subsequent revisions to its Facility Ratings Methodology did not change the Facility Ratings. Buckeye Power designed its generating facilities such that the transmission elements within its system never limit a generating unit’s output. Thus, Buckeye Power's identification of the most limiting element was always correct, and thereby mitigated the risk to the BPS posed by its insufficiently detailed Facility Ratings Methodology. | 6/18/2007 (When the Standard became mandatory and enforceable) | 12/18/2009 (When Buckeye Power updated its Facility Ratings Methodology to include transmission conductors, relay protective devices and terminal equipment) | 0 | Compliance Audit | During the Compliance Audit, ReliabilityFirst determined Buckeye Power mitigated the violation of the Standard when it implemented the current version of the Facility Ratings Methodology on December 18, 2009. | 2009-12-18 | 2011-07-25 | Agrees/ Stipulates | ReliabilityFirst considered Buckeye Power’s formal internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor. The ICP resides within the Power Supply division and was widely disseminated to all individuals within this division through small workshops, training by consultants, emails, meetings and in person. The program was supervised by three senior staff members who report to the Chief Operating Officer, who reports to the Chief Executive Officer and President. Buckeye Power’s self-assessment of its ICP resulted in expanding the scope of compliance activities to include more staff, including an additional consultant.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Wadsworth Electric & Communications (WEC) | NCR06020 | RFC201100829 | Settlement Agreement | On April 20, 2011, WEC, as a Distribution Provider, self-reported a violation of PRC-005-1 R2 to ReliabilityFirst prior to a scheduled compliance audit. WEC reported that it failed to maintain transmission relays as specified in its Program. Specifically, WEC failed to test all ten of its transmission relays within a five year interval. During the compliance audit, ReliabilityFirst found that all other protection system devices were tested and maintained within the intervals stated in WEC's Program. ReliabilityFirst determined that WEC violated the Standard by failing to include evidence of the last maintenance and testing, and documentation of the last date of testing and maintenance for relays. | PRC-005-1 | R2 | High | Severe | This violation posed a moderate risk to the bulk power system (BPS) because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. WEC has alarming in place via a Supervisory Control and Data Acquisition (SCADA) system, which would immediately notify its Electric Division Headquarters and operations supervisors of any device failures. In addition, WEC completed the outstanding maintenance and testing in April 2011 and found no problems with the devices. WEC also indicated that it had tested the relays in November 2005. | 06/18/2007 (date Standard became mandatory and enforceable) | 04/05/2011 (date WEC completed testing and maintenance for the relays as defined by its Program) | 5000 | Self-Report | WEC entered into an agreement with FirstEnergy Corporation (FirstEnergy), whereby FirstEnergy agreed to perform maintenance and testing on the relays for WEC's two 138 kV transmission lines. FirstEnergy completed this testing on behalf of WEC on April 5, 2011. WEC has also established a schedule with FirstEnergy to ensure timely future testing and maintenance of protection system devices. | 2011-04-05 | 2011-08-25 | Agrees/Stipulates | ReliabilityFirst considered certain aspects of WEC's Internal Compliance Program (ICP), which was in effect at the time of the violation, as mitigating factors when assessing the penalty. WEC's employees attend reliability-focused seminars, workshops, and conference calls, and WEC has identified individuals in its organization to be responsible for compliance with NERC standards. Reliability issues are communicated to staff at weekly staff meetings, and WEC conducted an internal audit in 2010. Since the Self-Report was submitted in anticipation of an audit, WEC did not receive the credit normally given for Self-Reports.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Wisconsin Electric Power Company (Wisconsin Electric) | NCR00951 | RFC201000388 | Settlement Agreement | From May 17, 2010 through May 21, 2010, ReliabilityFirst conducted a Compliance Audit of Wisconsin Electric during which it discovered a violation of PRC-005-1 R1. ReliabilityFirst determined that Wisconsin Electric, as a Distribution Provider (DP) and Generator Owner (GO), violated PRC-005-1 R1 by failing to include maintenance and testing intervals and a basis for those intervals for certain Protection System devices and by failing to include summaries of maintenance and testing procedures for certain Protection System devices, which are identified below. Wisconsin Electric's transmission Protection System maintenance and testing program for its DP function (DP Program) has been in place since January 2008 and Wisconsin Electric supplemented it on February 1, 2010. The 2008 version of the DP Program only included (i) maintenance and testing intervals and their basis for protective relays, and (ii) summaries of maintenance and testing procedures for protective relays. It did not include any maintenance and testing intervals and their basis or summaries of maintenance and testing procedures for the remaining Protection System devices. Specifically, this violation involved the omission of all of Wisconsin Electric's 243 transmission current sensing devices, 51 transmission station batteries and 111 transmission direct current control circuits, which constitutes 51.9% of its 779 total transmission Protection System devices. Wisconsin Electric's DP Program did not include voltage sensing devices or communication systems, since Wisconsin Electric has no DP voltage sensing devices and no DP communications systems. The 2010 version of Wisconsin Electric's DP Program required maintenance and testing on current transformers at installation only, thus the documentation did not include an acceptable maintenance and testing interval or an acceptable basis for that interval for current sensing devices. In addition, the 2010 version of Wisconsin Electric's DP Program did not include summaries of maintenance and testing procedures for current sensing devices. This violation involved the omission of all of Wisconsin Electric's transmission current sensing devices, which constitutes 31% of its 779 total transmission Protection System devices. Wisconsin Electric's generation Protection System maintenance and testing program for its GO function has been in place since 2006 (GO Program). Wisconsin Electric's GO Program documentation did not include any maintenance and testing interval or any basis for that interval for voltage and current sensing devices. In addition, the GO Program did not include summaries of maintenance and testing procedures for voltage and current sensing devices. This violation involved all of Wisconsin Electric's 72 generation voltage sensing devices and 408 generation current sensing devices, which constitute 28.6% of its total 1,678 generation Protection System devices. | PRC-005-1 | R1 | High | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. Although Wisconsin Electric's 2008 DP Program only included maintenance and testing intervals and their basis for protective relays, the audit team, as affirmed by ReliabilityFirst enforcement staff, confirmed that Wisconsin Electric performed maintenance and testing on its other Protection System devices in accordance with its 2010 DP Program throughout the time period of the violation. Although the 2010 program was not in effect for the entire duration of the violation, Wisconsin Electric had been performing maintenance and testing on all devices except sensing devices. The 2010 program memorialized Wisconsin Electric’s maintenance and testing activities. Furthermore, although Wisconsin Electric did not include maintenance and testing intervals for voltage, since it had no DP sensing devices and only included it in its program for thoroughness, and current sensing devices in its DP or GO Programs, Wisconsin Electric's program documentation, which are maintenance and testing programs in place since June 18, 2007, indicates that it historically has tested its voltage and current sensing devices during the installation of its equipment and when it identifies problems with the equipment as part of its operations and upon visual inspections, consistent with the recommendations of the equipment manufacturers. Additionally, Wisconsin Electric routinely performs substation inspections, which included visual checks and infrared scans of the voltage and current sensing devices. Wisconsin Electric also verifies the voltage and current sensing devices' inputs into Protection System relays as part of those relays' periodic preventative maintenance and testing. Wisconsin Electric undertook these actions throughout the duration of the violation. In addition, Wisconsin Electric continuously monitors its voltage sensing devices for proper operation. An alarm alerts an operator who is on duty 24 hours a day to correct any potential issues before any loss of protection or interruption of service occurs. As a result of these actions, Wisconsin Electric found its voltage and current sensing devices in working condition throughout the duration of the violation. | 6/18/2007 (When the Standard became mandatory and enforceable) | 1/3/2011 (When Wisconsin Electric revised its DP Program to comply with the Standard); 2/18/2011 (Date Wisconsin Electric revised its GO Program to comply with the Standard) | 10000 | Compliance Audit | Wisconsin Electric revised its DP Program and its GO Program to include maintenance and testing intervals for voltage and current sensing devices. The 2010 version of Wisconsin Electric's DP Program had been revised to include maintenance and testing intervals, their basis and summaries for transmission station batteries. | 2011-02-18 | 2012-01-25 | Neither Admits nor Denies | ReliabilityFirst considered as a mitigating factor certain aspects of Wisconsin Electric's internal compliance culture. Wisconsin Electric has an internal compliance program, which was in effect at the time of the violation which consists of the Federal Regulatory Affairs and Policy (FRAP) group. The FRAP group developed and implemented the Federal Energy Regulatory Compliance Program to assure and demonstrate compliance with the FERC electric regulations including the NERC Reliability Standards. The FRAP group also assists in the development and documentation of the necessary compliance processes and helps educate Wisconsin Electric individuals responsible for executing the compliance process. In addition, Wisconsin Electric requires all employees to annually certify their review and understanding of corporate policies, including the Code of Business Conduct. The Corporate Compliance Officer, who is the Corporate Secretary and Associate General Counsel, has independent access to the Audit and Oversight Committee of the Board of Directors, as well as to the CEO and Chairman of the Board of Wisconsin Energy Corporation. In addition, senior management approves policies, procedures, self-certifications, and data submittals, and receives quarterly reports on the level of FERC and NERC compliance in their respective areas.
2012-01-31 | FERC | NP12-12-000 | Texas Reliability Entity (Texas RE) | EDF Trading North America, LLC (EDF Trading) | NCR00551 | TRE201100366 | Settlement Agreement | On June 10, 2011, EDF Trading self-reported to Texas RE a possible violation of COM-002-2 R1. Texas RE determined that EDF Trading, as a Generator Operator (GOP), did not have communications available for addressing a real-time emergency condition, as required by the Standard. Specifically, during an Energy Emergency Alert (EEA) event on February 2, 2011, ERCOT ISO (the Balancing Authority and the Reliability Coordinator) issued a Verbal Dispatch Instruction (VDI) at 05:49 CPT via a hot line call to deploy 384 MW of ERCOT system Emergency Interruptible Load Service (EILS) system loads as part of a manual load shed to respond to the EEA. EDF Trading contends it did not receive the 05:49 CPT initial VDI via the hot line. ERCOT’s evidence indicates that EDF Trading’s phone was off the hook. EDF Trading reported that there was power to the phone system and operators were available to answer the phone. Texas RE determined that although EDF Trading had established communication links for addressing a real-time emergency condition, and although such communications were staffed, they were not available for addressing a real-time emergency situation on February 2, 2011. | COM-002-2 | R1 | High | Moderate | This violation posed a moderate risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS due to: (1) the small amount of interruptible load (7.4 MW, which is approximately 2% of ERCOT-wide EILS), and (2) the brief time period that EDF Trading was not available for answering the ERCOT communication link (approximately one hour). Additionally, once EDF Trading understood that EILS had been called by ERCOT, it successfully deployed its EILS pursuant to the ERCOT Protocols. The failure to follow the reliability directive in this case does not appear to be indicative of systemic issues adverse to system reliability. | 2/2/2011 (Date of communications failure) | 2011-02-02 | $21,000 (for TRE201100366 and TRE201100392) | Self-Report | On June 6, 2011, EDF Trading submitted to Texas RE a Mitigation Plan to address the violation of COM-002-2 R1. In accordance with the Mitigation Plan, EDF Trading has completed the following: (1) implemented a procedure requiring the EDF Trading real-time desk operator to check the phone status at the beginning of his/her shift, assuming system conditions are normal; (2) implemented a procedure to have APX (EDF Trading’s energy management service provider) alarm the EDF Trading real-time desk upon receipt of a hot line call to APX; (3) implemented an alarm upon the receipt of Market Information System (MIS, an ERCOT computer system) notification of deployments of EILS as well as other VDIs and emergency notices; (4) implemented monitoring and storing channel bank interface status to provide real-time status of “hook” indicators on the hot line phone analog channels; and (5) implemented monitoring and storing the condition of the ERCOT trunk interface to the hot line phone gear. | 2011-12-31 | 2012-01-04 | Neither Admits nor Denies | EDF Trading's internal compliance program, in place at the time of the violation, was considered by Texas RE to be a mitigating factor in the penalty determination. EDF Trading maintains and regularly updates a written compliance program. EDF Trading relies on the written compliance program and desk/department heads to ensure compliance with NERC standards. The written compliance program is both widely distributed and available to all employees. EDF Trading has engaged a third-party consultant to assist in the ongoing development of formal compliance policies. In addition, EDF Trading has hired outside counsel to assist in actively monitoring changing regulatory requirements. EDF Trading reviews NERC standards and requirements approximately every six months. EDF Trading engages in a regular compliance training program. New employees are assigned a mentor for training for approximately one month after hire. EDF Trading has a named and staffed director of regulatory affairs who is charged with overseeing implementation of its compliance program. The director of regulatory affairs reports to the senior vice president and general counsel, who has the overall responsibility for reliability compliance. Both the senior VP and general counsel and the senior vice president of trading and risk have independent access to the CEO.
2012-01-31 | FERC | NP12-12-000 | Texas Reliability Entity (Texas RE) | EDF Trading North America, LLC (EDF Trading) | NCR00551 | TRE201100392 | Settlement Agreement | On July 22, 2011, EDF Trading self-reported to Texas RE a possible violation of TOP-006-1 R1. Texas RE determined that EDF Trading, as a Generator Operator (GOP), failed to inform its Host Balancing Authority and Transmission Operator of all generation resources available for use, as required by the Standard. Specifically, on February 2, 2011, Bayou Cogeneration Combustion Turbine No. 2 tripped at 01:54 CPT and was back on-line at 02:20. During the 26-minute interval between the turbine trip and when it was brought back on-line, EDF Trading failed to indicate that the unit status was “OFF” via the telemetering signal to ERCOT, the Host Balancing Authority and Transmission Operator, thus failing to inform of all generation resources available for use. | TOP-006-1 | R1; R1.1 | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the generation at issue (75 MW nameplate rating) was unavailable for serving load for a 26-minute period regardless of whether the Standard was violated. The effect of failing to change the telemetered status to "OFF" was miscommunication. ERCOT operators believed that the ERCOT system had more operating reserve than they actually had. Although the ERCOT system was under stress (an Advisory was called at 02:47 and an Energy Emergency Alert (EEA) was called at 05:18), and there were limited and dwindling generation resources available, there were adequate operating reserves at the time regardless of the miscommunication and system frequency was stable at 59.97 Hz. Had the issue occurred during the EEA, it would have exacerbated the issues ERCOT was facing in the sense that miscommunication is inherently adverse to reliability. However, the resource would have been unavailable regardless of the quality of any communications. | 2/2/2011 (Date of entity's failure to inform its Host Balancing Authority and Transmission Operator of all generation resources available for use) | 2011-02-02 | $21,000 (for TRE201100366 and TRE201100392) | Self-Report | On June 6, 2011, EDF Trading submitted to Texas RE a Mitigation Plan to address the violation of TOP-006-1 R1. In accordance with the Mitigation Plan, EDF Trading has implemented automated processes with APX (EDF Trading’s energy management service provider) to update resource status upon change in telemetered or received elements or notices. | 2012-01-01 | 2012-01-04 | Neither Admits nor Denies | EDF Trading's internal compliance program, in place at the time of the violation, was considered by Texas RE to be a mitigating factor in the penalty determination. EDF Trading maintains and regularly updates a written compliance program. EDF Trading relies on the written compliance program and desk/department heads to ensure compliance with NERC standards. The written compliance program is both widely distributed and available to all employees. EDF Trading has engaged a third-party consultant to assist in the ongoing development of formal compliance policies. In addition, EDF Trading has hired outside counsel to assist in actively monitoring changing regulatory requirements. EDF Trading reviews NERC standards and requirements approximately every six months. EDF Trading engages in a regular compliance training program. New employees are assigned a mentor for training for approximately one month after hire. EDF Trading has a named and staffed director of regulatory affairs who is charged with overseeing implementation of its compliance program. The director of regulatory affairs reports to the senior vice president and general counsel, who has the overall responsibility for reliability compliance. Both the senior VP and general counsel and the senior vice president of trading and risk have independent access to the CEO.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Frederickson Power LP (FPWR) | NCR05164 | WECC201103015 | Settlement Agreement | On July 1, 2011, WECC notified FPWR that WECC was initiating the Self-Certification process for the reporting period of July 1, 2010 through August 31, 2011. Under this process, FPWR's Self-Certification submittal was due by September 20, 2011. On September 14, 2011, FPWR, as a Generator Operator (GOP), submitted a Self-Report addressing its noncompliance with VAR-002-1 R1 and on September 20, 2011, FPWR submitted its Self-Certification. WECC determined that the FPWR's Combustion Turbine Generator (CTG) was operating with the Automatic Voltage Regulator (AVR) in the wrong mode. Specifically, FPWR had been operating in VAR mode instead of Voltage Control mode from August 2, 2007 until January 12, 2011, when the unit was dispatched off-line. The computer interface has three generator mode options for the CTG: OFF, VAR (constant reactive power output), and PF (constant power factor). The OFF mode on the AVR computer interface is the correct mode for operating in voltage control mode. However, plant personnel believed the OFF position would remove the CTG AVR from service, so FPWR erroneously operated in VAR mode instead of Voltage Control/OFF mode. The change to the correct AVR mode was made during the period the unit was offline from January 12, 2011 to August 24, 2011. The unit was brought back online on August 24, 2011. FPWR notified its Transmission Operator (TOP), Bonneville Power Administration, of the change in AVR status on September 7, 2011. This is in violation of the Standard, which requires the GOP to operate in AVR mode and for the TOP to be notified of a change in AVR status within 30 minutes. | VAR-002-1 | R1 | Medium | Moderate | This violation posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS for several reasons. FPWR's net output of the combined cycle generation plant is based on the output of two distinct turbine-generators - the Combustion Turbine Generator (CTG) and the Steam Turbine Generator (STG). Although FPWR operated the CTG's AVR in VAR mode, the STG was consistently operated in the correct Voltage Control mode, thus reducing the potential risk that may have occurred through operating the CTG in an incorrect mode. Second, the output of the plant was always within the operating parameters defined by its transmission operator, BPA. Third, FPWR's operating personnel followed all directives given by BPA when deviations to the voltage schedule were required. FPWR's generation plant is a 249 MW facility with an annual operation of less than 50 percent. | 8/2/2007 (when the Standard became mandatory and enforceable) | 1/12/2011 (when FPWR's unit was dispatched off-line) | $1,000 (for WECC201103015 and WECC201103018) | Self-Certification | FPWR submitted a mitigation plan on November 1, 2011 with a completion date of September 7, 2011. To mitigate this violation FPWR performed the following: 1. Frederickson Power has applied the General Electric TIL 1731 on May 5, 2010 to update the control screen interface as evidenced by the completed work order. 2. The site manager at the Frederickson plant has contacted the Bonneville Power Administration (BPA) to review the voltage schedule for Frederickson Power/South Tacoma Switchyard. He has confirmed documentation of the proper control ranges and ensured Frederickson Power has maintained the voltage schedule. 3. Frederickson Power has revised the startup procedures to clarify the correct CTG AVR operation on September 7,2011. 4. Frederickson Power has re-trained operating personnel on startup procedures and circulated an email summarizing the procedural changes September 7, 2011. | 2011-09-07 | 2012-01-26 | Does Not Contest | WECC determined there were no aggravating factors that would warrant a penalty higher than the recommended penalty. Specifically, FPWR did not have repeat violations of this Standard nor relevant negative compliance history. FPWR did not fail to complete an applicable compliance directives. Additionally, there was no evidence of any attempt by FPWR to conceal the violation, or any evidence that FPWR’s violation was intentional.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Frederickson Power LP (FPWR) | NCR05164 | WECC201103018 | Settlement Agreement | On July 1, 2011, WECC notified FPWR that WECC was initiating the Self-Certification process for the reporting period of July 1, 2010 through August 31, 2011. Under this process, FPWR's Self-Certification submittal was due by September 20, 2011. On September 14, 2011, FPWR, as a Generator Operator (GOP), submitted a Self-Report addressing its noncompliance with VAR-002-1.1b R3 and on September 20, 2011, FPWR submitted its Self-Certification. WECC determined that the FPWR's Combustion Turbine Generator (CTG) was operating with the Automatic Voltage Regulator (AVR) in the wrong mode. Specifically, FPWR had been operating in VAR mode instead of Voltage Control mode from August 2, 2007 until January 12, 2011, when the unit was dispatched off-line. The change to the correct AVR mode was made during the period the unit was offline from January 12, 2011 to August 24, 2011. The unit was brought back online on August 24, 2011. FPWR notified its Transmission Operator (TOP), Bonneville Power Administration, of the change in AVR status on September 7, 2011. This is in violation of the Standard, which requires that the TOP be notified of a change in AVR status within 30 minutes. | VAR-002-1.1b | R3 | Medium | High | This violation posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS for several reasons. FPWR's net output of the combined cycle generation plant is based on the output of two distinct turbine-generators - the Combustion Turbine Generator (CTG) and the Steam Turbine Generator (STG). Although FPWR operated the CTG's AVR in VAR mode, the STG was consistently operated in the correct Voltage Control mode, thus reducing the potential risk that may have occurred through operating the CTG in an incorrect mode. Second, the output of the plant was always within the operating parameters defined by its transmission operator, BPA. Third, FPWR's operating personnel followed all directives given by BPA when deviations to the voltage schedule were required. FPWR's generation plant is a 249 MW facility with an annual operation of less than 50 percent. | 8/24/2011 (when FPWR's unit was brought back online in a different AVR mode) | 9/7/2011 (when FPWR notified BPA of the change in AVR status) | $1,000 (for WECC201103015 and WECC201103018) | Self-Certification | FPWR submitted a mitigation plan on November 1, 2011 with a completion date of September 7, 2011. To mitigate this violation FPWR performed the following: 1. Frederickson Power has applied the General Electric TIL 1731 on May 5, 2010 to update the control screen interface as evidenced by the completed work order. 2. The site manager at the Frederickson plant has contacted the Bonneville Power Administration (BPA) to review the voltage schedule for Frederickson Power/South Tacoma Switchyard. He has confirmed documentation of the proper control ranges and ensured Frederickson Power has maintained the voltage schedule. 3. Frederickson Power has revised the startup procedures to clarify the correct CTG AVR operation on September 7,2011. 4. Frederickson Power has re-trained operating personnel on startup procedures and circulated an email summarizing the procedural changes September 7, 2011. | 2011-09-07 | 2012-01-26 | Does Not Contest | WECC determined there were no aggravating factors that would warrant a penalty higher than the recommended penalty. Specifically, FPWR did not have repeat violations of this Standard nor relevant negative compliance history. FPWR did not fail to complete an applicable compliance directives. Additionally, there was no evidence of any attempt by FPWR to conceal the violation, or any evidence that FPWR’s violation was intentional.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Lower Valley Energy (LVE) | NCR05225 | WECC201102432 | Settlement Agreement | On February 14, 2011, LVE, as a Transmission Owner and Distribution Provider, self-certified noncompliance with PRC-005-1 R2 for failure to annually compare its current outputs to its System Control and Data Acquisition (SCADA) values, as required by its transmission Protection System maintenance and testing program. LVE should have compared its current outputs to its SCADA values by the end of August 2010. WECC determined that LVE maintained and performed most of the testing on its relevant protection equipment but failed to perform one test for comparing its current outputs to its SCADA values. LVE was in violation of this Standard for failing to maintain 100% of its current transformers (CTs) and potential transformers (PTs) within the defined intervals. | PRC-005-1 | R2; R2.1 | High | Severe | This violation posed a minimal risk to reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because LVE maintained and performed most of the testing on the relevant protection equipment and only failed to perform one test for comparing its current outputs to its SCADA values. Also, LVE's CTs and PTs are continuously monitored by its SCADA system. In addition, WECC considered the size of the entity, which is a 115 kV transmission system. | 8/31/2010 (When LVE should have maintained and tested its CTs and PTs) | 1/25/2011 (When LVE conducted maintenance and testing on the missed devices ) | 7500 | Self-Certification | On March 23, 2011, LVE submitted a Mitigation Plan, stating that it had addressed its noncompliance with this Standard by performing the missing CT and PT device testing. In addition, LVE updated its tracking spreadsheet to include the testing procedures that were missed. | 2011-04-26 | 2011-12-21 | Agrees/ Stipulates | WECC did not review an internal compliance program (ICP) for LVE and therefore, this factor had no impact on the penalty determination. WECC considered that LVE met its first Mitigation Plan milestone in January 2011 to perform maintenance and testing (essentially mitigating the instant violation), however LVE met its preventative measure milestone (to update its tracking spreadsheet) 34 days after the approved date. WECC determined that no adjustments to the penalty were warranted.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | NAES Corporation - Tracy (NAES-TR) | NCR05274 | WECC201102436 | Settlement Agreement | On January 20, 2011, NAES-TR, as a Generator Operator (GOP), submitted an Automatic Voltage Regulators (AVR) report for the fourth quarter of 2010 (Q4 2010), addressing a violation of VAR-STD-002a-1 WR1. Based on the record, WECC determined that NAES-TR did not operate its automatic control equipment in voltage control mode (VCM) for more than 92% of the hours during which its unit was on line for Q4 2010 and operated in power control mode instead. NAES-TR's operators were operating the AVR in a power control mode because they understood that its Transmission Operator, Pacific Gas and Electric Company, had instructed it to operate in this mode. However, WECC's regional Standard VAR-STD-002a-1 only allows the Transmission Operator to have the generator operate in a mode other than VCM under special conditions listed in the Standard, which were not applicable to this situation. As a result, WECC determined that NAES-TR violated VAR-STD-002a-1 WR1 for failure to operate its AVR in a VCM. | VAR-STD-002a-1 | WR1 | Lower | Level 4 Noncompliance | WECC determined that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NAES-TR did not operate in the proper mode, the generator involved (the Thermal Energy Development Partnership) is a synchronous biomass facility with a rated capacity of 23 MW, which is connected to a 115 kV transmission system. WECC took into consideration the entity's limited size and location and concluded that the entity has a very limited capacity to have more than a minimal impact on the reliability of the BPS. | 10/1/2010 (When NAES-TR failed to operate its AVR in VCM, without an applicable exemption listed in the Standard) | 4/21/2011 (When NAES-TR switched its AVR to the appropriate mode) | 500 | Self-Report | NAES-TR submitted its Mitigation Plan to WECC on 6/13/2011, with a completion date of 5/12/2011. NAES-TR switched its AVR into the appropriate mode on 4/21/2011. | 2011-04-21 | 2011-12-29 | Agrees/Stipulates | WECC considered that there were no aggravating factors.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Sierra Pacific Power Company (SPPC), d/b/a NV Energy | NCR05390 | WECC201102424 | Settlement Agreement | On February 2, 2011, SPPC self-certified that although it met its quarterly battery testing intervals, it missed certain annual battery testing intervals set forth in SPPC's Protection System maintenance and testing program. The annual testing was established to address SPPC's obligations set forth in PRC-005-1 R2.1. On February 22, 2011, SPPC supplemented its Self-Certification with a Self-Report addressing additional batteries that were not tested in accordance with the annual interval set forth in SPPC's Protection System maintenance and testing program. During an on-site compliance audit of SPPC in March 2011, WECC subject matter experts (SMEs) reviewed the Self-Certification and Self-Report. The SMEs determined, pursuant to SPPC's Self-Certification and Self-Report, that SPPC failed to maintain 12 transmission station batteries and an additional 4 generation station batteries within the intervals defined in SPPC's Protection System maintenance and testing program. These 16 batteries represent fewer than 25 percent of all of SPPC's Protection System batteries. SPPC is subject to this Standard because it is registered with NERC as a Transmission Owner, Distribution Provider and Generator Owner. | PRC-005-1 | R2; R2.1 | High | Lower | SPPC conducts quarterly station battery inspections. This violation relates to SPPC's failure to conduct its annual (not to exceed 16 month) scheduled battery tests. Although SPPC missed annual testing, it did not miss its quarterly battery inspections. SPPC personnel are aware of the condition of the batteries based on the quarterly inspections and would note and take action if SPPC detected a potential battery failure. Further, the batteries support only a small fraction of SPPC's transmission Protection System and an even smaller fraction of SPPC's generation Protection System. In addition, SPPC system protection engineers regularly review the battery maintenance records for consistency. For these reasons, WECC determined this violation did not pose a serious or substantial risk and posed minimal risk to the reliability of the bulk power system. | 12/10/2009 (Date of first missed interval for battery maintenance and testing) | 2/17/2011 (When SPPC tested its batteries pursuant to the Protection System maintenance and testing program) | $16,400 (for WECC201102424, WECC201102425, WECC201102426, WECC201102438) | Self-Certification | On May 5, 2011, SPPC submitted a Mitigation Plan to address this violation. In the Mitigation Plan, SPPC identified the cause of the violation as "SPPC identified 12 substation batteries as being out of compliance on their maintenance intervals, additionally SPPC self-reported 4 plant batteries as being out of compliance on their maintenance intervals when discovered." SPPC clarified that it missed the 16 batteries "due to a combination of human error, incorrect data from an old database, and lack of awareness." As a result of this observation, SPPC trained its employees "on NERC Compliance [including] the nature of compliance as well as the maintenance intervals." To avoid confusion, going forward, SPPC will ensure the date listed on the test results documentation is the date the actual test was performed (rather than the date the results were downloaded off the test instrument). SPPC also migrated its old database to a new database and configured the database to target Protection Systems, in this case batteries, subject to PRC-005. With the data migration, SPPC removed the necessity for manual, human oversight regarding the intervals. | 2011-04-04 | 2012-01-10 | Neither Admits nor Denies | Although there is a violation of this Reliability Standard on the part of an SPPC affiliate, Enforcement determined the SPPC affiliate violation occurred concurrent to a previous SPPC violation. Enforcement considered as an aggravating factor that this violation is SPPC's second assessed violation of PRC-005-1 R2. WECC evaluated SPPC's internal compliance program (ICP) and found the following: SPPC has a fully documented ICP that has been reviewed and approved by general counsel who also serves as its chief compliance officer. SPPC's oversight position is identified and staffed, and is supervised at a high level within the company. The ICP oversight position has direct access to the CEO and board of directors and SPPC operates and manages the ICP independently from personnel responsible for compliance with the Reliability Standards. The ICP has sufficient staff and an adequate budget, SPPC senior management support and participate in the ICP, and SPPC's ICP has an annual review cycle. Based on these findings, WECC concluded that SPPC has an effective compliance culture.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Sierra Pacific Power Company (SPPC), d/b/a NV Energy | NCR05390 | WECC201102425 | Settlement Agreement | From March 14, 2011 through March 25, 2011, WECC conducted an on-site compliance audit of SPPC (Audit). The Audit team clarified with SPPC that station batteries at Downs, Muller, Northstar, Anaconda Yerington and Tahoe City stations, which support SPPC's Under Frequency Load Shedding (UFLS) Protection System, were not in the UFLS program. Therefore, the Audit team determined SPPC's UFLS program did not include all UFLS station batteries, and was a possible violation of PRC-008-0 R1. The Audit team noted that WECC had previously audited SPPC and did not identify a possible violation of PRC-008-0 R1. The Audit team forwarded its findings to Enforcement. Enforcement reviewed the Audit findings and determined SPPC's failure to identify UFLS station batteries in its UFLS maintenance and testing program, including a schedule for testing, is a violation of PRC-008-0 R1. SPPC is subject to this Standard as a Transmission Owner and Distribution Provider. | PRC-008-0 | R1 | Medium | Moderate | Failure to ensure periodic maintenance of UFLS station batteries could lead to a failure of a specific UFLS relay. However, although SPPC did not identify station batteries in its UFLS program it did maintain and test UFLS station batteries as part of its routine station battery maintenance and testing. Further, only 5 of the 16 battery stations supporting UFLS were not addressed in SPPC's PRC-005 Protection System maintenance and testing program. SPPC adequately identified and addressed all other components of its UFLS Protection System in its UFLS program. For these reasons, WECC determined this violation posed minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). | 6/18/2007 (When the Standard was enforceable) | 5/31/2011 (Mitigation Plan completion) | $16,400 (for WECC201102424, WECC201102425, WECC201102426, WECC201102438) | Compliance Audit | On May 31, 2011, SPPC submitted a Mitigation Plan to address this violation. SPPC added UFLS station batteries previously not included to its UFLS program. SPPC updated it documented procedure on PRC-008 to include the newly identified batteries. | 2011-05-31 | 2011-06-27 | Neither Admits nor Denies | Enforcement considered that WECC's 2009 audit of SPPC did not identify a possible violation of PRC-008-1 R1 and WECC had previously indicated to SPPC that it was deemed compliant with this requirement. SPPC did not substantially alter its program with regard to UFLS station batteries since the 2009 audit and PRC-008-1 R1 had not been modified since WECC last deemed SPPC to be compliant with the standard. SPPC relied in good faith, in part, on the 2009 audit finding as SPPC implemented its UFLS program. WECC evaluated SPPC's internal compliance program (ICP) and found the following: SPPC has a fully documented ICP that has been reviewed and approved by general counsel who also serves as its chief compliance officer. SPPC's oversight position is identified and staffed, and is supervised at a high level within the company. The ICP oversight position has direct access to the CEO and board of directors and SPPC operates and manages the ICP independently from personnel responsible for compliance with the Reliability Standards. The ICP has sufficient staff and an adequate budget, SPPC senior management support and participate in the ICP, and SPPC's ICP has an annual review cycle. Based on these findings, WECC concluded that SPPC has an effective compliance culture.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Sierra Pacific Power Company (SPPC), d/b/a NV Energy | NCR05390 | WECC201102426 | Settlement Agreement | On February 2, 2011, SPPC self-certified possible noncompliance with PRC-008-0 R2. WECC subject matter experts (SMEs) reviewed the Self-Certification and associated evidence during an on-site compliance audit of SPPC in March 2011. The SMEs reviewed maintenance records for all SPPC Under Frequency Load Shedding (UFLS) equipment and determined SPPC appropriately self-certified noncompliance with this requirement. The SMEs also determined SPPC failed to maintain or test one UFLS relay (out of 22 total) within the interval defined in SPPC's UFLS maintenance and testing plan. The SMEs determined this was a possible violation of PRC-008-0 R2. The SMEs forwarded the Self-Certification and the SMEs' findings to Enforcement. Enforcement reviewed the Self-Certification and the SME's findings. Enforcement determined SPPC did not maintain and test a UFLS relay at the Fort Churchill substation within the interval defined within SPPC's UFLS maintenance and testing plan. Accordingly, Enforcement determined SPPC's failure to implement its UFLS program is a violation of PRC-008-0 R2. SPPC is subject to this Standard as a Transmission Owner and Distribution Provider. | PRC-008-0 | R2 | Medium | Lower | SPPC failed to test one UFLS relay out of 22 total UFLS relays. Thus, this violation is limited to a small fraction of the SPPC UFLS protective devices. Further, SPPC has a six-year interval for these devices and tested the relay six months beyond the defined interval. Such a testing delay in relation to the number of total devices does not represent a significant deviation from SPPC's UFLS program, and it is unlikely the relay would deteriorate or have its settings inadvertently misconfigured within the six-month delay in maintenance and testing. For these reasons, WECC determined this violation posed minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). | 5/6/2010 (Date of first missed interval for UFLS maintenance and testing) | 12/23/2010 (When SPPC tested its UFLS relay pursuant to the UFLS program) | $16,400 (for WECC201102424, WECC201102425, WECC201102426, WECC201102438) | Self-Certification | On May 5, 2011, SPPC submitted a Mitigation Plan to address this violation. In the Mitigation Plan, SPPC identified the cause of the violation as SPPC's "one UF relay (Ft Churchill 130) was self-certified as being out of compliance on its maintenance interval." WECC confirmed that SPPC tested the relay on December 23, 2010. SPPC ensured all relays were added to its automated tracking system, PowerBase, removing the necessity for a manual or human reference. SPPC also updated its PRC-008 policy by modifying its maintenance intervals for UFLS relays to match the maintenance interval associated with SPPC's PRC-005 program. | 2011-03-28 | 2011-06-27 | Neither Admits nor Denies | WECC evaluated SPPC's internal compliance program (ICP) and found the following: SPPC has a fully documented ICP that has been reviewed and approved by general counsel who also serves as its chief compliance officer. SPPC's oversight position is identified and staffed, and is supervised at a high level within the company. The ICP oversight position has direct access to the CEO and board of directors and SPPC operates and manages the ICP independently from personnel responsible for compliance with the Reliability Standards. The ICP has sufficient staff and an adequate budget, SPPC senior management support and participate in the ICP, and SPPC's ICP has an annual review cycle. Based on these findings, WECC concluded that SPPC has an effective compliance culture.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Sierra Pacific Power Company (SPPC), d/b/a NV Energy | NCR05390 | WECC201102438 | Settlement Agreement | From March 14, 2011 through March 25, 2011, WECC conducted an on-site compliance audit of SPPC (Audit). During and prior to the Audit, the Audit team reviewed SPPC's Special Protection System Maintenance and Testing Version 3, dated February 14, 2011 (SPS Plan). Of the six Special Protection Systems identified in SPPC's SPS Plan, the Audit team identified two Special Protection Systems where SPPC failed to maintain and test associated station batteries within the intervals defined in the SPS Plan. SPPC could not demonstrate that it maintained and tested the station batteries at the Rusty Spike station, associated with the Airport 173 Line Thermal Overload SPS, and the Eight Mile station, associated with the Eight Mile Creek Overload SPS, within the intervals defined in the SPS Plan. These two batteries were already self-reported as out of compliance in PRC-005, but were not self-reported again in PRC-017. Therefore, the Audit team determined SPPC had a possible violation of PRC-017-0 R2. The Audit team forwarded its findings to Enforcement. Enforcement reviewed the Audit findings and determined SPPC's failure to maintain and test station batteries at the Rusty Spike and Eight Mile facilities within the intervals defined in SPPC's Special Protection System maintenance and testing program resulted in SPPC not implementing its program. For these reasons, Enforcement determined SPPC had a violation of PRC-017-0 R2. SPPC is subject to this Standard as a Transmission Owner, Generator Owner and Distribution Provider. | PRC-017-0 | R2 | Lower | Lower | SPPC conducts quarterly station battery inspections. This violation relates to SPPC's failure to conduct its annual (not to exceed 16 month) scheduled SPS battery tests. Although SPCC did not perform annual inspection, SPPC did not miss its quarterly battery inspections. SPPC personnel are aware of the condition of the batteries based on the quarterly inspections and would note and take action if SPPC detected a potential battery failure. The violation only relates to two of SPPC's six Special Protection Systems. Further, the violation is associated with station batteries whose battery maintenance records receive regular review from protection engineers. For these reasons, WECC determined this violation posed minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). | 7/17/2010 (When SPPC missed testing station batteries pursuant to its program) | 3/23/2011 (Mitigation Plan completion) | $16,400 (for WECC201102424, WECC201102425, WECC201102426, WECC201102438) | Compliance Audit | On May 5, 2011, SPPC submitted a Mitigation Plan to address this violation. In the Mitigation Plan, SPPC stated SPPC personnel "is now aware that non-compliance should be reported under all standards the piece of equipment in violation is found under" and noted that SPPC is addressing the batteries "in the Mitigation Plan [submitted] under PRC-005-1 R2." | 2011-03-23 | 2012-01-10 | Neither Admits nor Denies | WECC evaluated SPPC's internal compliance program (ICP) and found the following: SPPC has a fully documented ICP that has been reviewed and approved by general counsel who also serves as its chief compliance officer. SPPC's oversight position is identified and staffed, and is supervised at a high level within the company. The ICP oversight position has direct access to the CEO and board of directors and SPPC operates and manages the ICP independently from personnel responsible for compliance with the Reliability Standards. The ICP has sufficient staff and an adequate budget, SPPC senior management support and participate in the ICP, and SPPC's ICP has an annual review cycle. Based on these findings, WECC concluded that SPPC has an effective compliance culture.
2011-12-30 | FERC | NP12-10-000 | Midwest Reliability Organization (MRO) | Midwest Independent Transmission System Operator, Inc. (MISO) | NCR00826 | MRO201100272 | Settlement Agreement | On September 18, 2007, the MRO region experienced a category four disturbance which included a cascade of multiple lines that form the Minnesota-Wisconsin Stability Interface. The loss of these lines was followed by over frequency generator tripping and under frequency load shedding which ultimately resulted in the formation of system islands. MRO initiated a Compliance Violation Investigation (CVI) on March 3, 2008 and NERC assumed leadership of this CVI on March 5, 2008. On September 14, 2009, NERC issued a Preliminary Notice of Findings and Analysis to MISO detailing a finding of noncompliance with the Standard. The CVI team determined that MISO, as the Reliability Coordinator (RC), failed to provide directives to generators in a clear, concise, and definitive manner; failed to use proper three-way communications; and did not ensure that three-way protocols were followed, as required by the Standard. In the first instance, the directive given by MISO to one entity was unclear when it failed to identify the amount of generation MISO was directing be brought online. MRO determined that the entity used three-way communication in repeating back the directive to MISO and responded appropriately. In the second instance, three-way communication procedure was not followed in the directive given by MISO to another entity. MRO determined that even though the directive from MISO to the second entity was clear and carried out properly by the recipient operator, the three-way communication protocol was not followed. The directives were given during the restoration period and did not contribute to the loss of load. | COM-002-2 | R2 | Medium | Severe (Note that COM-002-2, R2 did not have an assigned VSL or applicable Levels of Noncompliance on the date of the violation, September 18, 2007. The VSL assignments were approved subsequently.) | MRO determined that MISO's violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because in both instances, MISO's directives were followed and correctly implemented, thereby satisfying the Standard's purpose of ensuring effective communications by operating personnel. Further, the Event Analysis Report recognized that MISO's rapid coordination enabled quick restoration (accomplished in 8 minutes 11 seconds) and stabilization of the BPS in the area for which MISO is the Reliability Coordinator. | 2007-09-18 | 2007-09-18 | 0 | NERC Compliance Violation Investigation | On May 13, 2011, MISO submitted a Mitigation Plan (MIT-07-3708) to MRO to address the violation of COM-002-2 R2. In accordance with the Mitigation Plan, MISO engaged in various mitigation activities, including: (1) provided dedicated communications training to its personnel in two training cycles in 2009 and in every training cycle in 2010; (2) revised its policies and procedures to improve compliance with this Standard, including a script to be used by operators; (3) engaged its Members in development and use of appropriate telephone protocol procedures, training and drills to ensure that communications occur in compliance with the Standard; (4) initiated operator call sampling and incentives; (5) tied the results of such sampling directly to operator performance assessments; and (6) reinforced compliance with this Standard through a slogan contest, all-employee meeting, visual support, and dedicated training. | 2008-12-08 | 2011-05-16 | Does not contest | MRO considered the following mitigating factors when determining the penalty amount: (1) MISO has no previous violations of the instant Standard and has other violations in the ReliabilityFirst region which do not involve the same or similar Standards; (2) MISO has a documented compliance program and culture that are well-defined and well-established through its corporate policy. The MISO Standards Compliance and Strategy department has a staff of eight employees headed by a Compliance Officer; and (3) MISO will conduct by April 1, 2012 two "Communications Forums" focused on control room communications and compliance with this Standard, and intended to promote collaboration and coordination between the entities responsible for complying with this Standard. MRO did not consider the loss of load in the penalty determination because these directives were given during the restoration period after the loss of load. MRO determined that there were no additional mitigating or aggravating factors in determining the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Northeast Power Coordinating Council (NPCC) | Mirant Bowline, LLC (Mirant Bowline) | NCR07145 | NPCC200900121 | Settlement Agreement | During an October 11, 2009 through October 16, 2009 compliance audit of Mirant Bowline, NPCC discovered a violation of PRC-005-1 R1.1. NPCC determined that Mirant Bowline, as a Generator Owner, did not show maintenance and testing intervals for its current transformer (CT) and voltage or potential transformer (PT) generation Protection System devices. Documents provided to NPCC by Mirant Bowline, of its relay maintenance and testing program for the bulk power system, did not show maintenance and testing intervals for its CT and PT devices. The components of the Protection System include protective relays, associated communication systems, CTs, PTs, station batteries and DC control circuits. The 70 total CTs and PTs comprised fewer than 25% of the 408 applicable Protection System devices. | PRC-005-1 | R1; R1.1 | High | Lower | NPCC Enforcement determined that the violation posed a moderate but not serious or substantial risk to the reliability to the bulk power system. Although Mirant Bowline could not provide evidence that it verified the integrity of the CT and PT devices by performing testing on these devices periodically or defined testing intervals for these devices as per Mirant Bowline's maintenance document, there were no misoperation events or indication of failing/failed devices during the period. CT and PT testing was completed on April 1, 2010 for units 1 and 2, and all CT and PT devices tested satisfactorily. Also, based on evidence reviewed, no other potential evidence of noncompliance was identified with respect to all other aspects of Mirant Bowline. Mirant Bowline also employs back-up relaying providing backup protection should the primary systems fail. | 6/21/2007 (When Mirant Bowline registered for the Generator Owner function.) | 2/25/2010 (When Mirant Bowline's maintenance and testing program was enhanced to include maintenance and testing intervals for the CT and PT devices.) | $17,500 (for NPCC200900121 and NPCC200900122) | Compliance Audit | 1. Completed testing of CT and PT devices. 2. Revised the Protection System maintenance and testing program to include last testing date and next testing date for CT and PT devices. | 2011-05-03 | 2011-07-28 | Neither Admits nor Denies | Mirant Bowline has a documented internal compliance program which was reviewed and considered a neutral factor by NPCC.
2011-12-30 | FERC | NP12-10-000 | Northeast Power Coordinating Council (NPCC) | Mirant Bowline, LLC (Mirant Bowline) | NCR07145 | NPCC200900122 | Settlement Agreement | During an October 11, 2009 through October 16, 2009 compliance audit of Mirant Bowline, NPCC discovered a violation of PRC-005-1 R2.1 and R2.2. NPCC determined that Mirant Bowline, as a Generator Owner, did not show testing of any of its 70 current transformer (CT) and voltage or potential transformer (PT) devices on its generation Protection System list. This list did show a listing of all protective relays, date last tested, testing interval periodicity and next required test date. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | NPCC Enforcement determined that the violation posed a moderate but not serious or substantial risk to the reliability to the bulk power system. Although Mirant Bowline could not provide evidence that it verified the integrity of the CT and PT devices by performing testing on these devices periodically or defined testing intervals for these devices as per Mirant Bowline's maintenance document, there were no misoperation events or indication of failing/failed devices during the period. CT and PT testing was completed on April 1, 2010 for units 1 and 2, and all CT and PT devices tested satisfactorily. Also, based on evidence reviewed, no other potential evidence of noncompliance was identified with respect to all other aspects of Mirant Bowline's relay maintenance and testing program for the requirements of PRC-005-1. Mirant Bowline also employs back-up relaying providing backup protection should the primary systems fail. | 6/21/2007 (When Mirant Bowline registered for the Generator Owner function.) | 5/3/2011 (Mitigation Plan completion.) | $17,500 (for NPCC200900121 and NPCC200900122) | Compliance Audit | 1. Completed testing of CT and PT devices. 2. Revised the Protection System maintenance and testing program to include last testing date and next testing date for CT and PT devices. | 2011-05-03 | 2011-07-28 | Neither Admits nor Denies | Mirant Bowline has a documented internal compliance program which was reviewed and considered a neutral factor by NPCC. Affiliated entities of Mirant Bowline have prior violations of PRC-005-1 R2.1 which were not considered aggravating factors in penalty determination. The filings: NP09-25-000 (Mirant Mid-Atlantic LLC), NP-10-2-000 (Mirant Potomac River, LLC), NP10-65-000 (Mirant Delta, LLC) and NP11-88-000 (Mirant Potrero, LLC), all include prior PRC-005-1 R2.1 violations by affiliates of Mirant Bowline. These prior violations were not considered aggravating factors because the conduct involved in the instant violation was not repetitive of the prior affiliates' conduct. In addition, there was nothing in the record to suggest that broader corporate issues were implicated.
2011-12-30 | FERC | NP12-10-000 | Northeast Power Coordinating Council (NPCC) | Niagara Mohawk Power Corporation (NMPC) | NCR07163 | NPCC201000177 | Settlement Agreement | On April 13, 2010, NPCC conducted a Spot Check of NMPC and discovered a violation of COM-002-2 R2. NPCC determined that NMPC, as a Transmission Operator (TOP), was in violation of the Standard. The NMPC control room operator failed to issue directives in a clear, concise, and definitive manner as required by the Standard. When issuing a directive to perform switching at a substation, the NMPC control room operator did not use the proper communication technique. Further, the NMPC control room operator did not ensure that the recipient of the communication repeated the information back correctly, as required by the Standard. The operator at the substation willingly accepted the switching order and performed the switching without incident. | COM-002-2 | R2 | Medium | Severe | NPCC determined that this violation posed a moderate risk but not serious or substantial risk to the reliability of the bulk power system (BPS) because the communication at issue was given during a period of restoration of equipment, and therefore took place under normal conditions rather than during a time of high stress, system instability, or system emergency. Additionally, the directive which was given in an improper manner was nonetheless carried out by the recipient in the correct manner and thus did not cause any additional risk. NPCC determined that there was a moderate risk because the switching directives associated with the communication errors could have been performed incorrectly which would have resulted in delays in proper restoration or additional equipment being forced out of service. | 6/14/2009 (when the improper communication occurred) | 2009-06-14 | 25000 | Spot Check | On November 23, 2010, NMPC submitted a Mitigation Plan to address the violation of COM-002-2 R2. In accordance with the Mitigation Plan: (1) NMPC's Transmission Control Center management team began random auditing of three-part communications of Security and System Operator communications. An audit form was developed and random tapes of communications were reviewed and discussed with the operator. The operators are made aware of communication technique expectations during these audits; (2) NMPC performed enhanced internal refresher training during Cycle 3 training in June 2010. Material covered included the COM-002-2 Reliability Standard, the NYISO Communication Running Order, and featured an audit of random communication by all of the class participants; (3) NMPC participated in the NYISO Fall 2010 System Operator Training Seminar, which featured refresher training on COM-002-2 in addition to an exercise in three-part communications at the NYISO Training Center; and (4) NMPC instituted a greater emphasis on three-part communication in all continuing operator training. | 2010-12-03 | 2011-03-11 | Neither Admits nor Denies | NPCC considered NMPC's Internal Compliance Program, which was in place at the time of the violation, to be a mitigating factor when determining the penalty amount. Specifically, NPCC considered that NMPC's ICP exists with sufficient Senior Leadership involvement; the ICP describes the annual training program related to compliance; NMPC reviews the ICP program activities regularly; NMPC keeps up to date with NERC/NPCC activities; and NMPC provides ample communication of the company’s commitment and expectations of employees.
2011-12-30 | FERC | NP12-10-000 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Niles Light Department (City of Niles) | NCR02710 | RFC201000674 | Settlement Agreement | RFC conducted a compliance audit of the City of Niles from October 18, 2010 to October 29, 2010. RFC determined that the City of Niles, as a Distribution Provider (DP), failed to provide the basis for the testing and maintenance interval applicable to its DC control circuitry in its Protection System maintenance and testing program, in violation of PRC-005-1, R1. RFC determined that although the Program required testing and maintenance according to a four-year testing and maintenance interval, the City of Niles did not document the basis for the identified testing and maintenance interval, as required by PRC-005-1, R1. The DC control circuitry represents 2 of 53 Protection System devices. | PRC-005-1 | R1 | High | Severe (from July 18, 2007 to May 18, 2011); High from May 19, 2011 to June 22, 2011 | RFC determined that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, the City of Niles is a municipal utility with a peak load of 68 MW. Second, the City of Niles represented that it performed testing on its DC control circuitry devices in May 2007 as part of the installation and commissioning testing, although it did not retain records of the testing activity. In addition, the City of Niles completed maintenance and testing on its DC control circuitry on May 25, 2011 and found no problems with the devices. The entity completed this testing approximately four years from May 2007, the time it last tested the devices, which corresponds to the testing interval for DC circuitry now stated in its maintenance and testing program. | 9/28/2007(City of Niles was required to comply with this Standard) | 06/22/2011 (Mitigation Plan was completed) | $4000 (for RFC201000674 and RFC201000675) | Audit | On June 24, 2011, the City of Niles submitted as complete Mitigation Plan (MIT-07-3956) to address the violations of PRC-005-1 R1 and R2. In accordance with the Mitigation Plan, the City of Niles: (1) Revised its Program on June 22, 2011 to include the basis for the four-year testing and maintenance interval for its DC control circuitry; and (2) Performed all outstanding maintenance and testing on its DC control circuitry in accordance with the updated Plan. | 2011-06-22 | 2011-08-26 | Neither admits nor denies | RFC determined that there were no aggravating or mitigating factors in determining the penalty amount. RFC stated the City of Niles did not have a formal Internal Compliance Program (ICP).
2011-12-30 | FERC | NP12-10-000 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Niles Light Department (City of Niles) | NCR02710 | RFC201000675 | Settlement Agreement | RFC conducted a compliance audit of the City of Niles from October 18, 2010 to October 29, 2010. RFC determined that the City of Niles, as a Distribution Provider (DP), failed to provide documentation that it implemented its maintenance and testing program as it applied to its DC control circuitry. The City of Niles failed to provide documentation that it maintained and tested its two DC circuitry devices. As a result, the City of Niles failed to provide evidence (a) that it maintained and tested any of its DC control circuitry within the defined intervals of PRC-005-1, R2, and (b) of the date it last maintained and tested its DC control circuitry, as required by the PRC-005-1, R2 | PRC-005-1 | R2 | High | Severe | RFC determined that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, the City of Niles is a municipal utility with a peak load of 68 MW. Second, the City of Niles represented that it performed testing on its DC control circuitry devices in May 2007 as part of the installation and commissioning testing, although it did not retain records of the testing activity. In addition, the City of Niles completed maintenance and testing on its DC control circuitry on May 25, 2011 and May 27, 2011 and found no problems with the devices. The entity completed this testing approximately four years from May 2007, the time it last tested the devices, which corresponds to the testing interval for DC circuitry now stated in its maintenance and testing program. | 9/28/2007(City of Niles was required to comply with this Standard) | 5/27/2011 (date completed the maintenance and testing of its DC control circuitry) | $4000 (for RFC201000674 and RFC201000675) | Audit | On June 24, 2011, the City of Niles submitted as complete Mitigation Plan (MIT-07-3956) to address the violations of PRC-005-1 R1 and R2. In accordance with the Mitigation Plan, the City of Niles: (1) Revised its Program on June 22, 2011 to include the basis for the four-year testing and maintenance interval for its DC control circuitry; and (2) Performed all outstanding maintenance and testing on its DC control circuitry in accordance with the updated Plan. | 2011-06-22 | 2011-08-26 | Neither admits nor denies | RFC determined that there were no aggravating or mitigating factors in determining the penalty amount. RFC stated the City of Niles did not have a formal Internal Compliance Program (ICP).
2011-12-30 | FERC | NP12-10-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000629 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of VAR-002-1 R2. ReliabilityFirst determined that Sunbury, as a Generator Operator, had failed to maintain its voltage schedule as directed by its Transmission Operator (TOP). PJM Interconnection, LLC (PJM), Sunbury’s TOP, provides a default voltage schedule in the PJM Manual 03 "Transmission Operations" for those operators that do not receive a specific voltage schedule. The 230 kV voltage schedule is 235 kV, plus or minus 4 kV; PJM Manual 03 also lists a high limit voltage of 242 kV. Sunbury never received a specific voltage schedule from its TOP, and never obtained an exemption from the TOP. Sunbury does not and cannot control the transformers that control the switchyard voltages because they are located in the switchyards and are owned and operated by a different interconnected utility. On July 12, 2010 and August 20, 2010, the 230 kV switchyard at Sunbury exceeded the PJM default voltage schedule. On July 12, 2010 for forty-five minutes, the Sunbury 230 kV switchyard was at 239.5 kV, and on August 20, 2010 for six hours, the Sunbury 230 kV switchyard was above 239 kV. Although Sunbury exceeded the PJM default voltage schedule; it did not exceed the high limit of 242 kV. | VAR-002-1 | R2 | Medium | Lower | This violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system because at all relevant times, Sunbury cooperated with any voltage or reactive assistance requests received from the Transmission Owner or from the TOP. Sunbury has never received notification from either the Transmission Owner or the TOP that Sunbury failed to follow a directive related to voltage or reactive assistance. In addition, the Transmission Owner also provided a screen shot from its computers that monitor and control the Susquehanna region 230 kV voltages in which Sunbury is located. This screen shot indicates the high limit of 242 kV, which Sunbury did not exceed. Furthermore, the generator Automatic Voltage Regulators (AVRs) are always operated in automatic mode except during startup periods or in case of malfunction or system anomalies. In all cases, the TOP is notified whenever the AVR is switched to manual mode, and then again when it is returned to automatic mode. Sunbury conducted reactive testing on Unit 4 (required by PJM) on September 28, 2010. This testing requires that the generator be operated to its limit of MVAR lag operation for one hour. Subsequently, the generator must be operated to its limit of MVAR lead operation. Since Sunbury does not control or have access to the yard voltages, the voltage data was provided by the Transmission Owner. The voltage data provided by the Transmission Owner shows that there was no voltage change in the 230 kV yard, even though Sunbury operated the generator to both its lead and lag limits. | 8/2/2007 (When the Standard became mandatory and enforceable.) | 5/4/2011 (Mitigation Plan completion.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | 1. Sunbury conducted a conference call between Sunbury and the other interconnected utility to discuss voltage control capability; 2. Sunbury contacted PJM to discuss the voltage schedule issue to determine feasibility or possible exclusions; 3. The other interconnected utility conducted a system study to determine suitable voltage control based upon Sunbury maintaining low side generator step-up (GSU) voltage/reactive; 4. The information was submitted to PJM for approval; 5. Sunbury installed metering as necessary; 6. PJM reviewed the study and commented; and 7. PJM issued a voltage directive to Sunbury. | 2011-07-06 | 2011-12-28 | Neither Admits nor Denies | Due to extenuating circumstances associated with the violation of VAR-002-1 R2, there is no monetary penalty associated with the violation of VAR-002-1 R2. These included Sunbury never receiving a specific voltage schedule from its TOP, and never obtaining an exemption from the TOP, as well as the fact that Sunbury does not and cannot control the transformers that control the switch yard voltages. ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
2011-12-30 | FERC | NP12-10-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000630 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of FAC-008-1 R1.2.1. ReliabilityFirst determined that Sunbury, as a Generator Owner, failed to include the Ratings Methodology for its transmission conductors and relay protective devices in its Facility Ratings Methodology. Although Sunbury mentioned transmission conductors as part of its system and equipment, Sunbury failed to specifically mention transmission conductors and separately identify their Rating. | FAC-008-1 | R1.2.1 | Medium | High | This violation posed a moderate and not serious or substantial risk to the reliability of the bulk power system because Sunbury did mention the transmission conductors in the Facility Ratings Methodology, and had determined the Ratings for those devices throughout the violation duration. Specifying the transmission conductors as a separate circuit element had no impact on the Facility Ratings overall, nor did it change the identification of the most limiting element. | 6/18/2007 (When the Standard became mandatory and enforceable.) | 11/4/2010 (When Sunbury revised its Facility Ratings Methodology to include transmission conductors.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | 1. Sunbury revised its Facility Ratings Methodology to specify transmission conductors as a separate element included in the Facility Ratings; and 2. Sunbury also revised its Facility Rating Methodology spreadsheet to include the transmission conductors from the main unit transformers to the generator bay. | 2010-11-04 | 2011-02-15 | Neither Admits nor Denies | ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
2011-12-30 | FERC | NP12-10-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000631 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of PRC-005-1 R1. ReliabilityFirst determined that Sunbury, as a Generator Owner, failed to include all maintenance and testing intervals and their basis as well as summaries of maintenance and testing procedures for all of its Protection System devices in its Protection System maintenance and testing program. Sunbury’s Procedure PRC-005 Transmission and Generation Protection System Maintenance and Testing program (Program), dated February 8, 2010, failed to include all necessary elements. The Program failed to include maintenance and testing intervals and their basis for all 50 of its voltage and current sensing devices in violation of PRC-005-1 R1.1. In addition, the Program failed to include summaries of maintenance and testing procedures for all voltage and current sensing devices and its eight direct current control circuits in violation of PRC-005-1 R1.2. This violation involved 58 of Sunbury's 108 (55%) Protection System devices. | PRC-005-1 | R1 | High | Severe | This violation posed a moderate and not serious or substantial risk to the reliability of the bulk power system. Specifically, the risk was mitigated because Sunbury has redundant protection in place. In addition, Sunbury has alarms that sound in both the plant control rooms and the plant control house upon the loss of power or similar malfunction. Additionally, except as noted in these violation descriptions, Sunbury tested its Protection System devices in accordance with their intervals, and all devices were functional and available. | 6/18/2007 (When the Standard became mandatory and enforceable.) | 10/20/2010 (When Sunbury updated its Protection System maintenance and testing program.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | 1. Sunbury revised its Program to clarify battery maintenance and testing intervals, and that the maintenance and testing interval listed in the Program applies to all generator Protection System devices; and 2. The revised Program also includes summaries of maintenance and testing procedures for all Protection System devices. | 2010-12-03 | 2011-03-10 | Neither Admits nor Denies | ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
2011-12-30 | FERC | NP12-10-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Sunbury Generation LP (Sunbury) | NCR06030 | RFC201000632 | Settlement Agreement | ReliabilityFirst conducted a compliance audit of Sunbury (Audit) from September 13, 2010 through September 28, 2010, during which ReliabilityFirst discovered a violation of PRC-005-1 R2. ReliabilityFirst determined that Sunbury, as a Generator Owner, failed to provide evidence that it maintained and tested direct current control circuitry within the defined intervals and failed to identify the dates that it last tested direct current control circuitry. Sunbury failed to test direct current control circuitry within the defined interval, in violation of PRC-005-1 R2.1. In addition, Sunbury failed to identify the dates that it last tested its direct current control circuitry, in violation of PRC-005-1 R2.2. This violation involved all of Sunbury’s direct current control circuitry (100%) which constituted eight of Sunbury’s 108 (7.4%) Protection System devices. | PRC-005-1 | R2; R2.1; R2.2 | High | Severe | This violation posed a moderate and not serious or substantial risk to the reliability of the bulk power system. Specifically, the risk was mitigated because Sunbury has redundant protection in place. In addition, Sunbury has alarms that sound in both the plant control rooms and the plant control house upon the loss of power or similar malfunction. Additionally, except as noted in these violation descriptions, Sunbury tested its Protection System devices in accordance with their intervals, and all devices were functional and available. | 6/18/2007 (When the Standard became mandatory and enforceable.) | 10/20/2010 (When Sunbury updated its Protection System maintenance and testing program.) | $20,000 (for RFC201000629, RFC201000630, RFC201000631, and RFC201000632) | Compliance Audit | Sunbury completed all delayed maintenance and testing on direct current control circuitry and began recording the test dates of those devices. | 2010-12-03 | 2011-03-10 | Neither Admits nor Denies | ReliabilityFirst considered Sunbury’s compliance program as a mitigating factor in the penalty determination. Sunbury's primary compliance contact reports to the vice president of operations, and its internal compliance program is independent from departments having compliance obligations to the Reliability Standards. In addition, Sunbury reviews the Standards and revises its internal compliance program accordingly. Sunbury also ensures that its compliance staff attends workshops and other available training courses regarding compliance with the Standards.
2011-12-30 | FERC | NP12-10-000 | SERC Reliability Corporation (SERC) | Progress Energy Carolinas (PEC) | NCR01298 | SERC200900412 | Settlement Agreement | On December 8, 2009, PEC self-reported a violation of PRC-005-1 R1. During an investigation into battery inspection work orders, PEC discovered that it had failed to include the appropriate basis for battery maintenance intervals in its maintenance and testing documentation as required by the Standard. SERC was able to verify that PEC has a documented transmission Protection System maintenance and testing program. In 2008, PEC’s Asset Management group made a recommendation to revise the inspection of substation batteries from a six-month interval to a 12-month interval. The revised procedure was scheduled to become effective on August 1, 2009. With the revision, battery inspection and battery maintenance would be performed together on an annual basis. In addition, under the revised procedure, PEC would start conducting battery and battery charger maintenance together in order to streamline and eliminate unnecessarily redundant maintenance activities. PEC’s work management group completed the rescheduling of its battery maintenance activities in anticipation of the revised procedures’ August 1, 2009 implementation date but its procedure drafting group did not revise the Substation Equipment Maintenance Schedule until September 23, 2009, and the battery maintenance procedure until October 26, 2009. SERC determined that PEC, as a Transmission Owner, was in violation of PRC-005-1 R1.1 for failing to include the appropriate basis for battery maintenance intervals in its maintenance and testing documentation, as required by the Standard. There was no PRC-005-1 R2 issue in connection with this December 8, 2009 Self-Report. | PRC-005-1 | R1/ R1.1 | High | Lower | SERC determined that the PRC-005-1 R1.1 violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the revised procedure had been implemented in PEC’s work order management system so that performance of battery maintenance and testing would take place according to the authorized intervals. In addition, all battery voltages are continuously monitored. An alarm would activate if an abnormal voltage was detected, resulting in the initiation of maintenance activity. | 8/1/2009 (date PEC's work order management system was changed to implement the new intervals without updating its procedures) | 1/11/2010 (Mitigation Plan completion) | $12,000 (For SERC200900306, and SERC200900412) | Self-Report | To correct the violation of PRC-005-1 R1.1 and to prevent a recurrence of the violation, PEC performed the following: 1. Developed a specific basis procedure for battery and battery charger maintenance; 2. Revised its Protection Basis Document, which provides the basis for all time-directed preventative maintenance applied to Transmission, Distribution, and Generation Protective Systems on October 26, 2009; 3. Revised the Transmission Maintenance Program Policy to require the group that implements the work management system not to release or modify work orders until they have verified that the procedures governing the work orders have been approved; and 4. Developed check points in a Functional Support Work Scope Document that must be completed by the work management group prior to releasing or modifying work orders. The checklist requires that the procedure’s effective date be recorded and verified prior to the release or modification of a work order. | 2010-01-11 | 2010-08-10 | Admits | Based on PEC’s September 20, 2010 responses to SERC’s Compliance Culture Questionnaire, Progress Energy’s (PEC's parent company) documented compliance program was initially approved on December 13, 2007, and was developed to formally document and drive existing compliance business practices. PEC’s compliance program is disseminated to all organizations within PEC that must comply with NERC Standards. The existence of PEC’s compliance program was a mitigating factor in determining the penalty. Progress Energy’s compliance program is prepared for and approved by Progress Energy’s ERO Steering Committee. The ERO Steering Committee is comprised of officers of PEC and Progress Energy Florida and is chaired by the ERO Compliance Officer, who is Progress Energy’s Executive Vice President – General Counsel and Corporate Secretary. The ERO Compliance Officer is independent of all PEC organizations that must comply with NERC Standards. The ERO Compliance Officer reports directly to the Chairman/President/CEO and has direct access to the Board of Directors. Company Officers participate in bi-monthly ERO Steering Committee meetings and compliance initiatives within their respective departments.
2011-12-30 | FERC | NP12-10-000 | SERC Reliability Corporation (SERC) | Progress Energy Carolinas (PEC) | NCR01298 | SERC200900306 | Settlement Agreement | On August 26, 2009, PEC self-reported a violation of PRC-005-1 R2. PEC discovered this violation while performing an inventory of its Protection System assets located within customer-owned facilities. When PEC inventoried the customer-owned Kinston DuPont 115 kV substation on August 20, 2009, it found two Coupling-Capacitor Voltage Transformers (CCVTs) owned by PEC that were not captured in its database. PEC’s Protection System maintenance and testing program for these CCVTs required maintenance to be performed by April 1, 2009, which had not occurred. PEC performed the required maintenance on August 20, 2009. PEC performed a comprehensive inventory of its Protection System components associated with PRC-005-1 under its Mitigation Plan. On October 25, 2010, PEC filed another Self-Report explaining that during the inventory, it found a column ground relay that had not been included in its equipment database. PEC’s investigation confirmed that the identified column ground relay did not have sufficient documentation to demonstrate that calibrations had been performed within the eight year intervals (+25 %) as required in the maintenance and testing program. The previous test date was July 27, 1998 and therefore, the subsequent testing should have occurred no later than July 27, 2008; however, the required test was not performed until September 2, 2010. SERC reviewed PEC’s Self-Report and its procedure along with the associated records and determined that a violation of PRC-005-1 R2.1 had occurred due to PEC’s failure to complete the required testing and maintenance of the relay within the assigned interval. On December 9, 2010, PEC self-reported an additional violation that was discovered while performing its Mitigation Plan inventory. PEC identified a battery that should have been re-classified on July 1, 2008, as a Protection System device in its equipment database. PEC’s investigation confirmed that the identified battery did not have sufficient documentation to demonstrate that the required maintenance was performed for the six- and 12-month preventative maintenance (PM) (+25%) as required in the maintenance and testing program. The six-month PM should have been performed no later than June 26, 2008, and the twelve-month no later than August 1, 2008, however the required maintenance and testing was not performed until August 13, 2008. SERC reviewed PEC’s Self-Report and procedure along with the associated records and determined that an additional violation of PRC-005-1 R2.1 had occurred due to PEC’s failure to complete the required testing and maintenance of the battery within the assigned intervals. SERC determined that PEC, as a Transmission Owner, was in violation of PRC-005-1 R2.1 for failing to have evidence that its Protection System devices had been maintained and tested within the defined intervals as required. No issues of noncompliance were identified for PEC’s generation Protection System. | PRC-005-1 | R2/ R2.1 | High | Lower | SERC determined that the PRC-005-1 R2.1 violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) The CCVTs are designed to protect a customer’s delivery station and the tap lines serving the station. The CCVTs provide a back-up protective function for the components of the BPS. The devices that provide primary protection for the BPS were being tested and maintained at the prescribed intervals. In addition, testing and maintenance was performed on the CCVTs although not within the intervals specified in PEC's Protection System maintenance and testing program; (2) PEC has multiple layers of protection built into its system. Its 500 kV lines have redundant fast-tripping line protection systems that covers faults to the breakers. The column ground relay provides back-up protection. On September 2, 2010, testing was performed on the column ground relay and no recalibration was required; and (3) The maintenance and testing on the battery was performed two weeks out of interval. In addition, PEC monitors battery voltages in real time and monitors should trigger under-voltage alarms. This should allow for a timely response to a battery problem if the voltage were to drop below a pre-determined level. | 7/1/2008 (date the battery was re-classified as a Protection System device) | 9/30/2010 (Mitigation Plan completion) | $12,000 (For SERC200900306, and SERC200900412) | Self-Report | To correct the violation of PRC-005-1 R2.1 and to prevent a recurrence of the violation, PEC completed the following actions detailed in its Mitigation Plan: 1. Maintenance was performed on the two 115 kV CCVTs the same day that the location was field-verified; 2. PEC's equipment database was corrected to properly show the two CCVTs as located at the Kinston DuPont 115 kV Substation; 3. PEC performed an inventory of its NERC Protection System assets associated with its PRC-005 Protection System equipment. The inventory included verification of the assets within PEC's equipment database, a physical survey of the Protection System assets at PEC substations, including those with customer-owned equipment, as well as a reconciliation of the physical survey results with the PEC equipment database; and 4. PEC reviewed the equipment database process for improvements and re-emphasized the process through training and leadership with emphasis on the necessity of an accurate equipment database for NERC Protection System maintenance. The training targeted Engineering, Maintenance and Construction personnel and covered PEC's NERC Protection System maintenance & testing program, evidence requirements, the equipment database, and the Equipment Change Request process. | 2010-09-30 | 2010-02-14 | Admits | Based on PEC’s September 20, 2010 responses to SERC’s Compliance Culture Questionnaire, Progress Energy’s (parent company) documented compliance program was initially approved on December 13, 2007, and was developed to formally document and drive existing compliance business practices. PEC’s compliance program is disseminated to all organizations within PEC that must comply with NERC Standards. The existence of PEC’s compliance program was a mitigating factor in determining the penalty. Progress Energy’s compliance program is prepared for and approved by Progress Energy’s ERO Steering Committee. The ERO Steering Committee is comprised of officers of PEC and Progress Energy Florida and is chaired by the ERO Compliance Officer, who is Progress Energy’s Executive Vice President – General Counsel and Corporate Secretary. The ERO Compliance Officer is independent of all PEC organizations that must comply with NERC Standards. The ERO Compliance Officer reports directly to the Chairman/President/CEO and has direct access to the Board of Directors. Company Officers participate in bi-monthly ERO Steering Committee meetings and compliance initiatives within their respective departments.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Brazos Electric Power Co Op, Inc. (Brazos) | NCR04016 | TRE201100277 | Settlement Agreement | On February 21, 2011, Brazos, as a Generator Operator, submitted a Self-Report identifying a violation of IRO-001-1.1 R8. At 05:18 CST on February 2, 2011, Electric Reliability Council of Texas Independent System Operator (ERCOT ISO), its Reliability Coordinator, was experiencing a system emergency (EEA‐2a), when it issued the following verbal directive: “Do not take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. Report when online available capacity is at risk due to an adverse circumstance.” At 08:09 the same day, while the system emergency was still in effect, Brazos removed Unit 2 of Whitney Dam, a 15 MW hydroelectric resource, from service in order to conserve water for later use. Realizing the mistake, at 08:11, the Brazos operator requested the Whitney Dam operator return Unit 2 to service, but the unit was then subject to a 30-minute operational limitation delay before restart could occur. Unit 2 was returned to service at 08:42. During the course of the above events, ERCOT ISO was not contacted. Accordingly, Texas RE determined that Brazos did not follow a reliability directive issued by the Reliability Coordinator. | IRO-001-1.1 | R8 | High | High | Texas RE determined this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) due to the 15 MW size of the unit and because Brazos was able to deploy sufficient additional generation from its other available generation resources. | 2/2/2011 (When the Reliability Coordinator issued the directive) | 2/2/2011 (When Brazos complied with the directive) | $8,500 (for TRE201100277 and TRE201100278) | Self-Report | Brazos implemented its mitigation process which emphasizes and clarifies to the Qualified Scheduling Entity (QSE) control room operators and supervisors the required actions in the event of an ERCOT ISO directive. The following two parts reflect the key mitigation activities to this event: 1. Retraining of all QSE control room operators and supervisors to reemphasize their duty and the policy of Brazos to comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. In a meeting of QSE control room operators and supervisors which took place on February 22, 2011, the training was conducted emphasizing the critical nature of following all reliability directives. The importance of complying with Reliability Coordinator directives was reinforced by the manager of market operations and the vice president - power supply and generation at this same meeting. 2. Disciplinary action has been administered to the QSE resource operator on duty and his supervisor in accordance with the Brazos compliance plan dated September 29, 2010, Section D.3, Item 8.B.ii., which institutes “disciplinary action up to and including termination.” The resource operator on duty and the market operations specialist received a written reprimand for failing to follow Brazos’ procedures. The QSE resource supervisor and manager of market operations also received a written instruction to retrain staff. | 2011-04-25 | 2011-10-04 | Neither Admits nor Denies | Brazos' compliance program, in effect at the time of the violation, was considered a mitigating factor in the determination of the penalty amount. Brazos has a named compliance manager with the responsibility to oversee the development, implementation and maintenance of the compliance plan. The compliance manager has direct access to the CEO and/or the Brazos board of directors. Brazos regularly reviews and modifies its internal compliance program on an annual basis. The compliance manager also regularly conducts a compliance awareness program and compliance training program. The compliance training program is included in the compliance plan. Brazos senior management fully supports the compliance program and allocates adequate resources, including outsourcing, self-audits and budgets as well as establishing the necessary positions and associated responsibilities to ensure compliance. Brazos states that on an annual basis it conducts internal audits and reviews its compliance plan.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Brazos Electric Power Co Op, Inc. (Brazos) | NCR04016 | TRE201100278 | Settlement Agreement | On February 21, 2011, Brazos, as a Generator Operator, submitted a Self-Report identifying a violation of TOP-001-1 R3. At 05:18 CST on February 2, 2011, Electric Reliability Council of Texas Independent System Operator (ERCOT ISO), its Reliability Coordinator, was experiencing a system emergency (EEA‐2a), when it issued the following verbal directive: “Do not take units off-line while ERCOT is in emergency operations unless it is due to a forced outage. Report when online available capacity is at risk due to an adverse circumstance.” At 08:09 the same day, while the system emergency was still in effect, Brazos removed Unit 2 of Whitney Dam, a 15 MW hydroelectric resource, from service in order to conserve water for later use. Realizing the mistake, at 08:11, the Brazos operator requested the Whitney Dam operator return Unit 2 to service, but the unit was then subject to a 30-minute operational limitation delay before restart could occur. Unit 2 was returned to service at 08:42. During the course of the above events, ERCOT ISO was not contacted. Accordingly, Texas RE determined that Brazos did not follow a reliability directive issued by the Reliability Coordinator. | TOP-001-1 | R3 | High | Severe | Texas RE determined this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) due to the 15 MW size of the unit and because Brazos was able to deploy sufficient additional generation from its other available generation resources. | 2/2/2011 (When the Reliability Coordinator issued the directive) | 2/2/2011 (When Brazos complied with the directive) | $8,500 (for TRE201100277 and TRE201100278) | Self-Report | Brazos implemented its mitigation process which emphasizes and clarifies to the Qualified Scheduling Entity (QSE) control room operators and supervisors the required actions in the event of an ERCOT ISO directive. The following two parts reflect the key mitigation activities to this event: 1. Retraining of all QSE control room operators and supervisors to reemphasize their duty and the policy of Brazos to comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. In a meeting of QSE control room operators and supervisors which took place on February 22, 2011, the training was conducted emphasizing the critical nature of following all reliability directives. The importance of complying with Reliability Coordinator directives was reinforced by the manager of market operations and the vice president - power supply and generation at this same meeting. 2. Disciplinary action has been administered to the QSE resource operator on duty and his supervisor in accordance with the Brazos compliance plan dated September 29, 2010, Section D.3, Item 8.B.ii., which institutes “disciplinary action up to and including termination.” The resource operator on duty and the market operations specialist received a written reprimand for failing to follow Brazos’ procedures. The QSE resource supervisor and manager of market operations also received a written instruction to retrain staff. | 2011-04-25 | 2011-10-04 | Neither Admits nor Denies | Brazos' compliance program, in effect at the time of the violation, was considered a mitigating factor in the determination of the penalty amount. Brazos has a named compliance manager with the responsibility to oversee the development, implementation and maintenance of the compliance plan. The compliance manager has direct access to the CEO and/or the Brazos board of directors. Brazos regularly reviews and modifies its internal compliance program on an annual basis. The compliance manager also regularly conducts a compliance awareness program and compliance training program. The compliance training program is included in the compliance plan. Brazos senior management fully supports the compliance program and allocates adequate resources, including outsourcing, self-audits and budgets as well as establishing the necessary positions and associated responsibilities to ensure compliance. Brazos states that on an annual basis it conducts internal audits and reviews its compliance plan.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | ExxonMobil Refining and Supply Company (ExxonMobil) | NCR04058 | TRE201000124 | Settlement Agreement | On May 18, 2010, after receiving notices from Texas RE of an upcoming compliance audit, ExxonMobil submitted a Self-Report to Texas RE concerning a violation of PRC-005-1 R2. The Self-Report described a failure to perform maintenance and testing on station batteries, protective relays, and current and potential transformers with the defined intervals of ExxonMobil’s Protection System Maintenance and Testing Program (Program) and failure to provide adequate documentation of maintenance and test results as required by the Program. Texas RE determined that ExxonMobil, as a Generator Owner, missed quarterly testing on battery pilot cell tests, missed the annual battery system load tests and certain 5-year load tests that were required under ExxonMobil's battery maintenance and testing program. ExxonMobil missed testing some relays under its two year maintenance and testing cycle for its protective relays. ExxonMobil also missed some of its annual load check tests for current and potential transformers. 403 or 71% of ExxonMobil's 569 devices were affected. | PRC-005-1 | R2 | High | High | This violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because although there is a risk of protection system failure or misoperation due to the lack of proper maintenance and calibration of the protective relays and battery systems, Texas RE determined that if the facility experienced an issue, it would be isolated to ExxonMobil's facility. Furthermore, redundant relaying schemes were in place. In addition, the facility at issue is relatively small, providing the BPS with a net of 50 MW capacity operating at approximately 20% capacity factor. | 6/28/2007 (date ExxonMobil was registered on the Compliance Registry) | 7/15/2011 (Mitigation Plan completion) | $13,000 (for TRE201000124 and TRE201000123) | Audit | • ExxonMobil provided all available missing maintenance records for Protection Systems devices to Texas RE. • ExxonMobil discussed TRE's Audit findings with its maintenance personnel, and provided refresher training in the proper use of its scheduling/tracking and record retention systems. • ExxonMobil reviewed its maintenance and testing procedures for its Protection Systems devices, and made modifications to include steps for record retention. • ExxonMobil completed all outstanding maintenance and testing for its Protection Systems devices. | 2011-07-15 | 2011-07-20 | Neither Admits nor Denies | Texas RE received the Self-Report on May 18, 2010, after Texas RE sent an Audit notification to ExxonMobil. The Audit concluded July 21, 2010, and is the date the violations were deemed to have been discovered by Texas RE. A Settlement Agreement covering several violations, including a violation of PRC-005-1 R2 for ExxonMobil Oil Corporation - Beaumont Refinery (ExxonMobil BR) (NCR01239), an affiliate of ExxonMobil in the SERC Region, (NOC-428) filed with FERC under NP10-90-000 on March 31, 2010. On April 30, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Texas RE determined that ExxonMobil BR’s previous violation of PRC-005-1 R2 in NOC-428 constituted a prior violation that should be considered an aggravating factor in the penalty determination. While ExxonMobil has multiple documented operating and maintenance procedures in place to ensure NERC compliance, Texas RE did not consider ExxonMobil’s compliance program as a mitigating factor in determining the penalty.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | ExxonMobil Refining and Supply Company (ExxonMobil) | NCR04058 | TRE201000123 | Settlement Agreement | On May 18, 2010, after receiving notices from Texas RE of an upcoming compliance audit, ExxonMobil submitted a Self-Report to Texas RE concerning a violation of CIP-001-1 R2. The Self-Report described ExxonMobil’s failure to include consistent communications procedures in its sabotage reporting guidelines. Texas RE determined that ExxonMobil, as a Generator Operator, did not have a sabotage procedure sufficient to show compliance with the Standard. An ExxonMobil Baytown Complex Emergency Procedure (Procedure) was created in April 2008 to directly address sabotage events that would impact the bulk electric grid. The sabotage procedure did not consistently contain provisions for the communication of information concerning sabotage events to ERCOT Independent System Operator. Texas RE determined that the Procedure was not sufficient as a stand-alone document to demonstrate compliance, as it included multiple procedures concerning various types of sabotage that could impact the electric grid. | CIP-001-1 | R2 | Medium | High | This violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because ExxonMobil operators were aware of the requirement to contact ERCOT ISO as an operating practice. Certain, but not all, ExxonMobil sabotage procedures specify ERCOT ISO as a party to contact in the event of sabotage. Texas RE determined that this violation was principally documentation-related. | 6/28/2007 (date ExxonMobil was registered on the Compliance Registry | 1/12/2011 (Mitigation Plan completion) | $13,000 (for TRE201000124 and TRE201000123) | Audit | ExxonMobil included ERCOT ISO in the contact lists for the following emergency procedures: Bomb Threat, Suspicious Package, Suspicious Powder, and Unauthorized Intruder. | 2011-01-12 | 2011-07-20 | Neither Admits nor Denies | Texas RE received the Self-Report on May 18, 2010, after Texas RE sent an Audit notification to ExxonMobil. The Audit concluded July 21, 2010, and is the date the violations were deemed to have been discovered by Texas RE. While ExxonMobil has multiple documented operating and maintenance procedures in place to ensure NERC compliance, Texas RE did not consider ExxonMobil’s compliance program as a mitigating factor in determining the penalty.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Luminant Generation Company, LLC (Luminant) | NCR10219 | TRE201000273 | Settlement Agreement | On September 2, 2010, Luminant submitted a Self-Report identifying a violation of PRC-005-1 R2. Luminant, as a Generator Owner, failed to perform maintenance and testing on some of its protection system devices within the stated intervals required by its Protection System Maintenance and Testing Program (Program). Out of 1,068 protection system devices, tests for 76 devices (7.12% of total devices) comprising some relays and instrument transformers were completed outside the documented test intervals (three-year periodicity). These 76 protection system devices were not identified and included in Luminant's Program. All of these relays and sets of current transformers are related to generator breaker failure protection in the switchyard which was common to both the generating units and the Transmission Owner until 2001, when the ownership of the switchyard devices was segregated. After ownership transfer, Luminant did not consistently include the generator breaker failure and bus differential devices in its program which led to these devices not being identified. Prior to 2001, all these devices were maintained by the Transmission Owner. Overall, current transformers and potential transformers were included as a protection category in the maintenance and testing program, only the specific devices mentioned in this violation were left out of the program. | PRC-005-1 | R2 | Lower | Lower | The potential risk was considered a moderate risk but not a serious or substantial risk to the bulk power system. Most of the relays and associated CTs which were not timely tested are micro-processor based devices and self-monitored. NERC and industry maintenance standards recommend testing such devices anytime between five years and 12 years. Luminant has three-year testing intervals. Moreover, all devices were properly maintained and tested prior to September 2001 by the transmission provider. | 1/31/2008 (date Luminant registered with NERC registry) | 11/16/2011 (the date the Mitigation Plan was completed) | $18,000 (For TRE201000272, TRE201000273 and TRE201000274) | Self-Report | Luminant submitted a Mitigation Plan on September 3, 2010 to Texas RE outlining its mitigating actions, which included: 1. Verify the completeness of the Registered Entities’ Protection System device listing by utilizing protection system electrical drawings and/or physical site inspections; 2. Test the identified relays and current transformers; 3. Place identification labels on the affected relay devices to clearly identify ownership and responsibility for maintenance and testing; 4. Review and update Protection System Maintenance and Testing procedures and processes; 5. Review and modify the Luminant Compliance and Tracking System (LCATS) protective system maintenance and testing activities to ensure timely notifications are distributed to appropriate responsible company personnel. This will provide automatic notifications to ensure maintenance and testing activities are performed in order to meet the required periodicity, and provide management review of testing activities and documentation; and 6. Train appropriate company personnel on updated procedures and processes. | 2011-11-16 | 2011-12-21 | Admits | Texas RE considered the compliance program to be a mitigating factor in penalty determination. Luminant is a subsidiary of Energy Future Holdings Corp. (EFH). EFH has a designated corporate compliance office with responsibility to develop, implement, enforce, and maintain the EFH Compliance Program. The compliance office is accountable to the Audit Committee of the EFH Board of Directors and reports to the Audit Committee regarding the administration of the Compliance Program and any proposed substantive changes to the Compliance Program. The Compliance Leadership Team is made up of the heads of Internal Audit, Corporate Security, Human Resources, Compliance, Employment Law and Legal, or their designee(s), and meet as frequently as necessary to coordinate respective activities under the Compliance Program.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Big Brown Power Company, LLC (Big Brown) | NCR10217 | TRE201000272 | Settlement Agreement | On September 2, 2010, Big Brown submitted a Self-Report identifying a violation of PRC-005-1 R2. Big Brown, as a Generator Owner, failed to perform maintenance and testing on some of its protection system devices within the stated intervals required by its Protection System Maintenance and Testing Program (Program). Out of 58 protection system devices, ten (17.24% of total devices) devices comprising some relays and instrument transformers were completed outside the documented test intervals (three year periodicity). These ten protection system devices were not identified and included in Big Brown's Program. All of these relays and sets of current transformers are related to generator breaker failure protection in the switch yard which was common to both the generating units and the Transmission Owner until 2001, when the ownership of the switchyard devices was segregated. After ownership transfer, Big Brown did not consistently include the generator breaker failure and bus differential devices in its program which led to these devices not being identified. Prior to 2001, all these devices were maintained by the Transmission Owner. Overall, current transformers and potential transformers were included as a protection category in the maintenance and testing program, only the specific devices mentioned in this violation were left out of the program. | PRC-005-1 | R2 | Lower | Lower | The potential risk was considered a moderate risk but not a serious or substantial risk to the bulk power system. Most of the relays and associated CTs which were not timely tested are micro-processor based devices and self-monitored. NERC and industry maintenance standards recommend testing such devices anytime between five years and 12 years. Big Brown has three-year testing intervals. Moreover, all devices were properly maintained and tested prior to September 2001 by the transmission provider. | 1/31/2008 (date Big Brown registered with NERC registry) | 11/16/2011 (the date the Mitigation Plan was completed) | $18,000 (For TRE201000272, TRE201000273 and TRE201000274) | Self-Report | Big Brown submitted a Mitigation Plan on September 3, 2010 to Texas RE outlining its mitigating actions, which included: 1. Verify the completeness of the Registered Entities’ Protection System device listing by utilizing protection system electrical drawings and/or physical site inspections; 2. Test the identified relays and current transformers; 3. Place identification labels on the affected relay devices to clearly identify ownership and responsibility for maintenance and testing; 4. Review and update Protection System Maintenance and Testing procedures and processes; 5. Review and modify the Luminant Compliance and Tracking System (LCATS) protective system maintenance and testing activities to ensure timely notifications are distributed to appropriate responsible company personnel. This will provide automatic notifications to ensure maintenance and testing activities are performed in order to meet the required periodicity, and provide management review of testing activities and documentation; and 6. Train appropriate company personnel on updated procedures and processes. | 2011-11-16 | 2011-12-21 | Admits | Texas RE considered the compliance program to be a mitigating factor in penalty determination. Big Brown is a subsidiary of Luminant Holding Company LLC (LHC), a subsidiary of Energy Future Holdings Corp. Energy Future Holdings Corp. (EFH). EFH has a designated corporate compliance office with responsibility to develop, implement, enforce, and maintain the EFH Compliance Program. The compliance office is accountable to the Audit Committee of the EFH Board of Directors and reports to the Audit Committee regarding the administration of the Compliance Program and any proposed substantive changes to the Compliance Program. The Compliance Leadership Team is made up of the heads of Internal Audit, Corporate Security, Human Resources, Compliance, Employment Law and Legal, or their designee(s), and meet as frequently as necessary to coordinate respective activities under the Compliance Program.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Tradinghouse Power Company LLC (TPC) (TPC was removed from the NERC registry as a GO effective 1/1/2011) | NCR10220 | TRE201000274 | Settlement Agreement | On September 2, 2010, TPC submitted a Self-Report identifying a violation of PRC-005-1 R2. TPC , as a Generator Owner, failed to perform maintenance and testing on some of its protection system devices within the stated intervals required by its Protection System Maintenance and Testing Program (Program). Out of 29 protection system devices, eight (27.59% of total devices) devices comprising some relays and instrument transformers were completed outside the documented test intervals (three year periodicity). These eight protection system devices were not identified and included in TPC's Program. All of these relays and sets of current transformers are related to generator breaker failure protection in the switchyard which was common to both the generating units and the Transmission Owner until 2001, when the ownership of the switchyard devices was segregated. After ownership transfer, TPC did not consistently include the generator breaker failure and bus differential devices in its program which led to these devices not being identified. Prior to 2001, all these devices were maintained by the Transmission Owner. On December 31, 2010, Unit 2 of the Tradinghouse Steam Electric Station permanently retired from service. Unit 1 at Tradinghouse was retired in 2009. There are no other generating units at this plant site or assigned to this entity, therefore, TPC no longer has any generation assets and was removed from the NERC registry as a Generator Owner. Overall, current transformers and potential transformers were included as a protection category in the maintenance and testing program, only the specific devices mentioned in this violation were left out of the program. | PRC-005-1 | R2 | Lower | Moderate | The potential risk was considered a moderate risk but not a serious or substantial risk to the bulk power system. Most of the relays and associated CTs which were not timely tested are micro-processor based devices and self-monitored. NERC and industry maintenance standards recommend testing such devices anytime between five years and 12 years. TPC has three-year testing intervals. Moreover, all devices were properly maintained and tested prior to September 2001 by the transmission provider. | 1/31/2008 (date Tradinghouse registered with NERC Registry) | 12/31/2010 (the last date TPC's units were operational) | $18,000 (For TRE201000272, TRE201000273 and TRE201000274) | Self-Report | TPC submitted a Mitigation Plan on September 3, 2010 to Texas RE outlining its mitigating actions, which included: 1. Verify the completeness of the Registered Entities’ Protection System device listing by utilizing protection system electrical drawings and/or physical site inspections; 2. Test the identified relays and current transformers; 3. Place identification labels on the affected relay devices to clearly identify ownership and responsibility for maintenance and testing; 4. Review and update Protection System Maintenance and Testing procedures and processes; 5. Review and modify the Luminant Compliance and Tracking System (LCATS) protective system maintenance and testing activities to ensure timely notifications are distributed to appropriate responsible company personnel. This will provide automatic notifications to ensure maintenance and testing activities are performed in order to meet the required periodicity, and provide management review of testing activities and documentation; and 6. Train appropriate company personnel on updated procedures and processes. | 2011-11-16 | 2011-12-21 | Admits | Texas RE considered the compliance program to be a mitigating factor in penalty determination. TPC is a subsidiary of Luminant Holding Company LLC (LHC), a subsidiary of Energy Future Holdings Corp. Energy Future Holdings Corp. (EFH). EFH has a designated corporate compliance office with responsibility to develop, implement, enforce, and maintain the EFH Compliance Program. The compliance office is accountable to the Audit Committee of the EFH Board of Directors and reports to the Audit Committee regarding the administration of the Compliance Program and any proposed substantive changes to the Compliance Program. The Compliance Leadership Team is made up of the heads of Internal Audit, Corporate Security, Human Resources, Compliance, Employment Law and Legal, or their designee(s), and meet as frequently as necessary to coordinate respective activities under the Compliance Program.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | AES Alamitos (ALGS) | NCR05002 | WECC201102728 | Settlement Agreement | On December 8, 2010, WECC notified ALGS that it would be conducting an off-site compliance Audit. On February 18, 2011, ALGS submitted a Self-Report, stating that, as a Generator Owner, it was unable to produce evidence of testing and maintenance within defined intervals for all of its batteries subject to this Standard. During the Audit, WECC's Subject Matter Expert determined that ALGS had a documented Maintenance and Testing Program for its Protection System devices and sampled testing records for 29 devices. ALGS provided evidence of the date the batteries were last tested and maintained but was unable to demonstrate that the testing was performed within the defined intervals specified in its Program for one set of batteries comprised of three batteries. Based on the record and additional information obtained from ALGS, WECC enforcement determined that ALGS could not provide evidence of testing within the intervals defined in its program, in violation of this Standard. The scope of the violation was limited to one set of batteries, which account for less than 25% of ALGS's total batteries. | PRC-005-1 | R2.1 | High | Lower | WECC determined that this violation did not pose serious or substantial risk and posed a minimal risk to the reliability of the bulk power system because although ALGS failed to test its batteries within the specified intervals, it provided evidence that it tested the devices pursuant to its Plan for Protection Systems, including relays and DC circuitry. Also, ALGS was able to provide evidence of testing for the majority of its batteries subject to PRC-005-1. Further, WECC determined that in the event of a malfunction, ALGS's batteries are equipped with an alarm system designed to immediately alert personnel of any failure or defect. | 2007-06-18 | 2011-03-31 | 8700 | Self-Report | On March 4, 2011, ALGS submitted a Mitigation Plan and completed the following activities: (1) Assigned a Team Leader to oversee PRC-005-1 compliance and ensure maintenance and testing of its Protection System devices was appropriately documented; (2) Revised its Maintenance and Testing Procedures to include review and approval by the station manager; (3) Revised its Maintenance and Testing document forms; (4) Implemented the revised Maintenance and Testing procedures; and (5) Added an updated Preventative Maintenance work notification in the Systems Applications and Products (SAP) program. | 2011-03-31 | 2011-11-28 | Agrees and Stipulates to the Facts | WECC considered the following mitigating factors in determining the penalty amount: (1) ALGS took voluntary corrective actions to remediate this violation; (2) ALGS self-reported the violation; (3) ALGS's Internal Compliance Program was documented and disseminated throughout the operations staff; ALGS has ICP oversight staff, which is a supervised at a high level in the organization; ALGS has allocated sufficient resources to its ICP and the ICP has the support and participation of the senior management; ALGS reviews and modifies its ICP regularly and the ICP includes formal, internal self-auditing for compliance with the Reliability Standards on a periodic basis; the ICP includes disciplinary action for employees involved in violations of the Reliability Standards; (4) This is not a repeat violation; (5) ALGS was cooperative throughout the compliance process and completed all of WECC's compliance directives; and (6) WECC found no evidence that ALGS attempted to conceal the violation or that the violation was intentional. WECC determined that there were no aggravating factors in determining the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | City of Glendale (GLEN) | NCR05081 | WECC201102856 | Settlement Agreement | On June 30, 2011, GLEN submitted a Self-Report addressing a violation of the WECC Regional Reliability Standard IRO-STD-006-0, WR1. The purpose of this Standard is the mitigation of transmission overloads due to unscheduled line flow on Qualified Paths. Specifically, on May 11, 2011, GLEN's agent for real time trading and scheduling, ACES Power Marketing LLC (APM), notified GLEN of possible Unscheduled Flow (USF) violations which occurred on October 14, 2010, October 15, 2010, and June 5, 2010. The first instance, event 7617, occurred as a result of the trader failing to respond for one hour, which resulted in 2.2 MW of noncompliance. The second instance, event 7642, occurred when APM responded to a WebSAS alarm and curtailed tag 24096 by 4 MW, providing the necessary relief. Following this response, a purchase was made on tag 24130 which inadvertently pushed the line over its limit, resulting in 0.8 MW of noncompliance. APM attempted to adjust the tag back, which would have resulted in compliance, but WAPA-Lower Colorado (WALC) denied the adjustment due to late submission. The third instance, event 7311, occurred when APM failed to respond to a schedule and tag of 3 MW identified by WebSAS impacting path California-Oregon Intertie Path (COI) that should have been adjusted to 0 MW, resulting in 1.0 MW of noncompliance. At the time of the violation, this Standard applied to GLEN, in its function as a Load-Serving Entity. | IRO-STD-006-0 (Note that on July 1, 2011, this Standard was replaced by IRO-006-WECC-1. The new Standard applies to Balancing Authorities (BA) and Reliability Coordinators (RC). Because GLEN's registered functions do not apply to the new Standard's applicability criterion, the Standard no longer applies to GLEN.) | WR1 | N/A | N/A | WECC determined that this violation posed a minimal but not a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) the transmission operator continued to have the option of curtailing transactions that were directly scheduled on the Qualified Path to reduce loading in the event of an imminent overload; (2) the amount of flow increase on the path was less than 1% of the path ratings; and (3) the violation did not result in an overload of the transmission system. WECC determined that this violation is a "Level 1" noncompliance. | 10/14/2010, 10/15/2010, 6/5/2010 (the dates of the three separate events) | 10/14/2010, 10/15/2010, 6/5/2010 (the dates of the three separate events) | 500 | Self-Report | On July 1, 2011, GLEN submitted to WECC a Mitigation Plan (MIT-11-3882) to address the violation of IRO-STD-006-0, WR1. In accordance with the Mitigation Plan, GLEN has taken the following action: (1) reviewed the WebSAS utility training materials used by APM and received written confirmation from APM that all traders have received supplemental training; (2) GLEN's Energy Management group ran a monthly report using WebSAS to verify compliance with the USF standard from January 2010 to June 2011; (3) APM has taken steps to ensure that the audible and visual alarms associated with the WebSAS utility are checked by the trader each day and each shift to ensure they are in working order; and (4) GLEN's Internal Audit Department performed a review of APM’s desk procedures and activities, including a spot check of selected transactions. | 2011-07-27 | 2011-08-02 | Does Not Contest | WECC determined there were no aggravating factors in determining the penalty amount. GLEN has no prior violations of any Reliability Standards.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | Griffith Energy, LLC (GRGO) | NCR03052 | WECC201002858 | Settlement Agreement | On October 21, 2010, GRGO submitted a Self-Report stating that GRGO experienced a problem with its Steam Turbine Generator (STG) on October 12, 2010, and discovered that the Power System Stabilizer (PSS) control for the steam turbine was in an OFF position when it should have been in an ON position. GRGO's plant is comprised of one steam turbine and two combustion turbines. On March 23, 2010, the STG was powered down for a replacement of a bad communications card and then powered up and restored to normal operation. However, because GRGO was not aware that the default position was the OFF position, it did not turn it back ON, and the STG PSS system continued to operate in an OFF position. Based on the record, WECC determined that GRGO, as a Generator Operator, failed to ensure that the STG PSS control system was kept in service at all times in order to provide frequency support to the grid. | VAR-STD-002b-1 | WR1 | The sanctions for this regional standard are determined based on a level of non-compliance ranging from Level 1 to Level 4 | The sanctions for this regional standard are determined based on a level of non-compliance ranging from Level 1 to Level 4 | WECC determined that the violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because GRGO's two combustion turbines' PSSs were ON during the period of the violation, minimizing the need for GRGO's steam turbine to stabilize the generators. Although the STG PSS system was in the OFF position, the plant as a whole performed in an expected manner and was able to support grid frequency deviations per control design on two separate occasions. In addition, WECC determined that the size of the generator involved - 250 MW steam turbine generator, reduced the risk to the BPS. Also, GRGO investigated all generation data for the period of operation without the STG PSS in service and no abnormalities were noted. GRGO's Transmission Operator, the Western Area Power Administration, showed no abnormalities due to GRGO's STG PSS system being OFF. | 2010-03-23 | 2010-10-12 | 1000 | Self-Report | GRGO immediately restored the PSS to its normal ON operation position after discovering its status on October 12, 2010. According to its Mitigation Plan (MIT-10-3874), GRGO: 1) Conducted refresher training with all operations and management personnel on the PSS and VAR-STD-002b-1; 2) Committed to work with the steam turbine controls vendor to change PSS operational logic, if possible, so that the system defaults to "ON" position following a loss of power; 3) Updated the plant's distributed controls system to include alarm indication when PSS not in service; 4) Updated operator shift rounds to include a check of PSS operation. | 2011-01-28 | 2011-11-18 | Does Not Contest | WECC considered the following factors in determining the penalty amount: GRGO's violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS, the violation was self-reported, there were no aggravating factors in determining the penalty amount, and the violation did not pose an ongoing risk to the BPS.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102909 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing noncompliance with MOD-010-0 R1. According to the Self-Report, during an internal review of standards, NCPA found that, as a Generator Owner, it had not been submitting or checking all data from the regional coordinator Pacific Gas and Electric (PGAE) and had failed to provide complete equipment characteristics and system data and review of data as required. During the investigation, it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-010-0 | R1 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102910 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing noncompliance with MOD-010-0 R2. According to the Self-Report, during an internal review of standards, NCPA found that it, as a Generator Owner, failed to implement a formal process that ensures all data is reviewed for accuracy prior to being submitted to the area coordinator. Specifically, NCPA failed to jointly coordinate the development of the data requirements and reporting procedures with Pacific Gas and Electric (PGAE). NCPA's failure to follow a documented procedure for submitting data to PGAE resulted in data being submitted to PGAE prior to NCPA reviewing for accuracy. During the investigation it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-010-0 | R2 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102911 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing possible noncompliance with MOD-012-0 R1. According to the Self-Report, during an internal review of standards, NCPA found that it, as a Generator Owner, had not provided dynamic system modeling and simulation data to Pacific Gas and Electric (PGAE), the regional coordinator. During the investigation it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-012-0 | R1 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | Northern California Power Agency (NCPA) | NCR05278 | WECC201102912 | Settlement Agreement | On August 19, 2011, NCPA submitted a Self-Report addressing possible noncompliance with MOD-012-0 R2. According to the Self-Report, during an internal review of standards, NCPA found that it, as a Generator Owner, had not provided complete equipment characteristics and system data and review of data to Pacific Gas and Electric (PGAE), the regional coordinator, for use in the WECC system-wide model. During the investigation it was discovered that a procedure and process had not been developed or put in place that would ensure accountability and timely submittal and review of data to PGAE. | MOD-012-0 | R2 | Medium | Lower | WECC found that this violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because although NCPA did not review equipment characteristics and system data prior to submitting the data to PGAE, there had not been any changes to NCPA's system characteristics or load data that would have resulted in a change to its network model. Moreover, the purpose of MOD-010-0 and MOD-012-0 is to establish consistent data requirements, reporting procedures, and system models to be used in the analysis of the reliability of the Interconnected Transmission Systems. WECC relies on data from entities to support the design and operations of the western interconnected power system. The timely and accurate submittal of data is a key factor in preserving system reliability and affects significant economic decisions regarding system expansion and operation. In this case, NCPA's data was timely and accurate and had not changed since previous data submittals to PGAE. NCPA's failure to jointly coordinate reporting and data procedures with PGAE did not affect the reliability of the data submitted. For these reasons, WECC determined this violation posed a minimal risk to the reliability of the BPS. | 6/18/2007 (when the Standard became mandatory and enforceable) | 2011-11-23 | $1,000 (Settlement of WECC201102909, WECC201102910, WECC201102911, WECC201102912) | Self-Report | NCPA submitted a Mitigation Plan which outlined the following mitigation activities: 1) Work with area coordinator PGAE to determine all data requirements; 2) Develop a procedure and process to ensure that all required data is checked and sent to the area coordinator, and reviewed for accuracy prior to submitting data to WECC; and 3) Assign individuals or third party responsibility for following the procedure and process for data submittal to the area coordinator. The mitigation relates to both submittals to PGAE and from PGAE before it goes to WECC. | 2011-11-23 | 2011-12-21 | Does not contest | NCPA does not have a formal ICP documented with WECC, however it has a good compliance program with respect to its violation history. NCPA took voluntary corrective action to remediate these violations, NCPA self-reported these violations, NCPA was cooperative throughout the process, NCPA did not fail to complete any applicable compliance directives, and there was no evidence of any attempt by NCPA to conceal these violations. Further, NCPA did not have any aggravating factors. WECC did not give NCPA mitigating credit for the ICP.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901760 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD April 6, 2009 that BPA would no longer function as CKPD's TOP on and the notice was effective immediately. As a result of BPA's decision, CKPD had to register as a TOP and report itself as noncompliant with this NERC Standard. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD as a result of its TOP registration and the time of its registration, CKPD was unable to provide adequate and reliable telecommunications facilities for the exchange of interconnection and operating information, in violation of this Standard. | COM-001-1 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to provide adequate and reliable telecommunications facilities for the exchange of interconnection and operating information, the interim risk to the BPS was abated because the basic lines of communications (voice and data) with the Reliability Coordinator and BPA were still in place while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a Transmission Operator (TO), Purchasing-Selling Entity (PSE), Load-Serving Entity (LSE), Distribution Provider (DP), Generator Owner (GO) and Generator Operator (GOP). Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD identified telecommunication resources used to communicate with its TOPs and BA (BPA). CKPD communicates with the Reliability Coordinator (RC) through BPA. CKPD provided evidence of its completion in a document titled Telecommunications, Communications, and Coordination, dated July 31, 2009. | 2009-09-18 | 2009-12-18 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901761 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ( "BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP on and the notice was effective immediately. As a result of BPA's decision, CKPD had to register as a TOP and report itself as noncompliant with this Standard. In its Self-Report, CKPD stated that the requirements of the Standard were new and unexpected obligations for CKPD as a result of its TOP registration and the time of its registration, CKPD did not manage, alarm, test and/or actively monitor vital telecommunications facilities, in violation of this Standard. | COM-001-1 | R2 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to manage, alarm, test and/or actively monitor vital telecommunications facilities, the interim risk to the BPS was abated because the basic lines of communications (voice and data) with the RC and BPA were still in place, while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD developed procedures and guidance for alarming and testing its vital communications in its document titled Telecommunications, Communications, and Coordination, dated July 31, 2009. | 2009-09-18 | 2009-12-18 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901762 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. CKPD stated that the requirements of the Standard were new obligations for CKPD as a result of its TOP registration. WECC determined that at the time of its registration, CKPD failed to have written operating instructions and procedures to enable its continued operation during the loss of telecommunication facilities, in violation of this Standard. | COM-001-1 | R5 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to have written procedures in place to operate without such communication facilities, the risk to the BPS was abated because the basic lines of communications (voice and data) were in place, while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD developed a written plan to address system operation with loss of vital communications in its document titled Telecommunications, Communications, and Coordination, dated July 31, 2009. | 2009-09-18 | 2009-12-18 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901763 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for its non-compliance with this Standard. CKPD stated that Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. As a result of BPA's decision, at the time of its registration, CKPD failed to have communications (voice and data links) with the appropriate RCs, BAs and TOPs, in violation of this Standard. | COM-002-2 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to have communications (voice and data links) with the appropriate RCs, BAs and TOPs, the risk to the BPS was abated because the basic lines of communications (voice and data) with the RC and BPA were still in place, while CKPD completed its documentation to comply with the Standard. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided documentation of its voice and data links with its TOP and BA, set forth in a document titled Clark Public Utilities Telecommunications Facilities Adequacy and Reliability, dated July 31, 2009. | 2009-09-18 | 2009-12-15 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901790 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to develop, maintain, and implement a set of plans to mitigate operating emergencies, load shedding and system restoration, in violation of this Standard. | EOP-001-0 | R3 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. In addition, all of the requirements of this Standard were elements of emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements between the two entities would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions and incorporate them into its own plan. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the CKPD Emergency Operator Plans and Operator Controlled Manual Load Shedding Plan, dated January 26, 2010, that addressed insufficient generating capacity (at a level appropriate to a non-BA), for mitigating operating emergencies on the transmission system and for load shedding. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901791 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. At the time of its registration, CKPD had failed to have emergency plans to enable it to mitigate operating emergencies, including communications protocols and a list of controlling actions to resolve the emergency, in violation of this standard. | EOP-001-0 | R4 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were elements of emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions and incorporate them into its own plan. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided documentation of emergency plans that will enable it to mitigate operating emergencies. The CKPD Emergency Operator Plans and Operator Controlled Manual Load Shedding Plan, dated January 26, 2010, that addresses communications protocols, load reduction, tasks to be coordinated, and staffing levels. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901792 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to include the applicable elements in Attachment 1-EOP-001-0 when developing an emergency plan. | EOP-001-0 | R5 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were included as elements of emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements were sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions and incorporate them into its own plan. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the CKPD Emergency Operator Plans and Operator Manual Load Shedding Plan, dated January 26, 2010, that includes an “Additional Emergency Condition Considerations” section and also includes Attachment 1-EOP-001-0. The plan adopted the elements of Attachment 1 as a list of additional elements to be considered as potential responses during any emergency condition. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901793 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to review and update its emergency plan, and to provide a copy of its updated emergency plans to its RC and neighboring TOPs and BAs, in violation of this Standard. | EOP-001-0 | R6 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were included as elements of the emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that the plans developed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions, incorporate them into its own plan, and share the results with appropriate BAs and TOPs. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its Emergency Operator Plans (1/26/10), Operator Manual Load Shedding Plan (1/26/10), and System Restoration Plan(1/1/10). These emergency plans include provisions for annual reviews and updates, if appropriate. CKPD stated it will annually review and update each emergency plan and provide a copy of its updated emergency plans to its RC, TOP and BA. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901794 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to coordinate its emergency plans with neighboring TOPs and BAs as appropriate, in violation of this Standard. | EOP-001-0 | R7 | Medium | Lower | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. All of the requirements of this Standard were included as elements of the emergency operations provided for in CKPD's transmission service agreement, applicable Network Operating Agreement, and Technical Requirements for Interconnection with BPA. WECC determined that plans developed and coordinated by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) and contained in this set of agreements would be sufficient to ensure adequate mitigation of any operating emergencies during the short period of time required for CKPD to restate the agreements' provisions, incorporate them into its own plan, and coordinate the results with appropriate BAs and TOPs. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-26 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its Emergency Operator Plans and Operator Manual Load Shedding Plan, dated January 26, 2010, to show that it has coordinated with its neighboring BAs and TOPs. | 2010-01-26 | 2010-04-16 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901684 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD failed to have a restoration plan to reestablish its electric system in a stable and orderly manner in the event of a partial or total shutdown of its system, including necessary operating instructions and procedures to cover emergency conditions, and the loss of vital telecommunications channels, in violation of this Standard. | EOP-005-1 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WE#CC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901685 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD arising from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to develop restoration plans with a priority of restoring the integrity of the Interconnection, in violation of this Standard. | EOP-005-1 | R3 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Also, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center and CKPD could call on BPA for emergency response and system restoration in the interim if an emergency event occurred. Further, WECC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. The restoration plan includes a priority for restoring the integrity of the Interconnection. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901686 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to coordinate its restoration plans with the Generator Owners and Balancing Authorities within its area, its Reliability Coordinator, and neighboring Transmission Operators and Balancing Authorities, in violation of this Standard. | EOP-005-1 | R4 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of this Standard and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WECC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. The restoration plan includes a procedure for coordination with BPA and PacifiCorp West. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901687 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to periodically test its telecommunication facilities needed to implement the restoration plan, in violation of this Standard. | EOP-005-1 | R5 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. In addition, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WECC determined that the restoration of CKPD's facilities is not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-02-24 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided its System Restoration Plan, dated January 1, 2010, and associated Network Operating Agreement that is included as Exhibit C to the Service Agreement for Network Integration Transmission Service between CKPD and BPA. CKPD confirmed that its Plan requires that the telecommunication facilities are tested annually, and that CKPD regularly tests these telecommunications facilities on a monthly basis. | 2010-02-24 | 2010-03-08 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901688 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to train its operating personnel in the implementation of the restoration plan, in violation of this Standard. | EOP-005-1 | R6 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, WECC determined that the restoration of CKPD's facilities was not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-03-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC copies of 1) the System Restoration Plan, dated January 1, 2010, 2) the log sheet describing the March 27, 2010 test of the Plan, and 3) the training log sheet showing that all of CKPD’s Service Dispatchers had received initial training for the Plan. | 2010-03-27 | 2010-04-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901689 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD failed to verify the restoration procedure by actual testing or by simulation, in violation of this Standard. | EOP-005-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration, which met the requirements of EOP-005 and would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim. Further, restoration of CKPD's facilities is not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-03-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC a copy of its System Restoration Plan and evidence of testing dated March 27, 2010, to assure that the plan could be followed. The test included contacting neighboring entities. CKPD's restoration plan calls for CKPD to follow direction from BPA. | 2010-03-27 | 2010-04-06 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901683 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to have a plan to continue reliability operations in the event its control center became inoperable, in violation of this Standard. | EOP-008-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. BPA's control center is located in CKPD's service territory and in close proximity to CKPD's dispatch center. CKPD could call on BPA for emergency response and system restoration in the interim in the event of control center inoperability. Further, restoration of CKPD's facilities is not critical to the reliability of BPA's system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-03-25 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD completed its Loss of Control Center Functionality Plan on January 1, 2010. The plan states that CKPD will deploy personnel to critical facilities and will relocate its dispatchers to one of three locations and establish communication via cell phones with remote substations. On March 20, 2010 CKPD tested its plan and on March 23, 2010 trained its dispatchers on the implementation of its plan. | 2010-03-25 | 2010-04-01 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901798 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of the registration, CKPD had failed to provide its operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the BPS, in violation of this Standard. | PER-001-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD’s documentation failed to provide its operating personnel with the responsibility and authority to take actions, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration that would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. CKPD mitigated this violation in four months, as it was necessary to renegotiate union contracts in order to get the appropriate references to NERC requirements in the dispatch personnel job descriptions. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD submitted to WECC documentation of its System Operations Manual and job descriptions (as of 9/18/2009) that it provides operating personnel with the responsibility and authority to implement real-time actions to ensure the stable and reliable operation of the bulk electric system. | 2009-09-18 | 2010-01-22 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901745 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of the registration, CKPD was not staffed with adequately trained operating personnel, in violation of this Standard. | PER-002-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD's operations staff was not fully trained at the time it was registered on May 8, 2009, CKPD had begun its training program on April 14, 2009, to abate the risk to reliability. At the time of its registration as a TOP, CKPD had already started training its operators. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-21 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC its Clark Public Utilities System Operator Training Program, which served as a proof of training for CKPD's system operators. CKPD included training records with completion evidence showing that each dispatcher had accumulated dispatch related training of at least five days: specifically, the applicable CKPD operating personnel each had received between 65-129 hours of related training. In order to allow each employee to accumulate sufficient training hours, CKPD began this training on 4/14/2009 before the standard was applicable to CKPD. CKPD completed the training of its six operators on 9/21/2009. | 2009-09-21 | 2009-12-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901746 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD did not have a training program with training objectives and did not document initial and continuing training that addressed competencies and knowledge. The training staff was not identified and their competencies in both knowledge of system operations and instructional capabilities was not identified, in violation of this Standard. | PER-002-0 | R3 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD's existing program did not meet the criteria of this Standard, CKPD did have a training program in place and commenced training prior to its registration date. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-21 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC its Clark Public Utilities System Operator Training Program, which met the requirements of R3. CKPD included training records with completion evidence showing that each dispatcher had accumulated dispatch related training of at least five days: specifically, the applicable CKPD operating personnel each had received between 65-129 hours of related training. In order to allow each employee to accumulate sufficient training hours, CKPD began this training on 4/14/2009, before the standard was applicable to CKPD. CKPD completed the training of its six operators on 9/21/2009. | 2009-09-21 | 2009-12-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901747 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to provide its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel, in violation of this Standard. | PER-002-0 | R4 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD did not provide its operating personnel with the required drills and simulations to satisfy the requirements of the Standard, CKPD had a training program for operators that included simulations of system emergencies. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-21 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided WECC with its System Operator Training Program, dated September 16, 2009, to show that it provides its operating personnel at least five days per year of training and drills using realistic simulations of system emergencies, in addition to other training required to maintain qualified operating personnel. CKPD included training records with completion evidence showing that each dispatcher had accumulated dispatch related training of at least five days: specifically, the applicable CKPD operating personnel each had received between 65-129 hours of related training. In order to allow each employee to accumulate sufficient training hours, CKPD began this training on April 14, 2009, before the standard was applicable to CKPD. | 2009-09-21 | 2009-12-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901797 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to staff all operating positions that had the primary responsibility, either directly or through communications with others, with personnel that were NERC-certified for the applicable functions for the real-time operation of the interconnected BPS, and positions directly responsible for complying with NERC standards, in violation of this Standard. | PER-003-0 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD lacked NERC-certified operating personnel at the time of its registration as a TOP, its personnel did have experience and training to operate the CKPD system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-28 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided an email verifying completion of NERC Certification for all applicable positions as of 1/28/2010. | 2010-01-28 | 2010-02-26 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901653 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD failed to have documentation showing that its system operators had the responsibility and clear decision-making authority to take whatever actions were necessary to protect the BPS, in violation of this Standard. | TOP-001-1 | R1 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD lacks the appropriate documentation of authority to alleviate operating emergencies, BPA (CKPD's BA and the former TOP for CKPD's facilities) maintained plans and facilities for system restoration that would continue to be adequate for restoration during the short period of time until CKPD's plans were completed. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD submitted to WECC an operating procedure on 9/18/2009 titled CKPD - Reliability Responsibilities and Authorities (7/31/09) that states the operator has the authority and responsibility to take action, up to and including dropping load to respond to emergency conditions. | 2009-09-18 | 2009-11-04 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901692 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to: maintain a set of current plans designed to evaluate options, set procedures for reliable operation through a reasonable future time period and be responsible for using available personnel and system equipment to implement these plans to ensure that interconnected system reliability will be maintained, in violation of this Standard. | TOP-002-2 | R1 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Development of plans to evaluate options and set procedures for reliable operation through a reasonable future time period are long-term planning activities that are normally performed on an annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BPS and CKPD system reliability during the short period of time until CKPD's planning function became operational. Further, CKPD's violation was primarily documentation, i.e., CKPD's existing documentation needed to be organized, and planning guidelines for expected normal operations needed to be extended into the future. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided on 9/18/2009 its TOP-002-2 Clark Normal Operations Plan through 2010. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901693 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD as a result of BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to ensure its operating personnel participated in the system planning and design study processes, so that these studies contained the operating personnel perspective and system operating personnel were aware of the planning purpose, in violation of this Standard. | TOP-002-2 | R2 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. System planning and design study functions are long-term activities that are normally performed on an annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BPS and CKPD system reliability during the short period of time until CKPD's planning function became operational and incorporated the experience of its operating personnel. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC on 9/18/2009 its TOP-002-2 Clark Normal Operations Plan through 2010. Operating personnel participated in the implementation of this plan. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901695 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to coordinate (where confidentiality agreements allowed) its current-day, next-day, and seasonal planning and operations with neighboring Balancing Authorities and Transmission Operators and with its Reliability Coordinator, so that normal Interconnection operation will proceed in an orderly and consistent manner. | TOP-002-2 | R4 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Current-day, next-day, and seasonal planning are operations planning activities that are normally performed on a long-term or annual basis. Thus, the coordination for the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place to ensure that normal Interconnection operations would proceed in an orderly and consistent manner during the short period of time until CKPD's planning function became operational. The larger encompassing BA, which previously coordinated these activities, would be fully aware of CKPD planning and operations. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided on 9/18/2009 its TOP-002-2 Clark Normal Operations Plan, and an email showing proof of coordination with BPA and PacifiCorp West. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901696 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to plan to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns. | TOP-002-2 | R5 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. System planning to meet scheduled system configuration, generation dispatch, interchange scheduling and demand patterns is an operational planning activity that is normally performed on a long-term or annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BES and CKPD system reliability during the short period of time until CKPD's planning function became operational. Further, CKPD's violation was primarily documentation, i.e., CKPD's existing documentation needed to be organized and expanded to cover additional requirements. Also, CKPD has no interchange schedules. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD included information on expected demand (LSE) and expected generator operations (GOP). A copy of the results were provided to BPA as the BA and the Transmission Service Provider for CKPD. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901697 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to meet unscheduled changes in system configuration and generation dispatch (at a minimum N-1 Contingency planning) in accordance with NERC, Regional Reliability Organization, subregional, and local reliability requirements. | TOP-002-2 | R6 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. System planning to meet the conditions listed in this requirement are operational planning activities that are normally performed on a long-term or annual basis. Thus, the most recent plans completed by BPA (CKPD's surrounding BA and the former TOP for CKPD's facilities) were in place for ensuring BES and CKPD system reliability during the short period of time until CKPD's planning function became operational and the perspective of its operating personnel incorporated. Further, CKPD's violation was primarily documentation, i.e. CKPD's existing documentation needed to be better organized to demonstrate compliance with reliability requirements. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2009-09-18 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided on 9/18/2009 study results showing the scheduled system configuration, generation dispatch, and demand patterns (CKPD is not a BA and has no interchange schedules). CKPD indicated that this scheduled system configuration is expected to be used during seasonal normal conditions, seasonal extreme conditions and seasonal N-1 conditions. | 2009-09-18 | 2009-11-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC201002022 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration, CKPD had failed to monitor system frequency, in violation of this Standard. | TOP-006-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. CKPD is a small system composed of 69 kV and 115 kV lines, completely surrounded by BPA. BPA indicated in a letter dated April 6, 2009 that issues affecting CKPD's system would have minimal impact on the reliability of the BPA system. WECC determined that due to its relatively small impact with respect to the more robust surrounding system, the fact that it is not a BA, and the fact that it has no interchange schedules, failure to monitor system frequency would have little effect on its operations or on the reliability of the interconnected system. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-04-28 | 2009-07-28 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided evidence to WECC that it was monitoring system frequency, and that system frequency was added to the applicable display screens in the dispatch center. | 2009-07-28 | 2010-09-15 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901779 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD had not specified criteria that exempts generators from compliance with the requirements defined in Requirement 4, and Requirement 6.1, in violation of this Standard. | VAR-001-1 | R3 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to specify a criteria for exempting generators from having to maintain the voltage or reactive schedule on the CKPD transmission system, CKPD had only one generator connected to its system, and that generator was not exempt. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the following documentation on 1/29/2010: Clark Public Utilities – Voltage and Reactive Power Plan (dated 1/1/2010, Ver. No. 1), and Appendix A - applicable and exempt generators. CKPD maintains a list of exempt generators, and has procedures to notify owners and operators of their status. CKPD has no exempt generators connected to the transmission system. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901780 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD had failed to specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. CKPD did not provide the voltage or Reactive Power schedule to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage), in violation of this Standard. Also, the current voltage schedule was established by BPA, not CKPD. | VAR-001-1 | R4 | Lower | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to specify a voltage or reactive power schedule for its River Road generating facility, BPA (the surrounding BA and former TOP for CKPD's facilities) did establish a voltage schedule that is telemetered to the one generator connected to CKPD's system, River Road, in real-time. BPA continued to require the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided evidence on 1/29/2010 that it specified a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator. CKPD provided the voltage or Reactive Power schedule to the associated Generator Operator and directed the Generator Operator to comply with the schedule in automatic voltage control mode (AVR in service and controlling voltage). | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901781 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD did not know the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers (PSS), in violation of this Standard. The status was known by BPA, not CKPD. | VAR-001-1 | R6 | Medium | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD failed to know the status of the AVR and PSS at the River Road generating facility, BPA did establish a voltage schedule that is telemetered to River Road in real-time. The voltage at River Road and the status of the AVR and PSS are telemetered back to BPA. The issue with this violation is not that system operators did not know the status of the River Road AVR and PSS, but rather that the status must be known by the current Transmission Operator, CKPD. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided to WECC on 1/29/2010 its Voltage and Reactive Power Monitoring and Controlling Procedures, dated 1/2/2010. This evidence showed that CKPD knows the status of all transmission Reactive Power resources, including the status of voltage regulators and power system stabilizers. Under the Procedure, if CKPD is notified of the loss of an automatic voltage regulator control, CKPD will direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901782 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD was not able to operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow, in violation of this Standard. However, those functions were being performed by BPA. | VAR-001-1 | R7 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD was not able to independently direct the operation of the AVR and PSS at the River Road generating facility, BPA had established a voltage schedule that is telemetered to River Road in real-time. The voltage at River Road and the status of the AVR and PSS are telemetered back to BPA. The interconnection voltage of the River Road generating facility is at the discretion of BPA, which monitors and regulates voltage in the area. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the following documents on 1/29/2010: the Clark Public Utilities – Voltage and Reactive Power Plan (dated 1/1/2010, Ver. No. 1), and a letter from BPA to CKPD, dated June 25, 2009. The evidence showed that CKPD will operate or direct the operation of devices necessary to regulate transmission voltage and reactive flow. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Public Utility District No. 1 of Clark County (CKPD) | NCR05334 | WECC200901783 | Settlement Agreement | On April 28, 2009, CKPD, in anticipation of its NERC registration as a Transmission Operator (TOP), CKPD filed a Self-Report for non-compliance with this Standard. CKPD stated that the Bonneville Power Administration ("BPA" was CKPD's Transmission Operator) informed CKPD on April 6, 2009 that BPA would no longer function as CKPD's TOP and the notice was effective immediately. In its Self-Report, CKPD stated that the requirements of the Standard were new obligations for CKPD resulting from BPA's decision and CKPD's TOP registration. WECC determined that at the time of its registration with NERC, CKPD had failed to operate or direct the operation of capacitive and inductive reactive resources within its area – including reactive generation scheduling; transmission line and reactive resource switching; and, if necessary, load shedding – to maintain system and Interconnection voltages within established limits. Those functions were being performed by BPA. | VAR-001-1 | R8 | High | Severe | WECC determined this violation did not pose a serious or substantial risk to the reliability of the BPS. WECC took into consideration that CKPD was assuming a new TOP function, which was a one time registration issue unlikely to arise again. Although CKPD was not able to operate or direct the operation of capacitive and inductive reactive resources within its area to maintain system and Interconnection voltages within established limits, BPA controls to the voltages contained in its Voltage Schedules document at the interconnections with CKPD. BPA maintains the reactive flow at these stations by maintaining the voltage schedule at these stations, thus maintaining system and Interconnection voltages within established limits. In addition, at the time of its registration for the TOP function, CKPD was satisfying the requirements for its other functions as a TO, PSE, LSE, DP, GO and GOP. Prior to the Self-Report, BPA conducted a technical assessment of the entity’s electrical systems to determine whether BPA would offer to assume the TOP role. BPA's assessment determined that it was not performing the TOP function for the facility and that BPA did not need control for system reliability. In addition, BPA found that the entity was staffed with competent crews, had developed significant maintenance capabilities and operated a 24-hour dispatch center. CKPD resides in BPA's Balancing Authority (BA) footprint. As a BA, BPA has the responsibility to ensure reliability within its BA footprint. During the period during which CKPD was working towards TOP certification, BPA continued to coordinate outage plans, day-to-day routine realtime communications and notifications and any unplanned work forced by equipment failures, storms etc. BPA provided assurance to the Reliability Coordinator (RC) that it would continue to keep the RC apprised of planned and emergency outages of the utilities' transmission facilities during the interim period. This is normal operating procedure for all BAs. Through the normal reliability operating procedures, safeguards and coordination, BPA does not believe that any additional risk to the BPS was experienced as the entity completing its TOP certification. BPA offered and provided other assistance to the entity to ensure it had all the BPA resources and experience in helping it obtain full TOP certification. BPA responded very favorably during its neighboring BA and TOP questionnaires as BPA was requested during the entity’s TOP certification process. | 2009-05-08 | 2010-01-27 | $0 (Settlement of WECC200901760, WECC200901761, WECC200901762, WECC200901763, WECC200901790, WECC200901791, WECC200901792, WECC200901793, WECC200901794, WECC200901684, WECC200901685, WECC200901686, WECC200901687, WECC200901688, WECC200901689, WECC200901683, WECC200901798, WECC200901745, WECC200901746, WECC200901747, WECC200901797, WECC200901653, WECC200901692, WECC200901693, WECC200901695, WECC200901696, WECC200901697, WECC201002022, WECC200901779, WECC200901780, WECC200901781, WECC200901782, and WECC200901783) | Self-Report | To mitigate this violation, CKPD provided the following documents on 1/29/2010: the Clark Public Utilities – Voltage and Reactive Power Plan (dated 1/1/2010, Ver. No. 1), and a letter from BPA to CKPD, dated 6/25/2009. The evidence showed that CKPD will operate or direct the operation of capacitive and inductive reactive resources within its area to maintain system and Interconnection voltages within established limits. | 2010-01-27 | 2010-02-11 | Neither Admits nor Denies | WECC utilized its discretion to assess a zero dollar penalty for these violations due to the extenuating circumstances surrounding these violations. Specifically, on April 6, 2009, Bonneville Power Administration (BPA) unexpectedly notified CKPD that BPA would no longer be acting as the Transmission Operator (TOP) for CKPD. This notice was effective immediately. Consequently, CKPD was immediately responsible for registration and compliance with all applicable TOP standards. WECC also considered the following mitigating factors in determining the penalty amount: (1) CKPD self-reported in a timely manner; (2) Mitigation plans were promptly submitted to correct non-compliance; (3) Mitigation plans were successfully completed on time; (4) The violations did not pose serious or substantial risk to the reliability of the BPS; (5) The violations did not constitute a repeat violation of the applicable Reliability Standard; and (6) CKPD did not contest the violations.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Navopache Electric Cooperative, Inc. (NPEC) | NCR05260 | WECC201002041 | Settlement Agreement | On June 17, 2010, WECC conducted an off-site Compliance Audit of NPEC, as a Distribution Provider, and examined NPEC’s compliance with PRC-005-1 from June 17, 2007 to June 17, 2010. WECC determined that NPEC owns and operates a transmission Protection System that affects the reliability of the bulk power system (BPS). WECC concluded that in addition to its distribution systems, NPEC also owns and operates the Coronado Substation in St. John, Arizona, which includes a 500 kV-69 kV transformer and associated over-current and differential relaying and high-side protection systems. WECC determined that a potential failure of the high-side protection systems would cause an outage of the Sugarloaf 500 kV line and impact the BPS. WECC examined NPEC’s Protection System maintenance and testing program and concluded that it did not include maintenance and testing intervals for its voltage and current sensing devices, and that its maintenance and testing program failed to address DC circuitry, in violation of PRC-005-1 R1.1. | PRC-005-1 | R1 | High | Severe | WECC determined that the violations posed minimal risk and did not pose a serious or substantial risk to the reliability of the BPS because NPEC and the Salt River Project (SRP) have duplicative protective systems. SRP’s system has its own breakers, designed to prevent an outage beyond the 500 kV line. SRP’s breakers reduced the reliability risk to the BPS posed by a potential failure of NPEC’s transmission protection devices. | 2007-06-18 | 2011-02-28 | $40,000 (for WECC201002041, WECC201002042) | Compliance Audit | NPEC Revised its maintenance and testing program to include voltage and current sensing devices and DC circuitry. | 2011-02-28 | 2011-06-13 | Agrees and Stipulates to the Facts | A Settlement Agreement covering violations of PRC -005-1 R1 and R2 and PRC-008-0 R1 and R2 for NPEC (NOC-514) was approved by the BOTCC on May 14, 2010 and filed with FERC under NP10-160-000 on September 13, 2010. October 14, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although this is NPEC’s second violation, WECC Enforcement determined that a full penalty aggravation was not warranted with respect to R1. In the course of verifying completion of NPEC’s Mitigation Plan for the prior violation of PRC -005-1 R1, WECC erred in determining that NPEC’s Maintenance and Testing Program contained all of the elements required by the Standard. In fact, the Maintenance and Testing Program was still deficient because it did not include all Protection System equipment or maintenance and testing intervals, as required by R1. WECC acknowledged the error and that it could have provided a more rigorous review of the Maintenance and Testing Program when verifying completion of the Mitigation Plan related to the first violation of PRC-005-1 R1. Further, WECC considered NPEC’s repeat violation of PRC -005-1 R2 as an aggravating factor in its final penalty determination. WECC did not review NPEC’s Internal Compliance Program and did not give NPEC a mitigating credit for having a Compliance Program.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Navopache Electric Cooperative, Inc. (NPEC) | NCR05260 | WECC201002042 | Settlement Agreement | On June 17, 2010, WECC conducted an off-site Compliance Audit of NPEC, as a Distribution Provider, and examined NPEC’s compliance with PRC-005-1 from June 17, 2007 to June 17, 2010. WECC determined that NPEC owns and operates a transmission Protection System that affects the reliability of the bulk power system (BPS). WECC concluded that in addition to its distribution systems, NPEC also owns and operates the Coronado Substation in St. John, Arizona, which includes a 500 kV-69 kV transformer and associated over-current and differential relaying and high-side protection systems. WECC determined that a potential failure of the high-side protection systems would cause an outage of the Sugarloaf 500 kV line and impact the BPS. On the basis of the Compliance Audit and subsequent requests for information, WECC also concluded that NPEC could not provide evidence of testing of its DC circuitry and voltage/current sensing devices, and evidence of the date these devices were last maintained and tested. Therefore, WECC determined that NPEC also violated PRC-005-1 R2. | PRC-005-1 | R2 | High | Severe | WECC determined that the violations posed minimal risk and did not pose a serious or substantial risk to the reliability of the BPS because NPEC and the Salt River Project (SRP) have duplicative protective systems. SRP’s system has its own breakers, designed to prevent an outage beyond the 500 kV line. SRP’s breakers reduced the reliability risk to the BPS posed by a potential failure of NPEC’s transmission protection devices. | 2007-06-18 | 2011-07-18 | $40,000 (for WECC201002041, WECC201002042) | Compliance Audit | NPEC completed the required maintenance and testing and committed to have regular maintenance schedules as defined in its Protection System maintenance and testing program. | 2011-07-18 | 2011-11-16 | Agrees and Stipulates to the Facts | A Settlement Agreement covering violations of PRC -005-1 R1 and R2 and PRC-008-0 R1 and R2 for NPEC (NOC-514) was approved by the BOTCC on May 14, 2010 and filed with FERC under NP10-160-000 on September 13, 2010. October 14, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. Although this is NPEC’s second violation, WECC Enforcement determined that a full penalty aggravation was not warranted with respect to R1. In the course of verifying completion of NPEC’s Mitigation Plan for the prior violation of PRC -005-1 R1, WECC erred in determining that NPEC’s Maintenance and Testing Program contained all of the elements required by the Standard. In fact, the Maintenance and Testing Program was still deficient because it did not include all Protection System equipment or maintenance and testing intervals, as required by R1. WECC acknowledged the error and that it could have provided a more rigorous review of the Maintenance and Testing Program when verifying completion of the Mitigation Plan related to the first violation of PRC-005-1 R1. Further, WECC considered NPEC’s repeat violation of PRC -005-1 R2 as an aggravating factor in its final penalty determination. WECC did not review NPEC’s Internal Compliance Program and did not give NPEC a mitigating credit for having a Compliance Program.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Nevada Power Company (NEVP) | NCR05261 | WECC201102422 | Notice of Confirmed Violation | From March 14, 2011 to March 25, 2011, WECC conducted an on-site compliance audit of NEVP (Audit). During and prior to the Audit, the Audit Team reviewed NEVP’s Periodic Data Submittals related to its Power System Stabilizer (PSS) reports. On its Fourth Quarter 2008 Periodic Data Submittal, NEVP indicated it had a PSS outage from December 12, 2008 through December 15, 2008. The Audit Team conducted an interview with NEVP staff to discuss the circumstances and details associated with the December 2008 PSS outage. The Audit Team determined NEVP's Clark Station Unit #10 generator (Clark Unit #10) was in service when the PSS was out of service. The Audit Team noted that the PSS did not appropriately engage when NEVP brought Clark Unit #10 online and that NEVP was not aware of the PSS misoperation until NEVP ran an incident tracking report and determined the PSS was not in operation. NEVP clarified that failure of the PSS to engage upon start-up resulted in the unit operating for approximately 60.5 hours without the PSS in service. Similarly, NEVP discovered this issue approximately 60.5 hours after the unit start-up. Therefore, by the time NEVP, as a Generator Operator, was aware of the change in status of the PSS, the thirty-minute window to notify the Transmission Operator had elapsed. However, NEVP did notify the Transmission Operator upon discovering the change in status. | VAR-002-1a | R3 | Medium | Lower | WECC determined that the violation posed a minimal risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the PSS remained in service on the remaining units representing 97% of the NEVP system, which would protect the NEVP system and the BPS. In addition, the duration of the violation was limited to only 60.5 hours from December 12, 2008 to December 15, 2008. Clark Unit #10 is a steam turbine generator with a total capacity of approximately 85 MW fed by 2 combustion gas turbines. Together the three units make up a combined cycle block with approximately 253 MW of total generating capacity. The total generating capacity at the Clark Station generating facility is approximately 510 MW. NEVP’s total generating capacity is approximately 2,900 MW. Therefore, the violation is limited to a generating unit that represents 3% of the generation available to NEVP and the Transmission Operator. Further, the PSS remained in service for all other NEVP units when the Clark Unit #10 PSS was offline, therefore if Clark Unit #10 started to swing, the PSS on the remaining units (representing 97% of the NEVP system) would protect the NEVP system and the BPS. For these reasons, WECC determined this violation posed minimal risk to the reliability of the BPS. | 12/12/2008 (when the PSS outage began) | 12/15/2008 (when the PSS was restored) | 2000 | Compliance Audit / Periodic Data Submittal | NEVP immediately placed the PSS back in service once it was determined to be offline on December 15, 2008. NEVP then completed a root cause analysis to determine the break down in procedure and implemented the following actions to prevent this issue from recurring in the future: 1) installed relaying and connected the AVR and PSS to the Ovation software; 2) tested and installed new alarm logic to notify when PSS is out of service; 3) retrained all operators; 4) implemented new checklists for operators and shift supervisors; and 5) addressed personnel performance issues through corporate disciplinary actions. | 2009-01-16 | 2011-11-03 | Does Not Contest | WECC considered NEVP’s internal compliance program (ICP) as a mitigating factor. WECC found that: (1) NEVP has a fully documented ICP that has been reviewed and approved by the General Counsel who also serves as its Chief Compliance Officer; (2) NEVP’s oversight position is identified and staffed, and is supervised at a high level within the company; (3) the ICP oversight position has direct access to the CEO and Board of Directors; (4) NEVP operates and manages the ICP independently from personnel responsible for compliance with the Reliability Standards; (5) the ICP has sufficient staff and an adequate budget; (6) the ICP has NEVP senior management support and participation; and (7) NEVP’s ICP has a semi-annual or shorter review cycle.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Puget Sound Energy, Inc. (PSE) | NCR05344 | WECC201102620 | Notice of Confirmed Violation | On January 25, 2011, PSE, as a Generator Operator, self-reported VAR-002-1.1b R3 to WECC. At 1530 PPT on January 9, 2011, PSE's Mint Farm generating station (Mint Farm) control room operator indentified that the steam turbine Power System Stabilizer (PSS) had not been in operation for approximately 9.5 hours. Once the condition was identified, the PSS was turned on. However, the plant did not notify the Transmission Operator, Bonneville Power Administration (BPA), of the change in status to the PSS within the required 30 minutes. The Transmission Operator was notified the following morning once it was discovered that the notification had not occurred. A root cause analysis indentified operator error as the primary root cause since the PSS is alarmed on the control system human-machine interface (HMI). Standard operating procedures detail the proper plant startup steps for PSS and the plant dispatch protocol include notifying the Transmission Operator of changes to automatic voltage regulator (AVR) and PSS status. A subsequent assessment of past PSS PI application data at Mint Farm uncovered a similar event with the steam turbine PSS on August 22, 2010. On that occasion, the PSS was off for 53 minutes. The operator did not notify the Transmission Operator of the change in status once the PSS was reactivated. This was the same operator from the January 9, 2011 event and the root cause was also operator error for the reasons outlined above. Given the finding of a second issue at Mint Farm in the PI application data, PSE reviewed available PI data for its remaining units equipped with PSS. This analysis revealed four unreported instances of PSS outages on the combustion gas turbine at PSE's Goldendale generating station (Goldendale) on August 3, 2010 (73 hours), August 6, 2010 (4 hours), November 5, 2010 (3 hours) and December 27, 2010 (4.5 hours). PSE investigated an additional PSS outage in January 2010. In each instance, it appears the PSS failed to activate after the unit tripped offline. On February 17, 2011, plant personnel verbally confirmed that they had no record of notifying the Transmission Operator about the change in status to the PSS when it was reactivated on each of those occasions. On the August 6, 2010 incident, the site operator observed the PSS outage and reported it to the control room operator. The control room operator activated the PSS and noted it in the plant log. Although PSS status for Goldendale is transmitted real-time to BPA via ICCP (Inter-Control Communications Protocol), BPA does not actively monitor PSS status for the plant. The analysis has identified that the primary cause of the Goldendale incidents were PSE's operators being unaware of the requirement to notify the Transmission Operator of changes to the PSS status within 30 minutes. WECC determined that PSE, as the Generator Operator, had more than five, but less than ten incidents of failing to notify its Transmission Operator, as required by VAR-002-1.1b R3.2. | VAR-002-1.1b | R3 | Medium | High | WECC determined the violation posed a minimal risk and not a serious or substantial risk to the bulk power system (BPS). PSE was not aware of any impact to the BPS because of the PSS being out of service at either facility. All but one of the outages were in short duration. In addition, the PSS for the other turbine was activated (combustion turbine PSS at Mint Farm, steam turbine PSS at Goldendale), which would have helped with the system damping if needed. The Transmission Operator confirmed that there were no issues on the transmission lines for the Mint Farm January 9, 2011 event. For the remaining dates, BPA did not make PSE aware of any impact at the time of those past events. | 8/3/2010 (Date of first instance) | 1/10/2011 (When BPA was notified) | 10900 | Self-Report | 1) For the 1/9/2011 Mint Farm incident, PSE notified the Transmission Operator upon discovery that the Transmission Operator was not notified. (Completed 1/10/2011) 2) PSE reviewed the proper procedures with the control room operators at Mint Farm for notifying its Transmission Operator within 30 minutes of AVR or PSS change in status. (Completed 1/14/2011) 3) PSE reviewed the Mint Farm communications protocol and operating procedures for clarity and revised the procedures and protocols as needed to clarify the notification process descriptions. (Completed 2/18/2011) 4) PSE assessed past PI application data for other possible PSS outages at Mint Farm. (Completed 2/11/2011) 5) PSE assessed available 2010 - 2011 PI application data for the remainder of PSE units equipped with PSS. For any identified PSS outages, PSE evaluated records to determine if the Transmission Operator was notified when PSS status was changed. (Completed 2/17/2011) 6) PSE notified all its plant managers and supervisors to review with operators NERC requirement to notify the Transmission Operator within 30 minutes of a change in status to AVR and PSS and to provide confirmation after the review has been completed. (Notification sent 2/17/2010) 7) PSE reviewed and updated AVR and PSS procedures at all other PSE plants to ensure they clearly reflect the NERC notification requirement. (Completed 3/15/2011) 8) PSE provided internal webinar refresher training for generation operations staff regarding all the requirements of VAR-002. (Completed 3/16/2011) 9) PSE implemented PSS alarming on affected units at Mint Farm and Goldendale. (Completed 2/22/2011) 10) PSE developed a plan and schedule for implementing additional AVR and PSS alarming at the remainder of PSE generating units. This included adding alarms at locations currently without alarming and adding supplemental text about notifying the Transmission Operator at those sites already alarmed. (Completed 4/15/2011) 11) PSE conducted gap analysis of internal processes for collecting and reporting data for the WECC quarterly AVR/PSS data submittals and implemented process improvements. (Completed 5/1/2011) | 2011-05-01 | 2011-11-03 | Neither Admits nor Denies | PSE had a documented compliance program in place at the time of the violations that WECC considered a mitigating factor in determining the penalty. WECC reviewed PSE’s internal compliance program (ICP) and found that: PSE's ICP was well designed and implemented; processes and procedures are tightly managed and controls are in place; key individuals, including the ICP Manager and Director are committed; executive leadership is knowledgeable and actively supports the program; and PSE’s ICP addresses all elements identified in FERC’s Revised Policy Statement on Enforcement.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Sacramento Municipal Utility District (SMUD) | NCR05368 | WECC201102632 | Settlement Agreement | On January 20, 2011, SMUD, as a Load-Serving Entity, submitted a Self-Certification and on February 18, 2011, SMUD submitted a Self-Report addressing noncompliance with IRO-STD-006-0 WR1. SMUD discovered its possible noncompliance upon reviewing data related to Unscheduled Flow (USF) events. On October 14, 20101, the Path Operator for Path 66, a WECC Qualified Transfer Path, initiated a USF Curtailment Procedure, Step 5, at 14:25 Pacific Time which stayed in effect for hour ending 16:00. SMUD Initiated a Restricted Transaction at 14:28 by scheduling 20 MW on an off-path, after the Path Operator initiated the Curtailment Procedure, and contributed 3.4 MW of unscheduled flow on Path 66. The SMUD Power System Operations (PSO) acted to cut the schedule at 1503. Pursuant to the Sanction Table appended to the Standard, this violation represents one occurrence at Level One of Noncompliance. | IRO-STD-006 | WR1 | N/A | N/A | Although widespread failure to comply with IRO-STD-006 WR1 could pose significant risk to the reliability of the bulk power system (BPS), in this case, the line, the path operator and SMUD had compensating measures in place. Impact during USF events is dependent upon how much an entity contributes to flow on a potentially overloaded path, what other resources the path operator has available to mitigate potential overloads of the transmission system, and any available operating margin. The unscheduled flow involved with this violation is a fraction of one percent of the Path Rating for Path 66. Specifically, although SMUD scheduled 20 MW, it cut the schedule within three minutes of the curtailment procedure going into effect, resulting in SMUD only contributing 3.4 MW to Path 66. Path 66 is rated at 4,800 MW. Further, at the time the path operator initiated the curtailment procedure, Path 66 was below its operating limit by approximately 250 MW, leaving a 250 MW operating margin. The transmission operator continued to have the option of curtailing transactions directly scheduled on Path 66 to reduce flow in the event of an imminent overload. For these reasons, WECC determined that this violation posed minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. | 2010-10-14 | 2010-10-14 | 0 | Self-Certification | On November 1, 2010, a Principal Lead was hired to focus on communication and training for SMUD Real Time trading staff. The existing Unscheduled Flow desk procedure was emailed to all real-time trading staff upon final approval. One-on-one discussions were implemented with each real-time employee to insure their complete understanding of this standard and the revised desk procedure. This training was focused one-on-one instruction. | 2011-03-07 | 2011-08-04 | Does Not Contest | WECC considered the severity of the violation including compensating measures along with the length of the violations as mitigating factors. Pursuant to the Sanction Table appended to the Regional Standard, this violation represents one occurrence at Level One of Noncompliance. The Sanctions Table for this Standard state that the following sanction should be assessed "Letter to Responsible Entity's Chief Executive Officer informing the Responsible Entity of noncompliance with copies to NERC, WECC Member Representative, and WECC Operating Committee Representative."
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | White Creek Wind I, LLC (WCW) | NCR00541 | WECC201002374 | Settlement Agreement | On November 12, 2010, while conducting an internal audit, WCW discovered that it did not have a FRM. Rather, WCW utilized a Wind Energy Resource Assessment document that stated that the generators were the most limiting element, and included other information such as historical wind data, turbine placement, and other studies done in the development of the facility. However, the Wind Energy Resource Assessment did not reference other component types required in R1. On December 17, 2010, WCW submitted a Self-Report concerning a violation of FAC-008-1 R1 due to WCW’s failure, as a Generator Owner, to have a Facility Ratings Methodology (FRM) that met all the sub-requirements of FAC-008-1 R1. | FAC-008-1 | R1 | Medium | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the facility was designed such that the actual wind generators were the most limiting element, and WCW’s personnel were trained that the generators were the most limiting element. In addition, WCW has generating capacity of approximately 205 MW, and interconnects to the BPS at 230 kV via two 34.5 kV/230 kV transformers. | 2008-07-23 | 2010-11-12 | $7500 (Settlement of WECC201002374 and WECC201002375) | Self-Report | WCW put in place on November 12, 2010 NAES Corporation's standard methodology for Facility Ratings documentation, and will periodically review the Facility Ratings Methodology and Facility Ratings for verification. | 2010-11-12 | 2011-11-09 | Agrees and Stipulates to the Facts | WECC determined that there were no aggravating factors warranting a higher penalty. In addition, WECC considered that this is WCW’s first assessed violation of any reliability standard. WECC considered that WCW was cooperative throughout the process, and there was no evidence of any attempt to conceal the violation.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | White Creek Wind I, LLC (WCW) | NCR00541 | WECC201002375 | Settlement Agreement | On November 12, 2010, while conducting an internal audit, WCW discovered that it did not have a valid FRM, and therefore, its facility ratings were not developed in accordance with a FRM as required by FAC-009-1 R1. On December 17, 2010, WCW submitted a Self-Report concerning a violation of FAC-008-1 R1 due to WCW’s failure, as a Generator Owner, to develop facility ratings in accordance with a valid Facility Ratings Methodology (FRM). | FAC-009-1 | R1 | Medium | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the facility was designed such that the actual wind generators were the most limiting element, and WCW’s personnel were trained that the generators were the most limiting element. In addition, WCW has a generating capacity of approximately 205 MW, and interconnects to the BPS at 230 kV via two 34.5 kV/230 kV transformers. | 2008-07-23 | 2010-11-12 | $7500 (Settlement of WECC201002374 and WECC201002375) | Self-Report | WCW put in place on November 12, 2010 NAES Corporation's standard methodology for Facility Ratings documentation, and then WCW used this methodology to determine the Facility Ratings in accordance with FAC-009 R1. | 2010-11-12 | 2011-11-09 | Agrees and Stipulates to the Facts | WECC determined that there were no aggravating factors warranting a higher penalty. In addition, WECC considered that this is WCW’s first assessed violation of any reliability standard. WECC considered that WCW was cooperative throughout the process, and there was no evidence of any attempt to conceal the violation.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC201000344 | Settlement Agreement | PEF submitted a Self-Report to FRCC on March 17, 2010, and revised on April 8, 2010, reporting a violation of PRC-001-1 R3/3.2. PEF, as a Transmission Operator (TOP), did not coordinate changes to the protection systems with three neighboring Balancing Authorities (BAs) and TOPs in two instances. PEF had conducted an internal review to confirm documentation of protection system coordination on all interconnection lines and found two instances where changes to the protection systems were not coordinated with neighboring BAs and TOPs. The first change occurred October 9, 2008 when new settings were issued on the North Bartow to Pebbledale line. The second change occurred on December 2, 2008 when new settings were issued on the Barberville to Barberville line. | PRC-001-1 | R3; R3.2 | High | Severe | This violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system (BPS) because there were no changes to the settings values of the newly installed relays compared to the settings of the prior relays. In addition the interconnected entity did not have to make any changes in response to the installation of the new relays. | 10/9/08 (date of new relay installation) | 12/22/10 (Mitigation Plan completion) | $75,000 (for FRCC201000344, FRCC201000345, FRCC201000353, and FRCC201000357) | Self-Report | PEF completed and approved a procedure that documents the process for coordinating system protection and relay settings with neighboring utilities and Generator Operators. A report was developed listing all interconnections, setting changes and documentation of coordination. PEF communicated its interconnection relay settings to interconnected utilities and validated the coordination of all the interconnection relay settings. After confirming settings with interconnected utilities, PEF performed protection coordination studies to validate the settings and notified interconnected utilities of the results. | 2010-12-22 | 2011-03-24 | Neither Admits nor Denies | PEF had a compliance program at the time of the violation which FRCC considered a neutral factor.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC201000345 | Settlement Agreement | PEF submitted a Self-Report to FRCC on March 17, 2010, and revised on April 8, 2010, reporting a violation of PRC-001-1 R4. PEF, as a Transmission Operator (TOP), could not provide evidence that PEF had coordinated its protective system with interconnected neighboring Generator Operators (GOPs), Balancing Authorities (BAs), and Transmission Operators (TOPs) in 17 instances. PEF stated that it believed that the coordination of the relays was performed, but documentation to prove coordination was not retrievable or did not exist. PEF had conducted an internal review to confirm documentation of protection system coordination on all interconnection lines and PEF kept a spreadsheet of all coordinations. PEF stated that it believed that the coordination of the relays was performed based on its usual business practice, but documentation to prove coordination was not retrievable or did not exist. | PRC-001-1 | R4 | High | High | This violation posed a minimal and not serious or substantial risk to the reliability of the BPS because the PEF states that PEF's practice is to coordinate its settings. It is PEF's regular practice to coordinate settings and PEF believes the settings were coordinated in the 17 instances, but was unable to produce evidence to demonstrate that those 17 instances had been coordinated. | 9/13/07 (date of first change made without evidence of coordination) | 12/22/10 (Mitigation Plan completion) | $75,000 (for FRCC201000344, FRCC201000345, FRCC201000353, and FRCC201000357) | Self-Report | PEF completed and approved a procedure that documents the process for coordinating system protection and relay settings with neighboring utilities and GOPs. A report was developed listing all interconnections, setting changes and documentation of coordination. PEF communicated its interconnection relay settings to interconnected utilities and validated the coordination of all the interconnection relay settings. After confirming settings with interconnected utilities, PEF performed protection coordination studies to validate the settings and notified interconnected utilities of the results. | 2010-12-22 | 2011-03-24 | Neither Admits nor Denies | PEF had a compliance program at the time of the violation which FRCC considered a neutral factor.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC201000353 | Settlement Agreement | PEF submitted a Self-Report to FRCC on March 17, 2010, and revised on April 8, 2010, reporting a violation of FAC-001-1 R2. PEF, as a Transmission Owner (TO), did not include eight of the 16 sub-requirements of FAC-001-1 R2 in its facility connection document. During the months of February and March of 2010, PEF performed an internal review of FAC-001 compliance and found that its facility connection document did not include two of the 2 facility connection sub-requirement elements for end-user interconnection and transmission interconnection. Upon further investigation, PEF found a lack of documentation for a total of eight of the 16 sub-requirements of FAC-001-1 R2. The eight sub-requirements that PEF self-reported are: R2.1.3, R2.1.4, R2.1.5, R2.1.7, R2.1.8, R2.1.11, R2.1.12, and R2.1.15. | FAC-001-0 | R2 | Medium | Moderate | This violation posed a minimal and not serious or substantial risk to the reliability of the BPS because all applicable sub-requirements would have been discussed and negotiated during the engineering studies related to the interconnection. In addition only seven interconnections were made during the duration of the violation and those interconnections do not impact the BPS for purposes of this Standard. | 6/18/07 (when the Standard became mandatory and enforceable) | 10/14/10 (Mitigation Plan completion) | $75,000 (for FRCC201000344, FRCC201000345, FRCC201000353, and FRCC201000357) | Self-Report | PEF assessed its compliance with FAC-001, completed a revised facility connections requirements document, reviewed and assigned the document internally and posted the document publicly. | 2010-10-14 | 2010-11-23 | Neither Admits nor Denies | PEF had a compliance program at the time of the violation which FRCC considered a neutral factor.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Progress Energy Florida (PEF) | NCR00063 | FRCC201000357 | Settlement Agreement | FRCC discovered a violation of VAR-002-1 R3.1 during an April 23, 2010 Compliance Audit. An Automatic Voltage Regulator (AVR) event occurred on December 11, 2007. PEF, as a GOP, failed to communicate to its TOP the expected duration after a change in status for one of its generator reactive power resources. An AVR event occurred on December 11, 2007 at approximately 06:51 EST at Hines Energy Power Block-1B (Hines PB1B). According to the Hines PB1B operation logs, the AVR rejected to manual at 06:51 EST but did not indicate the duration was communicated to the Energy Control Center (ECC) operator. The ECC alarm screen recorded the AVR mode change at 06:51 EST indicating the TOP was aware the AVR rejected to manual but the ECC log did not indicate the duration was communicated. The logs indicated the duration was communicated at 10:07 EST. The GOP failed to communicate to its TOP the expected duration after a change in status for one of its generator Reactive Power resources. | VAR-002-1 | R3; R3.1 | Medium | Lower | This violation posed a minimal and not serious or substantial risk to the reliability of the BPS because the TOP was aware the AVR was unavailable and would have directed the GOP to adjust manually and the GOP was already instructed to maintain voltage schedules as previously provided. | 12/11/07 at 06:51 (when the AVR rejected to manual) | 12/11/07 10:07 (when logs indicate the duration was communicated) | $75,000 (for FRCC201000344, FRCC201000345, FRCC201000353, and FRCC201000357) | Compliance Audit | On September 23, 2010, PEF conducted a diagnostic/ evaluation process focused on identifying improvement opportunities, in order to mitigate opportunities for additional reportable incidents. The Progress Energy Power Operations Group issued an order that reiterated the requirements in VAR-002 as well as the logging, documentation and data retention period requirements. A PlantView Tool was funded, developed, tested and implemented from January to October 2011. The implementation of the new PlantView based reporting tool will allow Plant and ECC operators to communicate an AVR or MVAR status or capability change and duration via a common platform. Once the Plant operator has entered the requisite AVR/MVAR information, the ECC operator receives a notification at the TOP control console that prompts the ECC operator to acknowledge receipt of the event. Requiring all fields to be completed prior to advancing the log to the next step (i.e. initiate, acknowledge, closure) will ensure all of the VAR-002 requirements have been fulfilled for compliance. | 10/31/2011 (Approved Date) | TBD | Neither Admits nor Denies | PEF had a compliance program at the time of the violation which FRCC considered a neutral factor.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Dover | NCR00713 | RFC201000426 | Settlement Agreement | From June 14, 2010 through June 28, 2010, ReliabilityFirst conducted a Compliance Audit of City of Dover. During the Audit, ReliabilityFirst discovered a violation of PRC-005-1 R1. As a Distribution Provider (DP) that owns a transmission Protection System, City of Dover failed to include maintenance and testing intervals for its 60 station batteries and its four voltage and current sensing devices. In addition, City of Dover failed to include a basis for all maintenance and testing intervals as well as summaries of maintenance and testing procedures for its four voltage and current sensing devices. This violation involved all of City of Dover's 69 transmission Protection System devices. As a Generator Owner (GO) that owns a generation Protection System, City of Dover failed to include maintenance and testing intervals for its 20 station batteries, 17 direct current control circuits and 17 voltage and current sensing devices. In addition, City of Dover failed to include a basis for all maintenance and testing intervals as well as summaries of maintenance and testing procedures for its 20 station batteries and its 17 voltage and current sensing devices. | PRC-005-1 | R1 | High | Severe | ReliabilityFirst determined that, due to the facts and circumstances, this violation posed a moderate risk to the reliability of the bulk power system (BPS). City of Dover experienced a Misoperation at the Cartanza substation on November 25, 2008. City of Dover identified, corrected and submitted the information to ReliabilityFirst. The risk to the BPS was mitigated by the following factors: 1) the Cartanza substation has redundant and backup protection, and any alarms alert the operator of the control room, which is staffed 24 hours a day; 2) City of Dover monitors the Protection Systems and visually inspected such Protection Systems during the period notwithstanding the absence of a formal plan for maintenance and testing and scheduled intervals; 3) Unit 11, City of Dover's one generating unit with blackstart capability, has triple redundant protection, and when the Protection System operates, alarms sound and personnel respond immediately; and 4) City of Dover surveys and inspects Unit 11 at least once daily. | 6/18/2007 (mandatory effective date of the Standard) | 9/1/2010 (date City of Dover implemented its revised program) | $18,000 (for RFC201000426, RFC201000427, RFC201000616, and RFC201000617) | Compliance Audit | For its DP function, City of Dover developed a program that defines the intervals and basis for all maintenance and testing and includes summaries of the maintenance and testing procedures. For its GO function, City of Dover developed a revised program which defines maintenance and testing intervals and their basis for all Protection System devices. | 8/30/2010 (for DP function) 3/31/2011 (for GO function) | 10/26/2010 (for DP function) 4/20/2011 (for GO function) | Admits | ReliabilityFirst considered certain aspects of City of Dover's compliance program as mitigating factors. Individuals working in administration, line crews, and engineering and operations individually complete workshops and training. In addition, City of Dover compliance officers have direct contact with the City Manager. City of Dover’s Reliable Public Power Provider panel reviews the city’s plans and indices biennially, and City of Dover reviews them yearly. City of Dover’s Reliable Public Power Provider application is reviewed bi-annually, and City of Dover reviews all plans and indices yearly.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Dover | NCR00713 | RFC201000427 | Settlement Agreement | From June 14, 2010 through June 28, 2010, ReliabilityFirst conducted a Compliance Audit of City of Dover. During the Audit, ReliabilityFirst discovered a violation of PRC-005-1 R2. As a Distribution Provider (DP) that owns a transmission Protection System, City of Dover failed to provide evidence that it maintained and tested its station batteries and voltage and current sensing devices within the defined intervals. In addition, City of Dover failed to provide the date it last maintained and tested its voltage and current sensing devices. This violation involved City of Dover's single transmission station battery bank, which includes 60 batteries and all of its four transmission voltage and current sensing devices, which constitute 64 of City of Dover's 69 total transmission Protection System devices. As a Generator Owner (GO) that owns a generation Protection System, City of Dover failed to provide evidence that it maintained and tested its station batteries, direct current control circuitry and voltage and current sensing devices. In addition, City of Dover failed to provide the date it last maintained and tested its station voltage and current sensing devices. This violation involved all of City of Dover’s 20 generation station batteries, all of its 17 generation direct current control circuits, and all of its 17 generation voltage and current sensing devices, which constitute 54 of City of Dover’s 83 total generation Protection System devices. | PRC-005-1 | R2 | Lower | Severe | ReliabilityFirst determined that, due to the facts and circumstances, this violation posed a moderate risk to the reliability of the bulk power system (BPS). City of Dover experienced a Misoperation at the Cartanza substation on November 25, 2008. City of Dover identified, corrected and submitted the information to ReliabilityFirst. The risk to the BPS was mitigated by the following factors: 1) The Cartanza substation has redundant and backup protection, and any alarms alert the operator of the control room, which is staffed 24 hours a day; 2) all voltage and current sensing devices passed tests during installation in 2004, and City of Dover continually tested its station batteries despite failing to include intervals in its maintenance and testing program until 2009; 3) SCADA alarms monitor the direct current control circuitry and the station batteries; and 4) City of Dover found no issues with the voltage and current sensing devices and station batteries when it next tested those devices. In addition, City of Dover surveys and inspects Unit 11, City of Dover's one generating unit with blackstart capability, at least once daily. Unit 11 has triple redundant protection, and when the Protection System operates, alarms sound and personnel respond immediately. Furthermore, City of Dover installed an additional battery bank in parallel to the original battery bank in order to provide redundancy and extended battery power in the case of blackstart activity. | 6/18/2007 (mandatory effective date of the Standard) | 8/30/2010 (for DP function, date City of Dover completed all testing) 3/31/2011 (for GO function, date City of Dover completed all testing due to need to coordinate outages with PJM Interconnection, LLC) | $18,000 (for RFC201000426, RFC201000427, RFC201000616, and RFC201000617) | Compliance Audit | For its DP function, City of Dover conducted required maintenance and testing on all station batteries and voltage and current sensing devices pursuant to its revised Protection System maintenance and testing program. For its GO function, City of Dover conducted all required testing on all direct current control circuitry and voltage and current sensing devices pursuant to its revised Protection System maintenance and testing program. | 8/30/2010 (for DP function) 3/31/2011 (for GO function) | 10/26/2010 (for DP function) 4/20/2011 (for GO function) | Admits | ReliabilityFirst considered certain aspects of City of Dover's compliance program as mitigating factors. Individuals working in administration, line crews, and engineering and operations individually complete workshops and training. In addition, City of Dover compliance officers have direct contact with the City Manager. City of Dover’s Reliable Public Power Provider panel reviews the city’s plans and indices biennially, and City of Dover reviews them yearly. City of Dover’s Reliable Public Power Provider application is reviewed bi-annually, and City of Dover reviews all plans and indices yearly.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Dover | NCR00713 | RFC201000616 | Settlement Agreement | From June 14, 2010 through June 28, 2010, ReliabilityFirst conducted a Compliance Audit of City of Dover. During the Audit, ReliabilityFirst discovered a violation of FAC-008-1 R1. City of Dover, as a Generator Owner, failed to include terminal equipment in the scope of equipment addressed in its Facility Ratings Methodology. In addition, City of Dover's Facility Ratings Methodology failed to include a Ratings Methodology for relay protective devices and instead included its relay settings in its Facility Ratings Methodology; however, relay settings are not a Facility Rating. | FAC-008-1 | R1 | Medium | Moderate | ReliabilityFirst determined that, due to the facts and circumstances, this violation posed a moderate risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors: 1) the most limiting element of City of Dover’s Facility is the turbine generator, and this did not change when City of Dover added the missing terminal equipment; 2) City of Dover has not derated any generation facilities, and the Rating for the terminal equipment is well above the most limiting element; and 3) the Rating for Unit 11, City of Dover's one generating unit with blackstart capability, is accurate, as demonstrated by its performance as part of the PJM Interconnection, LLC's Summer and Winter Capacity Demonstration Programs. | 6/18/2007 (mandatory effective date of the Standard) | 8/30/2010 (the date City of Dover completed its mitigation plan) | $18,000 (for RFC201000426, RFC201000427, RFC201000616, and RFC201000617) | Compliance Audit | City of Dover revised its Facility Ratings Methodology to include terminal equipment and a correct rating for its relay protective devices. | 2010-08-30 | 2010-11-22 | Admits | ReliabilityFirst considered certain aspects of City of Dover's compliance program as mitigating factors. Individuals working in administration, line crews, and engineering and operations individually complete workshops and training. In addition, City of Dover compliance officers have direct contact with the City Manager. City of Dover’s Reliable Public Power Provider panel reviews the city’s plans and indices biennially, and City of Dover reviews them yearly. City of Dover’s Reliable Public Power Provider application is reviewed bi-annually, and City of Dover reviews all plans and indices yearly.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Dover | NCR00713 | RFC201000617 | Settlement Agreement | From June 14, 2010 through June 28, 2010, ReliabilityFirst conducted a Compliance Audit of City of Dover. During the Audit, ReliabilityFirst discovered a violation of the FAC-009-1 R1. ReliabilityFirst reviewed City of Dover’s Facility Ratings, as they were included in its Reliability Compliance Manual, which includes the Facility Ratings for the McKee Run and VanSant generating stations. City of Dover, as a Generator Owner, failed to include Ratings for transmission conductors and failed to include Emergency Ratings for its transmission conductors for the McKee Run and VanSant generating stations, consistent with the associated Facility Ratings Methodology. | FAC-009-1 | R1 | Medium | High | ReliabilityFirst determined that, due to the facts and circumstances, this violation posed a moderate risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors: 1) the most limiting element of City of Dover’s Facility is the turbine generator, and this did not change when City of Dover added the missing terminal equipment; 2) City of Dover has not derated any generation facilities; 3) the Rating for Unit 11, City of Dover's one generating unit with blackstart capability, is accurate, as demonstrated by its performance as part of the PJM Interconnection, LLC's Summer and Winter Capacity Demonstration Programs. | 6/18/2007 (mandatory effective date of the Standard) | 8/30/2010 (the date City of Dover completed its mitigation plan) | $18,000 (for RFC201000426, RFC201000427, RFC201000616, and RFC201000617) | Compliance Audit | City of Dover revised its plant procedures and supporting documents to include transmission conductors and Emergency Ratings for transmission conductors in its Facility Ratings. | 2010-08-30 | 2010-11-22 | Admits | ReliabilityFirst considered certain aspects of City of Dover's compliance program as mitigating factors. Individuals working in administration, line crews, and engineering and operations individually complete workshops and training. In addition, City of Dover compliance officers have direct contact with the City Manager. City of Dover’s Reliable Public Power Provider panel reviews the city’s plans and indices biennially, and City of Dover reviews them yearly. City of Dover’s Reliable Public Power Provider application is reviewed bi-annually, and City of Dover reviews all plans and indices yearly.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Duke Energy Corporation (Duke) | NCR00761 | RFC201000665 | Settlement Agreement | On October 28, 2010, Duke submitted a Self-Report indicating that Duke, as a Transmission Owner that owns a transmission Protection System, failed to produce evidence that 20 of its Protection System devices were maintained and tested with the defined intervals. Duke provided additional information via an amended Self-Report submitted on January 21, 2011. In these Self-Reports, Duke disclosed that it had failed to test 20 relays at its Wheatland combustion turbine peaking facility within the five-year interval specified in its Protection System maintenance and testing program. Duke purchased this facility in 2005 and, upon this transition, failed to identify and include these relays in its Protection System maintenance and testing program. Duke’s Protection System maintenance and testing program includes approximately 9,100 relays. This violation involved approximately 0.2% of these relays. | PRC-005-1 | R2.1 | High | Lower | Based on the nature of the violation, and offset by the mitigating factors described below, ReliabilityFirst determined that this violation posed a moderate risk to the reliability of the bulk power system. This risk posed by this violation was mitigated by the following factors: 1) Duke received documentation from the previous owner of the Wheatland facility showing that the relays were tested in 2003 and found to be in good working condition and within tolerance; 2) upon performing testing in 2010, Duke found the relays to be in good working condition and within tolerance; 3) Duke experienced no misoperations or system events regarding these relays; and 4) all of the relays at issue are protected by a back-up protection system and a majority of the relays at issue are further protected by a redundant Protection System. | 10/7/2009 (the date Duke missed the interval defined in its Protection System maintenance and testing program) | 10/28/2010 (the date that Duke completed testing on the 20 relays) | 14000 | Self-Report | Duke completed testing on these 20 relays. To prevent recurrence of this violation, Duke ensured that the 20 relays were included in the tracking documentation used in conjunction with its Protection System maintenance and testing program. In addition, a review of the relays identified in the transmission and generation Protection System maintenance and testing program was conducted to ensure all required relays were included in the program at the Wheatland generating station as well as two other Duke-purchased generation facilities. This analysis was completed on October 31, 2010. | 2010-10-28 | 2011-08-23 | Admits | ReliabilityFirst considered certain aspects of Duke’s compliance program as mitigating factors. Duke has a compliance administration program that is responsible for compliance with the Reliability Standards. The compliance administration program reports to the vice president of compliance and integration, who has independent access to the CEO. The compliance program is integrated and widely distributed throughout the company. ReliabilityFirst also considered an affiliate of Duke's, Duke Energy Carolinas, prior violation of PRC-005-1 R2 (NOC-378). ReliabilityFirst determined that the instant violation constituted a repetitive infraction and, accordingly, considered Duke’s violation history as an aggravating factor.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Fowler Ridge Wind Farm LLC (Fowler Ridge) | NCR10307 | RFC201100757 | Settlement Agreement | Fowler Ridge submitted a self report on February 18, 2011 regarding a violation of FAC-009-1 R1. Fowler Ridge, as a Generator Owner (GO), failed to include its Generation Interconnection Line in its Facility Ratings. Prior to NERC's October 7, 2010 Recommendation to Industry entitled "Consideration of Actual Field Conditions in Determination of Facility Ratings," Fowler Ridge was not aware that it needed to include Facility Ratings for the Generation Interconnection Line. During due diligence performed in preparation to respond to the Recommendation, AE Power, the company that manages Fowler Ridge's compliance program, discovered the issue. Fowler Ridge maintains a Facility Ratings Methodology in accordance with FAC-008-1. FAC-008-1 R1.2.1 describes a non-exclusive list of the scope of equipment to be included in that Facility Ratings Methodology. FAC-008-1 does not affirmatively indicate that it should apply to generation interconnection lines. AE Power incorrectly did not interpret scope of FAC-008-1 to include the Generation Interconnection Line, and it did not have a documented rating for the Generation Interconnection Line, as required by FAC-009-1 R1. Fowler Ridge violated FAC-009-1 R1 by failing to establish a facility rating for the Generation Interconnection Line consistent with the associated Facility Ratings Methodology. | FAC-009-1 | R1 | Medium | Moderate | In light of the nature of the alleged violation, offset by the aforementioned mitigating factors, ReliabilityFirst determined that the violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS presented by this violation was mitigated by several facts. Fowler Ridge indicates that it had correctly identified the most limiting element prior to revision of its facility ratings to include the Generation Interconnection Line. As a result, the most limiting component of the facility ratings did not change with the addition of the Generation Interconnection Line. The Fowler Ridge Wind Farm Complex has been in operation for just over two years, and in that time, Fowler Ridge has not experienced any system disturbances. Moreover, as wind-powered generating facilities, Fowler Ridge's facilities are intermittent in nature. Intermittent resources are characterized by a dependence on natural factors beyond the control of the resource operator for their energy production. | 3/11/2009 (date Fowler Ridge registered on the Compliance Registry) | 3/11/2011 (date Fowler Ridge revised its facility ratings to include the Generation Interconnection line) | $15,000 (For RFC201100757, RFC201100758, and RFC201100759) | Self-report | Fowler Ridge revised its facility ratings to include a facility rating for the Generation Interconnection Line in which it has an undivided ownership interest. | 2011-03-11 | 2011-05-25 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of Fowler Ridge's compliance program as mitigating factors in assessing the penalty. The Regulatory Compliance Manager directly reports to the Vice President of Operations and Asset Management with an indirect reporting relationship to the Electric Regulatory Attorney on compliance matters. Fowler Ridge is also taking proactive measures to implement a computerized maintenance management system to ensure compliance matters are performed according to schedule.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Fowler Ridge Wind II Farm LLC (Fowler Ridge II) | NCR03040 | RFC201100758 | Settlement Agreement | Fowler Ridge II submitted a self report on February 18, 2011 regarding a violation of FAC-009-1 R1. Fowler Ridge II, as a GO, failed to include its Generation Interconnection Line in its Facility Ratings. Prior to NERC's October 7, 2010 Recommendation to Industry entitled "Consideration of Actual Field Conditions in Determination of Facility Ratings," Fowler Ridge was not aware that it needed to include Facility Ratings for the Generation Interconnection Line. During due diligence performed in preparation to respond to the Recommendation, AE Power, the company that manages Fowler Ridge II's compliance program, discovered the issue. Fowler Ridge II maintains a Facility Ratings Methodology in accordance with FAC-008-1. FAC-008-1 R1.2.1 describes a non-exclusive list of the scope of equipment to be included in that Facility Ratings Methodology. FAC-008-1 does not affirmatively indicate that it should apply to generation interconnection lines. AE Power incorrectly did not interpret the scope of FAC-008-1 to include the Generation Interconnection Line, and it did not have a documented rating for the Generation Interconnection Line, as required by FAC-009-1 R1. Fowler Ridge II violated FAC-009-1 R1 by failing to establish a facility rating for the Generation Interconnection Line consistent with the associated Facility Ratings Methodology. | FAC-009-1 | R1 | Medium | Moderate | In light of the nature of the alleged violation, offset by the aforementioned mitigating factors, ReliabilityFirst determined that the violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS presented by this violation was mitigated by several facts. Fowler Ridge II indicates that it had correctly identified the most limiting element prior to revision of its facility ratings to include the Generation Interconnection Line. As a result, the most limiting component of the facility ratings did not change with the addition of the Generation Interconnection Line. The Fowler Ridge Wind Farm Complex has been in operation for just over two years, and in that time, Fowler Ridge II has not experienced any system disturbances. Moreover, as wind-powered generating facilities, Fowler Ridge II's generating facilities are intermittent in nature. Intermittent resources are characterized by a dependence on natural factors beyond the control of the resource operator for their energy production. | 12/18/2009 (date Fowler Ridge II registered on the Compliance Registry) | 3/11/2011 (date Fowler Ridge II revised its facility ratings to include the Generation Interconnection line) | $15,000 (For RFC201100757, RFC201100758, and RFC201100759) | Self-report | Fowler Ridge II revised its facility ratings to include a facility rating for the Generation Interconnection Line in which it has an undivided ownership interest. | 2011-03-11 | 2011-05-25 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of Fowler Ridge II's compliance program as mitigating factors in assessing the penalty. The Regulatory Compliance Manager directly reports to the Vice President of Operations and Asset Management with an indirect reporting relationship to the Electric Regulatory Attorney on compliance matters. Fowler Ridge II is also taking proactive measures to implement a computerized maintenance management system to ensure compliance matters are performed according to schedule.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Fowler Ridge Wind III Farm LLC (Fowler Ridge III) | NCR10308 | RFC201100759 | Settlement Agreement | Fowler Ridge III submitted a self report on February 18, 2011 regarding a violation of FAC-009-1 R1. Fowler Ridge, as a GO, failed to include its Generation Interconnection Line in its Facility Ratings. Prior to NERC's October 7, 2010 Recommendation to Industry entitled "Consideration of Actual Field Conditions in Determination of Facility Ratings," Fowler Ridge III was not aware that it needed to include Facility Ratings for the Generation Interconnection Line. During due diligence performed in preparation to respond to the Recommendation, AE Power, the company that manages Fowler Ridge's compliance program, discovered the issue. Fowler Ridge III maintains a Facility Ratings Methodology in accordance with FAC-008-1. FAC-008-1 R1.2.1 describes a non-exclusive list of the scope of equipment to be included in that Facility Ratings Methodology. FAC-008-1 does not affirmatively indicate that it should apply to generation interconnection lines. AE Power incorrectly did not interpret the scope of FAC-008-1 to include the Generation Interconnection Line, and it did not have a documented rating for the Generation Interconnection Line, as required by FAC-009-1 R1. Fowler Ridge III violated FAC-009-1 R1 by failing to establish a facility rating for the Generation Interconnection Line consistent with the associated Facility Ratings Methodology. | FAC-009-1 | R1 | Medium | Moderate | In light of the nature of the alleged violation, offset by the aforementioned mitigating factors, ReliabilityFirst determined that the violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS presented by this violation was mitigated by several facts. Fowler Ridge III indicates that it had correctly identified the most limiting element prior to revision of its facility ratings to include the Generation Interconnection Line. As a result, the most limiting component of the facility ratings did not change with the addition of the Generation Interconnection Line. The Fowler Ridge Wind Farm Complex has been in operation for just over two years, and in that time, Fowler Ridge III has not experienced any system disturbances. Moreover, as wind-powered generating facilities, Fowler Ridge III's generating facilities are intermittent in nature. Intermittent resources are characterized by a dependence on natural factors beyond the control of the resource operator for their energy production. | 3/11/2009 (date Fowler Ridge III registered on the Compliance Registry) | 3/11/2011 (date Fowler Ridge III revised its facility ratings to include the Generation Interconnection line) | $15,000 (For RFC201100757, RFC201100758, and RFC201100759) | Self-report | Fowler Ridge III revised its facility ratings to include a facility rating for the Generation Interconnection Line in which it has an undivided ownership interest. | 2011-03-11 | 2011-05-25 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of Fowler Ridge III's compliance program as mitigating factors in assessing the penalty. The Regulatory Compliance Manager directly reports to the Vice President of Operations and Asset Management with an indirect reporting relationship to the Electric Regulatory Attorney on compliance matters. Fowler Ridge III is also taking proactive measures to implement a computerized maintenance management system to ensure compliance matters are performed according to schedule.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC201002229 | Settlement Agreement | On September 27, 2010, AVGO, as a Generator Owner that owns a generation Protection System, submitted a Self-Report citing possible noncompliance with PRC-005-1 R2.2 for failure to test and maintain its Protection System equipment. WECC determined that AVGO was in violation of R2.1 because AVGO was able to provide the date last tested but was not able to provide evidence of maintenance and testing completed within defined intervals for 8 out of its 25 electromechanical relays. The protective relays had not been maintained within the three-year interval defined in AVGO's Protection System maintenance and testing program. AVGO's maintenance schedule indicates its protective relays were tested on February 17, 2006 and again on June 18, 2009, exceeding its three-year interval by approximately four months. AVGO should have tested and maintained its electromechnical relays no later than February 17, 2009. | PRC-005-1 | R2 | High | Medium | WECC determined that this violation posed a minimal risk to the reliability of the bulk power system (BPS) because all protective relays were tested shortly after the defined period (four months) and were verified to operate properly. In addition, AVGO has three generating units totaling 599 MW of generation. WECC determined that the loss of generation would have a minimal impact on the BPS. | 2/18/2009 (the day after the protective relays were due to be tested within the defined three-year interval) | 6/18/2009 (when the protective relays were actually tested) | $44,000 (for WECC201002229 and WECC201002275) | Self-Report | Upon discovering the violation, AVGO promptly performed the testing and maintenance to correct the noncompliance. AVGO's submitted a mitigation plan which addresses implementing a new Protection System maintenance and testing program that allows extra time for completion of maintenance and testing should scheduling issues arise. Specifically, in respect to its electromechanical relays, AVGO revised its Protection System maintenance and testing program to allow for relays to be tested and maintained within six months of the originally scheduled maintenance and testing date. | 2010-09-15 | 2010-10-27 | Agrees and Stipulates to the Facts of the Settlement Agreement | Prior to November 30, 2009, the AVGO generating facilities were encompassed in the former registration of Dynegy Arlington Valley, LLC (DYAV) (NCR05135) and Dynegy Inc. (DYN) (NCR00200). On or about November 30, 2009, there was a transfer of ownership and facility assignment associated with registration changes resulting in AVGO being responsible for compliance activities for the AVGO generation facilities and one additional facility originally owned by DYN. WECC applied as an aggravating factor that DYN had a prior violation of the same standard and considered the instant violation a second instance of noncompliance. On July 14, 2009, DYN submitted a Self-Certification for the first instance of noncompliance. In the first instance, station batteries were not maintained and tested within the interval defined in DYN's Protection System maintenance and testing program, as required by R2.1. WECC verified DYN's completion of the mitigation plan for the first violation on October 5, 2009. WECC did not take into account other DYN violations in other regions. WECC feels that the settlement penalty amount of $44,000 for two PRC-005 R2 violations is appropriate for the level of risk these violations represent.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Arlington Valley, LLC (AVGO) | NCR03051 | WECC201002275 | Settlement Agreement | On October 26, 2010, AVGO, as a Generator Owner that owns a generation Protection System, submitted a Self-Report citing possible noncompliance with PRC-005-1 R2 for failure to test and maintain its Protection System equipment within defined intervals. WECC determined AVGO had not tested and maintained three out of five station batteries, part of AVGO's Protection Systems, within defined intervals. AVGO's maintenance and testing program requires inspections on Protection System batteries to be performed monthly, plus seven days. AVGO documented inspections were performed on August 18, 2010 and August 19, 2010, but AVGO did not complete its subsequent inspections until September 29, 2010 and September 30, 2010. These testing intervals exceeded AVGO's maintenance and testing program interval by four days on three of its batteries. | PRC-005-1 | R2 | High | High | WECC determined that this violation posed a minimal risk to the reliability of the bulk power system (BPS) because all three batteries were tested shortly after the defined period (four months) and were verified to operate properly. In addition, AVGO has three generating units totaling 599 MW of generation. WECC determined that the loss of generation would have a minimal impact on the BPS. | 9/26/2010 (the day after the batteries were due to be tested within the defined interval) | 9/30/2010 (when the batteries were actually tested) | $44,000 (for WECC201002229 and WECC201002275) | Self-Report | Upon discovering the violation, AVGO promptly performed the testing and maintenance to correct the noncompliance. AVGO submitted a mitigation plan which states that it conducted PRC-005 training for all its operations, maintenance and management personnel on-site. Specifically, AVGO implemented a new maintenance tracking system in accordance with its revised Protection System maintenance and testing program. The new tracking system is designed to ensure action items are tracked based on its defined intervals as opposed to calendar dates. | 2010-12-17 | 2011-01-05 | Agrees and Stipulates to the Facts of the Settlement Agreement | Prior to November 30, 2009, the AVGO generating facilities were encompassed in the former registration of Dynegy Arlington Valley, LLC (DYAV) (NCR05135) and Dynegy Inc. (DYN) (NCR00200). On or about November 30, 2009, there was a transfer of ownership and facility assignment associated with registration changes resulting in AVGO being responsible for compliance activities for the AVGO generation facilities and one additional facility originally owned by DYN. WECC applied as an aggravating factor that DYN had a prior violation of the same standard and considered the instant violation a second instance of noncompliance. On July 14, 2009, DYN submitted a Self-Certification for the first instance of noncompliance. In the first instance, station batteries were not maintained and tested within the interval defined in DYN's Protection System maintenance and testing program, as required by R2.1. WECC verified DYN's completion of the mitigation plan for the first violation on October 5, 2009. WECC did not take into account other DYN violations in other regions. WECC feels that the settlement penalty amount of $44,000 for two PRC-005 R2 violations is appropriate for the level of risk these violations represent.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Kings River Conservation District (KRCD) | NCR05505 | WECC201102430 | Settlement Agreement | On February 17, 2011, KRCD, as a Generator Owner, submitted a Self-Report addressing its noncompliance with PRC-005-1 R2.1. According to the Self-Report, KRCD's Generator Protection System Maintenance and Testing Program requires monthly inspections of battery systems. The program further indicates that batteries are maintained and tested according to manufacturer's recommendations and/or industry standards. During an internal inspection of battery maintenance records, KRCD discovered that not all inspections were performed within the one-month plus 5 day grace period as specified in its program. A further detailed inspection of KRCD's battery maintenance records found that not all elements of the battery inspection program had been regularly performed as part of the current inspection practice. On March 25, 2011, a WECC Subject Matter Expert (SME) reviewed KRCD's Self-Report and determined that KRCD could not provide evidence of maintenance and testing within defined intervals for 9 monthly battery inspections. Specifically, KRCD missed 3 monthly inspections at the Pine Flat Generating station in February 2008, November 2008 and February 2009. Additionally, KRCD missed 6 battery inspections at the Malaga Generating Station; four in November 2008, one in October 2010 and one in November 2010. Based on this review, the WECC determined KCRD, as a Generator Owner, was in violation of PRC-005-1 R2.1 for failure to conduct 9 monthly battery inspections within defined intervals and failure to test and maintain 100% of its battery devices within defined intervals. | PRC-005-1 | R2.1 | High | Severe | WECC determined that this violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system because although KRCD could not provide evidence of Protection System maintenance and testing within the defined intervals for 9 required monthly battery inspections, KRCD had performed most of its maintenance and testing in accordance with its maintenance and testing plan. All of KRCD's battery voltages were consistently monitored in the control room at the Malaga Generation station. Additionally, a low voltage alarm is located at the Pine Flat Control Room where operators monitor voltages routinely. Any abnormal voltage conditions are immediately brought to the operator's attention and appropriate action is taken. KRCD's low voltage alarm was not triggered by any of the failed battery inspections. Moreover, KRCD maintained and tested its other Protection system devices in accordance with its plan. | 2/1/2008 (when KRCD first missed its monthly battery inspection) | 12/7/2010 (Mitigation Plan completion) | 9000 | Self-Report | KRCD completed and documented the next monthly battery maintenance scheduled and all monthly battery inspections are current on KRCD's schedule. KRCD modified its electronic maintenance and tracking system at Malaga (MP2) to prevent KRCD from missing more than one month of batter inspections. KRCD reviewed the Protection System Maintenance and Testing Program battery Maintenance and Testing requirements with all involved maintenance personnel to ensure they are aware of the importance of completing work orders on time and ensuring the proper evidence has been documented. KRCD now requires hardcopies of monthly battery records be submitted to the Maintenance Supervisor for review within five days of completion of the work. Finally, KRCD's Internal Compliance Program (ICP) personnel will review monthly battery records on a quarterly basis to ensure all work is complete. | 2010-12-07 | 2011-05-11 | Agrees and Stipulates to the Facts | WECC reviewed KRCD's ICP and considered it a mitigating factor in penalty determination. WECC found that: KRCD's ICP is documented; the ICP is disseminated throughout its operations staff; KRCD has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; the ICP oversight staff has independent access to the General Manager and/or board of directors; KRCD operates the ICP such that it is somewhat independent of staff responsible for compliance with the Reliability Standards; the ICP has the support and participation of senior management; KRCD reviews and modifies its ICP regularly; KRCD's ICP includes formal, internal self-auditing for compliance with all Reliability Standards on a periodic basis; and KRCD's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | PPL Montana, LLC (PPLM) | NCR05329 | WECC201102402 | Settlement Agreement | On January 10, 2011, PPLM, as a Generator Operator, self-reported a potential violation of VAR-002-1.1 b R3. A WECC subject matter expert (SME) reviewed PPLM's Self-Report and concluded that on October 10, 2010, PPLM did not notify NorthWestern Energy (NWE), its associated Transmission Operator (TOP), that the Power System Stabilizer (PSS) on its Colstrip Steam Electric Station (Colstrip) Unit No. 2 was out of service. NWE was not informed of the service interruption until 48.2 hours later when the PSS returned to service. Additionally, the WECC SME concluded that on November 1, 2010, PPLM failed for a second time to notify NWE that its PSS on Colstrip Unit No. 2 was out of service for approximately 36 minutes. Based on the Self-Report and supporting evidence, WECC concluded that PPLM was in violation of VAR-002-1.1b R3. | VAR-002-1.1b | R3 | Medium | Moderate | WECC determined that this violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). PPLM's Colstrip is comprised of four generators. During the times the PSS on Colstrip Unit No. 2 was out, the other units at Colstrip were operating and capable of responding to any need for system damping. For these reasons, WECC has determined that PPLM's violation posed a minimal risk to the BPS. | 10/10/2010 (date of first instance) 11/1/2010 (date of second instance) | 10/12/2010 (when the TOP was notified of the first instance) 11/1/2010 | 14000 | Self-Report | 1. The Colstrip operations specialist sent an email to relevant crews reminding them of the requirement to notify PPLM's associated TOP, the NWE Systems Operation Control Center (SOCC), of a status or capability change on any generator Reactive Power resource. This notification is to include the status of each automatic voltage regulator and PSS and the expected duration of the change in status or capability. 2. The operations specialist ensured that all PSS alarms include the words "Call SOCC" which is an indication for the Generator Operator to contact the SOCC in order to notify NWE of the status/capability change. 3. PPLM conducted reinforcement training for the affected operators of the need to notify the SOCC for all status/capability changes specified in R3. 4. The plant control systems on all four Colstrip units were configured to send email messages to certain supervisors and to appropriate SOCC personnel when there is any change in PSS (or AVR) status, as specified in R3. 5. A dashboard light for PSS/AVR alarms was added to the unit overview screen for each Colstrip Unit. These "dashboard lights" indicate to the Generator Operator that the unit has experienced a change in status. 6. The priority of the PSS/AVR alarms was raised from "Priority 2" to "Priority 1." (Priority 1 alarms are the highest priority alarms in the control system and remain visible to the operators until they are cleared.) 7. The plant control system has been programmed to automatically enable the PSS upon synchronization of the units. | 2011-03-12 | 2011-08-16 | Admits | WECC considered PPLM's internal compliance program (ICP), which was in place at the time of the violation, a mitigating factor. WECC found that PPLM's ICP is documented, the ICP is disseminated throughout its operations staff and that PPLM has ICP oversight staff. PPLM's ICP oversight staff is supervised at a high level in the organization. Key compliance personnel have independent access to the CEO and/or board of directors. PPLM operates the ICP such that it is independent of staff responsible for compliance with the Reliability Standards. PPLM has allocated sufficient resources to its ICP which has the support and participation of senior management. PPLM reviews and modifies its ICP regularly which includes formal, internal self auditing for compliance with all Reliability Standards on a periodic basis. PPLM's ICP includes disciplinary action for employees involved in violations of the Reliability Standards, when applicable. This violation was PPLM's second assessed violation of VAR-002-1 R3. WECC previously determined PPLM violated the Standard on several instances in 2007 and 2008. In the prior case, PPLM failed to notify its Transmission Operator within 30 minutes that certain AVRs were out of service at its Kerr Dam, Cochrane Dam and Morony Dam facilities. WECC determined that the violation herein is a repeat instance of noncompliance and an aggravating factor.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Armstrong Energy Limited Partnership, LLLP (Armstrong Energy) | NCR00211 | RFC201000408 | Settlement Agreement | During a compliance audit from June 14, 2010 through June 25, 2010 (Audit), ReliabilityFirst, determined that Armstrong Energy, as a Generator Owner, failed to include a basis for any of its maintenance and testing intervals in its Protection System maintenance and testing program in effect from August 5, 2008 to August 28, 2008 (Program). In addition, the Program did not include maintenance and testing intervals or a summary of maintenance and testing procedures for communications systems. On August 28, 2008, Armstrong Energy issued a new Protection System maintenance and testing program to replace the August 5, 2008 Program. | PRC-005-1 | R1 | High | Severe | ReliabilityFirst determined that this violation posed a moderate but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Program was in place for less than one battery testing cycle and the duration of the violation was for less than one month. Armstrong Energy missed no maintenance and testing intervals as a result of the violation. In addition, Armstrong Energy has alarms in place to detect abnormal conditions for its voltage sensing devices, relays and station batteries and these alarms did not sound during the period of the violation. Furthermore, Armstrong Energy conducts daily walk down inspections of its plant, including all relay and battery rooms, to check for faults and Armstrong Energy detected no faults during the time period of the violation. | 2008-08-05 | 2008-08-28 | $10,000 (for RFC201000408 and RFC201000409) | Compliance Audit | On August 17, 2011, Armstrong Energy submitted a mitigation plan to address the violation of PRC-005-1 R1. Armstrong Energy took the following action to mitigate the violation. Armstrong Energy issued a new Protection System maintenance and testing program on August 28, 2008, which included communication systems and the basis for all maintenance and testing intervals. | 2008-08-28 | 2011-08-08 | Admits | Although ReliabilityFirst reviewed a previous violation of PRC-005-1 R2 by Armstrong Energy's affiliate, Troy Energy LLC, ReliabilityFirst determined that this prior violation should not serve as a basis for aggravating the penalty since Armstrong Energy’s violation of PRC-005-1 R1 preceded Troy’s violation. Moreover, there was nothing in the record to suggest that broader corporate issues were implicated. ReliabilityFirst considered Armstrong Energy's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Armstrong Energy Limited Partnership, LLLP (Armstrong Energy) | NCR00211 | RFC201000409 | Settlement Agreement | During a compliance audit from June 14, 2010 through June 25, 2010 (Audit), ReliabilityFirst determined that while Armstrong Energy, as a Generator Owner, provided a Facility Ratings Methodology (Methodology), the Methodology did not include transmission conductors in its scope, as required by the Standard. In addition, the Methodology did not include Normal and Emergency Ratings for transmission conductors in its scope. | FAC-008-1 | R1 | Medium | Severe | ReliabilityFirst determined that this violation posed a moderate but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Armstrong Energy provided the manufacturer's ratings for the transmission conductors at the Audit, and did not deviate from the manufacturer's ratings when it amended its Methodology to include transmission conductors and their Normal and Emergency Ratings. | 2008-08-05 | 2010-07-12 | $10,000 (for RFC201000408 and RFC201000409) | Compliance Audit | On March 17, 2011, Armstrong Energy submitted a mitigation plan to address the violation of FAC-008-1 R1.2. Armstrong Energy took the following action to mitigate the violation. Armstrong Energy amended its Methodology to include transmission conductors, including their Normal and Emergency Ratings. | 2010-07-12 | 2011-08-05 | Admits | Although ReliabilityFirst reviewed a previous violation of PRC-005-1 R2 by Armstrong Energy's affiliate, Troy Energy LLC, ReliabilityFirst determined that this prior violation should not serve as a basis for aggravating the penalty since Armstrong Energy’s violation is not the same or similar to the standard. Moreover, there was nothing in the record to suggest that broader corporate issues were implicated. ReliabilityFirst considered Armstrong Energy's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Buckeye Power, Inc. (Buckeye Power) | NCR00700 | RFC201000654 | Settlement Agreement | From September 13, 2010 to September 28, 2010, ReliabilityFirst conducted a compliance audit of Buckeye Power, during which ReliabilityFirst discovered a violation of PRC-005-1 R1. ReliabilityFirst determined that Buckeye Power, as a Generator Owner that owns a generation Protection System, did not include maintenance and testing intervals for current and voltage sensing devices in its Protection System maintenance and testing program, violating PRC-005-1 R1.1. Additionally, ReliabilityFirst determined that Buckeye Power’s Protection System maintenance and testing program did not have a summary of maintenance and testing procedures for current and voltage sensing devices, violating PRC-005-1 R1.2. This violation pertained to all of Buckeye Power’s 327 voltage and current sensing devices constituting 27.6% of Buckeye Power’s 1,186 total Protection System devices. | PRC-005-1 | R1 | High | Moderate | In considering the risk to the reliability of the bulk power system (BPS), ReliabilityFirst considered the fact that Buckeye Power did not have any redundant or back up protections in place for the current and voltage sensing devices. Buckeye Power was also unable to provide evidence of prior testing to demonstrate that the current and voltage sensing devices were fully functional and within specifications prior to the missed intervals. ReliabilityFirst considered this in light of the important function fulfilled by current and voltage sensing devices. Current and voltage sensing devices, specifically the current transformers and voltage transformers, provide electrical information directly to the relays regarding events and operations on the system. In order to detect a fault, the relays require accurate information from the current and voltage transformers as input. Without input from these devices, the relays would not have information necessary to react correctly (e.g., resulting in a failure to trip or a false trip by the relay). ReliabilityFirst considered this important function of current and voltage sensing devices in determining the risk to the reliability of the BPS resulting from Buckeye Power’s failure to test these devices. Buckeye Power continues to test these devices to confirm that all devices are currently fully functional and within specifications and will complete this testing on December 31, 2011. Buckeye Power has tested 61 of the 327 current and voltage sensing devices and has confirmed that those devices were fully functional and within specifications. ReliabilityFirst considered these limited results as mitigating the risk. ReliabilityFirst also considered that the risk was mitigated by the fact that Buckeye Power monitored its system throughout the duration of the violation and represents that no generating unit outage, equipment failure, or confirmation of any current and voltage sensing misoperation occurred. In light of the nature of the violation, offset by the aforementioned mitigating factors, ReliabilityFirst determined that this violation posed a moderate risk to the reliability of the BPS. | June 18, 2007, the date of mandatory compliance. | December 31, 2011, the date on which Buckeye Power will complete its maintenance and testing of current and voltage sensing devices. | $25,000 (for RFC201000654) | Compliance Audit | Buckeye Power added intervals and their basis with a summary of the requisite maintenance and testing procedures for its current and voltage sensing devices to its maintenance and testing program. Buckeye Power has agreed to complete the maintenance and testing of these devices by December 31, 2011. | 12/31/2011 (approved date) | TBD | Agrees and Stipulates to the Facts | ReliabilityFirst considered Buckeye Power’s established, formal program for internal compliance as a mitigating factor. The internal compliance program resides within Buckeye Power's Power Supply division and was widely disseminated to all individuals within this division through small workshops, training by consultants, e-mails, meetings and in person. The program was supervised by three senior staff members who report to the Chief Operating Officer, who reports to the Chief Executive Officer and President. Buckeye Power’s self-assessment of its internal compliance program resulted in expanding the scope of compliance activities to include more staff, including an additional consultant.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Dover, Ohio (Dover) | NCR08007 | RFC201000461 | Settlement Agreement | During a Compliance Audit conducted from June 14, 2010 to June 25, 2010, ReliabilityFirst found that Dover, as a DP, failed to have: (a) a maintenance and testing program ("Program") that included maintenance and testing intervals and the basis for those intervals for 100% of its 48 voltage and current sensing devices; and (b) a summary of maintenance and testing procedures for 100% of its 48 voltage and current sensing devices and 100% of its battery system, which consists of 60 individual cells. | PRC-005-1 | R1 | High | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that this violation posed a moderate risk to the reliability of the bulk power system (BPS). The risk was mitigated due to these factors: (a) Dover's Protection System relays, battery systems, and voltage and current sensing devices were inspected monthly; (b) Dover's substation and 30 of Dover's voltage and current sensing devices are monitored by the SCADA system and state estimator, neither of which has shown abnormal conditions with Dover's voltage and current sensing devices; (c) the substation is inspected at least monthly by Dover personnel; and (d) personnel from the entity with which Dover contracts performed visual inspections of all meters, potential indicating lights, and any alarm functions during the time period of the violation, and this personnel has not reported any problems. | June 27, 2007, date Dover registered with NERC Compliance Registry. | June 7, 2011, the date Dover revised its Program to include maintenance and testing intervals for its voltage and current sensing devices. | $10,000 (Settlement for RFC201000461) | Compliance Audit | Dover included, in its Program, a six year interval, and its basis, for its voltage and current sensing devices. Additionally, Dover acquired a summary of maintenance and testing procedures for its voltage and current sensing devices and batteries from the entity with which Dover contracts to perform maintenance and testing on its Protection System devices. | 2011-07-12 | 2011-08-03 | Agrees and Stipulates to the Facts | ReliabilityFirst considered certain aspects of Dover's internal compliance program as mitigating factors. For instance, Dover has an internal compliance program to develop and update policies and procedures in order to comply with Reliability Standards. Dover will modify the internal compliance program on an annual basis or more frequently if necessary. Dover distributes its internal compliance policies and procedures to its personnel. Dover also designated its Electric Generation Superintendent as its reliability officer.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Michigan Public Power Agency (MPPA) | NCR00822 | RFC200900219 | Settlement Agreement | During a Compliance Audit conducted from June 14, 2010 through June 25, 2010, MPPA did not submit documentation of a protection system maintenance and testing program for its member city, City of Holland Board of Public Works (Holland)’s 48th Street Peaking Station (48th Street Peaking Station). MPPA incorrectly believed, since its registration, that PRC-005-1 R1 was not applicable because MPPA incorrectly believed that 48th Street Peaking Station was not part of the bulk power system. As a result, MPPA did not assemble documentation of its protection system maintenance and testing program prior to the Compliance Audit. Specifically, MPPA did not produce a comprehensive document that included maintenance and testing intervals and their basis and a summary of maintenance and testing procedures for protection system devices. MPPA, as a GO, violated PRC-005-1 R1 by failing to produce sufficient documentation of a protection system maintenance and testing program for the 48th Street Peaking Station. | PRC-005-1 | R1 | High | High | ReliabilityFirst found that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because there are multiple protective relays and breakers between the 48th Street Peaking Station and Holland's interconnection at the Black River switching station, which is configured to minimize the risk to the BPS in the event of a possible failure at the 48th Street Peaking Station. In addition, MPPA represents that no relay malfunctions occurred at the 48th Street Peaking Station since the relays' installation, and all relays were found to be in good condition upon testing in 2008. | June 18, 2007, the date MPPA registered with NERC Compliance Registry. | May 26, 2010, the date MPPA adopted a documented protection system maintenance and testing program for the 48th Street Peaking Station. | $12,000 (for RFC200900219; RFC200900220; RFC200900221; and RFC200900222) | Compliance Audit | MPPA documented and adopted a protection system maintenance and testing program that included maintenance and testing intervals and their basis, and a summary of maintenance and testing procedures. | 2010-05-26 | 2011-09-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of MPPA's compliance program as mitigating factors in the penalty determination. For example, MPPA’s Compliance Manager and Senior Engineer meet with key member personnel on an annual basis. Additionally, MPPA holds workshops to advise both member and non-member cities on compliance issues. MPPA’s compliance program has the support and involvement of senior management, including MPPA’s General Manager. The Compliance Manager reports directly to the General Manager and the two are in regular and frequent contact. In addition, the Compliance Manager regularly attends meetings of the Board of Commissioners (MPPA’s governing body) and reports on the compliance program as part of the regular agenda. MPPA’s Compliance Policy requires ongoing internal auditing and monitoring of the implementation of its compliance program and MPPA has hired consultants to conduct audits. MPPA’s General Manager has issued guidelines indicating that lack of compliance with the statutory and regulatory standards will affect employee compensation and opportunities for promotion.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Michigan Public Power Agency (MPPA) | NCR00822 | RFC200900220 | Settlement Agreement | During the Compliance Audit, MPPA submitted maintenance and testing documentation to support the compliance of Holland’s Generators 7 and 8 with PRC-005-1, R2, for the test year 2008, but did not submit complete maintenance and testing documentation sufficient to meet ReliabilityFirst's satisfaction to support the compliance of Holland’s Generators 7 and 8 with PRC-005-1 R2 for the test year 2004. Holland’s Generators 7 and 8 are located at the 48th Street Peaking Station. ReliabilityFirst was unable to verify the timely completion of a four-year maintenance and testing interval for some of the protection system devices at Holland’s Generators 7 and 8, due to incomplete maintenance and testing documentation for test year 2004. Specifically, for Generator 7, which contains 20 relays, MPPA produced documentation of 2004 work orders but no documentation that MPPA tested relays in 2004. For Generator 8, which also contains 20 relays, MPPA produced documentation that it tested 15 relays in 2004. MPPA, as a GO, violated PRC-005-1 R2 by failing to provide sufficient evidence that all of the protection system devices at Holland's Generators 7 and 8 were tested within the defined intervals of its protection system maintenance and testing program. | PRC-005-1 | R2 | High | Severe | ReliabilityFirst found that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because there are multiple protective relays and breakers between the 48th Street peaking Station and Holland's interconnection at the Black River switching station, which is configured to minimize the risk to the BPS in the event of a possible failure at the 48th Street Peaking Station. In addition, MPPA represents that all relays at the 48th Street Peaking Station functioned and were in good condition upon testing in October 2008. MPPA represents that no relay malfunctions occurred at the 48th Street Peaking Station since the relays' installation. | June 18, 2007, the date MPPA registered with NERC Compliance Registry. | October 22, 2010, date MPPA completed maintenance and testing for the protection system devices at issue. | $12,000 (for RFC200900219; RFC200900220; RFC200900221; and RFC200900222) | Compliance Audit | MPPA maintained and tested the relays at issue in the alleged violation in October 2008. MPPA documented and adopted a protection system maintenance and testing program that included maintenance and testing intervals and their basis, and a summary of maintenance and testing procedures. MPPA confirmed that all maintenance and testing was current and in accordance with its protection system maintenance and testing program. | 2010-05-26 | 2011-09-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of MPPA's compliance program as mitigating factors in the penalty determination. For example, MPPA’s Compliance Manager and Senior Engineer meet with key member personnel on an annual basis. Additionally, MPPA holds workshops to advise both member and non-member cities on compliance issues. MPPA’s compliance program has the support and involvement of senior management, including MPPA’s General Manager. The Compliance Manager reports directly to the General Manager and the two are in regular and frequent contact. In addition, the Compliance Manager regularly attends meetings of the Board of Commissioners (MPPA’s governing body) and reports on the compliance program as part of the regular agenda. MPPA's Compliance Policy requires ongoing internal auditing and monitoring of the implementation of its compliance program and MPPA has hired consultants to conduct audits. MPPA’s General Manager has issued guidelines indicating that lack of compliance with the statutory and regulatory standards will affect employee compensation and opportunities for promotion.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Michigan Public Power Agency (MPPA) | NCR00822 | RFC200900221 | Settlement Agreement | MPPA did not have a documented facility ratings methodology for the 48th Street Peaking Station as it incorrectly believed that the 48th Street Peaking Station, part of Holland's generation system, was not part of the bulk power system. On May 1, 2009, MPPA submitted a documented Facilities Ratings Methodology to ReliabilityFirst, which was adopted on April 20, 2009. MPPA, as a GO, violated FAC-008-1 R1 by failing to have a documented Facility Ratings Methodology for the 48th Street Peaking Station. | FAC-008-1 | R1 | Medium | Severe | ReliabilityFirst found that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because MPPA represents that it did have facility ratings for the 48th Street Peaking Station, and upon development and application of the facility ratings methodology, MPPA confirmed that it had correctly identified the most limiting element in the facility ratings in place during the time period of the alleged violation. In addition, there are no instances since the installation of the 48th Street Peaking Station of thermal overloads or exceeding of established facility ratings. | June 18, 2007, the date MPPA registered with NERC Compliance Registry. | April 20, 2009, the date MPPA adopted a documented facility ratings methodology. | $12,000 (for RFC200900219; RFC200900220; RFC200900221; and RFC200900222) | Compliance Audit | MPPA adopted a facility ratings methodology and provided it to ReliabilityFirst. MPPA then retained a technical consultant to further enhance its facility ratings methodology to include more background information and descriptions and adopted the enhanced facility ratings methodology. | 2010-05-28 | 2011-09-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of MPPA's compliance program as mitigating factors in the penalty determination. For example, MPPA’s Compliance Manager and Senior Engineer meet with key member personnel on an annual basis. Additionally, MPPA holds workshops to advise both member and non-member cities on compliance issues. MPPA’s compliance program has the support and involvement of senior management, including MPPA’s General Manager. The Compliance Manager reports directly to the General Manager and the two are in regular and frequent contact. In addition, the Compliance Manager regularly attends meetings of the Board of Commissioners (MPPA’s governing body) and reports on the compliance program as part of the regular agenda. MPPA's Compliance Policy requires ongoing internal auditing and monitoring of the implementation of its compliance program and MPPA has hired consultants to conduct audits. MPPA’s General Manager has issued guidelines indicating that lack of compliance with the statutory and regulatory standards will affect employee compensation and opportunities for promotion.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Michigan Public Power Agency (MPPA) | NCR00822 | RFC200900222 | Settlement Agreement | During the Compliance Audit, ReliabilityFirst determined that the facility ratings for the 48th Street Peaking Station were not consistent with an associated facility ratings methodology because there was no facility ratings methodology. MPPA's compliance procedure mistakenly concluded that FAC-009-1 R1 was not applicable to Holland. MPPA, as a GO, violated the Standard by not establishing facility ratings that were consistent with an associated facility ratings methodology because MPPA did not provide a documented facility ratings methodology for the 48th Street Peaking Station until April 20, 2009. | FAC-009-1 | R1 | Medium | Severe | ReliabilityFirst found that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because upon development and application of its facility ratings methodology, MPPA confirmed that it had correctly identified the most limiting element in its facility ratings in place during the time period of the alleged violation. In addition, there were no instances since June 18, 2007 of thermal overloads or exceeding of established ratings at the 48th Street Peaking Station. | June 18, 2007, the date MPPA registered with NERC Compliance Registry. | June 9, 2011, the date MPPA provided documentation of facility ratings for the 48th Street Peaking Station consistent with its facility ratings methodology. | $12,000 (for RFC200900219; RFC200900220; RFC200900221; and RFC200900222) | Compliance Audit | MPAA submitted its facility ratings methodology to ReliabilityFirst and later retained a technical consultant, and enhanced its facility ratings documentation by including more background information and descriptions to ensure that it was consistent with its facility ratings methodology. | 2011-06-09 | 2011-09-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of MPPA's compliance program as mitigating factors in the penalty determination. For example, MPPA’s Compliance Manager and Senior Engineer meet with key member personnel on an annual basis. Additionally, MPPA holds workshops to advise both member and non-member cities on compliance issues. MPPA’s compliance program has the support and involvement of senior management, including MPPA’s General Manager. The Compliance Manager reports directly to the General Manager and the two are in regular and frequent contact. In addition, the Compliance Manager regularly attends meetings of the Board of Commissioners (MPPA’s governing body) and reports on the compliance program as part of the regular agenda. MPPA's Compliance Policy requires ongoing internal auditing and monitoring of the implementation of its compliance program and MPPA has hired consultants to conduct audits. MPPA’s General Manager has issued guidelines indicating that lack of compliance with the statutory and regulatory standards will affect employee compensation and opportunities for promotion.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Midland Cogeneration Venture, Limited Partnership (Midland) | NCR10282 | RFC201000673 | Settlement Agreement | During a compliance audit from October 18, 2010 through October 29, 2010, ReliabilityFirst determined that Midland, as a Generator Operator, failed to maintain the generator schedule as directed by its Transmission Operator ("TOP"). Midland's TOP set the voltage schedule for the relevant time period for 360 kV for the hours between 0700 and 2300, with a tolerance band of plus or minus 2 kV. On April 7, 2010, Midland's voltage failed to reach 360 kV, and failed to stay within the specified tolerance band (358 kV to 362 kV) for most of the hours between 0700 and 2300 because 75% of its generators were offline. Midland's voltage remained at approximately 357 kV during those hours. | VAR-002-1 | R2 | Medium | Lower | ReliabilityFirst found that due to the nature of the violation, offset by the mitigating factors, this violation posed a moderate risk to the reliability of the bulk power system (BPS). This risk was mitigated by the fact that Midland's voltage never dropped below 357 kV, which is above the nominal voltage of 345 kV. Midland monitored the electrical parameters of its generators, including the voltage and current. In addition, Midland's control system has alarming capability, and the alarms sound when voltage is 362 kV and above or 353 kV and below. Thus, the alarms did not sound. | April 7, 2010, the date Midland failed to maintain its voltage schedule. | April 7, 2010. | $40,000 (for RFC201000610, RFC201000611, RFC201000673, and RFC201000755) | Compliance Audit | Midland worked with its TOP to put in place a voltage schedule that takes into account that Midland's generation operations. Midland's TOP implemented a revised temporary voltage schedule until it completes a study regarding Midland. Midland also provided its operators with mandatory communication requirements regarding reporting its inability to meet its voltage schedule. In addition, Midland trained its personnel regarding the voltage schedule and implemented internal auditing for compliance with VAR-002. | 2011-01-03 | 2011-02-16 | Neither Admits nor Denies | ReliabilityFirst considered as a mitigating factor that Midland self-reported two of the violations in this Agreement; however, ReliabilityFirst also considered that it discovered two of the violations at a Compliance Audit and did not provide mitigating credit for those violations. ReliabilityFirst considered certain aspects of Midland's internal compliance program as a mitigating factor. Midland distributes its compliance program throughout the organization, and the individuals with responsibility for compliance have access to the Chief Executive Officer. The Vice President and the General Counsel & Corporate Secretary oversee all regulatory compliance activities, and Midland expects all employees to identify potential noncompliance. Compliance program staff attends regional and national reliability seminars. In addition, Midland utilizes contractors to develop and manage its compliance program as well as to conduct compliance-based training. In addition, as part of its ongoing effort to enhance its operations and compliance with Reliability Standards, Midland began replacing the gas turbine AVRs on each generating unit. The new AVRs will provide better voltage control and provide real-time information to operators if any issues arise. While Midland was previously only able to observe the alarms on the former AVRs at the individual units, the new AVRs will also alarm directly to the central control room.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Midland Cogeneration Venture, Limited Partnership (Midland) | NCR10283 | RFC201000610 | Settlement Agreement | On September 3, 2010, Midland self-reported VAR-002-1, R3 to ReliabilityFirst. Midland, as a Generator Operator, failed to notify its Transmission Operator ("TOP") of a status change on its generator Reactive Power resource, specifically the status of the Automatic Voltage Regulator (AVR) on its generating Unit 14. Upon learning of issues regarding voltage control, Midland discovered that the AVR hardware on its generating Unit 14 failed, and as a result, Unit 14 was operating in manual mode. Midland had not adequately trained its operators to recognize when the voltage regulator was operating in manual mode or to report generating unit status changes. ReliabilityFirst dismissed a potential violation on June 16, 2011 as Midland had not anticipated the status change of the AVR on its generating Unit 14. | VAR-002-1 | R3 | Medium | Severe | ReliabilityFirst found that due to the nature of the violation, offset by the mitigating factors, this violation posed a moderate risk to the reliability of the bulk power system (BPS). The risk was mitigated by the fact that this violation affected only one of Midland's 15 generators. Midland eventually notified its TOP of the AVR failure and replaced the failed AVR. Midland continuously monitors the electrical parameters of its generators, including the voltage and current, which initially alerted Midland to the voltage control problems on Unit 14. Midland's operators perform local AVR status checks every four hours during normal generator operations and make necessary voltage adjustments, including during the time period of the violation. During the violation, Midland maintained its voltage schedule. Furthermore, if necessary, Midland could have compensated for the loss of Unit 14 because other generators at Midland's facility were operational at the time of the violation. | June 4, 2010, the date the AVR at Unit 14 failed. | September 3, 2010, the date Midland notified its TOP of the status change. | $40,000 (for RFC201000610, RFC201000611, RFC201000673, and RFC201000755) | Self-Report | Midland notified its TOP of the outage and provided all necessary information and dates surrounding the AVR outage to the TOP. Midland trained its maintenance, engineering and operations personnel regarding AVR status and outage reporting requirements. Control room operators were given the NERC required AVR outage reporting requirements. Midland's operator logs now demonstrate that AVR status is confirmed every four hours. Training was completed to strengthen Midland's culture of compliance, including topics on the awareness and the purpose of NERC and Reliability Standards, at an all-employee meeting. In addition, Midland will conduct periodic internal audits as well as audits completed by contractors to ensure compliance with AVR requirements. | 2010-12-03 | 2011-02-18 | Neither Admits nor Denies | ReliabilityFirst considered as a mitigating factor that Midland self-reported two of the violations in this Agreement; however, ReliabilityFirst also considered that it discovered two of the violations at a Compliance Audit and did not provide mitigating credit for those violations. ReliabilityFirst considered certain aspects of Midland's internal compliance program as a mitigating factor. Midland distributes its compliance program throughout the organization, and the individuals with responsibility for compliance have access to the Chief Executive Officer. The Vice President and the General Counsel & Corporate Secretary oversee all regulatory compliance activities, and Midland expects all employees to identify potential noncompliance. Compliance program staff attends regional and national reliability seminars. In addition, Midland utilizes contractors to develop and manage its compliance program as well as to conduct compliance-based training. In addition, as part of its ongoing effort to enhance its operations and compliance with Reliability Standards, Midland began replacing the gas turbine AVRs on each generating unit. The new AVRs will provide better voltage control and provide real-time information to operators if any issues arise. While Midland was previously only able to observe the alarms on the former AVRs at the individual units, the new AVRs will also alarm directly to the central control room.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Midland Cogeneration Venture, Limited Partnership (Midland) | NCR10284 | RFC201000755 | Settlement Agreement | During a compliance audit from October 18, 2010 through October 29, 2010, ReliabilityFirst determined that Midland, as a Generator Owner that owns a generation Protection System, had a deficient generation Protection System maintenance and testing program. In Midland's Protection System maintenance and testing program prior to August 30, 2010, Midland failed to include maintenance and testing intervals and their basis for all Protection System devices that affect the reliability of the bulk power system (BPS). Midland also failed to include a summary of maintenance and testing procedures. Midland's revised Protection System maintenance and testing program, dated August 30, 2010 (August 30, 2010 Program) failed to include maintenance and testing intervals and their basis for communications systems, voltage and current sensing devices, batteries, and DC control circuitry. Furthermore, the August 30, 2010 Program failed to include a summary of maintenance and testing procedures for communications systems, voltage and current sensing devices, batteries, and DC control circuitry. This violation implicated all of Midland's 1,284 generation Protection System devices. | PRC-005-1 | R1 | High | Severe | ReliabilityFirst found that due to the nature of the violation, offset by the mitigating factors, this violation posed a moderate risk to the reliability of the bulk power system (BPS). The risk was mitigated by the fact that despite a deficient Protection System maintenance and testing program, Midland only failed to test 5.8% of its Protection System devices. In addition, Midland has in place a backup Protection System for all protected generation equipment. In addition the Unit 1 generator and both of Midland's transmission/interconnection lines have redundant protection. All primary, backup and redundant Protection Systems alarm to the control room. Furthermore, Midland's facility has alarms in place to alert plant personnel of the failure of sensing devices and station batteries. These alarms did not sound during the time period of the violation. Midland also completed regular visual inspections on all Protection System devices. | December 9, 2008, the date Midland was required to comply with the Standard. | March 30, 2011, the date Midland revised its Protection System maintenance and testing program. | $40,000 (for RFC201000610, RFC201000611, RFC201000673, and RFC201000755) | Compliance Audit | Midland developed a revised Protection System maintenance and testing program that addressed the deficiencies of the August 30, 2010 Program. Additions included maintenance and testing intervals and their basis for communications systems, voltage and current sensing devices, batteries and DC control circuitry. Furthermore, a summary of maintenance and testing procedures for communications systems, voltage and current sensing devices, batteries and DC control circuitry was included in the revised document dated December 3, 2010. During the ReliabilityFirst review of the evidence of Mitigation Plan completion, ReliabilityFirst discovered that due to a misunderstanding of the ReliabilityFirst definition of the bulk power system (BPS), 16 relays were not included in Midland’s document. Midland provided a revision of its Protection System device summary table for relays dated March 30, 2011, that included the 16 relays previously omitted. Even though these relays had not previously been included in Midland’s formal Protection System maintenance and testing program, ReliabilityFirst reviewed the dates the 16 relays were last tested and maintained and found they were within the defined interval. Midland missed its original mitigation completion date due to this misunderstanding of the BPS definition. | 2011-03-30 | 2011-05-26 | Neither Admits nor Denies | ReliabilityFirst considered as a mitigating factor that Midland self-reported two of the violations in this Agreement; however, ReliabilityFirst also considered that it discovered two of the violations at a Compliance Audit and did not provide mitigating credit for those violations. ReliabilityFirst considered certain aspects of Midland's internal compliance program as a mitigating factor. Midland distributes its compliance program throughout the organization, and the individuals with responsibility for compliance have access to the Chief Executive Officer. The Vice President and the General Counsel & Corporate Secretary oversee all regulatory compliance activities, and Midland expects all employees to identify potential noncompliance. Compliance program staff attends regional and national reliability seminars. In addition, Midland utilizes contractors to develop and manage its compliance program as well as to conduct compliance-based training. In addition, as part of its ongoing effort to enhance its operations and compliance with Reliability Standards, Midland began replacing the gas turbine AVRs on each generating unit. The new AVRs will provide better voltage control and provide real-time information to operators if any issues arise. While Midland was previously only able to observe the alarms on the former AVRs at the individual units, the new AVRs will also alarm directly to the central control room.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Midland Cogeneration Venture, Limited Partnership (Midland) | NCR10285 | RFC201000611 | Settlement Agreement | On September 3, 2010, Midland self-reported PRC-005-1 R2 to ReliabilityFirst. Midland, as a Generator Owner that owns a generation Protection System, failed to have complete documentation regarding the maintenance and testing of a number of its protective relays. Specifically, Midland failed to provide evidence that it performed maintenance and testing on 75 of its 479 (15.7%) protective relays within their defined intervals, which constitutes 5.8% of its 1,284 generation Protection System devices. Furthermore, Midland failed to provide the date it last maintained and tested its protective relays. | PRC-005-1 | R2 | High | Lower | ReliabilityFirst found that due to the nature of the violation, offset by the mitigating factors, this violation posed a moderate risk to the reliability of the bulk power system (BPS). The risk was mitigated by the fact that although Midland provided no prior interval testing evidence, after Midland discovered the violation, it tested all Protection System devices and found them all to be functional; however, ten of the protective relays were out of calibration. These protective relays did not jeopardize any equipment because they were more sensitive to certain fault conditions. Due to the miscalibration of the protective relays, the zone of protection extended further from the Midland facility than designed, resulting in a reported Misoperation on February 12, 2009. Midland implemented a corrective action plan whereby it repaired and recalibrated the relay on March 31, 2009. Additionally, Midland has in place a backup Protection System for all protected generation equipment. In addition, the Unit I generator and both of Midland's transmission/interconnection lines have redundant protection as well. Furthermore, all primary, backup, and redundant Protection Systems alarm to the control room. Midland's facility has alarms in place to alert plant personnel of the failure of sensing devices and station batteries. These alarms did not sound throughout the duration of the violation. Furthermore, Midland's facility has alarms in place to alert plant personnel if sensing devices and station batteries failed. Midland also completed regular visual inspections of all generation Protection System devices. | December 9, 2008, the date Midland was required to comply with the Standard. | April 11, 2011, the date Midland completed testing of all relevant generation Protection System devices. | $40,000 (for RFC201000610, RFC201000611, RFC201000673, and RFC201000755) | Self-Report | Midland tested all 75 relay devices for which it lacked evidence of testing and provided the date last tested and maintained. 71 relays were last tested and maintained by February 27, 2010. Even though Midland’s list of protection relays indicated the last date that the remaining four relays were tested/maintained and that the relays had returned to compliance by September 9, 2009, Midland could not locate the corresponding test records. Therefore, Midland tested the relays and provided documents to show that the maintenance and testing for four relays was performed on April 11, 2011. Midland also developed a revised Protection System maintenance and testing program to ensure clarity and compliance as explained in its Mitigation Plan actions for PRC-005-1 R1. | 2011-04-11 | 2011-04-12 | Neither Admits nor Denies | ReliabilityFirst considered as a mitigating factor that Midland self-reported two of the violations in this Agreement; however, ReliabilityFirst also considered that it discovered two of the violations at a Compliance Audit and did not provide mitigating credit for those violations. ReliabilityFirst considered certain aspects of Midland's internal compliance program as a mitigating factor. Midland distributes its compliance program throughout the organization, and the individuals with responsibility for compliance have access to the Chief Executive Officer. The Vice President and the General Counsel & Corporate Secretary oversee all regulatory compliance activities, and Midland expects all employees to identify potential noncompliance. Compliance program staff attends regional and national reliability seminars. In addition, Midland utilizes contractors to develop and manage its compliance program as well as to conduct compliance-based training. In addition, as part of its ongoing effort to enhance its operations and compliance with Reliability Standards, Midland began replacing the gas turbine AVRs on each generating unit. The new AVRs will provide better voltage control and provide real-time information to operators if any issues arise. While Midland was previously only able to observe the alarms on the former AVRs at the individual units, the new AVRs will also alarm directly to the central control room.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC201000669 | Settlement Agreement | On October 29, 2010, Morgantown self-certified its noncompliance with VAR-002-1 R1. ReliabilityFirst determined that Morgantown, as a Generator Operator (GOP), did not operate the automatic voltage regulator in automatic voltage control mode, as required by the Standard, instead operating the automatic voltage regulator in power factor mode as a normal mode of operations. | VAR-002-1 | R1 | Medium | Severe | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because while the generator may not have been operating in automatic voltage mode, Morgantown was operating the generator in the automatic power factor control mode. In addition, Morgantown monitored its voltage and facility limits at all times. Furthermore, Morgantown has a single 138 kV connection to the BPS and is a minimal power productive entity of only 50 MW. | 2007-08-02 | 2010-09-06 | $15,000 (for RFC201000669, RFC201000670 and RFC201100781) | Self-Certification | Morgantown mitigated the issue by issuing standing orders to its operating personnel to notify its TOP of any changes in the operating status of its automatic voltage regulator and at any time it cannot maintain the TOP's prescribed voltage schedule. In addition, Morgantown trained its personnel on the new standing orders and generally on the Standard. | 2010-10-21 | 2011-03-09 | Neither Admits nor Denies | ReliabilityFirst considered Morgantown's internal compliance program (ICP) as a mitigating factor in assessing the penalty. Morgantown's ICP addresses NERC standards and requirements applicable to GOs and GOPs, describes how compliance with these requirements is met, and references external documents. The ICP is supplemented with a corporate reliability policy, an assessment program, and a group dedicated to compliance.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC201000670 | Settlement Agreement | On October 29, 2010, Morgantown self-certified its noncompliance with VAR-002-1 R2. ReliabilityFirst determined that Morgantown, as a GOP, during periods of low system voltage, could not maintain the voltage schedule prescribed by its Transmission Operator as required by the Standard. Morgantown failed to contact its Transmission Operator (TOP) during these periods and was therefore not exempt from following the voltage schedule. | VAR-002-1 | R2 | Medium | Severe | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because while the generator may not have been operating in automatic voltage mode, Morgantown was operating the generator in the automatic power factor control mode. In addition, Morgantown monitored its voltage and facility limits at all times. Furthermore, Morgantown has a single 138 kV connection to the BPS and is a minimal power productive entity of only 50 MW. | 2007-08-02 | 2010-09-06 | $15,000 (for RFC201000669, RFC201000670 and RFC201100781) | Self-Certification | Morgantown mitigated the issue by issuing standing orders to its operating personnel to notify its TOP of any changes in the operating status of its automatic voltage regulator and at any time it cannot maintain the TOP's prescribed voltage schedule. In addition, Morgantown trained its personnel on the new standing orders and generally on the Standard. | 2010-10-21 | 2011-03-09 | Neither Admits nor Denies | ReliabilityFirst considered Morgantown's ICP as a mitigating factor in assessing the penalty. Morgantown's ICP addresses NERC standards and requirements applicable to GOs and GOPs, describes how compliance with these requirements is met, and references external documents. The ICP is supplemented with a corporate reliability policy, an assessment program, and a group dedicated to compliance.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Morgantown Energy Associates (Morgantown) | NCR00834 | RFC201100781 | Settlement Agreement | On February 28, 2011, Morgantown self-reported a violation of PRC-005-1 R1 and R2. ReliabilityFirst determined that Morgantown, as a Generator Owner, failed to document a Protection System maintenance and testing program for its batteries. Specifically, Morgantown failed to define maintenance and testing intervals and their basis for its batteries. This involved a total of four battery banks, less than one percent of Morgantown's 504 Protection System devices in 2007 and 2008. ReliabilityFirst determined that the facts implicated only PRC-005-1 R1 because Morgantown had documented implementation of its maintenance and testing program, pursuant to PRC-005-1 R2, but that program was deficient. | PRC-005-1 | R1 | High | Low | ReliabilityFirst determined that this violation did not pose a serious or substantial risk to the bulk power system (BPS) because Morgantown implemented redundant protections. Specifically, Morgantown's primary source of direct current power is two 100% capacity battery chargers, one of which in service with the other in automatic standby mode. Each battery charger is powered from different motor control centers, with each motor control center supplied by a different power source. The battery chargers and batteries are continuously monitored. Morgantown also conducted routine battery surveillance in 2006, as well as battery load test in August of 2006. Data is available beginning December 1, 2008 for routine battery surveillance with satisfactory results. Additionally, Morgantown tested other Protection System devices during the identified period of missing battery data and determined that no misoperations occurred during the missed testing interval period. | June 25, 2007(the date Qualifying Facilities were responsible to comply with the Reliability Standards) | 2008-11-14 | $15,000 (for RFC201000669, RFC201000670 and RFC201100781) | Self-Report | On April 1, 2011, Morgantown submitted a mitigation plan addressing this violation. In this mitigation plan, Morgantown memorialized the actions it took to mitigate this violation by enhancing Protection System program document with descriptions of battery maintenance specifications. In November of 2008, Morgantown began to follow its new program for battery testing and by November 14, 2008, Morgantown completed all relevant testing. | 2008-11-14 | 2011-06-09 | Neither Admits nor Denies | ReliabilityFirst considered Morgantown's ICP as a mitigating factor in assessing the penalty. Morgantown's ICP addresses NERC standards and requirements applicable to GOs and GOPs, describes how compliance with these requirements is met, and references external documents. The ICP is supplemented with a corporate reliability policy, an assessment program, and a group dedicated to compliance. In addition, ReliabilityFirst considered Morgantown's Self Report of the PRC-005-1 R1 to be a mitigating factor.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Ohio Valley Electric Corporation (OVEC) | NCR00857 | RFC201000301 | Settlement Agreement | On March 30, 2010, OVEC, as a Generator Operator, submitted a Self-Report dated March 29, 2010 to ReliabilityFirst for a violation of VAR-002-1.1a R3. During a compliance audit from June 8, 2010 through June 11, 2010, ReliabilityFirst reviewed the Self-Report and concluded that OVEC failed to notify its Transmission Operator that it operated one of its generators in manual mode. In the Self-Report, OVEC stated that on October 18, 2009, OVEC's Clifty Creek Unit No. 6 generator (Unit No. 6) returned to service after being offline for a tube leak. The Automatic Voltage Regulator (AVR) was not in service at the time OVEC returned Unit No. 6 to service. Therefore OVEC operated Unit No. 6 in manual mode, rather than in automatic voltage control mode. OVEC did not notify the Transmission Operator of this occurrence until two hours and thirty minutes after OVEC operated Unit No. 6 in manual mode. ReliabilityFirst found that OVEC violated VAR-002-1.1a R1 by failing to notify the Transmission Operator of the operation of a generator connected to the interconnected transmission system in manual voltage control mode. | VAR-002-1.1a | R1 | Medium | Lower | ReliabilityFirst determined that this violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Unit No. 6 is located at a generating station which contains five other generators of similar capacity and vintage. The remaining five generators had their AVRs in service and were maintaining voltage during the period of the violation, which would compensate for any voltage variations during this period. Additionally, OVEC manually controlled the voltage on Unit No. 6, adhering to all issued voltage schedules during the time period of the violation. | 2009-10-18 | 2009-10-18 | $15,000 (for RFC201000301 and RFC201000320) | Self-Report | On September 21, 2010, OVEC submitted a Mitigation Plan to ReliabilityFirst addressing the violation of VAR-002-1.1a R1. In this plan, OVEC memorialized the actions it took to address the violation of VAR-002-1.1a R1. OVEC installed monitoring points to monitor the AVR status of its generators via the OVEC SCADA system. Monitoring points are now located on every AVR on each generator. The OVEC SCADA system alarms upon any change in AVR status, thus notifying the system operator immediately. | 2010-05-17 | 2010-11-23 | Admits | ReliabilityFirst considered OVEC's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Ohio Valley Electric Corporation (OVEC) | NCR00857 | RFC201000320 | Settlement Agreement | On April 9, 2010, OVEC, as a Balancing Authority and Transmission Operator, self-reported to ReliabilityFirst a possible violation of COM-002-2 R2. OVEC identified an event that occurred on February 1, 2010, during which OVEC issued a directive regarding a switching operation to remove the 345 kV circuit breaker "F" at the Kyger Creek Substation. During this event, OVEC did not ensure that the recipient of the directive repeated the information back correctly. ReliabilityFirst found that OVEC violated COM-002-2 R2 by failing to ensure the recipient of the directive repeated the information back correctly. | COM-002-2 | R2 | Medium | High | ReliabilityFirst determined that this violation posed a moderate risk did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Prior to the occurrence of the violation, OVEC created procedures to ensure the appropriate issuance of directives, provided proper training to employees on the use of these procedures, and routinely reviewed recordings to verify that the procedures are followed. Therefore, OVEC had procedures in place for the use of three-part communications and this violation did not evidence a systemic problem, but rather, an isolated incident. Furthermore, the recipient of the directive completed the switching operation successfully, and the circuit breaker on which the switching was performed resides in a substation that contains six breaker bays. In the event that OVEC had taken one breaker out of service due to an unclear directive, the redundant bus ties and breaker bay configuration would have minimized the impact on the BPS. | 2010-02-01 | 2010-02-01 | $15,000 (for RFC201000301 and RFC201000320) | Self-Report | On May 19, 2010, OVEC submitted a Mitigation Plan to ReliabilityFirst addressing the violation of COM-002-2 R2. In this plan, OVEC memorialized the actions it took to address the violation of COM-002-2 R2. OVEC refreshed the training of all system operators and field switching personnel, to reinforce the principles and importance of three-part communications. OVEC also committed to providing refresher training on three-part communications on a periodic basis. | 2010-07-30 | 2010-08-12 | Admits | ReliabilityFirst considered OVEC's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Panda Brandywine LP (Panda) | NCR00866 | RFC201000640 | Settlement Agreement | During a compliance audit of Panda from September 13, 2010 through September 28, 2010 (Audit), ReliabilityFirst determined that Panda, as a Generator Owner that owns a generation Protection System, did not include maintenance and testing intervals and their basis or a summary of maintenance and testing procedures for any of Panda's 15 DC control circuits in its Protection System maintenance and testing program (Program). | PRC-005-1 | R1 | High | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Panda visually inspected, on a daily basis, all DC control circuits that are not enclosed within other equipment, and identified no issues. (Approximately 40% of Panda's DC control circuits are not enclosed within other equipment.) Panda's daily visual inspections included an inspection of the lock-out relays associated with the DC control circuits. Additionally, Panda identified no issues upon the full testing of all the DC control circuits and determined that the DC control circuits were in excellent working order. | 2007-06-18 | 2010-11-23 | $50,000 (for RFC201000640, RFC201000641, RFC201000642, and RFC201000644) | Compliance Audit | On November 11, 2010, Panda submitted to ReliabilityFirst its mitigation plan to address the violation of PRC-005-1 R1. Panda amended its Program to include maintenance and testing intervals and their basis and a summary of maintenance and testing procedures for its DC control circuits. Panda also maintained and tested its DC control circuits. | 2010-11-23 | 2011-05-05 | Admits | ReliabilityFirst considered as a mitigating factor certain aspects of Panda's compliance program. For instance, Panda reviews and modifies its internal compliance program as necessary and performs assessments of compliance activities through the use of independent third parties specializing in NERC compliance. Panda's internal compliance program is supervised by Panda's General Manager, who also has direct access to the CEO of Panda's parent company, Panda Energy Corporation. Panda, its parent company Panda Energy Corporation, and its affiliated companies have no prior violations of the Reliability Standards. As a result, this violation does not constitute a repetitive infraction.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Panda Brandywine LP (Panda) | NCR00866 | RFC201000641 | Settlement Agreement | During a compliance audit of Panda from September 13, 2010 through September 28, 2010, ReliabilityFirst determined that Panda, as a Generator Owner that owns a generation Protection System, could not provide evidence that it maintained and tested its voltage and current sensing devices within the defined intervals of its Protection System maintenance and testing program. Specifically, Panda failed to test any of its 149 voltage and current sensing devices since 1996, and therefore missed its seven-year maintenance and testing intervals for voltage and current sensing devices. Panda represents that it misinterpreted PRC-005-1 R2.1's requirement to maintain and test its voltage and current sensing devices within defined intervals. Specifically, Panda believed that the calculation of the defined intervals for its voltage and current sensing devices began on the first day of mandatory compliance. As a result of this misinterpretation, Panda believed it was required to maintain and test its voltage and current sensing devices any time prior to June 18, 2014. | PRC-005-1 | R2.1 | High | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Panda visually inspected, on a daily basis, all voltage sensing devices that are not enclosed within other equipment, and verified that those voltage sensing devices were in excellent working condition. Approximately 50% of Panda's voltage sensing devices are not enclosed within other equipment. Panda's current sensing devices are enclosed in circuit breaker bushings or other equipment, which prevents daily visual inspection. Panda's voltage sensing devices have alarms that alert Panda to any abnormal conditions, and these alarms did not sound during the time period of the violation. Additionally, Panda identified no issues upon testing all voltage and current sensing devices in November 2010, and confirmed that all voltage and current sensing devices were in excellent working condition. | 2007-06-18 | 2010-11-19 | $50,000 (for RFC201000640, RFC201000641, RFC201000642, and RFC201000644) | Compliance Audit | On November 11, 2010, Panda submitted to ReliabilityFirst its mitigation plan to address the violation of PRC-005-1 R2.1. Panda maintained and tested its voltage and current sensing devices. In addition, Panda developed a document that will reference and track the maintenance and testing of voltage and current sensing devices. | 2010-11-19 | 2011-05-06 | Admits | ReliabilityFirst considered as a mitigating factor certain aspects of Panda's compliance program. For instance, Panda reviews and modifies its internal compliance program as necessary and performs assessments of compliance activities through the use of independent third parties specializing in NERC compliance. Panda's internal compliance program is supervised by Panda's General Manager, who also has direct access to the CEO of Panda's parent company, Panda Energy Corporation. Panda, its parent company Panda Energy Corporation, and its affiliated companies have no prior violations of the Reliability Standards. As a result, this violation does not constitute a repetitive infraction.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Panda Brandywine LP (Panda) | NCR00866 | RFC201000642 | Settlement Agreement | During a compliance audit of Panda from September 13, 2010 through September 28, 2010, ReliabilityFirst discovered a violation of PRC-001-1 R1. Panda, as a Generator Operator (GOP), failed to provide sufficient evidence to demonstrate that operations personnel were familiar with the purpose and limitations of protection system schemes applied in Panda's area. | PRC-001-1 | R1 | High | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Panda's training program did train its operations personnel on the fundamental aspects of electrical components, switching, and electrical systems, including the fundamental aspects of relay protection systems. Panda represents that it provided information to its operations personnel on the relay protection system schemes specific to the Panda facility via on the job training. | 2/25/2008 (GOP registration date) | 2010-12-15 | $50,000 (for RFC201000640, RFC201000641, RFC201000642, and RFC201000644) | Compliance Audit | On November 11, 2010, Panda submitted to ReliabilityFirst its mitigation plan to address the violation of PRC-001-1 R1. Panda amended its training program for operations personnel to include information on the relay protection system schemes specific to the Panda facility. Panda documented and maintained records for all employees who successfully completed the training program. | 2010-12-15 | 2011-05-06 | Admits | ReliabilityFirst considered as a mitigating factor certain aspects of Panda's compliance program. For instance, Panda reviews and modifies its internal compliance program as necessary and performs assessments of compliance activities through the use of independent third parties specializing in NERC compliance. Panda's internal compliance program is supervised by Panda's General Manager, who also has direct access to the CEO of Panda's parent company, Panda Energy Corporation. Panda, its parent company Panda Energy Corporation, and its affiliated companies have no prior violations of the Reliability Standards. As a result, this violation does not constitute a repetitive infraction.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Panda Brandywine LP (Panda) | NCR00866 | RFC201000644 | Settlement Agreement | During a compliance audit of Panda from September 13, 2010 through September 28, 2010, ReliabilityFirst determined that Panda, as a Generator Operator (GOP), failed to maintain its voltage within its Transmission Operator's voltage schedule. PJM Interconnection, LLC (PJM) is Panda's Transmission Operator. PJM Manual 03, which was publicly posted on the PJM website, provided a default voltage schedule of 235 with a bandwidth of +/- 4.0, which governed Panda. Although, Panda was required to follow this default voltage schedule, Panda operated outside PJM's voltage schedule without first receiving an exemption on several occasions. Specifically, Panda exceeded the high limit of 239 kV of the default voltage schedule on July 15, 2010, July 21, 2010, August 5, 2010 and August 31, 2010. On July 15, 2010, Panda operated at approximately 240 kV for one hour and forty eight minutes. On July 21, 2010, Panda operated between 241 kV and 240 kV for approximately two hours and thirty minutes. On August 5, 2010, Panda operated slightly above 239 kV for approximately twenty four minutes. On August 13, 2010, Panda operated between 239 kV and 241 kV for approximately one hour. | VAR-002-1.1a | R2 | Medium | Severe | ReliabilityFirst determined that this violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Panda operated in accordance with a power purchase agreement and Interconnection agreement with its Transmission Owner, which required Panda to maintain a nominal voltage of 230 kV, with reasonable variation of frequency and voltage consistent with prudent utility practices. Panda worked with its Transmission Owner and received a custom voltage schedule with an increased bandwidth that was consistent with Panda's historical operating practices. The Automatic Voltage Regulators at the Panda facility were in automatic mode at all times, and Panda continuously monitored voltage, amps, frequency, and real and Reactive Power at the Panda facility. | 2/25/2008 (GOP registration date) | 2010-12-15 | $50,000 (for RFC201000640, RFC201000641, RFC201000642, and RFC201000644) | Compliance Audit | On January 26, 2011, Panda submitted to ReliabilityFirst its mitigation plan to address the violation of VAR-002-1.1a R1. In this mitigation plan, Panda validated the accuracy of its voltage readings, and set up automated alarming to ensure that its voltage does not exceed scheduled limits. Additionally, Panda received a custom voltage schedule from the Transmission Owner and began operating in accordance with that voltage schedule. | 2010-12-15 | 2011-04-14 | Admits | ReliabilityFirst considered as a mitigating factor certain aspects of Panda's compliance program. For instance, Panda reviews and modifies its internal compliance program as necessary and performs assessments of compliance activities through the use of independent third parties specializing in NERC compliance. Panda's internal compliance program is supervised by Panda's General Manager, who also has direct access to the CEO of Panda's parent company, Panda Energy Corporation. Panda, its parent company Panda Energy Corporation, and its affiliated companies have no prior violations of the Reliability Standards. As a result, this violation does not constitute a repetitive infraction.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Troy Energy LLC (Troy Energy) | NCR00337 | RFC201100723 | Settlement Agreement | On January 7, 2011, Troy Energy, as a Generator Owner ("GO"), submitted a self-report to ReliabilityFirst identifying a possible violation of PRC-005-1, R2.1. Troy Energy reported that it failed to perform monthly battery maintenance and testing program ("Program") for the month of December, 2010, and that it failed to perform quarterly battery maintenance within the defined intervals of its Program for the fourth quarter of 2010. Specifically, on December 29, 2010, Troy Energy's general counsel received a letter from a Troy Energy employee alleging a possible violation of PRC-005-1 at the Troy Energy facility. In the letter, the Troy Energy employee alleged that the monthly and quarterly battery maintenance records at the Troy Energy facility were inaccurate and battery maintenance occurred outside the defined intervals of Troy Energy's Program. Troy Energy immediately initiated an internal investigation into the allegations, reviewed its records, interviewed all employees and examined its computer systems. Upon its completion of the internal investigation on January 5, 2011, Troy Energy concluded that, consistent with the employee's allegations, Troy Energy did not perform its December 2010 monthly battery maintenance until January 3, 2011. Troy Energy came to this conclusion even though its records stated that this monthly battery maintenance had occurred on December 14, 2010. Troy Energy also concluded that it failed to perform quarterly battery maintenance for the fourth quarter of 2010. | PRC-005-1 | R2.1 | High | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system ("BPS"). The risk to the reliability of the BPS was reduced, impart due to the duration. Troy Energy missed its monthly and quarterly battery maintenance intervals by only three and six days, respectively. Additionally, Troy Energy has alarms associated with its batteries to notify its operators of ground faults, low voltage, or charger problems. These alarms did not sound during the time period of the violation. Troy Energy's facility was not called into service and its generators did not operate during the time period of the alleged violation. Troy Energy's subsequent late battery maintenance did not reveal any abnormal conditions. | January 1, 2011, the date by which Troy Energy should have completed its monthly and quarterly battery maintenance. | January 6, 2011, the date Troy Energy completed its quarterly battery maintenance. | $10,000 (for RFC201100723) | Self-Report | Troy Energy conducted all deficient monthly and quarterly battery maintenance on January 3, 2011 and January 6, 2011, respectively. As a disciplinary action, Troy Energy removed the plant manager who was responsible during the time period of the alleged violation from his position as well as the responsible employee. The President of International Power America, Inc. was personally involved in the decision to remove the plant manager and the responsible employee from their duties. Additionally, Troy Energy now requires the Director of Compliance to personally review the evidence of completion for all Reliability Standard related tasks, including battery maintenance records, on the 21" day of each month. Troy Energy also conducted additional training emphasizing the importance of the Reliability Standards and the need to perform all required maintenance within the defined intervals of its Program. | 2011-01-18 | 2011-05-12 | Agrees and Stipulates | ReliabilityFirst considered certain aspects of Troy Energy's compliance program as mitigating factors. For instance, Troy Energy reviews all internal compliance procedures and practices annually. Troy Energy's Director of Corporate Services has direct access to the CEO of International Power America, Inc. International Power America, Inc. serves Troy Energy as a professional resource for internal assessment program modeling which include compliance driven audits and spot checks. When assessing the penalty for the alleged violation at issue, ReliabilityFirst considered Troy Energy's violation history. Troy Energy has a prior violation of PRC-005-1, R2.1. Additionally, Troy Energy's affiliate company, Armstrong Energy Limited Partnership, LLLP, (Armstrong Energy) has a violation of PRC-005-1, R1. As a result of these findings, ReliabilityFirst considered the violation as a repetitive infraction and the infraction an aggravating factor.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP200900131 | Settlement Agreement | During an August 10, 2009 through August 11, 2009 on-site compliance audit, SPP RE determined that Lubbock, as a Transmission Owner (TO), did not have documentation of facility connection requirements for prospective generation, transmission, and end user facilities. | FAC-001-0 | R1, R1.1, R1.2, R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Lubbock is a full requirements customer of the Southwestern Public Service Company (SPS). Lubbock’s full requirements contract with SPS includes contractual obligations that would cause Lubbock to fully vet any proposed connection to its 230 kV system with SPS. Additionally, the function and physical make-up of Lubbock’s 230 kV facilities limits the potential for any possible interconnections. Lubbock owns only 8.45 miles of 230 kV transmission lines which only function to connect Lubbock’s 69 kV system to the 230 kV system of SPS. | 1/30/2009 (the date Lubbock registered as a TO) | 10/27/2010 (Mitigation Plan completion) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Compliance Audit | Lubbock has created, maintained and published a facility connection requirements document and has made this document available to the users of the transmission system, the Regional Reliability Organization and NERC. This document addressed Reliability Standard FAC-001-0 R1-R3 and all required sub-requirements. | 2010-10-27 | 2010-11-15 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP200900132 | Settlement Agreement | During an August 10, 2009 through August 11, 2009 on-site compliance audit, SPP RE determined that Lubbock, as a Transmission Owner (TO), did not have documentation of facility connection requirements for prospective generation, transmission, and end user facilities and could not provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. | FAC-001-0 | R2, R2.1 et seq. | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Lubbock is a full requirements customer of the Southwestern Public Service Company (SPS). Lubbock’s full requirements contract with SPS includes contractual obligations that would cause Lubbock to fully vet any proposed connection to its 230 kV system with SPS. Additionally, the function and physical make-up of Lubbock’s 230 kV facilities limits the potential for any possible interconnections. Lubbock owns only 8.45 miles of 230 kV transmission lines which only function to connect Lubbock’s 69 kV system to the 230 kV system of SPS. | 1/30/2009 (the date Lubbock registered as a TO) | 10/27/2010 (Mitigation Plan completion) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Compliance Audit | Lubbock has created, maintained and published a facility connection requirements document and has made this document available to the users of the transmission system, the Regional Reliability Organization and NERC. This document addressed Reliability Standard FAC-001-0 R1-R3 and all required sub-requirements. | 2010-10-27 | 2010-11-15 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP200900133 | Settlement Agreement | During an August 10, 2009 through August 11, 2009 on-site compliance audit, SPP RE determined that Lubbock, as a Transmission Owner (TO), did not provide documentation of facility connection requirements for prospective generation, transmission, and end user facilities and therefore did not maintain and update its facility connection requirements as required. Lubbock also did not make documentation of these requirements available to the users of the transmission system, the Regional Reliability Organization, and North American Electric Reliability Corporation (NERC) on request, within the five business days stated in the Standard. | FAC-001-0 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Lubbock is a full requirements customer of the Southwestern Public Service Company (SPS). Lubbock’s full requirements contract with SPS includes contractual obligations that would cause Lubbock to fully vet any proposed connection to its 230 kV system with SPS. Additionally, the function and physical make-up of Lubbock’s 230 kV facilities limits the potential for any possible interconnections. Lubbock owns only 8.45 miles of 230 kV transmission lines which only function to connect Lubbock’s 69 kV system to the 230 kV system of SPS. | 1/30/2009 (the date Lubbock registered as a TO) | 10/27/2010 (Mitigation Plan completion) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Compliance Audit | Lubbock has created, maintained and published a facility connection requirements document and has made this document available to the users of the transmission system, the Regional Reliability Organization and NERC. This document addressed Reliability Standard FAC-001-0 R1-R3 and all required sub-requirements. | 2010-10-27 | 2010-11-15 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP200900081 | Settlement Agreement | On June 17, 2009, Lubbock, as a Transmission Owner (TO) and Distribution Provider (DP) that owns a transmission Protection System, submitted a Self-Report to SPP RE stating that its transmission Protection System maintenance and testing program did not include current and potential transformers. Subsequently, in its August 10, 2009 through August 11, 2009 on-site compliance audit, SPP RE found that Lubbock's Protection System maintenance and testing program also failed to include maintenance and testing procedures for associated communication systems, current and potential transformers, and DC control circuitry. Additionally, while Lubbock’s procedure outlined monthly inspections of its station batteries, the procedure did not include sufficient battery testing procedures. SPP RE subsequently determined that Lubbock did not own any associated communication systems and functionally tests its DC control circuitry as part of its 230 kV breaker inspection procedure. Therefore, Lubbock’s failure to satisfy PRC-005-1 R1 (1.1, 1.2) is limited to Lubbock’s 48 instrument transformers, and four 230 kV station battery banks. The battery banks and instrument transformers combined comprise 71% of Lubbock’s total Protection System devices. | PRC-005-1 | R1, R1.1, R1.2 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Lubbock’s instrument transformers were initially tested when placed into service, and the outputs from these instrument transformers are constantly monitored by Lubbock’s Supervisory Control and Data Acquisition (SCADA) system. Additionally, Lubbock was inspecting its station battery banks on a monthly basis. These tests included visual inspections and recording of the battery voltage. | 8/24/2007 (the date Lubbock registered as a DP (Lubbock's TO registration was effective 1/30/2009)) | 1/18/2011 (Mitigation Plan completion) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Self-Report | Lubbock revised its substation maintenance procedures to include a summary of maintenance and testing procedures and intervals for its instrument transformers. Additionally, Lubbock amended its procedure to reflect that it does not own any associated communication systems. Finally, Lubbock amended its documentation to include a more extensive battery voltage test and monitoring procedure. This new procedure included disconnecting the battery charger and conducting six interval readings of voltage over a 30-minute timeframe. | 2011-01-18 | 2011-01-25 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place. The Self-Report was made at the suggestion of SPP RE following an event analysis of an August 16, 2008 reportable event. As a result, no self-report credit was awarded.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP200900082 | Settlement Agreement | On June 17, 2009, Lubbock, as a Transmission Owner (TO) and Distribution Provider (DP) that owns a transmission Protection System, submitted a Self-Report to SPP RE stating that its transmission Protection System maintenance and testing program did not include current and potential transformers. Subsequently, during an August 10, 2009 through August 11, 2009, on-site compliance audit, SPP RE also found that Lubbock could not provide evidence of testing for its associated communication systems, instrument transformers, and DC control circuitry. Additionally, while it could demonstrate monthly battery inspections, Lubbock could not provide documentation of adequate battery testing. SPP RE subsequently determined that Lubbock’s Protection System maintenance and testing program did include the recorded dates of its breaker trip tests for its DC control circuitry. Additionally, because Lubbock does not own any associated communication systems, no test data was required. Therefore, this violation was limited to its 48 instrument transformers and four 230 kV station batteries. | PRC-005-1 | R2, R2.1, R2.2 | High | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Lubbock’s instrument transformers were initially tested when placed into service and the outputs from these instrument transformers are constantly monitored by Lubbock’s Supervisory Control and Data Acquisition (SCADA) system. Additionally, Lubbock was inspecting its station battery banks on a monthly basis. These tests included visual inspections and recording of the battery voltage. | 8/24/2007 (the date Lubbock registered as a DP (Lubbock's TO registration was effective 1/30/2009)) | 12/30/2010 (Mitigation Plan completion) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Self-Report | Lubbock implemented its Protection System maintenance and testing plan and provided testing/maintenance records and the last testing/maintenance dates of its potential and current transformers. The maintenance and testing activities included current and voltage readings, visual inspections, connection checks and ratio verification. Additionally, Lubbock provided evidence of its annual station battery testing, which included periodic voltage checks occurring in six intervals over a time period of 30 minutes. | 2010-12-30 | 2011-01-19 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place. The Self-Report was made at the suggestion of SPP RE following an event analysis of an August 16, 2008 reportable event. As a result, no self-report credit was awarded.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP200900084 | Settlement Agreement | On June 17, 2009, Lubbock, as a Load Serving Entity, submitted a Self-Report to SPP RE indicating that on August 16, 2008, it experienced a reportable incident and in response submitted a twenty-four hour emergency alert to its Regional Reliability Organization, the North American Electric Reliability Corporation (NERC), and the Department of Energy (DOE). Lubbock stated that it submitted the alert to NERC and DOE on an outdated form, and notified the wrong party at its Regional Reliability Organization. On August 10, 2009 through August 11, 2009, SPP RE conducted an on-site compliance audit of Lubbock and confirmed the statements made in Lubbock’s Self-Report. Additionally, SPP RE determined that Lubbock submitted a subsequent alert report on August 20, 2008, utilizing the correct form. This form was submitted to NERC, DOE, and the appropriate contact at SPP RE. | EOP-004-1 | R3, R3.1, R3.2 | Lower | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Lubbock did provide timely notification of the event to DOE and NERC, albeit on a prior version of the required form. Additionally, Lubbock had fully satisfied all of the reporting requirements as of August 20, 2008. Finally, Lubbock’s Protection Systems operated properly to isolate the disturbance from the BPS. Therefore, the incident that Lubbock failed to report presented only minimal risk to the surrounding BPS. | 8/16/2008 (the date the disturbance event occurred and the report was required to be submitted) | 8/20/2008 (the date Lubbock sent the correct form and notified the correct parties) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Self-Report | Lubbock has implemented a documented procedure to ensure the proper disturbance reporting of DOE reportable incidents in the future. Within that procedure it has attached the appropriate reporting form, and it has specifically identified the appropriate contact at its Regional Reliability Organization, NERC, and DOE. | 2010-12-30 | 2011-01-12 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place. The Self-Report was made at the suggestion of SPP RE following an event analysis of an August 16, 2008 reportable event. As a result, no self-report credit was awarded.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP200900134 | Settlement Agreement | During an August 10, 2009 through August 11, 2009 on-site compliance audit, SPP RE determined that Lubbock, as a Transmission Owner (TO), did not include a clear process for the immediate reporting of vegetation conditions that present an imminent threat of a transmission line outage in its transmission vegetation management program (TVMP). The full extent of Lubbock’s process for reporting immediate vegetation threats was a statement indicating “[r]eport all vegetation related outages as soon as possible.” | FAC-003-1 | R1, R1.5 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because Lubbock’s system is confined to the geographic area of the city of Lubbock, Texas. Within its transmission system, Lubbock has only approximately nine miles of 230 kV lines. These lines are foot patrolled annually, and any problems are required to be immediately reported. Lubbock’s rights-of-way maintenance is conducted by Asplundh, Lubbock’s vegetation management contractor. According to Lubbock, Asplundh is in daily contact with personnel at Lubbock while coordinating vegetation clearance activities, thereby reducing the risk that an imminent contact might not be reported during rights-of-way activities. Furthermore, the geographic proximity of the Lubbock system to its centralized control center in the city of Lubbock decreases the likelihood that an imminent outage threat would not reach the appropriate individuals. | 1/30/2009 (the date Lubbock registered as a TO) | 10/27/2010 (the date Lubbock completed its mitigation plan) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Compliance Audit | Lubbock has included, within its TVMP document, an instruction directing the immediate communication of vegetation conditions presenting an imminent threat to its transmission facilities to its control room dispatcher. The procedure lists contact numbers for the Lubbock dispatcher and the vegetation management contractor. | 2010-10-27 | 2010-11-05 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place.
2011-09-30 | FERC | NP11-270-000 | Southwest Power Pool Regional Entity (SPP RE) | Lubbock Power And Light (Lubbock) | NCR06048 | SPP201100529 | Settlement Agreement | During an August 10, 2009 through August 11, 2009 on-site compliance audit, SPP RE determined that Lubbock, as a Load Serving Entity (LSE), did not have a documented sabotage reporting procedure prior to August 18, 2008. On August 18, 2008, Lubbock approved a CIP-001 sabotage recognition and reporting procedure. This document outlined methods for identifying physical and cyber sabotage and processes for contacting operational personnel following a sabotage event. Accordingly, the SPP RE audit team found a violation of CIP-001-1 R1 from August 24, 2007, the date Lubbock registered as a LSE, until August 18, 2008, the date Lubbock implemented its sabotage recognition and reporting procedure. | CIP-001-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because despite Lubbock’s failure to initially have a procedure for the identification and awareness of sabotage events, it had previously implemented an employee emergency action plan on March 1, 2006. This plan outlined the use of a public address system and notification of the most senior supervisor available in the event of an explosion, fire, workplace violence, power failure or bomb threat. Additionally, on November 30, 2007, Lubbock’s dispatch personnel underwent sabotage training. This training included topics of both physical and cyber sabotage and outlined how those topics relate to critical infrastructure protection. Lubbock also included event reporting contacts at the North American Electric Reliability Corporation (NERC) and the Department of Homeland Security (DHS) in the training materials. | 8/24/2007 (the date Lubbock registered as a LSE) | 8/18/2008 (the date Lubbock implemented its sabotage reporting procedure) | $14,000 (for SPP200900131, SPP200900132, SPP200900133, SPP200900081, SPP200900082, SPP200900084, SPP200900134, and SPP201100529) | Compliance Audit | Lubbock implemented a formal procedure for the recognition and reporting of sabotage events in accordance with Reliability Standard CIP-001-1 R1. The procedure describes the process for identifying sabotage events and the process for contacting appropriate parties in response to an event. | 2008-08-18 | 2011-05-18 | Neither Admits nor Denies | While Lubbock did not have a documented compliance program at the time of the violation, the entity confirmed that it is working to put one in place.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Electrical District No. 2 (ED2) | NCR05142 | WECC201002329 | Settlement Agreement | On December 15, 2010, WECC conducted an off-site compliance audit of ED2 and discovered a violation of CIP-001-1 R1. ED2, as a Load-Serving Entity (LSE), failed to have procedures for the recognition of sabotage events or procedures to make its staff aware of sabotage events. | CIP-001-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because ED2 has only a radial connection to a 115 kV transmission system. ED2 is a small entity covering a service area of approximately 100 square miles and a peak load of only 60 MW. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/1/2008 (when ED2 completed its sabotage response guidelines and procedures) | $6,500 (for WECC201002329, WECC201002330, WECC201002331, and WECC201002332) | Compliance Audit | ED2 completed its sabotage response guidelines and procedures - Operating Procedure for Recognition, Response and Reporting of Sabotage Events. | 2008-04-01 | 2011-08-04 | Agrees and stipulates to the facts | ED2 had mitigated this violation by April 1, 2008, before the December 15, 2010 Audit.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Electrical District No. 2 (ED2) | NCR05142 | WECC201002330 | Settlement Agreement | On December 15, 2010, WECC conducted an off-site compliance audit of ED2 and discovered a violation of CIP-001-1 R2. ED2, as a LSE, failed to have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | CIP-001-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because ED2 has only a radial connection to a 115 kV transmission system. ED2 is a small entity covering a service area of approximately 100 square miles and a peak load of only 60 MW. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/1/2008 (when ED2 completed its sabotage response guidelines and procedures) | $6,500 (for WECC201002329, WECC201002330, WECC201002331, and WECC201002332) | Compliance Audit | ED2 completed its sabotage response guidelines and procedures - Operating Procedure for Recognition, Response and Reporting of Sabotage Events. | 2008-04-01 | 2011-08-04 | Agrees and stipulates to the facts | ED2 had mitigated this violation by April 1, 2008, before the December 15, 2010 Audit.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Electrical District No. 2 (ED2) | NCR05142 | WECC201002331 | Settlement Agreement | On December 15, 2010, WECC conducted an off-site compliance audit of ED2 and discovered a violation of CIP-001-1 R3. ED2, as a LSE, failed to provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | CIP-001-1 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because ED2 has only a radial connection to a 115 kV transmission system. ED2 is a small entity covering a service area of approximately 100 square miles and a peak load of only 60 MW. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/1/2008 (when ED2 completed its sabotage response guidelines and procedures) | $6,500 (for WECC201002329, WECC201002330, WECC201002331, and WECC201002332) | Compliance Audit | ED2 completed its sabotage response guidelines and procedures - Operating Procedure for Recognition, Response and Reporting of Sabotage Events. | 2008-04-01 | 2011-08-04 | Agrees and stipulates to the facts | ED2 had mitigated this violation by April 1, 2008, before the December 15, 2010 Audit.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Electrical District No. 2 (ED2) | NCR05142 | WECC201002332 | Settlement Agreement | On December 15, 2010, WECC conducted an off-site compliance audit of ED2 and discovered a violation of CIP-001-1 R4. ED2, as a LSE, failed to have communication contacts at its local FBI office. | CIP-001-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because ED2 has only a radial connection to a 115 kV transmission system. ED2 is a small entity covering a service area of approximately 100 square miles and a peak load of only 60 MW. | 6/18/2007 (when the Standard became mandatory and enforceable) | 4/1/2008 (when ED2 established communication contacts with its local FBI office) | $6,500 (for WECC201002329, WECC201002330, WECC201002331, and WECC201002332) | Compliance Audit | ED2 established communication contacts with its local FBI office. | 2008-04-01 | 2011-08-04 | Agrees and stipulates to the facts | ED2 had mitigated this violation by April 1, 2008, before the December 15, 2010 Audit.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Holy Cross Energy (HCE) | NCR05190 | WECC201102420 | Settlement Agreement | On June 10, 2010, HCE requested verification from Xcel Energy Inc. (Xcel), the company HCE contracted with to be responsible for Protection System operation and maintenance of HCE's facilities, that the four relays sets at the HCE-owned Wolcott and Cooley Mesa substations were in compliance with PRC-023-1. Verification of compliance was given by Xcel on June 30, 2010. On December 7, 2010, Xcel discovered that two distance relays (one relay set) at the Cooley Mesa Substation on line 5787 were not within range of the loadability standards prescribed under R1.1. Xcel implemented new relay settings consistent with the Standard on December 20, 2010 and reported noncompliance of PRC-023 to HCE in mid-January 2011. HCE thereafter conducted its own investigation to determine whether a reportable possible violation of PRC-023-1 existed. On November 1, 2010, WECC notified HCE that WECC was initiating the Self-Certification process for the period from January 1, 2010 to December 31, 2010. Under this process, HCE's Self-Certification submittal was due by February 16, 2011. On February 7, 2011, HCE submitted a Self-Report to WECC, during the Self-Certification submittal period, stating that the backup distance relay (Pkg-S) and the primary distance relay (Pkg-P) at its Cooley Mesa substation were not set in conformance with PRC-023-1 R1.1. | PRC-023-1 | R1 | High | Moderate | WECC determined that this violation posed a minimal risk to the reliability of the bulk power system (BPS). The scope of the violation includes two HCE relays located on a 230 kV transmission line that were set below the 150 percent threshold prescribed under PRC-023 R1.1. The risk posed by noncompliance is limited in that the relays were part of an extended zone of protection seldom called upon to operate. Further, the scope of the violation was limited to two relays on a single transmission line for a period less than six months. Finally, HCE is a single transmission facility operated by a third-party. | 7/1/2010 (enforceable date of the Standard) | 12/20/2010 (Mitigation Plan completion) | 5000 | Self-Report | On February 14, 2011, HCE submitted a completed Mitigation Plan indicating that HCE and Xcel, embarked on the following mitigation actions: 1) On December 9, 2010 the proper setting for relays was issued for Pkg-S and Pkg-P; 2) On December 20, 2010, relay settings were implemented and noncompliance was mitigated; and 3) HCE now requires Xcel to submit regular reports confirming ongoing PRC-023-1 compliance for all relays. | 2010-12-20 | 2011-04-05 | Admits to the Stipulated Facts in the Settlement Agreement | WECC did not consider an internal compliance program when assessing penalty.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | NAES Corporation - Burney | NCR05264 | WECC201002403 | Settlement Agreement | On December 30, 2010, NAES, as a Generator Operator, submitted a Self-Report addressing violations of VAR-002-1 R1 and R2, stating that due to a misunderstanding of its generator's configuration, NAES continuously operated its generator in power factor control mode during normal operations. NAES failed to notify the Transmission Operator that it was not operating in voltage control mode. WECC reviewed the Self-Report and determined that NAES operated its generator in a power factor mode instead of automatic voltage control mode and failed to notify its Transmission Operator of its operating mode, in violation of VAR-002-1 R1. Because NAES operated in a factor power mode from the start of mandatory compliance until January 4, 2011, WECC determined that there was no status or capability change on any of NAES's Reactive Power resources that may warrant an investigation of R3. | VAR-002-1 | R1 | Medium | Severe | This violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) and posed a minimal risk to the BPS because NAES maintained stable output of the unit despite not having an Automatic Voltage Regulator (AVR) in service. In addition, the risk was further mitigated by the fact that this violation is applicable to a single 30 MW generation facility with limited to minimal capacity to boost system voltage during BPS disturbances. The generator involved in this violation represents a small fraction of the total generation available to the Transmission Operator. For this reason, WECC determined that any potential harm would also be minimal, assuming a complete failure did not happen concurrent with protection system (even an N-1) failure. Also, NAES operated in power factor mode in accordance with the generator's capability curve. | 8/2/2007 (when the Standard was enforceable and mandatory) | 2011-01-04 | $3,500 (for WECC201002403 and WECC201002404) | Self-Report | On February 2, 2011, NAES submitted a Mitigation Plan. On January 4, 2011, NAES notified its Transmission Operator that it operated in power factor mode, revised its plant procedures and trained its operators regarding the NAES AVR. NAES developed an operator log to track potential AVR issues associated with communication with NAES's Transmission Operator. | 2011-01-04 | 2011-04-05 | Agrees and Stipulates to the Facts in the Settlement Agreement. | Mitigating Factors: NAES's internal compliance program is well-documented and supported by corporate management, NAES has a budget for compliance activities, it empowers its employees to report noncompliance to management, and NAES may elect to take disciplinary actions against employees involved in violations of the Reliability Standards. WECC did not consider two prior violations of VAR-002-1 R1 by NAES’s affiliates--NAES Corporation - Lincoln Generating Facility (NOC-476) and NAES Corporation - Covert (NOC-808)-- to be aggravating factors in determining the penalty amount because there was not a commonality of compliance responsibility among the NAES affiliates.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | NAES Corporation - Burney | NCR05264 | WECC201002404 | Settlement Agreement | On December 30, 2010, NAES, as a Generator Operator, self-reported that it had received a voltage schedule in 2011 from its Transmission Operator. The voltage schedule was initially approved by the Transmission Operator in October 2008, and distributed to NAES in December 2008. However, NAES did not have the December 2008 schedule on file and did not maintain historical data on voltage levels and could not verify voltage levels. WECC determined that NAES's Transmission Operator provided NAES with a voltage schedule but NAES did not maintain its generator voltage or Reactive Power output within applicable Facility Ratings as directed by the Transmission Operator. In addition, WECC determined NAES's Transmission Operator did not exempt NAES from maintaining its generator voltage output as directed by the Transmission Operator. | VAR-002-1 | R2 | Medium | Severe | This violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) and posed a minimal risk to the BPS because NAES maintained stable output of the unit despite not having an Automatic Voltage Regulator (AVR) in service. In addition, the risk was further mitigated by the fact that this violation is applicable to a single 30 MW generation facility with limited to minimal capacity to boost system voltage during BPS disturbances. The generator involved in this violation represents a small fraction of the total generation available to the Transmission Operator. For this reason, WECC determined that any potential harm would also be minimal, assuming a complete failure did not happen concurrent with protection system (even an N-1) failure. Also, NAES operated in power factor mode in accordance with the generator's capability curve. | 12/18/2008 (when the Transmission Operator originally distributed the voltage schedule) | 2011-01-04 | $3,500 (for WECC201002403 and WECC201002404) | Self-Report | On February 2, 2011, NAES submitted a Mitigation Plan. NAES contacted its Transmission Operator to ensure the voltage schedule on hand was the latest version. After review of the voltage schedule that was provided, NAES requested and was granted a modified (lower) voltage schedule due to equipment limitations. NAES also revised its plant procedures for operation in accordance to the voltage schedule and trained its personnel involved with the activity. | 2011-01-04 | 2011-04-05 | Agrees and Stipulates to the Facts in the Settlement Agreement. | Mitigating Factors: NAES's internal compliance program is well-documented and supported by corporate management, NAES has a budget for compliance activities, it empowers its employees to report noncompliance to management, and NAES may elect to take disciplinary actions against employees involved in violations of the Reliability Standards. WECC did not consider two prior violations of VAR-002-1 R1 by NAES’s affiliates--NAES Corporation - Lincoln Generating Facility (NOC-476) and NAES Corporation - Covert (NOC-808)-- to be aggravating factors in determining the penalty amount because there was not a commonality of compliance responsibility among the NAES affiliates.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC201002530 | Notice of Confirmed Violation | On October 27, 2010, while conducting an internal quality assurance review, PGAE discovered possible noncompliance with COM-002-2 after reviewing its system dispatcher voice logs. On October 27, 2010, PGAE submitted a Self-Report addressing its possible noncompliance. A WECC subject matter expert (SME) reviewed the Self-Report. During the SME’s review, PGAE provided its Quality Assurance report (QA report) that prompted PGAE’s Self-Report. PGAE stated on the QA report “fifty-one conversations” between September 1, 2009 and June 30, 2010 did not include three way communication in accordance with this Standard. In a telephone interview with PGAE staff, the SME determined many of the 51 conversations described in the QA report did not involve “directives” as considered by this Standard. Therefore, WECC submitted a data request to PGAE asking for additional information related to the conversations. WECC specifically requested that PGAE identify which of the conversations described included operational or reliability directives. PGAE and the SME identified four of the conversations as directives. The SME verified that the personnel on the recordings are NERC-certified operators. The SME reviewed voice recordings of the four conversations. The SME determined PGAE appropriately used three way communication in three of the voice recordings. While reviewing voice recording 607937000050736 (recorded October 23, 2009), the SME determined PGAE personnel did not ensure the recipient of a directive relating to the Martin-Millbrae #1 115 kV line repeated the directive information back correctly. Therefore, the SME determined PGAE, as a Transmission Operator (TOP), was in possible violation of COM-002-2 R2. The SME forwarded the Self-Report, data request information, and the SME’s findings to the WECC Compliance Enforcement Department (Enforcement). Enforcement reviewed the Self-Report, data request information, and the SME’s findings. Enforcement determined PGAE issued directives in a clear, concise and definitive manner but PGAE’s failure to ensure the recipient of the directive repeated the information back correctly is a violation of COM-002-2 R2. | COM-002-2 | R2 | Medium | High | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). PGAE did not use three way communication when it provided an operational directive, however, in this case the directive related to a planned outage discussion between a transmission and distribution dispatcher. The specific communication related to de-energizing a 115 kV line to enable a maintenance crew to work on a circuit breaker. As described above, PGAE issued the directive in a clear and concise manner, however, PGAE did not ensure the recipient repeated the information contained in the directive back. WECC determined, based on the voice recordings and SME’s investigation, that PGAE used three way communication when issuing reliability directives. WECC determined PGAE’s QA report, despite identifying 51 conversations with possible non-compliance with the Standard, demonstrated PGAE’s operators use three way communication to prevent errors during normal and emergency operations. | 2009-10-23 | 2009-10-23 | $20,300 (combined for WECC201002530, WECC201102527) | Self Report | PGAE submitted a Mitigation Plan on January 11, 2011. To mitigate this violation, PGAE planned to revise its dispatch procedures to better define the role of dispatchers and the use of three way communication, establish internal reviews to ensure PGAE’s operators maintain appropriate, compliant communication, conduct weekly peer reviews, quarterly supervisor reviews, and quarterly PGAE training team reviews of voice recordings and Quality Assurance spot checks of voice recordings. PGAE further plans to implement a record archival and retrieval system associated with dispatcher communication. PGAE also plans to prevent human errors through extensive training, including NERC Continuing Education Training (human performance and communication modules). WECC reviewed the mitigation plan. WECC determined the timeframe for PGAE to complete operator training (milestone expected to be completed as of January 1, 2012), was not timely and contacted PGAE staff. PGAE’s NERC Compliance Manager stated PGAE management is committing to completing the training earlier and that the reviews outlined previously provide PGAE adequate time to ensure PGAE’s training is effective. PGAE’s mitigation plan is comprehensive and PGAE’s NERC Compliance Manager indicated PGAE is committed to continuous improvement in three way communication, however WECC determined the mitigation plan documentation does not appropriately prioritize dispatcher training. In conversations with PGAE’s NERC Compliance Manager, Enforcement determined PGAE’s internal deadlines for completing the training did not match the timelines proposed in PGAE’s mitigation plan. Enforcement determined PGAE’s internal timeframe, wherein PGAE proposes to train the majority of its personnel on three way Communication by October and November 2011, reduces the risk this violation poses to the BPS. However, PGAE’s mitigation plan does not require PGAE to complete such training until January 2012 and does not reference PGAE’s internal deadlines. Accordingly, WECC rejected the mitigation plan. On May 31, 2011, WECC sent PGAE a Notice of Mitigation Plan Rejection. On the Notice of Mitigation Plan Rejection WECC stated “while PGAE’s proposed plan includes several satisfactory achievements, it does not appropriately prioritize PGAE’s tasks. Specifically, three-way communication involves human actions and PGAE’s deadline for training its operators on three-way communication is January 2012.” PGAE promptly responded, also on May 31, 2011, stating PGAE would submit a revised mitigation plan. PGAE submitted its revised Mitigation Plan on June 14, 2011. | 10/6/2011 (Approved Date) | TBD | Admits | PGAE had an internal compliance program (ICP) which was a mitigating factor. The ICP was documented; disseminated throughout PGAE's operations staff; had an oversight staff which was supervised at a high level in the organization and it has independent access to the CEO and/or board of directors; the ICP is operated such that it is independent of staff responsible for compliance of Standards; supported and participated by senior management; reviewed and modified regularly; includes formal, internal self-auditing of Standards on a periodic basis; and includes disciplinary action for employees involved in violations of the Standards.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Pacific Gas and Electric Company (PGAE) | NCR05299 | WECC201102527 | Notice of Confirmed Violation | On March 7, 2011, in reviewing an internal monthly compliance report PGAE discovered that oil samples on Midway 500 kV shunt reactors were completed four days past the compliance due date. No incident or impact to the BPS occurred. These reactors are located on Path 15, South of Los Banos or Midway-Los Banos. The SME determined PGAE's Transmission Maintenance and Inspection Plan (TMIP) required PGAE to sample the line reactor oil to ensure the internal functions of the reactors operate properly. Such sampling is compared to previous (and future) samples to verify the units remain in operable condition. PGAE, as a Transmission Owner and TOP, failed to sample the oil within the intervals defined in its TMIP, which resulted in the violation. This shunt reactor maintenance is part PG&E substation maintenance program in support of WECC Regional Standard PRC-STD-005-1 Requirement WR1. | PRC-STD-005-1 | WR1 | N/A (PRC-STD-005-1, WR1 is a WECC Regional Reliability Standard) | N/A (PRC-STD-005-1, WR1 is a WECC Regional Reliability Standard) | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the BPS. Oil samples were taken four days beyond the required interval. There were no events or equipment reliability impacts as a result of the late completion of this maintenance task. | 2011-02-01 | 2011-02-04 | $20,300 (combined for WECC201002530, WECC201102527) | Self Report | On May 27, 2011, PGAE submitted its Mitigation Plan. PGAE will complete the following actions to mitigate this violation: (1) refine and implement the roles and responsibilities of an Asset Strategist in support of Substation Maintenance headquarters; (2) develop and implement a Compliance Monitoring System; (3) deliver short-term training regarding PFC Standards to Substation and Maintenance and Testing personnel; (5) determine the extent of the scope; (6) develop and implement a more formalized long-term training program regarding the substation maintenance program and NERC/WECC compliance requirements. PGAE will implement the following to prevent future risk to the BPS: (1) a Training and Monitoring System, by having consistent training of the modified reports and monitoring system it will ensure that required maintenance to the BPS will be performed per PGAE's documented maintenance cycles; and (2) Validation of SAP Work Management System, which will ensure that changes to headquarter or substation assignments reflect required maintenance work. | 11/1/2011 (Approved Date) | TBD | Admits | PGAE had an ICP which was a mitigating factor. The ICP was documented; disseminated throughout PGAE's operations staff; had an oversight staff which was supervised at a high level in the organization and it has independent access to the CEO and/or board of directors; the ICP is operated such that it is independent of staff responsible for compliance of Standards; supported and participated by senior management; reviewed and modified regularly; includes formal, internal self-auditing of Standards on a periodic basis; and includes disciplinary action for employees involved in violations of the Standards.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Thermo Power and Electric LLC (THPE) | NCR05425 | WECC200901621 | Settlement Agreement | On August 4, 2009, THPE submitted a Self-Certification reporting it was in violation of CIP-001-1 R1. The noncompliance was discovered as a result of a third-party gap analysis performed for THPE to determine its overall NERC compliance status. WECC determined that THPE, as a Generator Operator, failed to ensure that current THPE sabotage reporting documentation contained procedures for the recognition of sabotage procedures, for the communication of information concerning sabotage to the appropriate parties within the interconnection, or sabotage response guidelines, as required by the Standard. | CIP-001-1 | R1 | Medium | Severe | THPE instructed facility personnel to remain vigilant and report any suspicious activity while THPE develops and implements updated sabotage procedures. Furthermore, THPE operates a single generating facility with three small generators that combine for approximately 80 MWs of generating capacity. In addition, THPE does not operate the generators at full capacity, but rather operates in limited circumstances pursuant to its power purchase contracts. THPE’s generation is fraction of the generation available to the transmission operation and an even smaller fraction of the generation available to the Balancing Authority. For these reasons, WECC believes this violation poses a minimal risk to the reliability of the bulk power system (BPS). | 6/18/2007 (date Standard was enforceable) | 9/8/2009 (date THPE completed Mitigation Plan) | $10,000 (for WECC200901621, WECC200901622, WECC200901623, WECC200901637, and WECC200901553) | Self-Certification | THPE stated in its mitigation plan that it would work with a third party vendor to develop robust sabotage reporting procedures that would address the requirements of CIP-001-1 R1, R2 and R3. THPE submitted its Sabotage Reporting Procedures and a personnel training log detailing the procedures required by CIP-001-1 R1, R2 and R3. WECC determined THPE developed procedures for the recognition and for making of its personnel aware of sabotage events on THPE facilities and multi-site sabotage affecting larger portions of the Interconnection, including procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. WECC determined the personnel training log demonstrated THPE provided its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | 2009-09-08 | 2009-12-31 | Agree and Stipulates to the Facts in the Settlement Agreement | WECC considered THPE's internal compliance program (ICP) as a mitigating factor in assessing the penalty. WECC found that THPE's ICP is documented; THPE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; THPE has allocated resources to Its ICP; the ICP has the support and participation of senior management; THPE reviews its ICP on an annual basis; THPE's ICP Includes formal, Internal self-auditing for compliance with all Reliability Standards on a periodic basis; and THPE's Compliance Department includes active engagement, and coordinated recurring meetings with, THPE senior management.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Thermo Power and Electric LLC (THPE) | NCR05425 | WECC200901622 | Settlement Agreement | On August 4, 2009, THPE submitted a Self-Certification reporting it was in violation of CIP-001-1 R2. The noncompliance was discovered as a result of a third-party gap analysis performed for THPE to determine its overall NERC compliance status. WECC determined that THPE, as a Generator Operator, failed to ensure that current THPE sabotage reporting documentation contained procedures for the recognition of sabotage procedures, for the communication of information concerning sabotage to the appropriate parties within the interconnection, or sabotage response guidelines, as required by the Standard. | CIP-001-1 | R2 | Medium | Severe | THPE instructed facility personnel to remain vigilant and report any suspicious activity while THPE develops and implements updated sabotage procedures. Furthermore, THPE operates a single generating facility with three small generators that combine for approximately 80 MWs of generating capacity. In addition, THPE does not operate the generators at full capacity, but rather operates in limited circumstances pursuant to its power purchase contracts. THPE’s generation is fraction of the generation available to the transmission operation and an even smaller fraction of the generation available to the Balancing Authority. For these reasons, WECC believes this violation poses a minimal risk to the reliability of the BPS. | 6/18/2007 (date Standard was enforceable) | 9/8/2009 (date THPE completed Mitigation Plan) | $10,000 (for WECC200901621, WECC200901622, WECC200901623, WECC200901637, and WECC200901553) | Self-Certification | THPE stated in its mitigation plan that it would work with a third party vendor to develop robust sabotage reporting procedures that would address the requirements of CIP-001-1 R1, R2 and R3. THPE submitted its Sabotage Reporting Procedures and a personnel training log detailing the procedures required by CIP-001-1 R1, R2 and R3. WECC determined THPE developed procedures for the recognition and for making of its personnel aware of sabotage events on THPE facilities and multi-site sabotage affecting larger portions of the Interconnection, including procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. WECC determined the personnel training log demonstrated THPE provided its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | 2009-09-08 | 2009-12-31 | Agree and Stipulates to the Facts in the Settlement Agreement | WECC considered THPE's ICP as a mitigating factor in assessing the penalty. WECC found that THPE's ICP is documented; THPE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; THPE has allocated resources to Its ICP; the ICP has the support and participation of senior management; THPE reviews its ICP on an annual basis; THPE's ICP Includes formal, Internal self-auditing for compliance with all Reliability Standards on a periodic basis; and THPE's Compliance Department includes active engagement, and coordinated recurring meetings with, THPE senior management.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Thermo Power and Electric LLC (THPE) | NCR05425 | WECC200901623 | Settlement Agreement | On August 4, 2009, THPE submitted a Self-Certification reporting it was in violation of CIP-001-1 R3. The noncompliance was discovered as a result of a third-party gap analysis performed for THPE to determine its overall NERC compliance status. WECC determined that THPE, as a Generator Operator, failed to ensure that current THPE sabotage reporting documentation contained procedures for the recognition of sabotage procedures, for the communication of information concerning sabotage to the appropriate parties within the interconnection, or sabotage response guidelines, as required by the Standard. | CIP-001-1 | R3 | Medium | Severe | THPE instructed facility personnel to remain vigilant and report any suspicious activity while THPE develops and implements updated sabotage procedures. Furthermore, there have been no incidents of sabotage at THPE’s facilities, and thus no actual impact to the BPS. For these reasons, WECC believes this violation poses a minimal risk to the reliability of the BPS. | 6/18/2007 (date Standard was enforceable) | 9/8/2009 (date THPE completed Mitigation Plan) | $10,000 (for WECC200901621, WECC200901622, WECC200901623, WECC200901637, and WECC200901553) | Self-Certification | THPE stated in its mitigation plan that it would work with a third party vendor to develop robust sabotage reporting procedures that would address the requirements of CIP-001-1 R1, R2 and R3. THPE submitted its Sabotage Reporting Procedures and a personnel training log detailing the procedures required by CIP-001-1 R1, R2 and R3. WECC determined THPE developed procedures for the recognition and for making of its personnel aware of sabotage events on THPE facilities and multi-site sabotage affecting larger portions of the Interconnection, including procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. WECC determined the personnel training log demonstrated THPE provided its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | 2009-09-08 | 2009-12-31 | Agree and Stipulates to the Facts in the Settlement Agreement | WECC considered THPE's ICP as a mitigating factor in assessing the penalty. WECC found that THPE's ICP is documented; THPE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; THPE has allocated resources to Its ICP; the ICP has the support and participation of senior management; THPE reviews its ICP on an annual basis; THPE's ICP Includes formal, Internal self-auditing for compliance with all Reliability Standards on a periodic basis; and THPE's Compliance Department includes active engagement, and coordinated recurring meetings with, THPE senior management.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Thermo Power and Electric LLC (THPE) | NCR05425 | WECC200901637 | Settlement Agreement | On August 4, 2009, THPE submitted a Self-Certification reporting it was in violation of FAC-008-1 R1. WECC determined that THPE, as a Generator Owner, failed to have a process for documenting its Facility Rating Methodology, as required by the Standard. In addition, WECC found that THPE did not have the Facility Rating statement, as required by R1.1. WECC also determined that THPE did not have a method for the determination of a Facility Rating and the scope of equipment covered by those Ratings, for its solely and jointly owned Facilities, as required by R1.2 of the Standard. WECC also determined that THPE did not have Facility Ratings that considered the Ratings provided by manufacturers, design criteria, ambient conditions and operating limitations, as required by R1.3 of the Standard. | FAC-008-1 | R1 | Medium | Severe | THPE reported that it did not have a Facility Ratings Methodology for its solely and jointly owned Facilities; however, THPE operates a single generating facility with three small generators that combine for approximately 80 MW of generating capacity. In addition, THPE does not operate the generators at full capacity, but rather operates in limited circumstances pursuant to its power purchase contracts. THPE’s generation is fraction of the generation available to the transmission operator and an even smaller fraction of the generation available to the Balancing Authority. For these reasons, WECC believes this violation poses a minimal risk to the reliability of the BPS. | 6/18/2007 (date Standard was enforceable) | 9/11/2009 (date THPE completed Mitigation Plan) | $10,000 (for WECC200901621, WECC200901622, WECC200901623, WECC200901637, and WECC200901553) | Self-Certification | THPE stated in its mitigation plan that it hired a third-party consultant to assist in the development of a Facility Rating Methodology. THPE submitted a mitigation plan completion form and it's Facility Ratings Methodology Via Electrical Component Analysis to WECC as evidence of compliance. THPE WECC determined THPE documented its current methodology used for developing Facility Ratings of its solely and jointly owned facilities. WECC further determined such methodology Included each of the subcomponents of FAC-008-1 R1. | 2009-09-11 | 2009-11-04 | Agree and Stipulates to the Facts in the Settlement Agreement | WECC considered THPE's ICP as a mitigating factor in assessing the penalty. WECC found that THPE's ICP is documented; THPE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; THPE has allocated resources to Its ICP; the ICP has the support and participation of senior management; THPE reviews its ICP on an annual basis; THPE's ICP Includes formal, Internal self-auditing for compliance with all Reliability Standards on a periodic basis; and THPE's Compliance Department includes active engagement, and coordinated recurring meetings with, THPE senior management.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Thermo Power and Electric LLC (THPE) | NCR05425 | WECC200901553 | Settlement Agreement | On August 4, 2009, THPE submitted a Self-Certification reporting it was in violation of FAC-009-1 R1. WECC determined that THPE, as a Generator Owner, failed to develop Facility Ratings for its solely and jointly owned Facilities that were consistent with the associated Facility Ratings Methodology, as required by R1 of the Standard. | FAC-009-1 | R1 | Medium | Severe | THPE reported that it did not have a Facility Ratings Methodology for its solely and jointly owned Facilities; however, THPE operates a single generating facility with three small generators that combine for approximately 80 MW of generating capacity. In addition, THPE does not operate the generators at full capacity, but rather operates in limited circumstances pursuant to its power purchase contracts. THPE’s generation is fraction of the generation available to the transmission operator and an even smaller fraction of the generation available to the Balancing Authority. For these reasons, WECC believes this violation poses a minimal risk to the reliability of the bulk power system (BPS). | 6/18/2007 (date Standard was enforceable) | 10/1/2009 (date THPE completed Mitigation Plan) | $10,000 (for WECC200901621, WECC200901622, WECC200901623, WECC200901637, and WECC200901553) | Self-Certification | THPE stated in its mitigation plan that it had hired a third-party consultant to assist in the development of Facility Ratings once a Facility Rating Methodology had been developed. WECC determined THPE established Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings Methodology. | 2009-10-01 | 2009-12-31 | Agree and Stipulates to the Facts in the Settlement Agreement | WECC considered THPE's ICP as a mitigating factor in assessing the penalty. WECC found that THPE's ICP is documented; THPE has ICP oversight staff; ICP oversight staff is supervised at a high level in the organization; THPE has allocated resources to Its ICP; the ICP has the support and participation of senior management; THPE reviews its ICP on an annual basis; THPE's ICP Includes formal, Internal self-auditing for compliance with all Reliability Standards on a periodic basis; and THPE's Compliance Department includes active engagement, and coordinated recurring meetings with, THPE senior management.