2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002814 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-006-1 R1, because WECC_URE1 failed to ensure that its Physical Security Perimeter (PSP) at its backup control center was completely enclosed in a "six-wall" border. The WECC Audit Team identified Critical Cyber Assets located at two of its Critical Asset facilities, a primary control center and a backup control center. The WECC Audit Team performed a walkthrough at the two facilities. During the walkthrough, the WECC Audit Team lifted ceiling tiles at both facilities and discovered that the entire length of the north wall of the backup control center did not have sheet rock that extended to the top of the ceiling. According to WECC Audit Team, this created an opening two feet high, which would allow a person access to the PSP. In addition, the WECC Audit Team found that WECC_URE1 failed to provide any documentation that it had performed testing procedures, applied security patches, deployed anti-virus and malware tools, or had created recovery plans for PSP access control and monitoring devices. WECC_URE1 failed to provide the necessary protective measures for its PSP access control and monitoring (ACM) devices in violation of CIP-006-1 R1.8. WECC Enforcement determined that WECC_URE1 had a violation of CIP-006-1 R1.1 for failing to ensure that the PSP at its backup control center was completely enclosed. WECC Enforcement also determined that WECC_URE1 had a violation of CIP-006-1 R1.8 for failing to afford its ACM Cyber Assets the protections in CIP-007-3 R1 (test procedures), CIP-007-3 R3 (security patches), CIP-007-3 R4 (anti-virus and malware tools); and CIP-009-3 R1 (recovery plans). | CIP-006-1 | R1; R1.1, R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the PSP resides in an area of controlled access. Because the PSP resides within an area of controlled access, the ability of unauthorized personnel gaining access to the PSP is limited. The PSP at issue resides within an WECC_URE1-operated controlled access area, where WECC_URE1 had protective measures prescribed by the Standard. WECC_URE1 had physical access controls, monitored physical access, logged physical access, retained access logs, and had a maintenance and testing program. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 completely enclosed the PSP at its backup control center; applied testing procedures for PSP ACM devices; created recovery plans for PSP ACM devices; modified its cyber security program and policy documents, where necessary, to explicitly address the requirements of CIP-006-1 R1.8 for PSP ACM devices; applied security patches for PSP ACM devices; and deployed anti-virus and malware tools for PSP ACM devices. | 2012-05-15 | 2012-07-18 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002813 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-004-1 R4 because WECC_URE1 did not have documentation that it had performed quarterly reviews of its personnel with access to the Critical Cyber Assets (CCAs). Although WECC_URE1 did perform some level of review, WECC_URE1 was unable to provide dates, times and signatures indicating how the lists were reviewed. | CIP-004-1 | R4; R4.1 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE1 provided some level of review but did not have evidence of dates, times, and signatures indicating how the lists were reviewed. Any time an individual's physical access was granted or modified in the system, the entire access list was reviewed and verified. In addition, during the violation period, the list was reviewed more frequently than quarterly because requests to grant or remove access occurred more frequently during this period. | when the Standard became mandatory and enforceable for WECC_URE1 | when the required quarterly review was completed | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | For quarterly reviews, WECC_URE1 utilizes a form that lists personnel with access to CCAs. This form is documented in WECC_URE1’s critical infrastructure cyber security program and records the date of review, location of review, the reviewer’s name, type of access that is being reviewed, and the access lists being reviewed. Copies of the access lists being reviewed are attached to the completed forms along with any required access changes as a result of the review. | 2009-06-29 | 2011-09-13 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002812 | Settlement Agreement | WECC determined that WECC_URE1 had a violation of CIP-003-1 R4 because WECC_URE1 failed to include the Critical Asset list, as required by Standard CIP-002-2, in its protected Critical Cyber Asset information program. | CIP-003-1 | R4; R4.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because not properly protecting a list of Critical Assets could expose the BPS to a cyber security attack. If unauthorized individuals gained access to this information, they could use it to perform malicious acts to the BPS. The risk to the BPS was mitigated by the following factors. WECC_URE1's Critical Asset list did not contain any Critical Cyber Asset information. In addition, although WECC_URE1 had not included the Critical Asset list, WECC_URE1 did have an information protection program in place during the duration of the violation. | when the Standard became mandatory and enforceable for WECC_URE1 | when WECC_URE1 modified its Critical Cyber Asset information protection program to include the Critical Asset list | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 modified its CIP compliance program document for CIP-003 R4 to explicitly classify the Critical Asset list as protected information. WECC_URE1 also modified its CIP-003 R4 compliance program document to explicitly classify floor plans which contain Critical Cyber Asset information as protected information. | 2011-07-20 | 2012-05-18 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002810 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-002-1 R3 because three switches should have been identified as Critical Cyber Assets (CCAs). These switches should have been identified as CCAs because they directly support WECC_URE1's primary control center. WECC concluded that three switches used in the access control and monitoring of one of WECC_URE1's Electronic Security Perimeters were not identified as CCAs as required by CIP-002-1 R3. WECC concluded that the three switches were CCAs because they were used to configure, provide access to, and monitor the primary control center, which is an identified WECC_URE1 Critical Asset. | CIP-002-1 | R1 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE1 provided some level of protection to these three switches as they are co-located and co-managed with WECC_URE1's other primary control center CCAs. The PSP at issue resides within an WECC_URE1-operated controlled access area, where WECC_URE1 had protective measures prescribed by the Standard. WECC_URE1 had physical access controls, monitored physical access, logged physical access, retained access logs, and had a maintenance and testing program. | when the Standard became mandatory and enforceable for WECC_URE1 | Mitigation Plan completion | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 performed configuration changes in the network switches at issue to remove the internet protocol (IP)-based management capability, thus making them no longer CCAs. | 2010-10-15 | 2011-10-04 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002267 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of IRO-STD-006-0 WR1 because WECC_URE1 failed to respond to a schedule curtailment request for 29 minutes. WECC_URE1's Transfer Distribution Factor matrix document indicated that WECC_URE1 did not respond to a schedule curtailment request of contributed 1.4 MW to a Qualified Path for 29 minutes. Pursuant to the Sanction Table appended to the Standard, this violation represents one occurrence at Level One of Noncompliance. | IRO-STD-006-0 | WR1 | N/A | N/A | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The identified Qualified Path was rated at approximately 500 MW at the time and was flowing at less than the rate of the Qualified Path, accommodating 100 MW of unscheduled flow. WECC_URE1's curtailment obligation amounted to 0.28% of the flow on the path. The required schedule relief in the curtailment request was 1.4 MW and the duration lasted 29 minutes. | when WECC_URE1 did not respond to a schedule curtailment request | when WECC_URE1 responded | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 initiated regular reviews of standard operating procedures (SOPs) by its system operators will help prevent future violations of this Standard. WECC_URE1 also initiated a tool to notify its operators of curtailments associated with the WECC Unscheduled Flow Mitigation Plan. WECC_URE1 also instituted a SOP to explain the use of the tool and associated transmission curtailments. All system operators have reviewed the SOP associated with Unscheduled Flow Curtailments. | 2007-09-30 | 2012-05-07 | Neither Admits nor Denies | Pursuant to the Sanction Table appended to the Regional Standard, this violation represents one occurrence at Level One of Noncompliance. The Sanctions Table for this Standard state that the following sanction should be assessed "Letter to Responsible Entity's Chief Executive Officer informing the Responsible Entity of noncompliance with copies to NERC, WECC Member Representative, and WECC Operating Committee Representative." The level of noncompliance in this case is 1 because the required relief was 1.4 MW, which is less than the 5 MW thresholds for Level 1 noncompliance as prescribed by the Standard. WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002266 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of EOP-005-1 R1 because its restoration plan did not include necessary operating instructions and procedures to cover the loss of vital telecommunications channels as required by the Standard. Although WECC_URE1 stated that loss of vital telecommunications channels is addressed in the design requirements of the WECC_URE1 telecommunication infrastructure, no commercial power or third-party telecommunications facilities are required at any point from the blackstart unit to load centers at the two pertinent substations. The telecommunications infrastructure is designed with the requirement that remote switching and supervisory control will be necessary to restore the WECC_URE1 system. WECC_URE1 also stated that its restoration plan includes a backup plan if anything in the proposed plan fails. WECC determined that this was insufficient to address the loss of vital telecommunications channels because WECC_URE1 was relying on the design requirement of WECC_URE1's own telecommunication equipment to be reliable and remain in service to address the loss of vital communications channels. | EOP-005-1 | R1 | Medium | Lower | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1 had a plan in place to connect directly with another entity to cover emergency conditions. Furthermore, WECC_URE1's system operators demonstrated during Audit interviews that they are well-trained to man critical facilities when necessary. | the first day following Certification of Mitigation Plan Completion for WECC_URE1's prior EOP-005-1 R1 violation | when WECC_URE1 revised its restoration plan to further address the loss of vital telecommunications systems | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 revised its system restoration plan to address the loss of vital telecommunications during a system restoration event. The revision directs the system operator to utilize the WECC_URE1 radio system to establish necessary communications and also dispatch personnel to the appropriate sites. | 2011-01-21 | 2012-03-15 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE1's violation history as an aggravating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002265 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of COM-001-1 R5 because WECC_URE1 did not have in place operating procedures and instructions that directed WECC_URE1 personnel to man substations in the event of a loss of communications and, therefore, WECC_URE1 did not have in place operating procedures and instructions to enable continued operations of its system during the loss of its telecommunications equipment. WECC reviewed three of WECC_URE1's standard operating procedure (SOP) documents. Although WECC previously determined that these documents adequately described the actions to be taken during a loss of telecommunications facilities, these documents were superseded by WECC_URE1's new SOP. WECC determined that the new SOP did not contain written operations and procedures to enable continued operations of its system in the event that WECC_URE1's telecommunications facilities are inoperable. | COM-001-1 | R5 | Lower | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1 had procedures in one of its SOP document to implement fully redundant communications facilities at its backup control center, and had provisions for training its system operators. In addition, although not explicitly documented, WECC_URE1 demonstrated, through interviews with the WECC Audit Team, that its system operators are well-trained to man substations when necessary. | when WECC_URE1's new SOP policy was established | when WECC_URE1 reinstated the previously retired SOP | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Compliance Audit | WECC_URE1 updated and reinstated its previously retired SOP document and provided training. The SOP document provides written operating procedures and instructions to enable continued operation of its system during the loss of voice and data communications. | 2011-01-21 | 2012-03-21 | Neither Admits nor Denies | WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002400 | Settlement Agreement | WECC sent WECC_URE1 a Notice of On-Site Compliance Audit. WECC_URE1 self-reported a violation of CIP-004-1 R2. WECC conducted an Audit of WECC_URE1's compliance with, among other Reliability Standards, CIP-004-1 R2. Because WECC_URE1 had previously self-reported a violation of CIP-004-1 R2, the WECC Audit Team reviewed WECC_URE1's Self-Report at the Audit. The WECC Audit Team concluded that, consistent with WECC_URE1's Self-Report, four WECC_URE1 contractors had not received training as required by CIP-004-1 R2.1. WECC Enforcement reviewed WECC Audit Team findings and determined that WECC_URE1 had a violation of CIP-004-1 R2.1 for failing to train four of its contractors prior to granting them access to Critical Cyber Assets (CCAs). | CIP-004-1 | R2; R2.1 | Medium | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the subject individuals are employees of an WECC_URE1 contractor that has been providing monitoring and optimization of the generation control software on WECC_URE1's supervisory control and data acquisition (SCADA) system since several years before the Reliability Standards became mandatory and enforceable. The affected individuals perform similar services for other NERC-registered entities and receive ongoing cyber security training from these entities. Personnel risk assessments were conducted on the affected individuals per CIP-004 R3, and were verified by WECC_URE1 personnel prior to adding the subject individuals to the approved CCA access list. For these contractors, cyber access to WECC_URE1's SCADA system requires two levels of authentication: (1) authentication at the corporate firewall VPN, and (2) authentication at the CIP access point firewall. The ability for a contractor to connect through the two access points is normally disabled. The contractor must specifically request access from SCADA support personnel and be authorized prior to gaining access. Access to WECC_URE1's SCADA system by the subject individuals is not continuous and is granted for short durations a few times per year. | when the Standard became mandatory and enforceable for WECC_URE1 | when the four individuals had their access revoked | $65,000 (for WECC201102731, WECC201002817, WECC201002816, WECC201002814, WECC201002813, WECC201002812, WECC201002810, WECC201002267, WECC201002266, WECC201002265, and WECC201002400) | Self-Report | Upon discovery of the violation, WECC_URE1 revoked access authorizations for the individuals involved. On the next day, WECC_URE1 provided them cyber security training specific to their role and added their names to the list of individuals requiring annual cyber security training and quarterly awareness programs. WECC_URE1 also verified that its training and access lists were current and correct. | 2011-08-20 | 2011-12-28 | Neither Admits nor Denies | WECC_URE1 was awarded credit for supplying additional useful information in its Self-Report. WECC considered WECC_URE1's internal compliance program (ICP) as a mitigating factor in the penalty determination. WECC considered WECC_URE1's violation history as an aggravating factor in the penalty determination.
2012-09-28 | FERC | NP12-47-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009304 | Notice of Confirmed Violation | WECC_URE2 submitted a Self-Certification to WECC stating it was in violation of CIP-007-1 R6. WECC_URE2 reported that after it completed its internal documentation sufficiency review, it recognized that some of its generation devices were not sending system event logs to its centralized logging server. Specifically, 52.8% of Critical Cyber Assets (CCAs) and Critical Assets (CAs) within the Electronic Security Perimeter (ESP) failed to log cyber security events to the centralized logging server system. WECC_URE2 stated that since its compliance enforcement date for the Standard it failed to ensure 52.8% of the devices within the ESP were logging cyber security events to its centralized logging system. WECC_URE2 stated further that 28 of the CCAs in scope are part of the operation of its Energy Management System (EMS), and the remaining 10 CAs are network devices (routers and switches) within the WECC_URE2 generating sites ESPs and PSPs . WECC_URE2 noted that the 52.8% devices in scope were unable to send cyber security system events to its centralized logging server system because of incorrect system configurations that did not allow the devices to log or monitor events. WECC determined that WECC_URE2 violated CIP-007-1 R6 for a failure to ensure that all CAs within the ESP implement automated tools or organizational process controls to monitor system events that are related to cyber security. Specifically, WECC_URE2 failed to implement and document organizational processes and technical and procedural mechanisms for monitoring for security events on 52.8% devices. | CIP-007-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the 52.8% devices in scope were located at WECC_URE2's generation sites within the ESPs and Physical Security Perimeters (PSPs), thereby reducing the risk related to cyber security events. As compensating measures, the ESPs at issue are equipped with intrusion detection systems and access point protections, including externally-connected communication end points, which allow for monitoring of security events. Additionally, the devices in scope have only necessary ports and services enabled and anti-virus and anti-malware software installed, further reducing the risk to the BPS related to cyber security events. For these reasons, WECC determined this violation posed moderate risk to the reliability of the BPS. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | 17400 | Self-Certification | In accordance with WECC_URE2's Mitigation Plan, WECC_URE2 completed the following activities: (1) Implemented a new system to improve the technical control for log management; (2) Improved ability to automatically identify when systems stop logging; (3) Increased the reliability to automatically track log activities and alerts; (4) Stated generating of automatic dashboards for real-time status reports of logging; (5) Established dedicated personnel to review, track, escalate, fix and monitor status on logging issues; (6) Established that the Information Technology (IT) department provides regular status reports to an Operations and IT Management confirming all CCA and CA devices are logging; (7) Updated IT procedural documentation for management of logging; (8) Established that an Operations department reviews and updates its procedure for ensuring that new assets are configured to log by default prior to deployment; and (9) Established that an Operations department reviews and updates its notification procedure to IT for all new or changed assets or for planned maintenance where logging and system events related to Cyber Security are required. | 2012-06-22 | 2012-09-25 | Agrees and Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP), which was in effect at the time of the violation, and considered it a mitigating factor in determining the penalty amount.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000409 | Settlement Agreement | FRCC_URE1 self-reported that it did not ensure that all Cyber Assets within the Electronic Security Perimeter (ESP) had the proper controls in place to monitor system events that are related to cybersecurity, as required by CIP-007-1 R6. FRCC_URE1 did not ensure that logs were properly maintained for the required duration. FRCC determined that the violation involved a number of individual devices: 15% were Cyber Assets not configured for logging system events; 24% were switches, where logs were not generated due to configuration issues resulting from remote authentication protocol and other upgrades; and 61% were Cyber Assets experiencing a four-day outage of a server and were unable to capture the logs related to cybersecurity. | CIP-007-1 | R6 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all the devices in scope were within identified and protected ESPs with protected access points. FRCC determined that the violation posed a moderate risk because lack of monitoring and logging for these assets could have resulted in an opportunity for internal compromise and weakened the defense in depth for the ESP. However, the risk was limited because logging at the access points was effectively implemented and remote access well-controlled. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1: (1) improved the Cyber Assets test procedure to require testing of monitoring and logging functions; (2) configured device log storage space; (3) required appropriate configuration of remote authentication protocol and other devices; (4) configured switches with correct log server configuration; (5) reviewed and reconciled all log activity to confirm the results of implementation; (6) locked the console ports for NERC-defined switches; (7) disabled remote access for switches which require physical access to apply changes through the local console port; and (8) trained staff on the new testing and verification process. | 2011-07-19 | 2012-05-02 | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007926 | Settlement Agreement | FRCC_URE1 self-reported that it failed to fully establish, document, and implement a process for ensuring that only ports and services required for normal and emergency operation were enabled. FRCC_URE1 secured most ports and services, but since it did not update documentation for each individual device, but rather created its baseline by device type, it was not possible for FRCC_URE1 to demonstrate compliance with CIP-007-1 R2. | CIP-007-1 | R2 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE1's evidence demonstrated that all Cyber Assets within an Electronic Security Perimeter were well-hardened and known vulnerabilities were patched and addressed. However, FRCC determined that the violation posed a moderate risk because failure to document the required ports and services can result in unknown ports being left open for attack from sources with malicious intent. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) complete a review of Cyber Assets including software inventory; (2) research and design procedures for ports and services monitoring solution; (3) complete a ports and services evaluation and create a baseline for each asset type; (4) implement ports and services monitoring solution; (5) update ports and services documentation; (6) train and communicate changes to personnel; and (7) request any required Technical Feasibility Exceptions where disabling ports and services is not technically feasible. | 1/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007927 | Settlement Agreement | FRCC_URE1 self-reported that it failed to perform a cyber vulnerability assessment (CVA) in accordance with the requirements of CIP-007-1 R8. FRCC_URE1 does have a documented process document and did complete the CVAs for the previous years, but these CVAs did not meet all of the requirements of the Standard. FRCC_URE1 conducted CVAs which included scans of ports and services for only some Cyber Assets, in violation of R8.2. The CVAs included a review of controls for default accounts, but did not include all Cyber Assets within the Electronic Security Perimeter (ESP). FRCC_URE1's CVA also included a review of configurations for patches and updates of known vulnerabilities. FRCC_URE1 did not create an action plan that included the status to remediate known vulnerabilities identified during the CVA, in violation of R8.4. | CIP-007-1 | R8 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all devices were afforded protection of the ESP. FRCC determined that the violation posed a moderate risk because lack of performing a complete CVA can result in vulnerabilities in the system that would not be discovered or mitigated. While FRCC_URE1 failed to conduct and document the CVA results in the required manner, evidence demonstrated that all Cyber Assets within an ESP were well-hardened and known vulnerabilities were addressed. | when FRCC_URE1 failed to complete a CVA which was in accordance with the Standard | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) complete a vulnerability scan that includes; review of default controls for passwords, review of ports and services, and update of the vulnerability assessment procedure; (2) document the results of the scan; and (3) create an action plan for remediating the identified vulnerabilities. | 1/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007928 | Settlement Agreement | FRCC_URE1 self-reported a violation of CIP-007-1 R5. Specifically, user account passwords for one local account on a number of workstations and several accounts on one server were not changed at least annually, as required by the Standard. Further, FRCC_URE1 could not demonstrate the following: that logging for all accounts was enabled, as required by R5.1.2; that a policy was implemented to minimize the usage of admin and shared accounts, as required by R5.2; that default account passwords were changed prior to putting systems in service, as required by R5.2.1; that required audit trails were maintained for all user accounts, as required by R5.2.3; and that passwords had the complexity required by R5.3.2. | CIP-007-1 | R5 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE1 did not document a policy to limit use of shared accounts and lacked documentation of all the accounts and users who have access to such accounts. FRCC determined this violation posed a moderate risk because lack of this documentation could limit FRCC_URE1's control and accountability for use of shared and administrative accounts. The risk from this violation was limited because all users with such access were well-trained and maintained control and accountability which included not sharing passwords for shared and administrative accounts, minimizing the use (using only when required), utilizing individual accounts for routine applications and changing passwords when users with access were relocated or transferred. Further, in any condition when a user did not require access as a result of change in status, his or her access was revoked immediately. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) change and update password controls to correct gaps in the account management process; (2) communicated the required password change to procedures for the addition of users in the card key system to ensure that new users are set up with the requirement for their passwords to expire at least annually; (3) document the change and train key individuals on the revised procedure to set up interactive card key user accounts in the card key system; (4) perform a complete review of CIP-007 R5 compliance and document and report the findings to FRCC; and (5) complete a comprehensive training and awareness workshop to incorporate all the lessons learned and introduce newly implemented procedure required to maintain compliance with CIP-007 R5. | 12/1/2012 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-09-28 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007930 | Settlement Agreement | FRCC_URE1 self-reported a violation of CIP-005-1 R1. FRCC_URE1 failed to identify and document its serially connected communication end points as access points to the Electronic Security Perimeter (ESP), as required by the Standard. Even though the devices are using serial communication protocols, configuration requires use of network switches and host subnet that uses routable protocol; therefore, the devices should have been identified and documented. The devices were protected within the Physical Security Perimeter (PSP) but not identified or documented on any of FRCC_URE1's CIP-005 evidence documentation. | CIP-005-1 | R1 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all the devices used serial, non-routable protocol and were protected within the PSP. FRCC determined that the violation posed a moderate risk because even though the access points were protected, devices connected to the access points were not completely protected and provided means of unauthorized access and misconfiguration. The risk was limited because the end points were protected with the termination of FRCC_URE1's fiber network and were only accessible to personnel who were thoroughly vetted and with direct responsibility for support and operation. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) update access points and the Critical Cyber Asset (CCA) documentation for newly identified access points: (2) create or update appropriate processes and procedures: (3) complete review of all Cyber Assets associated with Critical Assets to identify any additional access points using expanded interpretation; (4) determine and implement required controls for newly-identified access points including any required Technical Feasibility Exception requests, and report the findings to FRCC; (5) reduce access points by redesigning network and reconfiguring existing access point devices; and (6) relocate access points to new network segments and protect as per CIP requirements. | 12/1/2012 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit. FRCC considered FRCC_URE1's prior violation history.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007931 | Settlement Agreement | FRCC_URE1 self-reported that its cyber vulnerability assessments (CVAs) of the electronic access points to the Electronic Security Perimeter (ESP) did not comply with all requirements of CIP-005-1 R4. FRCC_URE1's documentation was not complete and could not demonstrate compliance with the requirements. The CVAs did include discovery of access points but did not include review of ports and services, review of default community strings, and a documented action plan for remediation of identified vulnerabilities. As part of its CVA, FRCC_URE1 performed a comprehensive scan with all results documented but did not complete all activities to comply with CIP-005-1 R4.2, R4.3 and R4.5. | CIP-005-1 | R4 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all devices were afforded the protections of the ESP. FRCC determined that the violation posed moderate risk because failure to perform a complete CVA can result in vulnerabilities in the system that would not be discovered or mitigated. While FRCC_URE1 failed to conduct and document the CVA results in the required manner, evidence demonstrated that all ESP access points were well-configured and only trusted network devices were allowed to communicate within the ESP. Further, known vulnerabilities and password controls were effectively addressed. | when FRCC_URE1 failed to complete a CVA which was in accordance with all requirements of the Standard | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) complete a vulnerability scan that includes discovery of all access points; (2) review default controls for accounts, passwords and community strings; (3) review ports and services; (4) update the vulnerability assessment procedure; and (5) document the results and create an action plan for remediating any identified vulnerabilities. | 12/1/2012 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007969 | Settlement Agreement | FRCC_URE1 self-reported that it failed to fully establish and implement a security patch management program for tracking, evaluating, testing, and installing applicable cybersecurity software patches for all Cyber Assets within the Electronic Security Perimeter (ESP). FRCC_URE1 did not complete the assessment and installation of all patches that were of lower risk. Further, some third-party applications were not included in the patch management program. | CIP-007-1 | R3 | Lower | Severe | FRCC determined that the violation posed a minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system (BPS) because a patch management program did exist to apply high and critical security patches to Critical Cyber Assets and Cyber Assets, and the Cyber Assets reside within the Electronic and Physical Security Perimeter (PSP) and are thus provided several layers of ESP and PSP protections. Further, no unauthorized use or breach occurred during the period of the violation. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) conduct a complete review of Cyber Assets including software inventory; (2) research and define requirement for patching solutions for all applications; (3) install and implement patching solution(s) infrastructure and rollout to all Cyber Assets; and (4) train and communicate changes to personnel and issue any required Technical Feasibility Exception requests. | 2/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007972 | Settlement Agreement | FRCC_URE1 self-reported that it did not identify three virtual servers and three workstations as Critical Cyber Assets (CCAs), as required by CIP-002-1 R3. | CIP-002-1 | R3 | High | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because these assets were protected within the Electronic Security Perimeter (ESP) and a Physical Security Perimeter (PSP). FRCC determined that the violation posed a moderate risk because failure to identify CCAs properly could jeopardize compliance with other CIP Standards. While these CCAs lacked some security controls, FRCC determined that none of the gaps posed a serious or substantial risk because all these systems were within the protected ESP and PSP, and security controls for access control, change management, testing, account management, and strong configuration were effectively applied to the subject Cyber Assets. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1: (1) completed a review of its CCA identification process(es) to include an expanded interpretation of virtual system hosts and classification based upon functional capability; (2) designed and implemented necessary environment changes; (3) updated the required documentation for newly-identified Cyber Assets; and (4) filed any required Technical Feasibility Exceptions (TFEs). | 2012-03-08 | 2012-08-02 | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007970 | Settlement Agreement | FRCC_URE1 self-reported a violation of CIP-004-3 R4. FRCC_URE1 failed to revoke access to Critical Cyber Assets (CCAs) for four employees within seven calendar days from the date when access was no longer required, as required by the Standard. Access was revoked as provided below: Employee 1 - Access was revoked more than 5 months after the required by date. This 11-year employee only had password change and report creation access. Employee 2 - Access was revoked less than 3 weeks after the required by date. This 14-year employee had physical access to all areas of the subject generation plant. Employee 3 - Access was revoked less than 3 weeks after the required by date. This 40-year employee had cyber access. Employee 4 - Access was revoked less than 1 week after the required by date. This 3-month intern-contractor had physical access to the subject generation plant. All four employees had completed a successful personnel risk assessment (PRA) and cybersecurity training prior to being granted access. | CIP-004-3 | R4.2 | Lower | Moderate | FRCC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the subject individuals were trusted employees who were thoroughly vetted by FRCC_URE1's PRA process and were appropriately trained as per CIP-004. These individuals were transferred or retired from service and none of the instances were for cause. None of the individuals accessed the systems after the status change. | when access should have been revoked for the first employee | when access was revoked for the fourth employee | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Self-Report | In accordance with its Mitigation Plan, FRCC_URE1: (1) completed a review of all NERC CCA access removal requests to identify all instances where access was not timely revoked and revoke any unnecessary access. No additional instances of failure to timely revoke access were discovered; (2) updated its termination documentation to clarify accounts being removed, deleted, or disabled; and (3) trained IT security team members on the access removal process. | 2011-12-08 | 2012-05-02 | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008231 | Settlement Agreement | During an Audit, FRCC discovered that FRCC_URE1 was in violation of CIP-005-1 R2.2. FRCC_URE1 did not ensure that, for one of its access points to the Electronic Security Perimeter (ESP), only ports required for operations and monitoring were enabled. It did allow certain networks to communicate to the assets within the ESP, but did not specify the ports. Additionally, FRCC_URE1 did not implement strong procedural or technical controls for remote interactive access, in violation of CIP-005-1 R2.4. FRCC_URE1 was using a login process which was repeated on two different systems but was not sufficient to demonstrate that the control addressed authenticity of the accessing party. | CIP-005-1 | R2; R2.2; R2.4 | Medium | Severe | FRCC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all the ports that were open but not required for operations and monitoring were limited to trusted networks also controlled and maintained by FRCC_URE1. FRCC determined that the violation posed a moderate risk because ports and services that are not required for normal operations can be exploited in cyber attacks and lack of strong authentication at the access points may allow an unauthorized remote interactive access to the ESP. The risk was limited because for all interactive remote access, FRCC_URE1 implemented a secured jump host that limited direct access to the ESP and only provided access to limited applications and control functions. Lastly, FRCC_URE1 has limited risk from remote access by use of encryption and digital certificates when such remote access is initiated over the internet. | when the Standard became mandatory and enforceable for FRCC_URE1 | Present | $75,000 (for FRCC201000409, FRCC2011007926, FRCC2011007927, FRCC2011007928, FRCC2011007930, FRCC2011007931, FRCC2011007969, FRCC2011007972, FRCC2011007970, and FRCC2011008231) | Compliance Audit | In accordance with its Mitigation Plan, FRCC_URE1 will: (1) review the complete firewall configuration and review use of ports for all Cyber Asset configuration; (2) create ports and services baseline identification; (3) update action plan; (4) reconcile ports and services with approved baselines; and (5) submit Technical Feasibility Exception requests as necessary. | 6/1/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC_URE1’s established, formal program for internal compliance was considered as a mitigating factor for penalty determinations. In those instances in which FRCC_URE1 submitted Self-Reports in close proximity to an upcoming audit, FRCC awarded cooperation credit.
2012-08-31 | FERC | NP12-44-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1), a subsidiary of Unidentified Registered Entity (RFC_URE) | NCRXXXXX | RFC2011001265 | Settlement Agreement | RFC_URE1 notified ReliabilityFirst by telephone of a violation of CIP-004-3 R3.1. RFC_URE1 submitted a written Self-Report to ReliabilityFirst. RFC_URE's subsidiary, on behalf of RFC_URE1, contracted with another entity to provide security services, including security officers and, for part of the relevant period, seven-year criminal checks for certain of those security officers. A RFC_URE corporate security employee was asked by a RFC_URE employee to look into what investigation is conducted for persons who have only recently arrived in the United States. Based upon that inquiry, the RFC_URE corporate security employee brought the concern to the attention of a supervisor. As a result of that inquiry, RFC_URE discovered that for two other entity contract security officers to whom RFC_URE1 granted authorized unescorted physical access to Critical Cyber Assets (CCAs), the other entity had not performed full seven-year criminal checks despite certifying that seven-year criminal checks were conducted. Instead, the other entity only conducted a criminal check for the time period the contract security officers resided in the United States. One contract security officer resided in the United States for two months before beginning work at RFC_URE, and the other contract security officer resided in the United States for three months before beginning work at RFC_URE. When RFC_URE discovered this issue, RFC_URE sought to determine whether other entity employees working at RFC_URE1 had similarly deficient personnel risk assessments (PRAs). RFC_URE discovered that four additional other entity employees currently working at RFC_URE1 with authorized unescorted physical access to CCAs had criminal checks for less than seven years. One of these employees had not been over eighteen years old for seven years, two of these employees had not resided in the United States for seven years, and one of these employees had resided in the United States for seven years. In addition, RFC_URE discovered that two other entity employees no longer working at RFC_URE facilities had criminal checks for less than seven years while working at RFC_URE1. All security officers at issue were assigned to the general RFC_URE office, where they could provide services for either RFC_URE1 or its affiliate RFC_URE2. The PRAs for these six individuals occurred in preparation for mandatory enforcement of the CIP Standards. A RFC_URE service provider conducted these PRAs of the other entity employees. While RFC_URE1 personnel performed a manual review of these PRAs provided by the vendor, RFC_URE1 was unaware of the lack of full seven-year criminal checks for these six individuals for a twenty-two month period. | CIP-004-3 | R3.1 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The facts and circumstances of this violation are confined to the PRAs conducted for the security officers for another entity, and do not evidence a systematic issue with RFC_URE1's PRA program. RFC_URE1's PRA program included the background check requirement. Also, the seven-year background check requirement was included in RFC_URE1's contract for security services with the other entity. Importantly, RFC_URE and RFC_URE1 discovered this issue when a RFC_URE corporate security employee recognized that it would be difficult to obtain a seven-year criminal check for an individual who had only been in the United States for a few months and brought the issue to the attention of a supervisor. RFC_URE corporate security employee’s conduct evidences an institutional awareness of the CIP Standards. In addition, RFC_URE1 terminated the contract security officers’ authorized unescorted physical access to CCAs promptly upon learning that a seven-year criminal check was not conducted. RFC_URE1 then conducted a PRA with a complete seven-year criminal check and subsequently re-issued authorized unescorted physical access to Critical Cyber Assets to the six contract security officers still working at RFC_URE1. When RFC_URE1 conducted the seven-year criminal checks for the six individuals who had physical access, they discovered no disqualifying adverse information regarding these six individuals. In addition to reviewing the PRAs for all other entity contract employees, RFC_URE corporate security conducted an audit of a sample of PRAs for the RFC_URE population of individuals working at RFC_URE for seven years or less with authorized unescorted physical access to CCAs, including both employees and contractors. RFC_URE chose a random sample of 74 background checks, reviewed those background checks, and found no errors. | the date RFC_URE1 was required to comply with CIP-004 | the date RFC_URE1 revoked authorized unescorted physical access from the affected individuals still working at RFC_URE1 | 0 | Self-Report | RFC_URE1 took the following actions to mitigate the violation: (a) removed authorized unescorted physical access from the six affected individuals; (b) rescreened the individuals; (c) updated and distributed the list of contractors from which RFC_URE will accept PRAs to remove the other entity; (d) updated the internal job aid documents to reinforce the review of the Social Security Number trace report and another document to ensure the identification of seven years of residences and the implementation of seven-year criminal checks; (e) revised the hard copy of its documentation to include a request for the applicant to provide his or her past seven years of residences (the on-line version already included such a request); (f) conducted a random sample of 74 background checks using RFC_URE corporate audit services’ data sampling tool; and (g) provided a notification reminding all contractors that provide PRA background checks to RFC_URE of their obligation to complete full seven-year criminal checks. | 2012-02-29 | 2012-06-14 | Admits | ReliabilityFirst considered certain aspects of RFC_URE’s compliance program as mitigating factors. ReliabilityFirst considered that it discovered the violation through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered as mitigating factors the degree and quality of RFC_URE1’s cooperation and remedial action during the enforcement processes. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation constituted repetitive infractions. RFC_URE’s internal controls and institutional awareness of the CIP Standards is evident based upon RFC_URE’s conduct in this matter. RFC_URE discovered the issue due to the diligence of an employee. RFC_URE acted quickly and thoroughly to remediate the issue, and RFC_URE provided detailed guidance to its peers to promote awareness of the issue.
2012-08-31 | FERC | NP12-44-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2), a subsidiary of Unidentified Registered Entity (RFC_URE) | NCRXXXXX | RFC2011001266 | Settlement Agreement | RFC_URE2 notified ReliabilityFirst by telephone of a violation of CIP-004-3 R3. RFC_URE2 submitted a written Self-Report to ReliabilityFirst. RFC_URE's subsidiary, on behalf of RFC_URE2, contracted with another entity to provide security services, including security officers and, for part of the relevant period, seven-year criminal checks for certain of those security officers. A RFC_URE corporate security employee was asked by a RFC_URE employee to look into what investigation is conducted for persons who have only recently arrived in the United States. Based upon that inquiry, the RFC_URE corporate security employee brought the concern to the attention of a supervisor. As a result of that inquiry, RFC_URE discovered that for two other entity contract security officers to whom RFC_URE2 granted authorized unescorted physical access to Critical Cyber Assets (CCAs), the other entity had not performed full seven-year criminal checks despite certifying that seven-year criminal checks were conducted. Instead, the other entity only conducted a criminal check for the time period the contract security officers resided in the United States. One contract security officer resided in the United States for two months before beginning work at RFC_URE, and the other contract security officer resided in the United States for three months before beginning work at RFC_URE. When RFC_URE discovered this issue, RFC_URE sought to determine whether other entity employees working at RFC_URE2 had similarly deficient personnel risk assessments (PRAs). RFC_URE discovered that four additional other entity employees currently working at RFC_URE2 with authorized unescorted physical access to CCAs had criminal checks for less than seven years. One of these employees had not been over eighteen years old for seven years, two of these employees had not resided in the United States for seven years, and one of these employees had resided in the United States for seven years. In addition, RFC_URE discovered that two other entity employees no longer working at RFC_URE facilities had criminal checks for less than seven years while working at RFC_URE2. All security officers at issue were assigned to the general RFC_URE office, where they could provide services for either RFC_URE2 or its affiliate RFC_URE1. The PRAs for these six individuals occurred in preparation for mandatory enforcement of the CIP Standards. A RFC_URE service provider conducted these PRAs of the other entity employees. While RFC_URE2 personnel performed a manual review of these PRAs provided by the vendor, RFC_URE2 was unaware of the lack of full seven-year criminal checks for these six individuals for a twenty-two month period. | CIP-004-3 | R3.1 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The facts and circumstances of this violation are confined to the PRAs conducted for the security officers for another entity, and do not evidence a systematic issue with RFC_URE2's PRA program. RFC_URE2's PRA program included the background check requirement. Also, the seven-year background check requirement was included in RFC_URE2's contract for security services with the other entity. Importantly, RFC_URE and RFC_URE2 discovered this issue when a RFC_URE corporate security employee recognized that it would be difficult to obtain a seven-year criminal check for an individual who had only been in the United States for a few months and brought the issue to the attention of a supervisor. The RFC_URE corporate security employee’s conduct evidences an institutional awareness of the CIP Standards. In addition, RFC_URE2 terminated the contract security officers’ authorized unescorted physical access to CCAs promptly upon learning that a seven-year criminal check was not conducted. RFC_URE2 then conducted a PRA with a complete seven-year criminal check and subsequently re-issued authorized unescorted physical access to CCAs to the six contract security officers still working at RFC_URE2. When RFC_URE2 conducted the seven-year criminal checks for the six individuals who had physical access, they discovered no disqualifying adverse information regarding these six individuals. In addition to reviewing the PRAs for all other entity contract employees, RFC_URE corporate security conducted an audit of a sample of PRAs for the RFC_URE population of individuals working at RFC_URE for seven years or less with authorized unescorted physical access to CCAs, including both employees and contractors. RFC_URE chose a random sample of 74 background checks, reviewed those background checks, and found no errors. | the date RFC_URE2 was required to comply with CIP-004 | the date RFC_URE2 revoked authorized unescorted physical access from the affected individuals still working at RFC_URE2 | 0 | Self-Report | RFC_URE2 took the following actions to mitigate the violation: (a) removed authorized unescorted physical access from the six affected individuals; (b) rescreened the individuals; (c) updated and distributed the list of contractors from which RFC_URE will accept PRAs to remove the other entity; (d) updated the internal job aid documents to reinforce the review of the Social Security Number trace report and another document to ensure the identification of seven years of residences and the implementation of seven-year criminal checks; (e) revised the hard copy of its documentation to include a request for the applicant to provide his or her past seven years of residences (the on-line version already included such a request); (f) conducted a random sample of 74 background checks using RFC_URE corporate audit services’ data sampling tool; and (g) provided a notification reminding all contractors that provide PRA background checks to RFC_URE of their obligation to complete full seven-year criminal checks. | 2012-02-29 | 2012-06-14 | Admits | ReliabilityFirst considered certain aspects of RFC_URE’s compliance program as mitigating factors. ReliabilityFirst considered that it discovered the violation through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered as mitigating factors the degree and quality of RFC_URE2’s cooperation and remedial action during the enforcement processes. When assessing the penalty for the violation at issue, ReliabilityFirst considered whether the facts of this violation constituted repetitive infractions. RFC_URE’s internal controls and institutional awareness of the CIP Standards is evident based upon RFC_URE’s conduct in this matter. RFC_URE discovered the issue due to the diligence of an employee. RFC_URE acted quickly and thoroughly to remediate the issue, and RFC_URE provided detailed guidance to its peers to promote awareness of the issue.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102753 | Notice of Confirmed Violation | WECC_URE1 submitted a Self-Report to WECC concerning a violation of CIP-004-3 R4 due to WECC_URE1's to revoke access within seven calendar days for personnel who no longer required access to Critical Cyber Assets (CCAs), and failure to identify employees specific access rights to CCAs. Specifically, WECC identified four instances in which WECC_URE1 failed to revoke access to CCAs within seven days for personnel who no longer required such access. In addition, WECC identified two instances in which WECC_URE1 access lists failed to identify specific access rights because two employees with both physical and cyber access to CCAs were listed as only having physical access rights to CCAs. | CIP-004-3 | 4 | Medium | Moderate | WECC determined that the violation posed a minimal risk to the reliability of the bulk power system (BPS) because WECC_URE1 did identify and list all individuals with access to CCAs. In addition, all individuals within the scope of the violation had completed requisite Cyber Security training, and had completed Personnel Risk Assessments (PRAs). Finally, while access was not revoked within seven days after such access was no longer required, WECC_URE1 did revoke the employees’ access to CCAs within eight to sixteen days. Further, all individuals within scope of the violation alleged herein completed requisite Cyber Security training and completed Personnel Risk Assessments. | when WECC_URE1 was required to comply with the Standard | when the Mitigation Plan was completed | $27,800 (Settlement of WECC201102753 and WECC201102407) | Self-Report | WECC_URE1 revoked access to those employees who no longer required access. WECC_URE1 completed a comprehensive quarterly review of the CIP access log. | 2011-02-17 | 2012-08-24 | Does Not Contest | WECC considered as a mitigating factor that WECC_URE1 self-reported the violation of CIP-004-1 R4.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102407 | Notice of Confirmed Violation | WECC notified WECC_URE1 that WECC was initiating the Self-Certification process. WECC_URE1 submitted a Self-Report and a Self-Certification concerning a violation of PRC-005-1 R2.1 due to WECC_URE1's failure to perform pre-operational testing of current transformer (CT)/ potential transformer (PT) devices for two units of the Facility before returning the units to service. WECC determined that pursuant to WECC_URE1's maintenance and testing program (Program), CT/PT testing at the Facility was scheduled. However, the facility and associated protection systems were removed from service six months prior to the scheduled testing. The facility was returned to service after WECC_URE1 completed trip and functional tests. WECC_URE1 reviewed functional and trip test reports for the facility, and determined that pre-operational CT/PT load testing was not performed at the facility. Although WECC_URE1 completed CT/PT load testing, WECC determined that WECC_URE1's failure to complete pre-operational testing before putting the facility into service constitutes a violation of PRC-005-1 R2. | PRC-005-1 | 2 | High | Lower | WECC determined that the violation posed a minimal risk to the reliability of the bulk power system (BPS) because the scope of the violation is limited, in that, WECC_URE1 completed required testing for all other protection systems at the facility. In addition, WECC_URE1's failure to complete CT/PT testing at the facility represents only 8.33% CT/PT protection systems. Finally, when WECC_URE1 completed the required testing, approximately a month after returning the units to service, the protection systems devices were in good working condition. | when WECC_URE1 failed to perform testing of CT/PT devices before returning the units to service | when WECC_URE1 completed testing of the CT/PT devices | $27,800 (Settlement of WECC201102753 and WECC201102407) | Self-Certification | WECC_URE1 instructed one of its divisions not to operate facility until the CT/PT load tests were performed. WECC_URE1 completed the CT/PT load tests for the two units. WECC_URE1 issued a memo which designated a manger in each field division to be responsible for overseeing the protection system testing program for that field division. In addition, WECC_URE1 managers are required to prevent a unit from being operated if the protection system tests have not been completed, documented, and reviewed according to the identified test intervals or after a long outage. WECC_URE1 e-mailed the memo to each of the field division chiefs shared the memo with the appropriate staff. One of WECC_URE1's divisions implemented an order to help prevent this type of occurrence in the future at the field division. The order outlines one of WECC_URE1's divisions acceptance procedures that must be followed before returning a unit to service after the completion of major maintenance activities. On its effective date, this order was added to the division file server and made available to the plant operations personnel. The division chief operator, who was involved in preparing the order, was informed that the order had become effective. Hard copies were distributed a couple of weeks later to other lead and supervisory personnel. | 2010-09-30 | 2011-11-08 | Does Not Contest | WECC considered as aggravating factors that WECC_URE1 had two previous PRC-005-1 R2 violations.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009556 | Settlement Agreement | WECC conducted an on-site compliance audit of WECC_URE2 (Audit) and determined that WECC_URE2 violated CIP-005-1 R2.2 for failing to ensure that only required ports and services for operations and monitoring of Cyber Assets within Electronic Security Perimeters (ESP) were enabled and documented as required by R2.2. At the Audit, WECC reviewed WECC_URE2's document annotating the authorized ports and services baseline for WECC_URE2's security operations control center and backup control center access points. Based on the record, WECC determined that WECC_URE2 failed to document an internet protocol and port as access points to its backup control center ESP. Also, a default password was enabled, thereby potentially allowing an attacker to enumerate critical information about the access point, including the ability to infer information concerning the ESP network topology. WECC_URE2 maintains that its internet protocol service, port, and the password were not enabled, as determined by WECC, because WECC_URE2's internet protocol service was in its default setting, which was precluding access to the ESP. Also, WECC_URE2's firewall was effectively denying access to the internet protocol server and port. However, WECC determined that despite the fact that it was in its default setting, it was still enabled, in violation of R2.2. WECC determined that WECC_URE2 failed to enable only those ports and services required for operations and monitoring of Cyber Assets within the ESP and failed to document an unauthorized service to its access point to its backup control center ESP, in violation of CIP-005-1 R2.2. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE2 did not identify an unauthorized service to its backup control center ESP, WECC_URE2 provided a defense-in-depth architecture, including electronic access controls for authentication and encryption at the ESP. In addition, WECC_URE2 had physical security controls in place at the Physical Security Perimeter (key card readers, locked doors and cameras), thus reducing the likelihood of a successful cyber attack. Further, WECC_URE2's internet protocol software vendor verified that the service was in its default setting, which was set to preclude access and prevent an attacker from enumerating critical information about the access point, including the ability to infer information concerning the ESP network topology, thereby reducing the risk to the BPS. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $30,000 (for WECC2012009556 and WECC2012009557) | Compliance Audit | In accordance with its Mitigation Plan, WECC_URE2 completed the following actions: 1) Contacted its internet protocol software vendor to confirm that the service was not configured, and that in its state, the internet protocol services were not available and a potential cyber attacker could not gain information about WECC_URE2's ESP network topography, or gain access to the ESP; 2) Retained a consultant to verify its vendor's representation of facts by testing the service independently; 3) Disabled the server and in so doing also stopped the server from running on the access point to the ESP; 4) Upgraded its cyber vulnerability assessment procedure to ensure the use of "show run all" to verify the server is not enabled; and 5) Conducted informal meetings to communicate the updated procedures to the appropriate WECC_URE2 subject matter experts. | 2012-01-24 | 2012-06-15 | Agrees/ Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009557 | Settlement Agreement | WECC conducted an on-site compliance audit of WECC_URE2 (Audit) and determined that WECC_URE2 violated CIP-005-1 R4 for failing to perform an accurate cyber vulnerability assessment (CVA) due to inconsistencies found in the CVA results, which did not correlate with the actual access point configurations. During the Audit, WECC determined that the CVA did not detect an internet protocol service running on a port open for an access point to the Electronic Security Perimeters (ESPs) of WECC_URE2's backup control center. WECC_URE2 failed to conduct a review to verify that only ports and services required for the operations of these access points were enabled and did not discover all access points to the backup control center ESP. WECC_URE2 maintains that its internet protocol service and port were not enabled, as determined by WECC, because WECC_URE2's internet protocol service was in its default setting, which was precluding access to the ESP. However, WECC determined that despite the fact that it was in its default setting, it was still enabled. WECC_URE2's firewall was effectively denying access to the internet protocol server and port. WECC determined that WECC_URE2 failed to verify in its CVA that only those ports and services required for operations at its access points were enabled and that it failed to appropriately discover all access points to the ESP, in violation of CIP-005-1 R4. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE2 did not identify an unauthorized service to its backup control center ESP, WECC_URE2 provided a defense-in-depth architecture, including electronic access controls for authentication and encryption at the ESP. In addition, WECC_URE2 had physical security controls in place at the Physical Security Perimeter (key card readers, locked doors and cameras), thus reducing the likelihood of a successful cyber attack. Further, WECC_URE2's internet protocol software vendor verified that the service was in its default setting, which was set to preclude access and prevent an attacker from enumerating critical information about the access point, thereby reducing the risk to the BPS. | when the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $30,000 (for WECC2012009556 and WECC2012009557) | Compliance Audit | In accordance with its Mitigation Plan, WECC_URE2 completed the following actions: 1) Contacted its internet protocol software vendor to confirm that the service was not configured, and that in its state, the internet protocol services were not available and a potential cyber attacker could not gain information about WECC_URE2's ESP network topography, or gain access to the ESP; 2) Retained a consultant to verify its vendor's representation of facts by testing the service independently; 3) Disabled the server and in so doing also stopped the server from running on the access point to the ESP; 4) Upgraded its CVA procedure to ensure the use of "show run all" to verify the server is not enabled; and 5) Conducted informal meetings to communicate the updated procedures to the appropriate WECC_URE2 subject matter experts. | 2012-01-24 | 2012-06-15 | Agrees/ Stipulates | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103008 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R2 for a failure to file timely Technical Feasibility Exception (TFE) requests for six devices on which it could not disable ports and services that were not used for normal or emergency operations. Approximately two months after the submittal of its Self-Certification, WECC_URE3 submitted a TFE for the six devices in question. WECC_URE3 stated that although the vendor published a configuration command to close ports on these devices, WECC_URE3 has not been able to successfully implement the configuration command and close ports not used for normal or emergency operations. WECC determined that for each of the six devices at issue, WECC_URE3 failed to ensure that all ports and services not required for normal and emergency operations were disabled pursuant to CIP-007-1 R2 by when WECC_URE3 was required to comply with the Standard. Further, WECC determined that the devices fall within the scope of WECC_URE3's TFE request and issued a notice of TFE approval. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, all six devices were physically secured within a Physical Security Perimeter (PSP), thereby limiting physical access to ports and reducing the risk to the BPS. Second, all ports were also secured within an Electronic Security Perimeter (ESP) equipped with an intrusion detection system that monitored traffic on all ports within the ESP. Should access be attempted through any one of the ten ports within scope of the violation, the intrusion detection system is programmed to detect intrusion and to immediately alert the cyber security staff, thereby reducing the risk to the BPS. WECC asserted that it is not aware of any instances of unauthorized access to the PSPs or ESPs during the pendency of this violation. Although WECC_URE3 originally failed to file a timely TFE request, WECC determined that the six devices at issue fell within the scope of WECC_URE3's TFE request, which was approved by WECC. | when WECC_URE3's prior violation of this Standard was mitigated | when WECC_URE3 filed its TFE for the six devices | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | WECC_URE3 submitted a Mitigation Plan, but WECC determined that the Mitigation Plan did not include all mitigating activities undertaken by WECC_URE3 and did not reflect the full scope of these activities. WECC_URE3 submitted a revised Mitigation Plan that included the full scope of the mitigating activities. In accordance with its Mitigation Plan, WECC_URE3 completed the following actions: 1) Performed a complete analysis of all in-scope Cyber Assets to determine where TFEs are required and filed Self-Reports and Mitigation Plans in the instances where TFEs were required; 2) Gathered all vendor and manufacturer documentation supporting its request for a TFE and all documentation describing the compensating measures that were in place on from the day WECC_URE3 was required to comply with this Standard; 3) Submitted all required TFEs to WECC and began a TFE monitoring process; 4) Initiated a change request to replace the switches; 5) Modified its Hardening Checklist to ensure vendor port and services recommendations are reviewed for applicability, and also modified its change management process to incorporate the completion of the Hardening Checklist. WECC_URE3 modified its security training to reinforce the use of the Hardening Checklist in the change management process; and 6) Configured a new switch and replaced four older ones; performed device hardening and security control testing, among other activities designed to ensure compliance with this Standard. | 2012-02-28 | 2012-05-25 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC reviewed WECC_URE3's compliance history and determined it was as an aggravating factor in determining the penalty.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103009 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R4 for a failure to file Technical Feasibility Exceptions (TFEs) for 27 devices on which the use of anti-virus software was not technically feasible. Approximately two weeks after the submittal of WECC_URE3's Self-Certification, WECC_URE3 submitted three TFE requests for 15 devices and amended the requests four days later. WECC confirmed that WECC_URE3 filed TFEs for the remaining 12 devices, thus requesting a TFE for all 27 devices. WECC determined the scope of the violation to include 27 devices associated with two Critical Assets at two of its facilities. WECC determined that WECC_URE3 failed to use anti-virus software and implement malware prevention measures for the twenty-seven (27) devices at issue as of the date it was required to comply with the Standard, in violation of this Standard. Further, WECC determined that the devices at issue fall within the scope of WECC_URE3's TFE requests and issued a notice of approval. | CIP-007-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, all devices were physically secured within a Physical Security Perimeter (PSP), thereby limiting physical access to ports. Further, all devices were logically secured within an Electronic Security Perimeter (ESP) equipped with an Intrusion Detection System that monitored traffic on all ports within the ESP. Finally, although WECC_URE3 failed to file a timely TFE request, WECC determined the 27 devices at issue fell within the scope of WECC_URE3's TFE requests, which were approved by WECC. | when WECC_URE3's prior violation of this Standard was mitigated | when WECC_URE3 filed its TFEs | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | In accordance with its Mitigation Plan, WECC_URE3 took the following actions: 1) Performed a complete analysis of all in-scope Cyber Assets to determine if additional TFEs were required and filed Self-Reports and Mitigation Plans where necessary; 2) Gathered all vendor and manufacturer documentation supporting its request for TFEs; 3) Gathered all documentation describing the compensating measures that were in place as of the day WECC_URE3 was required to comply with this Standard and describing any modifications since that date; and 4) Submitted all required TFEs to WECC and began a TFE monitoring process. | 2011-10-14 | 2012-03-16 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC considered WECC_URE3's negative compliance history as an aggravating factor when determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103010 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R5.3 for a failure to ensure that all passwords satisfied the criteria outlined under R5.3. Approximately two weeks after the submittal of WECC_URE3's Self-Certification, WECC_URE3 submitted three Technical Feasibility Exceptions (TFEs) requests for the 13 devices at issue. WECC_URE3 failed to comply with CIP-007-1 R5.3 and its subrequirements for one Cyber Asset, and failed to ensure that passwords were changed annually for 12 Cyber Assets, as required by R5.3.3. WECC determined that WECC_URE3 failed to ensure that the passwords implemented for the 13 Critical Cyber Asset (CCA) devices conformed to the criteria outlined in CIP-007-1 R5.3, in violation of this Standard. Further, WECC determined that the 13 CCAs at issue are within the scope of WECC_URE3's three TFE requests. | CIP-007-1 | R5.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE3 failed to ensure that the 13 CCAs satisfied the password criteria of R5.3.3, the risk was mitigated by the limited scope of the violation and the compensating measures in place during the violation period. The scope was limited because only 13 CCAs were involved in this violation. Also, access to the 13 CCAs was limited to personnel who have received training and had successfully completed Personnel Risk Assessments (PRA). Further, electronic access to these devices was logged and monitored by WECC_URE3. Finally, although the passwords were not fully compliant with the requirements of R5.3.3, WECC determined that some protection was afforded to a number of the devices equipped with passwords. | when WECC_URE3's prior violation of this Standard was mitigated | when WECC_URE3 filed its TFEs | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | WECC_URE3 submitted a Mitigation Plan, but WECC rejected it. WECC_URE3 submitted a revised Mitigation Plan outlining additional activities to mitigate this violation. WECC Reviewed WECC_URE3's Revised Mitigation Plan and rejected it due to an inconsistent completion date. WECC_URE3 submitted a second Revised Mitigation Plan. WECC reviewed the Revised Mitigation Plan issued Notice of Mitigation Plan Acceptance. In accordance with its Mitigation Plan, WECC_URE3 took the following actions: 1) Performed a complete analysis of all in-scope Cyber Assets to determine if additional TFEs were required and filed Self-Reports and Mitigation Plans where necessary; 2) Gathered all vendor and manufacturer documentation supporting its request for TFEs; 3) Gathered all documentation describing the compensating measures that were in place as of the day WECC_URE3 was required to comply with this Standard and describing any modifications since that date; 4) Submitted all required TFEs to WECC and began a TFE monitoring process; and 5) Opened a change request, assigned resources and developed test cases, performed integrated platform testing, staged changes for implementation; implemented the changes into the production environment and closed the change request. | 2012-03-30 | 2012-05-10 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC considered WECC_URE3's negative compliance history as an aggravating factor when determining the penalty amount.
2012-08-31 | FERC | NP12-44-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201103011 | Settlement Agreement | WECC notified WECC_URE3 that WECC was initiating the semi-annual CIP Self-Certification process and that WECC_URE3's Self-Certification submittal was due. WECC_URE3 submitted a Self-Certification citing noncompliance with CIP-007-1 R6 for a failure to implement automated tools and organizational process controls to monitor system events that are related to cyber security. WECC determined that WECC_URE3 failed to implement automated tools or organizational process controls to monitor system events for a total of 15 Cyber Assets within two Electronic Security Perimeters (ESPs). The 15 devices at issue include transmitters, Energy Management System (EMS) servers, historian servers, ICCP servers, data storage devices, and Human Machine Interface (HMI) devices. For one device, described as a "time server," implementation of controls was represented to be "technically infeasible" by WECC_URE3. Irrespective of WECC's Technical Feasibility Exceptions (TFEs) review, WECC determined that for the remaining 14 devices, implementation of automated or process controls under CIP-007-1 R6 was technically feasible. WECC, therefore, determined that WECC_URE3 was in violation of CIP-007-1 R6 for its failure to implement CIP-007-1 R6 controls for the 15 devices at issue. WECC_URE3 submitted three TFE filings, for the 15 devices included in the CIP-007-1 R6 noncompliance Self-Certification. WECC approved the TFEs for the 15 devices at issue. WECC determined that WECC_URE3's filing of a TFE for the "time server" may affect the violation period for this device, but did not obviate compliance with CIP-007-1 R6 prior to the TFE filing. WECC also determined that WECC_URE3 failed to implement controls to monitor and log system events for the 14 devices located within two ESPs, in violation of CIP-007-1 R6. | CIP-007-1 | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because although WECC_URE3 failed to implement automated tools and organizational process controls for 15 devices, the risk to the BPS was mitigated by the measures in place during the violation period. WECC determined that the scope of the violation was limited to 15 devices. Further, all individuals with logical and/or unescorted physical access rights have completed Personnel Risk Assessments (PRA) and Cyber Security training, thereby reducing the risk to the BPS. In addition, all devices within the scope of the violation were contained within a Physical Security Perimeter (PSP) and ESP, whereby access was controlled, logged and monitored. Additionally, any unauthorized access attempts would have triggered alarming. WECC, therefore, determined that WECC_URE3 noncompliance with CIP-007-1 R6 posed a moderate risk to the BPS. | when the Standard became mandatory and enforceable | when WECC_URE3 filed TFEs | $50,000 (for WECC201103008, WECC201103009, WECC201103010, and WECC201103011) | Self-Certification | WECC_URE3 submitted a Mitigation Plan but WECC determined that the Mitigation Plan did not include all mitigating activities undertaken by WECC_URE3 and did not reflect the full scope of these activities. WECC_URE3 submitted a revised Mitigation Plan. In accordance with its Mitigation Plan, WECC_URE3 took the following actions to mitigate the instant violation: 1) Performed a complete analysis of all in-scope Cyber Assets to determine where TFEs are required and filed Self-Reports and Mitigation Plans in the instances where TFEs were required; 2) Gathered all vendor and manufacturer documentation supporting the request for a TFE and all documentation describing the compensating measures that were in place from the day WECC_URE3 was required to comply with this Standard; 3) Gathered all documentation describing the compensating measures that were in place as of the day WECC_URE3 was required to comply with this Standard and describing any modifications since that date; 4) Submitted all required TFEs to WECC and began a TFE monitoring process; and 5) Opened a change request, assigned resources and developed test cases, performed integrated platform testing, staged changes for implementation; implemented the changes into the production environment and closed the change request. | 2012-03-30 | 2012-05-25 | Agrees/ Stipulates | WECC applied the following factors in determining the penalty amount: 1) During the past year, WECC_URE3 has taken significant steps to improve its compliance culture and its internal compliance program (ICP). Therefore, WECC considered WECC_URE3's ICP to be a mitigating factor in determining the penalty amount. 2) WECC considered WECC_URE3's negative compliance history as an aggravating factor when determining the penalty amount.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009702 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1.8 for failing to afford Cyber Assets used in the access control and monitoring of three Physical Security Perimeters (PSPs) protective measures, as specified in CIP-007-1 R5. Consequently, default accounts on nine physical access control panels were not disabled when installed. This failure to remove, disable or rename default accounts as required under CIP-007-1 R5 for nine physical access control panels used in the access control and monitoring of three PSPs resulted in a violation of CIP-006-1 R1.8. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1's physical access control panels were all located within PSPs with no direct external physical or cyber access. Also, only one default account was active per panel. In addition, WECC_URE1 failed to afford Cyber Assets protective measures specified in only CIP-007-1 R5.2.1 (the specific protective measure that was not afforded) and all the other protective measures were afforded. | when the Standard became mandatory and enforceable to WECC_URE1 | Mitigation Plan completion | 7500 | Self-Report | WECC_URE1 completed the following mitigation activities: 1) Followed its disciplinary procedure towards the employee who did not follow the associated change control program procedures for the installation of new assets; 2) Removed all default accounts from the physical access control panels; 3) Performed refresher training by reiterating to the physical security staff the importance of following WECC_URE1's change control program for new assets; 4) Created an electronic calendar reminder task for a manager to periodically spot check panel configurations; and 5) Submitted a Technical Feasibility Exception (TFE) for the physical access control panels. | 2012-02-27 | 2012-05-10 | Agrees/ Stipulates | WECC_URE1's internal compliance program (ICP) was a mitigating factor in the penalty determination. WECC applied cooperation credit for reporting this violation because WECC_URE1 submitted the Self-Report after WECC notified WECC_URE1 of its upcoming audit. WECC determined that no adjustments to the penalty were warranted because all milestones were completed by the approved completion date, except for submitting a TFE for the physical access control panels. The TFE submittal did not increase the risk to the BPS, albeit it did extend the completion date.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008699 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-005-1 R2. WECC_URE2 failed to fully document, individually or by specific groups, the configuration of the ports and services at all Electronic Security Perimeter (ESP) access points. WECC determined that WECC_URE2 did enable only those ports and services required for operations and for monitoring Cyber Assets within the ESP, but failed to document, individually or by specified grouping, the configuration of those ports and services, in violation of CIP-005-1 R2.2 | CIP-005-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to fully document the configuration of the ports and services in question, WECC_URE2 fully documented a process addressing services and addressing one category of ports. In addition, WECC determined that WECC_URE2 implemented processes and mechanisms used in ESP access controls. Finally, WECC determined that this violation presented a documentation issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) Identified and implemented enhancements needed in documentation and procedures to meet audit expectations; 2) Modified its CIP-005-3a R2 Electronic access controls procedure; 3) Developed of a new report to provide evidence for all access points; 4) Conducted management review and approval of WECC_URE2's enhanced processes and evidence for all cyber assets covered by CIP- 005 R2.2, in accordance with the WECC_URE2's internal compliance program (ICP); and 5) Conducted staff meetings and training to ensure that WECC_URE2's personnel understood the new procedure and followed all processes necessary to ensure complete and consistent evidence for all ports and services. | 2011-11-30 | 2012-05-31 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009701 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-005-1 R1.5. Based on the Self-Report, WECC determined that WECC_URE2 failed to fully document the configuration of ports and services for Cyber Assets used in the Electronic Security Perimeter (ESP) access control and monitoring, as described in CIP-005-1 R2.2 and required by CIP-005-1 R1.5. | CIP-005-1 | R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to fully document the configuration of the ports and services as described in R2.2, WECC_URE2 fully documented a process addressing services and addressing one category of ports. Also, WECC_URE2 ensured that only the ports and services required for normal operations and monitoring were enabled during the violation period. WECC_URE2 ensured that the Cyber Assets requiring electronic access control and monitoring were afforded 96.6% of the protective measures referenced in R1.5. Finally, WECC determined that this violation presented a documentation issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) Identified and implemented enhancements needed in documentation and procedures to meet audit expectations; 2) Modification to CIP-005-3a R2 Electronic access controls procedure; 3) Developed of a new report to provide evidence for all access control and monitoring (ACM); 4) Conducted management review and approval of WECC_URE2's enhanced processes and evidence for all cyber assets covered by CIP-005 R1.5, in accordance with WECC_URE2's internal compliance program (ICP); and 5) Conducted staff meetings and training to ensure that WECC_URE2 personnel understood the new procedure and followed all processes necessary to ensure complete and consistent evidence for all ports and services. | 2011-11-30 | 2012-05-31 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009043 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-006-1 R1 because it failed to secure five Critical Cyber Assets (CCAs) within a Physical Security Perimeter (PSP). Based on the Self-Report, WECC determined that WECC_URE2 failed to secure five CCAs within a PSP, in violation of CIP-006-1 R1.1. | CIP-006-1 | R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to ensure that five CCAs were located within a PSP, the risk was mitigated by several factors. The CCAs were located within a secured generation project with limited access to the site, which was monitored and controlled by WECC_URE2. Also, WECC determined that the scope of the violation was limited because it only involved five CCAs, thus reducing the risk to the BPS. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) WECC_URE2 took immediate steps to increase the physical security measures surrounding these devices; 2) WECC_URE2 completed an inventory of the assets applicable to the CIP standards that are required to be within a PSP and found no additional assets located outside of their defined PSPs; 3) Completed site walkthrough/visits of all PSPs; 4) Completed relocation of the devices to their appropriate identified PSP; and 5) Modified the annual review and approval of the CCA list as required in CIP-002-3 R3 to include a physical inventory of all the devices on the list to verify they are located within the appropriate PSP. | 2012-01-12 | 2012-05-18 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history in determining the penalty amount.
2012-08-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008647 | Settlement Agreement | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-007-1 R2. WECC_URE2 failed to fully document a process to ensure that only those ports and services required for the normal and emergency operations were enabled on 63 Cyber Assets and Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). Based on the Self-Report, WECC determined that although WECC_URE2 did enable only ports and services required for normal and emergency operations on Cyber Assets and CCAs within an ESP, WECC_URE2 failed to fully document the configuration of those ports and services, in violation of CIP-007-1 R2. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE2 failed to failed to document a comprehensive process pursuant to CIP-007-1 R2, WECC_URE2 did document a process addressing services and one category of ports. Also, WECC_URE2 ensured that only ports and services required for normal and emergency operations were enabled on the 63 Cyber Assets. Further, the Cyber Assets were located within the PSP and ESPs, and were afforded the protections required by CIP-005-1 and CIP-006-1, which reduced the risk to the BPS. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $15,000 (WECC2011008699; WECC2012009701; WECC2011009043; and WECC2011008647) | Self-Report | WECC_URE2 submitted as complete a Mitigation Plan, stating that the following actions were taken to mitigate the instant violation: 1) Identified and implemented enhancements needed in documentation and procedures to meet audit expectations; 2) Implemented documentation enhancements as follows: Modified its CIP-005-3a R2 Electronic access controls procedure; modified its CIP-007-3 R2 ports and services procedure; and developed new reports; and 3) Conducted management review and approval of WECC_URE2's enhanced processes and evidence for all cyber assets covered by CIP- 007-1 R2, in accordance with the WECC_URE2's internal compliance program (ICP). | 2011-11-30 | 2012-04-11 | Does not contest | WECC considered WECC_URE2's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102804 | Settlement Agreement | WECC_URE3 self-reported a violation of CIP-006-1 R1. Specifically, a WECC_URE3 employee logged onto a physical access control system server located in an Electronic Security Perimeter (ESP) without using two-factor authentication. The individual accessed the server using a tunneling protocol that was used for authentication between the ESP and a directory server. WECC_URE3's process to ensure strong access controls to the server is to implement two-factor authentication. WECC found that WECC_URE3 did not afford the protective measures of CIP-005 R2.4 to the server since the two-factor authentication controls were circumvented. Therefore, WECC determined that WECC_URE3 had a violation of CIP-006-1 R1.8 because it did not apply all the protective measures outlined in R1.8 to Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP), specifically one server. WECC also determined that CIP-005 R2 does not itself apply to the server as it is a server that is a Cyber Asset used in physical access control and monitoring, but is not a Critical Cyber Asset. | CIP-006-1 | R1.8 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, the server for the access control and monitoring was in an ESP and Physical Security Perimeter (PSP). The individual involved was authorized to access it and had current CIP training and a valid personnel risk assessment. Additionally, all devices within the ESP had anti-virus protections installed, only those ports and services necessary were enabled, devices were password protected, the entity had 24 hours a day and 7 days a week electronic monitoring for the ESP in scope, and access was limited to fewer than five WECC_URE3 personnel. | when the Standard became mandatory and enforceable for WECC_URE3 | when WECC_URE3 disabled the tunneling protocol, ensuring the protective measures required by CIP-006-1 R1.8 applied to WECC_URE3's Cyber Assets used in physical access control and monitoring Prior to 4/1/2010, WECC_URE3 was in violation of CIP-006-1 R1.8. When Version 2 of the Standard was approved, the requirement number for the applicable language was changed. Therefore, from 4/1/2010 until Mitigation Plan completion, WECC_URE3 was in violation of CIP-006 R2.2. | $39,000 (for WECC201102804; WECC201102943; and WECC201102944 ) | Self-Report | To mitigate the violation, WECC_URE3 immediately instructed its personnel to cease all remote access via the tunneling protocol and provided training associated with WECC_URE3's authentication procedures. WECC_URE3 also created an alert and associated escalation process for any protocol access to the Cyber Asset that did not originate from two-factor authentication. Finally, WECC_URE3 disabled the tunneling protocol. | 2011-05-24 | 2012-03-16 | Agrees/ Stipulates | WECC considered WECC_URE3's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC also considered WECC_URE3's compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102943 | Settlement Agreement | WECC_URE3 self-reported a violation of CIP-007-3 R5. WECC_URE3 uses a single security event monitoring solution to ensure compliance with CIP-007 R5 and R6. The solution requires that a log collector pull system event logs (used for audit trail and security status monitoring) from each Cyber Asset within the Electronic Security Perimeter (ESP). A configuration change to the service account from an administrator account to one with fewer privileges caused WECC_URE3's log collector to not pull logs from 23 Cyber Assets within two ESPs, specifically within WECC_URE3's ESPs at its control centers. WECC determined that WECC_URE3 did not generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days, resulting in a violation of CIP-007-3 R5.1.2. | CIP-007-3 | R5.1.2 | Lower | High | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, for 23 Cyber Assets, WECC_URE3 did not generate logs of sufficient detail to create historical audit trails of individual user account access activity. These assets are located in WECC_URE3's control centers. The risk was mitigated by the fact that WECC_URE3 has intrusion detection and prevention controls in place, including physical and electronic surveillance, for assets within the ESPs, and these controls could reduce or minimize the impact to the BPS. | when WECC_URE3 changed its historical audit trail configuration | when WECC_URE3 reconfigured its system and updated its test plan to ensure it generated applicable logs | $39,000 (for WECC201102804; WECC201102943; and WECC201102944 ) | Self-Report | To mitigate this violation, WECC_URE3 alerted its administrators to monitor systems that are not logging to further investigate the configuration change and logging issues. WECC_URE3 also ensured that all monitored assets generate appropriate logs. Finally, WECC_URE3 updated its test plan to ensure authentication changes associated with log collection do not disrupt logging capabilities. | 2011-09-30 | 2011-10-31 | Agrees/ Stipulates | WECC considered WECC_URE3's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC also considered WECC_URE3's compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102944 | Settlement Agreement | WECC_URE3 self-reported a violation of CIP-007-3 R6. WECC_URE3 uses a single security event monitoring solution to ensure compliance with CIP-007 R5 and R6. The solution requires that a log collector pull system event logs (used for audit trail and security status monitoring) from each Cyber Asset within the Electronic Security Perimeter (ESP). A configuration change to the service account from an administrator account to one with fewer privileges caused WECC_URE3's log collector to not pull logs from 23 Cyber Assets within two ESPs, specifically within WECC_URE3's ESPs at its control centers. WECC determined that WECC_URE3 did not maintain logs of security events for a minimum of ninety days, resulting in a violation of CIP-007-3 R6.4. | CIP-007-3 | R6.4 | Lower | Severe | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, for 23 Cyber Assets, WECC_URE3 did not maintain logs of security events for a minimum of ninety days. These assets are located in WECC_URE3's control centers. The risk was mitigated by the fact that WECC_URE3 has intrusion detection and prevention controls in place, including physical and electronic surveillance, for assets within the ESPs, and these controls could reduce or minimize the impact to the BPS. | when WECC_URE3 changed its historical audit trail configuration | when WECC_URE3 reconfigured its system and updated its test plan to ensure it generated applicable logs | $39,000 (for WECC201102804; WECC201102943; and WECC201102944 ) | Self-Report | To mitigate this violation, WECC_URE3 alerted its administrators to monitor systems that are not logging to further investigate the configuration change and logging issues. WECC_URE3 also ensured that all monitored assets generate appropriate logs. Finally, WECC_URE3 updated its test plan to ensure authentication changes associated with log collection do not disrupt logging capabilities. | 2011-09-30 | 2011-10-31 | Agrees/ Stipulates | WECC considered WECC_URE3's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC also considered WECC_URE3's compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201001884 | Settlement Agreement | WECC reviewed documentation from WECC_URE4 detailing its cyber security policy. WECC found that WECC_URE4’s cyber security policy was divided into two periods. In reviewing these documents, WECC determined WECC_URE4’s cyber security policy in effect for the first twelve months of the enforceable date of the Standard did not establish policies covering all the requirements in Standards CIP-002 through CIP-009, nor did it reference any external documents that provided this policy coverage. Despite WECC_URE4’s claims that its cyber security policy for this period was actually represented by its submitted document, WECC determined this document did not provide coverage for all the requirements in Standards CIP-002 through CIP-009. In addition, WECC determined WECC_URE4 could not establish that all the hyperlinked documents were made readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets (CCAs), as required by R1.2. Finally, WECC determined that WECC_URE4 could not document approval by the senior manager assigned pursuant to R2, as required by R1.3. While the senior manager’s approval of this document was typed in the revision history, this could not be verified by WECC as there was no other documentation of the review. WECC also reviewed the cyber security policy documentation in effect twelve months after the enforceable date of the Standard that was approved by WECC_URE4’s compliance officer, who was not the designated senior manager assigned pursuant to R2. WECC determined that this documentation addressed all the requirements for CIP-002 through CIP-009, except CIP-004-1 R3 dealing with a personnel risk assessment program, which WECC determined was not addressed until the approval of WECC_URE4’s document dated nineteen months after the enforceable date of the Standard. WECC determined that WECC_URE4 had a violation of CIP-003-1 R1 because WECC_URE4’s documentation did not demonstrate, for the duration of the violation period, that WECC_URE4 had a cyber security policy compliant with all the subrequirements of CIP-003-1 R1. | CIP-003-1 | R1; R1.2; R1.3 | Lower | N/A | WECC determined that this violation posed a moderate risk and not serious or substantial risk to the reliability of the bulk power system (BPS). Failure to document and implement a consistent cyber security policy that addresses the requirements of CIP-003-1 R1 may result in security controls required by the CIP Standards not being uniformly or consistently applied across all applicable CCAs, leading to security vulnerabilities for CCAs. In this instance, the entity could not demonstrate the implementation of a cyber security policy that addressed all requirements of CIP-002 through CIP-009 and was approved by the designated senior manager. Although WECC_URE4's policy did not address all of the relevant requirements, for at least a portion of the duration, it addressed most of them. Also, although WECC_URE4 had not accurately designated assigned CIP senior managers in accordance with the requirements of R2.1 and R2.2, for the first twelve months of the enforceable date of the Standard, WECC_URE4 did have CIP senior managers during this period who were implementing WECC_URE4’s CIP program. | when the Standard became mandatory and enforceable for WECC_URE4 | when WECC_URE4 implemented a cyber security policy covering all the requirements in Standards CIP-002 through CIP-009 | $22,000 (for WECC201001884, WECC201001885, and WECC201001886) | Spot Check | WECC_URE4 updated its cyber security policy twelve months after the enforceable date of the Standard to include comprehensive mapping of CIP-002 through CIP-009, and the policy was officially reviewed and approved by the designated senior manager. | 2010-04-07 | 2011-05-17 | Agrees/ Stipulates | WECC considered WECC_URE4's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201001885 | Settlement Agreement | WECC reviewed WECC_URE4’s cyber security-related document, which contained a historical list of assigned CIP senior managers. Based on this historical list and other documentation provided by WECC_URE4, WECC determined the documentation provided did not demonstrate the two specified CIP senior managers assigned pursuant to the Standard, for the first twelve months of the enforceable date of the Standard, were designated consistent with the requirements in R2.1 and R2.2. In addition, WECC determined this documentation provided conflicting information as to who the assigned CIP senior manager was during this period. In response to data requests issued to address these findings, WECC_URE4 indicated that the CIP senior manager assigned for the first three months of the enforceable date of the Standard was designated as such in WECC_URE4's other cyber security-related document. Nevertheless, WECC determined that this document did not identify this CIP senior manager by business phone and address as required by R2.1. WECC_URE4 also indicated that its compliance officer was the senior manager for the fourth month through twelfth month of the enforceable date of the Standard, assigned pursuant to the Standard, and that he delegated authority to someone else to act as the assigned CIP senior manager during this period. WECC_URE4 provided meeting minutes, company information pamphlets, and its internal compliance program (ICP) charter to demonstrate this delegation. Nevertheless, WECC determined this documentation did not identify this delegated CIP senior manager and did not designate this delegated CIP senior manager within thirty-calendar days of his designation three months after the enforceable date of the Standard, as required by R2.2. Various documents effective during the period of this violation identified WECC_URE4’s compliance officer as the assigned CIP senior manager. Nevertheless, WECC determined these documents were inconsistent with the other documentation references above and did not serve to identify the compliance officer as the assigned CIP senior manager within the thirty-calendar day time frame required by R2.2. WECC determined that WECC_URE4 had a violation of CIP-003-1 R2 because WECC_URE4’s assigned CIP senior managers were not designated consistent with the requirements in R2.1 and R2.2. Although, after the Spot Check, WECC_URE4 was able to produce documents which showed senior management assignments, these documents were approved by a senior manager who was not designated as the senior manager pursuant to CIP-003-1 R2. The confusion surrounding this issue was further exacerbated by the significant turnover of staff in the period leading up to the Spot Check. | CIP-003-1 | R2; R2.1; R2.2 | Lower | N/A | WECC determined that this violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system because, although WECC_URE4 could not prove its senior manager signed off on the security policy, WECC_URE4’s history included documentation of a manager’s approval of the policy. | when the Standard became mandatory and enforceable for WECC_URE4 | when the cyber security policy was approved | $22,000 (for WECC201001884, WECC201001885, and WECC201001886) | Spot Check | After the Spot Check, WECC_URE4 submitted a Mitigation Plan stating that it had located the documentation dated two months before and three months after the enforceable date of the Standard designating WECC_URE4’s senior manager for the period of this violation. In addition, 27 months after the enforceable date of the Standard, the cyber security policy was approved by the appropriate manager. | 2010-09-27 | 2011-04-26 | Agrees/ Stipulates | WECC considered WECC_URE4's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201001886 | Settlement Agreement | WECC determined that documentation presented by WECC_URE4 demonstrated that it had cyber security test procedures for new Cyber Assets in effect 38 days after the enforceable date of the Standard. As evidence for cyber security test procedures for new Cyber Assets before that date, WECC_URE4 provided a copy of its test procedures document. WECC determined from this document that WECC_URE4’s materials did not provide a set of procedures that tested the cyber security controls of new assets. In addition, WECC determined that the documentation provided for significant changes to existing Cyber Assets did not demonstrate cyber security controls tests were part of the procedure. WECC_URE4’s documentation focused on functionality and lacked specific tests that would assure the existing security controls were not adversely affected as a result of a significant change. Moreover, WECC discovered that WECC_URE4’s evidence could not demonstrate test results for the following two significant changes to Cyber Assets that took place twelve months after the enforceable date of the Standard: (1) WECC_URE4 submitted a change request for an installation of its firewall service module, and (2) added interfaces and routes to/from its energy management system (EMS) networks, and removed the transparent firewall. WECC determined that WECC_URE4 had a violation of CIP-007-1 R1 because WECC_URE4 did not create, implement and maintain adequate cyber security test procedures as required by R1 and R1.1 and did not document test results for two significant changes to existing Cyber Assets as required by R1.3. | CIP-007-1 | R1; R1.3 | Lower | N/A | WECC determined that this violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system because although WECC_URE4 could not provide documentation that it tested the security controls for new Cyber Assets, WECC_URE4 could provide documentation that it had cyber security test procedures for its new Cyber Assets. Despite lack of documentation, WECC_URE4 did actually complete the testing of the security controls for new Cyber Assets. | when the Standard became mandatory and enforceable for WECC_URE4 | when WECC_URE4 updated its cyber security test procedures per the requirements of the Standard | $22,000 (for WECC201001884, WECC201001885, and WECC201001886) | Spot Check | WECC_URE4 initiated a project, 38 days after the enforceable date of the Standard, to implement change management practices with a goal to achieve and maintain a controlled, consistent, collaborative and confident approach to meeting CIP-007 R1 change management requirements, inclusive of cyber security testing for new Critical Cyber Assets and significant changes to existing critical Cyber Assets. | 2011-01-21 | 2012-07-26 | Agrees/ Stipulates | WECC considered WECC_URE4's internal compliance program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC201102894 | Notice of Confirmed Violation | WECC_URE5 self-reported a violation of CIP-004-3 R3.2 for failing to ensure that two employees (less than 1% of the total employees) with authorized unescorted physical access to several of WECC_URE5's Physical Security Perimeters (PSPs) had personnel risk assessments (PRAs) that were updated at least every seven years. WECC_URE5 completed an initial PRA for these two individuals before the Standard became mandatory and enforceable but failed to update the PRAs for these two individuals seven years later. The first employee’s PRA completion date was incorrectly documented within WECC_URE5 corporate security’s records as having been completed three years after the actual date. The discrepancy was discovered four weeks after the actual due date, during an internal review. Consequently the employee did not have a valid PRA but still had had physical access to WECC_URE5’s PSPs for a 28-day period. The second employee’s PRA completion date was incorrectly documented as having been completed six months after the actual date. The discrepancy was discovered three months after the actual due date, during an annual review of the PRA master access list. Consequently, the WECC_URE5 employee did not have a valid PRA but still had physical access to WECC_URE5's PSPs for a 98-day period. WECC determined that WECC_URE5 was in violation of CIP-004-3 R3 for failing to update the PRAs for the two individuals identified above within the seven-year time period as required by the Standard. | CIP-004-3 | R3; R3.2 | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the two individuals in scope had initial PRAs and current training as required by CIP-004-3 R2. The individuals posed a lesser risk because they did have initial security threat assessment and were trained to properly handle Critical Cyber Assets. In addition, WECC_URE5 revoked the employees’ access rights immediately upon discovery. | date by which WECC_URE5 was required to update the first individual's PRA | date WECC_URE5 revoked the last affected individual's access rights | $12,600 (for WECC201102894 and WECC201102895) | Self-Report | Upon learning of these incidents WECC_URE5 took the following actions: 1. WECC_URE5 revoked the employees’ access rights immediately upon discovery of the violation instances; 2. The employees’ PRAs were completed; and 3. WECC_URE5 reinstated both employees’ physical access rights after completion of PRAs. | 2011-04-21 | 2012-04-20 | Does Not Contest | WECC reviewed WECC_URE5's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC considered WECC_URE5's and its affiliates' compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC201102895 | Notice of Confirmed Violation | WECC_URE5 self-reported a violation of CIP-004-3 R4.2 for failing to revoke an individual’s electronic access to Critical Cyber Assets (CCAs) within seven days of no longer requiring such access. The individual was employed by WECC_URE5's affiliate and no longer required access to WECC_URE5’s CCAs when he retired, but his access was not revoked by the due date. WECC_URE5’s corporate security department revoked the retired employee’s physical access rights before the due date, but the employee's supervisor did not submit a request to WECC_URE5’s Information Technology (IT) department to revoke the retired employee’s electronic access rights until the actual due date. The following day, upon receiving the request, the IT department revoked the retired employee's electronic access rights. | CIP-004-3 | R4 | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because WECC_URE5 uses two-factor authentication, has automated and manual logging, and all operator commands issued on the Energy Management System (EMS) are recorded in the event log. Therefore, WECC_URE5 was able to monitor the use of its CCAs and possibly identify malicious conduct. WECC_URE5 also stated the individual in scope had cyber security training and knew how to properly use CCAs and a personnel risk assessment which revealed no security threats. | when WECC_URE5 was required to revoke the employee's access to CCAs | when WECC_URE5 revoked the employee's access to CCAs | $12,600 (for WECC201102894 and WECC201102895) | Self-Report | WECC_URE5 conducted a review of the incident to ensure established procedures were followed. At the completion of the review, it was determined that the current process needed additional enhancements to specifically address employee retirements. Upon learning of these incidents,WECC_URE5 took the following actions: 1. WECC_URE5 confirmed that the employee’s physical access was revoked and the revocation records were retained; 2. WECC_URE5 revoked the employee’s electronic access rights; 3. WECC_URE5's affiliate developed new procedures for NERC CIP electronic and physical access; 4. WECC_URE5's affiliate ensured that WECC_URE5's procedure for requesting and maintaining NERC CIP electronic and physical access was integrated into the affiliate's own procedures; 5. As an enhancement to the developed procedure, on-boarding and off-boarding checklists were developed to ensure that affected managers and supervisors provide all necessary information and notifications to the appropriate groups who provision and de-provision access rights. These checklists became procedural and were formally released to the affected managers and supervisors; 6. Managers and supervisors were briefed and trained on the new procedures during monthly staff meetings; and 7. As on-going reinforcement, reminder notifications have been and will be communicated to WECC_URE5's affiliate managers. | 2011-08-26 | 2012-04-20 | Does Not Contest | WECC reviewed WECC_URE5's internal compliance program (ICP) to be a mitigating factor in the penalty determination. WECC considered WECC_URE5's and its affiliates' compliance history.
2012-07-31 | FERC | NP12-40-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC201102667 | Settlement Agreement | WECC_URE5 submitted a Self-Certification to WECC stating that it was in violation of CIP-004-3 R2. WECC found that 0.45% of employees with authorized unescorted physical access to 21 Physical Security Perimeters (PSPs) did not receive annual training during the calendar year. The Critical Cyber Assets (CCAs) inside these PSPs include servers, workstations, and networking equipment used in WECC_URE5's Energy Management System. | CIP-004-3 | R2; R2.1 | Medium | Severe | This violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system (BPS) because the 0.45% individuals in scope had a valid Personnel Risk Assessment (PRA) and had completed training the previous year. In addition, all PSPs are monitored twenty-four hours a day, and all CCAs require a username and password before an individual can gain access. | the date by which WECC_URE5 should have performed the required annual training | Mitigation Plan completion | 5000 | Self-Certification | WECC_URE5 implemented the following Mitigation Plan Activities: 1) WECC_URE5 removed access for personnel associated with this violation; 2) WECC_URE5 verified monthly training records; 3) WECC_URE5 implemented manual tracking of training expiration; 4) WECC_URE5 instituted the automated “early warning” notification for pending training expiration. This notice is sent directly to affected personnel and their manager/supervisor prior to the expiration of training; and 5) WECC_URE5 automated the notification of seven-day access revocation upon the expiration of training. Compliance staff from WECC_URE5 and supporting organizations manually verified that all training records for personnel with access to WECC_URE5's Electronic Security Perimeters and PSPs were valid. Confirmation of such manual verification was required in order to ensure data validity and consistent practice of manual verification across WECC_URE5. Manual verifications continue to occur. Automated notifications for upcoming expired training qualifications and revocation of access were implemented by WECC_URE5. | 2011-12-31 | 2012-05-25 | Does Not Contest | WECC considered WECC_URE5's Internal Compliance Program (ICP) to be a mitigating factor in the penalty determination.
2012-07-31 | FERC | NP12-36-000 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900347 | Settlement Agreement | The SERC CIP Spot Check team reported a violation of CIP-007-1 R1, because SERC_URE1 was unable to provide evidence that it was testing all significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP). SERC found that SERC_URE1 had a test procedure that included testing all cyber security controls for new Cyber Assets brought into the ESP, performing all tests in an appropriate test environment, and documenting all test results; however, this procedure failed to address the testing of all cyber security controls for significant changes to existing Cyber Assets to ensure that those changes would not have an adverse effect upon existing cyber security controls. SERC_URE1 had not considered certain resources, including ports and services, anti-virus software, and malware prevention tools, to be “controls” within the meaning of CIP-007-1 R1, therefore they were not included in the test procedure, as required by the Standard. Instead, these resources were addressed in SERC_URE1's internal procedures associated with other requirements of CIP-007-1. During the time this deficient procedure was in place, it was used to test three significant changes to existing Cyber Assets located within SERC_URE1’s ESP. These three changes were: (1) a software update on all Critical Cyber Assets (CCAs) to prevent the dispatcher training simulator from crashing when a real-time snapshot was taken; (2) a software update on four CCAs to fix discrepancies between the databases among four servers; and (3) a software update on one CCA in order to resolve non-updating communications protocol points. | CIP-007-1 | R1 | Lower | Severe | SERC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because, although SERC_URE1 failed to test in the manner required by the Standard, SERC_URE1 addressed the testing of some cyber security controls, conducted testing in an appropriate test environment, documented the results, and only used the deficient procedure three times. | when the Standard became mandatory and effective for SERC_URE1 | when SERC_URE1 updated its test procedures | 0 | Spot Check | To mitigate this violation, SERC_URE1 updated its test procedures to include the testing of all cyber security controls for significant changes to existing Cyber Assets. SERC_URE1’s test records and associated documentation were re-formatted to explicitly document the checks performed for cyber security controls during installations of new Cyber Assets and significant changes to existing Cyber Assets within the ESP. In addition, SERC_URE1’s test records and associated documentation were re-formatted to explicitly document checks of other systems, such as ports and services, performed during installations of new Cyber Assets and significant changes to existing Cyber Assets. | 2009-11-23 | 2012-02-22 | Neither Admits nor Denies | SERC considered SERC_URE1's internal compliance program to be a mitigating factor in the penalty determination. In addition, SERC_URE1 was cooperative in helping SERC understand the nature and scope of the violation.
2012-07-31 | FERC | NP12-36-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000348 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE indicating that it was in violation of CIP-006-1 R3. Texas RE_URE1 documented but failed to implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week (24/7) using at least one of the monitoring methods identified in CIP-006-1 R3. Specifically, Texas RE_URE1 failed to implement physical access monitoring at one fire exit door. While the evidence provided by Texas RE_URE1 suggests that video recording started with the surveillance camera installation that occurred four months after the mandatory compliance date, no evidence was provided that proves the video footage was reviewed 24/7. Further, a Texas RE_URE1 manager attested that he reviewed the surveillance videos during an eight week period at his leisure, but not 24/7. Texas RE_URE1 began reviewing the surveillance videos 24/7 8.5 months after the mandatory compliance date. With no 24/7 video surveillance in place prior to then, human observation was Texas RE_URE1’s only monitoring option. Human observation existed, but it was not in place 24/7. | CIP-006-1 | R3 | Medium | High | Texas RE determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because the access point was a fire exit door in the backup control center that was designed to be opened from inside the computer room only. This access point was a door within a defined PSP. Only personnel with authorized physical access are allowed to enter the PSP. Moreover, the fire exit door was secured by a crash bar from inside the computer room. However, without an operative door alarm and adequate physical access monitoring, a person within the control center computer room could open the door and allow an unauthorized person access into the PSP. A Texas RE_URE1 manager did review the surveillance videos, but this was not performed 24/7 in accordance with the Standard for the entire mandatory compliance period. Texas RE_URE1 personnel also attested that video footage from various cameras throughout the Texas RE_URE1 campus is manually cycled across large computer monitors where it is viewed by security personnel. | when the Standard became mandatory and enforceable for Texas RE_URE1 | Mitigation Plan completion Prior to 4/1/2010, Texas RE_URE1 was in violation of CIP-006-1 R3. When Version 2 of the Standard was approved, the requirement number for the applicable language was changed. Therefore, from 4/1/2010 until Mitigation Plan completion, Texas RE_URE1 was in violation of CIP-006 R5. | $8,000 (for TRE201000348 and TRE201000349) | Self-Report | To mitigate this violation, Texas RE_URE1 eliminated the subject computer room exit door by completely drywalling this access point and notifying Texas RE_URE1's internal NERC compliance group of the updated PSP floor plans, reflecting this change. Additionally, Texas RE_URE1 completed the following "above and beyond" measures: (1) Created a 12-month audit strategy for an applicable function, to ensure communication and success which included the following: creation of a formal audit timeline with deadlines to complete documents and evidence; formal meetings to roll out the audit plan to appropriate senior management; incorporation of a review of all CIP programs and evidence; incorporation of a series of mock audits on all CIP programs; and creation of a status tracking report used to update managers and executives at bi-weekly meetings. (2) Added a document control position to the internal compliance team. (3) Researched compliance tracking tools to automate many of the compliance functions and reporting; this included vendors conducting onsite demonstrations. (4) Conducted two self-audits. | 2010-11-02 | 2011-12-22 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program to be a mitigating factor in the penalty determination. In addition, "above and beyond" mitigating measures were considered in the penalty determination.
2012-07-31 | FERC | NP12-36-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000349 | Settlement Agreement | Texas RE_URE1 submitted a Self-Report to Texas RE indicating that it was in violation of CIP-006-1 R4. Texas RE_URE1 documented but failed to implement the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter (PSP) using one or more of the logging methods identified in CIP-006-1 R4. Specifically, Texas RE_URE1 failed to log physical entry at one fire exit door for a ten-month period. Based on the evidence provided by Texas RE_URE1, no mechanism for logging existed before the video surveillance camera installation for the aforementioned access point was completed four months after the mandatory compliance date. Texas RE_URE1 believes the subject fire exit door should not be classified as an access point. | CIP-006-1 | R4 | Lower | High | Texas RE determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS) because the access point was a fire exit door in the backup control center that was designed to be opened from inside the computer room only. This access point was a door within another defined PSP. Only personnel with authorized physical access are allowed to enter the PSP. Moreover, the fire exit door was secured by a crash bar from inside the computer room. | when the Standard became mandatory and enforceable for Texas RE_URE1 | Mitigation Plan completion Prior to 4/1/2010, Texas RE_URE1 was in violation of CIP-006-1 R4. When Version 2 of the Standard was approved, the requirement number for the applicable language was changed. Therefore, from 4/1/2010 until Mitigation Plan completion, Texas RE_URE1 was in violation of CIP-006 R6. | $8,000 (for TRE201000348 and TRE201000349) | Self-Report | To mitigate this violation, Texas RE_URE1 eliminated the subject computer room exit door by completely drywalling this access point and notifying Texas RE_URE1's internal NERC compliance group of the updated PSP floor plans, reflecting this change. Additionally, Texas RE_URE1 completed the following "above and beyond" measures: (1) Created a 12-month audit strategy for an applicable function, to ensure communication and success which included the following: creation of a formal audit timeline with deadlines to complete documents and evidence; formal meetings to roll out the audit plan to appropriate senior management; incorporation of a review of all CIP programs and evidence; incorporation of a series of mock audits on all CIP programs; and creation of a status tracking report used to update managers and executives at bi-weekly meetings. (2) Added a document control position to the internal compliance team. (3) Researched compliance tracking tools to automate many of the compliance functions and reporting; this included vendors conducting onsite demonstrations. (4) Conducted two self-audits. | 2010-11-02 | 2011-12-22 | Neither Admits nor Denies | Texas RE considered Texas RE_URE1's internal compliance program to be a mitigating factor in the penalty determination. In addition, "above and beyond" mitigating measures were considered in the penalty determination.
2012-07-31 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009825 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-3 R2.1. More specifically, during a periodic spot check, WECC_URE1 discovered that one individual was granted access to a Physical Security Perimeter (PSP) prior to completing required cyber security training. Access was inadvertently granted and taken away three days later when WECC_URE1 recognized the error. Upon discovering the error, WECC_URE1 performed a thorough analysis of the error and determined the individual in scope did not access the PSP at any time during the four days in which access was granted. Further, the individual in scope had a current personnel risk assessment (PRA) on file, and the individual was not aware he had such access. Consequently, WECC determined that WECC_URE1 failed to ensure that all personnel having such access to Critical Cyber Assets (CCAs), including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency, as required by CIP-004-3 R2.1. | CIP-004-3 | R2.1 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the individual had physical access, he did not have account access and could not log on to any of the CCA systems inside of the PSP. The CCAs in the PSP were also physically resistant, meaning there was no way to introduce information to the CCAs by way of any means of hardware communication. The PSP is monitored 24 hours a day, seven days a week via security cameras and security personnel. Lastly, the individual in question had a current PRA, and did not access the PSP while he was granted access to it. | date access to the PSP was granted in error | date access to PSP granted in error was revoked | 7000 | Self-Report | In accordance with the Mitigation Plan submitted by WECC_URE1 to WECC, WECC_URE1 revoked access for the individual who had inadvertently been granted access to a PSP prior to having completed the required cyber security training. WECC_URE1 completed a review of all provisioned physical and cyber access and determined that no other errors in training validation for any access afforded existed. In consideration of the need for further protections against human error, WECC_URE1 updated its procedure for access implementation. The procedure now includes steps for validating training records, including a peer review prior to approving the training completion part of the access request workflow. In addition, WECC_URE1 trained its personnel on the new procedure. | 2012-02-22 | 2012-06-05 | Does Not Contest | WECC considered WECC_URE1's internal compliance program and compliance history.
2012-07-31 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102926 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC indicating that it was in violation of CIP-005-1 R2. In its Self-Report, WECC_URE2 stated that it performed an incomplete review of its ports and services. WECC_URE2 stated that for six access points on its Electronic Security Perimeters (ESPs), it failed to ensure that only those ports and services required for normal operations were enabled. The access points WECC_URE2 identified are firewalls that control all of its ESPs. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system because, as a compensating measure, controls were in place during the duration of the violation, to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed 24 hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became mandatory and enforceable for WECC_URE2 | when WECC_URE2 conducted the required revisions and performed the training | $12,000 (for WECC201102926 and WECC201102927) | Self-Report | WECC_URE2 submitted a Mitigation Plan for this violation. Per its Mitigation Plan, WECC_URE2 revised its critical infrastructure protection program procedures for evaluating and assessing its ports and services for firewalls and switches, as well as conducted training on the revised procedures. | 2011-12-31 | 2012-05-07 | Agrees/ Stipulates | WECC considered WECC_URE2's compliance history.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102927 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC indicating that it was in violation of CIP-007-1 R2. In its Self-Report, WECC_URE2 stated that it performed an incomplete review of its ports and services. WECC_URE2 stated that for less than 8% of its total Cyber Assets, WECC_URE2 failed to ensure that only those ports and services required for normal operation were enabled. The Cyber Assets are network switches and workstations used for physical access monitoring. | CIP-007-1 | R2; R.2.1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system because, as a compensating measure, controls were in place during the duration of the violation, to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed twenty-four hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became mandatory and enforceable for WECC_URE2 | when WECC_URE2 conducted the required revisions and performed the training | $12,000 (for WECC201102926 and WECC201102927) | Self-Report | WECC_URE2 submitted a Mitigation Plan for this violation. Per its Mitigation Plan, WECC_URE2 revised its critical infrastructure protection program procedures for evaluating and assessing its ports and services for firewalls and switches, as well as conducted training on the revised procedures. | 2011-12-31 | 2012-05-07 | Agrees/ Stipulates | WECC considered WECC_URE2's compliance history.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2011008643 | Notice of Confirmed Violation | WECC_URE3 submitted a Self-Report addressing noncompliance with CIP-004-3 R4. WECC_URE3 did not timely update its access lists following employee retirement or transfers, including third-party contractors who had been given physical access rights to WECC_URE3 facilities that house Critical Cyber Assets (CCAs). Specifically, WECC_URE3 reported that its access list violation was associated with 11 individuals (three WECC_URE3 employees and eight third-party contractors), which represent less than 5% of WECC_URE3's authorized personnel. WECC_URE3 further determined it updated its access list two days late for a retired employee, 74 days late for a transferred employee, 210 days late for a different transferred employee, two days late for one contractor no longer requiring access, and between 140 and 159 days late for the remaining 7 contractors. During an on-site Compliance Audit, WECC reviewed the Self-Report and determined the individuals associated with the Self-Report initially had physical access to WECC_URE3's control centers. The individuals did not have electronic access to CCAs. WECC determined that WECC_URE3 revoked access for the individuals in question but did not update its authorized access lists. WECC determined that WECC_URE3 violated CIP-004-3 R4.1 for a failure to update its lists of personnel with authorized unescorted physical access to its CCAs. WECC also determined that WECC_URE3 violated CIP-004-3 R4.2 for a failure to revoke physical access to its CCAs within 24 hours for personnel who no longer require such access to CCAs. | CIP-004-3 | R4.1/ R4.2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, WECC determined that the violation did not include any issue with unauthorized access to WECC_URE3's CCAs and was limited to WECC_URE3's failure to update its lists of personnel with authorized unescorted physical access to its CCAs. Second, the contractors did not gain access to the CCAs. Third, the CCAs reside in a Physical Security Perimeter (PSP), which is subject to continuous monitoring and logging of both authorized logs and unauthorized access attempts. Also, the CCAs reside within an Electronic Security Perimeter (ESP); however none of the individuals associated with this violation had electronic access to CCAs. Finally, this instance of noncompliance is related to fewer than 5% of authorized WECC_URE3 employees or contractors, thus presenting a very limited risk to the BPS. | the date WECC_URE3 failed to update the access list associated with this violation | Mitigation Plan completion | $14,900 (for WECC2011008643 and WECC201102449) $0 (for WECC2012009561) These are two separate enforcement actions. | Self-Report | WECC_URE3 submitted a Mitigation Plan and completed the following actions to mitigate this violation: WECC_URE3 implemented a revised Access Program and enacted changes to the automated secure access request workflow process. The changes included: (1) Specific attention to third-party contractor authorization/termination of access privileges; (2) The addition of a process step within WECC_URE3's workflow process to route the process back to the authorized approver following the provisioning of authorized unescorted physical or cyber access; (3) Under the revised process, the authorized approver must review and attest that the list was updated; (4) The addition of a new confirmation process. After the authorized approver reviews and attests that the access list has been updated, WECC_URE3's Compliance group confirms the update. | 2012-03-21 | 2012-04-10 | Does Not Contest | WECC considered the internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102449 | Notice of Confirmed Violation | WECC_URE3 submitted a Self-Certification addressing possible noncompliance with this requirement. WECC_URE3 indicated on the Self-Certification that two operators did not meet the required training hours for the calendar year, but each operator did compile enough hours to maintain NERC certification and re-certification. WECC_URE3 further determined the two operators did not complete the required training time for system emergencies. WECC_URE3 added that it did not allow the employees to continue operating the WECC_URE3 system beyond the end of the year. Once the calendar year expired and the employees had not reached the minimum training requirements, WECC_URE3 did not allow the employees to operate. Thus, WECC_URE3 ensured that it maintained a staff of operating personnel with five days of emergency training, as required by this Standard. During an on-site Compliance Audit, WECC reviewed the Self-Certification and determined that the noncompliance was related to a single operator, not two operators. WECC determined that one individual received 17 hours of emergency training, approximately 15 hours short of the five days required by the Standard. WECC determined WECC_URE3's failure to provide at least five days per year of training and drills using realistic simulations of system emergencies to the operator resulted in a violation of PER-002-0 R4. | PER-002-0 | R4 | High | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. WECC_URE3's transmission system includes approximately 1,000 miles of 345 kV transmission lines, which increases the risk to the BPS. WECC_URE3 did not allow the employee to operate the system once the training deadline had passed, thus reducing the risk to the BPS. WECC_URE3 made sure that the operator associated with this violation was experienced, was NERC-certified, and maintained his NERC Certification. Also, the operator completed all of the required training in the prior year and 17 hours of training in the next year, the year when the violation occurred. Finally, all other WECC_URE3 operators received the training required by this Standard. | when the operator should have completed the required training | the operator was removed from the operating desk | $14,900 (for WECC2011008643 and WECC201102449) $0 (for WECC2012009561) These are two separate enforcement actions. | Self-Certification | According to its Mitigation Plan, WECC_URE3 took the following actions: (1) Removed the one operator who did not timely complete the requisite training hours from the WECC_URE3 system operations desk. After the end of the year, the employee did not serve in the operator capacity. (2) Ensured that all of its personnel allowed to operate the WECC_URE3 system remained adequately trained pursuant to this Standard. The employee did not return to the system operating desk until the employee completed training for the next calendar year. | 2010-12-31 | 2012-05-25 | Does Not Contest | WECC considered the internal compliance program (ICP) to be a mitigating factor in determining the penalty amount.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009561 | Settlement Agreement | During an on-site Compliance Audit, WECC discovered that WECC_URE3 violated PER-002-0 R1. WECC's Audit Team determined that one WECC_URE3 operator received 17 hours of emergency training for the calendar year, which was approximately 15 hours fewer than the 32 contact hours required by WECC_URE3's training plan. WECC determined that WECC_URE3 failure to provide at least 32 hours of contact hours per year of training and drills using realistic simulations of system emergencies to the operator resulted in a violation of PER-002-0 R4 (WECC201102449), which was addressed in a separate enforcement action that is concurrently being filed in WECC Violation ID# WECC201102449. WECC also determined based on the same set of facts that WECC_URE3 violated PER-002-0 R1 because the operator did not complete WECC_URE3's training requirement for the calendar year, and thus WECC_URE3 was not staffed with adequately trained operating personnel during the period of the violation. At the time of the violation, WECC_URE3 had 17 operators. | PER-002-0 | R1 | High | Lower | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. WECC_URE3's transmission system includes approximately 1,000 miles of 345 kV transmission lines, which increases the risk to the BPS. WECC_URE3 did not allow the employee to operate the system once the training deadline had passed, thus reducing the risk to the BPS. WECC_URE3 made sure that the operator associated with this violation was experienced, was NERC-certified, and maintained his NERC Certification. Also, the operator completed all of the required training in the prior year and 17 hours of training in the next year, the year when the violation occurred. Finally, all other WECC_URE3 operators received the training required by this Standard. | the last date the entity was staffed with adequately trained operator personnel | the operator was removed from the operating desk | $14,900 (for WECC2011008643 and WECC201102449) $0 (for WECC2012009561) These are two separate enforcement actions. | Audit | WECC_URE3 submitted a Mitigation Plan to address its violation of PER-002-0 R4. WECC determined that the instant violation and the violation of PER-002-0 R4 are a result of a single act of noncompliance stemming from WECC_URE3's violation of PER-002-0 R4. As a result, WECC also determined that WECC_URE3's remediating actions associated with the violation of PER-002-0 R4 serve as a remediating actions for the instant violation. According to its Mitigation Plan for PER-002-0 R4, WECC_URE3 took the following actions: (1) Removed the one operator who did not timely complete the requisite training hours from the WECC_URE3 system operations desk. After the end of the year, the employee did not serve in the operator capacity. (2) Ensured that all of its personnel allowed to operate the WECC_URE3 system remained adequately trained pursuant to this Standard. The employee did not return to the system operating desk until the employee completed training for the next calendar year. | 2010-12-31 | 2012-05-27 | Neither Admits nor Denies | WECC imposed a penalty for the related PER-002-0 R4 violation (WECC201102449, see above) and $0 for the instant violation. The PER-002-0 R4 penalty is addressed in a separate enforcement action that is being concurrently filed. WECC determined that no aggravation of the penalty was warranted in this case because the penalty for PER-002-0 R4 is a single penalty representative of the aggregate of the related violations.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002448 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-003-1 R5. WECC_URE4 submitted a Self-Report to WECC stating that it did not review the access privileges to protected information to confirm that the access privileges are correct and that they correspond with WECC_URE4's needs and appropriate personnel roles and responsibilities. Twenty-two WECC_URE4 personnel who previously had physical and/or logical access to protected information, based on job need, were "grandfathered" in as authorized personnel, but were not documented in accordance with procedures. WECC determined WECC_URE4 had a violation of CIP-003-1 R5, specifically R5.2, due to its failure to annually review the access privileges to protected Critical Cyber Asset (CCA) information to confirm that access privileges are correct. Although WECC_URE4 has a process in place for granting access to CCA information, twenty-two individuals who had been granted authorized access prior to the effective date of the standard were "grandfathered" and did not fill out the authorization form. Therefore, WECC_URE4 failed to confirm that, for these individuals, access privileges were correct. | CIP-003-1 | R5 (R5.2) | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The personnel within the scope of the violation had personnel risk assessments and CIP training, and access could be verified using Windows Active Directory. WECC_URE4 also stated its CCAs had updated anti-malware, logging enabled, and tripwire installed. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 reviewed and documented employees with "grandfathered" access to CCA information to ensure their authorized access to protected CCA information is appropriate and necessary and to verify continued compliance with WECC_URE4 procedure(s). | 2010-09-02 | 2011-04-29 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002490 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-003-1 R6. WECC_URE4 submitted a Self-Report to WECC stating that it had not used its own prescribed form for documenting changes to Critical Cyber Asset (CCA) / Critical Asset (CA) hardware and/or software, nor did it use its Change Log, as required by CIP-003-1 R6. WECC determined that WECC_URE4 failed to document WECC_URE4's use of a process of change control and configuration management for adding, modifying, replacing, or removing CCA hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of CCAs pursuant to WECC_URE4's change control process, as required by CIP-003-1 R6. WECC_URE4 failed to complete the documentation specified in its change control and configuration management procedure for six patch cycles for fourteen CCAs. The CCAs in scope were used for Windows Active Directory, Network Time Protocol, and vulnerability scanning. The devices in scope are located in WECC_URE4's Electronic Security Perimeter. | CIP-003-1 | R6 | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. At the time of the violation, information similar to that which was missed in the CIP-003-1 R6 documentation was captured in WECC_URE4's CIP-007 R3 documentation. WECC_URE4 also stated tripwire software was recording any changes made to CCAs, and systems were tested before being put into production. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 created, implemented, and maintained a CCA Inventory Worksheet and Change Control Log, as described in WECC_URE4's change control and configuration management procedure, and uses these documents to record configuration changes to CCAs retroactive to when the Standard became mandatory and enforceable. | 2010-09-30 | 2011-05-26 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002447 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-004-1 R4. WECC_URE4 submitted a Self-Report to WECC stating that it did not maintain a list of personnel authorized for cyber access to Critical Cyber Assets (CCAs). WECC_URE4 did not maintain a list of personnel with authorized cyber or authorized unescorted physical access to CCAs, including their specific electronic and physical access rights to CCAs. WECC_URE4 did not have a list of personnel with cyber access to CCAs. At the time of the violation, there were 26 individuals with cyber access to 21 CCAs. WECC found that WECC_URE4 failed to maintain lists of personnel with authorized cyber or authorized unescorted physical access to CCAs for 26 individuals with cyber access to CCAs. These CCAs were located in WECC_URE4's facilities. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because the personnel in scope had Personnel Risk Assessments and CIP Training, and access could be verified using Windows Active Directory. WECC_URE4 also stated the CCAs in scope had updated anti-malware, logging enabled, and tripwire installed. This violation affected 21.14% personnel. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 created a consolidated list of personnel with authorized cyber access to CCAs from existing documentation with relevant information, and maintains the list in accordance with CIP-004-1 R4 and WECC_URE4 procedure(s). | 2011-06-09 | 2011-07-08 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002491 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-005-1 R1. WECC_URE4 submitted a Self-Report to WECC stating that it failed to afford all the required protective measures to the RSA device that collects logs associated with access control and/or monitoring of WECC_URE4's Electronic Security Perimeter (ESP) and Critical Cyber Assets (CCAs). WECC found that WECC_URE4 had a violation of CIP-005-1 R1 for its failure to afford all the required protective measures for its Cyber Assets used in the access control and monitoring of the ESP, as specified in CIP-003, CIP-004 R3, CIP-005 R2 and R3, CIP-006 R2 and R3, CIP-007 R1 and R3 through R9, CIP-008, and CIP-009. The RSA device is used for monitoring the ESP and supporting WECC_URE4's access control and monitoring device. The RSA device is WECC_URE4's centralized logging server and maintains logs relating to log-ins, syslogs, and anomalous traffic. The device also maintains firewall rules and configuration changes made to firewalls. WECC_URE4 failed to provide the following protections for the RSA device. For protections required under CIP-005 R2.5.3, WECC_URE4 did not have a cyber access list, thus authorization rights for the three individuals with cyber access to this device could not be reviewed. For CIP-007 R1, WECC_URE4 failed to ensure one operating system patch for Windows Server 2003 would not adversely affect security controls, and failed to test the installation of anti-virus software prior to the software being put into production. For CIP-007 R4, the device in scope did not have anti-virus or anti-malware software installed. For CIP-007 R8, no cyber vulnerability assessment was performed on the device in scope. For CIP-009 R1 - R4, WECC_URE4 did not create a recovery plan for the device in scope. Following subsequent discussions with WECC_URE4, WECC determined that there were also four switches, externally connected devices with end points terminating within the ESP that were not identified and documented as access points to the ESP, as required by CIP-005 R1. WECC_URE4 stated these switches were classified as CCAs that contained a management port using an IP routable protocol, and the traffic did not route through the identified access points to the ESP. In addition, one Keyboard, Video, Mouse switch, which was not located inside an ESP, is used to provide the functions of a keyboard, monitor (video), and mouse to several servers and therefore allow remote control of the CCAs from outside the ESP. Thus, WECC_URE4 failed to identify and protect this Keyboard, Video, Mouse switch as an access point to the ESP. | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. Failure to ensure that Cyber Assets used in the access control and monitoring of the ESP are afforded the protective measures specified in CIP-005 R1 puts such assets at risk to be manipulated, allowing malicious access to Cyber Assets within the ESP to go unnoticed and unchecked. Such access may then be used to cause harm to CCAs essential to the operation of the BPS, thereby potentially negatively impacting the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because the personnel with access to the devices in scope had Personnel Risk Assessments and CIP training, and access could be verified using Windows Active Directory. WECC_URE4 also stated the RSA device was in a Physical Security Perimeter, and WECC_URE4 was maintaining firewall logs that were reviewed daily during the work week. Alerts for failed log-ins or odd traffic were automated and configured to be sent to the security staff, an intrusion detection system was installed, and logs were reviewed daily during the workweek. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 completed the testing, application and documentation of malicious software prevention software on the RSA device; instituted changes to related work procedures and processes to ensure use and documentation of the appropriate electronic access authorization process; completed a cyber vulnerability assessment on the RSA device, created a recovery plan for the RSA device; determined an acceptable solution to the test environment required by CIP-007 R1.2; defined a course of action toward the RSA device testing environment; implemented a solution to ensure that testing is done in an environment that reflects the RSA device's production environment; reclassified its switches as both CCAs and access control monitoring devices; and replaced remote access Keyboard, Video, Mouse devices with local Keyboard, Video, Mouse. | 2012-01-31 | 2012-06-07 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002492 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-006-1 R1.8. WECC_URE4 submitted a Self-Report to WECC stating that it failed to afford the protective measures specified in the Standard for its access control and/or monitoring (ACM) system for its Physical Security Perimeters (PSPs). The specific device is a WECC_URE4 server. The Standard requires WECC_URE4 to afford the server certain protections. Specifically, for the protections afforded under CIP-005 R2.5.3, WECC_URE4 has not provided the WinPak server the same process and mechanisms for control of electronic access as other critical systems. For CIP-005 R3.2, WECC_URE4 does not have a device in place for cyber access to the server that will monitor and alert of attempts at or actual unauthorized access. For CIP-007 R1, WECC_URE4 does not have test procedures in place as there is no test system available for the server. At the recommendation of its vendor, WECC_URE4 does not make changes/updates to the system due to its obsolescence. For CIP-007 R2, WECC_URE4 has not had a list of ports and services for the server. For CIP-007 R4, WECC_URE4 has not updated its anti-virus and malware prevention tools on the server based on the recommendation of its vendor. For CIP-007 R5, WECC_URE4 has not been following Account Management practices for the server. For CIP-007 R6, WECC_URE4 has not manually or electronically monitored the server operating system events. For CIP-007 R85, WECC_URE4 has not performed cyber vulnerability assessments to the PSP Cyber Assets at the recommendation of its vendor. WECC determined that WECC_URE4 had a violation of CIP-006-1 R1.8, for its failure to afford all the required protective measures of the Standard for its Server used in the access control and monitoring of its PSPs. The server is used for access control and monitoring of the PSPs. | CIP-006-1 | R1 (R1.8) | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. Failure to ensure that Cyber Assets used in the access control and monitoring of the PSP are afforded the protective measures specified in CIP-006-1 R1.8 puts such assets at risk to be manipulated, allowing malicious access to Cyber Assets within the PSP to go unnoticed and unchecked. Such access may then be used to cause harm to CCAs essential to the operation of the BPS, thereby potentially negatively impacting the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because the personnel with access to the device in scope had Personnel Risk Assessments and CIP training, and cyber access could be verified using Windows Active Directory. WECC_URE4 also stated the device was in a PSP with firewall logs to its Electronic Security Perimeter. The logs were reviewed daily during the work week and failed logins or odd traffic automated alerting was configured to be sent to the security staff. An intrusion detection system was installed and logs were reviewed daily during weekdays. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | This violation was primarily related to the recommendation by the vendor that the system not be modified or altered given that the system is no longer supported. The corrective action is the replacement of the system with a new ACM. WECC_URE4 reviewed and documented electronic access authorization; commenced account management practices; manually monitored system events; documented on the Cyber Security Exceptions Report these exceptions to requirements to heighten awareness, and prepared for the appropriate management of the new system. | 2011-02-18 | 2011-09-27 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002467 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-007-1 R1. WECC_URE4 submitted a Self-Report to WECC stating that it failed to implement full security testing following routine system patches in accordance with its implementation procedures prior to placing systems in production (testing was limited to operational checks only (R1.1)); failed to have test environments that accurately reflect the environment for three Critical Cyber Assts (CCAs): two Interface Servers and two Archive Servers (R1.2); and failed to document test results in accordance with WECC_URE4 test procedures (R1.3). With respect to R1.1, WECC_URE4 implemented a large number of patches (greater than 300) related to Windows Server 2003, Red Hat Linux 5, Windows XP Workstation, supervisory control and data acquisition (SCADA), and service packs for a back-up client. These patches were not tested as per WECC_URE4's CIP-007 R1 test procedures. WECC_URE4 did not test for security control created and/or modified by these patches, and only tested for operational issues created by the patches. There were 18 CCAs in scope located in an Electronic Security Perimeter (ESP). Examples of the functions performed by these CCAs are Windows Active Directory, Network Time Protocol, and vulnerability scanning. With respect to R1.2, WECC_URE4 has Historian software installed on three CCAs. WECC_URE4 had a test environment in place for the operating system the CCAs were using; however, this test environment did not include the Historian software and, as a result, failed to adequately reflect the production environment. The CCAs in scope are located in the network operations center. These devices are used to store and retrieve archived data from the SCADA system. This data is primarily used for decision-making. A total of 160 (out of the 300 listed in R1.1) operating system patches were applied to these CCAs. These patches were tested on the test environment that did not reflect the production environment. With respect to R 1.3, test results were not adequately documented for the 300 patches listed in R1.1. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. The devices in scope had software that was monitored daily, syslogs with automated alerting, anti-virus/anti-malware, and an Intrusion Detection System which was reviewed at least every three days. WECC_URE4 also stated that, although it did not perform security testing, operational testing was performed on the patches in scope that tested post-update functionality. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 completed the installation of test systems; reviewed and critiqued system security testing procedures; and developed and implemented test procedures to conduct full security testing and document results. | 2010-01-05 | 2011-08-02 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201002437 | Settlement Agreement | WECC notified WECC_URE4 that WECC was initiating the semi-annual CIP Self-Certification process. WECC_URE4 submitted its Compliance Certification Statement, certifying it was "Substantially Compliant" with CIP-007-1 R2. WECC_URE4 submitted a Self-Report to WECC stating that it had identified one required port on a Critical Cyber Asset (CCA) device that was not appropriately documented. Additionally, a required service was not appropriately documented which was running on two CCA devices. According to WECC_URE4 in the Self-Report, these documentation gaps had been corrected. WECC determined that WECC_URE4 had a possible violation of CIP-007-1 R2 for its failure to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled, as required by CIP-007-1 R2. WECC_URE4 failed to follow its process that included documenting all ports and services required for normal or emergency operations. The documentation required by WECC_URE4's CIP-007 R2 process includes the port/service, date of authorization, title of authorizer, and name of authorizer. The two errors were in an Electronic Security Perimeter (ESP). The ports and services were not documented as per WECC_URE4's CIP-007 R2 process. In addition, WECC discussed a potential increase in scope with WECC_URE4. During the interview WECC_URE4 stated that for four switches located in an ESP, it failed to document ports and services required for normal and emergency operations. The CCAs in scope were used for Windows Active Directory, Network Time Protocol, and vulnerability scanning. | CIP-007-1 | R2 | Medium | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. Anti-malware was installed on the devices in scope. The devices were being monitored by software, which would report any changes made to these CCAs. | when the Standard became mandatory and enforceable for WECC_URE4 | the date documentation of ports and services for the switches was completed | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Certification | WECC_URE4 validated the ports and services on all Cyber Assets within the ESP and completed the correct documentation. | 2011-08-09 | 2011-08-12 | Agrees/ Stipulates | WECC evaluated WECC_URE4's internal compliance program (ICP) and considered it a mitigating factor in penalty determination. Although WECC_URE4 self-reported this violation, because it self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Thus, Enforcement did not apply self-reporting credit.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201102840 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that its Security Patch Management program was not being applied consistently for four of eighteen Critical Cyber Assets (CCAs); specifically four switches. The cause of this oversight is miscommunication regarding the ownership and responsibility for these devices. Contributing factors include the retirement of a Manager responsible for the assignment of roles and responsibilities, as well as the lack of a documented approach for the assignment of asset ownership and responsibilities. WECC_URE4 had not documented the assessment of security patches and security upgrades for applicability to four CCAs (switches) within thirty calendar days of the availability of the patches or upgrades, in violation of R3.1. With respect to R3.2, in cases where a security patch was not installed, WECC_URE4 did not document the compensating measure(s) applied to mitigate risk exposure or an acceptance of risk associated with available upgrades to four CCAs (switches). Per WECC_URE4 some of the patches were applied, but the implementation was not documented. The four devices in scope are switches located in an Electronic Security Perimeter. WECC determined that WECC_URE4 had a possible violation of CIP-007-1 R3 for its failure to either separately, or as a component of the documented configuration management specified in CIP-003 R6, consistently apply its security patch management for tracking, evaluating, testing, and installing applicable cyber security software patches for all Critical Assets within the Electronic Security Perimeter(s) (ESP). Specifically, for four of eighteen CCAs, WECC_URE4 failed to assess patches within 30 days of availability and failed to document implementation of the patches. | CIP-007-1 | R3 | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. The purpose of this Standard is to ensure that WECC_URE4 defines its methods, processes and procedures for securing those systems determined to be Critical Cyber Assets, as well as the other (non-critical) Cyber Assets within the ESPs. WECC_URE4 failed to establish and document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESPs. However, as compensating measures, the devices in scope are located in a Physical Security Perimeter and ESP, and thus afforded the protections specified in CIP-005 and CIP-006. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Report | WECC_URE4 established the CIP compliance responsibilities regarding the four CCA devices to network services personnel; developed a means by which CCA device responsibilities are clearly delineated and communicated to responsible parties; and completed an evaluation of the security patches or other functional or configuration changes to these devices that have been evaluated in accordance with CIP-007 R3. | 2011-06-21 | 2011-11-23 | Agrees/ Stipulates | WECC evaluated WECC_URE's internal compliance program (ICP) and considered it a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201102841 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it failed to achieve strict compliance with CIP-009 R1. WECC_URE4 has a documented recovery plan for all Critical Cyber Assets (CCAs), but, according to WECC_URE4 there was a violation of WECC_URE4's implementing procedure that applies to CIP-009 R1 only, with no violation of the sub-elements of CIP-009-1 R1.1 or R1.2. This violation is specific to four CCAs (switches). There was a violation of WECC_URE4's implementing procedure (the Recovery Plan), in that these switches were not referenced in the Recovery Plan. The Recovery Plan specified that each CCA be identified in the Plan. WECC_URE4, however, has restoral procedures for the switches. The recovery plan specifies it will reference all CCAs. However, the recovery plan does not reference four out of eighteen CCAs. These four devices are switches located in an Electronic Security Perimeter (ESP). Although WECC_URE4 states it has a comprehensive recovery plan that references specific CCA recovery procedures, in this instance, the comprehensive recovery plan did not contain any reference to the four devices in scope. | CIP-009-1 | R1 | Medium | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and does not pose a serious or substantial risk to the BPS. The purpose of this Standard is to ensure that WECC_URE4 puts recovery plans in place for Critical Cyber Assets. Although WECC_URE4 failed to create and annually review recovery plans fit its Critical Cyber Assets, as a compensating measure, the devices in scope are redundant pairs and thus there would be no significant impact if one device of the pair failed. | when the Standard became mandatory and enforceable for WECC_URE4 | Mitigation Plan completion | $67,500 (for WECC201002448, WECC201002490, WECC201002447, WECC201002491, WECC201002492, WECC201002467, WECC201002437, WECC201102840, and WECC201102841) | Self-Report | WECC_URE4 revised its implementing procedure, the Recovery Plan, to include the four CCAs (switches). WECC_URE4 also developed a means by which CCA device responsibilities are clearly delineated and communicated to responsible parties. | 2011-06-24 | 2011-11-23 | Agrees/ Stipulates | WECC evaluated WECC_URE's internal compliance program (ICP) and considered it a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2011008663 | Settlement Agreement | WECC_URE5 submitted a Self-Report to WECC citing it was in violation of CIP-007-1 R3. More specifically, WECC_URE5 reported that it failed to document its assessment of certain types of security patches within 30 days of availability for Cyber Assets and Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). WECC reviewed WECC_URE5's Self-Report and contacted the entity to request additional information. WECC reviewed the additional information and determined that WECC_URE5 failed to document assessments of security patches for 230 devices within 10 ESPs associated with WECC_URE5's control centers. WECC determined that the scope of the violation included all WECC_URE5 CCAs. Compliance with CIP-007-1 R3 requires entities to assess and document all security patches within 30 days of availability. WECC determined that WECC_URE5's failure to document its assessment of certain types of patches for any Cyber Assets within the ESP constitutes a violation of CIP-007-1 R3. | CIP-007-1 | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by compensating measures in place during the violation period. First, WECC_URE5 assessed and documented all security patches and upgrades of a certain type. Second, although WECC_URE5 failed to document its assessment, WECC_URE5 did assess and implement all other types of applicable security patches and upgrades. All Cyber Assets and CCAs were secured within Physical Security Perimeters (PSPs) and ESPs. In addition, electronic and physical access to PSPs is controlled, monitored and logged. PSPs are manned and monitored by onsite security personnel at all times. All personnel and contractors that had access to Cyber Assets and Critical Cyber Assets had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with anti-virus software and malware prevention tools. | when the Standard became mandatory and enforceable for WECC_URE5 | Present | $12,500 (for WECC2011008663, WECC2012009235, WECC2012009233) | Self-Report | WECC_URE5 submitted a Mitigation Plan addressing its noncompliance with CIP-007-1 R3. In accordance with its Mitigation Plan, WECC_URE5 will complete the following actions: a. Formally implement a new patch management program (Program) to assure the evaluation and documentation of assessments for all required software security patches and upgrades within 30 days of security patches becoming available; b. Purchase a software product that will facilitate the identification of many security patches and upgrades; and c. Draft its new Program and begin a "pilot implementation" of this Program at its generating station. Institute full implementation of the Program at its facilities. | Approved completion date of 9/14/2012 | TBD | Does Not Contest | WECC considered WECC_URE5's internal compliance program.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012009235 | Settlement Agreement | WECC_URE5 submitted a Self-Certification to WECC citing it was in violation of CIP-006-1 R1.8. More specifically, WECC_URE5 reported that it failed to afford all security measures prescribed under CIP-006-1 R1.8 to Cyber Assets used in access control and monitoring of the Physical Security Perimeter (PSP). WECC reviewed WECC_URE5's Self-Certification and found that WECC_URE5 failed to document its assessment of certain types of security patches and upgrades for Cyber Assets while provisioning its PSP access control and monitoring system within 30 days of availability, as required in CIP-007-1 R3. WECC found WECC_URE5 in violation of CIP-006-1 R1.8 because WECC_URE5 failed to implement the protective measures described under CIP-007-1 R3 to Cyber Assets used in the access control and monitoring of the PSP. | CIP-006-1 | R1; R1.8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by compensating measures in place during the violation period. First, WECC_URE5 assessed and documented all security patches and upgrades of a certain type. Second, although WECC_URE5 failed to document its assessment, WECC_URE5 did assess and implement all other types of applicable security patches and upgrades. All Cyber Assets and CCAs were secured within Physical Security Perimeters (PSPs) and ESPs. In addition, electronic and physical access to PSPs is controlled, monitored and logged. PSPs are manned and monitored by onsite security personnel at all times. All personnel and contractors that had access to Cyber Assets and Critical Cyber Assets had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with anti-virus software and malware prevention tools. Lastly, WECC_URE5 failed to implement a single security measure out of 27 required by CIP-006-1 R1.8 by not documenting its assessment of patches. | when the Standard became mandatory and enforceable for WECC_URE5 | Present | $12,500 (for WECC2011008663, WECC2012009235, WECC2012009233) | Self-Certification | WECC_URE5 submitted a Mitigation Plan addressing its noncompliance with CIP-006-1 R1. In accordance with its Mitigation Plan, WECC_URE5 will complete the following actions: a. Formally implement a new patch management program (Program) to assure the evaluation and documentation of assessments for all required software security patches and upgrades within 30 days of security patches becoming available; b. Purchase a software product that will facilitate the identification of many security patches and upgrades; and c. Draft its new Program and begin a "pilot implementation" of this Program at its generating station. Institute full implementation of the Program at its facilities. | Approved completion date of 9/14/2012 | TBD | Does Not Contest | WECC considered WECC_URE5's internal compliance program as a mitigating factor in the penalty determination.
2012-06-29 | FERC | NP12-36-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012009233 | Settlement Agreement | WECC_URE5 submitted a Self-Certification to WECC citing it was in violation of CIP-005-1 R1.5. More specifically, WECC_URE5 reported that it failed to afford all security measures prescribed under CIP-005-1 R1.5 to Cyber Assets used in access control and monitoring for the Electronic Security Perimeter (ESP). WECC reviewed the Self-Certification and found that WECC_URE5 failed to document its assessment of certain types of security patches for Cyber Asset provisioning of the access control and monitoring to the ESP, in violation of CIP-005-1 R1.5. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by compensating measures in place during the violation period. First, WECC_URE5 assessed and documented all security patches and upgrades of a certain type. Second, although WECC_URE5 failed to document its assessment, WECC_URE5 did assess and implement all other types of applicable security patches and upgrades. All Cyber Assets and CCAs were secured within Physical Security Perimeters (PSPs) and ESPs. In addition, electronic and physical access to PSPs is controlled, monitored and logged. PSPs are manned and monitored by onsite security personnel at all times. All personnel and contractors that had access to Cyber Assets and Critical Cyber Assets had to complete a personnel risk assessment (PRA) and cyber security training. Devices within the ESPs are equipped with anti-virus software and malware prevention tools. Lastly, WECC_URE5 failed to implement a single security measure out of 26 required by CIP-005-1 R1.5 by not documenting its assessment of patches. | when the Standard became mandatory and enforceable for WECC_URE5 | Present | $12,500 (for WECC2011008663, WECC2012009235, WECC2012009233) | Self-Certification | WECC_URE5 submitted a Mitigation Plan addressing its noncompliance with CIP-005-1 R1. In accordance with its Mitigation Plan, WECC_URE5 will complete the following actions: a. Formally implement a new patch management program (Program) to assure the evaluation and documentation of assessments for all required software security patches and upgrades within 30 days of security patches becoming available; b. Purchase a software product that will facilitate the identification of many security patches and upgrades; and c. Draft its new Program and begin a "pilot implementation" of this Program at its generating station. Institute full implementation of the Program at its facilities. | Approved completion date of 9/14/2012 | TBD | Does Not Contest | WECC considered WECC_URE5's internal compliance program as a mitigating factor in the penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201000231 | Settlement Agreement | MRO_URE1 self-reported a violation of CIP-006-2 R2 because it failed to retain and review logs for Cyber Assets that authorize and/or log access to the Physical Security Perimeters (PSPs) as required by R2.2 and associated Standards referenced within the Requirement (CIP-007-2 R6.4 and CIP-005-2 R3.2). Additionally, MRO_URE1 reported that it failed to document a change per associated Standard CIP-003-2 R6 to a Cyber Asset that authorizes and/or logs access to PSPs. MRO_URE1 engaged a third-party consultant to conduct a compliance evidence review of its NERC CIP documentation. MRO_URE1 reported that the log retention sub-requirement of CIP-007-2 (R6.4) had not been fully met for the LAN controller at a control center for twenty days. In addition, MRO_URE1's internal investigation found that the log review sub-requirement of CIP-005-2 (R3.2) had not been fully met for the LAN controller at a control center for three and a half months. MRO_URE1 conducted a thorough investigation which verified that logs exist on the device and the log history going back to April 20, 2010 was recovered. As a result, a log review was completed which included the period from when the log history was recovered to when the log review was completed. Additionally, MRO_URE1 re-configured the servers for the LAN controllers that control access to MRO_URE1's PSP. This change involved logically moving the LAN controller that controls access to the PSP at the control center from one server to another server. With this change, the second server now includes all LAN controllers which control access to MRO_URE1's PSPs. During the compliance evidence review conducted with a third-party consultant, MRO_URE1 discovered that this change was not documented in accordance with MRO_URE1's documented change control and configuration management procedure. | CIP-006-2 | R2.2 | Medium | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems or the reliability of the bulk power system (BPS) because this violation related to the failure to retain and review certain logs and there were other layered defenses at MRO_URE1's control center that provided security to detect unauthorized access. While the failure to properly test and document a change in the pre-production environment could affect MRO_URE1's physical access control system by allowing unauthorized access or a change to existing cyber security controls on the LAN controller servers, MRO_URE1's control center building is staffed, partially surrounded by a security fence and the entire facility is protected by card readers. The PSP is located inside the alarmed perimeter. Additionally, entry into the control center computer room would have been detected by an active motion detector alarm system in the room. This system is also monitored continuously by MRO_URE1's security. The motion detector alarm system is partitioned separately from that of the building perimeter alarm system. MRO_URE1 took proper corrective actions immediately upon identifying the concern with failure to review logs. While MRO_URE1 did not have logs available for review about twenty days, it was able to identify the logs starting after that and performed reviews per the requirements which did not reveal any unauthorized access attempts. Additionally, MRO_URE1's failure to document the change related to the LAN controller servers’ configurations was a one-time change. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Self Report | 1. MRO_URE1 reconfigured the logging of remote interactive access for the LAN controllers that control access to MRO_URE1's PSPs to take place on the second server. The MRO_URE1 Physical Security Plan was updated to include the quarterly review of the second server logs. 2. Security improvements were made for remote interactive access to the LAN controllers that control access to MRO_URE1's PSP. The firewall that provided access control to the LAN controller at a control center was reconfigured to only allow remote interactive access from the second server. As part of the server login process, the user's login identity is captured and the user is required to explain why they are logging into the system. 3. The event application was reconfigured to provide the reporting function. 4. The security manager met with the IT supervisor for training on the use of the change control and configuration management procedure. | 2011-02-24 | 2011-03-18 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100275 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO determined that while MRO_URE1 had established and documented a change control and configuration management procedure for adding, modifying, replacing, or removing Critical Cyber Asset (CCA) hardware or software, MRO_URE1 was not consistently following its procedure. MRO examined files provided by MRO_URE1 to assess alignment with MRO_URE1's documented change control and configuration management procedure and determined that some change request forms were incomplete, their use was inconsistent, and in some cases the information provided on them lacked the specificity needed to determine compliance. For example, MRO reviewed a change to the inter-control center communications protocol (ICCP) node. The corresponding ticket for this change did not include reference to the ICCP primary node in the hardware listings. Additionally, the ticket showed an implementation date of more than five months after the change was made to the ICCP node. In addition, MRO_URE1's documented procedure requires “sign off” upon implementation of requested changes. MRO observed several instances where “sign off” was not noted, even months after a request was approved. MRO observed that in some instances, the change control request forms included a detailed list of individual CCAs subject to changes, whereas other change control request forms did not identify which individual CCAs were subject to changes. Without the detailed list of individual CCAs subject to changes, it was not possible to determine which among a group of CCAs on a single change request form had undergone a requested change, and which had not. The differences in how the change control request forms were completed were illustrative of internal inconsistencies. In the first instance, where detailed lists were included and individual CCA devices were checked off, the documentation evidences that MRO_URE1's procedures were followed. In the second instance, where the change control request forms did not identify the individual CCAs or indicated “sign off” upon completion of the change, the documentation does not evidence that MRO_URE1's procedures were followed. | CIP-003-1 | R6 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems or reliability and operability of the bulk power system (BPS). While the failure to properly manage changes to cyber security controls could possibly render one or many Critical Assets inoperable, in this instance MRO_URE1 had a compliant procedure and was able to evidence that it was following it for some changes to cyber security controls. MRO_URE1 maintained that it followed the procedure, but was not able to provide sufficient documentation to support that the procedure was followed in every instance. MRO_URE1 uses a phased approach in implementing changes on its system to better ensure that changes do not adversely affect the security of the control systems or reliability and operability of the BPS. MRO considered the failure to demonstrate consistent application of its procedure to manage changes to cyber security controls as demonstrating a need for training within MRO_URE1's staff. MRO expedited the mitigation of this violation to address concerns with testing and change management and worked with MRO_URE1 to implement an effective Mitigation Plan to strengthen its internal controls even before the CIP Spot Check report was finalized. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 reviewed and updated the change control and configuration management procedure and supporting documentation. 2. MRO_URE1 trained all applicable staff on the procedure including completeness of forms and log entries, consistent use, and required granularity for content. 3. MRO_URE1 implemented a review process to ensure consistent application of the change control and configuration management procedure. | 2011-09-07 | 2011-09-20 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100276 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain that MRO_URE1 had ensured that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. MRO_URE1's Energy Management System and backup Energy Management System systems security management plan describes the security management plan for Critical Cyber Assets (CCAs). This plan includes required actions to be taken to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter(s) do not adversely affect existing cyber security controls. The Energy Management System support group is responsible for ensuring that the installation of new Cyber Assets and significant changes to existing Energy Management System support group assets do not adversely affect cyber security controls. At a minimum, significant changes include security patches, service packs, vendor releases and version upgrades. While MRO_URE1 had a documented procedure to ensure system cyber security, MRO noted that the evidence to demonstrate that the required testing was conducted was not sufficient. MRO_URE1 maintained that the required testing was conducted according to its documented procedure, but MRO was not able to verify this with the documentation provided. | CIP-007-1 | R1.1 | Medium | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems or the reliability and operability of the bulk power system (BPS). In making this determination, MRO considered that MRO_URE1 had a documented procedure and maintained that it was following the procedure when implementing changes. MRO_URE1 was able to provide documentation of changes implemented, but MRO was not able to verify that the required testing was completed upon implementation of changes to CCAs to ensure changes did not adversely affect cyber security controls. However, MRO was not able to verify the extent of this testing based on the provided documentation. MRO expedited the mitigation of this violation to address concerns with testing and change management and worked with MRO_URE1 to implement an effective Mitigation Plan even before the CIP Spot Check report was finalized. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 developed changes to the existing test documentation for CCAs to generate the depth of evidence and test results required for an Audit. 2. MRO_URE1 developed a testing worksheet that provides the tester a means to develop, execute and document a test plan and test results for CCAs. 3. MRO_URE1 tested, approved and implemented the revised test documentation and testing worksheet. 4. MRO_URE1 updated, tested, approved and implemented the revised supporting test documentation. | 2011-08-30 | 2011-09-06 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100278 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain that MRO_URE1 had established, documented and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). MRO_URE1’s Energy Management System and backup Energy Management System systems security management plan describes the security management plans for MRO_URE1's Critical Cyber Assets (CCAs). This plan includes required actions to be taken to ensure that a security patch management program is established, documented and implemented, and that cyber security patches for all Cyber Assets and assets supporting Cyber Assets are tracked, evaluated, tested and installed as applicable. MRO determined that MRO_URE1 relies on its vendor to provide a security patch list on a monthly basis. MRO_URE1's Energy Management System support group reviews each vendor patch for applicability and then determines an implementation plan. The review is conducted within thirty days of receipt of the monthly security patch list from the vendor, and the review is documented in the IT system change log as required in MRO_URE1's security management procedure. MRO determined that for certain applications or systems supported by MRO_URE1, a process was not in place to review security patches within thirty days of availability. | CIP-007-1 | R3.1 | Lower | Severe | MRO determined that the violation posed moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the failure to evaluate patches and apply them in a timely manner to CCAs presents opportunities for exploitation of unpatched vulnerabilities which could render one or many CCAs inoperable. This risk was mitigated by the fact that MRO_URE1 was utilizing a vendor service which identified and evaluated newly available security patches for MRO_URE1's Energy Management System and backup Energy Management System critical and supporting Cyber Assets. Additionally, the service utilized by MRO_URE1 to identify and evaluate newly available security patches covered the majority of software installed on MRO_URE1's CCAs. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 completed inventory of software on all Cyber Assets. 2. MRO_URE1 identified software not covered by the existing security patch management program. 3. MRO_URE1 determined which applications were known to be safe for removal. 4. MRO_URE1 removed identified software from Cyber Assets. 5. MRO_URE1 identified and evaluated security patch availability for remaining software. 6. MRO_URE1 updated, tested, approved and implemented revised security patch management procedures. | 2011-08-15 | 2011-09-08 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-06-29 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100280 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain whether authorized exceptions to MRO_URE1's cyber security policy were reviewed and approved annually by the senior manager or delegate to ensure the exceptions were still required and valid. MRO was not able to determine if exceptions documented in 2008 were terminated or converted to Technical Feasibility Exceptions within a year of approval. The evidence provided to MRO did not demonstrate that documented exceptions from 2008 were closed prior to the annual review or reviewed in 2009 or 2010. | CIP-003-1 | R3.3 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because the violation is an administrative issue, dealing with proper documentation of cyber security policy exceptions and their review. While there was no evidence to demonstrate that documented exceptions had been reviewed, there was no concern with the exceptions or the compensating measures in place for any documented exception. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 re-evaluated documented exceptions. 2. MRO_URE1 received senior manager review and approval of required exceptions or attestation of no exceptions. | 2011-11-30 | 2012-01-16 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100281 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to ascertain whether MRO_URE1 conducted a review of access privileges to protected information for two years. MRO reviewed several policy and procedure documents which included entries relating to annual review in the version history section of the documents; however, none of these documents represented the access privileges list. MRO also reviewed notes from several meetings indicating that approvals took place, but it was not clear what exactly was being approved. Based on the information provided, MRO determined that there was not sufficient evidence to demonstrate that MRO_URE1 reviewed access privileges to protected information for two years. | CIP-003-1 | R5.2 | Lower | Severe | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because the violation is an administrative issue, dealing with proper documentation of reviews of access privileges to protected information. MRO_URE1 maintains that the reviews were conducted, and there are several documents referencing annual reviews and access privileges; however, the documentation is not complete and does not expressly indicate that the annual review of access privileges was conducted. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 reviewed and updated the access control program. 2. The MRO_URE1 cyber security team reviewed associated documents. 3. A MRO_URE1 compliance committee reviewed and approved associated documents. 4. MRO_URE1 documented completion of the required annual review. | 2011-12-27 | 2012-01-17 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100282 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO determined that MRO_URE1 failed to demonstrate that a list of sufficient detail is maintained that documents individuals’ specific electronic and physical access rights. MRO determined that only a limited number of MRO_URE1 personnel were aware of what privileges were actually granted through membership in various active directory groups. The privileges assigned to these groups were not clearly documented. Additionally, MRO_URE1 failed to demonstrate that quarterly reviews are sufficient to verify the appropriateness of individuals’ physical and cyber access privileges. | CIP-004-1 | R4.1 | Lower | Moderate | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because while inadequate management of access privileges may result in personnel retaining inappropriate levels of access after a job change or termination, MRO_URE1 had documented procedures in place to ensure that its CIP personnel list was being reviewed and updated as required, and was conducting the reviews. Additionally, the individuals on the list were properly qualified but the list failed to identify specific electronic access rights. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 modified existing procedures used to assign and review electronic access rights, including reviews of active directory accounts, active directory group privileges and verification of information. 2. MRO_URE1 verified privileges, verified the appropriateness of existing active directory group privileges and their membership using modified procedures. 3. MRO_URE1 approved and implemented modified procedures for electronic access rights. | 2012-02-02 | 2012-02-06 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100283 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO was unable to determine that MRO_URE1 reviewed, updated, and maintained all documentation to support the annual reviews required by CIP-005-1 R5.1. MRO observed that MRO_URE1 had not ensured that all documentation required by CIP‐005 had been reviewed, updated and maintained on an annual basis. Specifically, MRO identified a document which did not evidence that it had been reviewed annually and did not appear to be subject to versioning controls. Also, a second document did not evidence that it had been reviewed annually and did not appear to be subject to versioning controls. | CIP-005-1 | R5.1 | Lower | Moderate | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because while MRO_URE1 was not able to evidence a small number of documents had been reviewed, evidence was available for the majority of the documents examined. Additionally, the finding is not that any procedures were lacking, but that there was no evidence that a small number of those procedures were being reviewed on an annual basis. This violation is an administrative violation that relates to properly documenting review of policies and procedures. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. MRO_URE1 formalized the annual documentation review process. 2. MRO_URE1 completed training for all standard owners. 3. MRO_URE1 conducted annual review of all policies referenced in CIP documentation and security management. 4. MRO_URE1 completed annual review for CIP-005 documents. | 2011-09-20 | 2011-09-27 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100284 | Settlement Agreement | During a CIP Spot Check conducted by MRO, MRO observed that MRO_URE1's Physical Security Plan was not adequately maintained and that not all in‐scope identified Physical Security Perimeters (PSPs) incorporated a completely enclosed six‐wall border as required by CIP-006-1 R1.1. MRO found several inconsistencies in the version of the Physical Security Plan that was in effect at the time of the CIP Spot Check. The text of the document did not accurately reflect the controls that were actually implemented, nor was it internally consistent with other portions of the content. MRO determined that this version of the Physical Security Plan contained errors with regard to a control center. The location of a LAN controller was incorrectly shown on the diagram, and the visitor log book located at the door to the parking lot was not documented. Further, this version of the Physical Security Plan contained errors with regard to a second control center. The diagram for the second control center's computer room and communications room did not identify the two rooms as part of the PSP, nor did the diagram indicate that each room's door had a proximity card reader. The two rooms were misidentified, and there were no indications of where the alarm system components were located. The Physical Security Plan documented the procedures used to log visitor entry and exit. According to the document, visitors to the first control center were required to sign in and out using one of two specific log books. Based on interviews, however, visitors could sign in and out using any one of the log books located at six of the seven designated access points. During a tour of the first control center, it was determined that the seventh access point (parking lot door) also had a visitor log. The plan did not reflect the arrangement of visitor log books at the time of the tour. In the second control room's computer room, a square opening was found. The opening allowed passage from the uninterrupted power supply room to the second control room's computer room, bypassing PSP access controls. The opening was cut for HVAC work. The HVAC work had been suspended on the next day to facilitate the MRO Spot Check and to ensure safety of personnel while onsite. Prior to leaving the site, the contractor failed to properly cover the new duct opening due to miscommunication regarding what type of covering was needed. The contractor had assumed the covering was for dust control, and had not understood the need for a completely enclosed (six-wall) border. Upon identification of the opening during the walkthrough the local contractor was immediately contacted and the opening was properly closed before the MRO auditors left the site. The auditors observed and documented the mitigation. | CIP-006-1 | R1.1 | Medium | Moderate | MRO determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the security of the control systems and the reliability of the bulk power system (BPS) because while the unprotected opening in the six-wall perimeter allowed direct access to Critical Cyber Assets (CCAs) and the Electronic Security Perimeter (ESP), there were other mechanisms in place to monitor and limit access. The building is staffed, partially surrounded by a security fence, and the entire facility is protected by card readers. Security records show that the second control center was staffed until 21:06 on the day the HVAC work began at which time the security system was armed. The ESP is located inside the alarmed perimeter. The second control center remained armed and was continuously monitored by MRO_URE1's security department until 06:38 on the next day. MRO_URE1 staff were on-site from that time until the opening was secured. In addition, if, during the period when the building was unstaffed, an individual would have somehow managed to gain access to the building, entry into the second control center's computer room would have been detected by an active motion detector alarm system in the room. This system is also monitored continuously by the MRO_URE1 security department. The motion detector alarm system is partitioned separately from that of the building perimeter alarm system. | when the Standard became mandatory and enforceable for MRO_URE1 | Mitigation Plan completion | $12,000 (for MRO201000231, MRO201100275, MRO201100276, MRO201100278, MRO201100280, MRO201100281, MRO201100282, MRO201100283, and MRO201100284) | Spot Check | 1. The opening in the wall between the uninterrupted power supply room and the computer room was properly closed on the day the HVAC work was suspended while the MRO Audit staff was onsite. 2. The floor plans in MRO_URE1's Physical Security Plan were updated to reflect accurate representation of where the equipment, logs, and boundaries are located. 3. The Physical Security Plan was reviewed for accuracy, updated to eliminate any inconsistencies, and the plan was reviewed and approved. | 2011-02-24 | 2011-07-22 | Does Not Contest | 1. MRO_URE1 formalized the creation of a subcommittee where the purpose of the team is to provide advice, guidance, and recommendations for decision-making in areas affecting certain standards and requirements. 2. MRO_URE1 convened a meeting with supervisors to discuss NERC compliance objectives and concerns. Prior to the meeting, MRO_URE1's compliance department sent a survey to all standard and requirement owners to gain feedback and suggestions regarding MRO_URE1's compliance program. This meeting and the associated survey request will be held annually to provide compliance program updates, as well as to provide a forum for discussion and feedback between the supervisors and the compliance department. 3. MRO_URE1's IT department assigned an experienced manager the responsibility for assessing and providing recommendations for improvements to MRO_URE1's information security posture. The scope of this assessment includes CIP compliance efforts. 4. MRO_URE1 has a documented compliance program which was in place at the time of the violation which MRO considered a mitigating factor in penalty determination.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102918 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC indicating that it was in violation of CIP-002-1 R3. In its Self-Report, WECC_URE1 stated that its Critical Cyber Asset (CCA) inventory was incomplete because it did not include primary PC-integrated devices. WECC_URE1 stated that it failed to identify one Cyber Asset, essential to the operation of another Critical Asset, as a CCA. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because, as a compensating measure, the device in scope was located inside of an Electronic Security Perimeter and Physical Security Perimeter (PSP), which was subject to the protections required by CIP-005 and CIP-006. In addition, only authorized personnel are granted access to these devices. | when the Standard became enforceable for WECC_URE1 | Mitigation Plan completion | $21,000 (for WECC201102918, WECC201102919, and WECC201102920) | Self-Report | A complete review and assessment of the Critical Asset inventory and configuration per CIP-002 R3 was completed and corrected for the WECC_URE1's devices. The missing device was added to the inventory one week after the Self-Report and updated six weeks later. Unique device identifiers have been created for each device in the inventory for ease of tracking in data collection and oversight in the compliance activities. | 2011-08-15 | 2012-05-07 | Agrees
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102919 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC indicating that it was in violation of CIP-005-1 R2. In its Self-Report, WECC_URE1 stated that it performed an incomplete review of its ports and services. WECC_URE1 stated that for two access points on its Electronic Security Perimeter (ESP), it failed to ensure that only those ports and services required for normal operation were enabled. The access points WECC_URE1 identified are firewalls that control access to two of WECC_URE1's ESPs. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because, as a compensating measure, controls were implemented to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed twenty-four hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became enforceable for WECC_URE1 | Date of revised procedure and training | $21,000 (for WECC201102918, WECC201102919, and WECC201102920) | Self-Report | WECC_URE1 revised its critical infrastructure protection program procedure to evaluate and assess ports and services for firewalls and switches in order to better clarify the process, and training was completed. Unique device identifiers have been created for each device for ease of tracking in data collection. A review of the ports and services for the firewalls in question was also completed. | 2011-12-31 | 2012-05-07 | Agrees
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102920 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC indicating that it was in violation of CIP-007-1 R2. In its Self-Report, WECC_URE1 stated that it performed an incomplete review of its ports and services. WECC_URE1 stated that for thirteen Cyber Assets, WECC_URE1 failed to ensure that only those ports and services required for normal operation were enabled. The Cyber Assets are network switches and workstations used for physical access monitoring. | CIP-007-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) because, as a compensating measure, controls were implemented to log and monitor access to all Cyber Assets within the Electronic Security Perimeter (ESP). Physical and electronic alerts coming from these controls are reviewed twenty-four hours a day. In addition, only authorized personnel are granted access to these devices. | when the Standard became enforceable for WECC_URE1 | Date of revised procedure and training | $21,000 (for WECC201102918, WECC201102919, and WECC201102920) | Self-Report | WECC_URE1 revised its critical infrastructure protection program procedure to evaluate and assess ports and services for firewalls and switches in order to better clarify the process, and training was completed. Unique device identifiers have been created for each device for ease of tracking in data collection. A review of the ports and services for the switches in question was also completed. The remaining ports and service review for network switches and work stations involved in the violation were performed by scans. | 2011-12-31 | 2012-05-07 | Agrees | WECC considered WECC_URE1's compliance history.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008702 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-1 R5. WECC_URE2 reported that it failed to implement a process consistent with CIP-007-1 R5.2 and failed to identify those individuals with access to shared accounts pursuant to CIP-007-1 R5.2.2. WECC subject matter experts (SMEs) reviewed WECC_URE2's Self-Report and contacted the entity to request additional information. In response to queries from the SMEs, WECC_URE2 provided a list of individuals with electronic access to Critical Cyber Assets (CCAs) and Cyber Assets within the Electronic Security Perimeter (ESP) who had not been previously identified. Based on this information, SMEs found that WECC_URE2 failed to identify three individuals with access to a total of seven shared accounts. Further, the SMEs determined that these shared accounts provided access to approximately 29 Cyber Assets and CCAs associated with two WECC_URE2 Critical Assets, the control center and backup control center. WECC Enforcement determined that WECC_URE2 failed to identify three individuals with access to shared accounts, in violation of CIP-007-1 R5.2.2. | CIP-007-1 | R5; R5.2.2 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The risks posed by WECC_URE2's failure were limited given the existing compensating measures in place during the violation period. Each of the three individuals in question had completed training and personnel risk assessments pursuant to CIP-004. Further, such access was necessary for each individual in the course of performing their regular job-related duties. Cyber Assets and CCAs accessed through these seven, shared accounts were all secured with Physical Security Perimeters and ESPs. Lastly, all access to CCAs and Cyber Assets within an ESP through these shared accounts was documented. | when WECC_URE2 failed to identify the individuals with access to the shared accounts | Mitigation Plan completion | $15,600 (for WECC2011008702, WECC2011008703 and WECC2011008705) | Self-Report | WECC_URE2 compiled a list of all shared accounts and of the individuals that have access to the accounts that addresses the requirements of CIP-007 R5.2.2. WECC_URE2 also documented and implemented a new process designed to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. The process included provisions for the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system in service. In addition, WECC_URE2 process includes a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes. | 2011-12-30 | 2012-04-09 | Does Not Contest | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008703 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-006-1 R1.8. WECC_URE2 reported that it had failed to afford all security measures prescribed under R1.8 to Cyber Assets used in access control and monitoring of the Physical Security Perimeter (PSP). WECC Subject Matter Experts (SMEs) reviewed WECC_URE2's Self-Report and found that WECC_URE2 failed to identify individuals accessing shared user accounts to Cyber Assets used in PSP access control and monitoring. The SMEs found that WECC_URE2 failed to identify 11 individuals with access to shared accounts. WECC Enforcement determined that WECC_URE2's failure to implement protective measures described under CIP-007-1 R5 to Cyber Assets involved in PSP access control and monitoring, constituted a violation of CIP-006-1 R1.8. | CIP-006-1 | R1; R1.8 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The risks posed by WECC_URE2's failure were limited given compensating measures in place during the violation period. Each of the 11 individuals with access to shared accounts completed training and personnel risk assessments described under CIP-004. Further, electronic access to devices using shared accounts was logged and monitored. | date Standard became mandatory and enforceable | Mitigation Plan completion | $15,600 (for WECC2011008702, WECC2011008703 and WECC2011008705) | Self-Report | WECC_URE2 compiled a list of all shared accounts and the individuals that have access to the accounts that addresses the requirements of CIP-007 R5.2.2. WECC_URE2 also documented and implemented a process to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. The process includes provisions for the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system in service. In addition, WECC_URE2's process includes a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes. | 2011-12-30 | 2012-05-08 | Does Not Contest | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in assessing the penalty. Based on the NERC Sanction Guidelines, WECC determined the violations of CIP-006-1 R1 and CIP-007-1 R5 were related to a single act or common incidence of non-compliance for which WECC would assess a single aggregate penalty.
2012-05-30 | FERC | NP12-27-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008705 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-005-1 R1. WECC_URE2 reported that it had failed to afford all security measures prescribed under R1.5 to Cyber Assets used in access control and monitoring of the Electronic Security Perimeter (ESP), specifically one security measure per CIP-007-1 R5 that requires entities to identify individuals with access to shared accounts. WECC subject matter experts (SMEs) found that WECC_URE2 failed to identify individuals accessing shared user accounts to Cyber Assets used in ESP access control and monitoring. SMEs determined that three individuals were not identified as having access to shared accounts provisioning access to three ESP access points. WECC Enforcement determined that CIP-005-1 R1.5 incorporates protective measures described in CIP-007-1 R5 by reference. WECC Enforcement determined that WECC_URE2's failure to list individuals with access to shared accounts for ESP devices pursuant to CIP-007-5 R5 constituted a violation of CIP-005-1 R1.5. | CIP-005-1 | R1; R1.5 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. The risks posed by WECC_URE2's failure were limited given the existing compensating measures in place during the violation period. Each of the three unidentified individuals with access to shared accounts completed a personnel risk assessment and cyber security training under CIP-004. Further, access by these individuals using shared accounts was logged and monitored. All Critical Cyber Assets and Cyber Assets were secured within ESPs and Physical Security Perimeters. | date Standard became mandatory and enforceable | Mitigation Plan completion | $15,600 (for WECC2011008702, WECC2011008703 and WECC2011008705) | Self-Report | WECC_URE2 compiled a list of all shared accounts and the individuals that have access to the accounts that meets CIP-007 R5.2.2. WECC_URE2 also documented and implemented a process to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. The process includes provisions for the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system in service. In addition, WECC_URE2's process includes a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes. | 2011-12-30 | 2012-05-03 | Does Not Contest | WECC considered WECC_URE2's internal compliance program (ICP) as a mitigating factor in assessing the penalty. Based on the NERC Sanction Guidelines, WECC determined the violations of CIP-005-1 R1 and CIP-007-1 R5 were related to a single act or common incidence of non-compliance for which WECC would assess a single aggregate penalty.
2012-05-30 | FERC | NP12-26-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100249 | Notice of Confirmed Violation | During a CIP Spot Check, MRO determined that MRO_URE1 failed to provide evidence of recovery plans for every Critical Cyber Asset (CCA), as required by CIP-009-1 R1. MRO_URE1 provided evidence of a general recovery plan for all assets, which included disaster recovery and failover to the backup control center and backup systems, and also transfer to a backup center and recovery of the system in general. However, the plan did not include plans for recovering each CCA. | CIP-009-1 | R1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. Although MRO_URE1's recovery plan did not include documented procedures for recovery of each CCA individually, it did address disaster recovery and transfer to a backup center and recovery system. MRO_URE1 also has a support agreement with an established Energy Management System vendor for recovery support, including device recovery. Additionally, the recovery plan was tested annually via table top exercises. | When the Standard became mandatory and enforceable for MRO_URE1 | When MRO_URE1 completed its mitigation plan | 6000 | Spot Check | MRO_URE1 has completed the following mitigation activities: (1) updated its recovery plan to include procedures for every type of Critical Asset (and each CCA) as required by the Standard; and (2) reviewed, approved, and implemented its recovery procedures. | 2011-09-09 | 2011-10-05 | Admits | MRO considered MRO_URE1's internal compliance program, in place at the time of the violation, to be a mitigating factor in the penalty determination.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007731 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-005-2 R3 because it did not perform a manual 90-day review for unauthorized electronic access to the server associated with the physical security system. | CIP-005-2 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the existing physical and electronic controls in place. Specifically, the physical security system server could only be accessed from dedicated physical security control system personal computers that are within the Electronic Security Perimeter and Physical Security Perimeter. Further, a corporate user ID and password is required, and the user must be listed as an active user of the system to have authorization to use the program. There were no instances of unauthorized access in the timeframe of the violation. | When NPCC_URE1 should have reviewed the access logs | Mitigation Plan Completion | $8,000 (for NPCC2011007731, NPCC2011007732, and NPCC2011008068) | Self-Report | NPCC_URE1 completed the following mitigation activities, in accordance with its Mitigation Plan: (1) In the NPCC_URE1 calendar, a monthly pop-up reminder was created to remind administrator and manager to review the monthly server access reports for instances of unauthorized access; and (2) In the NPCC_URE1 calendar, a quarterly pop-up reminder was created to remind a manager, administrator, and appropriate department to perform a quarterly review to ensure that the monthly reviews were completed as described in item (1), above. The quarterly reminder also reminds the recipients to file evidence of the completed quarterly review with the department. | 2011-03-22 | 2011-10-14 | Neither Admits Nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP), which was in place at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007732 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R5 because the passwords associated with several accounts did not meet the requirements of the Standard. Specifically, the NPCC_URE1 physical security system had three shared default accounts associated with IT administration of the physical security system. Each of these three accounts had permissions allowing them to perform any function within the system, in violation of R5.2.1. The passwords associated with each of the accounts were not changed since placing the system into service, in violation of R5.3.3. In addition, the passwords did not meet the strong password requirements of R5.3.2. Further, there were four instances associated with individual IT accounts where the passwords of the users' physical security system were not changed at least annually, in violation of R5.3.3. In two of those instances, the passwords did not consist of a combination of alpha, numeric and special characters, as required by R5.3.2. | CIP-007-1 | R5; R5.2.1; R5.3.2; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the existing electronic access/account controls. Specifically, the user must obtain access to NPCC_URE1's parent company's domain via an active directory account, then must satisfy the requirements of the secure network device (user name, PIN and password) to gain access to the icon associated with the physical security system. The user then clicks on the physical security system icon and enters his or her physical security system user ID and password. There were no instances of unauthorized access associated with the shared accounts in the timeframe of the violation. | When the Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan Completion | $8,000 (for NPCC2011007731, NPCC2011007732, and NPCC2011008068) | Self-Report | NPCC_URE1 completed the following mitigation activities, in accordance with its Mitigation Plan: (1) Disabled two of the three shared accounts previously used by IT administrators. Only one shared account will remain as the hierarchy default account for emergency use; (2) Changed the password associated with the one account to meet strong password requirements. This account will now be used as an emergency administrator account only. A specific manager has the responsibility to ensure that the password associated with the hierarchy account is updated every April. A reminder has been added to the calendar to ensure that this will occur every April and that the appropriate department is notified; and (3) Reset the passwords of the four individual IT accounts, and implemented the functionality of the physical security system to automatically require that passwords associated with individual accounts be changed every 90 days and that the user creates a strong password. | 2011-07-26 | 2011-10-18 | Neither Admits Nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP), which was in place at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008068 | Settlement Agreement | NPCC_URE1 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R5 because it failed to properly identify individuals with access to shared accounts. Specifically, the shared account password to operate a certain type of personal computer (PC) at a number of Critical Asset substations was being shared by substation personnel who required the password to perform their job responsibilities. Personnel were obtaining the password from other substation personnel in an informal manner without coordinating this release with the password administrator. This resulted in the Electronic Security Perimeter (ESP) access list for the PCs not being updated as these individuals gained access, as required by R5.2.2. | CIP-007-1 | R5; R5.2.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the individuals that were obtaining the password in the "shared" fashion required the password to perform their normal job duties. Such personnel would have been given the password had the appropriate administrator been contacted, as personnel risk assessments and cyber security training had already been completed on the substation personnel. In addition, the PC is inside of the Physical Security Perimeter at the substation, so only authorized personnel or those with proper escort can gain access. | When the Standard became mandatory and enforceable for NPCC_URE1 | Mitigation Plan Completion | $8,000 (for NPCC2011007731, NPCC2011007732, and NPCC2011008068) | Self-Report | NPCC_URE1 completed the following mitigation activities, in accordance with its Mitigation Plan: (1) Changed the single password associated with the PC shared account; (2) Re-trained all substation management, operators and technicians on the expectations and proper use of the PC shared password account and overall corporate password policy. The procedure documenting the appropriate use of shared passwords was already in existence prior to this violation; (3) Revised the corporate master access list to include a column associated with the substation PC shared account. This list is used by corporate IT during their monthly corporate access reviews; and (4) Revised the substation master list to include a column associated with the PC access for substation personnel. This list is used by substations to track the types of access to all substation personnel. | 2011-11-17 | 2011-12-08 | Neither Admits Nor Denies | NPCC considered NPCC_URE1's internal compliance program (ICP), which was in place at the time of the violation, to be a mitigating factor in determining the penalty amount.
2012-05-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007269 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-005-1 R1.5 to NPCC. During an internal audit review of NPCC_URE2’s NERC CIP compliance program conducted, NPCC_URE2 discovered that, due to an oversight, it had not properly identified all Electronic Security Perimeter (ESP) access control and monitoring assets. Specifically, ten devices were not properly classified as access control and/or monitoring devices and therefore were not included in the NERC CIP compliance program. As a result of this identification failure, these assets were not afforded all of the protective measures required by R1.5. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the affected devices resided within a defined ESP and Physical Security Perimeter. In addition, the devices were afforded the following security controls: 1) Account management; 2) Strict firewall access control within a defined demilitarized zone between the process control network and the plant information network; and 3) Security event logging and network intrusion detection. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Updated its NERC CIP asset list to include the ESP access control and monitoring assets that were previously missing from the list; 2. Conducted internal analysis to identify the required controls for each asset added to the list; 3. Implemented the required controls on each asset; 4. Tracked the implementation of each control for each asset via a tracking spreadsheet; and 5. Performed a final review of the tracking spreadsheet to ensure that the control for each asset was in fact implemented in the proper fashion. | 2011-11-30 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor. NPCC considered that NPCC_URE2 completed the Mitigation Plan after the approved completion date. NPCC determined that no adjustments to the penalty were warranted because the entity was completing related work under a separate Mitigation Plan that followed a different timeline and NPCC was aware of the revised timeframe.
2012-04-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007270 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-007-1 R3. During an internal audit review of NPCC_URE2’s NERC CIP compliance program, NPCC_URE2 discovered that, due to an oversight, it did not include several Cyber Assets in the security patch management program. | CIP-007-1 | R3 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the affected devices resided within a defined Electronic Security Perimeter (ESP) and Physical Security Perimeter. In addition, the devices were afforded the following security controls: 1) Account management; 2) Anti-virus, where technically feasible; 3) Strict firewall access control within a defined demilitarized zone between the process control network and the plant information network; and 4) Security event logging and network intrusion detection. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Removed certain devices from the ESP that were not in the patch management program; 2. Identified additional assets within the ESP to include in the patch management program; 3. Developed a patch management process flow diagram; 4. Developed tracking spreadsheets for additional assets; and 5. Reviewed all previous security patches for the additional assets that were added to the NERC CIP patch management program. | 2011-12-23 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor.
2012-04-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007271 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-006-1 R1.8 to NPCC. During an internal review of NPCC_URE2’s NERC CIP compliance program, NPCC_URE2 discovered that, due to an oversight, it had not properly identified or included the Cyber Assets associated with the physical access control system on the Critical Cyber Assets (CCA) list. Thus, the physical access control system was not provided all of the protective measures required by R1.8. | CIP-006-1 | R1; R1.8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the affected devices resided within a defined Electronic Security Perimeter (ESP) and Physical Security Perimeter. In addition, the devices were afforded the following security controls: 1) Account management; 2) Strict firewall access control within a defined demilitarized zone between the process control network and the plant information network; and 3) Security event logging. In addition, NPCC_URE2 did not experience any cyber security-related events involving these assets. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Identified nine additional assets that must be included on the CCA list, including the physical access control system server and eight panels; 2. Conducted internal analysis to identify the required controls for each asset and created a tracking spreadsheet to monitor the implementation of the controls; 3. Updated the CCA list; 4. Implemented the required controls on each asset; and 5. Performed a final review of the tracking spreadsheet to ensure that the control for each asset was implemented correctly. | 2011-11-30 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor. NPCC considered that NPCC_URE2 completed the Mitigation Plan after the approved completion date. NPCC determined that no adjustments to the penalty were warranted because the entity was completing related work under a separate Mitigation Plan that followed a different timeline and NPCC was aware of the revised timeframe.
2012-04-30 | FERC | NP12-26-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007272 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-007-1 R1.1 to NPCC. During an internal review of NPCC_URE2’s NERC CIP compliance program, NPCC_URE2 discovered, due to an oversight, the lack of a documented cyber security testing procedure specific to verifying that changes made to existing Critical Cyber Assets (CCAs) did not adversely affect that same CCAs' security controls. | CIP-007-1 | R1; R1.1 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 has implemented and adheres to a comprehensive change management procedure that includes extensive testing and validation of changes to the CCAs prior to going into a production environment. NPCC_URE2 had a documented corporate change management procedure in place, while not specific to CCAs, was applied to all assets. | When the Standard became mandatory and enforceable for NPCC_URE2 | Mitigation Plan completion | $25,000 (for NPCC2011007269, NPCC2011007270, NPCC2011007271, and NPCC2011007272) | Self-Report | NPCC_URE2 submitted a Mitigation Plan to NPCC. In accordance with the Mitigation Plan, NPCC_URE2: 1. Developed and implemented a cyber security controls testing procedure to validate and document that existing cyber security controls are not adversely impacted when significant changes are made to CCAs, which was shared with all relevant employees; and 2. Provided documented cyber security test results for CCAs. | 2011-12-23 | 2012-01-18 | Neither Admits Nor Denies | In assessing the penalty, NPCC considered NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, as a mitigating factor.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100854 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF indicating a violation of CIP-009-1 R1. RFC_URE1 did not include 46% of its Critical Cyber Assets (CCAs) in its recovery plan, as required by CIP-009-1 R1.1. RFC_URE1’s recovery plan did not specify events or conditions of varying duration and severity that would activate the recovery plan, pursuant to CIP-009-1 R1.1. Additionally, RFC_URE1’s recovery plan did not define all of the roles and responsibilities of responders, as required by CIP-009-1 R1.2. RF determined that RFC_URE1 violated CIP-009-1 R1 when it did not include all of its CCAs within its recovery plan and did not address the requirements of CIP-009-1 R1.1 and R1.2 within its recovery plan. | CIP-009-1 | R1 | Medium | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, RFC_URE1 addressed responding to events of varying duration and severity within its CIP-008 Cyber Security Incident response plan. Similarly, RFC_URE1 addressed the roles and responsibilities of responders within its CIP-003 cyber security policy. Additionally, RFC_URE1 represents that the information that was not specifically stated within its recovery plan was readily available to authorized RFC_URE1 personnel responding to an event requiring the recovery of CCAs. | When RFC_URE1 was subject to compliance with CIP-009-1 R1 | When RFC_URE1 revised its recovery plan to comply with CIP-009-1 R1 | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Report | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-009-1 R1. In accordance with the Mitigation Plan, RFC_URE1 revised its recovery plan to specify events or conditions of varying duration and severity that would activate the recovery plan, defined the roles and responsibilities of responders, and included all of RFC_URE1’s CCAs. | 2011-01-28 | 2011-12-27 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount. RF also considered the fact that RFC_URE1 self-reported the violation, as a mitigating factor. Internal controls and Self-Reports of possible violations assist RF’s mission of improving the reliability of the BPS.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100922 | Settlement Agreement | RFC_URE1 self-certified noncompliance with Reliability Standard CIP-005-1 R3 with RF. RFC_URE1's security monitoring process to detect and alert for unauthorized access attempts at two firewalls located on an Electronic Security Perimeter (ESP) was not properly configured. Specifically, RFC_URE1's security management software tool was configured to alert RFC_URE1 about unauthorized access attempts based upon a threshold frequency of access denials from a specific IP address. However, RFC_URE1 did not configure its two firewalls to report access denial events to the security management software tool. As a result, RFC_URE1's security logging and alerts would not have functioned correctly if there had been unauthorized access attempts to the firewalls. RF determined that RFC_URE1 violated CIP-005-1 R3.2 when it could not detect and alert for attempts at or actual unauthorized accesses to the ESP. | CIP-005-1 | R3.2 | Medium | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the several factors. The firewalls on the ESP were configured to deny access by default, and therefore the Critical Cyber Assets (CCAs) within the ESP remained protected from unauthorized access attempts throughout the duration of the violation. Additionally, the security management software tool did log all permitted access attempts and firewall configuration changes. | When RFC_URE1 was subject to compliance with CIP-005-1 R3.2 | Date the firewalls were properly configured to log and report access denial events to the security management software tool | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Certification | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-005-1 R3.2. In accordance with the Mitigation Plan, the firewalls at RFC_URE1 were properly configured to log and alert for denied unauthorized access attempts. | 2010-10-12 | 2012-02-09 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100923 | Settlement Agreement | RFC_URE1 self-certified noncompliance with Reliability Standard CIP-007-1 R2 with RF. A network switch located inside the Electronic Security Perimeter (ESP) had ports and services that were not required for normal or emergency operations, but still enabled, in violation of CIP-007-1 R2. RF determined that RFC_URE1 violated CIP-007-1 R2 when it did not enable only those ports and services required for normal and emergency operations, and failed to disable other ports and services prior to production use of all Cyber Assets inside the ESP. | CIP-007-1 | R2 | Medium | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the network switch is located behind the ESP firewall and is therefore not accessible from outside the ESP. | When RFC_URE1 was subject to compliance with CIP-007-1 R2 | Date the ports and services on the network switch were disabled | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Certification | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-007-3 R2. In this Mitigation Plan, RFC_URE1 outlined the actions it took to mitigate the violation. RFC_URE1 disabled the ports and services that were enabled on the network switch. | 2010-11-19 | 2011-12-20 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100924 | Settlement Agreement | RFC_URE1 self-certified noncompliance with Reliability Standard CIP-007-1 R5 to RF. RFC_URE1 did not remove or disable factory default accounts on a network switch pursuant to CIP-007-1 R5.2.2 (this network switch is also described in the violation of CIP-007-1 R2). In addition, these factory default accounts did not meet the password requirements of CIP-007-1 R5.3. Specifically, a network switch within the Electronic Security Perimeter (ESP) had factory default accounts that were not removed, disabled, or renamed. Additionally, passwords for the two factory default accounts were not created prior to placing them into service, and the passwords did not conform to the requirements of CIP-007-1 R5.3. RF determined that RFC_URE1 violated CIP-007-1 R5.3 when it did not manage the scope and acceptable use of factory default accounts and when it did not require and use passwords that conform to CIP-007-1 R5.3. | CIP-007-1 | R5; R5.2.2; R5.3 | Lower | Severe | RF determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the network switch containing the two factory default accounts is located behind the ESP firewall and is therefore not accessible from outside the ESP. | When RFC_URE1 was subject to compliance with CIP-007-1 R5.3 | Date RFC_URE1 set complex passwords which comply with CIP-007-1 R5.3 for the two factory default accounts on the network switch | $12,000 (for RFC201100854, RFC201100922, RFC201100923, and RFC201100924) | Self-Certification | RFC_URE1 submitted to RF a Mitigation Plan to address the violation of CIP-007-3 R5. In accordance with the Mitigation Plan, RFC_URE1 set complex passwords for the two factory default accounts on the network switch that conform to CIP-007-1 R5. | 2010-11-19 | 2011-12-20 | Agrees/ Stipulates | RF considered certain aspects of RFC_URE1’s compliance program as mitigating factors when determining the penalty amount.
2012-04-30 | FERC | NP12-26-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | SPP201000278 | Settlement Agreement | SPP-RFC-TRE_URE1s submitted Self Reports to SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions) reporting a violation of CIP-006-1 R1.6 which occurred in four different instances: 1. The first instance of this violation, an SPP-RFC-TRE_URE1s employee (a mail delivery person), who was authorized to physically access SPP-RFC-TRE_URE1s's operations physical security perimeter (PSP), accessed a restricted area to deliver mail. While the mail delivery person was pushing the mail cart through the door, another SPP-RFC-TRE_URE1s employee (visitor) without authorized physical access slipped past the mail delivery person and entered the restricted area without the mail delivery person's knowledge. The visitor was attempting to find a conference room that is located outside the operations area to attend a meeting and was unaware of the actual location of the meeting. Within seconds of the visitor’s entry into the restricted area, an operations employee noticed him from a distance and began walking after him and redirected the visitor to where he was trying to go. The total time of the visitor’s unauthorized access was approximately three minutes; 2. The second instance of this violation, an SPP-RFC-TRE_URE1sIT support technician signed in and escorted a vendor technician into SPP-RFC-TRE_URE1s's data center, which is located within a PSP. The original IT support technician who was escorting the technician was the only person working the mainframe desk and had to leave the vendor to return to work the mainframe desk. About 45 minutes later, following a shift change, a different SPP-RFC-TRE_URE1s employee, who had authorized unescorted physical access to the data center, noticed the vendor technician working in the automatic tape library (ATL) without an escort. The SPP-RFC-TRE_URE1s employee escorted the vendor technician until he completed his work and signed out of the restricted area of the data center. Video surveillance showed that the vendor technician was never in the proximity of the Electronic Security Perimeter Critical Asset devices and never gained access to such devices while inside the data center; 3. The third instance of this violation, an SPP-RFC-TRE_URE1s employee, believing he had authorized physical access to a telecom room, went to the telecom room to check the fire extinguisher. The visitor had authorized unescorted physical access to other Critical Cyber Assets (CCAs) within the same facility, but the approval for the telecom room was still pending. The employee presented his card and fingerprint at the bio-reader next to the access door. When the employee pushed on the door, it opened, he entered the telecom room and the door closed behind him. Immediately after the visitor opened the door, SPP-RFC-TRE_URE1s's security received an alarm of a forced door. A security employee called the telecom room and the visitor answered, while two other SPP-RFC-TRE_URE1s employees were troubleshooting the alarm, the security employee checked the authorized access list to the telecom room and discovered the visitor did not have unescorted physical access to the telecom room. Upon this discovery, the SOC employee asked the visitor to leave the telecom room immediately. The employee remained in the restricted room for about three minutes. Upon further investigation, SPP-RFC-TRE_URE1s determined that the magnetic lock on the door was not working properly and was the reason the door was prevented from being fully secured. SPP-RFC-TRE_URE1s maintained human observation at the door until the vendor completed the repair to the magnetic lock; and 4. The fourth instance of this violation, SPP-RFC-TRE_URE1s was conducting a fire alarm test in one of its facilities. As a safety precaution, some of the doors in the facility automatically unlocked during the fire alarm test. One such door provided access to the data center, which is located within a PSP. An SPP-RFC-TRE_URE1s employee who was participating in the fire alarm test walked briskly past the security guard who was standing approximately 20 feet from the data center door. The SPP-RFC-TRE_URE1s employee was checking fire alarms and believed that he had authorized unescorted physical access to the data center because he already requested access to that area, and SPP-RFC-TRE_URE1s granted him authorized unescorted physical access for a nearby PSP approximately three months earlier. SPP-RFC-TRE_URE1s discovered that the security guard failed to follow SPP-RFC-TRE_URE1s's protocol to stop all individuals attempting to enter restricted areas and to call security to verify access rights before allowing entry into such areas. | CIP-006-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-006-1 R1.6 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For the first instance, after the visitor entered the operations PSP, he was immediately noticed by an SPP-RFC-TRE_URE1s operations employee who followed him and corrected him. Additionally, the visitor was never near the location of the operations generation dispatch workstations (SPP-RFC-TRE_URE1s CCAs). These workstations are continuously manned, and as a precautionary measure, have biometric keyboard locks should the workstations ever be unmanned. For the second instance of this violation, an SPP-RFC-TRE_URE1s IT support technician was granted unescorted physical access to the data center. However, video surveillance showed that the support technician was never in the proximity of the ESP Critical Asset devices and never gained access to such devices while inside the data center. There were also password protective measures in place to ensure the technician didn't acquire electronic access to Critical Asset devices. Additionally, the ATL is neither a Critical Asset nor inside the data center's ESP. For the third instance of this violation, the individual was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted, and he had completed cyber security training. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the telecom room less than a month after the incident. Finally, the SPP-RFC-TRE_URE1s employee was only in the restricted room for about three minutes. For the fourth instance of this violation, the employee was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted and cyber security training had been completed for the employee. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the PSP. Finally, the visitor was in the restricted room for less than one minute. | the date of the first instance of non-compliance with CIP-006-1 R1 | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Self-Report | Upon learning of each instance, SPP-RFC-TRE_URE1s promptly investigated to determine the appropriate corrective actions needed to prevent a reoccurrence of a violation of CIP-006-1 R.1. To help ensure compliance with CIP-006-1 R1.6, SPP-RFC-TRE_URE1s delivered to all personnel with authorized unescorted physical access to operations PSP, telecom room, and data center a flyer with guidelines in preventing tailgating and unescorted access. (Instance Nos. 1, 3, and 4). The guidelines, in part, remind SPP-RFC-TRE_URE1s personnel to be aware of individuals around them when accessing and exiting SPP-RFC-TRE_URE1s facilities, not allow others to use their access card to enter a restricted area behind them; to know that SPP-RFC-TRE_URE1s access is different from CIP security access and to know that an individual’s authorized physical access to one CIP restricted area does not necessarily mean the individual has access to another CIP restricted area. The flyer reinforces security training already included in SPP-RFC-TRE_URE1s's annual training courses for CIP access. At the time of the violation, SPP-RFC-TRE_URE1s had signs posted at each operations PSP access door. The signs remind SPP-RFC-TRE_URE1s employees and visitors (those without authorized unescorted access) that the operations PSP is a restricted area; only those with ID card approved access are allowed to enter the restricted area and that all visitors must sign in and out on each visit to the area and are to be escorted at all times. As part of SPP-RFC-TRE_URE1s's Mitigation Plan, SPP-RFC-TRE_URE1s installed additional door signs at each operations PSP access door (Instance No. 1). SPP-RFC-TRE_URE1s used the flyer it circulated to the operations staff and made it into a sign; therefore, the signs contain the identical language and guidelines as the flyers described above. SPP-RFC-TRE_URE1s also required all corporate IT personnel to conduct cyber security training to ensure that they understand SPP-RFC-TRE_URE1s's security procedures and access requirements for CIP restricted areas (Instance Nos. 1 and 2). SPP-RFC-TRE_URE1s further required affected IT personnel to retake CIP training to ensure they have clear guidance on how to request assistance to support an increase in workload (Instance No. 2). The IT personnel also received a call-out policy and escalation procedure for requesting assistance when they are short-staffed. The faulty magnetic lock on the door leading to the telecom room was repaired (Instance No. 3). The security personnel were interviewed about the fourth instance and counseled to ensure their understanding about their roles and responsibilities for CIP compliance (Instance No. 4). | 2010-12-31 | 2011-03-22 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | RFC201000366 | Settlement Agreement | SPP-RFC-TRE_URE1s submitted Self Reports to SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions) reporting a violation of CIP-006-1 R1.6 which occurred in four different instances: 1. The first instance of this violation, an SPP-RFC-TRE_URE1s employee (a mail delivery person), who was authorized to physically access SPP-RFC-TRE_URE1s's operations physical security perimeter (PSP), accessed a restricted area to deliver mail. While the mail delivery person was pushing the mail cart through the door, another SPP-RFC-TRE_URE1s employee (visitor) without authorized physical access slipped past the mail delivery person and entered the restricted area without the mail delivery person's knowledge. The visitor was attempting to find a conference room that is located outside the operations area to attend a meeting and was unaware of the actual location of the meeting. Within seconds of the visitor’s entry into the restricted area, an operations employee noticed him from a distance and began walking after him and redirected the visitor to where he was trying to go. The total time of the visitor’s unauthorized access was approximately three minutes; 2. The second instance of this violation, an SPP-RFC-TRE_URE1sIT support technician signed in and escorted a vendor technician into SPP-RFC-TRE_URE1s's data center, which is located within a PSP. The original IT support technician who was escorting the technician was the only person working the mainframe desk and had to leave the vendor to return to work the mainframe desk. About 45 minutes later, following a shift change, a different SPP-RFC-TRE_URE1s employee, who had authorized unescorted physical access to the data center, noticed the vendor technician working in the automatic tape library (ATL) without an escort. The SPP-RFC-TRE_URE1s employee escorted the vendor technician until he completed his work and signed out of the restricted area of the data center. Video surveillance showed that the vendor technician was never in the proximity of the Electronic Security Perimeter Critical Asset devices and never gained access to such devices while inside the data center; 3. The third instance of this violation, an SPP-RFC-TRE_URE1s employee, believing he had authorized physical access to a telecom room, went to the telecom room to check the fire extinguisher. The visitor had authorized unescorted physical access to other Critical Cyber Assets (CCAs) within the same facility, but the approval for the telecom room was still pending. The employee presented his card and fingerprint at the bio-reader next to the access door. When the employee pushed on the door, it opened, he entered the telecom room and the door closed behind him. Immediately after the visitor opened the door, SPP-RFC-TRE_URE1s's security received an alarm of a forced door. A security employee called the telecom room and the visitor answered, while two other SPP-RFC-TRE_URE1s employees were troubleshooting the alarm, the security employee checked the authorized access list to the telecom room and discovered the visitor did not have unescorted physical access to the telecom room. Upon this discovery, the SOC employee asked the visitor to leave the telecom room immediately. The employee remained in the restricted room for about three minutes. Upon further investigation, SPP-RFC-TRE_URE1s determined that the magnetic lock on the door was not working properly and was the reason the door was prevented from being fully secured. SPP-RFC-TRE_URE1s maintained human observation at the door until the vendor completed the repair to the magnetic lock; and 4. The fourth instance of this violation, SPP-RFC-TRE_URE1s was conducting a fire alarm test in one of its facilities. As a safety precaution, some of the doors in the facility automatically unlocked during the fire alarm test. One such door provided access to the data center, which is located within a PSP. An SPP-RFC-TRE_URE1s employee who was participating in the fire alarm test walked briskly past the security guard who was standing approximately 20 feet from the data center door. The SPP-RFC-TRE_URE1s employee was checking fire alarms and believed that he had authorized unescorted physical access to the data center because he already requested access to that area, and SPP-RFC-TRE_URE1s granted him authorized unescorted physical access for a nearby PSP approximately three months earlier. SPP-RFC-TRE_URE1s discovered that the security guard failed to follow SPP-RFC-TRE_URE1s's protocol to stop all individuals attempting to enter restricted areas and to call security to verify access rights before allowing entry into such areas. | CIP-006-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-006-1 R1.6 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For the first instance, after the visitor entered the operations PSP, he was immediately noticed by an SPP-RFC-TRE_URE1s operations employee who followed him and corrected him. Additionally, the visitor was never near the location of the operations generation dispatch workstations (SPP-RFC-TRE_URE1s CCAs). These workstations are continuously manned, and as a precautionary measure, have biometric keyboard locks should the workstations ever be unmanned. For the second instance of this violation, an SPP-RFC-TRE_URE1s IT support technician was granted unescorted physical access to the data center. However, video surveillance showed that the support technician was never in the proximity of the ESP Critical Asset devices and never gained access to such devices while inside the data center. There were also password protective measures in place to ensure the technician didn't acquire electronic access to Critical Asset devices. Additionally, the ATL is neither a Critical Asset nor inside the data center's ESP. For the third instance of this violation, the individual was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted, and he had completed cyber security training. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the telecom room less than a month after the incident. Finally, the SPP-RFC-TRE_URE1s employee was only in the restricted room for about three minutes. For the fourth instance of this violation, the employee was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted and cyber security training had been completed for the employee. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the PSP. Finally, the visitor was in the restricted room for less than one minute. | the date of the first instance of non-compliance with CIP-006-1 R1 | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Self-Report | Upon learning of each instance, SPP-RFC-TRE_URE1s promptly investigated to determine the appropriate corrective actions needed to prevent a reoccurrence of a violation of CIP-006-1 R.1. To help ensure compliance with CIP-006-1 R1.6, SPP-RFC-TRE_URE1s delivered to all personnel with authorized unescorted physical access to operations PSP, telecom room, and data center a flyer with guidelines in preventing tailgating and unescorted access. (Instance Nos. 1, 3, and 4). The guidelines, in part, remind SPP-RFC-TRE_URE1s personnel to be aware of individuals around them when accessing and exiting SPP-RFC-TRE_URE1s facilities, not allow others to use their access card to enter a restricted area behind them; to know that SPP-RFC-TRE_URE1s access is different from CIP security access and to know that an individual’s authorized physical access to one CIP restricted area does not necessarily mean the individual has access to another CIP restricted area. The flyer reinforces security training already included in SPP-RFC-TRE_URE1s's annual training courses for CIP access. At the time of the violation, SPP-RFC-TRE_URE1s had signs posted at each operations PSP access door. The signs remind SPP-RFC-TRE_URE1s employees and visitors (those without authorized unescorted access) that the operations PSP is a restricted area; only those with ID card approved access are allowed to enter the restricted area and that all visitors must sign in and out on each visit to the area and are to be escorted at all times. As part of SPP-RFC-TRE_URE1s's Mitigation Plan, SPP-RFC-TRE_URE1s installed additional door signs at each operations PSP access door (Instance No. 1). SPP-RFC-TRE_URE1s used the flyer it circulated to the operations staff and made it into a sign; therefore, the signs contain the identical language and guidelines as the flyers described above. SPP-RFC-TRE_URE1s also required all corporate IT personnel to conduct cyber security training to ensure that they understand SPP-RFC-TRE_URE1s's security procedures and access requirements for CIP restricted areas (Instance Nos. 1 and 2). SPP-RFC-TRE_URE1s further required affected IT personnel to retake CIP training to ensure they have clear guidance on how to request assistance to support an increase in workload (Instance No. 2). The IT personnel also received a call-out policy and escalation procedure for requesting assistance when they are short-staffed. The faulty magnetic lock on the door leading to the telecom room was repaired (Instance No. 3). The security personnel were interviewed about the fourth instance and counseled to ensure their understanding about their roles and responsibilities for CIP compliance (Instance No. 4). | 2010-12-31 | 2011-03-22 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | TRE201000180 | Settlement Agreement | SPP-RFC-TRE_URE1s submitted Self Reports to SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions) reporting a violation of CIP-006-1 R1.6 which occurred in four different instances: 1. The first instance of this violation, an SPP-RFC-TRE_URE1s employee (a mail delivery person), who was authorized to physically access SPP-RFC-TRE_URE1s's operations physical security perimeter (PSP), accessed a restricted area to deliver mail. While the mail delivery person was pushing the mail cart through the door, another SPP-RFC-TRE_URE1s employee (visitor) without authorized physical access slipped past the mail delivery person and entered the restricted area without the mail delivery person's knowledge. The visitor was attempting to find a conference room that is located outside the operations area to attend a meeting and was unaware of the actual location of the meeting. Within seconds of the visitor’s entry into the restricted area, an operations employee noticed him from a distance and began walking after him and redirected the visitor to where he was trying to go. The total time of the visitor’s unauthorized access was approximately three minutes; 2. The second instance of this violation, an SPP-RFC-TRE_URE1sIT support technician signed in and escorted a vendor technician into SPP-RFC-TRE_URE1s's data center, which is located within a PSP. The original IT support technician who was escorting the technician was the only person working the mainframe desk and had to leave the vendor to return to work the mainframe desk. About 45 minutes later, following a shift change, a different SPP-RFC-TRE_URE1s employee, who had authorized unescorted physical access to the data center, noticed the vendor technician working in the automatic tape library (ATL) without an escort. The SPP-RFC-TRE_URE1s employee escorted the vendor technician until he completed his work and signed out of the restricted area of the data center. Video surveillance showed that the vendor technician was never in the proximity of the Electronic Security Perimeter Critical Asset devices and never gained access to such devices while inside the data center; 3. The third instance of this violation, an SPP-RFC-TRE_URE1s employee, believing he had authorized physical access to a telecom room, went to the telecom room to check the fire extinguisher. The visitor had authorized unescorted physical access to other Critical Cyber Assets (CCAs) within the same facility, but the approval for the telecom room was still pending. The employee presented his card and fingerprint at the bio-reader next to the access door. When the employee pushed on the door, it opened, he entered the telecom room and the door closed behind him. Immediately after the visitor opened the door, SPP-RFC-TRE_URE1s's security received an alarm of a forced door. A security employee called the telecom room and the visitor answered, while two other SPP-RFC-TRE_URE1s employees were troubleshooting the alarm, the security employee checked the authorized access list to the telecom room and discovered the visitor did not have unescorted physical access to the telecom room. Upon this discovery, the SOC employee asked the visitor to leave the telecom room immediately. The employee remained in the restricted room for about three minutes. Upon further investigation, SPP-RFC-TRE_URE1s determined that the magnetic lock on the door was not working properly and was the reason the door was prevented from being fully secured. SPP-RFC-TRE_URE1s maintained human observation at the door until the vendor completed the repair to the magnetic lock; and 4. The fourth instance of this violation, SPP-RFC-TRE_URE1s was conducting a fire alarm test in one of its facilities. As a safety precaution, some of the doors in the facility automatically unlocked during the fire alarm test. One such door provided access to the data center, which is located within a PSP. An SPP-RFC-TRE_URE1s employee who was participating in the fire alarm test walked briskly past the security guard who was standing approximately 20 feet from the data center door. The SPP-RFC-TRE_URE1s employee was checking fire alarms and believed that he had authorized unescorted physical access to the data center because he already requested access to that area, and SPP-RFC-TRE_URE1s granted him authorized unescorted physical access for a nearby PSP approximately three months earlier. SPP-RFC-TRE_URE1s discovered that the security guard failed to follow SPP-RFC-TRE_URE1s's protocol to stop all individuals attempting to enter restricted areas and to call security to verify access rights before allowing entry into such areas. | CIP-006-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-006-1 R1.6 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). For the first instance, after the visitor entered the operations PSP, he was immediately noticed by an SPP-RFC-TRE_URE1s operations employee who followed him and corrected him. Additionally, the visitor was never near the location of the operations generation dispatch workstations (SPP-RFC-TRE_URE1s CCAs). These workstations are continuously manned, and as a precautionary measure, have biometric keyboard locks should the workstations ever be unmanned. For the second instance of this violation, an SPP-RFC-TRE_URE1s IT support technician was granted unescorted physical access to the data center. However, video surveillance showed that the support technician was never in the proximity of the ESP Critical Asset devices and never gained access to such devices while inside the data center. There were also password protective measures in place to ensure the technician didn't acquire electronic access to Critical Asset devices. Additionally, the ATL is neither a Critical Asset nor inside the data center's ESP. For the third instance of this violation, the individual was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted, and he had completed cyber security training. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the telecom room less than a month after the incident. Finally, the SPP-RFC-TRE_URE1s employee was only in the restricted room for about three minutes. For the fourth instance of this violation, the employee was a trusted SPP-RFC-TRE_URE1s employee and had authorized unescorted physical access to other CCAs within the same facility. A personnel risk assessment had been conducted and cyber security training had been completed for the employee. SPP-RFC-TRE_URE1s granted the employee unescorted physical access to the PSP. Finally, the visitor was in the restricted room for less than one minute. | the date of the first instance of non-compliance with CIP-006-1 R1 | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Self-Report | Upon learning of each instance, SPP-RFC-TRE_URE1s promptly investigated to determine the appropriate corrective actions needed to prevent a reoccurrence of a violation of CIP-006-1 R.1. To help ensure compliance with CIP-006-1 R1.6, SPP-RFC-TRE_URE1s delivered to all personnel with authorized unescorted physical access to operations PSP, telecom room, and data center a flyer with guidelines in preventing tailgating and unescorted access. (Instance Nos. 1, 3, and 4). The guidelines, in part, remind SPP-RFC-TRE_URE1s personnel to be aware of individuals around them when accessing and exiting SPP-RFC-TRE_URE1s facilities, not allow others to use their access card to enter a restricted area behind them; to know that SPP-RFC-TRE_URE1s access is different from CIP security access and to know that an individual’s authorized physical access to one CIP restricted area does not necessarily mean the individual has access to another CIP restricted area. The flyer reinforces security training already included in SPP-RFC-TRE_URE1s's annual training courses for CIP access. At the time of the violation, SPP-RFC-TRE_URE1s had signs posted at each operations PSP access door. The signs remind SPP-RFC-TRE_URE1s employees and visitors (those without authorized unescorted access) that the operations PSP is a restricted area; only those with ID card approved access are allowed to enter the restricted area and that all visitors must sign in and out on each visit to the area and are to be escorted at all times. As part of SPP-RFC-TRE_URE1s's Mitigation Plan, SPP-RFC-TRE_URE1s installed additional door signs at each operations PSP access door (Instance No. 1). SPP-RFC-TRE_URE1s used the flyer it circulated to the operations staff and made it into a sign; therefore, the signs contain the identical language and guidelines as the flyers described above. SPP-RFC-TRE_URE1s also required all corporate IT personnel to conduct cyber security training to ensure that they understand SPP-RFC-TRE_URE1s's security procedures and access requirements for CIP restricted areas (Instance Nos. 1 and 2). SPP-RFC-TRE_URE1s further required affected IT personnel to retake CIP training to ensure they have clear guidance on how to request assistance to support an increase in workload (Instance No. 2). The IT personnel also received a call-out policy and escalation procedure for requesting assistance when they are short-staffed. The faulty magnetic lock on the door leading to the telecom room was repaired (Instance No. 3). The security personnel were interviewed about the fourth instance and counseled to ensure their understanding about their roles and responsibilities for CIP compliance (Instance No. 4). | 2010-12-31 | 2011-03-22 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | SPP200900156 | Settlement Agreement | During a joint SPP RE and ReliabilityFirst Spot Check, SPP RE and ReliabilityFirst determined that SPP-RFC-TRE_URE1s had a violation of CIP-007-1 R1. Specifically, although SPP-RFC-TRE_URE1s conducted functionality testing to ensure the installation of a patch or upgrade did not adversely affect the proper operation of the application software running on the operations centers, SPP-RFC-TRE_URE1s failed to conduct testing on existing cyber security controls to ensure they had not been affected by the installation of such patches or upgrades. In addition, SPP-RFC-TRE_URE1s support staff periodically moved laptops into and out of the operations centers, which are within SPP-RFC-TRE_URE1s defined Electronic Security Perimeters (ESPs), to configure and administer supervisory control and data acquisition (SCADA) local area networks (LANs) of CIP substations; the laptops were not treated or tested as new Critical Assets each time they were moved back into the operation centers. During implementation of the Mitigation Plan for this violation, SPP-RFC-TRE_URE1s subsequently self-reported five other instances not included in the Spot Check in SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions): 1. A new version of the software was installed on the station personal computers at two substations, each within an SPP-RFC-TRE_URE1s ESP. The installation was completed without testing to confirm that cyber security controls would not be adversely affected; 2. Second, a patch was installed on the station personal computers at two substations, which is within an SPP-RFC-TRE_URE1s ESP, without prior testing to ensure that existing security controls would not be adversely affected; 3. Third, SPP-RFC-TRE_URE1s installed operating system security patches to a small subset of servers, which are within an SPP-RFC-TRE_URE1s ESP. SPP-RFC-TRE_URE1s applied a service pack to those servers without first testing whether the application would adversely affect existing security controls; 4. Fourth, while verifying the installation of past patches for SPP-RFC-TRE_URE1s's patch management process, SPP-RFC-TRE_URE1s discovered that an update was inadvertently pushed to production machines within a substation ESP without first being tested. Upon further investigation, it was found that the account, which had been disabled, had been re-enabled due to a push of an update to the production machines; and 5. Fifth, personal computer intended to be placed on the corporate network was inadvertently placed on an ESP network (the backup site). The following day SPP-RFC-TRE_URE1s's intrusion detection software alerted SPP-RFC-TRE_URE1s that the personal computer was on the wrong network, and access to the ESP network on the computer was disabled. | CIP-007-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-007-1 R1 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In one instance, a security control was affected; specifically, a system account that had been disabled as part of the security configuration of the affected system was enabled through the installation of the security patch. In the absence of testing, SPP-RFC-TRE_URE1s was not aware that the system account had been re-enabled until it performed a routine review of patches and discovered the issue. In another instance, a Cyber Asset was inadvertently connected to the wrong network, placing the system within the ESP without undergoing the necessary pre-installation CIP compliance steps. The risk introduced by the failure to test was mitigated by the in-depth layered defense SPP-RFC-TRE_URE1s had implemented during the violation period. SPP-RFC-TRE_URE1s utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. In the case of the system account, a routine path review discovered the error. In the case of the inadvertent network connection, the intrusion detection system detected and alerted staff to the error within twenty-four hours. Finally, the laptops in question were never re-purposed, were under the control of vetted personnel while outside the subject ESPs, and SPP-RFC-TRE_URE1 had installed intrusion detection software, firewall software, and anti-malware software to prevent the laptops from being compromised. | the date the Standard became mandatory and enforceable for SPP-RFC-TRE_URE1s | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Spot Check | SPP-RFC-TRE_URE1s modified its policies, procedures and associated documentation, where necessary, to implement cyber controls testing prior to deployment of patches and/or significant software changes. To accomplish this, SPP-RFC-TRE_URE1s tested a representative group of all the systems being modified in an offline, dedicated environment. The changes were deployed on these systems first, and scans and/or additional testing was performed, prior to the deployment on the remainder of the existing Cyber Assets within the ESP ensuring existing cyber security controls were not affected. To address the issue of laptops being moved in and out of the ESP, SPP-RFC-TRE_URE1s moved the "daily" laptop users outside of the ESP, and now requires an additional level of authentication for those users to gain electronic access to the ESP. Additionally, a policy to prohibit laptops, or any other cyber assets, from being connected within the ESP without first being properly tested was implemented. | 2011-02-08 | 2011-03-30 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | RFC200900327 | Settlement Agreement | During a joint SPP RE and ReliabilityFirst Spot Check, SPP RE and ReliabilityFirst determined that SPP-RFC-TRE_URE1s had a violation of CIP-007-1 R1. Specifically, although SPP-RFC-TRE_URE1s conducted functionality testing to ensure the installation of a patch or upgrade did not adversely affect the proper operation of the application software running on the operations centers, SPP-RFC-TRE_URE1s failed to conduct testing on existing cyber security controls to ensure they had not been affected by the installation of such patches or upgrades. In addition, SPP-RFC-TRE_URE1s support staff periodically moved laptops into and out of the operations centers, which are within SPP-RFC-TRE_URE1s defined Electronic Security Perimeters (ESPs), to configure and administer supervisory control and data acquisition (SCADA) local area networks (LANs) of CIP substations; the laptops were not treated or tested as new Critical Assets each time they were moved back into the operation centers. During implementation of the Mitigation Plan for this violation, SPP-RFC-TRE_URE1s subsequently self-reported five other instances not included in the Spot Check in SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions): 1. A new version of the software was installed on the station personal computers at two substations, each within an SPP-RFC-TRE_URE1s ESP. The installation was completed without testing to confirm that cyber security controls would not be adversely affected; 2. Second, a patch was installed on the station personal computers at two substations, which is within an SPP-RFC-TRE_URE1s ESP, without prior testing to ensure that existing security controls would not be adversely affected; 3. Third, SPP-RFC-TRE_URE1s installed operating system security patches to a small subset of servers, which are within an SPP-RFC-TRE_URE1s ESP. SPP-RFC-TRE_URE1s applied a service pack to those servers without first testing whether the application would adversely affect existing security controls; 4. Fourth, while verifying the installation of past patches for SPP-RFC-TRE_URE1s's patch management process, SPP-RFC-TRE_URE1s discovered that an update was inadvertently pushed to production machines within a substation ESP without first being tested. Upon further investigation, it was found that the account, which had been disabled, had been re-enabled due to a push of an update to the production machines; and 5. Fifth, personal computer intended to be placed on the corporate network was inadvertently placed on an ESP network (the backup site). The following day SPP-RFC-TRE_URE1s's intrusion detection software alerted SPP-RFC-TRE_URE1s that the personal computer was on the wrong network, and access to the ESP network on the computer was disabled. | CIP-007-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-007-1 R1 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In one instance, a security control was affected; specifically, a system account that had been disabled as part of the security configuration of the affected system was enabled through the installation of the security patch. In the absence of testing, SPP-RFC-TRE_URE1s was not aware that the system account had been re-enabled until it performed a routine review of patches and discovered the issue. In another instance, a Cyber Asset was inadvertently connected to the wrong network, placing the system within the ESP without undergoing the necessary pre-installation CIP compliance steps. The risk introduced by the failure to test was mitigated by the in-depth layered defense SPP-RFC-TRE_URE1s had implemented during the violation period. SPP-RFC-TRE_URE1s utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. In the case of the system account, a routine path review discovered the error. In the case of the inadvertent network connection, the intrusion detection system detected and alerted staff to the error within twenty-four hours. Finally, the laptops in question were never re-purposed, were under the control of vetted personnel while outside the subject ESPs, and SPP-RFC-TRE_URE1 had installed intrusion detection software, firewall software, and anti-malware software to prevent the laptops from being compromised. | the date the Standard became mandatory and enforceable for SPP-RFC-TRE_URE1s | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Spot Check | SPP-RFC-TRE_URE1s modified its policies, procedures and associated documentation, where necessary, to implement cyber controls testing prior to deployment of patches and/or significant software changes. To accomplish this, SPP-RFC-TRE_URE1s tested a representative group of all the systems being modified in an offline, dedicated environment. The changes were deployed on these systems first, and scans and/or additional testing was performed, prior to the deployment on the remainder of the existing Cyber Assets within the ESP ensuring existing cyber security controls were not affected. To address the issue of laptops being moved in and out of the ESP, SPP-RFC-TRE_URE1s moved the "daily" laptop users outside of the ESP, and now requires an additional level of authentication for those users to gain electronic access to the ESP. Additionally, a policy to prohibit laptops, or any other cyber assets, from being connected within the ESP without first being properly tested was implemented. | 2011-02-08 | 2011-03-30 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1-1 (Registered in SPP RE); Unidentified Registered Entity 1-2 (Registered in ReliabilityFirst); Unidentified Registered Entity 1-3 (Registered in Texas RE) (collectively, Unidentified Registered Entities 1 (SPP-RFC-TRE_URE1s) | NCRXXXXX | TRE201000225 | Settlement Agreement | During a joint SPP RE and ReliabilityFirst Spot Check, SPP RE and ReliabilityFirst determined that SPP-RFC-TRE_URE1s had a violation of CIP-007-1 R1. Specifically, although SPP-RFC-TRE_URE1s conducted functionality testing to ensure the installation of a patch or upgrade did not adversely affect the proper operation of the application software running on the operations centers, SPP-RFC-TRE_URE1s failed to conduct testing on existing cyber security controls to ensure they had not been affected by the installation of such patches or upgrades. In addition, SPP-RFC-TRE_URE1s support staff periodically moved laptops into and out of the operations centers, which are within SPP-RFC-TRE_URE1s defined Electronic Security Perimeters (ESPs), to configure and administer supervisory control and data acquisition (SCADA) local area networks (LANs) of CIP substations; the laptops were not treated or tested as new Critical Assets each time they were moved back into the operation centers. During implementation of the Mitigation Plan for this violation, SPP-RFC-TRE_URE1s subsequently self-reported five other instances not included in the Spot Check in SPP RE, ReliabilityFirst, and Texas RE (collectively, the Regions): 1. A new version of the software was installed on the station personal computers at two substations, each within an SPP-RFC-TRE_URE1s ESP. The installation was completed without testing to confirm that cyber security controls would not be adversely affected; 2. Second, a patch was installed on the station personal computers at two substations, which is within an SPP-RFC-TRE_URE1s ESP, without prior testing to ensure that existing security controls would not be adversely affected; 3. Third, SPP-RFC-TRE_URE1s installed operating system security patches to a small subset of servers, which are within an SPP-RFC-TRE_URE1s ESP. SPP-RFC-TRE_URE1s applied a service pack to those servers without first testing whether the application would adversely affect existing security controls; 4. Fourth, while verifying the installation of past patches for SPP-RFC-TRE_URE1s's patch management process, SPP-RFC-TRE_URE1s discovered that an update was inadvertently pushed to production machines within a substation ESP without first being tested. Upon further investigation, it was found that the account, which had been disabled, had been re-enabled due to a push of an update to the production machines; and 5. Fifth, personal computer intended to be placed on the corporate network was inadvertently placed on an ESP network (the backup site). The following day SPP-RFC-TRE_URE1s's intrusion detection software alerted SPP-RFC-TRE_URE1s that the personal computer was on the wrong network, and access to the ESP network on the computer was disabled. | CIP-007-1 | R1 | Medium | Severe | The Regions determined that SPP-RFC-TRE_URE1s's violation of CIP-007-1 R1 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In one instance, a security control was affected; specifically, a system account that had been disabled as part of the security configuration of the affected system was enabled through the installation of the security patch. In the absence of testing, SPP-RFC-TRE_URE1s was not aware that the system account had been re-enabled until it performed a routine review of patches and discovered the issue. In another instance, a Cyber Asset was inadvertently connected to the wrong network, placing the system within the ESP without undergoing the necessary pre-installation CIP compliance steps. The risk introduced by the failure to test was mitigated by the in-depth layered defense SPP-RFC-TRE_URE1s had implemented during the violation period. SPP-RFC-TRE_URE1s utilized security control measures, such as intrusion prevention systems, intrusion detection systems, and rogue computer detection systems to monitor and prevent attacks on Critical Assets located within the subject ESPs. In the case of the system account, a routine path review discovered the error. In the case of the inadvertent network connection, the intrusion detection system detected and alerted staff to the error within twenty-four hours. Finally, the laptops in question were never re-purposed, were under the control of vetted personnel while outside the subject ESPs, and SPP-RFC-TRE_URE1 had installed intrusion detection software, firewall software, and anti-malware software to prevent the laptops from being compromised. | the date the Standard became mandatory and enforceable for SPP-RFC-TRE_URE1s | the date SPP-RFC-TRE_URE1s completed its Mitigation Plan | $27,000 (for SPP201000278, SPP200900156, RFC201000366, RFC200900327, TRE201000180, and TRE201000225) | Spot Check | SPP-RFC-TRE_URE1s modified its policies, procedures and associated documentation, where necessary, to implement cyber controls testing prior to deployment of patches and/or significant software changes. To accomplish this, SPP-RFC-TRE_URE1s tested a representative group of all the systems being modified in an offline, dedicated environment. The changes were deployed on these systems first, and scans and/or additional testing was performed, prior to the deployment on the remainder of the existing Cyber Assets within the ESP ensuring existing cyber security controls were not affected. To address the issue of laptops being moved in and out of the ESP, SPP-RFC-TRE_URE1s moved the "daily" laptop users outside of the ESP, and now requires an additional level of authentication for those users to gain electronic access to the ESP. Additionally, a policy to prohibit laptops, or any other cyber assets, from being connected within the ESP without first being properly tested was implemented. | 2011-02-08 | 2011-03-30 | Neither Admits nor Denies | SPP RE, ReliabilityFirst, and Texas RE considered certain aspects of SPP-RFC-TRE_URE1s's compliance program as mitigating factors.
2012-04-30 | FERC | NP12-26-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102977 | Notice of Confirmed Violation | WECC_URE1 self-certified noncompliance with CIP-005-3 R5. WECC_URE1 stated that it was in violation of the Standard because it failed to review the documentation specified in CIP-005-3 R5 in the calendar year. Specifically, WECC_URE1 identified that it failed to review documentation relating to: (1) establishing and maintaining Electronic Security Perimeters; (2) monitoring system events related to Cyber Security; (3) user account access activities; and (4) the manual retrieval of system account logs. | CIP-005-3 | R5 (R5.1.) | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. There were no changes to the four CIP-005 procedures in scope. Also, WECC_URE1 demonstrated that all Critical Cyber Assets (CCAs) are located inside Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs) and are afforded all the protections of CIP-005 and CIP-006. | the date by which WECC_URE1 should have reviewed the documentation) | TBD | $17,300 (for WECC201102977 and WECC201102983) | Self-Certification | WECC_URE1 will review the documents specified in CIP-005-3 R5. In addition, WECC_URE1 will research and implement a more robust NERC compliance administrative task tracking calendar system. | Anticipated 7/1/2012 | TBD | Does Not Contest | WECC reviewed WECC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination.
2012-04-30 | FERC | NP12-26-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102983 | Notice of Confirmed Violation | WECC_URE1 self-certified noncompliance with CIP-007-3 R9. WECC_URE1 stated that it was in violation of the Standard because it failed to review the documentation specified in CIP-007-3 in the calendar year. Specifically, WECC_URE1 identified that it failed to review the documentation for 29 CIP-007 procedures, which topics include: (1) change implementation; (2) anti-virus and malware prevention; (3) tests to produce when Cyber Assets are modified; (4) security patches; (5) risk assessment; (6) user account access activities; (7) shared accounts; (8) passwords; (9) asset disposal or redeployment requests; (10) data destruction; (11) security tests; and (12) ports and services. | CIP-007-3 | R9 | Lower | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS. There were no changes to the 29 CIP-007 procedures in scope and all Critical Cyber Assets are located inside Electronic Security Perimeters and Physical Security Perimeters and are afforded all the CIP-005 and CIP-006 protections. | the date by which WECC_URE1 should have reviewed the documentation | TBD | $17,300 (for WECC201102977 and WECC201102983) | Self-Certification | WECC_URE1 will review the documents specified in CIP-007-3 R9. In addition, WECC_URE1 will research and implement a more robust NERC compliance administrative task tracking calendar system. | Anticipated 7/1/2012 | TBD | Does Not Contest | WECC reviewed WECC_URE1's Internal Compliance Program (ICP) and considered it to be a mitigating factor in the penalty determination.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201000219 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-006-2 R5. NPCC determined that NPCC_URE1 did not implement the technical controls for monitoring physical access at all access points to the Physical Security Perimeter twenty-four hours a day, seven days a week, as required by the Standard. NPCC_URE1 failed to do this for two of its Critical Assets at two of its facilities. | CIP-006-2 | R5 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 implements several other security solutions designed to minimize overall cyber security and physical security risk, including but not limited to: intrusion detection, anti-virus, security logging, access control (cyber and physical) and a defense-in-depth network design to minimize the risk to the BPS. Moreover, the two assets at issue were in fact determined not to be Critical Assets. NPCC_URE1 completed a risk-based asset management (RBAM) study after having its Mitigation Plan approved and determined the two assets did not need to be part of the Critical Asset list. NPCC Enforcement verified the one-line diagram and agreed with the assessment. Lastly, there were no incidents at NPCC_URE1 facilities related to the lack of proper monitoring of physical access. | when the Standard became mandatory and enforceable to NPCC_URE1 | date Mitigation Plan was completed | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-006-2 R5. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) interviewed the network engineer and plant personnel to better understand the best way to implement the Mitigation Plan; (2) scheduled conference calls with its telecommunications vendor to discuss various options and the expected timeframe for resolution (specifically, NPCC_URE1 attempted to install higher speed lines at each location to provide sufficient bandwidth to allow video and card reader access data combined with generation data); (3) scheduled installation and testing of satellite network, test camera and card reader functionality on the satellite line; (4) monitored continuous operations of alarms for two weeks; and (5) updated all relevant documentation associated with CIP-006 R5 and communicated those updates to all relevant staff. | 2011-04-28 | 2011-10-21 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201000220 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-002-2 R3. NPCC determined that NPCC_URE1 did not include the continuous emissions monitoring system on the list of Critical Cyber Assets (CCA) essential to the operation of the identified Critical Assets, as required by the Standard. The system (used as a means to comply with government air emission standards) is connected to the Critical Asset by serial communications, where a single stream of data is transmitted. NPCC_URE1 determined that due to the remote dial-up connectivity to this system, the asset would be identified as a CCA. | CIP-002-2 | R3 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 had developed a list of associated CCA essential to the operation of the Critical Asset and reviewed this list at least annually, and updated it as necessary. Also, the continuous emissions monitoring system has physical security control to the device and system logical access to the system is maintained, which provides additional security. There were no incidents at NPCC_URE1 facilities related to this violation. | when the Standard became mandatory and enforceable to NPCC_URE1 | when the violation was mitigated by updating all relevant documentation | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-002-2 R3. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) added the continuous emissions monitoring system to the CCA list; (2) interviewed the network engineer and applied the appropriate protective measures to the continuous emissions monitoring system equipment to conform to the CIP requirements; (3) required that all continuous emissions monitoring system equipment be afforded the protective measures required in the remaining CIP requirements; where any of the equipment cannot meet the standard, Technical Feasibility Exceptions will be submitted; (4) completed application of all relevant CIP requirements; (5) updated documentation relevant to CIP-002 R3 to ensure that it is in line with the requirements and establishes the expectations to maintain a state of compliance; and (6) all staff engaged in managing Cyber Assets within the ESP were notified of the changes and made aware of the requirements. | 2011-06-30 | 2011-10-25 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination. For the CIP-002-2 R3 violation, mitigation activities were not completed by the approved due date, and no extension was requested. This delay was considered by NPCC to be an aggravating factor in the penalty determination.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100247 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-006-2 R2. NPCC determined that NPCC_URE1 did not protect a server, a digital video recorder (DVR) and a personal computer (PC) from unauthorized physical access, as required by the Standard. These devices create badges; therefore they qualify as Cyber Assets that authorize and/or log access to the Physical Security Perimeter, and authorized access is needed for these devices to be considered access control and monitoring assets. | CIP-006-2 | R2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 documents and implements a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. NPCC_URE1 also implements several other security solutions designed to minimize overall cyber security and physical security risk, including but not limited to: intrusion detection, anti-virus, security logging, access control (cyber and physical) and a defense-in-depth network design to minimize the risk to the BPS. Additionally, there were no incidents at NPCC_URE1 facilities related to this violation. | when the Standard became mandatory and enforceable to NPCC_URE1 | date Mitigation Plan was completed | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-006-2 R2. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) interviewed the network engineer to better understand how best to implement the Mitigation Plan; (2) scheduled the protection of the Cyber Assets in accordance with CIP-006 R2.2; specifically, the server, DVR and PC were afforded all protections required in accordance with the Standard, and in instances where it is not technically feasible the appropriate TFE submittals will be made; (3) updated all documentation relevant to CIP-006 R2.2 to ensure that it is in line with the Standard and establishes the expectations to maintain a state of compliance; and (4) all staff engaged in managing Cyber Assets within the ESP were notified of changes and made aware of the requirements. | 2011-07-29 | 2011-10-25 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination. NPCC considered NPCC_URE1's and its affiliates' compliance history.
2012-04-30 | FERC | NP12-22-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100248 | Notice of Confirmed Violation | NPCC_URE1 self-reported a violation of CIP-007-1 R2. NPCC determined that NPCC_URE1 did not disable unused ports prior to production use of all Cyber Assets inside the Electronic Security Perimeter (ESP), as required by the Standard. The cause of the violation was NPCC_URE1's misunderstanding that the unused ports and services needed to be disabled on each Cyber Asset within the ESP. The unused ports were shut down on the firewalls, but not the specific Cyber Assets. | CIP-007-1 | R2 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE1 has processes and procedures for securing those systems determined to be Critical Cyber Assets, as well as the non-critical Cyber Assets within the ESP. NPCC_URE1 also implements several other security solutions designed to minimize overall cyber security and physical security risk, including but not limited to: intrusion detection, anti-virus, security logging, access control (cyber and physical) and a defense-in-depth network design to minimize the risk to the BPS. Additionally, there were no incidents at NPCC_URE1 facilities related to this violation. | when the Standard became mandatory and enforceable to NPCC_URE1 | when the violation was mitigated by updating all relevant documentation | $10,000 (for NPCC201000219, NPCC201000220, NPCC201100247, and NPCC201100248) | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-007-1 R2. In accordance with the Mitigation Plan, NPCC_URE1 has completed the following: (1) interviewed the network engineer to better understand how best to implement a Mitigation Plan; (2) reviewed each Cyber Asset within the ESP to determine the existing ports and services that are not currently disabled; (3) scheduled the disabling of all unused ports and services; (4) disabled all unused ports and services on each Cyber Asset within the ESP, or, if they could not be disabled for operational reasons, NPCC_URE1 documented the compensating measures applied to each Cyber Asset in order to mitigate the risk; (5) updated all documentation relevant to CIP-007 R2 to ensure that it is in line with the Standard and establishes the expectations to maintain a state of compliance; and (6) all staff engaged in managing Cyber Assets within the ESP were notified of changes and made aware of the requirements. | 2011-05-31 | 2011-10-21 | Does Not Contest | NPCC considered certain aspects of NPCC_URE1's compliance program, in effect at the time of the violation, to be mitigating factors in the penalty determination. NPCC considered NPCC_URE1's and its affiliates' compliance history.
2012-04-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000234 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to identify two substations as Critical Assets. The substations are essential to the regional blackstart cranking path and should have been identified using the criteria set forth in SPPRE_URE1's risk-based assessment methodology (RBAM). The RBAM states that blackstart resources that are in the SPP RE Regional Restoration Plan are to be considered and identifies blackstart assets as critical assets. SPPRE_URE1 correctly identified the combustion turbine, which is connected to one of the substations, as a blackstart generator and therefore a Critical Asset. Also, the transmission line between the two substations was properly identified as the blackstart cranking path and a Critical Asset. As the two substations are essential to energize the transmission line and allow power from the combustion turbine to flow across the cranking path, the two substations should have been deemed Critical Assets. | CIP-002-1 | R2 | High | High | SPP RE determined that SPPRE_URE1's violation of CIP-002-1 R2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because, upon adding the two substations to the critical asset list, SPPRE_URE1 determined that the two substations contained no associated Critical Cyber Assets. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 applied the approved methodology to its list of assets, added the two substations to its Critical Asset list, and the Chief Security Officer reviewed and approved the revised list. | 2010-06-14 | 2010-08-18 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000236 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to address, in its cyber security policy (CSP), all of the requirements of CIP-002 through CIP-009 as required by R1.1. Specifically, the following requirements: CIP-003-1 R1.1, 1.2, 1.3, 5.1, 5.1.2, 5.2.; CIP-004-1 R4; CIP-005-1 R1.2, 1.3, 2.3, 2.5, 2.5.1, 2.5.2, 2.5.4, 3, 3.1; CIP-006-1: R1.5, 1.8, 3, 3.1, 4; and CIP-007-1: R2.3, 5.2.2, 6.5. SPPRE_URE1 also did not make the CSP readily available to the supervisory control and data acquisition (SCADA)/Energy Management System (EMS) vendor support personnel with authorized electronic access, as required by R1.2. Further, there was no evidence of an annual review and approval of the CSP during the calendar year, as required by R1.3. | CIP-003-1 | R1 | Medium | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-003-1 R1 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because SPPRE_URE1 had a CSP in place, and although every requirement was not addressed in the consolidated policy document, individual policies addressing the CIP requirements were in place. Although the CSP was not readily available to the SCADA/EMS vendor personnel, no vendor personnel had accessed Critical Cyber Assets since prior to July 1, 2008. Further, the CSP was reviewed in two non-sequential years and only the one review was missed. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 revised its CSP to address all of the requirements from CIP-002 through CIP-009 and obtained Chief Security Officer approval. Also, SPPRE_URE1 made the CSP available to the SCADA/EMS vendor and added review and approval of the CSP to the list of annual reviews necessary under the Standards to ensure that the review is performed every year and is not omitted again. | 2010-10-01 | 2010-11-11 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000238 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1's failed to address, in its cyber security training (CST), proper use of Critical Cyber Assets (CCAs) pursuant to R2.2.1 and did not include recovery procedure training for CCAs pursuant to R2.2.4. Further, SPPRE_URE1 failed to provide documentation demonstrating that the janitorial staff members with authorized, unescorted access were trained pursuant to R2.3. This violation affected three janitorial staff members, SPPRE_URE1 attested that the janitorial staff received training. However, no other documentation supported the referenced attestation. | CIP-004-1 | R2; R2.2.1; R.2.2.4; R2.3 | Medium | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-004-1 R2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the training on CCAs under R2.2 only omitted part R2.2.1 until the 2009 updated annual training. Also, SPPRE_URE1 employees were generally aware of the proper use of the long-standing CCAs. All personnel with CCA access did receive CCA recovery procedure training in the previous year. For R2.3, SPPRE_URE1 provided an attestation that the janitorial staff had received training, although documentation could not be provided. Only three janitors had unescorted access, and they had received Personnel Risk Assessments. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 updated its CST materials to ensure that all required items were covered in the version of the training program. SPPRE_URE1 contracted with a new janitorial services provider, replacing its old provider. The on-site staff of the newly contracted company were provided the proper CST appropriate for their level of access prior to the issuance of such access. | 2010-07-01 | 2010-08-18 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000239 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to sufficiently document the cyber access afforded its supervisory control and data acquisition (SCADA)/Energy Management System (EMS) vendor support personnel via an administratively privileged shared user account. Additionally, SPPRE_URE1 violated R4.2 because it failed to demonstrate that one employee's physical access to Critical Cyber Assets was revoked within seven days of the employee's transfer, after which the employee no longer required such access. | CIP-004-1 | R4; R4.2 | Lower | Moderate | SPP RE determined that SPPRE_URE1's violation of CIP-004-1 R4 posed a minimal risk to the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because no SCADA/EMS vendor personnel had logged in via the shared user account since prior to the Standard became mandatory and enforceable. Further, SPPRE_URE1 utilized a physical safeguard by not maintaining a continuous open line for dial-in to SPPRE_URE1's system. If the vendor were to require access, SPPRE_URE1 would physically plug in a line to allow access and then unplug the line when the vendor was finished. As for R4.2, SPPRE_URE1's badge system showed that the employee's badge access rights were changed the day after the employee was transferred; however, the change could not be tied to the transferred employee because the badge system logged only the fact that a change occurred without indicating which employee's access was changed. Further, access logs demonstrate that subsequent to the employee's transfer, the transferred employee never attempted to gain physical access to the area from which his access was to be revoked. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 developed a written procedure to ensure proper management of the shared vendor account access. To mitigate the R4.2 violation, SPPRE_URE1 implemented a physical access request and revocation procedure. The procedure documents the change request and documents the date and time that the change is made. The procedure will be utilized until such time that SPPRE_URE1 obtains a badge system that will log specific identifying information regarding access changes. | 2010-05-11 | 2010-08-28 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000240 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 could not provide evidence demonstrating that it had compared test data from before and after the introduction of new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter in order to ensure that there were no adverse effects on existing cyber security controls. Specifically, SPPRE_URE1 did not save the results of running the software tool to perform a comparison of the before and after the network statistic tool runs (which SPPRE_URE1 did save), which were performed to test network and internet connections. The software tool comparison produces test results that demonstrate the testing was properly performed. | CIP-007-1 | R1.3 | Lower | Moderate | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R1.3 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because testing was performed before and after the introduction of new Cyber Assets and significant changes to existing Cyber Assets. In order to determine if the changes had an effect on cyber security controls, the results of the before and after tests need to be compared. SPPRE_URE1 performed such comparison as part of its testing procedure and was able to demonstrate the procedure to SPP RE; it had only failed to maintain documentation of having performed the comparison testing. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 amended its cyber security controls testing procedures to require that the results of the before and after comparison testing be saved. | 2010-09-15 | 2010-09-29 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000241 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 did not change a Windows shared user account password or otherwise secure the account following the retirement of an employee who had access to the shared account. | CIP-007-1 | R5.2 | Lower | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R5.2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because although the entity did not change the Windows account password, each employee has an individual Energy Management System application account that must be used to further authenticate access to the operator console. Additionally, physical access to the operator console and login access to the corporate network was revoked for the retiring employee. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 changed the account password and provided additional steps in its user account policy that specify that when an individual's access to a shared account is revoked, the password to the shared account is to be changed as well. | 2010-08-30 | 2010-09-24 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000242 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 had not changed a Windows shared user account password in over four years. CIP-007-1 R5.3 requires that passwords be changed at least annually. | CIP-007-1 | R5.3 | Lower | Lower | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R5.3 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the shared user account was local to a particular workstation and was only used to logon to the workstation following a reboot. Further, the workstation requires employees of SPPRE_URE1 to have individual Energy Management System application accounts which are changed annually. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 reviewed and ensured that all local and domain accounts had been changed within the required time. SPPRE_URE1 also set its software settings to enforce password changes to meet the requirements of CIP-007-1 R5.3. | 2010-07-31 | 2010-09-24 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000243 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to include in its Cyber Security Incident Response Plan (CSIRP) a defined process to ensure reporting of incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC) pursuant to R1.3. The CSIRP in effect prior to this plan, which was in effect a few years before the Standard became mandatory and enforceable, did not include: sufficient procedures to characterize and classify incidents as being reportable pursuant to R1.1; incident handling procedures pursuant to R1.2; a defined process to ensure reporting to the ES-ISAC pursuant to R1.3; or requirements to update within 90 days of any changes to the response plan pursuant to R1.4. Further, SPPRE_URE1 failed to perform an adequate test of the CSIRP pursuant to R1.6. SPPRE_URE1 had self-reported the violation of R1.6 indicating that it did not perform a test of its incident response plan by the date SPPRE_URE1 was first required to be compliant with CIP-008-1 R1. | CIP-008-1 | R1 | Lower | High | SPP RE has determined that SPPRE_URE1's violation of CIP-008-1 R1 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the bulk power system. The CSIRP provided that incidents at a certain security level (as defined in the CSIRP) involving Critical Cyber Assets were to be reported to the ES-ISAC. However, the CSIRP provided no ES-ISAC contact information or other details regarding how such reporting was to be accomplished. The omission of this process was the only deficiency found in the CSIRP. The plan, which was in effect prior to the date the Standard became mandatory and enforceable, had other deficiencies that were resolved upon implementation of the revised CSIRP. The prior plan did not include sufficient procedures to characterize and classify events as reportable or sufficient incident handling procedures. However, it did provide some examples of cyber security incidents and provided that in the event of an incident, an operations supervisor should be notified immediately. Had an incident occurred, an operations supervisor would have coordinated the response and handling of the incident. The operations supervisor is an electrical engineer with 20 years of experience in the electric industry, twelve years experience in a supervisory role in operations at SPPRE_URE1, and was responsible for the implementation of SPPRE_URE1's current SCADA/EMS system. Additionally, guidelines were provided in the prior plan to be considered during a cyber attack, although specific incident handling procedures were not provided. As for the violation of R1.6, an initial attempt at a response plan test was made. The test was a continuity of operations test in which the response to a virus taking down the EMS/SCADA server was to evacuate to the backup site and begin manual operations. No formal incident response procedure was followed. Another attempt was made to test the procedure. The documentation of that test provides that a review of the process was performed and general scenarios were tested. However, the scenarios were not documented so as to demonstrate that the plan was actually tested with respect to an incident involving Critical Cyber Assets. A compliant test was performed as part of the mitigation plan and documented. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 updated its CSIRP to include all elements required by CIP-008-1 R1, such as classification of reportable events, incident handling procedures, and detailed steps for reporting an incident to ES-ISAC, along with the requirement to update the plan within 90 days of any changes. SPPRE_URE1 ensured that the annual Incident Response Test fully tested the CSIRP. | 2010-10-28 | 2010-11-11 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor. Although SPPRE_URE1 self-reported part of the violation, the self-reported portion of the violation discovered during the Spot Check was a very small piece of the violation on the whole, so no self-reporting credit was given in the penalty assessment.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000244 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to sufficiently define in its recovery plan the roles and responsibilities of responders. | CIP-009-1 | R1 | Medium | High | SPP RE determined that SPPRE_URE1's violation of CIP-009-1 R1 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because SPPRE_URE1 had an otherwise well-defined plan for recovery of CCAs and a small enough staff that failure to fully document roles and responsibilities would not likely hamper the ability to execute the recovery plan when needed. In the event that the recovery plan had needed to be activated, the recovery of CCAs would have been coordinated by an experienced operations supervisor, who is the individual to which cyber incidents were required to be reported. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 updated its recovery plan to define roles and responsibilities based on job title and duties. These definitions are to be included in the updated Cyber Security Training materials. | 2010-10-01 | 2010-11-12 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000259 | Settlement Agreement | During a Spot Check, SPP RE discovered that SPPRE_URE1 failed to perform an adequate test of its recovery plan. The test, performed was a continuity of operations tabletop exercise that did not include restoration of the failed systems back to normal operation. SPPRE_URE1 had self-reported that it did not perform a test prior to the date SPPRE_URE1 was first required to be compliant with CIP-009-1 R2. | CIP-009-1 | R2 | Lower | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-009-1 R2 posed a minimal risk to the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because SPPRE_URE1 had a recovery plan in place, but failed to fully test the plan. SPPRE_URE1 did perform a continuity of operations table top exercise, however, that test did not include restoration of the failed systems back to normal operation. The scenario involved a tornado and the evacuation of operations to a backup location. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for SPP201000234; SPP201000236; SPP201000238; SPP201000239; SPP201000240; SPP201000241; SPP201000242; SPP201000243; SPP201000244; and SPP201000259) | Spot Check | SPPRE_URE1 performed and documented a full test of its recovery plan as required by CIP-009-1 R2. | 2010-10-11 | 2010-11-15 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violations, and it was considered a neutral factor. Since SPPRE_URE1 self-reported non-compliance with the Standard, SPP RE gave SPPRE_URE1 self-reporting credit.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000345 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-005-1 R2, more specifically R2.2 and R2.4. SPP RE_URE2 reported that it had not documented the configuration for those ports and services used in accessing its Electronic Security Perimeter (ESP) as required by R2.2. Additionally, SPP RE_URE2 had not documented the process utilized by its information technology administrators to remotely access SPP RE_URE2’s Energy Management System (EMS) through its ESP firewall, nor had SPP RE_URE2 adequately documented the external login process utilized by its read-only EMS users as required by R2.4. | CIP-005-1 | R2; R2.2; R2.4 | Medium | High | SPP RE determined that SPP RE_URE2's violation of CIP-005-1 R2 was documentary in nature and posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because regarding access restriction (R2.4), EMS access was restricted to user access and Cyber Asset administrator access through the ESP’s firewall. EMS users were allowed only read-only access through the firewall to the EMS server. Further, the users were first required to authenticate through the SPP RE_URE2 Physical Security Perimeter, then through the workstation console, and finally into the EMS application. Administrator access was accomplished by the same process but was limited to three individuals at SPP RE_URE2. In addition, SPP RE_URE2 administrators could only obtain configuration level access to the EMS network devices following the submission of a CIP access level request form that allowed administrators access to the “enable” password. Also, an encryption protocol was utilized for gaining access to the EMS server through the devices. These redundant authentication mechanisms helped to insulate the EMS servers from unauthorized access. Regarding ports and services (R2.2), despite the omission from SPP RE_URE2’s CIP-005-1 procedure, SPP RE_URE2 had documented its ports and services for ESP access in two earlier CIP-005 vulnerability assessments. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 documented its process for controlling access to the EMS web server inside the SPP RE_URE2 ESP. The process explains how a firewall protects the ESP from the corporate network allowing read-only access to the EMS server within the ESP for EMS users and requiring two layers of electronic authentication. In addition, administrators are limited to a subset of EMS network device commands after entering their corporate password. Also, a greater number of commands can only be obtained by submitting a CIP access level request form to gain access to the enable password on the SPP RE_URE2 network devices. SPP RE_URE2 created a procedure documenting its ports and services and provided evidence that the required ports and services were documented in the vulnerability assessments conducted. | 2010-09-17 | 2011-04-01 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000346 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-005-1 R3 and R3.2. SPP RE_URE2 reported that its policies and procedures lacked specific detail on electronic or manual processes for monitoring and logging access at access points to the Electronic Security Perimeter (ESP) in accordance with R3. Specifically, SPP RE_URE2 failed to identify the order of firewall logging; corporate firewalls log first while Energy Management System (EMS) firewalls log second. SPP RE_URE2 also failed to record or review its firewall access logs. Finally, SPP RE_URE2 failed to document the process to be followed by its IT department in response to a user being locked out of a firewall. | CIP-005-1 | R3; R3.2 | Medium | High | SPP RE determined that SPP RE_URE2's violation of CIP-005-1 R3 and R3.2 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE2 had security measures in place to protect its network against unauthorized access. To provide redundant authentication mechanisms, user and administrator access to the SPP RE_URE2 EMS required two factor authentication through both the workstation and then to the EMS application. To limit administrative configuration access to the network, SPP RE_URE2 limited authorized IT administrator access to three personnel. In addition, it required an additional layer of authentication to achieve full enable level access on its network devices, and utilized an encryption protocol for device communication. SPP RE_URE2 was utilizing a server to support overall network security within the ESP. This particular server analyzes event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress. Prior to automated alerting being achieved, SPP RE_URE2 was conducting manual reviews of the server logs. Finally, while the logging and review process was not documented during the violation period, no reportable cyber security events occurred. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 documented and implemented a procedure for the monitoring and logging of all access points to its ESP twenty-four hours a day using a server appliance. Successful/unsuccessful access attempts are captured. Data including, but not limited to: date, time, user ID, device ID and IP address for each access attempt is retained. Logs are collected into a centralized event server and are actively monitored by another server. This other server sends an alert on suspicious activity and also monitors specific ports for unauthorized addresses. Active alerts are reviewed by SPP RE_URE2 personnel. Any identified security incident will be logged into SPP RE_URE2’s ticket tracking system for further investigation. Additionally, SPP RE_URE2 IT personnel have procedures to check access logs each morning, Monday through Friday (excluding holidays). Finally, SPP RE_URE2 updated its processes to provide a process for user recovery of locked accounts following five failed authentication attempts. | 2010-08-31 | 2011-03-21 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000348 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-005-1 R5 and R5.1. SPP RE_URE2 stated that it did not have documentation to reflect current access point and Cyber Asset configurations, and its processes for access and logging were not sufficiently documented. Additionally, because it did not have all the required documentation, SPP RE_URE2 had not reviewed the documents and procedures referenced in Standard CIP-005 at least annually, as required by the Standard. | CIP-005-1 | R5; R5.1 | Lower | High | SPP RE determined that SPP RE_URE2's violation of CIP-005-1 R5 and R5.1 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because while SPP RE_URE2 had not documented its ports and services in its CIP-005 procedure, SPP RE determined that SPP RE_URE2 did have current and historical documentation of its access points to the Electronic Security Perimeter (ESP) and their configuration. This documentation was contained in two vulnerability assessment reports conducted by its Energy Management System (EMS) vendor. Additionally, the EMS vendor’s two ESP access point reviews served as a review of the SPP RE_URE2 access point configurations. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 EMS and IT staff have reviewed previously existing documents and either created new documents or modified its previously existing documents to provide details on SPP RE_URE2 Cyber Assets and their configurations as well as supporting processes and procedures to ensure compliance with the CIP-005-1 R5. SPP RE_URE2 developed a process to maintain ESP documentation and provided a revised topology map of the ESP identifying all access points to the ESP. Additionally, SPP RE_URE2 developed a process for monitoring and logging access at all access points to the ESP twenty-four hours a day and included evidence of logging processes (in the form of a checklist identified in the monitoring procedure), sample access logs for access control devices at the ESP, and evidence of log reviews. SPP RE_URE2 also provided a screen shot of its newly implemented warning banner. Additionally, SPP RE_URE2 updated its account management procedure for access control, authentication and accountability. Finally, SPP RE_URE2 documented its authorization rights and created a list of access rights mapped to user groups segregated by servers and workstations. | 2011-08-05 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000349 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R1.3. SPP RE_URE2 reported that when changes were made on EMS application servers, performance testing was conducted on non-critical systems using a network security scanner application. At the time of its Self-Report, SPP RE_URE2 indicated that it was utilizing this application to perform security scans of offline workstations and EMS servers in both pre- and post-installation timeframes. Following installation, the application compares the post installation scan to the pre-installation base line scan to determine if any security issues exist. While SPP RE_URE2 was performing the required security scans at the time of its Self-Report, it indicated that it had failed to adequately document and preserve its historical application scans (security test results). | CIP-007-1 | R1.3 | Lower | Lower | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R1.3 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because SPP RE_URE2 was performing security testing using a network security and vulnerability scanner on Critical Cyber Assets (servers and workstations) within the Electronic Security Perimeter (ESP) after a software/hardware upgrade. Although SPP RE_URE2 failed to save the application monitoring results as evidence of testing, SPP RE_URE2 indicated that it was utilizing the application to perform checks for current security patches, and as of SPP RE_URE2’s earlier vulnerability assessment, all systems within the ESP had current update patches installed. Moreover, SPP RE_URE2 was utilizing a server to analyze event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 was conducting manual reviews of the server logs. There were also no reportable cyber security events during the violation period. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 configured its network security scanner application to be able to collect and maintain complete system test results on all Cyber Assets (CAs) within the ESP. The information collected is broader than the CIP-007 R1 Standard. SPP RE_URE2 demonstrated that it has the ability to comply with CIP-007 R1 by submitting a sample of the test report for a Critical Asset used in the access control and monitoring of the ESP, a Critical Asset used in the access control and monitoring of the Physical Security Perimeter, and a Critical Cyber Asset within the ESP. An application report will be run on Critical Assets affected by changes or upgrades for purposes of satisfying CIP-007 R1 as part of the change control procedure. | 2011-01-01 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000352 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R4. SPP RE_URE2 reported that it did not have documentation outlining which assets did not have anti-virus software installed and did not monitor the anti-virus management console for virus alerts. Additionally, SPP RE_URE2 was not performing any testing of anti-virus signature files prior to rolling them out onto critical systems within the production environment. SPP RE also discovered that SPP RE_URE2 failed to have anti-virus installed on its Energy Management System (EMS) servers by the Standard's compliance enforcement date. | CIP-007-1 | R4; R4.1; R4.2 | Medium | Lower | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R4.1 and R4.2 posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because, notwithstanding SPP RE_URE2’s failure to test anti-virus signatures prior to updating critical systems, the signatures were being pushed to the production system on a regular basis and updated. Additionally, while the failure to install anti-virus software on the EMS servers presents a vulnerability into the EMS environment, the servers' previous operating system was replaced with another operating system and anti-virus software was installed. Further, SPP RE_URE2 was utilizing a server with automated alerting. The server analyzes event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Finally, for the duration of the violation, no cyber events occurred on its EMS systems. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 documented and implemented a process for distribution of anti-virus signatures to Critical Assets within the ESP. The anti-virus platform is now configured to distribute anti-virus signatures to a small subset of non-critical computers within the EMS environment for testing prior to deploying updates to critical production systems, similar to the patch management process. Once it has been verified and documented that no issues have been introduced, the signature files are then deployed to the remaining systems. These steps are then documented within the existing logs. SPP RE_URE2 also configured the anti-virus platform to automatically alert EMS engineers for anti-virus events. Further, SPP RE_URE2 replaced its servers' operating system with another operating system, and anti-virus software was installed. SPP RE_URE2 also created a document containing a list of Critical Cyber Assets which do not have anti-virus installed and an explanation of why an anti-virus solution could not be implemented. The devices addressed include printers and network devices. SPP RE_URE2 requested a Technical Feasibility Exception on the remaining devices without anti-virus installation. | 2011-04-06 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000353 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R5. Specifically, SPP RE_URE2 had not performed an in-depth review of the user accounts with access to its Energy Management System (EMS) application. Further, SPP RE_URE2 had not enforced passwords that met the CIP-005-1 R5.3 password requirements. | CIP-007-1 | R5; R5.1.3; R5.3 | Medium | Severe | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R5.1.3 and R5.3 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because user access to the EMS application at the time of the violation was a three-step process that began with Physical Security Perimeter authentication, followed by EMS corporate workstation authentication, and finally EMS application authentication. While EMS application passwords were identified as having failed to meet the requirements of CIP-007-1 R5.3, the reliability risk to the BPS was low because redundant authentication procedures were in place for access from the EMS workstation through the ESP to servers hosting EMS applications as stated above. Additionally, user access was limited to read-only access. Further, a redundant application, a server was in place to monitor for “system events” on the local area networks within the ESP. This application monitored event logs to ensure that systems and devices were functioning within defined parameters. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Such redundant network monitoring serves to detect changes made to the network configurations via unauthorized access. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 developed a comprehensive account management process and form to record the user account review. SPP RE_URE2 EMS employees performed a thorough review of EMS user accounts. This review is now performed at least annually as prescribed in the account management process. Additionally, SPP RE_URE2 EMS employees were trained in CIP password requirements and SPP RE_URE2 strengthened its EMS application passwords to meet the CIP-005-1 R5.3 Standard. | 2010-08-24 | 2011-03-21 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000354 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-007-1 R6. Specifically, SPP RE_URE2 failed to implement a process for monitoring security events on all Critical Assets (CAs) within its ESP as required by R6.1. Additionally, although four Energy Management System (EMS) servers located within its ESP were configured to log all events, SPP RE_URE2 did not have security monitoring controls in place for automated or manual alerts for detected Cyber Security Incidents as required by R6.2. Moreover, the logs were not reviewed on a regular basis as required by R6.5. | CIP-007-1 | R6; R6.1; R6.2; R6.5 | Medium | Lower | SPP RE determined that SPP RE_URE2's violation of CIP-007-1 R6.1, R6.2 and R6.5 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because SPP RE_URE2 had been logging all events relating to its CA servers within the ESP, and such logs were periodically being reviewed but not on a consistent basis. All CA servers and workstations are located within SPP RE_URE2’s Physical Security Perimeter and are accessible only by personnel with authorized card access privileges. Additionally, SPP RE_URE2 was utilizing a server to monitor its network. The server analyzes event logs collected from network devices within the ESP to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Moreover, no reportable Cyber Security Incidents occurred during the violation period. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | SPP RE_URE2 implemented and documented a process to monitor for cyber security events on CAs within the ESP. The process utilizes an event log monitoring, management and archiving application to correlate and alert on events from its particular operating system. Network devices are monitored through a server. Alerts from these CAs are reviewed daily by SPP RE_URE2 personnel. | 2010-08-27 | 2011-03-21 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000441 | Settlement Agreement | SPP RE_URE2 self-reported a violation of CIP-003-1 R3. Specifically, SPP RE_URE2 was unable to institute security monitoring controls capable of issuing automated alerts for detected Cyber Security Incidents as required by SPP RE_URE2’s cyber security policy until 71 days after the Standard became mandatory and enforceable. This instance should have been identified as an exception to SPP RE_URE2’s cyber security policy, and authorized by the senior manager. | CIP-003-1 | R3 | Lower | Severe | SPP RE determined that SPP RE_URE2's violation of CIP-003-1 R3 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because when the violation was mitigated, SPP RE_URE2 began utilizing a server to meet the requirement of its cyber security policy. The server analyzes event logs collected from network devices within the Electronic Security Perimeter (ESP) to determine if a cyber attack has occurred or is in progress and provides automated alerts to system administrators. Prior to automated alerting being achieved, SPP RE_URE2 conducted manual reviews of the server logs. Additionally, SPP RE_URE2 attested that there have been no reportable Cyber Security Incidents during the violation period. | date Standard became mandatory and enforceable | date Mitigation Plan was completed | $12,000 (for violations SPP201000345, SPP201000346, SPP201000348, SPP201000349, SPP201000352, SPP201000353, SPP201000354, and SPP201000441) | Self-Report | Since the installed software/hardware used to monitor SPP RE_URE2’s Critical Assets within its ESP was incapable of issuing automated alerts for detected Cyber Security Incidents as intended, until the feasibility of the automation could be completed, SPP RE_URE2 revised its cyber security policy to require manual security monitoring. At that time, SPP RE_URE2 began monitoring logs for security incidents. SPP RE_URE2 began installing updates to its security monitoring controls. SPP RE_URE2 successfully tested its security monitoring controls and began receiving automated alerts for security events. | 2009-09-10 | 2011-12-05 | Neither Admits nor Denies | SPP RE considered SPP RE_URE2's compliance history.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002076 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating its semi-annual CIP self-certification process. WECC_URE1 self-reported a violation of CIP-006-1 R3 and a couple days later submitted its self-certification for CIP-006-1 R3. WECC_URE1 failed to implement controls to monitor access at access points to a single Physical Security Perimeter (PSP). WECC_URE1 was required by the Standard to implement technical controls to monitor access at all PSP access points. Although access points to the PSP were equipped with card readers, the existing card access system did not provide 24/7 monitoring consistent with CIP-006-1 R3. Further, the card access system did not trigger an alarm in the event of unauthorized access to the PSP. WECC determined that WECC_URE1 was in violation of the Standard for failing to implement technical controls monitoring access at PSP. Specifically, the existing controls did not provide for 24/7 access monitoring and alarming. | CIP-006-1 | R3 | Medium | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because the PSP was afforded, during the violation period, a significant degree of layer security and monitoring. WECC determined access to the PSP required entry through a separate access point that did have 24/7 monitoring. In addition, WECC_URE1 did have a card access system in place that provided monitoring through a shared system on a limited basis and without alarming. | when WECC_URE1 was required to comply with the Standard | date Mitigation Plan was completed | $8,000 (for WECC201002076 and WECC201002138) | Self-Certification | WECC_URE1 submitted a Revised Mitigation Plan outlining the following mitigating actions: 1. Switched card access system from shared system to a standalone system, which provided 24/7 monitoring and unauthorized access alarming capability; 2. The new card access system was secured within the PSP; and 3. Control and Monitoring of the card access system assigned to the Critical Asset for full operability. | 2010-06-29 | 2010-10-13 | Agrees/ Stipulates | Although WECC_URE1 self-reported the CIP-006-1 violation during a self-certification period, WECC applied mitigating credit based on WECC_URE1's attempts to disclose noncompliance prior to when WECC_URE1 was required to comply with the Standard. WECC applied mitigating credit based on evidence of WECC_URE1's attempts to self-disclose the violation prior to receiving notice to self-certify.
2012-03-30 | FERC | NP12-22-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002138 | Settlement Agreement | WECC_URE1 self-reported a violation of PRC-023-1 R2. WECC_URE1 failed to obtain agreements from its Planning Coordinator (PC), Transmission Operator (TOP) and Reliability Coordinator (RC), in which parties agree to use the calculated circuit capability as the Facility Rating of the circuit. This violation affected four of WECC_URE1's facilities. While WECC_URE1 did apply the R1.6 criteria to calculate circuit capability with respect to three facilities and the R.1.13 criteria for the fourth facility, WECC_URE1 did not obtain the required agreements with its PC, TOP and RC. In addition, although WECC_URE1 did submit the necessary requests to secure such agreements it had not reached an agreement with any of the other parties. WECC determined that although WECC_URE1 did apply circuit capabilities prescribed under PRC-023-1 R2, WECC_URE1 failed to execute agreements with its PC, TOP and RC pursuant to R2. | PRC-023-1 | R2 | Medium | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because, although the WECC_URE1 failed to ensure that protective relay settings do not limit transmission loadability and do not interfere with system operators' ability to protect the BPS and failed to secure the necessary agreements from its PC, TOPs, and RC, the Facility Ratings used by all parties were calculated using criteria in accordance with PRC-023-1 R1. | when Standard became mandatory and enforceable | date Mitigation Plan was completed | $8,000 (for WECC201002076 and WECC201002138) | Self-Report | WECC_URE1 identified all parties with which it was required to execute an agreement and entered into agreements with the appropriate entities. | 2011-07-19 | 2011-12-22 | Agrees/ Stipulates | WECC considered that WECC_URE1 submitted a Self-Report for this violation and that WECC_URE1 did not have any repeat violations of this Standard or any relevant negative compliance history.
2012-03-30 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000306 | Settlement Agreement | FRCC_URE1 determined that a total of 109 changes made to Critical Cyber Assets (CCA) were not controlled or documented properly according to the entity's change control and configuration management process, as required by CIP-003-1 R6. FRCC_URE1 determined that 17 package changes, 83 display changes, 8 code changes and 1 configuration (.rc) file change were not documented due to ineffective implementation and failure to adhere to FRCC_URE1's practice. This violation was self-reported by FRCC_URE1. | CIP-003-1 | R6 | Lower | High | FRCC determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because changes to FRCC_URE1's CCAs were tracked using brief change logs, but no formal documentation was maintained. Out of 109 changes that were not formally tracked during the violation period, most of the changes were day to day routine configuration and update changes. | The date of first change | The completion of MP | $10,000 (for FRCC201000306, FRCC201000307 and FRCC201000362) | Self-Report | FRCC_URE1 has reviewed and revised its change control practice to ensure that all changes are accompanied with change control/request forms and processes. These processes include an evaluation of new applications to determine whether codes and revisions are stored; peer review is conducted for all the changes including file changes to the Supervisory Data and Acquisition (SCADA) system. All changes were implemented using a newly designed service request form and evaluation of existing security controls for any adverse effect as a result of change. Additionally, FRCC_URE1 provided training to affected employees in the revised change control practice and service request forms. | 2010-05-04 | 2011-08-12 | Neither Admits nor Denies | FRCC_URE1's has a Internal Compliance Program (ICP) that was reviewed and included as a mitigating factor.
2012-03-30 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000307 | Settlement Agreement | During the Spot Check it was discovered that FRCC_URE1 was unable to demonstrate having test procedures for all significant changes to 2 Cyber Assets within the Electronic Security Perimeter (ESP) that minimized adverse effects to the cyber security controls, as required by CIP-007-1 R1. The entity's evidence did not demonstrate that the router test procedure addressed ESP configuration controls, ports and services to maintain the ESP integrity, lockout or change of password for default user access, user access controls, review of physical security for access control, review of banners, or review of modems access for the ESP. Similarly, the testing process for application changes did not address adverse effects to existing security controls. Further, the entity did not document test results as per the entity's own test procedure. | CIP-007-1 | R1/ R1.1; R1.2; R1.3 | Medium | Lower | FRCC determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because during the workstation and router configuration updates the entity used its Supervisory Control and Data Acquisition (SCADA) vendor's approved configurations and performed operational testing only. The application changes (Wave file recorder) for which CIP-007 R1 testing was found deficient are widely used within the control center environment but did not add any new ports and services. Furthermore, the changes were from trusted control system vendors. | The date of first change with limited testing | The completion of MP | $10,000 (for FRCC201000306, FRCC201000307 and FRCC201000362) | Spot Check | As a part of FRCC_URE1's mitigating activity, FRCC_URE1 re-designed checklists and controls on third-party testing and service request forms of various types. FRCC_URE1 also produced revised testing guidelines for the tests identified as incomplete and corrected any deficiencies. Training was given to all affected personnel including those who implement these changes. Testing was performed to ensure that no additional ports or services were opened as a result of the installation of the “Power Play” software. A command line tool, was used to show all open and listening ports on the client. Ports were translated to processes which were further defined via a task list. As a result of the testing, all ports and services were determined to be legitimate. All findings were documented on a testing worksheet. For the router, security was configured on the router; a port scan performed against the router confirmed that only the required open ports and services were available. All findings and test results were documented on a testing worksheet. | 2010-07-15 | 2011-08-12 | Neither Admits nor Denies | FRCC_URE1's has a Internal Compliance Program (ICP) that was reviewed and included as a mitigating factor.
2012-03-30 | FERC | NP12-18-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000362 | Settlement Agreement | Four of FRCC_URE1's switches contained within the entity's ESP were not configured for automatic logging of system events as required by CIP-007-1 R6. The configuration had been set to the original EMS vendor specifications as delivered. This was self reported by FRCC_URE1. | CIP-007-1 | R6/ R6.1; R6.3; R6.4 | Medium | Lower | FRCC determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The lack of logging limits the capability of the environment to monitor for possible Cyber Security Incidents and allows for exploitation. While these switches used redundant configurations, they lacked logging which could allow an unauthorized person the opportunity to gain access without detection. The likelihood of these occurrences was reduced substantially because of the switches being located in a secure ESP. | The date Standard became enforceable for FRCC_URE1 | When FRCC_URE1 configured Syslog on the switches; review logs and add to scheduled reporting | $10,000 (for FRCC201000306, FRCC201000307 and FRCC201000362) | Self-Report | FRCC_URE1 corrected the logging configuration to enable logging of the system events for the concerned switches. FRCC_URE1 also updated hardware and software testing forms to address logging and training of all affected staff responsible for installation of networking devices. Additionally, FRCC_URE1 hired an EMS Administrator to update and revise existing practices and guidelines. | 2010-05-21 | 2011-08-12 | Neither Admits nor Denies | FRCC_URE1's has a Internal Compliance Program (ICP) that was reviewed and included as a mitigating factor.
2012-03-30 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100249 | Settlement Agreement | NPCC_URE1 self-reported a violation of CIP-004-2 R3. NPCC determined that NPCC_URE1 failed to conduct a personnel risk assessment (PRA) for one of its employees. Specifically, a NPCC_URE1 employee was granted authorized unescorted physical access to Critical Cyber Assets (CCAs) at a power station, prior to having a PRA conducted. The mistake was discovered approximately six months later during an internal review of PRA documentation. The manager responsible for granting access had requested a PRA for the employee three months before the required access date but did not confirm that the PRA was completed when access was granted. | CIP-004-2 | R3 | Medium | High | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because this involved a single employee. Further, this employee did not access the CCA Physical Security Perimeter during the period of time the PRA was not performed. Also, this employee is required to have government-approved credentials to work at this location and this was completed two years prior to the violation. This check verified his identity, looked at criminal history records, terrorist watch lists and immigration databases. | When the NPCC_URE1 employee at issue was granted access to CCAs | When the PRA was completed | 3800 | Self-Report | NPCC_URE1 submitted to NPCC a Mitigation Plan to address the violation of CIP-004-2 R3. In accordance with the Mitigation Plan, NPCC_URE1: (1) completed a PRA for the affected employee; (2) revised the form for approving personnel physical access to CCAs to include the source of the PRA date listed on the form. This change makes the approving manager responsible for confirming that a PRA was in fact completed and logged in the system rather than assuming, in the absence of a report to the contrary, that the PRA was completed before the manager submits the access approval form; (3) conducted critical infrastructure protection awareness training; (4) discussed the incident with the employee directly responsible for granting the access and reinforced the need for compliance. | 2010-11-30 | 2011-08-10 | Does Not Contest | NPCC viewed the compliance program, in effect at the time of the violation, to be a mitigating factor in the penalty determination. NPCC took into consideration NPCC_URE1's violation history.
2012-03-30 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC201000190 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-007-1 R2.1. NPCC_URE2 discovered, during an internal assessment, that all of the ports and services required for normal and emergency operations were not properly documented for a subset of servers and workstations associated with the Energy Management System (EMS). The internal assessment determined that select devices within the Electronic Security Perimeter (ESP) lacked adequate documentation of ports and services. These devices are initially configured to a corporate standard configuration. After initial configuration, additional applications are installed depending upon the function to be performed by the device. Documentation of the initial standard corporate configurations were controlled and documented, but this documentation did not include ports and services information. | CIP-007-1 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because access to the ESP is controlled by a combination of firewall rules and router access control lists. Device cyber access is monitored by an intrusion detection system. Cyber access to the devices is limited to a small number of authorized personnel. Access to the public internet is not possible from inside the ESP. CCA devices are contained within a Physical Security Perimeter which has limited access by authorized personnel. In addition, there were no incidents at NPCC_URE2 related to the lack of proper documentation of the normal and emergency ports and services. | Date the Standard became mandatory and enforceable for the entity | Mitigation Plan Completion | $5,000 (for NPCC201000190 and NPCC201000191) | Self-Report | NPCC_URE2 submitted a Mitigation Plan with the following mitigation activities: 1. Existing configurations of active services and open ports, including those of devices affected by the violation, for each identified Critical Cyber Asset (CCA) were documented; 2. Subject matter experts reviewed and documented the configuration of the standard corporate client and server images on all CCAs to identify required ports and services; 3. Based on the current year's vulnerability assessment results, updates were made to appropriate documentation associated with all applicable CCAs; 4. The standard client and server configurations per the Mitigation Plan were supplemented with services required for specific asset types to create device specific ports and services configurations; 5. Device configurations were modified to conform with the device specific documentation developed per the Mitigation Plan; and 6. A procedure was created for the documentation of ports and services. | 2011-03-01 | 2011-04-19 | Neither Admits nor Denies | NPCC considered certain aspects of NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty.
2012-02-29 | FERC | NP12-18-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC201000191 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-005-1 R2.2. NPCC_URE2 discovered during an internal assessment that certain baseline ports and services associated with the primary control center firewall had incomplete configuration documentation. NPCC_URE2's assessment of firewall ports determined that a firewall selected for inspection did not have proper documentation of enabled ports. Upon discovery of this violation, NPCC_URE2 reviewed all documentation of ports and services on the rest of its control center firewalls. NPCC_URE2 discovered that the other firewalls had the same documentation issues as the firewall reported in the Self-Report; however, these issues were also resolved through mitigation activities for this violation. | CIP-005-1 | R2; R2.2 | Medium | Moderate | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the BPS because NPCC_URE2 had Critical Cyber Asset account management controls, an intrusion detection system and access log review protocols. Access to the NPCC_URE2 Energy Management System (EMS) network is not allowed from the public internet, nor can devices within the EMS and Electronic Security Perimeter reach the public internet directly as the EMS network space utilizes non-routable private addresses to further enhance protection of the environment. In addition, there were no incidents at NPCC_URE2 related to the lack of proper configuration documentation of the primary control center firewall. | Date the Standard became mandatory and enforceable for the entity | Mitigation Plan Completion | $5,000 (for NPCC201000190 and NPCC201000191) | Self-Report | NPCC_URE2 submitted a Mitigation Plan with the following mitigation activities: 1. Port and service documentation for all checkpoint firewalls, including the affected firewall, was reviewed and updated as necessary; 2. Based on the current year's vulnerability assessment results, updates were made to the appropriate documentation associated with all ESP access devices; 3. The access point device configurations were updated as appropriate; and 4. A procedure was created for the documentation of ports and services. | 2011-03-01 | 2011-04-19 | Neither Admits nor Denies | NPCC considered certain aspects of NPCC_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in determining the penalty.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100830 | Settlement Agreement | RFC_URE1 submitted Self-Reports identifying violations of CIP-004-1 R2.1, R2.3; R3.1, R3.3; R4.1, and R4.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-004 compliance program in all cases. RFC_URE1 discovered that in many instances, employees and contractors had access to Critical Cyber Assets (CCAs) without first receiving either cyber security training or personnel risk assessments (PRAs), and while RFC_URE1 did have lists of personnel with authorized cyber access, it failed to accurately maintain these lists. Many tenured employees and contractors who had access to CCAs prior to the implementation of RFC_URE1's CIP compliance program and the CIP Standards retained their access to those CCAs, despite the fact that they did not receive PRAs or cyber security training. In total, more than 56% of employees and contractors were affected at least in part by the oversight. Specifically, 95.6% of employees and contractors did not receive training,38.8% of employees and contractors did not receive criminal background checks, and 92.8% of employees and contractors did not receive identity verifications. RFC_URE1 determined that the cause of the oversight was human error by those responsible for maintaining the lists of personnel with authorized access to CCAs and ensuring that all personnel met the CIP-004-1 requirements prior to the mandatory compliance date. RF determined that RFC_URE1 violated CIP-004-1 R2 by failing to implement its annual cyber security training program for all personnel having authorized cyber or authorized unescorted physical access to CCAs. | CIP-004-1 | R2/ R2.1; R2.3 | Medium, Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, RF determined that this violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that the affected personnel were long-term employees or contractors who had received background checks and/or other verifications at the commencement of their employment. Additionally, RFC_URE1 confirmed that no individuals who had access to its facilities had any issues of concern identified via personnel risk assessments, upon their eventual completion. The average service tenure of the affected personnel is greater than 21 years of service. All individuals have been brought into compliance. Although the required training for some individuals occurred after the effective date of the Standard, all affected personnel were experienced in the proper treatment of CCAs through either formal training or on-the-job informal training. For example, RFC_URE1's training department taught a course on RFC_URE1's emergency plan to all relevant employees, a course on substation entry to all relevant employees and a course on job briefings to all relevant employees. Additionally, RFC_URE1 provided training to its relevant employees on laptop security, substation network access, and the proper handling of CCA information. Other formal departmental training included refresher training on a number of departmental procedures related to compliance with many applicable Reliability Standards, as well as refresher training on the proper use of RFC_URE1's technology relating to full compliance. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 corrected its CCA access list and completed all deficient cyber security training and personal risk assessments | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | RFC_URE1 reviewed and corrected its CCA access list to remove the employees and contractors who no longer required access to CCAs. In order to ensure future compliance, RFC_URE1 will take several steps to improve its processes, including re-training employees on the CIP Standards and their implementation; instituting a two-person verification requirement to modify the access list; increasing communications between corporate security and information technology; and improving the access list maintenance and documentation process, including alerts and a central repository for documentation. RFC_URE1 is also consulting with two outside independent auditors to determine best practices for CIP compliance and identify process improvements | 2011-12-31 | 2012-02-20 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100831 | Settlement Agreement | RFC_URE1 submitted Self-Reports identifying violations of CIP-004-1 R2.1, R2.3; R3.1, R3.3; R4.1, and R4.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-004 compliance program in all cases. RFC_URE1 discovered that in many instances, employees and contractors had access to Critical Cyber Assets (CCAs) without first receiving either cyber security training or personnel risk assessments (PRAs) because RFC_URE1 failed to accurately maintain its lists of personnel with authorized cyber access. Many tenured employees and contractors who had access to CCAs prior to the implementation of RFC_URE1's CIP compliance program and the CIP Standards retained their access to those CCAs, despite the fact that they did not receive PRAs or cyber security training. In total, more than 56% of employees and contractors were affected at least in part by the oversight. Specifically, 95.6% of employees and contractors did not receive training, 38.8% of employees and contractors did not receive criminal background checks, and 92.8% of employees and contractors did not receive identity verifications. RFC_URE1 determined that the cause of the oversight was human error by those responsible for maintaining the lists of personnel with authorized access to CCAs and ensuring that all personnel met the CIP-004-1 requirements prior to the mandatory compliance date. RF determined that RFC_URE1 violated CIP-004-1 R3 by failing to conduct PRAs for all personnel having authorized cyber or authorized unescorted physical access to CCAs. | CIP-004-1 | R3/ R3.1; R3.3 | Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, RF determined that this violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that the affected personnel were long-term employees or contractors who had received background checks and/or other verifications at the commencement of their employment. Additionally, RFC_URE1 confirmed that no individuals who had access to its facilities had any issues of concern identified via personnel risk assessments, upon their eventual completion. The average service tenure of the affected personnel is greater than 21 years of service. All individuals have been bought into compliance. Although the required training for some individuals occurred after the effective date of the Standard, all affected personnel were experienced in the proper treatment of CCAs through either formal training or on-the-job informal training. For example, RFC_URE1's training department taught a course on RFC_URE1's emergency plan to all relevant employees, a course on substation entry to all relevant employees and a course on job briefings to all relevant employees. Additionally, RFC_URE1 provided training to its relevant employees on laptop security, substation network access, and the proper handling of CCA information. Other formal departmental training included refresher training on a number of departmental procedures related to compliance with many applicable Reliability Standards, as well as refresher training on the proper use of RFC_URE1's technology relating to full compliance. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 corrected its CCA access list and completed all deficient cyber security training and personal risk assessments | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | RFC_URE1 reviewed and corrected its CCA access list to remove the employees and contractors who no longer required access to CCAs. In order to ensure future compliance, RFC_URE1 will take several steps to improve its processes, including re-training employees on the CIP Standards and their implementation; instituting a two-person verification requirement to modify the access list; increasing communications between corporate security and information technology; and improving the access list maintenance and documentation process, including alerts and a central repository for documentation. RFC_URE1 is also consulting with two outside auditors to determine best practices for CIP compliance and identify process improvements | 2011-12-31 | 2012-02-20 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100832 | Settlement Agreement | RFC_URE1 submitted Self-Reports identifying violations of CIP-004-1 R2.1, R2.3; R3.1, R3.3; R4.1, and R4.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-004 compliance program in all cases. RFC_URE1 discovered that in many instances, employees and contractors had access to Critical Cyber Assets (CCAs) without first receiving either cyber security training or personnel risk assessments (PRAs) because RFC_URE1 failed to accurately maintain its lists of personnel with authorized cyber access. Many tenured employees and contractors who had access to CCAs prior to the implementation of RFC_URE1's CIP compliance program and the CIP Standards retained their access to those CCAs, despite the fact that they did not receive PRAs or cyber security training. In total, more than 56% of employees and contractors were affected at least in part by the oversight. Specifically, 95.6% of employees and contractors did not receive training, 35.8% of employees and contractors did not receive criminal background checks, and 92.8% of employees and contractors did not receive identity verifications. RFC_URE1 determined that the cause of the oversight was human error by those responsible for maintaining the lists of personnel with authorized access to CCAs and ensuring that all personnel met the CIP-004-1 requirements prior to the mandatory compliance date. RF determined that RFC_URE1 violated CIP-004-1 R4 by failing to maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to CCAs | CIP-004-1 | R4/ R4.1; R4.2 | Lower, Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, RF determined that this violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that the affected personnel were long-term employees or contractors who had received background checks and/or other verifications at the commencement of their employment. Additionally, RFC_URE1 confirmed that no individuals who had access to its facilities had any issues of concern identified via personnel risk assessments, upon their eventual completion. The average service tenure of the affected personnel is greater than 21 years of service. All individuals have been bought into compliance. Although the required training for some individuals occurred after the effective date of the Standard, all affected personnel were experienced in the proper treatment of CCAs through either formal training or on-the-job informal training. For example, RFC_URE1's training department taught a course on RFC_URE1's emergency plan to all relevant employees, a course on substation entry to all relevant employees and a course on job briefings to all relevant employees. Additionally, RFC_URE1 provided training to its relevant employees on laptop security, substation network access, and the proper handling of CCA information. Other formal departmental training included refresher training on a number of departmental procedures related to compliance with many applicable Reliability Standards, as well as refresher training on the proper use of RFC_URE1's technology relating to full compliance. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 corrected its CCA access list and completed all deficient cyber security training and personal risk assessments | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | RFC_URE1 reviewed and corrected its CCA access list to remove the employees and contractors who no longer required access to CCAs. In order to ensure future compliance, RFC_URE1 will take several steps to improve its processes, including re-training employees on the CIP Standards and their implementation; instituting a two-person verification requirement to modify the access list; increasing communications between corporate security and information technology; and improving the access list maintenance and documentation process, including alerts and a central repository for documentation. RFC_URE1 is also consulting with two independent outside auditors to determine best practices for CIP compliance and identify process improvements | 2011-12-31 | 2012-02-20 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100833 | Settlement Agreement | RFC_URE1 submitted a Self-Report identifying a violation of CIP-006-3c R1.6. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-006 compliance program in all cases. RFC_URE1 failed to maintain visitor logs to document the entry and exit of visitors at its Physical Security Perimeters (PSPs), as required by CIP-006- 3c R1.6; however, RFC_URE1 did maintain company policies related to visitor control and observation, and did maintain electronic logs of the entry and exit of authorized personnel at its facilities. RF determined that RFC_URE1 violated CIP-006-3c R1.6 by failing to implement a visitor control program for visitors (personnel without authorized unescorted access to a PSP) in its physical security plan. | CIP-006-3c | R1/ R1.6 | Medium | Severe | In light of the nature of the violations, offset by the mitigating factors, RF determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). For the violation of CIP-006-3c R1, the risk to the BPS was mitigated by the fact that, while RFC_URE1 did not implement CIP-006-1 visitor logs at all PSPs, RFC_URE1 trained its employees and contractors in visitor control and monitoring within PSP boundaries, and the visitors posed no actual security risk during the duration of the violation, as there was always an escort present. At no time were unauthorized visitors allowed to access its PSPs without an authorized escort present. | The effective date of Standard | When RFC_URE1 completed mitigating actions | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | The visitor log issue has been corrected. Upon discovery of this issue, RFC_URE1 immediately instituted a new process, whereby escorts at each Critical Area must call a central guard desk, with specific identifying information for all escorts and visitors to Critical Cyber Assets, including the name and company of the visitor, and the purpose of the visit; these visitors are logged going in and out of these facilities, including date and time, and all of the information is maintained in a log at the central guard facility. While it is maintained manually at this point, it is RFC_URE1's intent to develop and implement electronic logging of all visitors. In furtherance of this new process, signs reminding all personnel of this process and its requirements were posted at each Critical Area. Additionally, RFC_URE1 provided a company-wide communication detailing this new process via conference call and email, which included a reminder on visitor escort responsibilities. With respect to all of these issues of non-compliance under CIP-006, the RFC_URE1 is taking several additional measures to strengthen its program and to ensure that such an occurrence does not happen in the future, including: (1) the Compliance Department has had discussions with the individuals currently responsible for these duties and has reviewed the regulations with such individuals to ensure that the requirements are understood and met; (2) RFC_URE1 has created a new managerial level position that handles these particular CIP standards to assure that adequate resources are allocated to these CIP standards, and the individual previously responsible for compliance with this standard has been relieved of those responsibilities and is no longer with the Company; and finally, (3) RFC_URE1 will provide additional training with respect to CIP-006. | 2011-12-31 | 2012-02-13 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100834 | Settlement Agreement | RFC_URE1 submitted a Self-Report identifying a violation of CIP-006-1 R2.2. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-006 compliance program in all cases. RFC_URE1 failed to afford all of the protective measures specified in CIP-006-1 R2.2 to two personal computers that had the capability to control access to Physical Security Perimeters (PSPs). Until the time it submitted the Self-Report, RFC_URE1 incorrectly believed that the personal computers did not have capability to control access to PSPs, and as a result, RFC_URE1 did not provide the protective measures specified in ClP-005 R2 and R3 and ClP-007 to those personal computers. RF determined that RFC_URE1 violated ClP-006-1 R2.2 by failing to afford the protective measures specified in ClP-003, CIP-004 R3, ClP-005 R2 and R3, ClP-006 R4 and R5; ClP-007, ClP-008, and CIP-009 to two cyber assets that authorize access to the PSP. | CIP-006-1 | R2/ R2.2 | Medium | Severe | In light of the nature of the violations, offset by the mitigating factors, RF determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). For the violation of CIP-006-1 R2.2, the risk to the BPS was mitigated by the fact that the two computers at issue were both located within secure PSPs, preventing unauthorized physical access. The two computers were also on secure network segments, which provided additional protections against cyber vulnerabilities. Additionally, one of the two computers resided in the main guard facility, which RFC_URE1 staffs and monitors 24 hours per day. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 completed mitigating actions | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | With respect to the two computers that had physical access control functionality which were not adequately electronically protected under CIP-006 R2.2, this issue was an isolated incident. That said, it was immediately remedied, and the computers were afforded all required electronic protections. A complete review of the operating capabilities of the system hardware components has been performed, and RFC_URE1 has verified there are no other unidentified physical access control devices. With respect to all of these issues of non-compliance under CIP-006, RFC_URE1 is taking several additional measures to strengthen its program and to ensure that such an occurrence does not happen in the future, including: (1) the Compliance Department has had discussions with the individuals currently responsible for these duties and has reviewed the regulations with such individuals to ensure that the requirements are understood and met; (2) RFC_URE1 has created a new managerial level position that handles these particular CIP standards to assure that adequate resources are allocated to these CIP standards, and the individual previously responsible for compliance with this standard has been relieved of those responsibilities and is no longer with the Company; and finally, (3) RFC_URE1 will provide additional training with respect to CIP-006. | 2011-12-31 | 2012-02-13 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100835 | Settlement Agreement | RFC_URE1 submitted a Self-Report identifying a violation of CIP-006-1 R5. While preparing for a compliance audit, RFC_URE1 found that it had not properly implemented its CIP-006 compliance program in all cases. RFC_URE1 failed to maintain full documentation for all physical security alarms to demonstrate that it reviewed and responded to unauthorized access attempts in accordance with the procedures specified in its physical security plan, pursuant to ClP-006-1 R5. RFC_URE1 investigated all physical security alarms and had documentation of the alarms and who acknowledged them, but failed to generate written documentation of the security reviews and responses for each alarm. RF determined that RFC_URE1 violated ClP-006-1 R5 by failing to document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeters (PSPs) twenty-four hours a day, seven days a week. | CIP-006-1 | R5 | Medium | Severe | In light of the nature of the violations, offset by the mitigating factors, RF determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). For the violation of CIP-006-1 R5, the risk to the BPS was mitigated by the fact that although RFC_URE1 failed to document controls for monitoring physical access to PSPs, its corporate security procedures required the guard on duty to respond to and investigate each event. Additionally, RFC_URE1 has documentation of every alarm received and when the security professional on duty acknowledged each alarm. | When RFC_URE1 was subject to compliance with the Standard | When RFC_URE1 completed mitigating actions | $65,000 (For RFC201100830, RFC201100831, RFC201100832, RFC201100833, RFC201100834, RFC201100835) | Self-Report | Regarding the documentation of responses to alarm events and unauthorized access attempts, the security guards charged with investigating these alarm alerts are now well versed on the required documentation, and are maintaining evidentiary documentation of each alarm or unauthorized access attempt response. This was instituted shortly after the issue was discovered. With respect to all of these issues of non-compliance under CIP-006, RFC_URE1 is taking several additional measures to strengthen its program and to ensure that such an occurrence does not happen in the future, including: (1) the Compliance Department has had discussions with the individuals currently responsible for these duties and has reviewed the regulations with such individuals to ensure that the requirements are understood and met; (2) RFC_URE1 has created a new managerial level position that handles these particular CIP standards to assure that adequate resources are allocated to these CIP standards, and the individual previously responsible for compliance with this standard has been relieved of those responsibilities and is no longer with the company; and finally, (3) RFC_URE1 will provide additional training with respect to CIP-006. | 2011-12-31 | 2012-02-13 | Neither Admits nor Denies | RF favorably considered certain aspects of RFC_URE1's compliance program.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100778 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-006-2c R2.2 (the duration of this violation involves versions 2 and 3 of CIP-006. Other than referencing the corresponding version of the CIP Reliability Standards, the text of all applicable versions of CIP-006 R2 and R2.2 are identical). RFC_URE2 determined that it failed to identify three devices as Cyber Assets that authorize access to its Physical Security Perimeter (PSP), and did not afford them the protective measures as specified in CIP-006-2c R2.2. Specifically, RFC_URE2 failed to afford these protective measures to a physical security server, a digital video recorder, and a personal computer (collectively, the Server/DVR/PC), each of which RFC_URE2 used to create access badges and authorize access to the PSP. ReliabilityFirst determined that RFC_URE2 violated CIP-006-2c R2.2 by failing to afford the Server/DVR/PC the protective measures specified in CIP-006-2c R2.2. | CIP-006-2c | R2; R2.2 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. RFC_URE2 implemented, at all relevant times, separate security mechanisms designed to minimize overall cyber and physical security risks at the facility including intrusion detection, anti-virus, security logging, access control (both cyber and physical), and defense-in-depth network design. These mechanisms help RFC_URE2 to, among other things, detect possible attacks on its system, help prevent virus and malware infection, and limit inbound traffic. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 afforded the protective measures specified in CIP-006-2c R2.2 to the Server/DVR/PC | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Report | RFC_URE2 afforded all the protective measures specified in CIP-006-2c R2.2 to the Server/DVR/PC. RFC_URE2 also updated all relevant documentation associated with the Server/DVR/PC to reflect the protective measures RFC_URE2 afforded to the Server/DVR/PC. These updates were communicated to all relevant staff. | 2011-04-30 | 2011-11-28 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100779 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-007-2a R2 (the duration of this violation involves version 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R2 are identical). RFC_URE2 determined that it failed to disable its unused ports and services on a single transmission control room personal computer, located within the Electronic Security Perimeter (ESP) pursuant to Reliability Standard CIP-007-2a R2. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2a R2 by failing to implement its established, documented process to ensure it enabled only ports and services used for normal and emergency operations. | CIP-007-2a | R2 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. Although RFC_URE2 did not disable its unused ports and services on one personal computer in the ESP, RFC_URE2 has a documented process to perform such actions, but in this instance failed to implement its process. In addition, RFC_URE2 disabled the unused ports and services on the firewall surrounding the personal computer at issue, thereby minimizing the exposure of Cyber Assets inside the ESP to outside attacks. RFC_URE2 also implements separate security mechanisms designed to minimize overall cyber and physical security risks including intrusion detection, anti-virus, security logging, access control (both cyber and physical), as well as defense-in-depth network design. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 disabled the unused ports and services on the personal computer located within the ESP | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Report | RFC_URE2 disabled the unused ports and services on the transmission control room personal computer within the ESP. RFC_URE2 also updated all relevant documentation associated with CIP-007 R2 and these updates were communicated to all relevant staff. | 2011-04-30 | 2012-02-09 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100913 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-005-2 R1.5 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-005-1 R1 (the duration of this violation involves versions 2 and 3 of CIP-005. Other than referencing the corresponding version of the CIP Reliability Standards, the text of all applicable versions of CIP-005 R1.5 are identical). RFC_URE2 determined it had not afforded certain Cyber Assets used in access control and monitoring of its Electronic Security Perimeter (ESP) all the protective measures described in CIP-005-2 R1.5. Specifically, RFC_URE2 did not afford two servers the protections specified in CIP-007 R4, CIP-005 R2.6 and CIP-007 R2. ReliabilityFirst determined that RFC_URE2 violated CIP-005-2 R1.5 by failing to afford two Cyber Assets used in access control and monitoring of its ESP the protective measures specified in CIP-007 R4, CIP-005 R2.6 and CIP-007 R2. | CIP-005-2 | R1; R1.5 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. RFC_URE2 was affording its Cyber Assets used in controlling and monitoring its ESP some of the protective measures required by CIP-005-2 R1.5. This included the protective measures found in Reliability Standards CIP-005 R3 and CIP-004 R3. In addition, RFC_URE2 implements separate security mechanisms to minimize overall cyber security risk including intrusion prevention systems, anti-virus software, security logging, and defense-in-depth network design. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 afforded all protective measures included in CIP-005-2 R1.5 to its Cyber Assets used in the access control and monitoring of its ESP) | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 updated all documentation associated with those Cyber Assets to reflect the newly afforded protections, as well as communicated the required protective measures with all relevant staff. | 2011-11-30 | 2012-02-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100915 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-006-2 R3 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-006. The text of versions 2 and 3 of CIP-006 R3 are identical). RFC_URE2 determined that it did not position two servers, both Cyber Assets used in the access control and monitoring of its Electronic Security Perimeter (ESP) (ACM Cyber Assets), within an identified Physical Security Perimeter (PSP). ReliabilityFirst determined that RFC_URE2 violated CIP-006-2 R3 by failing to position the ACM Cyber Assets within an identified PSP. | CIP-006-2 | R3 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. While RFC_URE2 did not locate its ACM Cyber Assets within an identified PSP, it did position the ACM Cyber Assets in a secured room. RFC_URE2 controlled access to the secured room by a badge reader and biometrics, which required fingerprinting, to enter. In order for RFC_URE2 to grant access to the secured room, an individual first had to go through a personnel risk assessment (PRA) and receive CIP training. Additionally, RFC_URE2 monitored the ACM Cyber Assets within the secured room via security camera. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 completed installation of the equipment necessary to create a PSP around the ACM Cyber Assets | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 installed the equipment necessary to create a PSP surrounding ACM Cyber Assets. Additionally, RFC_URE2 updated all relevant documentation associated with CIP-006 R3 and notified all staff engaged in managing Cyber Assets within the PSP of the changes. | 2011-11-30 | 2012-02-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100917 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-006-2 R8 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-006 R8. The duration of this violation involves versions 2 and 3 of CIP-006. The text of all applicable versions of R8 are identical). RFC_URE2 determined that it did not implement a maintenance and testing program to help ensure all its physical security systems under CIP-006 R4, R5 and R6 function properly. ReliabilityFirst determined that RFC_URE2 violated CIP-006-2 R3 by failing to implement its maintenance and testing program to help ensure all its physical security systems under CIP-006 R4 R5 and R6 function properly. | CIP-006-2 | R8 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the following factors. RFC_URE2 tested the physical security systems just prior to its mandatory compliance date. At the time of testing, RFC_URE2's security vendor initially performed a number of tests on the physical security system. These included verifying that: (a) card readers work properly and record logging of entrants; (b) the system creates and maintains a database of entrants; (c) the system denies access to unauthorized cards; (d) the system alarms when a door is forced open or remains open for certain period of time; (e) the security cameras face all points of entry to each PSP and record footage to a DVR server; and (f) the badge creation system ensured that the created badges work and deactivated badges are denied. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 implemented a documented maintenance and testing program to help ensure its physical security systems under CIP-006-2 R4, R5, and R6 function properly | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 obtained a documented maintenance and testing program for the installed security system from its vendor to help ensure that all physical security systems under CIP-006 R4, R5 and R6 function properly. RFC_URE2 also updated all relevant documentation associated with CIP-006 R8 and notified all staff involved in managing Cyber Assets within the ESP of the newly created maintenance and testing program for its physical security systems. | 2011-04-30 | 2011-09-29 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100918 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-007-2 R1 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-007 R1. ReliabilityFirst determined the violation implicated sub-requirements R1.2 and R1.3. The duration of this violation spans versions 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R1 and its sub-requirements, other than the reference to the corresponding version of CIP-007, is identical). RFC_URE2 reported that while it has a procedure in place to help ensure new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) do not adversely affect existing cyber security controls, it had no procedures for actual testing of any Critical Cyber Assets (CCAs) or Cyber Assets. Further, ReliabilityFirst determined that RFC_URE2 could not provide evidence that it performed security testing for Cyber Assets within the ESP or the results of the testing. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2 R1 by failing to document the testing it performed. Additionally, it failed to document the results of that testing, and therefore could not demonstrate that testing was performed in a manner that reflects the production environment or the results of that testing pursuant to CIP-007-2 R1.2 and R1.3. | CIP-007-2 | R1 | Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a minimal, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the fact that this is the result of a documentation error. It is a documentation error because RFC_URE2 represents it performed testing in a test environment that reflects the production environment to Cyber Assets prior to RFC_URE2 installing any new Cyber Assets or making significant changes to existing Cyber Assets within the ESP. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 established and documented the security testing procedures and manner of testing | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 established and documented the security testing procedures and manner of testing for each category of Cyber Assets within its ESP and communicated the updates to all relevant staff. | 2012-05-31 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100919 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-007-2 R3 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-007 R3. The duration of this violation involves versions 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R3 and its sub-requirements, other than the reference to the corresponding version of CIP-003, is identical). RFC_URE2 determined it had not established, documented or implemented a security patch management program for a specific class of Critical Cyber Assets (CCAs), access control and monitoring devices, and other Cyber Assets within its Electronic Security Perimeter (ESP) pursuant to CIP-007-2 R3. RFC_URE2 did not apply security patches to one Cyber Asset within its ESP during the duration of the violation. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2 R3 by failing to establish, document or implement a security patch management program for its specified class of CCAs, access control and monitoring devices, and other Cyber Assets within its ESP pursuant to CIP-007-2 R3. | CIP-007-2 | R3 | Lower | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the fact that RFC_URE2 subscribes to multiple security alerts to evaluate, on a monthly basis, if the indentified vulnerabilities are applicable to RFC_URE2's Cyber Assets and the possible level of threat. | Date RFC_URE2 was subject to compliance with the Standard | Date RFC_URE2 implemented its documented security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESP pursuant to CIP-007-2 R3 | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 determined which CCAs within the ESP it must subject to security patch testing and determined whether security patches exist for the identified equipment. RFC_URE2 installed all applicable security patches to CCAs and Cyber Assets within its ESP and documented its security patch management program in accordance with CIP-007-2 R3's requirements. These updates were communicated to all relevant staff. | 2012-05-31 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100920 | Settlement Agreement | RFC_URE2 self-certified non-compliance with Reliability Standard CIP-007-2 R4 to ReliabilityFirst (RFC_URE2 initially self-certified noncompliance to only version three of CIP-007 R4. The duration of this violation involves versions 2 and 3 of CIP-007. The text of all applicable versions of CIP-007 R4 and its sub-requirements is identical). RFC_URE2 determined it did not test its malware prevention signatures (Signatures) prior to installing the Signatures on one Cyber Asset, a transmission control room personal computer, within its Electronic Security Perimeter (ESP) (RFC_URE2 has other Cyber Assets within the ESP, however, they were not involved in this violation). RFC_URE2 had set the transmission control room personal computer to automatically update the anti-virus signature files directly from a server without prior testing. ReliabilityFirst determined that RFC_URE2 violated CIP-007-2 R4 by failing to test its Signatures prior to installing the Signatures on one Cyber Asset within its ESP. | CIP-007-2 | R4 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate, not serious or substantial, risk to the reliability of the bulk power system (BPS). This risk to the BPS was mitigated by the fact that RFC_URE2 continued to use network intrusion detection systems, access controls at the firewall and system logging during the duration of the violation. Additionally, the Cyber Assets on which RFC_URE2 failed to test its Signatures prior to installation had no direct Internet access, which reduced the potential for exposure to malware. | Date RFC_URE2 was subject to compliance with the Standard | Date by which RFC_URE2 implemented a process for the update of its Signatures which included testing and installation | $55,000 (for RFC201100778, RFC201100779, RFC201100913, RFC201100915, RFC201100917, RFC201100918, RFC201100919, and RFC201100920) | Self-Certification | RFC_URE2 constructed an environment to test Signatures prior to installing them on assets within the ESP. RFC_URE2 also updated all documentation relevant to CIP-007-2 R4.2 compliance and notified staff engaged in managing Cyber Assets within the ESP of the changes to the documentation. | 2012-05-31 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE2's compliance program as mitigating factors.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000302 | Settlement Agreement | SPP RE discovered a violation of CIP-004-1 R2.1 during a Spot Check. SPP RE determined that SPPRE_URE1 was noncompliant with the Standard by failing to train all personnel having authorized access to Critical Cyber Assets within 90 days of such authorization. SPPRE_URE1 had 58 employees that had physical and/or electronic access to Critical Cyber Assets (CCAs) at SPPRE_URE1’s primary control center (CC) and/or backup control center (BCC), but only six had received cyber security training required by CIP-004-1 R2.1 by the end of the year. Such training was provided in the summer of that year, and all of SPPRE_URE1's applicable operators received training on that date. By the end of the following year, seven more employees had been granted access to CCAs at the CC and/or BCC for a total of 65 employees. In spring of that year, the six employees who received training in the prior year were trained again, along with 28 others, leaving 31 employees without training at the end of the year. As of the beginning of the next year, assets beyond the control centers came into scope and 47 additional personnel (employees and contractors) with physical access to non-control center CCAs were required to be trained pursuant to CIP-004-1 R2.1. Thirty-two (32) of these individuals received training in the prior year. The remaining 15 had not received training within 90 days of the beginning of the year. Forty-five (45) individuals were removed from the access list and had their access revoked during the spring, the majority of whom were management personnel who did not require access to CCAs. As of the spring, seven total individuals remained on the access list without having received training; these seven individuals received their training by the end of the summer. | CIP-004-1 | R2.1 | Medium | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all five energy control system operators completed training. Further, the 45 individuals removed in the spring were in roles that did not require access to CCAs. The access of these individuals was revoked in the spring. After removal of those individuals, only seven remained without training. These individuals were all trained by the end of the summer. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date individuals were trained | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | All individuals with electronic and unescorted physical access to CCAs who had not received the proper cyber security training received such training. A new training procedure was implemented to ensure that new employees and existing employees that are granted access to critical cyber assets receive timely cyber security training. Also, the procedure provides steps to ensure that annual training is timely received. The new program covers all of the requirements included in CIP-004 R2, and access list designees were required to take the new training program. SPPRE_URE1 will enforce revocation of access privileges in the event of expiration of any access designee's CIP-004 R2 training. Similarly, new access shall not be granted until successful completion of CIP-004 R2 online training is verified by the CIP Senior Manager. | 2011-03-28 | 2011-04-14 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000303 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-004-1 R3 during a Spot Check. An SPPRE_URE1 procedure did not provide for conducting background checks on incumbent employees. Although SPPRE_URE1 was required to comply with CIP-004-1 R3 for personnel with authorized access to control center assets, the earliest evidence indicating that SPPRE_URE1 informed the human resources department of the need to conduct background checks was almost a year later. The SPPRE_URE1 procedure was revised to include a provision requiring background checks in order to comply with CIP-004-1 R3. CIP-004-1 R3 allowed for a 30-day window in which Personnel Risk Assessments (PRAs) must be performed after issuance of authorized cyber or authorized unescorted physical access to Critical Cyber Assets. However, the required PRAs were not completed within 30 days of the effective date of the revised policy. There was only one employee who required newly granted access subsequent to when the procedure went into effect. That employee received access almost two months later and then had his access removed about six months later and never received a PRA. Managers and directors that had access to CCAs did not receive PRAs and had their access removed in the spring prior to the Spot Check. | CIP-004-1 | R3 | Medium | High | SPP RE determined that the violation posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The personnel that had not received PRAs were incumbent employees, many of them long-term SPPRE_URE1 employees. Most of the PRAs were completed within six months of the policy revision, and all were completed within eight months. None of the personnel failed to successfully pass a PRA. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date last affected employee's access was revoked | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 performed a review to ensure that all required PRAs had been conducted. A SPPRE_URE1 manager of Compliance reviewed the personnel and training procedure to ensure its sufficiency and attested that SPPRE_URE1 understands and will ensure that CCA access will not be granted in the future without first conducting a PRA. | 2010-10-01 | 2010-10-29 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000304 | Settlement Agreement | SPP RE discovered a violation of CIP-004-1 R4 during a Spot Check. A SPPRE_URE1 employee with authorized unescorted physical access to Critical Cyber Assets (CCAs) retired. The retired employee’s name was not removed from the SPPRE_URE1 CCA access list within seven days, as required by CIP-004-1 R4.1. Further, a review and approval of the list was performed almost two weeks after the employee retired, but SPPRE_URE1 failed to remove the retired employee’s name before approving the list. In addition, CIP-004-1 R4.2 requires the actual revocation of access to CCAs to occur within seven days for personnel who no longer require such access. SPP RE was unable to verify that such revocation occurred within seven days. Although SPPRE_URE1 took possession of the employee's access card on the day the employee retired, the employee was not removed from the access list until four months later. | CIP-004-1 | R4 | Medium | Moderate | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the retired employee was not removed from the access list until four months later, SPPRE_URE1 indicated that it in effect revoked access by taking possession of the retired employee's access card on the date of the retirement. The SPP RE spot check team verified that, as of the date of the spot check, the retired employee had been removed from the access control system, but could not verify the date of removal. The employee, who had been employed by SPPRE_URE1 since 1989, retired and was not involuntarily terminated. There was no evidence that the retired employee attempted to gain access subsequent to the date of retirement. Further, the employee had only unescorted physical access, not electronic access. Therefore, had the retired employee successfully gained physical access, he still would not have had a username and password with which to access the Supervisory Control and Data Acquisition System. The size of SPPRE_URE1 reduced the potential impact on the BPS. | The date by which retired employee's access should have been revoked | The date the retired employee was removed from the access list | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 removed the retired employee from the access list. SPPRE_URE1 performed a detailed review of its access list to ensure that the list is accurate and up-to-date. To help ensure future compliance, SPPRE_URE1 managers with duties pursuant to SPPRE_URE1's access control procedure certified that they are aware of their responsibilities under that procedure. | 2010-10-01 | 2010-10-29 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000305 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-007-1 R1 during a Spot Check. SPPRE_URE1 did not have a procedure per CIP-007-1 R1 for testing to ensure that cyber security controls were not adversely affected by new Cyber Assets introduced into the Electronic Security Perimeter (ESP) or by significant changes that were made to existing Cyber Assets within the ESP. The procedure that was in place prior to the revised procedure only included testing to ensure proper functionality. The testing procedure did not test for adverse effects on security controls. Therefore, security controls testing pursuant to CIP-007-1 R1 was not being performed before that date. | CIP-007-1 | R1 | Medium | Severe | SPP RE determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). At the time of the spot check, SPPRE_URE1 had already implemented a security controls testing procedure per CIP-007-1 R1; however, prior to the revised procedure, SPPRE_URE1's procedures only called for functional testing. As a result, the potential existed for the new assets and changes to existing assets to have an adverse impact on security controls, thereby causing SPPRE_URE1's Critical Cyber Assets to be more vulnerable to attack. Despite this vulnerability, the size of SPPRE_URE1 reduced the impact that potential attacks would have had on the BPS. | When Standard became mandatory and enforceable | The date SPPRE_URE1 implemented a security controls testing procedure per CIP-007-1 R1 | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 submitted its Mitigation Plan as complete because a complete security controls testing procedure has been created. The implementation of testing procedures for Cyber Assets within the ESP address testing of security controls where previous plans did not. | 2010-01-01 | 2010-11-09 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000306 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-008-1 R1.6 during a Spot Check. SPPRE_URE1 tested its incident response plan the two prior years, but the forms documenting the tests do not demonstrate that the plan was fully tested. The documentation shows that for each of the tests a mock cyber incident was considered, the cause was determined, the potential impact was analyzed, and the incident handling steps to be taken were outlined. However, the documentation does not demonstrate that the incident was characterized as reportable and that the incident would have been reported to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC) as required by the incident response plan. Further, the completed forms do not show that all members of the cyber security incident response team were or would have been contacted as required by the plan. | CIP-008-1 | R1.6 | Lower | High | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although SPPRE_URE1 did not maintain sufficient documentation to demonstrate that the incident response plan was fully tested the two prior years, tests involving simulated cyber incidents were performed. Performing regular tests helps to ensure that SPPRE_URE1 will rely on and follow its incident response plan in the event of a true cyber incident. The size of SPPRE_URE1, reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date Mitigation Plan was completed | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 updated its plan and exercise to include the following Spot Check Team recommendations: - Adding alternative contact information to ES-ISAC; - Adding an ES-ISAC checkbox to response documentation; and - Aligning incident response classification and characterization criteria with NERC Incident Reporting Guideline. SPPRE_URE1 also performed a test per CIP-008-1 R1.6 of its incident response. Revisions to the plan went into effect. SPPRE_URE1 initially performed a test that SPP RE deemed to be still not fully in line with the Standard. After review and further discussion with SPPRE_URE1, SPP RE requested and received evidence demonstrating that a test per the Standard was performed. | 2011-01-18 | 2011-02-02 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000307 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-009-1 R1 during a Spot Check. The two prior versions of SPPRE_URE1's recovery plans only covered the restoration of backed-up data and information from tape. The plan did not address the recovery of all Critical Cyber Assets such as remote terminal units, server hardware, and other networking assets. The plans did not address recovery situations involving varying duration and severity as required by R1.1. The revised recovery plan addresses the requirements of the Standard. | CIP-009-1 | R1 | Medium | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPPRE_URE1, in addition to maintaining a backup control center, retains a standby unit for all CCA hardware. In the absence of a recovery plan for a particular asset, SPPRE_URE1 had the option to place the standby unit into service. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date Mitigation Plan was completed | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 revised its recovery plan to address the recovery of all Critical Cyber Assets such as remote terminal units, server hardware, and other networking assets and address recovery situations involving varying duration and severity. The revised recovery plan was implemented per the Standard. | 2010-05-07 | 2010-11-09 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000308 | Settlement Agreement | SPP RE discovered a violation by SPPRE_URE1 of CIP-009-1 R2 during a Spot Check. SPPRE_URE1's exercise of its CIP-009-1 recovery plans in the two prior years both involved actual occurrences of hardware failure; however, neither recovery scenario was covered in the existing recovery plans. The two prior versions of the recovery plans were found to be deficient, and a separate violation was found regarding R1 as well. To comply with R2, SPPRE_URE1 needed to test the recovery plan that was in place; it did not, and instead followed undocumented recovery procedures for assets not covered in the recovery plan. | CIP-009-1 | R2 | Lower | Severe | SPP RE determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE1's existing recovery plan did not cover the actual occurrences of hardware failure, the two prior versions of the exercises of its recovery plans still applied the framework of its recovery plans in recovering from the loss of a hard drive and the loss of a motherboard. The size of SPPRE_URE1 reduced the potential impact on the BPS. | When Standard became mandatory and enforceable | The date Mitigation Plan was completed | $20,800 (for SPP201000302, SPP201000303, SPP201000304, SPP201000305, SPP201000306, SPP201000307, and SPP201000308) | Spot Check | SPPRE_URE1 developed a new form to better document both Critical Cyber Asset (CCA) recovery exercises and actual incident recovery. In addition, SPPRE_URE1 expanded the scope of its recovery plan to consider CCAs at the component level, allowing for better planning of individual CCA recovery. SPPRE_URE1 performed an exercise of its revised recovery plan per the Standard. | 2010-12-21 | 2011-02-02 | Neither Admits nor Denies | SPPRE_URE1 had an internal compliance program (ICP) in place at the time of the violation and it was considered a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000330 | Settlement Agreement | During a Spot Check, SPP RE determined that SPP RE_URE2 was noncompliant with CIP-007-1 R1 for not adequately testing security controls when performing significant changes to Cyber Assets (CAs) within the Electronic Security Perimeter (ESP). Cyber security controls testing for updates made to existing CAs was not performed until 22 months after the compliance enforcement date. Only application functionality testing was being performed according to the Energy Management System (EMS) staff and confirmed by SPP RE by examining the submitted test results documentation. | CIP-007-1 | R1 | Medium | High | SPP RE determined that SPP RE_URE2’s violation of CIP-007-1 R1 posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE2 had additional cyber security control measures in place that reduced its risk profile, including strict firewall rules and automated security analysis tools monitoring for security threats. Consequently, had there been a successful cyber attack against CAs within SPP RE_URE2's ESP, additional security control measures were in place to detect the event. Due to these factors, SPP RE determined that the risk to the BPS was moderate. | When the standard became enforceable for the entity | Mitigation Plan completion | $8,800 (for SPP201000330, SPP201000331, SPP201000332, and SPP201000334) | Spot Check | To mitigate its violation of CIP-007-1 R1 and to prevent reoccurrence, SPP RE_URE2 implemented a new procedure for testing cyber security controls. The new procedure utilizes a vulnerability program, which is used to scan SPP RE_URE2's network system, create scan reports, and compare scan reports against one another for potential vulnerabilities and remediation prior to implementing significant changes in SPP RE_URE2’s production systems. | 2010-05-13 | 2010-10-29 | Neither Admits nor Denies | SPP RE recognized SPP RE_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000331 | Settlement Agreement | During a Spot Check, SPP RE determined that SPP RE_URE2 was noncompliant with CIP-008-1 R1.5 and R1.6. Regarding R1.5, although SPP RE_URE2 had an informal process for reviewing its Cyber Security Incident response plan and did conduct a review of the plan 15 months before the Spot Check, a formal process was not included in SPP RE_URE2’s Cyber Security Incident response plan until 3 months after that review or 1 year after the compliance enforcement date. Regarding R1.6, SPP RE_URE2 was required to test its Cyber Security Incident response plan by the date stated in the Implementation Plan for Cyber Security Standards Table; however, the test was not conducted until approximately 9 months after the enforceable date. | CIP-008-1 | R1; R1.5; R1.6 | Lower | High | SPP RE determined that SPP RE_URE2’s violation of CIP-008-1 R1 posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE2 failed to include a formal process in its Cyber Security Incident response plan (Plan) by the mandatory and effective compliance date of the Standard, SPP RE_URE2 did have an informal process for reviewing its Plan and conducted a review of the Plan. SPP RE_URE2 revised its Plan to include a process for an annual review. In addition, the identified incident response team had received comprehensive training on CIP Standards and are very experienced in the support of Critical Cyber Assets and would have reasonably been expected to recognize cyber security events, contain, and ultimately recover from an incident. Moreover, there have been no reported Cyber Security Incidents to date requiring activation of the Plan. Due to these factors, SPP RE determined that the risk to the BPS was minimal. | When the standard became enforceable for the entity | Mitigation Plan completion | $8,800 (for SPP201000330, SPP201000331, SPP201000332, and SPP201000334) | Spot Check | To mitigate its violation of CIP-008-1 R1 and to prevent reoccurrence, SPP RE_URE2 implemented a process for testing the Plan and began testing the Plan. SPP RE_URE2 revised its Plan to include a formal process to ensure an annual review of the plan. | 2009-03-25 | 2010-10-18 | Neither Admits nor Denies | SPP RE recognized SPP RE_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000332 | Settlement Agreement | During a Spot Check, SPP RE determined SPP RE_URE2 was noncompliant with CIP-009-1 R1. Specifically, although SPP RE_URE2’s Critical Cyber Asset (CCA) recovery plan outlined how operations could be restored, it did not address how CCAs would be recovered from an actual incident. | CIP-009-1 | R1 | Medium | Severe | SPP RE determined that SPP RE_URE2’s violation of CIP-009-1 R1 posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because SPP RE_URE2 had a recovery plan in place, as well as a business continuity plan, which addressed long-term recovery plans. Additionally, SPP RE_URE2’s backup control center could reasonably be expected to allow operations to continue at length until the primary control center could be recovered. Further, the entity support staff were experienced in the support of CCAs and could have performed the appropriate recovery steps for a wide variety of incidents. Due to these factors, SPP RE determined that the risk to the BPS was minimal. | When the standard became enforceable for the entity | Mitigation Plan completion | $8,800 (for SPP201000330, SPP201000331, SPP201000332, and SPP201000334) | Spot Check | To mitigate its violation of CIP-009-1 R1 and to prevent reoccurrence, SPP RE_URE2 amended its CCA recovery plan to include the recovery of CCAs. | 2010-10-27 | 2010-12-15 | Neither Admits nor Denies | SPP RE recognized SPP RE_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000334 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report to SPP RE stating that it was in violation of CIP-007-1 R3. Specifically, during an internal compliance assessment, SPP RE_URE2 discovered that security patches were not being assessed for applicability within 30 days of availability for the Energy Management System (EMS) environment as required by R3.1. Since the assessments for security patches were not being performed, SPP RE_URE2 was unable to determine whether there were any system vulnerabilities and whether it needed to document compensating measures to mitigate any risk exposure or an acceptance of risk as required by R3.2. | CIP-007-1 | R3 | Lower | Severe | SPP RE determined that SPP RE_URE2’s violation of CIP-007-1 R3 posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS). Failing to conduct assessments of security patches potentially exposed SPP RE_URE2’s Critical Cyber Assets (CCAs) to a number of vulnerabilities, which could have allowed for successful cyber attacks against CCAs essential to the reliability of the BPS. However, at the time of the violation, SPP RE_URE2 did have additional cyber security control measures in place that reduced its risk profile, including strict firewall rules and automated security analysis tools monitoring for security threats. During implementation of the Mitigation Plan, SPP RE_URE2 electronically reviewed operating system logs for potential breaches of its production system. The application used to monitor the logs is capable of electronically notifying SPP RE_URE2 staff of any potential security issues on a real-time basis. Moreover, SPP RE_URE2 used a file usage monitoring application that would have notified EMS staff of any application or operating system file additions, changes, or deletions that would have indicated a potential virus or malware attack. Due to these factors, SPP RE determined that the risk to the BPS was moderate. | When the standard became enforceable for the entity | Mitigation Plan completion | $8,800 (for SPP201000330, SPP201000331, SPP201000332, and SPP201000334) | Self- Report | To mitigate its violation of CIP-007-1 R3 and to prevent reoccurrence, SPP RE_URE2 contracted with an EMS vendor to upgrade to a new operating system and to track, evaluate, and test EMS operating system security patches prior to deployment. SPP RE_URE2 implemented EMS security patch review procedures for the EMS vendor. Since completion of the upgrade, the EMS vendor now tracks, evaluates, and tests EMS operating system security patches for applicability and provides the results to SPP RE_URE2 as required by R3.1. SPP RE_URE2 then applies the security patches to the new EMS operating system and retains implementation documentation as required by R3.2. | 2011-05-31 | 2011-06-22 | Neither Admits nor Denies | SPP RE recognized SPP RE_URE2's internal compliance program (ICP), in effect at the time of the violation, to be a mitigating factor in the penalty determination.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102518 | Notice of Confirmed Violation | WECC_URE1 self-reported to WECC a violation of CIP-007-3 R3. In the Self-Report, WECC_URE1 stated that it failed to document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for Cyber Assets within its Electronic Security Perimeters (ESPs). Four months later, a WECC subject matter expert (SME) discussed the violation with WECC_URE1. During the discussion, WECC_URE1 stated that it used a management console to install and test the patches on its system; however, due to a compatibility issue with WECC_URE1’s network configuration, the management console was unable to distribute the patches to WECC_URE1’s Cyber Assets. In order to solve the network configuration problem and distribute the patches to its Cyber Assets, WECC_URE1 manually applied the patches to its Cyber Assets, but did not document these actions. In addition, WECC_URE1’s manual process for implementing patches to its Cyber Assets was not established or documented. Three months after the initial contact, WECC_URE1 submitted a second Self-Report to WECC which included additional patches that it failed to install on its system. The WECC SME concluded that the additional information WECC_URE1 self-reported to WECC was an expanded scope of WECC_URE1’s first self-reported violation and not a new violation. WECC Enforcement reviewed the WECC SME’s findings and determined that WECC_URE1 was in violation of CIP-007-3 R3 for failing to establish, document and implement its manual patch program. | CIP-007-3 | R3 | Lower | High | Failure to assess and install security patches could result in vulnerabilities remaining unaddressed for extended periods of time. This increases the risk of a successful cyber attack against Critical Cyber Assets essential to the operation of the bulk power system (BPS). In this instance, WECC_URE1 failed to document its manual patch program as well as its implementation; however, the risk to the BPS was minimized by the devices in scope having anti-virus software, system logs enabled and daily log reviews. The devices were located in an ESP and Physical Security Perimeter (PSP) which were afforded the protections specified in CIP-005 and CIP-006. Accordingly, WECC Enforcement determined that this violation posed a moderate and not serious or substantial risk to the reliability of the BPS. | When WECC_URE1 was required to be compliant with the Standard | Mitigation Plan completion | $12,300 (for WECC201102518 and WECC201102519) | Self-Report | WECC_URE1 submitted a Mitigation Plan for this violation. In accordance with the Mitigation Plan, WECC_URE1 has competed the following: (1) retroactively installed previous patches that were originally missed; (2) remediated configuration issues so the management console can distribute signatures to the Cyber Assets; (3) assigned a dedicated IT contractor to assist with implementation and verification of security patches and updates; (4) created a documentation log to track the implementation of security patches and updates; and (5) created updated procedures to address manual implementation of signatures if the automated system fails. | 2011-01-12 | 2012-02-14 | Does Not Contest | WECC took into consideration WECC_URE1's and its affiliates' violation history.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102519 | Notice of Confirmed Violation | WECC_URE1 self-reported a violation of CIP-007-3 R4. Four months later, a WECC subject matter expert (SME) contacted WECC_URE1 to discuss the violation. According to the WECC SME, WECC_URE1 stated that it failed to implement anti-virus and malware prevention tools on all seventeen of its Cyber Assets. Specifically, WECC_URE1 stated that it failed to implement a process for updating anti-virus and malware prevention “signatures.” Three months after the initial contact, WECC_URE1 submitted an additional Self-Report to WECC which highlighted that it failed to install anti-virus and anti-malware software on its Cyber Assets used to control its generation station, in violation of CIP-007-3 R4.1. The WECC SME concluded that WECC_URE1 was in violation of CIP-007-3 R4.1 and R4.2 and referred the matter to WECC Enforcement. WECC Enforcement determined that WECC_URE1 was in violation of CIP-007-3 R4.1 and R4.2 because it failed to implement a process for updating anti-virus and malware prevention “signatures.” | CIP-007-3 | R4; R4.1, R4.2 | Medium | High | Failure to update anti-virus and malware prevention signatures could allow existing and/or new malicious software to be introduced to Cyber Assets, exposing them to security vulnerabilities. Such vulnerabilities could negatively impact the bulk power system (BPS). In this instance, WECC_URE1 did not implement anti-virus and malware prevention "signatures" to all seventeen Cyber Assets within its Electronic Security Perimeters (ESP); however, risk to the BPS was minimized by the devices in scope having anti-virus and malware prevention tools installed and daily reviews. The devices in the scope of the violation were located in an ESP and a Physical Security Perimeter (PSP) which were afforded the protections specified in CIP-005 and CIP-006. Accordingly, WECC Enforcement determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the BPS. | When anti-virus updates were scheduled to be performed automatically but failed to operate and manual loading also failed to be performed | Mitigation Plan completion | $12,300 (for WECC201102518 and WECC201102519) | Self-Report | WECC_URE1 submitted a Mitigation Plan for this violation. In accordance with the Mitigation Plan, WECC_URE1 has competed the following: (1) performed all updates for its anti-virus and malware software; and (2) documented the updates. | 2011-09-30 | 2011-12-02 | Does Not Contest | WECC took into consideration WECC_URE1's and its affiliates' violation history.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102520 | Notice of Confirmed Violation | WECC_URE2 self-reported to WECC a violation of CIP-007-3 R3. Seven months later, WECC_URE2 submitted a second Self-Report to WECC. A WECC subject matter expert concluded that this additional information was an expanded scope of the initial violation and not a new violation. WECC concluded that WECC_URE2 was in violation of the Standard when it failed to document a security patch management program for tracking, evaluating, testing, and installing applicable cyber security patches for Cyber Assets within its Electronic Security Perimeters (ESPs). Specifically, WECC_URE2 used a management console to install and test the patches on its system, but due to a compatibility issue with WECC_URE2's network configuration, the management console was unable to distribute the patches to WECC_URE2's Cyber Assets. Initially, WECC_URE2 did not install the necessary security patches, but the patches were then applied manually. However, WECC_URE2's manual process for implementing patches to its Cyber Assets was not established or documented, nor was the implementation of this process documented, as required by the Standard. The second Self-Report disclosed additional patches that it failed to install on its system. | CIP-007-3 | R3 | Lower | High | WECC determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the following factors: (1) the security patches were installed on all seven of the entity's Cyber Assets located in the ESPs at two locations which were used for controlling WECC_URE2's remote turbines; (2) the devices in scope had anti-virus installed; (3) the system logs for the devices in scope were enabled and the logs were reviewed daily; (4) the devices in scope were in an ESP and Physical Security Perimeter (PSP) and were afforded the protections specified in CIP-005 and CIP-006. | When WECC_URE2 was required to be compliant with the Standard | Mitigation Plan completion | $12,300 (for WECC201102520; and WECC201102521) | Self-Report | WECC_URE2 submitted a Mitigation Plan to address the violation of CIP-007-1 R3. In accordance with the Mitigation Plan, WECC_URE2 (1) retroactively installed previous patches that were originally missed; (2) remediated configuration issues so the management console can distribute signatures to the Cyber Assets; (3) assigned a dedicated IT contractor to assist with implementation and verification of security patches and updates; (4) created a documentation log to track the implementation of security patches and updates; and (5) updated procedures to address manual implementation of signatures if the automated system fails. | 2011-01-12 | 2012-02-14 | Does Not Contest | WECC took into consideration WECC_URE2's and its affiliates' violation history.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102521 | Notice of Confirmed Violation | WECC_URE2 self-reported to WECC a violation of CIP-007-3 R4 for its Electronic Security Perimeters (ESPs) at five locations which are used to control WECC_URE2's remote turbines. WECC determined that WECC_URE2 was in violation of CIP-007-3 R4.2 for its failure to implement a process for updating anti-virus and malware prevention signatures on all seven of its Cyber Assets. Seven months later, WECC_URE2 submitted a second Self-Report to WECC expanding the scope of this violation to include WECC_URE2's generating station. This violation spans multiple versions of the Standard. WECC applied the violation to CIP-007-1 which was the earliest applicable version of the Standard. WECC determined that WECC_URE2 failed to install anti-virus and anti-malware software on its Cyber Assets used to control its generating station, in violation of CIP-007-1 R4.1. | CIP-007-3 | R4 | Medium | High | WECC determined that this violation posed a minimal and not serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) the devices in scope had anti-virus and malware prevention tools installed; (2) the devices in scope were reviewed daily; (3) the devices in scope were in an ESP and Physical Security Perimeter (PSP); (4) the devices in scope were afforded the protections specified in CIP-005 and CIP-006. | When anti-virus updates were scheduled to be performed automatically but failed to operate and manual loading also failed to be performed | Mitigation Plan completion | $12,300 (for WECC201102520; and WECC201102521) | Self-Report | WECC_URE2 submitted a Mitigation Plan to address the violation of CIP-007-1 R4. In accordance with the Mitigation Plan, WECC_URE2 (1) performed all updates for its anti-virus and malware software and (2) documented the updates. | 2011-09-30 | 2011-12-02 | Does Not Contest | WECC took into consideration WECC_URE2's and its affiliates' violation history.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102641 | Settlement Agreement | WECC_URE3 submitted a self-certification addressing noncompliance with CIP-005-3 R1. The self-certification addressed a failure to ensure that Cyber Assets used in the access control for monitoring of the Electronic Security Perimeter(s) (ESPs) were afforded the protective measures as specified in this Standard. WECC_URE3 failed to provide three protective measures on 16 devices used in access control of ESPs. A WECC Subject Matter Expert (SME) reviewed WECC_URE3's self-certification and requested additional information from its compliance staff. WECC_URE3 responded to WECC's data request stating that as part of its year-end review, it determined that it may have been deficient in producing the type of documentation specified by this requirement. During the course of its internal review, WECC_URE3 had realized it failed to document the assessment and implementation of security patches (CIP-007 R3), identify all individuals with access to shared accounts (CIP-007 R5.2.2), and annually review and update security patch management (CIP-007 R9). Furthermore, WECC_URE3 stated it failed to document 24 security patch assessments for the Cyber Assets used in the access control and/or monitoring of ESPs. WECC_URE3 also failed to review and update the security patch assessments because the implementation of the security patches was never documented, there were 15 upgrades applicable during this time period which could not be installed because of memory limitation and therefore the security upgrades could not be installed and the existing compensating measures were not documented. Additionally, WECC_URE3 reported a possible violation related to five firewall accounts used in the access control and/or monitoring of the ESPs, which share the same console, port, username and password. WECC_URE3 failed to identify five individuals with access to the shared firewall accounts used in the access control of the Control Center, backup Control Center, and the facilities. However, WECC_URE3 noted that the shared firewall accounts were changed as soon as the issue was discovered. For these reasons, WECC determined that WECC_URE3 violated CIP-005-3 R1.5. | CIP-005-3 | R1.5 | Medium | Severe | WECC determined that this violation posed a moderate risk to the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. In this instance, WECC_URE3 failed to provide three protective measures to 16 devices used in access control. These devices or Cyber Assets monitor and/or control access to ESPs containing CCAs and are used for network access and management. These 16 devices were located within identified ESPs and PSPs and had protections required by CIP-005 and CIP-006. In addition, Intrusion Detection and Prevention systems are in place at these ESPs. Alerts from these systems are reviewed 24x7 at the security operations center. For these reasons, WECC considered this violation to have a moderate impact on the BPS. | The date WECC_URE3 was required to comply with this Standard | Mitigation Plan completion date | $27,900 (for WECC201102641 and WECC201102639) | Self-Certification | The following actions were completed by WECC_URE3 to mitigate this violation: 1. Network Administrator changed console-port passwords on all cyber assets used in the access control and monitoring of the ESP. 2. At the time of the Password change, WECC_URE3 identified and documented any and all personnel given the password for the console-port. 3. WECC_URE3 developed and documented a policy for managing the use of shared accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes. 4. The shared account policy was communicated to the appropriate WECC_URE3 personnel and management. 5. WECC_URE3 revised the CIP Standards security patch procedure to require specific evidence to track the evaluation and implementation of security patches on the cyber assets used in the access control and monitoring of the ESP. 6. WECC_URE3 communicated the revisions to the CIP Standards security patch procedure to the appropriate WECC_URE3 personnel and management. | 11/17/2011 (Mitigation Plan completion date) | 2012-02-27 | Agrees and Stipulates to the Facts | WECC reviewed WECC_URE3's Internal Compliance Program (ICP) and considered it a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102639 | Settlement Agreement | WECC_URE3 submitted a self-certification addressing noncompliance with CIP-006-1 R1.8. WECC_URE3 reported that as a result of its year-end review, it determined that access and control monitoring (ACM) assets that authorize and/or log access to the PSP were inadvertently excluded from the scope of some of the protections required by this Standard. These assets were used for access control and monitoring of PSPs containing Critical Cyber Assets (CCAs). As a result, WECC_URE3 realized it failed to document a personnel risk assessment (PRA) on two individuals prior to their receiving access to these cyber assets (CIP-004 R3). The ACM assets in scope are WECC_URE3 servers. WECC_URE3 failed to identify all administrators with access to a shared account (CIP-007 R5.2). In addition, WECC_URE3 failed to implement anti-virus and anti-malware prevention tools on the servers panels (CIP-007 R4). WECC_URE3 misinterpreted the phrase "shall use antivirus software or other malware prevention tools" in the Standard not to include the panels. However, because the panels are configured with an IP address and could be reached by assets on the company network, the panels should have anti-virus and anti-malware tools installed. For these reasons, the SME determined that WECC_URE3 has a possible violation of CIP-006-1 R1.8. WECC Enforcement reviewed WECC_URE3's self-certification and the SME's findings and determined that WECC_URE3 is in violation of CIP-006-1 R1.8 from when WECC_URE3 was required to be compliant with this Standard, to Mitigation Plan completion. Failing to provide the required protections to cyber assets used in access control and monitoring is a violation of CIP-006-1 R1.8. Based on the self-certification and the supporting information given, WECC determined that WECC_URE3 violated CIP-006-1 R1.8. This violation spanned multiple versions of CIP-006, and thus included CIP-006-1 R1.8, CIP-006-2 R2.2, and CIP-006-3 R2.2. | CIP-006-1 | R1.8 | Medium | Severe | WECC determined that this violation posed a minimal risk to the bulk power system (BPS) and did not pose a serious or substantial risk to the BPS. Failure to ensure that Cyber Assets used in the access control and monitoring of the PSPs are afforded protective measures puts such assets at risk to be manipulated. Unauthorized access may be used to cause harm to CCAs essential to the operation of the BES, thereby potentially negatively impacting the BES. In this case, WECC_URE3 failed to provide three protective measures to two assets used in access control. These assets were used for access control and monitoring of all PSPs containing CCAs used for Transmission and Generation. As compensating measures, WECC_URE3 stated that Intrusion Detection and Prevention systems are in place at the associated Electronic Security Perimeters. These systems identify, alert, and block malicious communications traffic which creates a "fingerprint" of known harmful packets. In addition, WECC_URE3 has implemented centralized logging, security event correlation, and incident response on a 24 hour, 7 days a week basis. Finally, WECC_URE3 has a vulnerability reporting system in place which scans the covered assets and provides detailed reports about the security posture of such assets including open ports, services, and vulnerabilities of the software residing on the assets. For these reasons, WECC considered this violation to have a minimal impact on the BPS. | The date WECC_URE3 was required to comply with this Standard | Mitigation Plan completion date | $27,900 (for WECC201102641 and WECC201102639) | Self-Certification | The following actions were completed by WECC_URE3 to mitigate this violation: 1) WECC_URE3 isolated the password in the password vault and limited access to the appropriate server administrators via a unique active directory security group. 2) WECC_URE3 submitted a Technical Feasibility Exception to CIP-007-1 R4 for the server panels in scope per CIP-006 R2.2 (CIP-006 R2.2 requires the protections afforded by CIP-007). 3) WECC_URE3 created and/or edited an existing process or procedure to specifically address shared and generic accounts on the server system. 4) WECC_URE3 communicated the new or edited procedure in milestone 2 to all server administrators. | 11/9/2011 (Mitigation Plan completion date) | 2012-02-27 | Agrees and Stipulates to the Facts | WECC reviewed WECC_URE3's Internal Compliance Program (ICP) and considered it a mitigating factor.
2012-02-29 | FERC | NP12-18-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201102661 | Settlement Agreement | WECC_URE4 self-certified a violation of CIP-004-1 R4. WECC_URE4 stated that it failed to list four individuals (two employees, a vendor and a consultant) who had been given access to Critical Cyber Assets (CCAs) on its list of personnel with authorized access to CCAs. WECC determined that WECC_URE4 violated this Standard by failing to include all individuals with access to its CCAs on its list of personnel with authorized access. | CIP-004-1 | R4 | Lower | Lower | This violation posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk to the reliability of the BPS because although WECC_URE4 failed to include four individuals with access to its CCAs on its list of authorized personnel, the four individuals had up-to-date training and Personnel Risk Assessments (PRAs). Also, the consultant helped develop many of the information technology systems in the CCA. The individuals were trained to handle CCAs and their PRAs did not reveal any adverse information. | When the Standard became mandatory and enforceable | When the Mitigation Plan was completed | 2000 | Self-Certification | According to the Mitigation Plan, WECC_URE4 took the following actions: 1) Added the employee who was omitted from the CCA list to its CCAs access list; 2) Added the vendor who was omitted from the CCA list to its access list; 3) WECC_URE4's IT Department added the omitted employee to the IT-maintained CCAs access list; 4) WECC_URE4's IT Department reassessed the consultant's need for access to the CCAs and decided to approve the consultant's access rights to those shared accounts. | 2011-07-11 | 2012-02-28 | Does Not Contest | In its determination to use an Expedited Settlement Agreement and the penalty amount, WECC considered the following factors, among others: 1) The violation posed a minimal risk to the BPS and; 2) There were no aggravating factors.
2012-02-29 | FERC | NP12-12-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100260 | Notice of Confirmed Violation | MRO conducted a CIP Spot Check of MRO_URE1. MRO determined that MRO_URE1 did not provide sufficient evidence reflecting the use of appropriate test procedures to ensure that new Cyber Assets (CAs) and significant changes to CAs within the Electronic Security Perimeter (ESP) do not adversely affect existing cyber security controls. Specifically, MRO_URE1 periodically utilized an intermediate anti-virus server to download anti-virus signature and security patch updates for the CAs within the ESP. MRO_URE1 failed to test the server each time it was reintroduced into the ESP, because it did not consider the anti-virus server to be a "new" CA each time it reconnected to the ESP, and therefore did not have evidence demonstrating that appropriate test procedures had been followed. MRO_URE1 indicated that this violation was due to an insufficient understanding among responsible MRO_URE1 personnel of the criteria for defining and classifying non-critical CAs residing within the ESP. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS). This violation did not pose a serious or substantial risk to the reliability of the bulk power system because: (1) although the introduction of new CAs or the modification of existing CAs without verification that cyber security controls are functioning properly can put many or all Critical Cyber Assets in a given ESP at risk and jeopardize the proper functioning of existing CAs, the intermediate anti-virus server utilized by MRO_URE1 was configured as a hardened, single-purpose device, thus reducing the risk of compromise by malware or other exploits; (2) MRO_URE1 tested anti-malware signatures and security patch updates in a development environment prior to introduction to the ESP; and (3) the intermediate anti-virus server was not connected simultaneously to the ESP and the MRO_URE1 corporate network. | The date MRO_URE1 was required to comply with the Reliability Standard. | Mitigation Plan completion | 4000 | Spot Check | MRO_URE1 submitted a Mitigation Plan to address the violation of CIP-007-1 R1. In accordance with the Mitigation Plan, MRO_URE1: (1) ceased the practice of updating anti-virus signatures using a temporary intermediate anti-virus server; (2) revised the EMS anti-virus signature update process and procedure to eliminate the need to introduce a temporary intermediate anti-virus server into the ESP; and (3) reviewed and confirmed all energy management system (EMS) cyber assets are properly identified and protected. | 2010-12-31 | 2011-09-29 | Admits | MRO considered MRO_URE1's Internal Compliance Program, which was in place at the time of the violation, to be a mitigating factor when determining the penalty amount.
2012-02-29 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000305 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a possible violation of CIP-004-1 R2. RF determined that RFC_URE1 did not ensure that individuals with cyber or unescorted physical access to Critical Cyber Assets (CCAs) received training within 90 calendar days of receiving authorization or annual training, pursuant to CIP-004-1 R2. Six months later, RFC_URE1 provided additional information to supplement the information contained in the first Self-Report and identified another possible violation of the Standard. First, RFC_URE1 did not train 39 individuals within 90 days of granting them access to CCAs, as required by CIP-004-1 R2.1.3. Specifically, RFC_URE1 did not provide the requisite CIP training to 33 of the 39 individuals within 90 days of authorization. Out of the 33 individuals not trained within 90 days: 3 were RFC_URE1 employees with cyber access to CCAs; 12 were RFC_URE1 employees with unescorted physical access to CCAs; two were contractors with cyber access to CCAs; and 16 were contractors with authorized unescorted physical access. In addition, RFC_URE1 did not provide any CIP training to six of the 39 individuals with access to CCAs. One of the six individuals was an RFC_URE1 employee with cyber access to CCAs, three of the six were RFC_URE1 employees with unescorted physical access to CCAs, and two of the six individuals were contractors with unescorted physical access to CCAs. Second, RFC_URE1 did not administer annual CIP training sessions for 183 individuals as required by CIP-004-1 R2.3. Of the 183 individuals: 61 of these individuals were RFC_URE1 employees with cyber access to CCAs; eight were RFC_URE1 employees with both cyber and unescorted physical access to CCAs; 66 were employees with only unescorted physical access to CCAs; and 48 were contractors with unescorted physical access to CCAs. RFC_URE1 identified the cause of this violation as failure to integrate its list of individuals with access to CCAs with its rosters of those individuals requiring CIP training. | CIP-004-1 | R2; R2.1.3; R2.3. | Lower | Lower | This violation posed a moderate risk to the reliability of the bulk power system (BPS) because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. All individuals involved in the violation of CIP-004-1 R2 had successfully completed personnel risk assessments (PRAs) that revealed no criminal history or other identity issues that would have prevented them from receiving CIP qualifications prior to RFC_URE1 granting the individuals at issue access to Critical Cyber Assets (CCAs). Further, all individuals involved in the violation received either CIP training or corporate cyber awareness training in advance of RFC_URE1 granting them access to CCAs. While six of those individuals had not received any of the required CIP training, they did receive corporate cyber awareness training. RFC_URE1’s corporate cyber awareness training, while not a substitute for formal CIP training, includes basic information on cyber risks. Additionally, of the 183 individuals who did not receive annual training pursuant to CIP-004-1 R2.3, 54 of the individuals with cyber access had read-only access and could not effect a change in the Energy Management System. The remaining 15 individuals with cyber access had all completed initial CIP training, but did not undergo timely annual training. The remaining 122 individuals with physical access who had not received annual training pursuant to CIP-004-1 R2.3 all had previously completed either CIP training or RFC_URE1’s corporate cyber awareness training. Of the total employees and contractors with access to RFC_URE1 CCAs, less than 5% were involved in the violation of CIP-004-1 R2.1. The violation of CIP-004-1 R2.3 involved less than 5% of the total training sessions RFC_URE1 has administered in a 34-month period. | Effective date of the Standard | Mitigation Plan completion | $25,000 (for RFC201000305; RFC201000662; RFC201000306; RFC201100774; RFC201100775; and RFC201100999) | Self-Report | RFC_URE1 separated CIP training from corporate cyber awareness training in order to create a clearer delineation between courses. RFC_URE1 updated its database, which now prevents RFC_URE1 personnel from granting access to CCAs unless a current CIP training date is provided. RFC_URE1 also took direct control over administering CIP training for contractors. Prior to this mitigating action, RFC_URE1 believed its contractors provide RFC_URE1-approved CCA training to their (non-RFC_URE1) employees. Additionally, RFC_URE1 improved its process by developing training lists which will integrate RFC_URE1’s Energy Management System cyber access with its physical access lists. The integration of these two lists allows RFC_URE1 to determine which individuals require CIP training and by what deadline. The integration of these two lists allows RFC_URE1 to determine which individuals require CIP training and by what deadline. | 2011-05-06 | 2011-06-09 | Agrees/ Stipulates | In assessing the penalty, RF favorably considered certain aspects of RFC_URE1’s compliance program. RF also favorably considered that RFC_URE1 now has a single work flow system to grant or remove access to CCAs, as well as manage employee or contractor transfers and separations in order to improve compliance with the Standard. The system also validates CIP training and PRA dates for individuals requesting access to CCAs prior to submitting the access requests to managers for final approval.
2012-02-29 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000662 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a possible violation of CIP-004-1 R3. RF determined that RFC_URE1 violated CIP-004-1 R3 when it did not perform initial personnel risk assessments (PRAs) or updated PRAs for a total of 109 individuals with cyber or unescorted physical access to Critical Cyber Assets (CCAs). RFC_URE1 discovered that 109 individuals did not undergo an initial PRA or receive an updated PRA, as required by CIP-004-1 R3 and CIP-004-1 R3.2. Specifically, RFC_URE1 determined that 107 individuals did not have an initial PRA within 30 days from the date RFC_URE1 granted them access to CCAs, as required by CIP-004-1 R3. Out of the 107 individuals: 52 were RFC_URE1 employees with cyber access to CCAs; 38 were RFC_URE1 employees with unescorted physical access to CCAs; and 17 were contractors with physical access to CCAs. Of the 52 individuals with cyber access, none had cyber access to CCAs located at the system control center. Three of the individuals with physical access had access to CCAs located at the system control center. Additionally, RFC_URE1 did not perform an updated PRA for two RFC_URE1 employees within seven years of their previous PRAs as required by CIP-004-1 R3.2. RFC_URE1 previously granted these two employees unescorted physical access to CCAs. RFC_URE1 identified the cause of this violation as insufficient monitoring of the process for updating PRAs and incomplete PRA document maintenance. RFC_URE1 noted that it granted 100 of the 109 individuals at issue access to CCAs prior to CIP-004-1 R2’s mandatory compliance date and identified this as a contributing factor to this violation. | CIP-004-1 | R3; R3.2 | Medium | High | This violation posed a moderate risk to the reliability of the bulk power system (BPS) because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. The 52 individuals with cyber access and missing PRAs had read-only access and could not effect a change to the Energy Management System. Additionally, the location to which 57 of the individuals had unescorted physical access is staffed and monitored 24 hours a day, seven days a week. In addition, the location has procedural controls for monitoring physical access at all access points that uniquely identifies the individuals involved and records when the individuals accessed the location. | Effective date of the Standard | Mitigation Plan completion | $25,000 (for RFC201000305; RFC201000662; RFC201000306; RFC201100774; RFC201100775; and RFC201100999) | Self-Report | Internal maintenance of PRAs was centralized over one year before the mandatory compliance date of the Standard. At that point, the corporate Human Resources group began collection and storage of all PRAs in an internal electronic database. With this centralization, the risk of misplaced PRAs has been reduced. As discussed in the last column, a system to improve compliance with the Standard is implemented. As all access to CCAs is now centralized, the reporting capabilities that will result from the implementation of this project allows RFC_URE1 to receive alerts of impending expirations of PRAs. Additionally, current PRA dates are automatically available though the integration with other systems. This provides RFC_URE1 with a more comprehensive, proactive approach to the management of PRAs and ensures that future lapses do not occur. | 2011-05-06 | 2011-06-09 | Agrees/ Stipulates | In assessing the penalty, RF favorably considered certain aspects of RFC_URE1’s compliance program. RF also favorably considered that RFC_URE1 now has a single work flow system to grant or remove access to CCAs, as well as manage employee or contractor transfers and separations in order to improve compliance with the Standard. The system also validates CIP training and PRA dates for individuals requesting access to CCAs prior to submitting the access requests to managers for final approval.
2012-02-29 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000306 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a possible violation of CIP-004-1 R4. RF determined that RFC_URE1 violated the Standard by not maintaining its Critical Cyber Assets (CCAs) access list, not reviewing its CCA access list on a quarterly basis beginning on the effective compliance date, and not removing 67 individuals who no longer required access to the CCAs from its CCA access lists within the required timeframes. This violation includes three separate issues, all of which of involved CIP-004-1 R4. First, during a quarterly review conducted for the period 18 months after the effective compliance enforcement date, RFC_URE1 determined that 105 individuals (85 RFC_URE1 employees and 20 contractors) had unescorted physical access to CCAs without evidence that RFC_URE1 had granted them access at a prior date. None of the 105 individuals had physical access to CCAs located at the system control center. This quarterly review was the first during which RFC_URE1 compared its paper-based CCA access list to its database access list. RFC_URE1 could not locate original documentation from its paper-based process to demonstrate it previously granted physical access to the 105 individuals. Therefore, RFC_URE1 did not maintain a list of authorized personnel, as required by CIP-004-1 R4. Second, RFC_URE1 did not perform reviews of its physical access lists for CCAs during the required first twelve months of mandatory compliance. Pursuant to the CIP Implementation Plan promulgated by NERC, RFC_URE1 was not required to implement CIP-006-1, which requires RFC_URE1 to create and maintain a physical security plan for access points to CCA, until a year after the effective compliance date of CIP-004-1. RFC_URE1 incorrectly concluded, based on its understanding of CIP-006-1, that it therefore did not have to conduct quarterly reviews of its access lists pursuant to CIP-004-1 R4.1 until CIP-006-1's effective compliance date; however, RFC_URE1 was required to review its physical access lists on a quarterly basis beginning one year prior, and therefore did not comply with CIP-004-1 R4.1. Finally, RFC_URE1 discovered that for a 22-month period, it did not revoke cyber or physical access to CCAs for 67 individuals within the required timeframe pursuant to CIP-004-1 R4.1 and R4.2. Specifically, 55 of the 67 individuals resigned but RFC_URE1 did not revoke their access within seven calendar days. Also, RFC_URE1 transferred nine of the 67 individuals to positions that did not require access to CCAs but did not revoke their access within seven calendar days. The remaining three individuals were terminated for cause, but RFC_URE1 did not revoke their access to CCAs within 24 hours, as required by CIP-004-1 R4.2. Regarding the third issue, 41 occurrences involved resignation or transfers for which RFC_URE1 cannot locate any documented evidence that it revoked access. Seventeen occurrences involved an RFC_URE1 supervisor who did not notify appropriate staff within seven days that the individuals no longer needed access to the CCAs. Six occurrences involved human error in which RFC_URE1 staff did not notify necessary personnel of a revocation within the seven day time period. As to the individuals terminated for cause, RFC_URE1 personnel did not notify appropriate staff necessary to effectuate revocation of these individuals’ access within the required 24-hour timeframe. The employees terminated for cause remained on the access list 81, 20 and 70 days in excess of the 24-hour timeframe, respectively. | CIP-004-1 | R4; R4.1; R4.2 | Medium | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. RFC_URE1 performed CIP training and personnel risk assessments (PRAs) for the 105 individuals with access to RFC_URE1’s CCAs, but for whom RFC_URE1 could not produce evidence of authorized access. Additionally, for the instances where RFC_URE1 did not revoke CCA access from individuals who resigned, were transferred, or terminated for cause, RFC_URE1 confirmed that 64 of the 67 individuals did not access the CCAs beyond the prescribed time period. In the three instances in which individuals may have accessed CCAs, the individuals had read-only access and therefore could not modify any CCAs. These individuals were not the same three individuals that were terminated for cause. These three individuals were transferred or rehired and remain employees of RFC_URE1. | Effective date of the Standard | Date RFC_URE1 revoked access rights to CCAs for individuals who had either resigned, were transferred, or were terminated for cause and had incorrectly remained on RFC_URE1's access list | $25,000 (for RFC201000305; RFC201000662; RFC201000306; RFC201100774; RFC201100775; and RFC201100999) | Self-Report | RFC_URE1 implemented a project to reinforce the timeliness of initiating the personnel change process. In this program, RFC_URE1 implemented a system of checklists to provide consistent steps for transfers and terminations of employees with access to CCAs. This system helps ensure RFC_URE1 removes access to CCAs within the proper time period. Additionally, RFC_URE1 implemented targeted training with management level individuals to help ensure those involved in terminations and transfers are properly trained regarding the relevant requirements and time frames pursuant to CIP-004-1 R4. | 2011-05-06 | 2011-06-09 | Agrees/ Stipulates | In assessing the penalty, RF favorably considered certain aspects of RFC_URE1’s compliance program. RF also favorably considered that RFC_URE1 now has a single work flow system to grant or remove access to CCAs, as well as manage employee or contractor transfers and separations in order to improve compliance with the Standard. The system also validates CIP training and PRA dates for individuals requesting access to CCAs prior to submitting the access requests to managers for final approval.
2012-02-29 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100774 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a possible violation of CIP-007-2 R4. RF determined that RFC_URE1 was in violation of the Standard for failing to use anti-virus software and other malware prevention tools or implement and document compensating measures on three Critical Cyber Assets (CCAs) within its Electronic Security Perimeter in violation of CIP-007-2 R4. RFC_URE1 discovered it was not using anti-virus software and other malware prevention tools on three CCAs pursuant to CIP-007-2 R4. None of the three CCAs had an ability to control bulk power system (BPS) facilities. The CCAs were incapable of using anti-virus software and other malware prevention tools, but RFC_URE1 never submitted a Technical Feasibility Exception (TFE) request to RF for the three CCAs at issue. RFC_URE1 incorrectly categorized one CCA on the RFC_URE1 CCA list as a server, rather than an appliance based on an operating system. Due to this error, RFC_URE1 did not create a TFE request for this CCA. RFC_URE1 did not submit TFE requests for the remaining two CCAs because it did not account for the two CCAs while reviewing its CCA list. RF determined that RFC_URE1 did not use anti-virus software and other malware prevention tools or implement and document compensating measures on three CCAs within its Electronic Security Perimeter in violation of CIP-007-2 R4. | CIP-007-2 | R4 | Medium | Severe | This violation posed a moderate risk to the reliability of the BPS because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. RFC_URE1 kept all three CCAs in physically protected locations at all times during the duration of the violation. Also, although it was technically infeasible for RFC_URE1 to employ malware prevention tools on the CCAs, RFC_URE1 did have multiple layers of defenses in place during the duration of the violation to reduce the CCA’s risk of exposure to malware. These included, but were not limited to: perimeter defenses such as firewalls and logging; network defenses such as intrusion detection and prevention software; host defenses such as firewalls and malware on other assets; and procedural controls such as cyber policies and procedures. | Deadline for submitting timely TFEs for the three CCAs at issue | Date RFC_URE1 removed the last of the three CCAs from its system | $25,000 (for RFC201000305; RFC201000662; RFC201000306; RFC201100774; RFC201100775; and RFC201100999) | Self-Report | RFC_URE1's corporate entity removed the three CCAs as RFC_URE1 CCAs from its network. Since the devices are no longer CCAs, they are no longer subject to mandatory compliance with CIP-007-2 R4. | 2010-11-17 | 2012-01-11 | Agrees/ Stipulates | In assessing the penalty, RF favorably considered certain aspects of RFC_URE1’s compliance program. RF also favorably considered that RFC_URE1 now has a single work flow system to grant or remove access to CCAs, as well as manage employee or contractor transfers and separations in order to improve compliance with the Standard. The system also validates CIP training and personnel risk assessment dates for individuals requesting access to CCAs prior to submitting the access requests to managers for final approval.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100775 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a possible violation of CIP-007-2 R5.3. This Self-Report identified two separate issues, both of which involved CIP-007-2 R5.3. RF determined that RFC_URE1 was in violation of the Standard as it did not use, and change within the required timeframe, passwords that met the specifications of CIP-007-2 R5.3. First, RFC_URE1 determined three Critical Cyber Assets (CCAs), although capable of processing passwords, were incapable of processing complex passwords such as those required by CIP 007-2 R5.3.1 and R5.3.2. The three CCAs at issue in this violation are the same CCAs associated with the CIP-007-2 R4.1 violation. RFC_URE1 never submitted TFE requests for the three CCAs at issue. Second, RFC_URE1 did not update 91 shared account passwords associated with the three CCAs at issue within the annual timeframe as required by CIP-007-2 R5.3.3. RFC_URE1 did not change the passwords due to insufficient controls to validate that it changed all shared account passwords annually. | CIP-007-2 | R5; R5.3 | Lower | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. RFC_URE1 kept all three CCAs in physically protected locations at all times during the duration of the violation. Also, although it was technically infeasible for RFC_URE1 to require and use passwords subject to the requirements found in CIP-007-2 R5.3’s sub-requirements for the three CCAs, RFC_URE1 had multiple layers of defenses in place to protect the CCAs during the duration of the violation. These defenses included, but were not limited to: perimeter defenses such as firewalls and logging; network defenses such as intrusion detection and prevention software; host defenses such as firewalls and malware on other assets; and procedural controls such as cyber policies and procedures. | Deadline for submitting timely TFEs for the three CCAs at issue | Date RFC_URE1 removed the last of the three CCAs from its system | $25,000 (for RFC201000305; RFC201000662; RFC201000306; RFC201100774; RFC201100775; and RFC201100999) | Self-Report | RFC_URE1's corporate entity removed the three CCAs as RFC_URE1 CCAs from its network. RFC_URE1 also executed password changes for 90 of the 91 passwords and permanently disabled the remaining account. RFC_URE1 also updated and instituted procedures to improve process controls related to password changes. | 2010-11-17 | 2011-08-03 | Agrees/ Stipulates | In assessing the penalty, RF favorably considered certain aspects of RFC_URE1’s compliance program. RF also favorably considered that RFC_URE1 now has a single work flow system to grant or remove access to CCAs, as well as manage employee or contractor transfers and separations in order to improve compliance with the Standard. The system also validates CIP training and personnel risk assessment dates for individuals requesting access to CCAs prior to submitting the access requests to managers for final approval.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100999 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF identifying a violation of CIP-007-3 R6. During a review of historical logs, RFC_URE1 discovered that it was missing the log records for a 41-day period for one Cyber Asset within its Electronic Security Perimeter (ESP). The Cyber Asset at issue is installed on host servers that are Critical Cyber Assets (CCAs) and part of the Energy Management System. The Cyber Asset allows multiple operating systems to function concurrently on the host servers. The violation was caused by an error-handling routine that created a number of log files, but which eliminated the oldest logs, some of which were less than 90 days old. RF determined RFC_URE1 violated the Standard by failing to retain the logs specific to the Cyber Asset within its ESP for ninety calendar days pursuant to CIP-007-3 R6.4. Further, RF determined that because RFC_URE1 could not locate the logs for one Cyber Asset within its ESP, it was incapable of reviewing all the logs of system events related to cyber security and therefore did not comply with CIP-007-3 R6.5. | CIP-007-3 | R6; R6.4; R6.5 | Lower | Severe | This violation posed a moderate risk to the reliability of the bulk power system (BPS) because of the nature of the violation, offset by the mitigating factors. This violation did not pose a serious or substantial risk to the reliability of the BPS because the risk was mitigated by the following factors. The Cyber Asset at issue is physically located within PSPs. Further, the purpose of the Cyber Asset is to manage operating systems within a host server and as such, the Cyber Asset provides no ability to control BPS facilities. | First date which RFC_URE1 did not have historical logs for the Cyber Asset at issue | Last date for which RFC_URE1 was missing historical logs for the Cyber Asset at issue | $25,000 (for RFC201000305; RFC201000662; RFC201000306; RFC201100774; RFC201100775; and RFC201100999) | Self-Report | RFC_URE1 implemented an automated log storage process that automatically stores any local event log files for the device on an existing CIP log server and subsequently scans each event for potential incidents. Additionally, RFC_URE1 set logs for a minimum retention period of 90 days. Last, the entity's corporate office completed an extent of condition evaluation to identify possible similar deficiencies for its affiliate CCAs. | 2011-12-15 | 2012-01-31 | Agrees/ Stipulates | In assessing the penalty, RF favorably considered certain aspects of RFC_URE1’s compliance program. RF also favorably considered that RFC_URE1 now has a single work flow system to grant or remove access to CCAs, as well as manage employee or contractor transfers and separations in order to improve compliance with the Standard. The system also validates CIP training and personnel risk assessment dates for individuals requesting access to CCAs prior to submitting the access requests to managers for final approval.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000646 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst identifying a possible violation of CIP-004-1 R4. During a quarterly review, RFC_URE2 determined that unescorted physical access to its system given to some personnel was not documented, in violation of the Standard. The group consisted of 64 individuals - 60 employees and 4 contractors. RFC_URE2 conducted quarterly reviews; however, this quarterly review was the first during which RFC_URE2 compared its paper-based CCA access list to its CIP access database system. RFC_URE2 could not locate evidence for the 64 individuals through its paper-based process or in its CIP access database system access list to demonstrate that RFC_URE2 previously authorized physical access to the 64 individuals at issue. ReliabilityFirst determined that RFC_URE2 violated CIP-004-1 R4 for failing to maintain its CCA access list for 64 individuals. | CIP-004-1 | R4 | Lower | Lower | ReliabilityFirst determined that this violation posed a moderate and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the is a collection of Critical Cyber Assets (CCAs) with the ability to monitor the parent company's power plants allowing for limited control over power levels. At no time did any unqualified, unauthorized individuals have the ability to use the system to monitor or control any of the parent company's power plants. Of the 64 individuals at issue in this violation, 54 had no logical access to the system. The remaining ten individuals were qualified for logical access to the system. RFC_URE2 granted these ten individuals authorized cyber access to the system prior to the violation. All 64 individuals that had unescorted physical access completed CIP training prior to the violation. Additionally, RFC_URE2 conducted personnel risk assessments (PRAs) for 63 of the 64 of the individuals prior to the violation. None of the PRAs revealed any criminal history or other identity issues that would have prevented the employees’ CIP qualification. The PRA for the employee who did not have one performed prior to the violation revealed no criminal history or other identity issues that would have prevented the employee’s CIP qualification. | When Standard became mandatory and enforceable | When RFC_URE2 either revoked physical access or properly granted unescorted physical access rights to its CCAs for each of the 64 individuals at issue | $7,500 (for RFC201000646 and RFC2011001073) | Self-Report | RFC_URE2 states that upon discovery, it either removed the individuals’ physical access to the CCAs or granted unescorted physical access to the individuals through its CIP access database system. RFC_URE2 completed its total conversion from the paper-based system for granting physical access to the CIP access database system. RFC_URE2 will also use automated systems to collect and document the access rights granted to CCAs. | 2011-05-06 | 2011-11-07 | Agrees/ Stipulates | ReliabilityFirst favorably considered certain aspects of RFC_URE2’s compliance program. ReliabilityFirst also gave Self-Reporting credit for RFC_URE2.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2011001073 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst in its response to a Request for Information issued by ReliabilityFirst in relation to a violation of CIP-004-1 R4. RFC_URE2 could not provide evidence that it conducted a Personnel Risk Assessment (PRA) for one employee within thirty days of that employee having physical access to Critical Cyber Assets (CCAs). ReliabilityFirst determined that RFC_URE2 violated CIP-004-1 R3 when it could not provide evidence it conducted a PRA for an employee within thirty days of that employee having physical access to CCAs. | CIP-004-1 | R3 | Medium | High | ReliabilityFirst determined that this violation posed a moderate and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the system is a collection of Critical Cyber Assets (CCAs) with the ability to monitor the parent company's power plants allowing for limited control over power levels. Further, RFC_URE2 did not report this alleged violation as part of its initial self report. Rather, RFC_URE2 discovered the violation several months later while compiling responses to a formal Request for Information from ReliabilityFirst concerning the self reported violation of CIP-004. At no time did any unqualified, unauthorized individuals have the ability to use the system to monitor or control any of the parent company's power plants. The employee completed CIP training prior to the violation. Further, RFC_URE2 removed the employee’s physical access rights. Also, when RFC_URE2 conducted a PRA for the employee, it revealed no criminal history or other identity issues that would have prevented the employee’s CIP qualification. Finally, RFC_URE2 examined the access logs and determined that although the employee had unescorted physical access rights, the employee did not actually access any RFC_URE2 physical security perimeters during the duration of the violation. | When Standard became mandatory and enforceable | When RFC_URE2 removed the employee's physical access rights to CCAs | $7,500 (for RFC201000646 and RFC2011001073) | Self-Report | RFC_URE2 did not submit a separate Mitigation Plan for this violation. ReliabilityFirst determined that the Mitigation Plan for RFC201000646, contained the mitigating activities necessary to resolve the violation of CIP-004-1 R3. RFC_URE2 states that upon discovery, it either removed the individuals’ physical access to the CCAs or granted unescorted physical access to the individuals through its CIP access database system. As part of this process, RFC_URE2 removed the physical access rights of the employee at issue. | 2011-05-06 | 2011-11-07 | Agrees/ Stipulates | ReliabilityFirst favorably considered certain aspects of RFC_URE2’s compliance program. ReliabilityFirst also gave Self-Reporting credit for RFC_URE2.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) RFC_URE3a, RFC_URE3b and RFC_URE3c are subsidiaries of a single parent company, collectively known as the RFC_UREs | NCRXXXXX | RFC201000440 | Settlement Agreement | The RFC_UREs submitted Self-Reports to ReliabilityFirst identifying possible violations of CIP-004-1 R4. During an internal audit, the RFC_UREs discovered that they failed to review their access lists of personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) quarterly, in violation of CIP-004-1 R4.1. The RFC_UREs failed to revoke authorized cyber or authorized unescorted physical access to CCAs for 23 individuals in a timely manner, a violation of CIP-004-1 R.4.2. As a result, the RFC_UREs failed to timely update the access lists within seven calendar days to reflect these access right changes, a violation of CIP-004-1 R4.1. Specifically, RFC_URE3a failed to revoke the access of five individuals who no longer required such access within seven calendar days. The CCAs at issue at RFC_URE3a were transmission assets. | CIP-004-1 | R4; R4.1;R4.2 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because all physical access locations are controlled areas requiring card key access and are staffed or monitored using alarm systems and video at all times. All individuals at issue in the violations received the requisite personnel risk assessments and NERC CIP training. In addition, all RFC_URE3a individuals were transferred within the RFC_UREs and were employees in good standing at the time. Lastly, for all individuals whose access was not timely revoked, there were no attempts to access CCAs prior to the revocation of access. | Date access should have been revoked in first instance | Date access was revoked and interim process for access review implemented | $15,000 (for RFC201000440, RFC201000441, and RFC201000442) | Self-Report | In the Mitigation Plan, RFC_UREs memorialized the actions they took to address CIP-004-1 R4, including inter alia, an extensive root cause investigation across the RFC_UREs. A full review of all CIP-004 policies and procedures and subsequent changes to add rigor to the program was performed. Revisions to training for all authorizers and performers responsible for assuring CIP-004 compliance were added, including the addition of an annual requirement. A task force for routine assessments of some of the key tools used to implement the program was also created. | 2/29/2012 (Approved Date) | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of the RFC_UREs’ compliance program as mitigating factors. In addition, ReliabilityFirst also considered the quick response by the RFC_UREs to the identification of the incidents, the implementation of immediate remediation actions including interim processes consisting of significant manual controls and levels of cross-checks, the dedication of a cross-functional team to a full investigation of the entire CIP-004 program and the subsequent development and implementation of a comprehensive mitigation plan.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) RFC_URE3a, RFC_URE3b and RFC_URE3c are subsidiaries of a single parent company, collectively known as the RFC_UREs | NCRXXXXX | RFC201000441 | Settlement Agreement | The RFC_UREs submitted Self-Reports to ReliabilityFirst identifying possible violations of CIP-004-1 R4. During an internal audit, the RFC_UREs discovered that they failed to review their access lists of personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) quarterly, in violation of CIP-004-1 R4.1. The RFC_UREs failed to revoke authorized cyber or authorized unescorted physical access to CCAs for 23 individuals in a timely manner, a violation of CIP-004-1 R.4.2. As a result, the RFC_UREs failed to timely update the access lists within seven calendar days to reflect these access right changes, a violation of CIP-004-1 R4.1. Specifically, RFC_URE3b failed to revoke the access of seven individuals who no longer required such access within seven calendar days. The CCAs at issue at RFC_URE3b were transmission assets. | CIP-004-1 | R4; R4.1;R4.2 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because all physical access locations are controlled areas requiring card key access and are staffed or monitored using alarm systems and video at all times. All individuals at issue in the violations received the requisite personnel risk assessments and NERC CIP training. In addition, only one of the RFC_URE3b individuals was terminated (not for cause); all remaining individuals were transferred within the RFC_UREs and were employees in good standing at the time. The terminated individual’s employee badge key card used for physical access was confiscated and disabled along with the employee’s computer network logins upon termination. Lastly, for all individuals whose access was not timely revoked, there were no attempts to access CCAs prior to the revocation of access. | Date access should have been revoked | Date access was revoked and interim process for access review implemented | $15,000 (for RFC201000440, RFC201000441, and RFC201000442) | Self-Report | In the Mitigation Plan, RFC_UREs memorialized the actions they took to address CIP-004-1 R4, including inter alia, an extensive root cause investigation across the RFC_UREs. A full review of all CIP-004 policies and procedures and subsequent changes to add rigor to the program was performed. Revisions to training for all authorizers and performers responsible for assuring CIP-004 compliance were added, including the addition of an annual requirement. A task force for routine assessments of some of the key tools used to implement the program was also created. | 2/29/2012 (Approved Date) | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of the RFC_UREs’ compliance program as mitigating factors. In addition, ReliabilityFirst also considered the quick response by the RFC_UREs to the identification of the incidents, the implementation of immediate remediation actions including interim processes consisting of significant manual controls and levels of cross-checks, the dedication of a cross-functional team to a full investigation of the entire CIP-004 program and the subsequent development and implementation of a comprehensive mitigation plan.
2012-01-31 | FERC | NP12-12-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) RFC_URE3a, RFC_URE3b and RFC_URE3c are subsidiaries of a single parent company, collectively known as the RFC_UREs | NCRXXXXX | RFC201000442 | Settlement Agreement | The RFC_UREs submitted Self-Reports to ReliabilityFirst identifying possible violations of CIP-004-1 R4. During an internal audit, the RFC_UREs discovered that they failed to review their access lists of personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) quarterly, in violation of CIP-004-1 R4.1. The RFC_UREs failed to revoke authorized cyber or authorized unescorted physical access to CCAs for 23 individuals in a timely manner, a violation of CIP-004-1 R.4.2. As a result, the RFC_UREs failed to timely update the access lists within seven calendar days to reflect these access right changes, a violation of CIP-004-1 R4.1. Specifically, RFC_URE3c failed to revoke the access of eleven individuals who no longer required such access within seven calendar days. The CCAs at issue at RFC_URE3c were generation assets. | CIP-004-1 | R4; R4.1;R4.2 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because all physical access locations are controlled areas requiring card key access and are staffed or monitored using alarm systems and video at all times. All individuals at issue in the violations received the requisite personnel risk assessments and NERC CIP training. In addition, all RFC_URE3c individuals were transferred within the Exelon Companies and were employees in good standing at the time. Lastly, for all individuals whose access was not timely revoked, there were no attempts to access CCAs prior to the revocation of access. | Date access should have been revoked | Date access was revoked and interim process for access review implemented | $15,000 (for RFC201000440, RFC201000441, and RFC201000442) | Self-Report | In the Mitigation Plan, RFC_UREs memorialized the actions they took to address CIP-004-1 R4, including inter alia, an extensive root cause investigation across the RFC_UREs. A full review of all CIP-004 policies and procedures and subsequent changes to add rigor to the program was performed. Revisions to training for all authorizers and performers responsible for assuring CIP-004 compliance were added, including the addition of an annual requirement. A task force for routine assessments of some of the key tools used to implement the program was also created. | 2/29/2012 (Approved Date) | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of the RFC_UREs’ compliance program as mitigating factors. In addition, ReliabilityFirst also considered the quick response by the RFC_UREs to the identification of the incidents, the implementation of immediate remediation actions including interim processes consisting of significant manual controls and levels of cross-checks, the dedication of a cross-functional team to a full investigation of the entire CIP-004 program and the subsequent development and implementation of a comprehensive mitigation plan.
2012-01-31 | FERC | NP12-12-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000136 | Settlement Agreement | Six months after the mandatory compliance enforcement date, Texas RE_URE1 determined that it did not make its cyber security policy readily available to contractors with access to, or responsibility for, Critical Cyber Assets (CCAs) in another reliability region. As a result of an extended investigation, Texas RE_URE1 determined that the same issue existed in the Texas RE region and self-reported a violation of CIP-003-1 R1. The cyber security policy was not made available to contractors, which make up 6.7 percent of employees. None of the contractors were actually responsible for CCAs. The policy was readily available to the remaining 93.3 percent of permanent employees. | CIP-003-1 | R1; R1.2 | Lower | Severe | This violation posed a minimal risk to the reliability of the bulk power system (BPS). The violation did not pose a serious or substantial risk to the BPS because Texas RE_URE1 failed to make the cyber security policy available to only a small percentage (6.7%) of employees (all the contractors). The policy was readily available to permanent employees. Second, there were no compromises, or attempts to compromise, the Electronic Security Perimeter or Physical Security Perimeter of a CCA during the period of the violation. Further, there were no disruptions or attempts to disrupt the operation of a CCA during the period of the violation. | The date the requirement became enforceable for the entity | Mitigation Plan completion | 9000 | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to address the violation of CIP-003-1 R1. In accordance with the Mitigation Plan, Texas RE_URE1 conducted two main activities. First, Texas RE_URE1 mailed a copy of the cyber security policy to each contractor with remote authorized cyber access. Second, Texas RE_URE1 placed a copy of the cyber security policy at a central location of each Critical Asset within the Texas RE region and explained on the Physical Security Perimeters’ sign-in, sign out logs the availability of the cyber security policy. | 2010-09-01 | 2011-05-31 | Admits | Texas RE considered that Texas RE_URE1 had an internal compliance program, in place at the time of the violation, as a mitigating factor when determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002604 | Settlement Agreement | WECC_URE1 self-reported a violation of regional standard BAL-004-WECC-01 R4.4. WECC_URE1 stated that it failed to synchronize its Time Error to the nearest 0.001 seconds of the System Time Error by comparing its reading to the reading broadcast by the Interconnection Time Monitor. WECC_URE1 failed to inform its Energy Management System (EMS) personnel of the requirement to obtain this daily time error value. Also, WECC_URE1 failed to synchronize its time error daily value with the value issued by the WECC Reliability Coordinator (WECC RC). In response to a WECC information request, WECC_URE1 stated that the lapse was due to internal communication error and the notification was misplaced. WECC_URE1's support staff became aware of the issue and immediately implemented the daily synchronization. Based on the record, WECC determined that WECC_URE1 failed to synchronize its time error, in violation of this Standard. | BAL-004-WECC-01 | R4.4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE1 failed to synchronize its daily Time Error with the WECC RC, it did compute its hourly Primary Inadvertent Interchange value, which is used to calculate the Automatic Time Error Correction and maintain the reliability of the BPS. Also, because the hourly time error was synchronized, WECC_URE1's failure to synchronize daily the Time Error value did not affect the scheduled flow of energy needed in real time to support demand, and therefore posed a minimal risk to the reliability of the BPS. | The date WECC_URE1 was required to comply with this Standard | When WECC_URE1 began performing the required daily Time Error checks | $45,000 (for WECC201002604, WECC201102807, WECC201102599, WECC201102609, WECC201102606, WECC201102613, and WECC200901475) | Self-Report | WECC_URE1 submitted a Mitigation Plan, stating an automated Supervisory Control and Data Acquisition Systems (SCADA) calculation was implemented, which triggers the receipt of the WECC RC Time Error every day, calculates the difference between the required time values, and documents it in WECC_URE1's system. | 2010-12-15 | 2011-11-16 | Agrees/ Stipulates | WECC reviewed WECC_URE1's Internal Compliance Program and considered it a mitigating factor in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102807 | Settlement Agreement | WECC_URE1 submitted a Self-Report for noncompliance with CIP-004-1 R2, stating that in preparation of its Audit, it discovered some discrepancies in its training records. WECC_URE1 failed to ensure that all personnel having access to Critical Cyber Assets (CCAs), including contractors and vendors, are trained prior to being granted such access, except in specified circumstances such as an emergency. Also, WECC_URE1 failed to maintain documentation that training is conducted at least annually, and did not keep a record of the date training was completed and a record of attendance. WECC determined that one individual did not receive training prior to receiving access to the CCAs and four employees did not receive annual training. Based on the record, WECC determined that WECC_URE1 violated CIP-004-1 R2.1 for failure to ensure that all individuals with access to the CCAs are trained prior to being granted such access, and violated CIP-004-1 R2.3 for failure to maintain documentation that training was completed at least annually. | CIP-004-1 | R2.1/R2.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE1 failed to ensure proper training and maintain documentation related to employee training, the individuals in scope had current Personnel Risk Assessments (PRAs) and their electronic access was read-only. Also, the individuals had access to six Physical Security Perimeters (PSPs) and one Electronic Security Perimeter (ESP) which contain CCAs, but the PSPs and the ESP have logging and monitoring systems in place. Therefore, WECC determined that this violation had a minimal impact on the reliability of the BPS. | When WECC_URE1 failed to implement its annual training program | When WECC_URE1 completed its Mitigation Plan | $45,000 (for WECC201002604, WECC201102807, WECC201102599, WECC201102609, WECC201102606, WECC201102613, and WECC200901475) | Self-Report | WECC_URE1 submitted a Mitigation Plan, stating that it completed the following actions: 1) trained all individuals who lacked initial or annual training; 2) revoked access for individuals who no longer required access; 3) updated its procedures for training newly-hired employees; 4) updated its procedures to conduct annual training for all employees once a year regardless of the original training date; 5) consolidated two training sessions into a single training each year; and 6) trained process members of new procedures. | 2011-05-13 | 2011-09-01 | Agrees/ Stipulates | WECC reviewed WECC_URE1's Internal Compliance Program and considered it a mitigating factor in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102599 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating the semi-annual Self-Certification process. WECC_URE1 submitted a Self-Certification. WECC_URE1 self-reported a violation of CIP-006-1 R1, stating that it failed to ensure Cyber Assets used in the Access Control and Monitoring (ACM) of the Physical Security Perimeters (PSPs) were afforded all the protections specified in CIP-006-1 R1.8. WECC performed an on-site Audit, which included compliance with CIP-006-1 R1.8, and determined that WECC_URE1 failed to ensure that Cyber Assets used in the ACM of the PSPs were afforded the protective measures specified in CIP-005 R3 (WECC_URE1 has five switches which are electronic access points to seven physical ACM controllers, these switches were not configured to send syslogs to the WECC_URE1's syslog server; therefore, alerts generated from these controllers were not able to appropriately notify designated personnel), CIP-007 R3 (WECC_URE1 failed to document an assessment for applicability of security patches within 30 days of the patch being made available for three physical ACM devices and WECC_URE1 failed to document an assessment of security patches for sixteen Cyber Assets (switches) located in the Electronic Security Perimeters (ESPs) and for five devices used in the access control and monitoring of the ESPs), and CIP-009 R4 and R5 (WECC_URE1 failed to include the backup and restore procedures for seven physical ACM control panels in its Recovery Plan, which are used to store access control authentication data for the card readers and WECC_URE1 failed to follow its documented procedure of documenting annual testing of information essential to recovery that is stored on backup media; specifically, testing was done but documentation was not completed to demonstrate compliance), in violation of CIP-006-1 R1.8. | CIP-006-1 (the violation involves later versions of this standard--CIP-006-2 R2.2 and CIP-006-3 R2.2) | R1.8 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because there were several compensating measures in place to mitigate the risk. First, WECC_URE1 stated that only personnel with current training and Personnel Risk Assessments (PRAs) had access to the devices in question. Also, WECC_URE1's server was equipped with anti-virus and malware protection tools, and was also located within a Physical Security Perimeter (PSP) and secured by a firewall. The seven controllers associated with noncompliance with CIP-009 R4 were located in physically secured rooms. | The date WECC_URE1 was required to comply with this Standard | When WECC_URE1 mitigated its violation | $45,000 (for WECC201002604, WECC201102807, WECC201102599, WECC201102609, WECC201102606, WECC201102613, and WECC200901475) | Self-Certification | WECC_URE1 submitted a Mitigation Plan, outlining the following mitigating actions: 1) for CIP-005 R3- deployed a system to provide monitoring and logging of access-to-access points at all times. The system is configured to alert designated personnel of attempted or actual unauthorized access. In addition, some documentation recording measures were put in place; 2) for CIP-007 R3- documented an assessment for applicability of security patches within 30 days of the patch being made available; 3) for CIP-009 R4- included backup and restored procedures for its seven Physical Access Control and Monitoring (ACM) control Panels in its Recovery Plan; 4) for CIP-009- R5- included annual testing of information essential to recovery that it stored on backup media. | 2011-03-25 | 2011-07-21 | Agrees/ Stipulates | WECC reviewed WECC_URE1's Internal Compliance Program and considered it a mitigating factor in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102609 | Settlement Agreement | WECC_URE1 submitted a Self-Certification stating that it failed to document the assessment of thirteen security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades. Based on the record, WECC determined that WECC_URE1 failed to assess security patches for 21 Cyber Assets, which resulted in WECC_URE1's failure to make sufficient records of its security patch management program, in violation of CIP-007-1 R3.1. | CIP-007-1 | R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the fact that the devices in scope are located in a Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP) and thus afforded the protections specified in CIP-005 and CIP-006, including automated security status monitoring. | The date WECC_URE1 was required to comply with this Standard | When WECC_URE1 completed its Mitigation Plan | $45,000 (for WECC201002604, WECC201102807, WECC201102599, WECC201102609, WECC201102606, WECC201102613, and WECC200901475) | Self-Certification | WECC_URE1 submitted a Mitigation Plan, stating that it had completed the following actions: 1) set up an automatic notification of security patch releases from its vendors; 2) purchased a software tool, which ensures that the process owner has the ability to track and audit the completion of these tasks within 30 calendar days. | 2011-04-15 | 2011-12-07 | Agrees/ Stipulates | WECC reviewed WECC_URE1's Internal Compliance Program and considered it a mitigating factor in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102606 | Settlement Agreement | WECC_URE1 submitted a Self-Report for a violation of CIP-007-1 R6. WECC_URE1 stated that it failed to implement monitoring and logging for two new Cyber Assets and failed to document the process for monitoring and logging for eight existing Cyber Assets located in its Generation Management System (GMS) Electronic Security Perimeter (ESP). WECC determined that WECC_URE1 failed to implement and document the organizational process and technical and procedural mechanisms for monitoring of security events on all Cyber Assets within the ESP, in violation of CIP-007-1 R6. | CIP-007-1 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the fact that the devices in scope were not classified as Critical Cyber Assets (CCAs). Also, the Cyber Assets were afforded the physical protection required by CIP-006 and did not have remote access. | The date WECC_URE1 was required to comply with this Standard | When WECC_URE1 completed its Mitigation Plan | $45,000 (for WECC201002604, WECC201102807, WECC201102599, WECC201102609, WECC201102606, WECC201102613, and WECC200901475) | Self-Report | WECC_URE1 submitted a Mitigation Plan, committing to the following actions: 1) WECC_URE1 followed its Cyber Security Event Procedure when replacing or receiving new Cyber Assets; 2) implement a manual alert-to-auto alert timelines for CIP requirements; 3) conduct a weekly log review with process owners, retains logs for 90 days; and 4) create new documents outlining the process and method used for monitoring the logging for new assets. | 2011-03-18 | 2011-12-07 | Agrees/ Stipulates | WECC reviewed WECC_URE1's Internal Compliance Program and considered it a mitigating factor in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102613 | Settlement Agreement | WECC_URE1 submitted a Self-Certification stating that it failed to perform annually an assessment on its system for the time period. WECC_URE1 last performed an assessment in the fall of the prior year and again in the winter of the next year. WECC_URE1's system contains 12 Cyber Assets. Based on the record, WECC determined that WECC_URE1 failed to perform an annual assessment on 12 Cyber Assets, in violation of CIP-007-3 R8. | CIP-007-3 | R8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by the fact that the devices in scope were located in a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP) and thus were afforded the protections listed in CIP-005 and CIP-006. In addition, all individuals with access to the devices had completed training and Personnel Risk Assessments (PRAs), thus minimizing the risk to the BPS. | When WECC_URE1 failed to perform annual assessment | When WECC_URE1 completed its Mitigation Plan | $45,000 (for WECC201002604, WECC201102807, WECC201102599, WECC201102609, WECC201102606, WECC201102613, and WECC200901475) | Self-Certification | WECC_URE1 submitted a Mitigation Plan, stating that WECC_URE1 performed an assessment on the system and developed a task management software system to help track deadlines and train users on the new tracking software system. | 2011-04-01 | 2011-06-30 | Agrees/ Stipulates | WECC reviewed WECC_URE1's Internal Compliance Program and considered it a mitigating factor in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC200901475 | Settlement Agreement | WECC_URE1 submitted five Self-Reports for noncompliance with this Standard in the period for approximately six months. Based on the record, WECC determined that the first Self-Report identified the initial instance of noncompliance and the subsequent Self-Reports expanded the scope of the initial Self-Report. In its first Self-Report, WECC_URE1 stated that after upgrading its e-tagging applications, it experienced intermittent database deadlocks that interfered with normal operations. WECC_URE1 failed to respond to numerous e-tag requests requiring WECC_URE1's approval from the Interchange Authority to transition Arranged Interchanges to Confirmed Interchanges, and as a result the e-tags expired. WECC reviewed all five reports and determined that WECC_URE1 failed to respond to more than 50 e-tag requests identified in each Self-Report. | INT-006-2 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although WECC_URE1 failed to respond to 63 e-tags, it responded to the majority of requests from Interchange Authorities within the requisite timeframe during the violation period. Also, WECC_URE1 has the ability to process expired tags through direct contact with the appropriate entities. Finally, WECC determined that when the more than 50 expired e-tags are considered in the context of the total number of e-tags coordinated by WECC_URE1, the risk to the BPS from non-compliance is reduced. | When WECC_URE1 failed to respond before tags expired | When WECC_URE1 completed its Mitigation Plan | $45,000 (for WECC201002604, WECC201102807, WECC201102599, WECC201102609, WECC201102606, WECC201102613, and WECC200901475) | Self-Report | WECC_URE1 submitted a Mitigation Plan and two subsequent revised plans . According to its plan, WECC_URE1: 1) changed its vendor, with the new vendor providing full service to WECC_URE1; 2) completed testing and validated its new system with the new vendor, which ensured that WECC_URE1 could respond to requests from an Interchange Authority to transition an Arranged Interchange to a Confirmed Interchange before the e-tag expired. | 2010-08-02 | 2011-08-12 | Agrees/ Stipulates | WECC reviewed WECC_URE1's Internal Compliance Program and considered it a mitigating factor in determining the penalty amount.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002246 | Settlement Agreement | WECC performed an on-site audit of WECC_URE2's compliance with the Reliability Standards (Audit). During the Audit, WECC found that for 20 minutes, on a single day, WECC_URE2 operated in an Automatic Generation Control (AGC) mode other than the Automatic Time Error Correction (ATEC) and failed to notify all other Balancing Authorities (BAs) of its operating mode. Specifically, the WECC Audit team (Audit Team) determined that WECC_URE2 operated with its ATEC out of service from 12:44 to 13:04 when it switched to its Tie Line Bias (TLB) AGC mode. WECC_URE2 dispatcher logs reflect that at 12:40 pm the dispatcher changed WECC_URE2’s AGC mode from ATEC to its TLB AGC because the ATEC was sending incorrect values to one of WECC_URE2’s neighboring BAs. The dispatcher logs further reflect that at 13:04, the ATEC problem was resolved. WECC_URE2 could not provide evidence that it notified other BAs when it operated its AGC in a mode other than ATEC from 12:44 through 13:04. WECC determined that WECC_URE2 was in violation of BAL-004-WECC-01 R2 for failing to notify its BAs when it operated its AGC system in a mode other than ATEC. | BAL-004-WECC-01 | R2 | Lower | Lower | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) due to the limited duration (20 minutes) WECC_URE2 was operating in an AGC mode other than ATEC. In addition, WECC_URE2 created an alarm for the AGC so that when the AGC system is functioning in any mode except ATEC mode, an alarm is generated to send WECC a message immediately. WECC RC's messaging system, in turn, automatically retransmits the message to its subscribers which include the region's BAs. This alarm will prevent future instances of failing to notify the BA. | Date WECC_URE2 operated its AGC in a mode other than ATEC without notifying its BAs | Date WECC_URE2 operated its AGC in a mode other than ATEC without notifying its BAs | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Audit | 1. WECC_URE2 continues to operate under its AGC procedure, which directs operators to notify the Adjacent BAs and Reliability Coordinator if the ATEC is disabled for any reason. 2. WECC_URE2 issued a critical communication message. A critical communication is a message sent out in order to communicate and inform operating personnel of information which is critical to operating the system. Critical communication messages also document the receipt and understanding by noting which personnel have read, have not read, and if any have questions concerning the communication. 3. In response to the violation, WECC_URE2 has created an alarm for the AGC as follows: When the AGC system is functioning in any mode except ATEC mode, the following alarm is to be generated: "AGC in NON-ATEC Mode, Send WECC Message Immediately." WECC RC's messaging system, in turn, automatically retransmits the message to its subscribers which include the region's BAs. | 2011-04-21 | 2012-01-25 | Agrees/ Stipulates
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002391 | Settlement Agreement | WECC performed an on-site audit of WECC_URE2's compliance with the Reliability Standards (Audit). As a part of the Audit, the WECC Audit team (Audit Team) requested from WECC_URE2 documentation of its cyber security policy, in compliance with CIP-003-1 R1. According to the Audit Team, WECC_URE2 provided three different versions of its cyber security policy. After reviewing all three versions of WECC_URE2's cyber security policy, the Audit Team concluded that WECC_URE2's first two versions of WECC_URE2's cyber security policy violated the Standard because they addressed CIP-002 through CIP-009 in a general manner, as opposed to a more specific directive tailored to how the entity's management intend that the organization will go about addressing each requirement individually. WECC determined that WECC_URE2 was in violation of CIP-003-1 R1 because its cyber security policy did not sufficiently address the requirements of CIP-002 through CIP-009. Specifically, WECC_URE2's cyber security policy addressed the requirements of CIP-002 through CIP-009 too broadly and should have addressed those requirements in more detail in compliance with the Standard. | CIP-003-1 | R1 | Medium | Severe | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). Although an insufficient cyber security policy would have resulted in WECC_URE2 personnel not having proper direction and guidance in the proper handling of Critical Cyber Assets (CCAs), causing a lack of understanding or the unavailability of CCAs, WECC_URE2 did have some documentation of a cyber security policy that addressed the requirements of CIP-002 through CIP-009, though not in specific detail. In addition, WECC_URE2 developed a detailed cyber security policy prior to the Audit to address the requirements of the Standard. | When the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Audit | WECC_URE2 attended a WECC-organized Critical Infrastructure Protection User Group meeting. At that meeting, WECC staff explained the WECC view that “The cyber security policy must address all requirements in the Standard CIP-002 through CIP-009" and not merely a statement that the entity will comply with all requirements in CIP-002 through CIP-009. Upon receipt of this WECC guidance, WECC_URE2 promptly modified its policy accordingly. WECC_URE2 updated its policy to address each requirement individually. The policy is directive in nature and tailored to how management intends WECC_URE2 to go about addressing each requirement individually. | 2010-08-30 | 7/7/2011 | Neither Admits nor Denies
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002393 | Settlement Agreement | WECC performed an on-site audit of WECC_URE2's compliance with the Reliability Standards (Audit), including CIP-003-1 R6. As a part of the Audit, the WECC Audit team (Audit Team) requested from WECC_URE2 documentation that it had a change control and configuration management program, in compliance with CIP-003-1 R6. WECC_URE2 provided three procedure documents. Upon review of these documents, WECC determined that these documents did not include processes for configuration management and thus, WECC_URE2 was in violation of the Standard. | CIP-003-1 | R6 | Lower | Lower | WECC determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS). Configuration management is essential to controlling system changes. It is possible that if a change to the system is improperly configured due to the lack of configuration management, the improperly configured change can negatively impact other parts of the system. However, the CCAs in question were located inside Electronic Security Perimeters and Physical Security Perimeters and afforded some of the protections of CIP-005-1 R1 and CIP-006- R1. | When the Standard became mandatory and enforceable for WECC_URE2 | Date WECC_URE2 documented a process for configuration management | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Audit | WECC_URE2 modified its document to include a configuration management process. Additionally WECC_URE2 purchased a product which assists in properly documenting and implementing configuration management activities in order to enhance WECC_URE2's efforts to adhere to the requirements set forth by CIP-003-1 R6. This product is now part of the documented configuration management process. | 2010-05-24 | 7/7/2011 | Agrees/ Stipulates
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002296 | Settlement Agreement | WECC_URE2 self-reported potential noncompliance with CIP-004-1 R2.3. 4.5 months later, a WECC subject matter expert (SME) held a conference call with WECC_URE2 to discuss the violation. On the call the WECC SME confirmed the information contained in WECC_URE2's Self-Report that WECC_URE2 identified an employee who had exceeded his annual training date requirement. Subsequently, WECC_URE2 conducted an internal review and identified three additional employees who had exceeded their training renewal dates. These individuals were due for training 40 days before the discovery date. WECC_URE2 stated in its Self-Report that the personnel identified as having exceeded their training dates had been trained within fourteen months, their access rights to Critical Cyber Assets (CCAs) were immediately revoked and, once the personnel had been properly trained, their access to CCAs were reinstated. WECC determined that WECC_URE2 was in violation of CIP-004-1 R2.3 because it failed to maintain an annual cyber security training program and allowed the training of four of its employees with access to CCAs to lapse. | CIP-004-1 | R2; R2.3 | Lower | High | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the violation was limited to only four individuals, and those few individuals only missed their training dates by two months. Although this lack in proper training could have led to mismanagement of CCAs and reduced reliability to the BPS, this risk was mitigated by the fact these individuals had previous training and previous authorized access to the CCAs. | When the Standard became mandatory and enforceable for WECC_URE2 | When WECC_URE2 revoked access to CCAs for the affected personnel | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Self-Report | WECC_URE2 completed the following mitigation actions: 1. Personnel access lists to CCAs have been reviewed to re-evaluate the business need for access. 2. Improved software queries have been developed to eliminate duplicative training records and clearly identify personnel that are within 30 days of their cyber security training expiration date. These personnel are notified and flagged as requiring training. They are rechecked within 7 days of their training expiration date. If they have not completed their training, their access is revoked until their training is completed; 3. Verification of cyber security training dates is independently reviewed by two WECC_URE2 employees; 4. September 1st of each year was established as the annual retraining date for all personnel that have access to WECC_URE2's CCAs; 5. Additional fields were added to the cyber security training database that will decrease duplication of records for individuals who have taken cyber security training and allow removal of individuals from the list by indicating that training is no longer needed due to transfer or termination; 6. Created and maintained a unique identifier for personnel, contactors and any other personnel in the training database, reducing the risk of human error by reducing the manual processes required in cross-referencing data; and 7. Created an automatic annual training notification. This provided an automatic mechanism to notify personnel that renewal of training is required and CCA access needs to be revoked for personnel whose training has not been renewed within a predetermined time prior to the training expiration date. | 2010-04-20 | 2010-11-30 | Agrees/ Stipulates | When assessing the penalty, WECC did not apply any self-reporting credit since WECC_URE2 self-reported during its self-certification period.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002394 | Settlement Agreement | WECC performed an on-site audit of WECC_URE2's compliance with the Reliability Standards (Audit). During the Audit, WECC found that WECC_URE2 maintained a list of all personnel with unescorted physical cyber access to Critical Cyber Assets (CCAs) and reviewed the access on a quarterly basis; however, the quarterly reviews did not include its personnel's specific electronic access rights to CCAs. WECC determined that WECC_URE2 was in violation of the Standard for not including electronic access rights in its quarterly reviews of personnel who have unescorted access to CCAs. | CIP-004-1 | R4 | Lower | Moderate | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). Although it was possible that because WECC_URE2 did not review electronic access right in its quarterly reviews of personnel with unescorted access to CCAs, unauthorized personnel could have gained electronic access to CCAs and acted maliciously, WECC_URE2 did have compensating measures in place. WECC_URE2 did perform quarterly reviews of its personnel assigned to particular job functions, and WECC_URE2's electronic access rights were tied to specific job functions. While this review of job functions was not a sufficient review to make it compliant with CIP-004-1 R4, it functioned as an indirect review of specific electronic access rights. | When the Standard became mandatory and enforceable for WECC_URE2 | When WECC_URE2 mitigated the violation | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Audit | WECC_URE2's Mitigation Plan required it to improve its access rights review process. The new process links specifically-defined electronic access rights to specific user roles. Each role is directly associated with a specific job function. WECC_URE2 management will approve the access rights associated with an individual role and assign the roles to personnel as required. WECC_URE2 will review and validate the specific access rights associated with each individual user on a quarterly basis. | 2011-09-01 | 2011-09-15 | Agrees/ Stipulates | WECC assessed a single aggregate penalty for WECC_URE2's violations of CIP-004-1 R4 and CIP-007-1 R5.1.3. WECC_URE2's failure to perform annual reviews of its electronic access rights is a single incidence of noncompliance that resulted in a violation of CIP-007-1 R5.1.3. WECC determined WECC_URE2's failure to perform annual reviews of electronic access rights resulted in WECC_URE2's violations of CIP-004-1 R4 and CIP-007-1 R5.3.1. Accordingly, the penalty assessed for CIP-004-1 R4 is a single penalty representative of the aggregate of the related violations.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002399 | Settlement Agreement | WECC_URE2 self-reported a potential violation CIP-005-1 R1.5. In its Self-Report, WECC_URE2 stated that it had test procedures in place to test security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms or other third-party software or firmware before placing software or firmware into production on Cyber Assets. WECC_URE2 also stated in the Self-Report that, based on a misinterpretation of CIP-007-1 R1, WECC_URE2 did not specifically test software and firmware to determine if it would have adverse affects on existing cyber security controls. In addition, WECC_URE2 self-reported that it has a patch management program in place to evaluate, test, and install applicable security patches for all Cyber Assets inside its Electronic Security Perimeter, but the program is focused on operating system and major application patches, and minor or peripheral applications were not addressed consistently. Seven months after self-reporting, WECC_URE2 submitted additional evidence identifying specifically the Cyber Assets that were not afforded the protections in CIP-007-1 R1 and R3. WECC determined that WECC_URE2 was in violation of the Standard because it did not afford its Cyber Assets used in the access control and monitoring of its Electronic Security Perimeter the protections in CIP-007-1 R1 and R3. Specifically, WECC_URE2 was in violation of CIP-005-1 R1.5 because it did not test its Cyber Assets to ensure that new Cyber Assets and significant changes to Cyber Assets would not adversely affect existing cyber security controls. Additionally, WECC_URE2 did not evaluate, test and install applicable security patches for all Cyber Assets as prescribed by CIP-007-1 R3. | CIP-005-1 | R1; R1.5 | Lower | Moderate | WECC determined that this violation posed a moderate and not a serious or substantial risk to the bulk power system (BPS). The purpose of this Standard is to identify and protect the Electronic Security Perimeter by protecting all access points on the perimeter. Failure to ensure that Cyber Assets used in the access control and/or monitoring (ACM) of the Electronic Security Perimeter have the appropriate protective measures as specified in CIP-007-1 R1 and R3 may allow unauthorized internal and or external access to these Cyber Assets, which could then allow for successful cyber attacks against Critical Cyber Assets essential for operation of the BPS thereby negatively impacting the operation of the BPS. In this instance, WECC_URE2 failed to ensure that new and changes to Cyber Assets would not have a negative impact on the existing cyber controls and also failed to evaluate, test, and install security patches for all Cyber Assets. However, the Cyber Assets were afforded all the remaining protection required by CIP-005-1 R1. | When the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Self-Report | WECC_URE2's Mitigation Plan required it to reevaluate its test procedures to test that new and significant changes to cyber assets do not adversely affect existing security controls to meet the requirements of CIP-007 R1, as well as refine its patch management process to meet the requirements of CIP-007 R3. | 2010-10-15 | 2011-05-17 | Agrees/ Stipulates | When assessing the penalty, WECC did not apply any self-reporting credit since WECC_URE2 reported during its self-certification period.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002397 | Settlement Agreement | WECC_URE2 self-reported a potential violation CIP-006-1 R1. In its Self-Report, WECC_URE2 stated that it has not created or implemented cyber security test procedures for its physical access control that are performed in a manner that reflects its production environment. In addition, because these tests have not been performed, they have not been documented. WECC_URE2 further self-reported that it was in violation of CIP-006-2 R2.2 because its physical access control systems run on one type of operating systems and WECC_URE2's program for security patch management has not been formally documented and does not appear to comply strictly with what is called for in requirement CIP-006-2 R2.2. Seven months after self-reporting, WECC_URE2 submitted additional evidence identifying specifically the Cyber Assets what were not afforded the protections in CIP-007-1 R1 and R3. WECC determined that WECC_URE2 was in violation of CIP-006-1 R1.8 because it did not afford its Critical Cyber Assets used in the access control and monitoring of its Physical Security Perimeters the protections in CIP-007-1 R1 and R3. Specifically, WECC_URE2 was in violation of CIP-006-1 R1.8 because it did not test its Critical Cyber Assets to ensure that new Cyber Assets and significant changes to Cyber Assets would not adversely affect existing cyber security controls. Additionally, WECC_URE2 did not evaluate, test, and install applicable security patches for all Cyber Assets as prescribed by CIP-007-1 R3. WECC_URE2 also did not did not implement the protective measures specified in CIP-006-2 R2. | CIP-006-1 (WECC has determined that WECC_URE2 violated CIP-006-1 R1.8 from when the Standard became enforceable for WECC_URE2, until when CIP-006-1 R1.8 was replaced by CIP-006-2 R2.2. Furthermore, WECC_URE2 violated CIP-006-2 R2.2 until when CIP-006-2 R2.2 was replaced by CIP-006-3 R2.2.) | R1; R1.8 | Lower | Moderate | WECC determined that this violation posed a moderate and not a serious or substantial risk to the reliability of the bulk power system (BPS). The purpose of this Standard is to identify and protect the Electronic Security Perimeter by protecting all access points on the perimeter. Failure to ensure that Cyber Assets used in the access control and/or monitoring (ACM) of the Electronic Security Perimeter have the appropriate protective measures as specified in CIP-007-1 R1 and R3 may allow unauthorized internal and or external access to these Cyber Assets, which could then allow for successful cyber attacks against Critical Cyber Assets essential for operation of the BPS thereby negatively impacting the operation of the BPS. In this instance, WECC_URE2 failed to ensure that new and changes to Cyber Assets would not have a negative impact on the existing cyber controls and also failed to evaluate, test and install security patches for all Cyber Assets. However, the Cyber Assets were afforded all the remaining protection required by CIP-006-1 R1. | When the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Self-Report | The CIP-006-1 R1.8 Mitigation Plan addressed the issues with CIP-007-1. WECC_URE2 developed and enhanced existing processes to address security control testing and patch management. This along with establishing a test environment for performing these processes and enhancing the production environment fully met the requirement. The following actions were taken: 1. Implemented new test environment for security patch management and security control testing prior to any significant changes or upgrades to the physical access control system; 2. Enhanced production environment by making changes in order to utilize and streamline the security patch process and security controls testing; 3. Implemented and utilized enhanced security patch process; and 4. Established processes for security control testing which will be used to baseline the physical access control system configuration enabling security control testing in the new environment prior to updating production. | 2010-12-06 | 2011-05-26 | Agrees/ Stipulates | When assessing the penalty, WECC did not apply any self-reporting credit since WECC_URE2 self-reported during its self-certification period. WECC assessed a single aggregate penalty for WECC_URE2's violations of CIP-006-1 R1.8 and CIP-007-1 R1 and R3. WECC_URE2's failure to provide the protections in CIP-007-1 R1 and R3 to the ACM Cyber Assets is a single incidence of noncompliance that resulted in violations of CIP-007-1 R1 and R3. Accordingly, the penalty assessed for CIP-006-1 R1.8 is a single penalty representative of the aggregate of the related violations.
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002294 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-1 R1. In its Self-Report, WECC_URE2 indicated that, although it has a procedure in place to test security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms before placing software and firmware into production on Critical Cyber Assets, it does not specifically test the software and firmware to determine if significant changes would have adverse effects on cyber security controls. 41 days later, a WECC subject matter expert (SME) held a conference call with WECC_URE2 to confirm the facts contained in WECC_URE2's Self-Report. On the conference call, the WECC SME further clarified that, although WECC_URE2 had existing procedures to test significant changes to ensure there were no existing adverse impacts on functional changes, WECC_URE2 was not testing for significant changes in security controls, as required by the Standard. WECC determined that WECC_URE2 was in violation of ClP-007-1 R1 because it did not have test procedures to ensure that significant changes to existing Cyber Assets within its Electronic Security Perimeter do not adversely affect existing cyber security controls. | ClP-007-1 | R1 | Medium | High | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 had substantial testing in place. Although, WECC_URE2 did not test the potential adverse impacts on cyber security controls of significant changes to existing Cyber Assets, WECC_URE2 had existing test procedures in place to test the potential adverse impacts of functional changes. | When the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Self-Report | Pursuant to WECC_URE2's Mitigation Plan, WECC_URE2 has developed new test procedures to test the adverse impacts on security controls of significant changes to Cyber Assets. | 2010-07-29 | 2011-05-17 | Agrees/ Stipulates | WECC assessed a single aggregate penalty for WECC_URE2's violations of CIP-005-1 R1.5, CIP-006-1 R1.8 and CIP-007-1 R1. WECC_URE2's failure to provide the protections in CIP-007-1 to its Critical Cyber Assets is a single incidence of noncompliance that resulted in violations of CIP-005-1 R1.5 and CIP-006-1 R1.8. Accordingly, the penalty assessed for CIP-007-1 R1 is a single penalty representative of the aggregate of the related violations
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002295 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-1 R3. In its Self-Report, WECC_URE2 explained that it has a patch management program in place to evaluate, test and install applicable security patches for all Cyber Assets which reside its Electronic Security Perimeter. WECC_URE2 further explained that the program was focused only on operating systems and major application patches, but minor, as well as peripheral applications, were not addressed consistently. A WECC subject matter expert (SME) found that although WECC_URE2 had a security patch management program, the program did not track, evaluate, or test applicable ancillary cyber security software. WECC determined that WECC_URE2 is in violation of CIP-007-1 R3 because it failed to establish and document a security patch management program for tracking, evaluating, and testing all of its applicable cyber security software patches for all Cyber Assets within its Electronic Security Perimeter. | ClP-007-1 | R3 | Lower | Lower | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 did establish and document a security patch management program. Although the program did not include ancillary cyber security software, and as a result a security weakness could affect all Cyber Assets within the Electronic Security Perimeter if ancillary software is not properly patched, the risk was minimal because WECC_URE2 did have a security patch management program and the Cyber Assets were being afforded the protections in the program. | When the Standard became mandatory and enforceable for WECC_URE2 | Mitigation plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Self-Report | In order to mitigate its violation, WECC_URE2 implemented an automated solution for identifying changes which affect WECC_URE2's security posture. WECC_URE2 refined its security patch management process to fully meet the requirements of the Standard by implementing the following actions: 1. Inventory all operating systems and applications that reside on Cyber Assets within the Electronic Security Perimeters; and 2. Enhance the program to track, evaluate, test and install security patches for all identified operating systems and applications that reside on Cyber Assets within the Electronic Security Perimeters. | 2010-10-15 | 2011-10-31 | Agrees/ Stipulates | WECC assessed a single aggregate penalty for WECC_URE2's violations of CIP-005-1 R1.5, CIP-006-1 R1.8 and CIP-007-1 R3. WECC_URE2's failure to provide the protections in CIP-007-1 to its Cyber Assets is a single incidence of noncompliance that resulted in violations of CIP-005-1 R1.5 and CIP-006-1 R1.8. Accordingly, the penalty assessed for CIP-007-1 R3 is a single penalty representative of the aggregate of the related violations
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002396 | Settlement Agreement | WECC performed an on-site audit of WECC_URE2's compliance with the Reliability Standards (Audit). The WECC Audit team (Audit Team) reviewed the documents WECC_URE2 presented as evidence of a Cyber Security Incident response plan and found that the first version of the plan did not include roles and responsibilities or a communication plan as required by CIP-008-1 R1.2. Furthermore, the Cyber Security Incident response plan was updated two more times, and neither of these versions included roles and responsibilities or a communication plan. In addition, the Audit Team noted that version two of CIP-008 requires a Cyber Security Incident response plan to be updated within 30 days of any changes to the plan. WECC_URE2's Cyber Security Incident response plan was not updated to reflect the requirement in version two of CIP-008. WECC determined that WECC_URE2 was in violation of CIP-008-1 R1.2 for not including personnel roles and responsibilities or a communication plan in its Cyber Security Incident response plan. Additionally, WECC determined that WECC_URE2 was in violation of CIP-008-2 R1 for not updating its Cyber Security Incident response plan within 30 days. | ClP-008-1 | R1 | Lower | High | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2's Cyber Security Incident response plan did identify personnel to be contacted if a Cyber Security Incident did occur. | When the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Audit | WECC_URE2's Mitigation Plan required it to modify its Cyber Security Incident response plan to include a section devoted to roles and responsibilities that details the identification of specific employee positions that are the primary "owners" or designated lead personnel for the maintenance, protection and use of NERC CIP assets. Additionally, WECC_URE2's Mitigation Plan required it to add a section to address a communications plan and a procedure for updating the document within 30 days. | 2010-06-30 | 2011-07-08 | Neither Admits nor Denies
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002392 | Settlement Agreement | WECC performed an on-site audit of WECC_URE2's compliance with the Reliability Standards (Audit). To demonstrate its compliance with CIP-003-2 R5, WECC_URE2 provided the WECC Audit team (Audit Team) its Critical Cyber Asset access control program in two documents. The Audit Team found that WECC_URE2's first document did not include the annual verifications required by R5.1.2, R5.2, and R5.3. WECC determined that WECC_URE2 was in violation of CIP-003-2 R5 for not documenting the annual reviews and verifications as required by CIP-003-2 R5.1.2, R5.2 and R5.3. | CIP-003-2 | R5 | Lower | Moderate | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 originally documented the annual reviews and verifications required by CIP-003-1 R5.1.2, R5.2 and R5.3 in its access control procedure document. Furthermore, WECC_URE2 did conduct the actually annual reviews and verifications required by CIP-003-2 R5.1.2, R5.2 and R5.3 but simply did not document the reviews and verifications for 2010. | When WECC_URE2 revised its program document and did not include the required annual reviews and verifications | Mitigation Plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Audit | WECC_URE2's Mitigation Plan required it to update its cyber security plan for managing access to protected Critical Cyber Asset information, to require annual reviews and verifications as required by CIP-003-2 R5.1.2, R5.2 and R5.3. WECC_URE2 also communicated the document changes to the appropriate areas and had the appointed compliance manager approve and sign the revised document. | 2011-07-30 | 2011-08-19 | Agrees/ Stipulates
2012-01-31 | FERC | NP12-12-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002395 | Settlement Agreement | WECC performed an on-site audit of WECC_URE2's compliance with the Reliability Standards (Audit). The WECC Audit team (Audit Team) requested from WECC_URE2 evidence that it was reviewing, at least annually, its user accounts to verify that access privileges are in accordance with CIP-004-1 R4. At the Audit, WECC_URE2 produced a spreadsheet which demonstrated that WECC_URE2 knew the specific electronic access rights of its personnel; however, this spreadsheet was created at the Audit and did not demonstrate that WECC_URE2 was annually reviewing the electronic access rights of its personnel in accordance with CIP-004-1 R4, as required by CIP-007-1 R5. WECC determined that WECC_URE2 was in violation of CIP-007-1 R5.1.3 for failing to review its user accounts annually to verify they are in accordance with CIP-004-1 R4. | CIP-007-1 | R5; R5.1.3 | Medium | Severe | WECC determined that this violation posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 was able to produce a spreadsheet demonstrating that it knew what the electronic access rights of its personnel were even though WECC_URE2 did not review the electronic access rights of its personnel. Although this could have resulted in personnel gaining unauthorized access to WECC_URE2's Electronic Security Perimeters and those unauthorized personnel could possibly present a threat to the reliability of the BPS, this particular violation has a minimal risk because WECC_URE2 knew the electronic access rights of its personnel. | When the Standard became mandatory and enforceable for WECC_URE2 | Mitigation Plan completion | $55,000 (for WECC201002246; WECC201002391; WECC201002393; WECC201002296; WECC201002394; WECC201002399; WECC201002397; WECC201002294; WECC201002295; WECC201002396; WECC201002392; and WECC201002395) | Audit | WECC_URE2's Mitigation Plan required it to update its quarterly review process to review specific access rights in accordance with CIP-007-1 R5. | 2011-09-01 | 2011-09-15 | Agrees/ Stipulates | WECC assessed a single aggregate penalty for WECC_URE2's violations of CIP-004-1 R4 and CIP-007-1 R5.1.3. WECC_URE2's failure to perform annual reviews of its electronic access rights is a single incidence of noncompliance that resulted in a violation of CIP-007-1 R5.1.3. WECC determined WECC_URE2's failure to perform annual reviews of electronic access rights resulted in WECC_URE2's violations of CIP-004-1 R4 and CIP-007-1 R5.3.1. Accordingly, the penalty assessed for CIP-004-1 R4 is a single penalty representative of the aggregate of the related violations.
2012-01-31 | FERC | NP12-10-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100223 | Settlement Agreement | NPCC_URE1 Self Reported a violation of CIP-004-1 R4 to NPCC. NPCC determined that NPCC_URE1 was in violation of the Standard. NPCC_URE1 failed to review the list of its personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets quarterly, as required by the Standard. Specifically, NPCC_URE1 did not review the list of personnel who were in possession of keys that allowed Physical Security Perimeter (PSP) substation access in the cases where the card reader was out of service. Additionally, NPCC_URE1 failed to revoke access within the proper timeframe (seven days) for personnel who no longer needed to be in possession of those keys. Approximately 30-50 keys were unaccounted for from when NPCC_URE1 was required to comply with the Standard to when new locks and keys were installed. | CIP-004-1 | R4 | Medium | Severe | NPCC determined that this violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1 has processes in place to ensure that only authorized personnel are allowed access to the substation. Specifically, there is and was at the time of the violation a documented key system in place to track key access to the outer gate. There is also a background check required for gate access. Additionally, the standard method of accessing the substation is a swipe card, and there was and is a procedure in place for tracking and revoking swipe card access. The keys at issue here are used only in the event that the swipe card system is not functioning; at no time during the violation did the swipe card system fail to force the use of the keys. These keys are numbered but otherwise unidentifiable and are useless with gate access. Second, NPCC_URE1 has alarms generated immediately to Security if the card reader is bypassed using the key. Third, there was no actual impact as there were no incidents at NPCC_URE1 facilities related to the lack of proper documentation and revocation of the keys. | When the Standard became mandatory and enforceable | When the new lock system was implemented | $15,000 (Settlement of NPCC201100223 and NPCC201100224) | Self-Report | In accordance with the Mitigation Plan, NPCC_URE1 implemented a new system for PSP substation access. First, NPCC_URE1 provided documentation that site-specific lock boxes have been installed at each facility in question, and the old locks associated with the undocumented keys have been removed. Individuals no longer have a physical key to access the substation should the card reader system fail. Second, NPCC_URE1 provided documentation that a new procedure has been created, in which just one key is kept at a separate office in a site-specific lock box with security personnel who are trained in the documented access procedure. Thus, the general procedure in place for reviewing access lists and revoking substation and PSP access is now in effect in instances in which the card reader system is not functioning. | 2011-01-10 | 2011-03-22 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination.
2012-01-31 | FERC | NP12-10-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100224 | Settlement Agreement | NPCC_URE1 Self Reported a violation of CIP-006-1 R1 to NPCC. NPCC determined that NPCC_URE1 was in violation of the Standard. NPCC_URE1 failed to create and maintain a physical security plan to address procedures for the appropriate use of physical access controls, as required by the Standard. Specifically, NPCC_URE1 did not have a procedure in place to document: (1) the appropriate use of keys that granted PSP substation access; or (2) the appropriate response to loss of such keys that allowed entrance into the PSP. Approximately 30-50 keys were unaccounted for from when NPCC_URE1 was required to comply with the Standard to when new locks and keys were installed. | CIP-006-1 | R1 | Medium | Severe | NPCC determined that this violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1 has processes in place to ensure that only authorized personnel are allowed access to the substation. Specifically, there is and was at the time of the violation a documented key system in place to track key access to the outer gate. There is also a background check required for gate access. Additionally, the standard method of accessing the substation is a swipe card, and there was and is a procedure in place for tracking and revoking swipe card access. The keys at issue here are used only in the event that the swipe card system is not functioning; at no time during the violation did the swipe card system fail to force the use of the keys. These keys are numbered but otherwise unidentifiable and are useless with gate access. Second, NPCC_URE1 has alarms generated immediately to Security if the card reader is bypassed using the key. Third, there was no actual impact as there were no incidents at NPCC_URE1 facilities due to inappropriate use of keys. | When the Standard became mandatory and enforceable | When the new lock system was implemented | $15,000 (Settlement of NPCC201100223 and NPCC201100224) | Self-Report | In accordance with the Mitigation Plan, NPCC_URE1 implemented a new system for PSP substation access. First, NPCC_URE1 provided documentation that site-specific lock boxes have been installed at each facility in question, and the old locks associated with the undocumented keys have been removed. Individuals no longer have a physical key to access the substation should the card reader system fail. Second, NPCC_URE1 provided documentation that a new procedure has been created, in which just one key is kept at a separate office in a site-specific lock box with security personnel who are trained in the documented access procedure. Thus, the general procedure in place for reviewing access lists and revoking substation and PSP access is now in effect in instances in which the card reader system is not functioning. | 2011-01-10 | 2011-03-22 | Neither Admits nor Denies | NPCC considered NPCC_URE1's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination.
2012-01-31 | FERC | NP12-10-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC201100225 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-004-1 R4 to NPCC. NPCC determined that URE was in violation of the Standard. NPCC_URE2 failed to review the list of its personnel who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets quarterly, as required by the Standard. Specifically, NPCC_URE2 did not review the list of personnel who were in possession of keys that allowed Physical Security Perimeter (PSP) substation access in the cases where the card reader was out of service. Additionally, NPCC_URE2URE failed to revoke access within the proper timeframe (seven days) for personnel who no longer needed to be in possession of those keys. Approximately 30-50 keys were unaccounted for from when NPCC_URE2 was required to comply with the Standard to when new locks and keys were installed. | CIP-004-1 | R4 | Medium | Severe | NPCC determined that this violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 has processes in place to ensure that only authorized personnel are allowed access to the substation. Specifically, there is and was at the time of the violation a documented key system in place to track key access to the outer gate. There is also a background check required for gate access. Additionally, the standard method of accessing the substation is a swipe card, and there was and is a procedure in place for tracking and revoking swipe card access. The keys at issue here are used only in the event that the swipe card system is not functioning; at no time during the violation did the swipe card system fail to force the use of the keys. These keys are numbered but otherwise unidentifiable and are useless with gate access. Second, NPCC_URE2 has alarms generated immediately to Security if the card reader is bypassed using the key. Third, there was no actual impact as there were no incidents at NPCC_URE2 facilities related to the lack of proper documentation and revocation of the keys. | When the Standard became mandatory and enforceable | When the new lock system was implemented | $5,000 (Settlement of NPCC201100225 and NPCC201100226 | Self-Report | In accordance with the Mitigation Plan, NPCC_URE2 implemented a new system for PSP substation access. First, NPCC_URE2 provided documentation that site-specific lock boxes have been installed at each facility in question, and the old locks associated with the undocumented keys have been removed. Individuals no longer have a physical key to access the substation should the card reader system fail. Second, NPCC_URE2 provided documentation that a new procedure has been created, in which just one key is kept at a separate office in a site-specific lock box with security personnel who are trained in the documented access procedure. Thus, the general procedure in place for reviewing access lists and revoking substation and PSP access is now in effect in instances in which the card reader system is not functioning. | 2011-01-10 | 2011-03-22 | Neither Admits nor Denies | NPCC considered NPCC_URE2's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination.
2012-01-31 | FERC | NP12-10-000 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC201100226 | Settlement Agreement | NPCC_URE2 self-reported a violation of CIP-006-1 R1 to NPCC. NPCC determined that NPCC_URE2 was in violation of the Standard. NPCC_URE2 failed to create and maintain a physical security plan to address procedures for the appropriate use of physical access controls, as required by the Standard. Specifically, NPCC_URE2 did not have a procedure in place to document: (1) the appropriate use of keys that granted PSP substation access; or (2) the appropriate response to loss of such keys that allowed entrance into the PSP. Approximately 30-50 keys were unaccounted for from NPCC_URE2 was required to comply with the Standard to when new locks and keys were installed. | CIP-006-1 | R1 | Medium | Severe | NPCC determined that this violation posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 has processes in place to ensure that only authorized personnel are allowed access to the substation. Specifically, there is and was at the time of the violation a documented key system in place to track key access to the outer gate. There is also a background check required for gate access. Additionally, the standard method of accessing the substation is a swipe card, and there was and is a procedure in place for tracking and revoking swipe card access. The keys at issue here are used only in the event that the swipe card system is not functioning; at no time during the violation did the swipe card system fail to force the use of the keys. These keys are numbered but otherwise unidentifiable and are useless with gate access. Second, NPCC_URE2 has alarms generated immediately to Security if the card reader is bypassed using the key. Third, there was no actual impact as there were no incidents at NPCC_URE2 facilities due to inappropriate use of keys. | When the Standard became mandatory and enforceable | When the new lock system was implemented | $5,000 (Settlement of NPCC201100225 and NPCC201100226 | Self-Report | In accordance with the Mitigation Plan, NPCC_URE2 implemented a new system for PSP substation access. First, NPCC_URE2 provided documentation that site-specific lock boxes have been installed at each facility in question, and the old locks associated with the undocumented keys have been removed. Individuals no longer have a physical key to access the substation should the card reader system fail. Second, NPCC_URE2 provided documentation that a new procedure has been created, in which just one key is kept at a separate office in a site-specific lock box with security personnel who are trained in the documented access procedure. Thus, the general procedure in place for reviewing access lists and revoking substation and PSP access is now in effect in instances in which the card reader system is not functioning. | 2011-01-10 | 2011-03-22 | Neither Admits nor Denies | NPCC considered NPCC_URE2's internal compliance program, which was in place at the time of the violation, to be a mitigating factor in the penalty determination.
2012-01-31 | FERC | NP12-10-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1, Unidentified Registered Entity 2, Unidentified Registered Entity 3, Unidentified Registered Entity 4 (collectively, RFC_URE1) | NCRXXXXX | RFC201000391 | Settlement Agreement | RFC_URE1 self-reported a violation of CIP-006-2 R1.6 to ReliabilityFirst. The retail business of RFC_URE1’s parent company was sold. During a subsequent period, including the time period relevant to this violation, the parent company and purchasing company shared certain spaces. Specifically, the purchasing company's data storage servers were located in the same locked room as RFC_URE1's data storage servers. RFC_URE1's data storage servers were located in locked cabinets within this room. These servers were capable of performing as RFC_URE1's backup control center, and as such, RFC_URE1 considered them as Critical Cyber Assets (CCAs). According to the Self-Report, an employee of the purchasing company escorted a visitor inside the Physical Security Perimeter (PSP) surrounding these servers. This individual failed to document the entry of the visitor into the PSP. After entering the PSP, the visitor was left unescorted for 25 minutes. The visitor was a computer manufacturer vendor. RFC_URE1 discovered the violation while checking the access logs for the PSP. Upon discovery of the possible violation, RFC_URE1 ensured the access rights of the purchasing company's employee who left the computer manufacturer vendor unescorted within the PSP were terminated. | CIP-006-2 | R1/1.6 | Medium | Severe | This violation posed a moderate risk to the bulk power system (BPS) because failure to continuously escort personnel who do not have authorized physical access to a PSP poses an increased risk to CCAs essential to the operation of the BPS. This violation did not pose a serious or substantial risk to the reliability of the BPS because, while a visitor did enter RFC_URE1's PSP and remained within that perimeter unescorted for 25 minutes, RFC_URE1's CCAs were located in fully enclosed and locked cabinets, which the unescorted visitor could not and did not access. Furthermore, the data center was under video surveillance, which confirmed that the unescorted visitor did not approach RFC_URE1's assets. | The date RFC_URE1 failed to ensure an unauthorized visitor to its PSP was continuously escorted while inside the PSP | The date RFC_URE1 failed to ensure an unauthorized visitor to its PSP was continuously escorted while inside the PSP | 6000 | Self-Report | Upon discovery of the violation, RFC_URE1 ensured that the access rights of the purchase company's employee who left the computer manufacturer vendor unescorted within the PSP were terminated. The purchase company's has moved its employees and assets, including its data storage servers, out of RFC_URE1's building, ensuring that a similar incident will not be possible in the future. RFC_URE1 disabled any and all purchase company cards that still showed to be "Active." | 2011-04-29 | 2011-06-03 | Agrees and Stipulates to the Facts | ReliabilityFirst commends certain aspects of RFC_URE1's compliance program, in effect at the time of the alleged violation, and considered them as mitigating factors.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000288 | Settlement Agreement | During a Spot Check, the SPP RE found that SPPRE_URE1’s Cyber Security Policy (Policy) did not address all of the requirements of CIP-002-1 through CIP-009-1 as required by CIP-003-1 R1.1. For example, its Policy did not address the requirement for authentication of access into the electronic security perimeter required by CIP-005-1 R2.5. Also, the Policy had no reference to the vulnerability assessment required by CIP-005-1 R4. Also, SPPRE_URE1 had not updated its Policy to reflect Version 2 of the CIP Standards that were in effect at the time of the Spot Check. For example, the Policy provided for a 90-day period to update the Incident Response Reporting Procedure following any changes, which was consistent with CIP-008-1 R1.4, while CIP-008-2 R1.4 required a process to ensure that updates occur within a shorter 30-day period. | CIP-003-1 | R1.1 | Lower | Severe | SPP RE determined that SPPRE_URE1’s violation of CIP-003-1 R1.1 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk because the deficiency was documentation-related, involving the SPPRE_URE1 Policy itself. SPPRE_URE1 had a Policy in place that addressed most, though not all, of the CIP-002 through CIP-009 requirements. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Spot Check | To mitigate its violation of CIP-003-1 (2) R1.1, SPPRE_URE1 updated its Policy to include the applicable requirements of CIP-002 through CIP-009, Version 3. SPPRE_URE1 trained all affected employees on the updated Policy and documented its training to make certain all affected employees were included in the training. | 2010-12-10 | 2011-01-04 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000289 | Settlement Agreement | During a Spot Check, the SPP RE found SPPRE_URE1 could not provide evidence of the testing of cyber security controls for a Microsoft security patch implementation on the SPPRE_URE1 system, in violation of this Standard. SPPRE_URE1 submitted additional evidence to rebut the Spot Check team’s finding, stating that at the Spot Check SPPRE_URE1’s Subject Matter Expert (SME) incorrectly provided that the patch was implemented and that the test records were actually collected when the Microsoft patch was implemented the next month. The SPP RE determined that the evidence submitted by SPPRE_URE1 was still insufficient because the test records did not show that SPPRE_URE1 had tested its cyber security controls to verify that the Microsoft security patch did not adversely impact the security of its affected Cyber Assets. | CIP-007-1 | 1.3 | Lower | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R1.3 posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk because SPPRE_URE1 was applying security patches on its system although it failed to test the security controls prior to implementation of a Microsoft security patch. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Spot Check | To mitigate its violation of CIP-007-1 R1.3, SPPRE_URE1 took the following mitigating actions: developed a security patch management policy to identify and review all applicable security patches for all devices and Cyber Assets within the Electronic Security Parameter (ESP) within 30 days of their release; amended its policy to include requirements for documenting rationale and any compensating measures for any patches not installed; created a template to use where each new patch is reviewed for consideration; implemented a policy that all reviewed patches should follow the defined template; and trained all affected employees on the patch management policy. | 2010-11-12 | 2010-12-06 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000394 | Settlement Agreement | SPPRE_URE1 reported in its Self-Certification that it was not in compliance with CIP-005-2 R1.5 because of its potential violations of CIP-003-1 R4 and R6, CIP-005-1 R2 and R3, and CIP-007-1 R3, R5, R6, R8, and R9. SPPRE_URE1 was not fully compliant with a number of the requirements related to the protection of its Critical Cyber Assets (CCAs), but also regarding protection of its Cyber Assets used for Electronic Security Perimeter (ESP) access control and/or monitoring. | CIP-005-1 | 1.5 | Medium | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-005-1 R1.5 posed a moderate risk to the reliability of the bulk power system (BPS) but did not pose a serious or substantial risk. SPPRE_URE1’s failure to afford several of the required protective measures to its CAs used in ESP access control and/or monitoring and its failure to provide protection to its CCAs within its ESP rendered its system more vulnerable to attack. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate the violation of CIP-005-1 R1.5, SPPRE_URE1 completed its Mitigation Plans associated with its violations of CIP-003-1 R1, R4, R5, and R6, CIP-005-1 R2 and R3, and CIP-007-1 R1, R3, R5, R6, R8 and R9. SPPRE_URE1 ensured not only that its CCAs are protected pursuant to those requirements, but also that its CAs used in the access control and/or monitoring of its ESP are afforded the same protective measures as required by CIP-005-3 R1.5. Also, SPPRE_URE1 developed a process to ensure that all newly implemented CAs will be afforded the protective measures as required by CIP-005-3 R1. | 2011-03-02 | 2011-03-17 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000395 | Settlement Agreement | SPPRE_URE1 reported in its Self-Certification that it was not in compliance with CIP-005-2 R2 because it had not documented configurations for all ports and services on Critical Cyber Assets (CCAs). Additionally, SPPRE_URE1 did not have explicit default deny rules set for outbound communications through one firewall that was protecting a web console server, and it did not have technical procedures to log unauthorized outbound communications from both trusted and entrusted interfaces. | CIP-005-1 | 2 | Medium | High | The SPP RE determined that SPPRE_URE1's violation of CIP-005-1 R2 posed a minimal risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk because SPPRE_URE1 followed the required manufacturer (Siemens) configurations for ports and services which represent the majority of its Critical Cyber Asset (CCA) equipment. SPPRE_URE1 had also implemented a control mode that denies by default on most of its electronic access points to the SPPRE_URE1 ESP. The only electronic access point without deny by default settings was at the web console server, which was used solely for capturing and transmitting EMS/SCADA images. Only outbound communications, not inbound communications, were missing deny by default protection. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-005-1 R2, SPPRE_URE1 took the following actions: reviewed all of its current firewall configurations for correctness; ensured that all default deny configurations were applied in all of its firewall rules for inbound and outbound communications; documented baseline configurations of all of its firewalls including comments on the use of open ports; reviewed all of its ports and services configurations for correctness; documented baseline configurations of all ports and services including the use for all CCA devices; and developed a procedure associated with ports and service and firewall configurations. | 2010-11-04 | 2010-11-23 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000396 | Settlement Agreement | SPPRE_URE1 reported in its Self-Certification that it was not compliant with CIP-005-2 R3 because SPPRE_URE1 had not developed a logging and monitoring program for unauthorized attempts and access within its Energy Management System (EMS) network for all access points of its Electronic Security Perimeter (ESP). Additionally, SPPRE_URE1 did not have a logging procedure for security events for Linux OS, Windows, firewalls, switches and routers. | CIP-005-1 | 3 | Medium | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-005-1 R3 posed a moderate risk to the reliability of the bulk power system (BPS) and did not pose a serious or substantial risk because, SPPRE_URE1 began to use TripWire to monitor its system. However, SPPRE_URE1 was not utilizing a logging and monitoring process prior to TripWire and the TripWire program did not monitor all EMS access points on the SPPRE_URE1 ESP. Due to the lack of a monitoring and logging program to monitor electronic access for all EMS access points within its ESP, SPPRE_URE1 did not have a method of detecting whether or not unauthorized attempts or access had occurred on its system. This left the ESP vulnerable to attacks and made it difficult to monitor for suspicious activity that may have occurred on the SPPRE_URE1 system, therefore decreasing the likelihood of early detection of a cyber attack and creating a moderate risk to the BPS. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-005-1 R3, SPPRE_URE1 completed the following actions: performed a feasibility assessment for an automated tool to enable security logging and monitoring; created a process for logging security events for access points to the ESP through an automated tool process; developed an updated policy for monitoring the security events through an automated tool or process; and trained all affected SPPRE_URE1 employees on the updated policy. | 2011-02-16 | 2011-03-17 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000397 | Settlement Agreement | SPPRE_URE1 reported in its Self-Certification that it was not compliant with CIP-005-2 R4 because SPPRE_URE1 had not developed a procedure to describe its vulnerability assessment process. Specifically, SPPRE_URE1 had not identified the steps utilized in performing the vulnerability assessment, the process for identifying the results of the vulnerability assessment, and it had not created an action plan to remediate or mitigate any vulnerabilities identified in the assessment. Additionally, SPPRE_URE1 could not provide evidence that it reviewed default accounts, passwords and Simple Network Management Protocol (SNMP) community strings inside its Electronic Security Perimeter (ESP) as part of its vulnerability assessment. SPPRE_URE1 performed its first vulnerability assessment on its ESP about ten months past the date it was required to comply with CIP-005-1 R4. | CIP-005-1 | 4 | Medium | Severe | The SPP RE determined that SPPRE_URE1's violation of CIP-005-1 R4 posed a moderate risk to the reliability of the bulk power system (BPS) but did not pose a serious or substantial risk because although SPPRE_URE1 had an outside contractor perform a vulnerability assessment, it did not utilize the results of the vulnerability assessment to create and implement action plans to remediate or mitigate the vulnerabilities that were identified. Because SPPRE_URE1 did not implement action plans to mitigate the vulnerabilities regarding the electronic access points on its ESP, there was not a guarantee that its ESP was secure. Further, because SPPRE_URE1 had not formally documented its vulnerability assessment process, there was a risk that the assessment would not be performed thoroughly and consistently. The vulnerability assessment conducted was in fact missing some elements required by CIP-005 R4. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-005-1 R4, SPPRE_URE1 identified the recommendations from its vulnerability assessment and developed and documented action plans to mitigate any vulnerabilities. SPPRE_URE1 developed a written procedure that included the scope of the vulnerability assessment, the steps required for completing the vulnerability assessment, the process for documenting the assessment results, and the process for mitigating the vulnerabilities found during the assessment. Additionally, SPPRE_URE1 developed a template to document the mitigation process for its vulnerability assessments. Finally, SPPRE_URE1 scheduled and performed a Vulnerability Assessment according to its new revised procedure. | 2011-02-25 | 2011-03-17 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000399 | Settlement Agreement | SPPRE_URE1 reported in its Self Certification, that it was not compliant with CIP-007-2 R2 because SPPRE_URE1 had not documented the proper configurations of enabled ports and services for all of its network devices within the Electronic Security Perimeter (ESP). Because there was not a documented baseline for comparison, SPPRE_URE1 was unable to determine if solely the ports and services required for normal and emergency operations of some of its devices were enabled at any given time. However, for all of its Siemens devices, SPPRE_URE1 had enabled and documented the ports and services that were required for operations. SPPRE_URE1 relied on the Security Administration Manual (Manual) supplied by Siemens to identify the ports and services that are required for its Energy Management System (EMS). Section 6.4 of the Manual lists the various unnecessary ports that should be disabled and the procedure for doing so. In Section 11.0, the Manual also provides details regarding which ports should be enabled to provide proper functioning to the SPPRE_URE1 EMS. SPPRE_URE1 verified that these are the only enabled ports during the installation of new Versions of software and also performed a review of the services file on each machine during the annual assessment of its Critical Cyber Assets (CCAs) inside the ESP. | CIP-007-1 | 2 | Medium | Moderate | The SPP RE has determined that SPPRE_URE1's violation of CIP-007-1 R2 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPPRE_URE1 had documented its ports and services for all of its Siemens devices within the ESP, and these devices were monitored by the SPPRE_URE1 EMS SCADA system. The Siemens devices within the ESP are deemed to be the most critical devices within the ESP. For all of its Siemens devices, SPPRE_URE1 had enabled and documented the ports and services that were required for operations and verified that these are the only enabled ports during the installation of new versions of software. SPPRE_URE1 also performed a review of the services file on each machine during the annual assessment of its Critical Cyber Assets (CCAs) inside the ESP. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-007-1 R2, SPPRE_URE1 reviewed all of its ports and services configurations for correctness and then documented baseline configurations of all ports and services taking into consideration that different ports and services are utilized during emergency situations. With the configurations, SPPRE_URE1 is able to ensure that only the ports and services required for normal and emergency operations are enabled. | 2010-11-04 | 2010-11-23 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000400 | Settlement Agreement | SPPRE_URE1 reported in its Self-Certification that it was not compliant with CIP-007-2 R3. SPP RE determined that SPPRE_URE1 did not document the reasons why certain security patches were not selected to be installed on Cyber Assets (CAs) within the Electronic Security Perimeter (ESP). SPPRE_URE1 did not document the compensating measures applied to mitigate risk exposure or an acceptance of risk when a security patch was not chosen for installation. However, SPPRE_URE1 had evaluated all security patches that were installed within its ESP and documented when a security patch was installed. | CIP-007-1 | 3 | Lower | Severe | The SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R3 posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS) because SPPRE_URE1 had documented when security patches were installed for CAs within the ESP and the reason why a particular security patch was installed. Because SPPRE_URE1 was reviewing all security patches to determine whether or not a patch should be installed, the violation had a minimal impact on the reliability of the BPS because SPPRE_URE1 was only lacking the documentation of the rationale for not installing particular security patches. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-007-1 R23, SPPRE_URE1 developed a security patch management policy to identify and review all applicable security patches for all CAs within its ESP within 30 days of the patch release. In its revised policy, SPPRE_URE1 included requirements for documenting rationale and any compensating measures for patches that were not installed. SPPRE_URE1 created a template that will be used when a new patch is reviewed for consideration and implemented its security patch management program to follow the defined templates, forms and change systems. Finally, SPPRE_URE1 trained its affected employees on the patch management policy and documented attendance of the training. | 2010-11-12 | 2010-11-23 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000401 | Settlement Agreement | SPPRE_URE1 reported in its Self Certification that it was not compliant with CIP-007-2 R5 because it had not established, implemented, and documented sufficient controls to enforce the access authentication of, and accountability for, all user activity on individual and shared user accounts. SPPRE_URE1 did not have a policy in place to ensure that user accounts were implemented and approved by designated personnel, as required by R5.1.1. Further, SPPRE_URE1's system logs were not capturing data on its network devices sufficient to maintain 90-day audit trails of user account activity as required by R5.1.2. SPPRE_URE1 did not perform an annual review of specific access privileges to its Critical Cyber Assets (CCAs) for 2009. With regard to R5.2, SPPRE_URE1 did not have a policy for managing its shared and generic account privileges and did not maintain a list of persons with access to those accounts. | CIP-007-1 | 5 | Lower | Severe | The SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R5 posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although SPPRE_URE1 was not managing a proper environment for security, it had been performing an annual review of the general access privileges to its CCAs. Because SPPRE_URE1 was not reviewing specific access privileges to its CCAs, the potential existed for someone to falsify an account and have free use of SPPRE_URE1's system. In failing to adequately monitor its system, SPPRE_URE1 left its system more vulnerable to attack, which in turn created reliability risk to its system and the BPS. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-007-1 R5, SPPRE_URE1 developed a comprehensive list of all shared, default and generic accounts for all CCA devices and the SPPRE_URE1 personnel who have access to those accounts. SPPRE_URE1 developed processes for new shared accounts that are created or deleted and for an annual review to be performed on the list of employees who have access to its CCAs and each employee’s privileges. Also, SPPRE_URE1 developed a process to ensure that all security related information is properly logged and maintained. SPPRE_URE1 completed its mitigation of CIP-005-1 R3, which implemented its logging and monitoring system. Finally, SPPRE_URE1 updated the applicable policies to include the revised account management procedures. | 2011-02-18 | 2011-03-17 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000402 | Settlement Agreement | SPPRE_URE1 reported in its Self Certification that it was not compliant with CIP-007-2 R6 because SPPRE_URE1 had not implemented tools or controls to monitor for, alert personnel of, and retain and review logs of security events on Cyber Assets (CAs) within the Electronic Security Perimeter (ESP) on the Energy Management System (EMS) network and SPPRE_URE1 failed to create a program to log, monitor, identify, review and react to security events on all Cyber Assets within the ESP. | CIP-007-1 | 6 | Lower | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R6 posed a moderate and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SPPRE_URE1 began to use TripWire to monitor its system. However, prior to that date, the entity did not have an alternative system in place to monitor its system and TripWire program did not monitor all CAs within the EMS network. Due to the lack of a monitoring and logging program to monitor CAs within the EMS network, SPPRE_URE1 did not have a method of detecting whether or not unauthorized attempts to tamper with the CAs had occurred within the EMS network. This left SPPRE_URE1’s CAs vulnerable to attacks and made it difficult to monitor for suspicious activity that may have occurred on the SPPRE_URE1 system, therefore decreasing the likelihood of early detection of a cyber attack and creating a moderate risk to the BPS. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-007-1 R6, SPPRE_URE1 performed a feasibility assessment for an automated tool to enable security logging and monitoring. SPPRE_URE1 then implemented the chosen automated tool for logging security events for its CAs within its EMS. A policy for monitoring security events through the automated tool and process was developed and included procedures with detailed requirements for retention of electronic access logs for at least 90 days, and for at least 3 years for security-related incidents. Finally, SPPRE_URE1 trained and documented attendance of training for all employees who are responsible for implementing and following the updated policy and procedures. | 2011-02-16 | 2011-03-17 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000403 | Settlement Agreement | SPPRE_URE1 reported in its Self Certification that it was not compliant with CIP-007-2 R8 because SPPRE_URE1 had not developed a procedure describing its vulnerability assessment process. SPPRE_URE1 had not identified the steps that it utilized to perform the vulnerability assessment and to review and document the results. Further, SPPRE_URE1 had not created an action plan to remediate or mitigate any vulnerabilities identified in the assessment. Additionally, SPPRE_URE1 could not provide evidence that it reviewed controls for default accounts as required by R8.3. SPPRE_URE1 performed its first vulnerability assessment on its Critical Assets (CAs) within its ESP about ten months past the date it was required to comply with CIP-007-1 R8. | CIP-007-1 | 8 | Lower | Severe | SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R8 posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE1 performed a vulnerability assessment, it did not utilize the results of the vulnerability assessment to create and implement action plans to remediate or mitigate the vulnerabilities that were identified. Because SPPRE_URE1 did not implement action plans to mitigate the vulnerabilities regarding the electronic access points on its ESP, there was not reasonable assurance that its ESP was secure. Vulnerabilities that were identified in the assessment included, but were not limited to, firewall rules that did not ensure access was denied by default, the lack of a centralized logging and monitoring process, and some users on the SPPRE_URE1 system logging into the system under the root password. Further, because SPPRE_URE1 had not formally documented its vulnerability assessment process, there was a risk that the assessment would not be performed thoroughly and consistently. The vulnerability assessment conducted was in fact missing some elements required by CIP-007-1 R8. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-007-1 R8, SPPRE_URE1 identified the recommendations from its Vulnerability Assessment and developed and documented action plans to mitigate any vulnerabilities. SPPRE_URE1 developed a written procedure that included the scope of the vulnerability assessment, the steps required for completing the vulnerability assessment, the process for documenting the assessment results and the process for mitigating the vulnerabilities found during the assessment. Additionally, SPPRE_URE1 developed a template to document the mitigation process for its vulnerability assessments. Finally, SPPRE_URE1 scheduled and performed a Vulnerability Assessment according to its new revised procedure. | 2011-02-25 | 2011-03-17 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000404 | Settlement Agreement | SPPRE_URE1 reported in its Self Certification that it was not compliant with CIP-007-2 R9 because SPPRE_URE1 did not have documentation that it had performed an annual review of the documents and procedures it maintains pursuant to CIP-007. Additionally, SPPRE_URE1 failed to document changes resulting from modifications to the systems and controls required under CIP-007 within ninety calendar days of those changes. | CIP-007-1 | 9 | Lower | Severe | The SPP RE determined that SPPRE_URE1's violation of CIP-007-1 R9 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because it had documentation and procedures referenced in CIP-007 but did not have evidence that it reviewed and updated its documentation annually. Therefore, this is an issue of documentation and SPPRE_URE1’s lack of performance is addressed in its corresponding CIP-007 violations. | The date SPPRE_URE1 was required to comply with the Reliability Standard | The date the Mitigation Plan was completed | $68,000 (Settlement of SPP201000288, SPP201000289, SPP201000394, SPP201000395. SPP201000396, SPP201000397, SPP201000399, SPP201000400, SPP201000401, SPP201000402, SPP201000403, and SPP201000404) | Self-Certification | To mitigate its violation of CIP-007-1 R9, SPPRE_URE1 completed its Mitigation Plans for CIP-007 R1, R2, R3, R5, R6 and R8 and developed a procedure to review all documents and procedures referenced in CIP-007 at least annually and any changes that result from the review will be documented within 90 calendar days. | 2011-02-28 | 2011-03-17 | Does Not Contest | SPPRE_URE1 implemented a formal Internal Compliance Program and SPP RE considered it to be a mitigating factor in determining the penalty amount for the instant violations.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000130 | Settlement Agreement | Texas RE_URE1 is required under CIP-005-1 R2, at all access points to the Electronic Security Perimeter (ESP), to enable only ports and services required for operations and to monitor Cyber Assets within the ESP, and to document the configuration of those ports and services. Texas RE_URE1 determined it was necessary to increase the level of detail in its procedures, programs, supporting documentation, and evidence regarding the CIP-002 through CIP-009 Reliability Standards. As a result, all scans and associated enabling/disabling of ports and services which should have been completed by a certain time but were not completed until almost a month later, when Texas RE_URE1's ports and services acceptability procedure document was approved, dated and signed. | CIP-005-1 | R2; R2.2 | Medium | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not verifying and providing documentation and proof of controlling performance between when it was required to comply with the Standard and it when it afforded a possible intruder the opportunity to gain unauthorized access into the ESP. However, Texas RE_URE1 reported that it had in place certain compensating measures to mitigate risk including two firewalls and physical access restrictions. Texas RE_URE1 reported that the appropriate ports and services were enabled and disabled all along but that it had failed to timely document them. Lastly, Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-005-1 | Mitigation Plan Completion | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-005-1 R2. In accordance with the Mitigation Plan, Texas RE_URE1 completed the cyber vulnerability assessment process, ports and services documentation, and review of accounts as required by the Standard. The procedure document was approved, dated and signed by the authorized senior manager and fully implemented by Texas RE_URE1. | 2010-01-27 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000132 | Settlement Agreement | Texas RE_URE1 is required under CIP-005-1 R2, at all access points to the Electronic Security Perimeter (ESP), to enable only ports and services required for operations and to monitor Cyber Assets within the ESP, and to document the configuration of those ports and services. Texas RE_URE1 determined it was necessary to increase the level of detail in its procedures, programs, supporting documentation, and evidence regarding the CIP-002 through CIP-009 Reliability Standards. As a result, all scans and associated enabling/disabling of ports and services which should have been completed by a certain time but were not completed until almost a month later, when Texas RE_URE1's ports and services acceptability procedure document was approved, dated and signed. | CIP-005-1 | R2; R2.2 | Medium | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not verifying and providing documentation and proof of controlling performance between when it was required to comply with the Standard and it when it afforded a possible intruder the opportunity to gain unauthorized access into the ESP. However, Texas RE_URE1 reported that it had in place certain compensating measures to mitigate risk including two firewalls and physical access restrictions. Texas RE_URE1 reported that the appropriate ports and services were enabled and disabled all along but that it had failed to timely document them. Lastly, Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-005-1 | Mitigation Plan Completion | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-005-1 R2. In accordance with the Mitigation Plan, Texas RE_URE1 completed the cyber vulnerability assessment process, ports and services documentation, and review of accounts as required by the Standard. The procedure document was approved, dated and signed by the authorized senior manager and fully implemented by Texas RE_URE1. | 2010-01-27 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000131 | Settlement Agreement | Texas RE_URE1 is required under CIP-005-1 R4, to perform a cyber vulnerability assessment of the electronic access points to the ESP at least annually, which is to include certain information. Texas RE_URE1 determined it was necessary to increase the level of detail in its procedures, programs, supporting documentation, and evidence regarding the CIP-002 through CIP-009 Reliability Standards. As a result, Texas RE_URE1 did not complete the following until early in 2010: a document identifying the vulnerability assessment process; its review to verify that only ports and services required for operations at electronic access points was enabled; its review of controls for default accounts, passwords, and network management community strings; and document the results of the assessment. | CIP-005-1 | R4; R4.1; R4.2; R4.4; R4.5 | Medium | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not verifying and providing documentation and proof of controlling performance between the date it was required to comply with the Standard and when it afforded a possible intruder the opportunity to gain unauthorized access into the ESP. However, Texas RE_URE1 reported that it had in place certain compensating measures to mitigate risk including two firewalls and physical access restrictions. Texas RE_URE1 reported that the appropriate ports and services were enabled and disabled all along but that it had failed to timely document them. Lastly, Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-005-1 | The date on which Texas RE_URE1 completed documenting its cyber vulnerability assessment process | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-005-1 R4. In accordance with the Mitigation Plan, Texas RE_URE1 completed the cyber vulnerability assessment process, ports and services documentation, and review of accounts as required by the Standard. The procedure document was approved, dated and signed by the authorized senior manager and fully implemented by Texas RE_URE1. | 2010-01-27 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000133 | Settlement Agreement | Texas RE_URE1 is required under CIP-005-1 R4, to perform a cyber vulnerability assessment of the electronic access points to the ESP at least annually, which is to include certain information. Texas RE_URE1 determined it was necessary to increase the level of detail in its procedures, programs, supporting documentation, and evidence regarding the CIP-002 through CIP-009 Reliability Standards. As a result, Texas RE_URE1 did not complete the following until early in 2010: a document identifying the vulnerability assessment process; its review to verify that only ports and services required for operations at electronic access points; its review of controls for default accounts, passwords, and network management community strings; and document the results of the assessment. | CIP-005-1 | R4; R4.1; R4.2; R4.4; R4.5 | Medium | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not verifying and providing documentation and proof of controlling performance between the date it was required to comply with the Standard and when it afforded a possible intruder the opportunity to gain unauthorized access into the ESP. However, Texas RE_URE1 reported that it had in place certain compensating measures to mitigate risk including two firewalls and physical access restrictions. Texas RE_URE1 reported that the appropriate ports and services were enabled and disabled all along but that it had failed to timely document them. Lastly, Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-005-1 | The date on which Texas RE_URE1 completed documenting its cyber vulnerability assessment process | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-005-1 R4. In accordance with the Mitigation Plan, Texas RE_URE1 completed the cyber vulnerability assessment process, ports and services documentation, and review of accounts as required by the Standard. The procedure document was approved, dated and signed by the authorized senior manager and fully implemented by Texas RE_URE1. | 2010-01-27 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000227 | Settlement Agreement | Texas RE_URE1 is required under CIP-007-1 R2, to enable only those ports and services required for normal and emergency operations. Texas RE_URE1 did this for 84.6% of its servers by the date it was required to be compliant the rest were enabled prior to the end of the month. The Standard further requires that Texas RE_URE1 disable all other ports and services prior to production use of all Cyber Assets inside the ESP. Texas RE_URE1 did this for 80.8% of its servers by the date it was required to be compliant the rest were disabled prior to the end of the month. Where unused ports and services cannot be disabled due to technical limitations, Texas RE_URE1 is required under the Standard to document compensating measures applied to mitigate risk exposure or an acceptance of risk. Texas RE_URE1 completed this documentation for 80.8% of its servers by the date it was required to be compliant the rest were documented prior to the end of the month. Thus in each instance, Texas RE_URE1 was in violation of the Standard for less than a month. | CIP-007-1 | R2; R2.1; R2.2; R2.3 | Medium | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not documenting and/or verifying performance, afforded a possible intruder the opportunity to gain unauthorized access into the ESP. The potential risk to the BPS was moderate as the correct and appropriate ports and services were enabled/disabled for the duration of this violation. The procedures described were of a verification and documentation nature for purposes of complying with CIP-007-1. In addition, the violation period was relatively brief and Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-007-1 | The last date Texas RE_URE1 was out of compliance with CIP-007-1 R2 | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-007-1 R2. In accordance with the Mitigation Plan, Texas RE_URE1 completed documentation for enabling required ports and services, disabling other ports and services, and compensating measures in cases where ports and services cannot be disabled. The procedure document was approved, dated and signed by the authorized senior manager and fully implemented by Texas RE_URE1. | 2010-01-29 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000233 | Settlement Agreement | Texas RE_URE1 is required under CIP-007-1 R2, to enable only those ports and services required for normal and emergency operations. Texas RE_URE1 did this for 84.6% of the servers by the date it was required to be compliant and the rest were enabled by the end of the month. The Standard further requires that Texas RE_URE1 disable all other ports and services prior to production use of all Cyber Assets inside the ESP. Texas RE_URE1 did this for 80.8% of its servers by the date it was required to be compliant the rest were disabled by the end of the month. Where unused ports and services cannot be disabled due to technical limitations, Texas RE_URE1 is required under the Standard to document compensating measures applied to mitigate risk exposure or an acceptance of risk. Texas RE_URE1 completed this documentation for 80.8% of its servers by the date it was required to be compliant the rest were documented prior to the end of the month. Thus in each instance, Texas RE_URE1 was in violation of the Standard for less than a month. | CIP-007-1 | R2; R2.1; R2.2; R2.3 | Medium | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not documenting and/or verifying performance, afforded a possible intruder the opportunity to gain unauthorized access into the ESP. The potential risk to the BPS was moderate as the correct and appropriate ports and services were enabled/disabled for the duration of this violation. The procedures described were of a verification and documentation nature for purposes of complying with CIP-007-1. In addition, the violation period was relatively brief and Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-007-1 | The last date Texas RE_URE1 was out of compliance with CIP-007-1 R2 | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-007-1 R2. In accordance with the Mitigation Plan, Texas RE_URE1 completed documentation for enabling required ports and services, disabling other ports and services, and compensating measures in cases where ports and services cannot be disabled. The procedure document was approved, dated and signed by the authorized senior manager and fully implemented by Texas RE_URE1. | 2010-01-29 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000230 | Settlement Agreement | Texas RE_URE1 is required under CIP-007-1 R6, to ensure that its Cyber Assets within the ESP have security monitoring tools which issue automated or manual alerts for detected Cyber Security Incidents. Between the date it was required to be compliant and the first two weeks, 15.8% of Texas RE_URE1's Cyber Assets were not monitored preventing recognition of automated or manual alerts issued for detected Cyber Security Incidents. | CIP-007-1 | R6; R6.2 | Lower | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not documenting and/or verifying performance, afforded a possible intruder the opportunity to gain unauthorized access into the ESP. The potential risk to the BPS was moderate as the correct and appropriate ports and services were enabled/disabled for the duration of this violation. The procedures described were of a verification and documentation nature for purposes of complying with CIP-007-1. In addition, the violation period was relatively brief and Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-007-1 | When proper monitoring resumed | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-007-1 R6. In accordance with the Mitigation Plan, Texas RE_URE1 completed the appropriate monitoring on Cyber Assets within the ESP. The procedure was fully implemented by Texas RE_URE1. | 2010-01-29 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000236 | Settlement Agreement | Texas RE_URE1 is required under CIP-007-1 R6, to ensure that its Cyber Assets within the ESP have security monitoring tools which issue automated or manual alerts for detected Cyber Security Incidents. Between the date it was required to be compliant and the first two weeks 5.8% of Texas RE_URE1's Cyber Assets were not monitored preventing recognition of automated or manual alerts issued for detected Cyber Security Incidents. | CIP-007-1 | R6; R6.2 | Lower | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not documenting and/or verifying performance, afforded a possible intruder the opportunity to gain unauthorized access into the ESP. The potential risk to the BPS was moderate as the correct and appropriate ports and services were enabled/disabled all along. The procedures described were of a verification and documentation nature for purposes of complying with CIP-007-1. In addition, the violation period was relatively brief and Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-007-1 | When proper monitoring resumed | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-007-1 R6. In accordance with the Mitigation Plan, Texas RE_URE1 completed the appropriate monitoring on Cyber Assets within the ESP. The procedure was fully implemented by Texas RE_URE1. | 2010-01-29 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000232 | Settlement Agreement | Texas RE_URE1 is required under CIP-007-1 R8, to perform a cyber vulnerability assessment of all Cyber Assets within the ESP at least annually. Texas RE_URE1 failed to comply with this Standard in several respects. First, Texas RE_URE1 did not complete and approve its Cyber Asset Vulnerability Assessment Process document until almost a month after it was required to comply with the Standard. Second, for 15.4% of its servers, Texas RE_URE1 did not finalize all work necessary to verify that only those ports and services required for normal and emergency operations were enabled until almost a month after it was required to comply with the Standard. Third, Texas RE_URE1 finalized its review of controls for default accounts and finalized the results of the assessment almost a month after it was required to comply with the Standard. | CIP-007-1 | R8; R8.1; R8.2; R8.3; R8.4 | Lower | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not documenting and/or verifying performance, afforded a possible intruder the opportunity to gain unauthorized access into the ESP. The potential risk to the BPS was moderate as the correct and appropriate ports and services were enabled/disabled all along. The procedures described were of a verification and documentation nature for purposes of complying with CIP-007-1. In addition, the violation period was relatively brief and Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-007-1 | The date Texas RE_URE1 had a vulnerability assessment process document | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-007-1 R8. In accordance with the Mitigation Plan, Texas RE_URE1 completed its annual cyber vulnerability assessment of all Cyber Assets within the ESP. The procedure was fully implemented by Texas RE_URE1. | 2010-01-29 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201000238 | Settlement Agreement | Texas RE_URE1 is required under CIP-007-1 R8, to perform a cyber vulnerability assessment of all Cyber Assets within the ESP at least annually. Texas RE_URE1 failed to comply with this Standard in several respects. First, Texas RE_URE1 did not complete and approve its Cyber Asset Vulnerability Assessment Process document until almost a month after it was required to comply with the Standard. Second, for 15.4% of its servers, Texas RE_URE1 did not finalize all work necessary to verify that only those ports and services required for normal and emergency operations were enabled until almost a month after it was required to comply with the Standard. Third, Texas RE_URE1 finalized its review of controls for default accounts and finalized the results of the assessment almost a month after it was required to comply with the Standard. | CIP-007-1 | R8; R8.1; R8.2; R8.3; R8.4 | Lower | N/A (VSLs for NERC Standards CIP-002 through CIP-009 were not approved by FERC until March 18, 2010). | Texas RE determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE_URE1, by not documenting and/or verifying performance, afforded a possible intruder the opportunity to gain unauthorized access into the ESP. The potential risk to the BPS was moderate as the correct and appropriate ports and services were enabled/disabled all along. The procedures described were of a verification and documentation nature for purposes of complying with CIP-007-1. In addition, the violation period was relatively brief and Texas RE_URE1 indicated that there were no breaches of security for the time period in question. | The date on which Texas RE_URE1 was subject to compliance with CIP-007-1 | The date Texas RE_URE1 had a vulnerability assessment process document | $10,000 (for TRE201000130, TRE201000132, TRE201000131, TRE201000133, TRE201000227, TRE201000233, TRE201000230, TRE201000236, TRE201000232, and TRE201000238) | Self-Report | Texas RE_URE1 submitted a Mitigation Plan to Texas RE to address the violation of CIP-007-1 R8. In accordance with the Mitigation Plan, Texas RE_URE1 completed its annual cyber vulnerability assessment of all Cyber Assets within the ESP. The procedure was fully implemented by Texas RE_URE1. | 2010-01-29 | 2011-07-20 | Neither Admits nor Denies | Texas RE_URE1's compliance program was considered a mitigating factor in the determination of the penalty amount.
2011-12-30 | FERC | NP12-10-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102598 | Notice of Confirmed Violation | WECC_URE1 submitted a Self-Report stating that it failed to secure Cyber Assets provisioning physical access control and monitoring (PACM) to its Physical Security Perimeters (PSPs) in violation of CIP-006-1 R1 R1.8. WECC determined that the scope of the violation included fourteen Cyber Assets. Specifically, WECC determined that WECC_URE1 failed to identify two Cyber Assets as Cyber Assets provisioning access control and monitoring. Further WECC determined that WECC_URE1 failed to afford protective measures described under CIP-005-1 R2, CIP-007-1 R2, R3, R5 and R8, and CIP-009-1 R5 to three Cyber Assets; and, WECC_URE1 did not afford two protective measures (CIP-008-1 R8 and CIP-009-1 R5) to nine Cyber Assets provisioning access control and monitoring. | CIP-006-1 | R1; R1.8 | Lower | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was offset given the limited scope of WECC_URE1's violation. Nine of the twelve devices in scope were identified as Cyber Assets provisioning access control and monitoring. Even Cyber Assets that were not identified as access points, were equipped with protections that limited access. WECC_URE1's PACM network design. WECC_URE1's PSPs are dedicated to a specific network, which operates in a complete isolation, thus reducing the risk to the BPS. Further, the PACM network itself is physically and electronically isolated, and access to it is controlled and monitored. | The date on which WECC_URE1 was required to be compliant with CIP-006-1 | The date on which WECC_URE1 revised its physical security plan to comply with R1.8 | 5600 | Self-Report | WECC_URE1 submitted a Mitigation Plan and took the following actions: 1) Reviewed and revised its existing CIP Critical Cyber Asset (CCA) procedures to increase their scope to include the addition of the PACM devices; 2) Utilized the revised procedures to implement each protective measure and documented successful completion of each procedure; 3) Agreed that every PACM device in all four identified classes will undergo all WECC_URE1 CIP procedures related to CIP-005 R2 and R3; CIP-007 R2 to R6 and R8; and CIP-009 R5; and 4) Incorporated all PACM assets used in the access control and monitoring of the PSP, which were previously contained in a separate program, into WECC_URE1's existing program for CCAs. | 2011-06-14 | 2011-11-18 | Accepts | WECC_URE1 has an internal compliance program which WECC considered a mitigating factor.
2011-12-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000633 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF for a possible violation of CIP-007-1 R1. RFC_URE1 reported that it installed a back-up hard drive on a computer inside an Electronic Security Perimeter (ESP) without providing the proper patch management designation for the computer. RFC_URE1 designated the computer to receive new patches before other devices, when it should have designated the computer to receive new patches after a testing and approval process occurs. As a result of this improper patch management designation, RFC_URE1 applied patches to the computer, without first performing the proper testing and documentation pursuant to CIP-007-1 R1. RF determined that RFC_URE1 violated CIP-007-1 R1 by failing to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the ESP do not adversely affect existing cyber security controls. | CIP-007-1 | R1 | Medium | High | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated because the computer at issue was only associated with RFC_URE1's lower voltage transmission equipment vs. the higher voltage transmission equipment, which is the basis for the substation's Critical Asset designation. Additionally, RFC_URE1 discovered the patch management designation error quickly, and fully tested the patches within three days of its premature application to the computer. | The date on which RFC_URE1 implemented a change to existing Cyber Assets within the ESP without ensuring that the change did not adversely affect existing security controls | The date on which RFC_URE1 completed testing the patches and corrected the patch management designation for the computer | $40,000 (for RFC201000633, RFC201000634, RFC201000635, RFC201000639) | Self-Report | RFC_URE1 tested the patches on the computer, performed a system impact assessment, corrected the computer's patch management designation, and implemented a new process for deployment of patch updates that includes additional approvals before installation of patches. | 2011-02-08 | 2011-04-05 | Admits | RF favorably considered certain aspects of RFC_URE1's compliance program. RF also considered RFC_URE1's violation history.
2011-12-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000634 | Settlement Agreement | RFC_URE1 submitted Self-Reports to RF for possible violations of CIP-006-1 R4 and CIP-006-1 R1.6. RFC_URE1 reported that it failed to log two unauthorized contractors' access to the Physical Security Perimeter (PSP) at a transmission line control house, pursuant to CIP-006-1 R4 and failed to escort them within the PSP, pursuant to CIP-006-1 R1.6. RF determined that RFC_URE1 violated CIP-006-1 R4 by failing to implement and document the technical and procedural mechanisms for logging physical entry at all access points to the PSP. The failure to log occurred when the two contractors returned from lunch. RFC_URE1 had properly logged and escorted them within the PSP earlier that day. Upon the contractors’ return from lunch, the escort returned to its vehicle to retrieve a tool for approximately two minutes. | CIP-006-1 | R4 | Lower | Moderate | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated because the contractors did not have electronic privileges to access the Critical Cyber Assets devices within the PSP. Additionally, the violations lasted approximately two minutes, and the two contractors did not perform any work and remained at the door waiting for their escort to return during the two minutes they were unescorted. In addition, the two contractors were familiar with the CIP standards and had worked on RFC_URE1 projects for 14 years. | The time period which RFC_URE1 failed to log physical access at a PSP access point for two contractors | When RFC_URE1 returned to following its logging procedures to comply with R4 | $40,000 (for RFC201000633, RFC201000634, RFC201000635, RFC201000639) | Self-Report | RFC_URE1 strengthened its awareness of security procedures by issuing a compliance assessment activity based on this scenario, and issuing a newsletter with similar content. RFC_URE1 also revised and implemented improved technical and procedural mechanisms for logging physical entry at all access points to the PSP, and developed visitor log training material. | 2010-11-30 | 2011-04-05 | Admits | RF favorably considered certain aspects of RFC_URE1's compliance program. RF also considered RFC_URE1's violation history.
2011-12-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000635 | Settlement Agreement | RFC_URE1 submitted Self-Reports to RF for possible violations of CIP-006-1 R4 and CIP-006-1 R1.6. RFC_URE1 reported that it failed to log two unauthorized contractors' access to the Physical Security Perimeter (PSP) at a transmission line control house, pursuant to CIP-006-1 R4 and failed to escort them within the PSP, pursuant to CIP-006-1 R1.6. RF determined that RFC_URE1 violated CIP-006-1 R4 by failing to implement and document the technical and procedural mechanisms for logging physical entry at all access points to the PSP. The failure to log occurred when the two contractors returned from lunch. RFC_URE1 had properly logged and escorted them within the PSP earlier that day. Upon the contractors’ return from lunch, the escort returned to its vehicle to retrieve a tool for approximately two minutes. | CIP-006-1 | R1; R1.6 | Medium | High | RF determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated because the contractors did not have electronic privileges to access the Critical Cyber Asset devices within the PSP. Additionally, the violations lasted approximately two minutes, and the two contractors did not perform any work and remained at the door waiting for their escort to return during the two minutes they were unescorted. In addition, the two contractors were familiar with the CIP standards and had worked on RFC_URE1 projects for 14 years. | The time period which RFC_URE1 failed to provide escorted access for 2 minutes | When RFC_URE1 returned to following its physical security plan procedures to comply with R1.6 | $40,000 (for RFC201000633, RFC201000634, RFC201000635, RFC201000639) | Self-Report | RFC_URE1 strengthened its awareness of security procedures by issuing a compliance assessment activity based on this scenario, and issuing a newsletter with similar content. RFC_URE1 also revised and implemented improved technical and procedural mechanisms for logging physical entry at all access points to the PSP, and developed visitor log training material. | 2010-05-30 | 2011-04-05 | Admits | RF favorably considered certain aspects of RFC_URE1's compliance program. RF also considered RFC_URE1's violation history.
2011-12-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000639 | Settlement Agreement | RFC_URE1 submitted Self-Reports to RF for a possible violation of CIP-004-1 R4.2. RFC_URE1 reported that while performing an internal review, it discovered that it failed to terminate physical access to Critical Cyber Assets (CCAs) to an employee who had resigned (Employee A). Access for Employee A was revoked 10 days later. RFC_URE1 also reported that while performing an internal review using a newly-developed account reporting tool, it discovered a second discrepancy involving the removal of an employee's system account access (Employee B) 29 days after the effective resignation date. Access for Employee B was revoked upon discovery. RF determined that RFC_URE1 violated CIP-004-1 R4.2 by failing to revoke access to CCAs within seven calendar days for two employees who no longer required such access to CCAs. | CIP-004-1 | R4; R4.2 | Medium | Moderate | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following facts. Employee A did not have remote electronic access to CCAs and RFC_URE1 confirmed that he did not use his physical access to CCAs beyond his last day of employment with RFC_URE1. Employee B had read-only access to CCAs and could access the firewalls to the CCAs only after passing through multiple layers of security beyond the basic account access that RFC_URE1 failed to revoke. Additionally, RFC_URE1 did revoke Employee B's physical access and primary means of electronic access to CCAs within the required seven-day period. | The date by which RFC_URE1 was required to revoke access and update its CCA access list for Employee A | The date on which RFC_URE1 revoked access and updated its CCA access list to remove Employee B | $40,000 (for RFC201000633, RFC201000634, RFC201000635, RFC201000639) | Self-Report | RFC_URE1 issued a newsletter to remind employees and supervisors about access removal requirements, added a new daily database query that searches for terminated and inactive employees who retain access and updated its NERC CIP training material to emphasize that employees should contact the help desk when handling personnel terminations. | 2011-01-31 | 2011-04-01 | Admits | RF favorably considered certain aspects of RFC_URE1's compliance program. RF also considered RFC_URE1's violation history.
2011-12-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) (affiliates RFC_URE2, RFC_URE3 and RFC_URE4 are collectively referred to herein as the Corporate Entities) | NCRXXXXX | RFC201100823 | Settlement Agreement | RFC_URE2 submitted a Self-Report identifying a violation of CIP-004-3 R4. RFC_URE2 failed to revoke within seven days the physical access rights of an individual who had physical access to two Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs) and who no longer required such access. The individual was a facilities management contract worker. RFC_URE2 failed to revoke the individual's access until 15 calendar days after the individual no longer required access. ReliabilityFirst found that RFC_URE2 violated the Standard by failing to revoke unescorted access within seven calendar days for an individual who no longer required such access. | CIP-004-3 | R4 | Lower | Moderate | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The individual never accessed the PSPs containing CCAs after RFC_URE2 determined that the individual no longer required access. As the individual had, at all relevant times, a valid personnel risk assessment and up-to-date cyber security training, the individual was eligible for unescorted physical access rights. | Date RFC_URE2 was required to revoke the individual's access | Date RFC_URE2 revoked the individual's access | $25,000 (for RFC201100823, RFC201100824, RFC201100825, RFC201100826, RFC201100827, and RFC201100858) | Self-Report | RFC_URE2 expanded its mitigating activities to correct the specific root cause of the violation. A facilities management supervisor was designated to oversee all facilities management contract workers to provide enhanced oversight and monitoring of CIP access. In addition, a procedure for facilities management directing the removal of access to CIP restricted areas for facilities management contract workers upon the completion of contract work was implemented. A review of the list of individuals with unescorted physical access to restricted areas solely for emergency or other situations in order to determine whether those individuals should retain unescorted physical access for certain CIP restricted areas was also implemented. Those who do not need to retain such access from the access list were removed. In addition, training was provided to supervisors of individuals with authorized cyber or authorized unescorted physical access to CIP restricted areas that reinforced the requirements of RFC_URE2's access control program. Furthermore, RFC_URE2 revoked the contract worker's access to the PSPs and counseled the supervisor on RFC_URE2's procedures for removing access to PSPs. | 2011-07-13 | 2011-10-31 | Neither Admits nor Denies | In assessing the penalty, ReliabilityFirst considered certain aspects of the Corporate Entities' compliance program as mitigating factors. ReliabilityFirst also considers as a mitigating factor that corporate is engaged in constant reevaluation of its system. ReliabilityFirst also considered the Corporate Entities' violation history.
2011-11-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) (affiliates RFC_URE2, RFC_URE3 and RFC_URE4 are collectively referred to herein as the Corporate Entities) | NCRXXXXX | RFC201100824 | Settlement Agreement | RFC_URE2 and RFC_URE3 submitted a Self-Report identifying a violation of CIP-005-1 R1. This constitutes one issue that affected both RFC_URE2 and RFC_URE3. During a network operational overview, RFC_URE2 and RFC_URE3 discovered an undocumented access point to the Electronic Security Perimeter (ESP). This access point was a router that allowed internal corporate information services department network traffic to flow through the ESP based on a network configuration for specific types of non-NERC CIP-related traffic originating outside the ESP to traverse the ESP in order to reach its destination, devices outside the ESP. This non-NERC CIP-related network traffic originated from traffic flows managed by information services department support personnel, all of whom are NERC CIP-cleared. There was no electronic access to Cyber Assets inside the ESP from use of this router, as network traffic was configured to traverse through the ESP, not to access Cyber Assets within the ESP. The router served the single ESP of RFC_URE2 and RFC_URE3 until when corporate redesigned the ESP. After that date, the router only served the RFC_URE3 ESP. | CIP-005-1 | R1 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The router only allowed traffic to traverse the ESP, not access it. The information traversing the ESP was non-critical information services department information. In addition, the RFC_URE2 and RFC_URE3 have in place strong procedural access controls to the router such as firewall rules and two-factor authentication. Furthermore, in order to gain access to the router, personnel must have had authorized access and authentication. The RFC_URE2 and RFC_URE3 granted a limited number of personnel access to the router and its physical surroundings, and all personnel with access had valid personnel risk assessments and current cyber security training. | Date RFC_URE2 was required to comply with CIP-005-1 | When the ESP was redesigned | $25,000 (for RFC201100823, RFC201100824, RFC201100825, RFC201100826, RFC201100827, and RFC201100858) | Self-Report | RFC_URE2 and RFC_URE3 eliminated the ESP access point by reconfiguring the router. In addition, RFC_URE2 and RFC_URE3 reviewed similar devices and documentation of another Corporate Entity in order to determine if the issue existed elsewhere and found that it did not. RFC_URE2 and RFC_URE3 reviewed and updated the information services department vulnerability assessment process to ensure it includes proper instructions to identify and analyze detailing routing tables. | 2011-06-30 | 2011-09-20 | Neither Admits nor Denies | In assessing the penalty, ReliabilityFirst considered certain aspects of the Corporate Entities' compliance program as mitigating factors. ReliabilityFirst also considers as a mitigating factor that corporate is engaged in constant reevaluation of its system. ReliabilityFirst also considered the Corporate Entities' violation history.
2011-11-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) (affiliates RFC_URE2, RFC_URE3 and RFC_URE4 are collectively referred to herein as the Corporate Entities) | NCRXXXXX | RFC201100825 | Settlement Agreement | RFC_URE3 submitted a Self-Report identifying a violation of CIP-004-3 R2. An individual processing an employee's request for access to a Physical Security Perimeter (PSP) containing Critical Cyber Assets (CCAs) believed that she correctly granted access rights to the employee. RFC_URE3 discovered that the individual mistakenly granted access rights to a contract worker who had the same first and last name, but a different middle initial, as the employee requesting access. Due to RFC_URE3's weekday daily reconciliation process during which RFC_URE3 reviews access rights each business day, RFC_URE3 discovered that it granted access to the contract worker who had not completed required training, in violation of CIP-004-3 R2.1. ReliabilityFirst found that RFC_URE3 violated the Standard by failing to ensure that all personnel having unescorted physical access to CCAs are trained prior to being granted such access. | CIP-004-3 | R2 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. RFC_URE3 granted the contract worker access rights for only 22 hours, during which the contract worker never accessed the PSP containing CCAs and was unaware that he had any such rights. Moreover, the process in place to verify correct access authorization promptly permitted RFC_URE3 to identify and eliminate the incorrectly authorized access rights before any access occurred. The corporate security daily reports review process facilitated correction of the issue in a time period shorter than the 24 hours allotted for removing access in other contexts. In addition, RFC_URE3 had previously granted this contract worker access to certain non-critical areas since September 2003. The contract worker currently has access to other Corporate Entities' areas, and during the time period that the contract worker had such access, there were no security events associated with the contract worker. | The date RFC_URE3 granted the contract worker access rights | The date RFC_URE3 revoked access rights | $25,000 (for RFC201100823, RFC201100824, RFC201100825, RFC201100826, RFC201100827, and RFC201100858) | Self-Report | RFC_URE3 expanded its mitigating activities to correct for the specific root cause in the instant violation. RFC_URE3 added a "peer check" step to the process of granting unescorted physical access rights to PSPs, whereby a second individual from corporate security verifies that the correct access is being given to the correct person prior to granting access in the security system. In addition, RFC_URE3 revoked the contract worker's access rights. | 2011-03-25 | 2011-09-19 | Neither Admits nor Denies | In assessing the penalty, ReliabilityFirst considered certain aspects of the Corporate Entities' compliance program as mitigating factors. ReliabilityFirst also considers as a mitigating factor that corporate is engaged in constant reevaluation of its system. ReliabilityFirst also considered the Corporate Entities' violation history.
2011-11-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) (affiliates RFC_URE2, RFC_URE3 and RFC_URE4 are collectively referred to herein as the Corporate Entities) | NCRXXXXX | RFC201100826 | Settlement Agreement | This violation is related to the above violation of CIP-004-3 R2 (RFC201100825). RFC_URE3 submitted a Self-Report to ReliabilityFirst identifying a possible violation of CIP-004-3 R3. RFC_URE3 mistakenly granted unescorted physical access to a Physical Security Perimeter (PSP) containing Critical Cyber Assets (CCAs) to the contract worker (described above in RFC201100825) who did not have a valid personnel risk assessment. | CIP-004-3 | R3 | Medium | High | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. RFC_URE3 granted the contract worker access rights for only 22 hours, during which the contract worker never accessed the PSP containing CCAs and was unaware that he had any such rights. Moreover, the process in place to verify correct access authorization promptly permitted RFC_URE3 to identify and eliminate the incorrectly authorized access rights before any access actually occurred. The corporate security daily reports review process facilitated correction of the issue in a time period shorter than the 24 hours allotted for removing access in other contexts. In addition, RFC_URE3 had previously granted this contract worker access to certain non-critical areas since September 2003. The contract worker currently has access to other Corporate Entities' areas, and during the time period that the contract worker had such access, there were no security events associated with the contract worker. | The date RFC_URE3 granted the contract worker access rights | The date RFC_URE3 revoked access rights | $25,000 (for RFC201100823, RFC201100824, RFC201100825, RFC201100826, RFC201100827, and RFC201100858) | Self-Report | RFC_URE3 expanded its mitigating activities to correct for the specific root cause in the instant violation. RFC_URE3 added a "peer check" step to the process of granting unescorted physical access rights to PSPs whereby a second individual from corporate security verifies that the correct access is being given to the correct person prior to granting access in the security system. In addition, RFC_URE3 revoked the contract worker's access rights. | 2011-03-25 | 2011-09-19 | Neither Admits nor Denies | In assessing the penalty, ReliabilityFirst considered certain aspects of the Corporate Entities' compliance program as mitigating factors. ReliabilityFirst also considers as a mitigating factor that corporate is engaged in constant reevaluation of its system. ReliabilityFirst also considered the Corporate Entities' violation history.
2011-11-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) (affiliates RFC_URE2, RFC_URE3 and RFC_URE4 are collectively referred to herein as the Corporate Entities) | NCRXXXXX | RFC201100827 | Settlement Agreement | RFC_URE2 and RFC_URE3 submitted a Self-Report identifying a violation of CIP-005-1 R1. This constitutes one issue that affected both RFC_URE2 and RFC_URE3. During a network operational overview, RFC_URE2 and RFC_URE3 discovered an undocumented access point to the Electronic Security Perimeter (ESP). This access point was a router that allowed internal corporate information services department network traffic to flow through the ESP based on a network configuration for specific types of non-NERC CIP-related traffic originating outside the ESP to traverse the ESP in order to reach its destination, devices outside the ESP. This non-NERC CIP-related network traffic originated from traffic flows managed by information services department support personnel, all of whom are NERC CIP cleared. There was no electronic access to Cyber Assets inside the ESP from use of this router, as network traffic was configured to traverse through the ESP, not to access Cyber Assets within the ESP. The router served the single ESP of RFC_URE2 and RFC_URE3 until when corporate redesigned the ESP. After that date, the router only served the RFC_URE3 ESP. | CIP-005-1 | R1 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The router only allowed traffic to traverse the ESP, not access it. The information traversing the ESP was non-critical information services department information. In addition, the RFC_URE2 and RFC_URE3 have in place strong procedural access controls to the router such as firewall rules and two-factor authentication. Furthermore, in order to gain access to the router, personnel must have had authorized access and authentication. The RFC_URE2 and RFC_URE3 granted a limited number of personnel access to the router and its physical surroundings, and all personnel with access had valid personnel risk assessments and current cyber security training. | Date RFC_URE3 was required to comply with CIP-005-1 | When the ESP access point was eliminated | $25,000 (for RFC201100823, RFC201100824, RFC201100825, RFC201100826, RFC201100827, and RFC201100858) | Self-Report | RFC_URE2 and RFC_URE3 eliminated the ESP access point by reconfiguring the router. In addition, RFC_URE2 and RFC_URE3 reviewed similar devices and documentation of another Corporate Entity in order to determine if the issue existed elsewhere and found that it did not. RFC_URE2 and RFC_URE3 reviewed and updated the information services department vulnerability assessment process to ensure it includes proper instructions to identify and analyze detailing routing tables. | 2011-06-30 | 2011-09-20 | Neither Admits nor Denies | In assessing the penalty, ReliabilityFirst considered certain aspects of the Corporate Entities' compliance program as mitigating factors. ReliabilityFirst also considers as a mitigating factor that corporate is engaged in constant reevaluation of its system. ReliabilityFirst also considered the Corporate Entities' violation history.
2011-11-30 | FERC | NP12-5-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) (affiliates RFC_URE2, RFC_URE3 and RFC_URE4 are collectively referred to herein as the Corporate Entities) | NCRXXXXX | RFC201100858 | Settlement Agreement | RFC_URE4 submitted a Self-Report to ReliabilityFirst identifying a violation of CIP-006-3c R1. RFC_URE4 discovered that an escort failed to maintain continuous control over two visitors for a five-hour period. The two visitors to the RFC_URE4 Physical Security Perimeter (PSP) were RFC_URE2 electrical test technicians who had authorized access to other PSPs, but not the specific PSP they accessed that day. RFC_URE4 attempted to limit those with unescorted physical access to PSPs, so it did not grant such access and instead required continuous escorted access for the visitors. The escort, who was the primary plant control operator, failed to follow the documented physical security plan by leaving the visitors in the room adjoining the escort's workspace. Therefore, the escort failed to maintain continuous escorted access of these two visitors, in violation of CIP-006-3c R1.6.2. ReliabilityFirst found that RFC_URE4 violated CIP-006-3c R1 by failing to implement its physical security plan when it failed to maintain continuous escorted access of visitors within the PSP. | CIP-006-3c | R1 | Medium | Severe | In light of the nature of the violation, offset by the mitigating factors, ReliabilityFirst determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The escort properly completed the visitor log forms documenting two visitors to the PSP. The two visitors were 34-year and 5-year RFC_URE2 employees. Both had a valid personnel risk assessment and current cyber security training at all relevant times. Therefore, they were eligible for unescorted physical access rights. | Date that RFC_URE4 failed to provide continuous escorted access of visitors within the PSP and failed to log out the visitors from the PSP | Date that RFC_URE4 failed to provide continuous escorted access of visitors within the PSP and failed to log out the visitors from the PSP | $25,000 (for RFC201100823, RFC201100824, RFC201100825, RFC201100826, RFC201100827, and RFC201100858) | Self-Report | RFC_URE4 counseled the escort for the two visitors on the proper procedures for escorting individuals without authorized unescorted physical access. In addition,RFC_URE4 revised its practice to disallow the primary plant control operator from performing the duties of an escort for visitors in most situations. Furthermore, RFC_URE4 provided refresher training to the appropriate personnel, including active supervisors, on the importance of ensuring proper escort procedures. | 2011-07-13 | 2011-10-31 | Neither Admits nor Denies | In assessing the penalty, ReliabilityFirst considered certain aspects of the Corporate Entities' compliance program as mitigating factors. ReliabilityFirst also considers as a mitigating factor that corporate is engaged in constant reevaluation of its system. ReliabilityFirst also considered the Corporate Entities' violation history.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002064 | Notice of Confirmed Violation | WECC_URE1 discovered this violation during an internal quarterly review and submitted a Self-Report. WECC_URE1 reported that one employee with authorized physical access to critical cyber assets (8 energy management system (EMS) workstations in the control center), missed CIP training, but WECC_URE1 removed access for this employee as soon as the violation was discovered. This employee did complete the CIP training in 2009. WECC_URE1 personnel further clarified that the employee missed training due to a process gap and that WECC_URE1 subsequently updated the process to trigger CIP training for applicable employees. The employee was temporarily working on a special project with the expectation that she would resume her regular duties after the completion of the project. Due to a Human Resources process gap, she was not appropriately flagged for CIP training during the special project and therefore she did not complete the annual CIP training within the required timeline. WECC_URE1 Human Resources Department is responsible for assigning CIP training to employees with CCA access by flagging each applicable employee in the system used to process employee payroll information. The flag then triggers CIP training to be added to each employee’s training plan in WECC_URE1’s learning system. Human Resources would remove the CIP training flag when they are notified that access has been removed. In this instance, Human Resources removed the CIP training flag when they were notified that the employee had a temporary job change to work on a special project, even though the employee retained his/her CCA access. WECC determined WECC_URE1 failed to maintain documentation that it conducts training at least annually, including the date the training was completed and attendance records as required by CIP-004-2 R2.3. WECC_URE1 allowed more than 13 months to pass between CIP training sessions for one individual with access to critical cyber assets. | CIP-004-2 | R2 | Lower | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because only one employee was involved in the violation. WECC_URE1’s compliance staff conducted an assessment to ensure that there were no other employees who were not adequately trained. The employee had been trained properly in the previous year. The employee had physical access to Critical Cyber Assets, but not cyber access to Critical Cyber Assets. In addition, the employee was past due on training for less than 2 months before WECC_URE1 revoked the employee’s access. Thus, the employee’s prior year training was less than 14 months old. | When the employee was due to receive training and therefore, WECC_URE1 should have had documentation showing training was conducted | When WECC_URE1 revoked the employee’s access | $18,2000 (for WECC201002064, WECC200901949, WECC201002009, WECC201002052) | Self-Report | Human Resources revised their internal process to remove the CIP training flag only after they receive confirmation from the Employment group within Human Resources that access must be removed. Additionally, upon notification that this employee’s 2010 training had not been completed, Compliance contacted the IT service desk and access was removed immediately. | 2010-07-02 | 2011-02-08 | Does Not Contest | WECC reviewed WECC_URE1’s Internal Compliance Program (ICP) which was in place at the time of the violations and applied a mitigating factor based on such review.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC200901949 | Notice of Confirmed Violation | This violation was discovered during an internal review and was submitted to WECC in a Self-Report. WECC_URE1 discovered its noncompliance through a Human Resources review of access and PRAs. One WECC_URE1 employee with cyber access to Critical Cyber Assets (CCAs) via an administrative group did not have a personnel risk assessment. WECC_URE1 had overlooked the employee because his name was not listed out individually as an employee with cyber access. He did not require access but did have cyber access because he belongs to an administrative group that can log onto the server on which the card access system runs. WECC_URE1 had provided training pursuant to CIP-004 R2 for the employee without the PRA. | CIP-004-1 | R3 | Lower | N/A | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1 provided training pursuant to CIP-004-1 R2 for the employee prior to the employee having cyber access. In addition, the employee’s access was limited to one server and not general access to all Cyber Assets or CCAs, specifically the employee had cyber access to CCAs and did not have unescorted physical access to CCAs. | When WECC_URE1 was required to be compliant with the Standard | When WECC_URE1 revoked access for the employee without a PRA | $18,2000 (for WECC201002064, WECC200901949, WECC201002009, WECC201002052) | Self-Report | Access for the individual without authorized CCA access was immediately removed and a new process was established for the Card Access servers. All default groups were removed from the Card Access servers including the Domain Admin group and normal system administration groups added to all servers built within the WECC_URE1 domain. A new process was implemented to prevent the issue from reoccurring by creating a global group on the domain specific to each Card Access server. In this new process, access to the Card Access servers can only be attained via membership in each server’s specific global group. Members of the group that receive access to a Card Access server are individually added to the specific global group (no nesting) and must be approved by the manager of security, as the access custodian, prior to access being granted. | 2009-11-06 | 2010-07-28 | Does Not Contest | WECC reviewed WECC_URE1’s Internal Compliance Program (ICP) which was in place at the time of the violations and applied a mitigating factor based on such review.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002009 | Notice of Confirmed Violation | This violation was discovered during an internal review, and WECC_URE1 submitted a Self-Report to WECC. WECC_URE1 made a configuration change to a physical access control device (specifically, card access servers). As a result of the change to the physical access control device, a Security Information and Event Management (SIEM) device did not collect the system access logs from the card access servers. Prior to making the configuration change, WECC_URE1 tested how such a configuration change would impact its operations. Testing of the change to the card access servers was not sufficient to detect the failure of the security control that addresses the collection of access logs. | CIP-006-1 | R1 | Lower | N/A | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE1 implemented a defense in depth strategy. Its card access servers are protected by an access control list within the WECC_URE1 corporate network security. All activity within the application log-ins was captured by backup or additional devices. The back-up and additional devices were not affected by the violation and did not detect abnormal or malicious activity. WECC_URE1 employs multiple layers of protection to detect and prevent unauthorized access. Additionally, prior to making the configuration change, WECC_URE1 tested how such a configuration change would impact its operations, as stated above. | When the cyber access group permissions were changed on the card access servers | When the SIEM device collected the system access logs | $18,2000 (for WECC201002064, WECC200901949, WECC201002009, WECC201002052) | Self-Report | WECC_URE1 added the domain service account to the global security groups. These groups are only domain groups with access to the servers, and this account is the account the SIEM application uses to access the servers to pull the logs back to the main repository. A manager of IT performed a review of the test procedures for the card access application against current practices and decided to create new process. This manager also created a testing verification log to verify that proper testing occurs prior to a change being implemented to an IT based system. The IT manager also provided training to the system administrators responsible for the card access servers on the changes to the Patch and Change management procedures. | 2011-04-07 | 2011-10-31 | Does Not Contest | WECC reviewed WECC_URE1’s Internal Compliance Program (ICP) which was in place at the time of the violations and applied a mitigating factor based on such review.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002052 | Notice of Confirmed Violation | WECC_URE1 discovered a violation of this Standard during a Post-outage compliance review, WECC_URE1 submitted a Self-Report addressing its noncompliance. WECC_URE1 stated on the Self-Report that at 1821, WECC_URE1 experienced an outage on a 230 kV line (Line A) and on a second 230 kV line (Line B). The Line A line is a part of a WECC path. WECC_URE1 stated on the Self-Report that one tagged transaction flowing on the line…was not curtailed. WECC_URE1 further stated on the Self-Report the Operating Transfer Capability was zero because of the outage. WECC_URE1 provided the following additional details on the Self-Report: The loss schedule in question averaged 3.5 MW/h, did not exceed 7 MW for any of the 15 hours that it was not curtailed, and did not impose a significant impact on the remaining parallel lines. The path limit in a west to east direction (the direction of the schedule) is 700 MW with the Line A line out of service. WECC determined WECC_URE1 is the path operator for the path and had a net schedule on a transmission element of an interconnection, which was out of service for a period of 15 hours. WECC_URE1 had a transmission element with a net schedule exceeding its operating limit. Thus, WECC_URE1 had a violation of TOP-STD-007-0 WR1. | TOP-STD-007-0 | WR1 | N/A | N/A | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the line was out of service, the transfer path was unaffected by this error, and no actual power flow occurred on the path since the transmission element was out of service. | When WECC_URE1 experienced the outage and did not curtail a tagged transaction | When the tag was curtailed | $18,2000 (for WECC201002064, WECC200901949, WECC201002009, WECC201002052) | Self-Report | WECC_URE1 took the following actions to mitigate the issue: 1) identified the modeling error that caused WECC_URE1 to not curtail the tag and directed an operations analyst to correct the error; 2) Initiated a review to ensure all line segments were modeled correctly and had not impacted curtailment procedures; and 3) Changed the process by which it modifies the OATI model to include a review and approval process. | 2010-03-31 | 2011-03-11 | Does Not Contest | WECC reviewed WECC_URE1’s Internal Compliance Program (ICP) which was in place at the time of the violations and applied a mitigating factor based on such review.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002418 | Settlement Agreement | WECC_URE2 self-reported violations of CIP-007-1 R4 and R5. WECC_URE2 filed technical feasibility exceptions (TFEs) for the devices within the scope of the self-reported violations. Three affiliates of WECC_URE2 submitted TFEs for the same devices in the ReliabilityFirst Corporation Region and received the TFE Notices of Acceptances. These devices are located in a facility in the ReliabilityFirst Region and are used as part of a common security system for assets owned by various NERC registered affiliates located in multiple reliability regions. Specifically, the vender locked down the configuration for a security console. | CIP-007-1 | R4 | Medium | Lower | WECC determined that the violation did not pose a serious or substantial and posed a minimal risk to the reliability of the bulk power system (BPS) because the TFEs were valid and ultimately approved by WECC. WECC determined that the violation occurred because the TFEs were filed late. | The date the TFEs were due to be filed | The date WECC_URE2 filed the TFE | $6,000 (for WECC201002418, WECC201002419, WECC201002433, WECC201002442, WECC201002443, WECC201002907) | Self-Report | WECC_URE2 filed a Mitigation Plan with WECC, stating that the violations of R4 and R5 were mitigated when WECC_URE2 filed a TFEs with WECC. WECC_URE2's filing and acceptance of the TFEs by WECC mitigated the violation. | 2010-09-24 | 2011-07-11 | Neither Admits nor Denies | WECC determined that: 1)The violations posed a minimal risk to the reliability of the BPS; 2) The violations were self-reported by WECC_URE2; 3) The violations have a Lower and Medium VRFs and Lower and Moderate VSLs; 3) The Violations do not pose an ongoing risk to the BPS; and 4) There were no aggravating factors for determining the penalty amount.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002419 | Settlement Agreement | WECC_URE2 self-reported violations of CIP-007-1 R4 and R5. WECC_URE2 filed technical feasibility exceptions (TFEs) for the devices within the scope of the self-reported violations. Three affiliates of WECC_URE2 submitted TFEs for the same devices in the ReliabilityFirst Corporation Region and timely received the TFE Notices of Acceptances. These devices are located in a facility in the ReliabilityFirst Region and are used as part of a common security system for assets owned by various NERC registered affiliates located in multiple reliability regions. Specifically, the Protective Relay uses a proprietary operating system and is incapable of account management. | CIP-007-1 | R5 | Lower | Lower | WECC determined that the violation did not pose a serious or substantial and posed a minimal risk to the reliability of the bulk power system (BPS) because the TFEs were valid and ultimately approved by WECC. WECC determined that the violation occurred because the TFEs were filed late. | The date the TFEs were due to be filed | The date WECC_URE2 filed the TFE | $6,000 (for WECC201002418, WECC201002419, WECC201002433, WECC201002442, WECC201002443, WECC201002907) | Self-Report | WECC_URE2 filed a Mitigation Plan with WECC, stating that the violations of R4 and R5 were mitigated when WECC_URE2 filed a TFEs with WECC. WECC_URE2's filing and acceptance of the TFEs by WECC mitigated the violation. | 2010-09-24 | 2011-07-11 | Neither Admits nor Denies | WECC determined that: 1)The violations posed a minimal risk to the reliability of the BPS; 2) The violations were self-reported by WECC_URE2; 3) The violations have a Lower and Medium VRFs and Lower and Moderate VSLs; 3) The Violations do not pose an ongoing risk to the BPS; and 4) There were no aggravating factors for determining the penalty amount.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002433 | Settlement Agreement | WECC_URE2, as a GO and GOP, self-reported a violation of CIP-006-2 R1. WECC_URE2 stated that one newly hired WECC_URE2 employee was permitted access to its control center at WECC_URE2's generation plant, a Physical Security Perimeter (PSP), containing four Critical Cyber Assets (CCAs), before the employee was given unescorted access rights. The employee was not accompanied by an escort even though he had not yet been given unescorted access rights, in violation of this Standard. | CIP-006-2 | R1 | Medium | Moderate | WECC determined that the violation did not pose a serious or substantial and posed a minimal risk to the reliability of the bulk power system (BPS) because the employee had undergone CIP training and had a Personnel Risk Assessments (PRA) conducted prior to this incident. The employee was supervised when operating the generation facility by the journeyman who was training him. | The date the employee was permitted access to the control center | The date the employee's access was revoked | $6,000 (for WECC201002418, WECC201002419, WECC201002433, WECC201002442, WECC201002443, WECC201002907) | Self-Report | WECC_URE2 filed a Mitigation Plan stating that it had completed the following actions: 1) Counseled WECC_URE2's supervisors and managers with responsibility for the facility involved in this incident on the importance of consistently enforcing the requirements for unescorted access to CCAs; 2) Updated the checklists in WECC_URE2's new employee orientation package to ensure proper clearances are obtained before giving new personnel an unescorted physical or logical access to CCAs; 3) Conducted refresher training for WECC_URE2 supervisors and operators at the PSPs on process steps for granting/providing physical access to CCA's as well as escorting visitors within NERC Critical Infrastructure Protection (CIP) Areas; 4 )Updated its online training module required for employees needing access to CCAs in order to reinforce the requirement that authorizing access is required prior to granting such access. This training has been updated and is now required for WECC_URE2 personnel who are applying for NERC CIP clearance or who will be renewing their clearance in accordance with WECC_URE2's annual training requirements. | 2011-04-19 | 2011-08-12 | Does not contest | WECC determined that: 1)The violations posed a minimal risk to the reliability of the BPS; 2) The violations were self-reported by WECC_URE2; 3) The violations have a Lower and Medium VRFs and Lower and Moderate VSLs; 3) The Violations do not pose an ongoing risk to the BPS; and 4) There were no aggravating factors for determining the penalty amount.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002907 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-006-1 R6, stating that one newly hired WECC_URE2 employee was permitted access to its control center, a Physical Security Perimeter (PSP) containing four Critical Cyber Assets (CCAs), at WECC_URE2's generation plant prior to receiving unescorted access rights. WECC determined that during this time, the employee did not log his physical entry at all access points when entering the PSP, in violation of this Standard. | CIP-006-2 | R6 | Lower | Moderate | WECC determined that the violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because the employee had been given access to the PSP but failed to log in when entering the PSP. Also, the employee was supervised by a WECC_URE2's journeyman, had undergone CIP training and had a Personnel Risk Assessments (PRA) conducted prior to this incident. | The date the employee was permitted access to the control center | The date the employee's access was revoked | $6,000 (for WECC201002418, WECC201002419, WECC201002433, WECC201002442, WECC201002443, WECC201002907) | Self-Report | WECC_URE2 filed a Mitigation Plan stating that it had completed the following actions: 1) Counseled supervisors and managers with responsibility for the facility involved in this incident on the importance of consistently enforcing requirements for unescorted access to CCAs; 2) Updated checklists in WECC_URE2's new employee orientation package to ensure proper clearances are obtained before allowing new personnel unescorted physical or logical access to CCAs; 3) Conducted a refresher training for WECC_URE2 supervisors and operators at WECC_URE2 PSPs on process steps for granting/providing physical access to CCAs as well as escorting visitors within NERC Critical Infrastructure Protection (CIP) Areas. 4) Updated the online training module required for employees needing access to CCAs to reinforce the requirement that authorizing of access is required prior to granting of access. This training is now required for WECC_URE2 personnel who are applying for NERC CIP clearance or who will be renewing their clearance per the annual training requirements. | 2011-04-19 | 2011-11-23 | Does not contest | WECC determined that: 1)The violations posed a minimal risk to the reliability of the BPS; 2) The violations were self-reported by WECC_URE2; 3) The violations have a Lower and Medium VRFs and Lower and Moderate VSLs; 3) The Violations do not pose an ongoing risk to the BPS; and 4) There were no aggravating factors for determining the penalty amount.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002443 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-2a R3 to WECC. WECC_URE2 stated that it failed to assess fifteen Microsoft security patches for Critical Cyber Assets (CCAs) located in its control room for a period of four days beyond the period allowed by CIP-007-2a R3.1. | CIP-007-2a | R3 | Lower | Lower | WECC determined that the violation did not pose a serious or substantial and posed a minimal risk to the reliability of the bulk power system (BPS) because WECC_URE2 had malicious software detection and prevention measures in place. WECC determined that these measures provided some protections against malicious cyber attacks for the assets in question. | The date the assessment of the patch should have been completed | The date the patch was assessed | $6,000 (for WECC201002418, WECC201002419, WECC201002433, WECC201002442, WECC201002443, WECC201002907) | Self-Report | WECC_URE2 submitted a Mitigation Plan for this violation. According to the plan, WECC_URE2: 1) Assessed the security patch; 2) Counseled the individual responsible for reviewing security patch availability and scheduling their assessment. WECC_URE2 emphasized the importance of timely assessment of security patches and the need to schedule the assessment of available security patches far before the deadline to allow for timely completion in the event of any unforeseen problems. | 2010-07-12 | 2011-09-13 | Does not contest | WECC determined that: 1)The violations posed a minimal risk to the reliability of the BPS; 2) The violations were self-reported by WECC_URE2; 3) The violations have a Lower and Medium VRFs and Lower and Moderate VSLs; 3) The Violations do not pose an ongoing risk to the BPS; and 4) There were no aggravating factors for determining the penalty amount.
2011-11-30 | FERC | NP12-5-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002442 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-007-2a R5 to WECC. WECC_URE2 stated that it gave one employee unauthorized access to a shared account used to access six Critical Cyber Assets (CCAs) located in the control room at its generating plant, in violation of this Standard. | CIP-007-2a | R5 | Lower | Moderate | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the employee given the unauthorized access was a newly hired employee who had received CIP training and was supervised when operating WECC_URE2 generation facility by the journeyman training him. | The date the employee was granted access to the shared account | The date the employee's access was revoked | $6,000 (for WECC201002418, WECC201002419, WECC201002433, WECC201002442, WECC201002443, WECC201002907) | Self-Report | WECC_URE2 submitted a Mitigation Plan for this violation. According to the plan, WECC_URE2: 1) Reviewed the list of personnel with access to group (shared) accounts on cyber assets within its ESPs. The list of personnel with access to such accounts was validated without the need to add or revoke access for any such personnel; 2) Updated its checklists for new employee orientation package to ensure proper clearances are obtained before allowing new personnel unescorted physical or logical access to its CCAs; 3) Conducted a refresher training for supervisors and operators at WECC_URE2 Critical Assets on process steps for following cyber access controls for CCAs as well as escorting visitors within NERC Critical Infrastructure Protection (CIP) Areas. 4) Updated its online training module for new employees needing access to CCAs to reinforce the requirement that authorizing of access is required prior to granting such access. The training is now required for WECC_URE2 personnel who are applying for NERC CIP clearance or who will be renewing their clearance per the annual training requirements. | 2011-04-19 | 2011-08-12 | Does not contest | WECC determined that: 1)The violations posed a minimal risk to the reliability of the BPS; 2) The violations were self-reported by WECC_URE2; 3) The violations have a Lower and Medium VRFs and Lower and Moderate VSLs; 3) The Violations do not pose an ongoing risk to the BPS; and 4) There were no aggravating factors for determining the penalty amount.
2011-11-30 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC200900254 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-005-1 R2.6. FRCC determined that two of FRCC_URE1's firewall devices identified as access points to the electronic security perimeter had an acceptable use banner, but the banner did not conform to the language specified in the entity's procedure document. | CIP-005-1 | R2; R2.6 | Lower | Severe | This violation pose minimal risk and not a serious or substantial risk to the reliability of the bulk power system because the entity already had an acceptable use banner in place for electronic access control devices which was sufficient to inform, caution and deter an individual for any unauthorized access attempts even though that acceptable use banner did not exactly match the banner described in the entity's procedure. | When the Standard became mandatory and enforceable | When the banner was corrected | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 corrected the banner on the two firewall devices, developed, reviewed, and approved a checklist to use for new equipment | 2009-10-15 | 2011-06-29 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-11-30 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC200900317 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-005-1 R1. FRCC determined that FRCC_URE1 classified one device incorrectly when developing the list of Cyber Assets. The device was determined to be a communication link connecting discrete Electronic Security Perimeters (ESPs). The device connecting two ESPs formed a wide area network utilizing a point to point virtual private network. Since the device is used to ensure that all CCAs are within a secure ESP, it should have been classified as an "access point to the ESP" as required by CIP-005-1 R1.3. | CIP-005-1 | R1 | Medium | High | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because the device was located within a Physical Security Perimeter that was a secured and guarded facility which had no workstations present to connect to the corporate wide area network. In addition, the access point was in a dedicated encrypted point to point (VPN) tunnel with no remote access. | When the Standard became mandatory and enforceable | Mitigation Plan completion | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 verified and documented the ports and services in operation for the device, verified the required appropriate use banner was implemented for the device, verified the device was covered in a disaster recovery plan, and verified that the device disaster recovery plan includes requirements for backup and recovery. | 2009-12-17 | 2011-06-29 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-11-30 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000314 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-002-1 R3 and revised the Self-Report to include additional Critical Cyber Assets (CCAs). FRCC_URE1 staff performed a CIP-002-1 self-assessment at one of its facilities. FRCC_URE1 staff found that there were six CCA devices (two monitoring racks and four control racks) that were not identified in its CCA list as required by CIP-002-1 R3. | CIP-002-1 | R3 | High | Lower | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because the devices were not properly identified as CCAs for 26 days and the devices were within a locked 6-wall boundary protected by card access inside a fenced generating plant site with armed guards. Devices were not accessible remotely as the generating plant VLAN restricted any outside access. | When the Standard became mandatory and enforceable | Mitigation Plan completion | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 placed guards in identified rooms and logged access for the newly identified CCAs. FRCC_URE1 implemented balance of standards for the newly identified CCAs related to the Self-Report and performed a walk down of the plant’s electronic security perimeter(s) with additional IT staff members. Corporate IT assisted and trained plant staff during the annual review of CCAs and Cyber Assets within the Electronic Security Perimeter. Finally, FRCC_URE1 implemented 6-walled protection and card readers. | 2010-05-21 | 2011-06-29 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-11-30 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000315 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-006-1 R2. FRCC_URE1 staff performed a CIP-006 self-assessment at one of its facilities and as a result reported that operational and procedural controls to manage physical access at all access points to the Physical Security Perimeters (PSPs) twenty-four hours a day, seven days a week had not been fully implemented at six PSPs. FRCC_URE1 has installed special locks on the PSPs to allow entry when card readers are inoperable. There were 5 keys available for the special locks (restricted keyway). The facility could not account for one key for the restricted keyways. All locks to the restricted keyways were changed as a result of the missing key. PSPs at the facility with a card reader door were also equipped with physical key locks (which were not restricted keyways) could be operated with a master key. The physical key locks on these doors were not disabled and special Locks (restricted keyways) were not installed. | CIP-006-1 | R2 | Medium | High | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because while the devices could have been compromised to trip the two units, the assets were located inside a secured facility with armed guards, and these devices could not be remotely accessed. Finally, the exposure was for 26 days for four PSPs and 45 days for two PSPs. | When the Standard became mandatory and enforceable | When guards were added to monitor, secure, and log access to the PSP | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 placed guards in identified rooms and manually logged access. FRCC_URE1 installed and programmed card readers for identified rooms for NERC CIP access. FRCC_URE1 replaced the special keys and key cores and installed a special key lock in at least one door in each protected area and disabled the key lock access to the other doors. | 2010-04-30 | 2011-06-29 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-11-30 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000382 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-007-1 R5.3. FRCC determined that FRCC_URE1 had Cyber Assets that could not enforce password requirements as required by CIP-007 R5.3, and were technically infeasible. FRCC_URE1 did not submit Technical Feasibility Exceptions (TFEs) in time and submitted a Self-Report on account of late submission of the TFE. | CIP-007-1 | R5; R5.3 | Lower | Lower | This violation posed minimal risk and not a serious or substantial risk to the reliability of the bulk power system because FRCC_URE1 has applied security controls that provide higher security for password complexity then required by CIP-007 R5.3.2. | When the Standard became mandatory and enforceable | When FRCC_URE1 submitted its TFEs | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 created and submitted TFEs for all assets that could not technically enforce CIP-007 R5.3 password complexity requirements. 16 TFEs were submitted to mitigate this item. FRCC_URE1 has applied security controls that provides higher security for password complexity then required by CIP-007 R5.3.2. | 2010-05-07 | 2011-03-23 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000386 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-005-1 R2.1 and 2.2. FRCC_URE1 did not apply the access control model of deny by default for its identified access points and failed to implement access control rules which permit a clearly identified unique host access to only ports and services required for normal operation. Their practice did not meet the requirement of R2.1 to provide explicit access permissions (deny by default) or R2.2 so that an access point only enables ports and services required for operations and monitoring. | CIP-005-1 | R2; R2.1; R2.2 | Medium | Moderate | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because the firewall rules did limit access to trusted networks and only allowed non-interactive ports and services as the interactive ports were blocked. In addition only three employees have access to the firewall ruleset and configuration files. | When the Standard became mandatory and enforceable | Mitigation Plan completion | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 modified its access control lists to build a least privilege model to bring firewalls within the requirements of the Standard. Some of the policy rules included a larger amount of hosts and were adjusted to be more specific. Rules were also reorganized to omit the "denies" within the ESP control areas. FRCC_URE1 also updated the ACLs to provide comments that better explain what firewall rules allow. | 2010-09-15 | 2011-06-29 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000387 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-007-1 R2. FRCC_URE1 documented but did not establish a process to ensure that only ports and services required for normal and emergency operations were enabled for the Physical Security Perimeter (PSP) access control devices at the generating sites (20 micro devices) and at the control center (4 micro devices). | CIP-007-1 | R2 | Medium | Lower | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because these devices use proprietary operating systems and remote access is not available from outside the FRCC_URE1 network. In addition, when accessing the micro devices from inside the network a user would need both the password and IP address which are not readily available. | When the Standard became mandatory and enforceable | Completed ports and services scan | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 created an add/remove Critical Asset/Critical Cyber Asset (CA/CCA) checklist around NERC CIP-007 R2 compliance. FRCC_URE1 reviewed and updated change and configuration management procedures to reference the CA/CCA checklist. FRCC_URE1 submitted Technical Feasibility Exceptions (TFEs) for devices where ports and services scans cannot be completed. FRCC_URE1 created add/remove checklists for CAs used in the access control and monitoring of the PSP and Electronic Security Perimeter to account for change and configuration management issues. Finally, FRCC_URE1 completed a ports and services scan. | 2011-01-31 | 2011-09-08 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000388 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-007-1 R5.2. FRCC determined that FRCC_URE1's factory default accounts for Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP) (micro devices) that authorize and/or log access to PSP(s) were not changed prior to putting the devices in service. The passwords were changed in 2010. FRCC_URE1 did not implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | CIP-007-1 | R5; R5.2 | Medium | Lower | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because these devices use proprietary operating systems and the account passwords are not commonly available and remote access is not available from outside the entity’s network. In addition, when accessing the micro devices from inside the network a user would need both the password and IP address which are not readily available. | When the Standard became mandatory and enforceable | Date of the password change | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 completed changing factory default passwords for all the micro devices designated as Critical Cyber Assets (CCAs). FRCC_URE1 will ensure the personnel that administer these assets will be trained on the password administration requirement of the FRCC_URE1 cyber security policy. The Corporate Security procedure was revised to clarify responsibility for password maintenance on physical access control devices. FRCC_URE1 incorporated configuration management guidance in the Physical Access Control System Administration procedure to include a checklist for the addition, replacement and retirement of assets. | 2011-03-31 | 7/13/11 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000389 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-007-1 R6.2 and 6.5. FRCC determined that FRCC_URE1 failed to properly configure logging devices to provide an alarm when a Cyber Security incident was detected and the entity failed to review the logging devices logs of system events as required by CIP-007-1 R6.2 and 6.5. | CIP-007-1 | R6; R6.2; R6.5 | Lower | Lower | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because all the concerned devices were within the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP), had card reader access controls and only a limited number of trusted users had access to these devices which required two-factor authentication and further, these devices did not have any control capability of the BPS. | When the Standard became mandatory and enforceable | When the devices were integrated with a central logging and monitoring solution and for the balance of devices, a Technical Feasibility Exception (TFE) was submitted) | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 submitted a Technical Feasibility Exceptions (TFE) with four mitigating factors of comparable security measures to managing shared accounts via a central password vault that requires two-factor authentication. FRCC_URE1 updated procedure to document how compliance with CIP-007 R6 will be met. FRCC_URE1 implemented technical (automated rules and alerts) and procedural changes. FRCC_URE1 integrated all Cyber Assets used in the access control and monitoring of the ESP with the enterprise logging and monitoring solution. FRCC_URE1 submitted closed-ended TFE devices and open-ended TFE devices. FRCC_URE1 applied needed configuration to close-ended devices and integrated closed-ended devices with central logging and monitoring solution. | 2011-07-31 | 2011-09-08 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000410 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-007-1 R5. FRCC determined that FRCC_URE1 failed to maintain list of users with access to shared accounts and shared user accounts that provide access to the Critical Cyber Assets (CCAs) (80 users) and other Cyber Assets (CAs) within the Electronic Security Perimeter (ESP), CAs used for access control and monitoring for the ESP (four users) and the Physical Security Perimeter (PSP) (three users) were not documented in the master account list. | CIP-007-1 | R5 | Lower | Lower | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because FRCC_URE1 failed to document the names of all individuals who had access to shared user accounts but these individuals had been appropriately granted access. In addition, two-factor authentication are required for access to the CCAs. | When the Standard became mandatory and enforceable | When FRCC_URE1 created the list of all shared and system accounts including users with authorization to use such accounts | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | For shared accounts used in the access and monitoring of the PSP, FRCC_URE1 created shared account master list 1 and updated procedure to reflect management of shared accounts. For Cyber Assets within the ESP, FRCC_URE1 created shared account master list 2 and updated worksite procedures to reflect management of shared accounts. For shared accounts used in the access and monitoring of the ESP, FRCC_URE1 created shared account master lists 3 and 4, created shared account master list 5, and updated procedure to reflect management of shared accounts. | 2010-12-23 | 2011-06-29 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-10-31 | FERC | NP12-2-000 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201100415 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC reporting a violation of CIP-004-1 R2.1. FRCC determined that one of FRCC_URE1’s contractors was granted electronic access to Critical Cyber Assets (CCAs) without completing all the required training. As per CIP-004-1 R2.1, such training should be completed within 90 days from date of granting access. CIP-004-2 R2.1 requires that such training should be completed before granting any access to the CCA. The entity failed to comply with this requirement and upon realizing the error, it immediately revoked the access on June 30, 2010. | CIP-004-1 | R2; R2.1 | Medium | Lower | This violation posed moderate risk and not a serious or substantial risk to the reliability of the bulk power system because the contractor was from a trusted vendor, with a current personnel risk assessment (PRA), and trained on all but one of FRCC_URE1's training modules. | 90 days from when the Standard became mandatory and enforceable | Date of access revocation | $55,000 (Settlement of FRCC200900254, FRCC200900317, FRCC201000314, FRCC201000315, FRCC201000382, FRCC201000386, FRCC201000387, FRCC201000388, FRCC201000389, FRCC201000410, and FRCC201100415) | Self-Report | FRCC_URE1 removed cyber access for the improperly trained contractor. The contractor completed the correct training. FRCC_URE1 consolidated the two training modules into one. | 2010-10-15 | 2011-07-01 | Neither Admits nor Denies | FRCC_URE1 has a documented internal compliance program which was reviewed and considered a neutral factor by FRCC.
2011-10-31 | FERC | NP12-2-000 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201000197 | Settlement Agreement | MRO_URE1 submitted a Self-Report to MRO stating that it had discovered a violation of CIP-007 R2 while it was preparing for its self-certification. The Self-Report was submitted prior to the start of the self certification submission period. MRO_URE1 had encountered various technical problems during functional testing and assessment of a third-party security provider port management solution. MRO_URE1 engaged the security provider to assist with installation and to demonstrate proof of concept of its port management solution. The security provider purported to offer a solution that allows only authorized software to execute, and to utilize the ports and other system resources. MRO_URE1 encountered various conflicts with anti-virus software, intermittent system lock-ups and screen errors while testing the port management solution. MRO_URE1 tried working with the security provider to resolve the technical problems, but the efforts were ultimately unsuccessful. Upon reviewing MRO_URE1’s system configuration and Self-Report, MRO determined that MRO_URE1 failed to enable only those ports and services required for normal and emergency operations, and disable other ports and services as required by CIP-007-2 R2.1 and R2.2. | CIP-007-1 | R2 | Medium | Severe | MRO determined that this violation did not pose a serious or substantial risk to the reliability of the bulk power system (BPS), but did pose a moderate risk to the BPS because ports were improperly enabled for most of MRO_URE1’s Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). Although MRO_URE1 had other protective measures employed within the ESP to detect and alert of any malicious activity such as other anti-virus software, firewall, intrusion detection system, and port restrictions configured between VLANs (virtual local area networks), improper port management increases the risk of exposure to malicious software and other forms of cyber attack. | The date on which MRO_URE1 was required to be compliant with CIP-007-1 R2. | The date on which MRO_URE1 disabled the ports and services that were enabled on the network switch. | 0 | Self-Report | 1. MRO_URE1 revised its Critical Infrastructure Protection policies and procedures to reflect the port management solutions. 2. MRO_URE1 disabled all ports on CCAs not necessary for normal and emergency operations. 3. The firewall has been configured for all CCAs where applicable. For CCAs that do not support the firewall, MRO_URE1 configured firewall services and VLANs on the firewall services modules residing in network switches within the ESP as mitigating controls to secure all ports not necessary for normal and emergency operations. 4. For all CCAs, the network is strategically segmented and firewall services modules are enabled to manage the network traffic that is authorized between VLANs. These measures provide a defense in depth approach, which exceeds the requirements of CIP-007-2 R2. 5. In addition, MRO_URE1 will purchase cyber security training modules related to Reliability Standards CIP-006, CIP-007 and CIP-009. These training modules will be installed on MRO_URE1’s electronic system operations training center and made available to all personnel with access to CCAs. These training modules will supplement the existing cyber security training provided to personnel with access to CCAs. | 2010-12-27 | 2011-01-21 | Admits | MRO considered MRO_URE1’s internal compliance program a mitigating factor in this enforcement action.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000437 | Settlement Agreement | RFC_URE1 submitted a self report identifying a possible violation of CIP-004-2, R2.1. RFC_URE1 has an established and documented cyber security training program. In this program, RFC_URE1 states that users with authorized access to Critical Cyber Asset (CCA) shall receive CIP specific training prior to receiving access authorization. RFC_URE1 authorized unescorted physical access to an area of RFC_URE1’s operations building that contains RFC_URE1’s energy control system, a CCA, to an employee who had not fully completed RFC_URE1’s CIP specific training. The individual required physical access to this area to perform job duties related to coordinating distribution system restoration activities. The individual’s job responsibilities did not include direct contact with the energy control system, but did require the individual to work in proximity to the energy control system, thus necessitating authorized physical access pursuant to CIP-004-2. RFC_URE1’s CIP training consists of two programs: (1) business Cyber Security training; and (2) basic Cyber Security and Information Protection training. The employee in question had only completed basic Cyber Security and Information Protection training. A RFC_URE1 supervisor mistakenly believed the employee in question had completed both sessions of CIP training when the supervisor authorized unescorted physical access to the energy control system. RFC_URE1 violated CIP-004-2 R2.1 when it authorized unescorted physical access to an employee prior to that employee completing RFC_URE1's cyber security training program. | CIP-004-2 | R2.1 | Medium | Lower | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power (BPS). The RFC_URE1 employee to whom RFC_URE1 granted access to CCAs successfully passed a personnel risk assessment and attended partial CIP training prior to RFC_URE1’s grant of unescorted physical access. Moreover, RFC_URE1 has confirmed that the employee in question did not take any action relating to the energy control system other than performing his distribution restoration functions in the proximity of the energy control system. | When RFC_URE1 had an employee that did not have CIP training to access CCAs | When RFC_URE1 revoked access to the employee | $17,000 (For RFC201000437 and RFC201000438) | Self-Report | On the same day the of discovery RFC_URE1 revoked the individual in question's unescorted physical access rights to CCAs. The employee completed training and access was restored on the same day of discovery. | 2011-09-28 | 2011-10-26 | Neither Admits nor Denies | Certain aspects of the Internal Compliance program were a partial mitigating factor.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000438 | Settlement Agreement | RFC_URE1 submitted a self report identifying a possible violation of CIP-004-1, R4.1 and R4.2. On six occasions, RFC_URE1 did not update its Access Control List (ACL) of personnel with access to Critical Cyber Assets (CCAs) within seven days of a change in personnel in violation of CIP-004-1, R4.1. On three occasions, RFC_URE1 personnel failed to correctly account for data transferred during an upgrade of a physical access control system . On two occasions, RFC_URE1 personnel failed to process the underlying access removal in a timely fashion. The remaining occasion is attributable to a software issue in RFC_URE1’s previous physical access control system, which has since been upgraded. Additionally, on six occasions unrelated to the six occasions of the violation of CIP-004-1, R4.1, RFC_URE1 failed to revoke access to CCAs within seven days after personnel no longer required access in violation of CIP-004-1, R4.2. On four occasions, RFC_URE1 personnel failed to ensure access revocation information was transferred to the newly upgraded physical access control system. On two occasions, RFC_URE1 personnel failed to follow established procedures to timely process physical and logical access revocation requests within seven days of an employee no longer requiring access to CCAs. RFC_URE1 violated CIP-004-1, R4 by failing to update its lists of personnel to reflect a change in access rights to CCAs and to revoke access to CCAs within the required timeframe for personnel who no longer required access rights. | CIP-004-1 | R4 | Medium | High | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The six individuals for whom RFC_URE1 did not update its ACL and the other six individuals for whom RFC_URE1 did not revoke access to CCAs in a timely manner all received CIP training. These individuals had also successfully completed personnel risk assessments prior to the occurrence of the violation. | When RFC_URE1 first failed to update its list of personnel to reflect a change in access rights to CCAs and revoke access to CCAs within required timeframe | When RFC_URE1 updated its list of personnel that have access rights to CCAs | $17,000 (For RFC201000437 and RFC201000438) | Self-Report | RFC_URE1's internal department that coordinates access revocation requests will review on a daily basis, all CIP operational request tickets. This process helps ensure access revocation requests are not left open beyond the 24 hour or seven day time periods required by CIP-004-1, R4. RFC_URE1 upgraded its physical access control system to improve performance of the system and establish a dedicated system for CIP regulated panels. RFC_URE1's compliance and legal personnel with the personnel involved and reiterated the CIP-004 Standard requirements and company procedures for complying with those requirements. Additionally, RFC_URE1 implemented and executed targeted awareness communications covering key elements of its CIP-004 compliance program and delivered/distributed to all CIP designated personnel and their leadership. | 2011-09-28 | 2011-10-26 | Neither Admits nor Denies | Certain aspects of the Internal Compliance program were a partial mitigating factor.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100821 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-006-3c R5, because RFC_URE1 experienced a system failure where alarms on two doors to a Physical Security Perimeter containing Critical Cyber Assets (CCAs) were not functioning properly. Specifically at 7:57 p.m., security received a system communication failure notification indicating that the alarms on two doors to a Physical Security Perimeter were not transmitting back to RFC_URE2’s security. The security officers attempted to monitor the two doors with video cameras, but could not locate the applicable cameras. They then alerted the field investigator to report the issue. Throughout the night, the field investigator and other security individuals periodically monitored the two doors and brought in technicians to fix the issue. However, the technicians reported that they could not fix the issue that night. On the following morning, corporate security staff reviewed the incident report and immediately advised security to begin monitoring the two doors via video camera. The security started to monitor the two doors via video camera at 7:50 a.m. In addition the technicians fixed the issue with the alarms that day. ReliabilityFirst determined that RFC_URE2 violated CIP-006-3c R5 by failing to implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter twenty-four hours a day, seven days a week. | CIP-006-3c | R5 | Medium | Severe | ReliabilityFirst determined that the violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the two doors are emergency exit only doors and cannot be opened from the outside. One of the two doors opens into the main working area at the building, which houses the system control room, and was monitored by the system control operator during the violation. In addition, all of RFC_URE2’s system control operators receive cyber security training and understand the critical nature of the system control room. The other door was outside the proximity of the main working area of system control, and while the system control operator did not visually monitor it during the duration of the violation, this door was essentially sealed shut due to ongoing maintenance work. Opening the temporarily sealed door would have been very noisy, and the system control operator would most likely have heard any opening of the door. | The date on which RFC_URE2 failed to continuously monitor the access points. | The date on which monitoring resumed. | $35000 (Settlement of RFC201100821, RFC201100859, RFC201100860, RFC201100861, and RFC201100862) | Self-Report | RFC_URE2 fixed the issue with the door alarms. RFC_URE2 developed a quarterly review process of all applicable security job aids to ensure accurate information is maintained. RFC_URE2 also developed a new controls process that requires a comprehensive review, with sign off, of all changes to CCA security equipment. RFC_URE2 provided training to all security officers and corporate security field investigators on NERC requirements, CCA camera locations, types of CCA monitoring alarms and implications for those types of alarms. RFC_URE2 completed additional programming to provide direct links to any applicable cameras and playback in all CCA door alarms. | 2011-04-06 | 2011-06-07 | Neither admits nor denies/Stipulates to the Facts | ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100859 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-007-3 R5 because RFC_URE2 failed to reset a password for one account on a Critical Cyber Asset within an Electronic Security Perimeter (ESP). RFC_URE2 utilized a password reset tracking spreadsheet to track accounts in the ESP and uses that data as a basis for manually resetting passwords annually. While preparing for a routine password change task, RFC_URE2 discovered that a single account was missing from the 2010 password reset tracking spreadsheet, and it consequently failed to reset the password of that account in 2010. ReliabilityFirst determined that RFC_URE2 violated CIP-007-3 R5 by failing to change each password at least annually. | CIP-007-3 | R5 | Lower | Severe | ReliabilityFirst determined that the violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the missed account on the Cyber Asset resides on a server limited to archived data. In addition, RFC_URE2 changed the password annually in prior years. | The date by which RFC_URE2 should have at least annually reset the password. | The date the password was reset. | $35000 (Settlement of RFC201100821, RFC201100859, RFC201100860, RFC201100861, and RFC201100862) | Self-Report | RFC_URE2 updated the password tracking reset spreadsheet with the missing account information. RFC_URE2 reset the account password. RFC_URE2 will implement an automated process to manage the majority of the required password resets. | 12/31/2011 (Approved Date) | TBD | Neither admits nor denies/Stipulates to the Facts | ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100860 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-006-3c R1.4 because RFC_URE2 failed to implement the physical security plan at its generating facility. RFC_URE2’s generating facility has five different levels of Critical Cyber Asset (CCA) access, based on the needs of both employees and contractors to perform their work. RFC_URE2 discovered three instances at the generating facility where RFC_URE2’s security staff granted a higher level of CCA access than the level authorized by RFC_URE2 site management. First, a RFC_URE2 security officer erroneously granted an individual employee (Employee 1) temporary, full access for approximately 16.5 hours, despite the fact that Employee 1 was authorized only for access levels 1, 2 and 3. Second, a RFC_URE2 security officer erroneously granted another individual employee (Employee 2) temporary, full access for approximately 15.5 hours, despite the fact that Employee 2 was only authorized for access levels 1, 2, 3 and 4. Third, a RFC_URE2 security officer again granted Employee 2 temporary, full access for approximately 1.5 hours because the security officer used the prior access grant as the basis for the new access. However, the security officer revoked those improper access rights approximately one hour later, after verifying with the RFC_URE2 security that Employee 2 was only authorized for access levels 1, 2, 3 and 4. | CIP-006-3c | R1 | Medium | Severe | ReliabilityFirst determined that the violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because both Employee 1 and Employee 2 received personnel risk assessments (PRA) and cyber security training. In addition, neither Employee 1 nor Employee 2 accessed any assets or areas beyond their respective authorized access levels. | The date of RFC_URE2's first instance of erroneously granting access rights to Employee 1. | The last date on which RFC_URE2 revoked erroneous access rights. | $35000 (Settlement of RFC201100821, RFC201100859, RFC201100860, RFC201100861, and RFC201100862) | Self-Report | RFC_URE2 revised the security procedures for its generating facility. RFC_URE2 had all security personnel at the generating facility review and sign off on the revised security procedures. RFC_URE2 created a new security procedure on the temporary CCA badge distribution process. RFC_URE2 had all appropriate security personnel review and signoff on the new procedure. RFC_URE2 administered discipline to the at-fault contracted security officer involved in the February 5, 2011 incident. RFC_URE2 reviewed all temporary CCA badge issuance and usage at the generating facility from January 1, 2010 through March 11, 2011 to ensure comprehensive identification of any additional violations. | 2011-03-14 | 2011-09-23 | Neither admits nor denies/Stipulates to the Facts | ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100861 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-006-2 R2.2 due to RFC_URE2's failure to protect its physical access control system by affording the protective measures specified in Standard CIP-007-3 R5. RFC_URE2 discovered that the database that stores data for its physical access control system software has a shared administrator account (Shared Account), for which RFC_URE2 never changed the password. Database administrators use the Shared Account to run the physical access control system and to generate related reports. In order to change the password, RFC_URE2 would have to take the physical access control system offline, which would disable physical access monitoring to Critical Cyber Assets. Therefore, RFC_URE2 did not reset the password on the Shared Account at least annually, as required by CIP-007-3 R5.3.3. In addition, RFC_URE2 identified four instances where personnel who had access to the Shared Account no longer required such access. RFC_URE2 failed to reset the password within 90 days from the date that personnel no longer required access to the Shared Account, in violation of its shared password guidance documents created pursuant to CIP-007-3 R5.2.3. Therefore, RFC_URE2 failed to implement its policy for securing a shared account in the event of personnel changes, as required by CIP-007-3 R5.2.3. | CIP-006-2 | R2 | Medium | Severe | ReliabilityFirst determined that the violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because none of the four individuals were terminated for cause. In addition, RFC_URE2 revoked the individuals’ physical and cyber access rights, so they could not physically or electronically access the database after their employment ended. Furthermore, the system owner and IT security would be aware of human access to the Shared Account because the Shared Account is primarily accessed electronically automatically in order to run the physical access control system and generate reports, rather than by human users. Finally, RFC_URE1 tracks any attempted human use of the Shared Account with an alert sent to the system owner and to IT security. For example, over the past three months, there have been no occurrences of human use of the Shared Accounts. | The date by which RFC_URE2 should have at least annually reset the password. | The date the password was reset. | $35000 (Settlement of RFC201100821, RFC201100859, RFC201100860, RFC201100861, and RFC201100862) | Self-Report | RFC_URE2 reset the shared account password. RFC_URE2 developed an automated email notification that will inform the database administrators group and corporate security whenever there is a personnel change to the database administrators group. This would result in corporate security completing a review of the personnel change to determine if a password change is necessary. RFC_URE2 developed an automated email notification that will inform corporate security whenever there is a personnel change to the Shared Account and physical access control system test user group to corporate security. This would result in corporate security completing a review of the personnel change to determine if a password change is necessary. RFC_URE2 created an annual commitment through the company's commitments tracking database to ensure a shared account password reset is completed annually. RFC_URE2 created a physical access control system cross-functional committee that includes representatives from all stakeholder groups to be responsible for training and awareness. RFC_URE2 completed a full review of all password and confidential information accessible within the physical access control system. RFC_URE2 developed a shared account password change outage process. RFC_URE2 added the requirement to reset the shared account password to the existing physical access control system procedures. RFC_URE2 created a formal review process regarding physical access control system procedures to be approved by legal and NERC ClP compliance assurance managers. | 2011-08-29 | 2011-10-04 | Neither admits nor denies/Stipulates to the Facts | ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100862 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-006-3c R6 due to its failure to record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. While conducting an annual review of its physical security plan, RFC_URE2 discovered that some of its manual log entries were incomplete. Specifically, 23 of more than 1,000 escorted visitor log entries made in a one-year period were incomplete and could not be completed with data from alternate sources. The incomplete visitor log entries, all from the generating facility, included eight log entries that were missing exit times, nine log entries that were missing the escort’s name, and six log entries that were missing a combination of two of the following: escort’s name, entry date, entry time or exit time. | CIP-006-3c | R6 | Lower | Severe | ReliabilityFirst determined that the violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because all Critical Cyber Asset access points are equipped with alarms for access denied attempts, door held situations, and door-forced situations. These alarms include a local audible alarm at each access point, in addition to notification back to security. | The date on which RFC_URE2 first failed to log a visitor entry. | The date after which there were no additional occurrences of improper logging. | $35000 (Settlement of RFC201100821, RFC201100859, RFC201100860, RFC201100861, and RFC201100862) | Self-Report | RFC_URE2 revised the Physical Security Perimeter log entry form to more clearly indicate how to properly complete the form, including format guidance and an example log entry. In addition, RFC_URE2 revised the physical security plan to include a process for regular retrieval and review of the log books. The revised physical security plan also includes a process for investigations of any log entry discrepancies. | 2011-07-01 | 2011-09-23 | Neither admits nor denies/Stipulates to the Facts | ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors.
2011-10-31 | FERC | NP12-2-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000696 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst reporting a violation of CIP-006-3c R1. RFC_URE3 reported that it did not use its visitor pass management control program appropriately, pursuant to CIP-006-3c R1.4. RFC_URE3 also determined that it did not document the entry and exit of two visitors, including the date and time, to and from RFC_URE3's Physical Security Perimeter (PSP), and did not continuously escort visitors within the PSP, pursuant to CIP-006-3c R1.6. A RFC_URE3 employee with authorized physical access to RFC_URE3’s PSP used his badge to gain access to the PSP, and then allowed two maintenance employees to enter the PSP without logging the required information in the visitor's log book. In addition, the same RFC_URE3 employee failed to escort the maintenance employees inside the PSP for a period of 12 minutes while they performed the necessary repairs. When the two maintenance employees completed their repairs, they pressed the emergency release button in order to exit the PSP, which immediately notified RFC_URE3 security of the situation. RFC_URE3 security followed its documented procedures to notify the appropriate personnel, and the CIP compliance department notified generation management to secure the PSP and begin its investigative process. ReliabilityFirst determined that RFC_URE3 failed to: a) Appropriately use visitor pass management; b) Properly log the entrance and exit, including date and time, of two unauthorized RFC_URE3 maintenance employees to and from the PSP; and c) Continuously escort the same two maintenance employees for a period of approximately 12 minutes within the PSP, pursuant to CIP-006-3c R1.4 and R1.6. | CIP-006-3c | R1 | Medium | Severe | ReliabilityFirst determined that this violation posed a moderate but not serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE3 reviewed video evidence for the time period of the violation and confirmed that the violation was limited to only the two maintenance employees, both of whom worked for RFC_URE3. RFC_URE3 further verified that the two maintenance employees did not alter, and in fact did not have the ability to alter, any of the settings for the equipment in the PSP at issue. Additionally, both of the maintenance employees had authorized physical access to the plant site, and had to present their badges at multiple security points before gaining access to the plant site. Further, one of the maintenance employees has been an employee of RFC_URE3 for approximately 30 years, and voluntarily underwent CIP training prior to the violation. RFC_URE3 performed a background check for the other maintenance employee prior to the time period of the violation when he was hired in 2008, which revealed no issues. | The time period which the maintenance employees gained entry to the PSP without escort. | When RFC_URE3 secured the perimeter of the PSP. | 5000 | Self-Report | Upon discovery, RFC_URE3's CIP compliance department notified the supervisor of the RFC_URE3 employee involved in the incident, and disciplinary action was taken. RFC_URE3 also conducted re-education training for its generation CIP personnel. In this training, RFC_URE3 emphasized CIP and the RFC_URE3 CIP-006 physical security plan, which includes the appropriate visitor pass management control program. | 2010-10-28 | 2011-03-15 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE3's internal compliance program as mitigating factors.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002191 | Settlement Agreement | In its self-report, WECC_URE1 stated that it did perform a Critical Asset Assessment as required by CIP-002-1 R2 prior to the date it was required to comply with the Standard, but the assessment was completed verbally and without written documentation. Almost a week later, WECC_URE1 submitted its Self-Certification stating it was in violation of CIP-002-1 R2. WECC_URE1 submitted a revised self-report stating that it incorrectly labeled certain assets as "Critical." WECC_URE1 submitted its Critical Asset Assessment document to WECC, which detailed WECC_URE1's Critical Assets. | CIP-002-1 | R2 | High | Severe | WECC determined that this violation posed a minimal risk to the reliability of the Bulk Power System (BPS). Non-identification of Critical Assets could result in the subsequent failure to protect Critical Assets essential to reliable operation of the BPS. Unidentified and unprotected Critical Assets may be vulnerable to threats and may put the operation of the BPS at risk. Though it wasn't document, WECC_URE1 performed a Critical Asset Assessment verbally which minimized risk and promoted reliable operation. Because WECC_URE1 had only three misidentified Critical Assets and WECC_URE1 has less than 100 miles of transmission lines, WECC determined that its impact on the BPS with respect to its CIP-002-1 R2 violation would be minimal. | When WECC_URE1 was required to comply with the Standard | Mitigation Plan Completion Date | $27,000 (For WECC201002191, WECC201002192, WECC201002351, WECC201002371 mad WECC201002368) | Self-Report | To mitigate these self reported issues, WECC_URE1 initiated the following milestones for completion to ensure that a reassessment of Critical Assets be performed, fully documented and approved to meet compliance requirements. -Completed the review of requirements and definitions for determining Critical Assets. -Completed the Reassessment of WECC_URE1 assets for determination of whether they are Critical Assets. -Completed the full documentation, approval, and reporting to WECC of a reassessment of critical assets for WECC_URE1. In addition, WECC_URE1 required staff to document its verbally completed Critical Cyber Asset Assessment that was completed prior to June 30, 2009, and have it reviewed, and approved by senior management for inclusion in the Mitigation completion documentation. | 2010-05-21 | 2010-10-22 | Agrees and Stipulates to the Facts | WECC reviewed WECC_URE1's Internal Compliance Program (ICP) and considered it a mitigating factor.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002192 | Settlement Agreement | WECC_URE1 self-reported noncompliance with CIP-002-1 R4 for not having its Critical Asset Assessment list approved by a senior manager or a delegate thereof. | CIP-002-1 | R4 | Lower | High | WECC determined that this violation posed a minimal risk to the reliability of the BPS. The failure of an entity to have its list of Critical Assets reviewed and approved by a senior manager could also result in the failure of an entity to identify and protect its Critical Assets. Though it was not documented, WECC_URE1 performed a Critical Asset Assessment verbally which minimized risk and promoted reliable operation. WECC_URE1 had only three misidentified Critical Assets and WECC_URE1 has less than 100 miles of transmission lines, WECC determined that the impact on the BPS as a result of its CIP-002-1 R4 violation would be minimal. | When WECC_URE1 was required to comply with the Standard | Mitigation Plan Completion Date | $27,000 (For WECC201002191, WECC201002192, WECC201002351, WECC201002371 mad WECC201002368) | Self-Report | To mitigate these self reported issues, WECC_URE1 initiated the following milestones for completion to ensure that a reassessment of Critical Assets be performed, fully documented and approved to meet compliance requirements. -Completed the review of requirements and definitions for determining Critical Assets. -Completed the reassessment of WECC_URE1 assets for determination of whether they are Critical Assets. -Completed the full documentation, approval, and reporting to WECC of a reassessment of critical assets for WECC_URE1 In addition, WECC_URE1 required staff to document its verbally completed Critical Cyber Asset Assessment that was completed prior to the date it was required to comply with the Standard, and have it reviewed, and approved by senior management for inclusion in the Mitigation completion documentation. | 2010-05-21 | 2010-10-22 | Agrees and Stipulates to the Facts | WECC reviewed WECC_URE1's ICP and considered it a mitigating factor.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002351 | Settlement Agreement | WECC_URE1 self-reported that it was in violation of CIP-003-1 R1.2 for failing to make its security policy readily available to all personnel who have access to or are responsible for Critical Cyber Assets. The next day, WECC_URE1 submitted its Self-Certification stating it was in violation of CIP-003-1 R1.2. A WECC Subject Matter Expert (SME) held a conference call to discuss WECC_URE1's self reported CIP-003-1 R1.2 violation. On the conference call, the WECC SME concluded that WECC_URE1 was not in violation of CIP-003-1 R1.2 because WECC_URE1 had made its Cyber Security Policy readily available to all personnel who have access to or are responsible for Critical Cyber Assets. However, on the conference call, the WECC SME also determined that WECC_URE1 was in violation of CIP-003-1 R1.1 and CIP-003-2 R1.1 because its Cyber Security Plan did not address all the requirements in Standards CIP-002-2 through CIP-009-2. Specifically, WECC_URE1 is in violation of CIP-003-2, R1.1 because its Cyber Security Plan did not address: • CIP-002-2, R1, R2, R3, R4; • CIP-003-2, R1, R2, R6; • CIP-004-2, R3, R4; • CIP-005-2, R1, R2, R3, R4, R5; • CIP-006-2, R1, R2, R3, R5, R6, R7, R8B; • CIP-007-2, R1, R2; • CIP-008B-2, R1, R2; and • CIP-009-2, R1, R2, R3, R5. | CIP-003-2 | R1 | Lower | Severe | WECC determined that this violation posed a minimal risk to the reliability of the BPS. WECC_URE1's cyber security policy did not reflect all the requirements in Standards CIP-002 through CIP-009. It is not clear that WECC_URE1's management is committed to the security of WECC_URE1's Critical Cyber Assets at the level required by the CIP Standards. Despite the failure to develop a comprehensive policy, WECC_URE1 did perform an assessment of its Critical Assets. Also, WECC_URE1 has less than 100 miles of transmission lines. | When WECC_URE1 was required to comply with the Standard | Mitigation Plan Completion Date | $27,000 (For WECC201002191, WECC201002192, WECC201002351, WECC201002371 mad WECC201002368) | Self-Report | WECC_URE1 submitted to WECC evidence including a revised WECC_URE1 Cyber Security Policy. This policy was reviewed and verified by WECC as part of WECC_URE1's Mitigation Plan. | 2010-06-30 | 2011-04-29 | Agrees and Stipulates to the Facts | WECC reviewed WECC_URE1's ICP and considered it a mitigating factor.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002371 | Settlement Agreement | WECC_URE1 self-reported a potential violation of CIP-003-1 R2 because it could not provide documentation that it had assigned a senior manager responsible for implementing and assuring that WECC_URE1 was adhering to Standards CIP-002 through CIP-009. Although WECC_URE1 maintains it did designate a senior manager, WECC_URE1 was unable to provide documentation that it had designated, with all the information required by the Standard, a senior manager responsible for overall implementation of the Standards CIP-002 through CIP-009. | CIP-003-1 | R2 | Medium | Severe | WECC determined that this violation posed a moderate risk to the reliability of the BPS. Failure to assign a senior manager for leading and managing the entity's implementation of CIP Standards increases the risk that, due to a lack of executive supervision, the implementation of protective measures required by the CIP standards for Critical Cyber Assets. WECC_URE1 did designate a senior manager, but the designation wasn't documented. In addition, WECC_URE1 only has less than 100 miles of transmission lines making its impact on the BPS minimal. For this reason, WECC determined WECC_URE1's violation posed minimal risk to the reliability of the BPS. | When WECC_URE1 was required to comply with the Standard | Mitigation Plan Completion Date | $27,000 (For WECC201002191, WECC201002192, WECC201002351, WECC201002371 mad WECC201002368) | Self-Report | WECC_URE1 provided a document entitled that verified the manager of information technology, was designated as senior manager responsible for implementation, as well as ensuring that WECC_URE1 adheres to Standards CIP-002 through CIP-009 | 2009-07-22 | 2011-02-08 | Neither Admits nor Denies | WECC reviewed WECC_URE1's ICP and considered it a mitigating factor.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002368 | Settlement Agreement | WECC_URE1 self-reported a potential violation of CIP-004-1 R2.1 stating that it may be unable to provide satisfactory training records that would demonstrate training took place within the required timeframe for all applicable personnel. WECC_URE1 also self-reported a potential violation of CIP-004-1 R2.3 stating that it may be unable to provide training records for certain individuals. WECC_URE1 submitted to WECC a sufficient cyber security training program. According to WECC_URE1, its submitted cyber security training program was implemented earlier that year. A WECC Subject Matter Expert (SME) reviewed WECC_URE1's potential violations and determined that WECC_URE1 was not in violation of CIP-004-1 R2.1 or R2.3 because WECC_URE1 did provide sufficient documentation, but was in violation of CIP-004-1 R2.2 because its cyber security training program prior to the effective date did not address all of the requirements of the Standard. Based on this self-report and supporting evidence, the WECC determined that WECC_URE1 was in violation of CIP-003-2 R2. | CIP-004-1 | R2 | Medium | Severe | WECC determined that this violation posed a minimal risk to the reliability of the BPS. WECC_URE1 failed to have an adequate cyber security training program. Without an adequate cyber security training program, it is less likely that WECC_URE1's employees will be properly trained on cyber security exposing the BPS to an increased risk of cyber attacks. Although WECC_URE1's training program was incomplete, there was a program in place which immunized risk to the BPS and promoted reliable and safe operation. In addition, WECC_URE1 only has less than 100 miles of transmission lines. For this reason, WECC determined this violation posed minimal risk to the reliability of the BPS. | When WECC_URE1 was required to comply with the Standard | Mitigation Plan Completion Date | $27,000 (For WECC201002191, WECC201002192, WECC201002351, WECC201002371 mad WECC201002368) | Self-Report | WECC_URE1's CIP Manager submitted to WECC evidence including the newly implemented Training curriculum to personnel labeled. This program was reviewed and verified by WECC as part of WECC_URE1's Mitigation Plan. | 2010-06-15 | 2011-03-11 | Agrees and Stipulates to the Facts | WECC reviewed WECC_URE1's ICP and considered it a mitigating factor.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC200902018 | Settlement Agreement | WECC_URE2 self-reported a violation of CIP-005-1 R1.5 for its failure to afford the protective measures as specified in CIP-007-1 R5.1.2 and CIP-005-1 R3 to all of its Critical Cyber Assets. During an internal investigation WECC_URE2 discovered that 10 of its Critical Cyber Asset logs were not being gathered and stored by its central log collector system and were not, in accordance with the procedures WECC_URE2 developed pursuant to CIP-007-1 R5.1.2: (1) being processed in accordance with the policies and procedures for logging user account access; and (2) being monitored for access. | CIP-005-1 | R1; R1.5 | Medium | High | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because logging was being generated at the device level and was available for a manual review if required. | When WECC_URE2 was required to comply with the Standard | Mitigation Plan Completion Date | $37,000 (for WECC200902018, WECC201001972, WECC201001973, and WECC201002024) | Self-Report | 1. WECC_URE2 gathered and monitored logs for its 10 access control Cyber Assets. 2. WECC_URE2 improved its change control and configuration management procedure for impact evaluation of its status event monitoring systems. 3. WECC_URE2 conducted training on the revised procedure. 4. WECC_URE2 developed a verification procedure to ensure that its status event monitoring systems are collecting appropriate messages when assets are being added and provided training. 5. WECC_URE2 developed a quarterly process for manual audits to ensure that all appropriate assets are being logged. | 2009-12-01 | 2010-06-29 | Admits | WECC considered that the violation constituted WECC_URE2’s first occurrence of violation of the subject NERC Reliability Standard. In addition, WECC considered as a mitigating factor that WECC_URE2 had an internal compliance program (ICP) at the time of the violation.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201001972 | Settlement Agreement | WECC_URE2 self-reported a violation of EOP-005-1 R1 for its failure to provide annual training on the implementation of its system restoration plan to four power dispatchers. According to the Settlement Agreement, WECC_URE2 discovered that, in 2008, four power dispatchers had not received the required annual training on the WECC_URE2 system restoration plan. Specifically, one employee was trained after 477 days instead of within 365 days; another was trained after 408 days; the third was trained after 445 days; and the fourth employee was trained after 446 days. | EOP-005-1 | R1 | Medium | Lower | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because (1) all four employees that are the subject of the violation had previously received the annual training; (2) copies of the plan were readily available to all WECC_URE2 operators; and (3) the annual training requirement for 2008 was exceeded by 112, 43, 80 and 81 days for the four employees. | When WECC_URE2 first missed the annual traininig | When WECC_URE2 trained the last dispatcher | $37,000 (for WECC200902018, WECC201001972, WECC201001973, and WECC201002024) | Self-Report | WECC_URE2 updated its system restoration plan to clarify that the annual training interval shall not exceed 13 months. | 2010-05-24 | 2010-06-16 | Admits | WECC considered that the violation constituted WECC_URE2’s first occurrence of violation of the subject NERC Reliability Standard. In addition, WECC considered as a mitigating factor that WECC_URE2 had an internal compliance program (ICP) at the time of the violation.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201001973 | Settlement Agreement | WECC_URE2 self-reported a violation of EOP-008-0 R1 for its failure to provide annual training on the implementation of its system restoration contingency plan in the event its control center becomes inoperable to eight power dispatchers. According to the Settlement Agreement, WECC_URE2 reported that eight power dispatchers, six in 2008 and two in 2009, did not receive the required annual training. In 2008, one employee was trained after 477 days instead of within 365 days; another employee was trained after 439 days; the third employee was trained after 420 days; the fourth employee was trained after 463 days; the fifth employee was trained after 420 days and the sixth employee was trained after 671 days. With regard to 2009, one employee received training after 419 days and the second employee was trained after 421 days. | EOP-008-0 | R1 | High | Lower | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because all eight employees that are the subject of the violation had received the training previously, and copies of the system restoration contingency plan were readily available to all WECC_URE2 operators. | When WECC_URE2 first missed the annual traininig | When WECC_URE2 trained the last dispatcher | $37,000 (for WECC200902018, WECC201001972, WECC201001973, and WECC201002024) | Self-Report | WECC_URE2 updated its system restoration contingency plan to clarify that the annual training interval shall not exceed 13 months. | 2010-05-25 | 2010-06-18 | Admits | WECC considered that the violation constituted WECC_URE2’s first occurrence of violation of the subject NERC Reliability Standard. In addition, WECC considered as a mitigating factor that WECC_URE2 had an internal compliance program (ICP) at the time of the violation.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002024 | Settlement Agreement | WECC_URE2 self-reported a violation of TOP-006-1 R6 for its failure to have a sufficient range for some of its metering to accurately monitor all operating conditions for both normal and emergency situations. WECC_URE2 conducted an internal review and discovered that the Energy Management System (EMS) Supervisory Control And Data Acquisition (SCADA) scaling limits were set below an alarm setting at 55 of its 736 monitoring points. As a result of these incorrect range settings, WECC_URE2 was using inaccurate data to monitor operating conditions, and could not perform timely monitoring of operating conditions for normal or emergency situations. Twenty-six of WECC_URE2’s 120 substations were affected by the subject violation. | TOP-006-1 | R6 | High | Severe | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) at all times, WECC_URE2 operators had real-time visibility of actual and predicted line flows; (2) WECC_URE2's state estimator performs data checking and line flow verification and alerts WECC_URE2's operators of any data mismatches; (3) WECC_URE2 conducts hourly reviews with its intertie neighbors during which any meter anomaly would trigger further review; and (4) WECC_URE2 performs contingency analysis studies that highlight any approaching reliability concerns, and WECC_URE2's Balancing Authority monitors and studies WECC_URE2's transmission system. | When WECC_URE2 was required to comply with the Standard | Mitigation completion date | $37,000 (for WECC200902018, WECC201001972, WECC201001973, and WECC201002024) | Self-Report | 1. WECC_URE2 lowered the alarms of the impacted lines to within the scalable limits of the identified 55 devices. 2. WECC_URE2 documented processes relative to transmission lines and associated MW, MVA and kV measurements and critical data transfer to the EMS system, including new transmission projects and existing transmission system improvements. The process documentation is intended to make sure the metering package which includes the meters, SCADA and EMS elements are reviewed for suitable range and if necessary adjusted prior to finalizing critical data alarm settings associated with issuing new transmission ratings and rerating of existing facilities. This includes any procedural documents that need to be created or modified for how work is actually accomplished. 3. WECC_URE2 established a records management process for capturing the meter package range, accuracy rating and test data. 4. WECC_URE2 evaluated key elements of its critical BPS metering packages to validate that no other insufficiencies would prevent the trigger and receipt of critical data alarms. This may include review of existing records and/or field review of approximately 736 measurement devices in approximately 120 substations. 5. WECC_URE2 adjusted and/or replaced any device found lacking suitable monitoring range. If necessary, critical data alarms were adjusted until any identified insufficiency were resolved. Permanent operation at lower alarm limits is acceptable for this mitigation plan. | 2011-02-15 | 2011-07-08 | Admits | WECC considered that the violation constituted WECC_URE2’s first occurrence of violation of the subject NERC Reliability Standard. In addition, WECC considered as a mitigating factor that WECC_URE2 had an internal compliance program (ICP) at the time of the violation.
2011-10-31 | FERC | NP12-2-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102640 | Notice of Confirmed Violation | WECC_URE3 failed to identify personnel with access to a shared account. WECC_URE3’s shared account is on 25 routers and switches which are accessible via a serial or network connection within the Physical Security Perimeter (PSP). These devices are located at WECC_URE3’s Control, Backup Control Center, and Generation facilities. WECC_URE3 also failed to have a policy for managing the use of shared accounts. Consequently, WECC_URE3 could not provide an audit trail of the account’s use demonstrating that the account was secure in the event of personnel changes. | CIP-007-1 | R5 | Lower | Severe | WECC considered this violation to have a minimal impact on the reliability of the bulk power system (BPS). In this instance, WECC_URE3 failed to implement a policy to manage shared accounts, maintain an audit trail of account use and identify personnel with access to a shared account on 25 routers and switches. These routers and switches are CCAs that are located at the three Electronic Security Perimeters (ESPs) and are used for network access and management. As a compensating measure, WECC_URE3 stated that these devices were in identified ESPs and PSPs and had protections required by CIP-005 and CIP-006. In addition, WECC_URE3 stated that intrusion detection and prevention systems are in place at these ESPs. Alerts from these systems are reviewed 24x7 at the security operations center. | When WECC_URE3 was required to be compliant with the Standard | Mitigation completion date | 8200 | Self-Certification | In its mitigation plan, WECC_URE3 identifies four milestones: (1) Network Administrator to change console-port password on all network Critical Cyber Assets and all Network Cyber Assets inside the Electronic Security Perimeter, (2) At the time of Password change, identify and document any and all personnel given the password for the console-port password, (3) Develop and document a policy for managing the use of shared accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes, and (4) Communicate the policy above to the appropriate WECC_URE3 personnel and management. The policy will require that any personnel with access to the console-port are identified and documented. In addition, passwords for this account will be changed annually. | 2011-09-10 | 2011-10-06 | Does Not Contest | WECC considered WECC_URE3’s Internal Compliance Program (ICP) as a mitigating factor.
2011-10-31 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000692 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that its security monitoring process failed to detect and alert for unauthorized access attempts for two firewalls located on an electronic security perimeter (ESP). Specifically, RFC_URE1’s security management software tool was configured to alert RFC_URE1 to unauthorized access attempts based upon a threshold frequency of access denials from a specific IP address. RFC_URE1 did not configure two firewalls to report access denial events to the security management software tool. As a result, RFC_URE1’s security logging and alerts would not have functioned correctly if there had been unauthorized access attempts to the firewalls. | CIP-005-1 | R3/ R3.2 | Medium | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because RFC_URE1 configured the firewalls on the ESP to deny access by default, and therefore the Critical Cyber Assets (CCAs) within the ESP remained protected from unauthorized access attempts throughout the duration of the violation. Additionally, the security management software tool did log all permitted access attempts and firewall configuration changes. | The date on which RFC_URE1 was subject to compliance with CIP-005-1. | The date on which RFC_URE1 corrected the configuration of the firewalls to log and report access denial events to the security management tool. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Self-Report | RFC_URE1 corrected the configuration of its firewalls to log and alert RFC_URE1 to all denied unauthorized access attempts. | 2010-10-12 | 2011-08-17 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which RF considered a mitigating factor.
2011-10-31 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000693 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it discovered a network switch that had ports and services that were not required for normal or emergency operations but that were still enabled, in violation of CIP-007-1 R2. While performing an annual vulnerability assessment, RFC_URE1 discovered that the network switch, which is located inside the electronic security perimeter (ESP), had ports and services that were not required for normal and emergency operations, but that were still enabled | CIP-007-1 | R2/ R2.1, R2.2 | Medium | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the network switch is located behind the ESP firewall and is therefore not accessible from outside the ESP. | The date on which RFC_URE1 was subject to compliance with CIP-007-1. | The date on which RFC_URE1 disabled the ports and services that were enabled on the network switch. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Self-Report | RFC_URE1 disabled the ports and services that were enabled on the network switch. | 2010-11-19 | 2011-08-16 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which RF considered a mitigating factor.
2011-10-31 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201000694 | Settlement Agreement | RFC_URE1 submitted a Self-Report to RF stating that it failed to remove or disable factory default accounts on a network switch (the same network switch as RFC201000693), and failed to meet password requirements as required by CIP-007-1 R5. Specifically, RFC_URE1 discovered a network switch within the electronic security perimeter (ESP) had two factory default accounts that RFC_URE1 had not removed, disabled, or renamed. Additionally, RFC_URE1 failed to create passwords for the two factory default accounts that conform with the requirements of CIP-007-1 R5.3, prior to placing them into service. RFC_URE1 discovered this oversight during its annual vulnerability assessment. | CIP-007-1 | R5 | Lower | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the network switch containing the two factory default accounts is located behind the ESP firewall and is therefore not accessible from outside the ESP. | The date on which RFC_URE1 was subject to compliance with CIP-007-1. | The date on which RFC_URE1 set complex passwords for the two factory default accounts on the network switch. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Self-Report | RFC_URE1 set complex passwords for the two factory default accounts on the network switch that conform to CIP-007-1 R5.3. | 2010-11-19 | 2011-08-16 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which RF considered a mitigating factor.
2011-10-31 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100752 | Settlement Agreement | RF conducted a compliance audit of RFC_URE1 (the Compliance Audit). During the Compliance Audit, RF discovered that RFC_URE1’s physical security plan failed to satisfy two requirements of CIP-006-1. First, RFC_URE1’s physical security plan failed to address response to loss and prohibition of inappropriate use of physical access controls, as required by CIP-006-1 R1.4. Second, RFC_URE1’s physical security plan stated that it would be updated within 90 calendar days of a physical security system design or configuration change. Although Version 1 of CIP-006, R1.7 allowed for a 90-day period to update a physical security plan, on April 1, 2010 Version 2 of CIP-006 took effect, which requires a narrower, 30-day update period. Therefore, from the effective date of CIP-006-2, RFC_URE1 failed to include a requirement in its physical security plan to update the physical security plan within 30 days of a physical security system design or configuration change. | CIP-006-1 | R1/ R1.4, R1.7 | Medium | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE1’s physical security plan did not include information about responding to loss or a prohibition of inappropriate use of physical access controls, RFC_URE1 addressed these topics in another RFC_URE1 document, and trained its employees on these topics. Additionally, although RFC_URE1’s physical security plan stated that RFC_URE1 must update the physical security plan within 90 days of any changes rather than within 30 days, RFC_URE1 made no changes to its physical security plan during the duration of this violation, and did not need to make any updates. | The date on which RFC_URE1 was required to be compliant with CIP-006-1. | The date on which RFC_URE1 revised its physical security plan to comply with CIP-006-1 R1.4 and R1.7. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Compliance Audit | RFC_URE1 revised its physical security plan to address response to loss and prohibition of inappropriate use of physical access controls, and to include a requirement to update the physical security plan within 30 days of a physical security system design or configuration change. | 2011-01-27 | 2011-08-19 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which RF considered a mitigating factor.
2011-10-31 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100753 | Settlement Agreement | RF conducted a compliance audit of RFC_URE1 (the Compliance Audit). During the Compliance Audit, RF discovered that RFC_URE1’s Cyber Security incident response plan failed to include a process for updating the Cyber Security incident response plan within 30 calendar days of any changes. Instead, RFC_URE1’s Cyber Security incident response plan included a process for updating the Cyber Security incident response plan within 90 calendar days of any changes. Although Version 1 of CIP-008 allowed for a 90-day period to update the Cyber Security incident response plan, on April 1, 2010 Version 2 of CIP-008 took effect, which requires a narrower, 30-day period. Therefore, from the effective date of CIP-008-2, RFC_URE1 failed to comply with CIP-008-2 R1.4. | CIP-008-2 | R1 | Lower | High | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE1’s Cyber Security incident response plan stated that RFC_URE1 must update the Cyber Security incident response plan within 90 days of any changes rather than within 30 days, RFC_URE1 made no changes to the Cyber Security incident response plan during the time period of this violation, and therefore, did not need to make any updates. | The date on which RFC_URE1's Cyber Security incident response plan was not compliant with the updated Version 2 of CIP-008. | The date on which RFC_URE1 revised its Cyber Security incident response plan to include a process for updating the Cyber Security incident response plan within 30 calendar days of changes. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Compliance Audit | RFC_URE1 revised its Cyber Security incident response plan to include a process for updating the Cyber Security incident response plan within 30 calendar days of any changes. | 2011-01-27 | 2011-08-12 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which RF considered a mitigating factor.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100754 | Settlement Agreement | RF conducted a compliance audit of RFC_URE1 (the Compliance Audit). During the Compliance Audit, RF discovered that RFC_URE1’s recovery plan failed to satisfy both sub-requirements of CIP-009-1 R1. First, RFC_URE1’s recovery plan failed to specify events or conditions of varying duration and severity that would activate the recovery plan, as required by R1.1. Second, RFC_URE1’s recovery plan failed to define the roles and responsibilities of responders, as required by R1.2. In addition, RFC_URE1 failed to address all of its Critical Cyber Assets (CCAs) in its recovery plan. The plan addressed only six of RFC_URE1’s 13 total CCAs. | CIP-009-1 | R1 | Medium | Severe | RF determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE1 did not specify events or conditions of varying duration and severity that would activate the recovery plan, it did address responding to events of varying duration and severity in its CIP-008 Cyber Security Incident response plan. Similarly, although RFC_URE1 did not define the roles and responsibilities of responders in its recovery plan, it did address those roles and responsibilities in its CIP-003 cyber security policy. RFC_URE1 represents that the information that it failed to specifically state within its recovery plan would have been readily available to authorized RFC_URE1 personnel responding to an event requiring the recovery of CCAs. | The date on which RFC_URE1 was required to be compliant with CIP-009-1. | The date on which RFC_URE1 revised its recovery plan to comply with CIP-009-1 R1. | $30,000 (for RFC201000692, RFC201000693, RFC201000694, RFC201100752, RFC201100753, and RFC201100754) | Compliance Audit | RFC_URE1 revised its recovery plan to specify events or conditions of varying duration and severity that would activate the recovery plan, define the roles and responsibilities of responders, and address all of RFC_URE1’s CCAs. | 2011-01-27 | 2011-08-16 | Neither Admits nor Denies | RFC_URE1 had a compliance program at the time of the violation which RF considered a mitigating factor.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000689 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-004-2 R4.1, due to RFC_URE2’s failure to update the list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets within seven days of a change of personnel with such access to Critical Cyber Assets. Specifically, RFC_URE2 terminated an employee for cause but did not update the list of personnel with access to Critical Cyber Assets within seven days of the change in access rights. Nevertheless, RFC_URE2 did revoke the terminated employee’s access within 24 hours, as required by CIP-004-2 R4.2. RFC_URE2 violated CIP-004-2 R4.1 by failing to update the list of personnel who have access to Critical Cyber Assets within seven days of any change of personnel with such access to Critical Cyber Assets. | CIP-004-2 | R4 (R4.1) | Lower | High | ReliabilityFirst determined the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because RFC_URE2 revoked access control cards, passwords, and appropriate accounts from the terminated employee within twenty-four hours of the employee’s termination. In addition, while the terminated employee was on the list of personnel who have access to Critical Cyber Assets because of his access to electronic confidential records, the employee did not have electronic access or control privileges to the Supervisory Control and Data Acquisition (SCADA) system or any other Critical Cyber Assets. | The date by which RFC_URE2 was required to update its Critical Cyber Assets access list. | The date on which RFC_URE2 updated its list of personnel with access to Critical Cyber Assets to remove the terminated individual. | $1,000 (Settlement for RFC201000689) | Self-Report | RFC_URE2 updated its list of personnel with access to Critical Cyber Assets to reflect the updated accesses to Critical Cyber Assets. In addition, RFC_URE2 informed all managers of the need to report the change in status of any employee on the CIP confidential list. | 2011-01-04 | 2011-05-24 | Agrees and Stipulates to the Facts | ReliabilityFirst determined that there was nothing in the record to suggest that broader corporate issues were implicated.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000457 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst concerning a violation of CIP-005-1 R3.2. RFC_URE3’s internal computer network supports RFC_URE3’s Energy Management Systems (EMS). RFC_URE3’s interior firewalls separate the internal computer network from its general business network. The interior firewalls serve as the Electronic Security Perimeter (ESP) for RFC_URE3’s internal computer network, as well as the access points to the ESP. While conducting an internal review , RFC_URE3 discovered that it had not fully enabled its logging and alerting system to alert for unauthorized access attempts to the ESP, as required by CIP-005-1 R3.2. ReliabilityFirst determined RFC_URE3 failed to implement its processes for monitoring and logging access at access points to the ESP. Specifically, RFC_URE3 failed to enable its logging and alert system for attempts at or actual unauthorized access to RFC_URE3's ESP, as required by CIP-005-1 R3.2. | CIP-005-1 | R3 (R3.2) | Medium | Severe | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because, for the duration of the violation, RFC_URE3’s internal computer network was monitored by two intrusion detection software products. Although RFC_URE3’s intrusion detection software did not monitor ESP access points, in the event of actual unauthorized access to or suspicious behavior on RFC_URE3’s ESP, the intrusion detection software would detect the intrusion or suspicious behavior and notify RFC_URE3. In addition, RFC_URE3 reviewed logs from January 1, 2010, through August 12, 2010, the date RFC_URE3 reconfigured its ESP settings to comply with CIP-005-1, R3.2, and found that there were no attempts to access the ESP from any unauthorized IP addresses. | The date RFC_URE3 failed to implement its processes for monitoring and logging access points to the ESP. | The date RFC_URE3 fully enabled detection and alerting for unauthorized access attempts on its ESP. | $6,000 (Settlement of RFC201000457) | Self-Report | RFC_URE3 reconfigured its ESP to send system logging alerts to the administrator and supervisor of the EMS . In addition, RFC_URE3 conducted a test to ensure all configured controls were working as required, which was successful. Finally, RFC_URE3 now retains all logs for a rolling 365-day cycle and all alerts for a minimum of 90 days. | 2010-08-12 | 2011-05-13 | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RFC_URE3’s compliance program as mitigating factors.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000395 | Settlement Agreement | During a Spot Check of RFC_URE4, ReliabilityFirst determined that RFC_URE4 failed to identify six of its Cyber Assets that either use a routable protocol to communicate outside the Electronic Security Perimeter or use a routable protocol within a control center as Critical Cyber Assets. First, RFC_URE4 failed to identify four remote workstations that communicate outside the Electronic Security Perimeter using a routable protocol as Critical Cyber Assets, in violation of CIP-002-1 R3.1. These four remote workstations are enabled to monitor and control the bulk power system (BPS). Second, RFC_URE4 also failed to identify two of its workstations, which use a routable protocol within a control center as Critical Cyber Assets, in violation of CIP-002-1 R3.2. (RFC_URE4 did, however, list the two workstations as Cyber Assets.) | CIP-002-1 | R3 | High | Severe | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. All users of the six workstations at issue had completed personnel risk assessments and had authorized access to Critical Cyber Assets. The four workstations that used a routable protocol to communicate outside the Electronic Security Perimeter utilized three levels of password protection, which provided protection against unauthorized users from utilizing the workstations to control any BPS assets. The two workstations that used a routable protocol within a control center remained within the Physical Security Perimeter and the Electronic Security Perimeter, and therefore received all the same protections as Critical Cyber Assets. | The date on which RFC_URE4 was subject to compliance with CIP-002-1 R3. | The date on which RFC_URE4 reconfigured its workstations. | $16,500 (for RFC201000395, RFC201000398, and RFC201000399) | Spot Check | On August 31, 2010, RFC_URE4 submitted to ReliabilityFirst its mitigation plan to address the violation of CIP-002-1 R3. In this mitigation plan, RFC_URE4 memorialized the actions it took to address the violation of CIP-002-1 R3. RFC_URE4 reconfigured the four workstations that communicated outside the Electronic Security Perimeter, and removed their control functionality. These four workstations are currently not classified as Critical Cyber Assets, since they are now limited to monitoring functions and are therefore not "essential to the operation of the Critical Asset." RFC_URE4 also added the two workstations that use a routable protocol within the control center to the RFC_URE4 Critical Cyber Asset list. | 2010-06-23 | 2010-10-22 | Admits | ReliabilityFirst considered RFC_URE4's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000398 | Settlement Agreement | During a Spot Check, ReliabilityFirst determined that RFC_URE4 failed to ensure that a significant change to existing Cyber Assets within the Electronic Security Perimeter did not adversely affect existing security controls. Specifically, ReliabilityFirst examined evidence of a software upgrade, including RFC_URE4's testing of the software upgrade, but the evidence of testing did not provide sufficient information to establish that the software upgrade did not adversely affect RFC_URE4's cyber security controls. RFC_URE4 provided evidence of later testing of the software upgrade, which showed significant discrepancies from the evidence of the original testing. | CIP-007-1 | R1 | Medium | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE4 utilizes two fully redundant systems at its primary location and two fully redundant systems at its backup location. These systems are upgraded at different times, thereby providing protection in the event of adverse effects from the software upgrade. | The date on which RFC_URE4 implemented a change to existing Cyber Assets within the ESP without ensuring that the change did not adversely affect existing security controls. | The date on which RFC_URE4 documented testing of cyber security controls. | $16,500 (for RFC201000395, RFC201000398, and RFC201000399) | Spot Check | On August 31, 2010, RFC_URE4 submitted to ReliabilityFirst its mitigation plan to address the violation of CIP-007-1 R1. In this mitigation plan, RFC_URE4 memorialized the actions it took to address the violation of CIP-007-1 R1. RFC_URE4 created a check list for documenting all future testing of changes to Cyber Assets to ensure that it properly tests security controls both before and after the changes to Cyber Asset are made. | 2010-06-22 | 2010-10-22 | Admits | ReliabilityFirst considered RFC_URE4's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000399 | Settlement Agreement | During a Spot Check, ReliabilityFirst determined that RFC_URE4 failed to demonstrate that it annually tested its Cyber Security Incident response plan. Therefore, RFC_URE4 failed to ensure that its Cyber Security Incident response plan is tested at least annually. ReliabilityFirst found that RFC_URE4 violated CIP-008-1 R1.6 by failing to ensure that its Cyber Security Incident response plan is tested at least annually. | CIP-008-1 | R1.6 | Lower | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although, RFC_URE4 did not produce sufficient documentation at the Spot Check to establish compliance with CIP-008-1 R1, RFC_URE4 represents that it tested the Cyber Security Incident response plan. Furthermore, RFC_URE4 has conducted a recent test of the Cyber Security Incident response plan, which demonstrates the efficacy of the Cyber Security Incident response plan in responding to incidents. | The date on which RFC_URE4 was subject to compliance with CIP-008-1 R1. | The date on which RFC_URE4 developed a test report form for its Cyber Security Incident response plan. | $16,500 (for RFC201000395, RFC201000398, and RFC201000399) | Spot Check | On August 31, 2010, RFC_URE4 submitted to ReliabilityFirst its mitigation plan to address the violation of CIP-008-1 R1.6. RFC_URE4 memorialized the actions it took to address the violation of CIP-008-1 R1.6. RFC_URE4 developed a test report form to cover all steps required in RFC_URE4's Cyber Security Incident response plan. | 2010-06-21 | 2010-10-22 | Admits | ReliabilityFirst considered RFC_URE4's internal compliance program (ICP) as a mitigating factor in assessing the penalty.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000393 | Settlement Agreement | RFC_URE5 submitted a Self-Report indicating a violation of CIP-004-1 R4.2, to ReliabilityFirst. RFC_URE5 failed to remove one employee (Employee A) which no longer required access to CCAs from their Critical Cyber Asset (CCA) Electronic Access List within seven days. On March 22, 2010, RFC_URE5 designated Employee A as inactive but did not remove CCA electronic access or update the CCA Electronic Access List until May 11, 2010. RFC_URE5 submitted a Self-Report update indicating that the violation of CIP-004-1 R4.2 expanded in scope. RFC_URE5 did not remove an additional employee (Employee B) from its CCA Physical Access list within seven days of Employee B no longer requiring access. Specifically, Employee B resigned from the company effective August 7, 2010, but was not removed from the Physical Access List until August 18, 2010. RFC_URE5 did revoke all access rights for Employee B on August 7, 2010. RFC_URE5 submitted a second update to the Self-Report. RFC_URE5 granted an employee (Employee C) temporary access to a Physical Security Perimeter (PSP) from June 2, 2010 to June 4, 2010, but failed to remove Employee C from the CCA Physical Access List within seven calendar days of revoking Employee C's access on June 4, 2010. RFC_URE5 did not remove Employee C from the CCA Physical Access List until September 21, 2010. RFC_URE5 violated CIP-004-1 R4 on three separate occasions when it failed to remove Employees A, B and C from its CCA Access Lists within seven days of those employees no longer requiring access to CCAs. | CIP-004-1 | R4/ R4.2 | Medium | Moderate | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Employee A did not have physical access to the PSP in which the CCAs reside during the time period of the violation. Moreover the CCAs could not be electronically accessed by Employee A from anywhere outside the PSP. Employee B did not have physical access to the PSP during the time period of the violation. RFC_URE5 collected all access devices that would allow Employee B to physically enter the PSP on the same day as Employee B resigned. As a result, it was impossible for Employee B to physically access the PSP after August 7, 2010. Employee B also had completed CIP training and had a clear personnel risk assessment (PRA) in place at the time of the violation. Although Employee C did have key card access to the PSP, Employee C did not have key access to the perimeter gate surrounding the PSP, and did not have a non-forcible means of access to the perimeter gate surrounding the PSP. Additionally, Employee C had completed CIP training and had a clear PRA in place at the time of the violation. | The date by which RFC_URE5 should have removed Employee A from the CCA Electronic Access List. | The date RFC_URE5 removed Employee C from the CCA Physical Access List. | $30,000 (for RFC201000393, RFC201000394, and RFC201000773) | Self-Report | RFC_URE5 updated the CCA Access Lists to reflect the personnel status changes for Employees A, B, and C. RFC_URE5 also removed Employee C's key access to the PSP. RFC_URE5 reviewed the incidents of non-compliance and the procedures that were not followed, and then revised those procedures. Senior management from the Human Resources and Legal departments reinforced the importance of adhering to the CIP procedures to the entire company. RFC_URE5 developed a process to compare its Human Resources personnel database with the database used to identify roles in the CIP Compliance program. RFC_URE5 now generates a daily report to identify any changes in the status of an employee with physical or electronic access to the PSP. | 2011-02-22 | 2011-06-07 | Neither Admits nor Denies | The parent company of RFC_URE5 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor. RFC_URE5 does not have any prior violations of the CIP Reliability Standards. ReliabilityFirst did consider the repetitive nature of the violations addressed within this Settlement Agreement as an aggravating factor in the penalty determination. In considering the instant violations, ReliabilityFirst did not observe any evidence of involvement of the entire holding company system or other affiliates.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000394 | Settlement Agreement | RFC_URE5 submitted a Self-Report indicating a violation of CIP-006-1 R2 to ReliabilityFirst. On March 31, 2010, a RFC_URE5 employee with authorized unescorted physical access to a Physical Security Perimeter (PSP) (Authorized Employee) failed to manage a PSP access point on three occasions, for a combined duration of approximately 15 minutes. Individuals without authorized access were performing maintenance on the floor below the PSP access point, and as a result of the maintenance, RFC_URE5 left the door that is used to secure the PSP ajar. During the time period that the door to the PSP was ajar, the Authorized Employee left the area on three occasions and failed to monitor this PSP access point. RFC_URE5 violated CIP-006-1 R2 by failing to implement its physical security plan and manage physical access to all access points to the PSP. | CIP-006-1 | R2 | Medium | High | ReliabilityFirst determined this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system to the reliability of the bulk power system because RFC_URE5 had a documented Physical Security Plan in place that addressed the requirement to control access points to the PSP, and trained the Authorized Employee on this requirement. The PSP access point is located within an access-controlled facility and also within a further restricted, access-controlled, corporate data center. Therefore, the PSP access point has multiple layers of protection. The PSP is also under video surveillance, which allowed RFC_URE5 to monitor any attempts by an unauthorized individual to enter through this PSP access point. No such attempts were made during the alleged violation. Finally, the violation was short in duration, lasting approximately 15 minutes. | The time period which RFC_URE5 failed to manage physical access to a PSP for 15 minutes. | When RFC_URE5 returned to monitoring physical access to the PSP. | $30,000 (for RFC201000393, RFC201000394, and RFC201000773) | Self-Report | RFC_URE5 enhanced its Physical Security Plan, and developed a targeted CIP training session specifically for business services employees who may be involved in maintenance activities at PSP access points. The CIP training session reinforced the companies' visitor escort policy and clarified the requirements for monitoring PSP access points. RFC_URE5 conducted additional CIP training sessions for RFC_URE5 employees and contractors. RFC_URE5 also posted signs at PSP access points and distributed laminated cards to remind employees and contractors that access is restricted to authorized individuals, and detail requirements for access control, visitor escorting, and entry logging. | 2010-08-30 | 2011-04-13 | Neither Admits nor Denies | The parent company of RFC_URE5 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor. RFC_URE5 does not have any prior violations of the CIP Reliability Standards. ReliabilityFirst did consider the repetitive nature of the violations addressed within this Settlement Agreement as an aggravating factor in the penalty determination. In considering the instant violations, ReliabilityFirst did not observe any evidence of involvement of the entire holding company system or other affiliates.
2011-09-30 | FERC | NP11-270-000 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000773 | Settlement Agreement | RFC_URE5 submitted a Self-Report indicating a violation of CIP-004-1 R3 to ReliabilityFirst. On October 1, 2010, RFC_URE5 discovered that it provided an employee (Employee 1) with authorized unescorted physical access to a Physical Security Perimeter (PSP) on January 1, 2010, who did not have a personnel risk assessment (PRA) within 30 days of access. On October 1, 2010, RFC_URE5 also discovered that it provided a second employee (Employee 2) with authorized unescorted physical access to a PSP on April 15, 2010, who did not have a PRA within 30 days of access. Finally, on October 14, 2010, RFC_URE5 discovered that it provided a third employee (Employee 3) with authorized unescorted physical access to a PSP on October 13, 2010, who did not have a PRA within 30 days of access. RFC_URE5 violated CIP-004-1 R3 by failing to conduct PRAs for three employees within 30 days of providing those employees with authorized access to a PSP. | CIP-004-1 | R3 | Medium | High | ReliabilityFirst determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system because Employee 1 and Employee 2 did not enter the PSP during the time period of the violation. Additionally, RFC_URE5 later conducted PRAs for Employee 1,2, and 3, which identified no issues. Employee 3 did not have key access or any other means of non-forcible access to the perimeter gate surrounding the PSP at issue, and RFC_URE5's records of Employee 3 indicate that Employee 3 never attempted to access the PSP during the violation. | 30 days after Employee 1 had access to the PSP without a PRA. | The date on which RFC_URE5 revoked the authorized unescorted physical access rights for Employee 3. | $30,000 (for RFC201000393, RFC201000394, and RFC201000773) | Self-Report | RFC_URE5 revoked access rights to Employees 1, 2, and 3. RFC_URE5 also conducted PRAs for Employees 1, 2 and 3, which identified no issues. Additionally, RFC_URE5 is adding a control to its PSP access request process which will require the requestor to confirm PRA status before submitting a request for access to the PSP. | 2011-02-22 | 2011-06-07 | Neither Admits nor Denies | The parent company of RFC_URE5 had a compliance program at the time of the violation which ReliabilityFirst considered a mitigating factor. RFC_URE5 does not have any prior violations of the CIP Reliability Standards. ReliabilityFirst did consider the repetitive nature of the violations addressed within this Settlement Agreement as an aggravating factor in the penalty determination. In considering the instant violations, ReliabilityFirst did not observe any evidence of involvement of the entire holding company system or other affiliates.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001887 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence, WECC determined that WECC_URE1 failed to demonstrate that it had procedures in place for the recognition of sabotage events and for making its operating personnel aware of sabotage events on its facilities and on multi-site sabotage events affecting larger portions of the Interconnection, in violation of CIP-001-1 R1. | CIP-001-1 | R1 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity but has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although sabotage recognition procedures helps personnel assess the sabotage event and determine further actions, the impact on the BPS from a potential sabotage event at WECC_URE1 would have been very limited because of WECC_URE1's limited size, single interconnection to another entity, and unique supply profile serving that other entity only. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R1. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001888 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. As a result, WECC determined that WECC_URE1 failed to demonstrate that it had procedures in place for the communication of information concerning sabotage events to appropriate parties in the Interconnection. | CIP-001-1 | R2 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although notifying other operating systems of possible sabotage events increases the situational awareness of the entities interconnected to the BPS, the impact on the BPS from a potential failure to communicate a sabotage event at WECC_URE1 would have been very limited because of WECC_URE1's limited size and single interconnection to another entity, which minimizes the risk to the BPS. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R2. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001889 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. As a result, WECC determined that WECC_URE1 failed to provide its operating personnel with sabotage response guidelines, including personnel to contact, for reporting disturbances due to sabotage events. | CIP-001-1 | R3 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although a lack of sabotage communication guidelines could delay corrective actions on behalf of the entity, the impact on the BPS from a potential failure of WECC_URE1's personnel to report a sabotage event would have been very limited because of WECC_URE1's limited size and single interconnection to another entity, which minimizes the risk to the BPS. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R3. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001890 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. As a result, WECC determined that WECC_URE1 failed to establish communications contacts with local FBI officials and to develop reporting procedures. | CIP-001-1 | R4 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. WECC determined that although a lack of reporting procedures to the local FBI could lead to sabotage events being unreported, the impact on the BPS from a potential failure of WECC_URE1's personnel to contact the FBI would have been very limited because of WECC_URE1's limited size and single interconnection to another entity, which minimizes the risk to the BPS. | The date on which WECC_URE1 was subject to compliance with CIP-001-1 R4. | The date on which WECC_URE1 documented and implemented its sabotage reporting procedure. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan, covering the violations of CIP-001-1 R1-R4. According to the Mitigation Plan, WECC_URE1 implemented procedures for the recognition of sabotage events and for making its personnel aware of such events on its facilities and of multi-site sabotage affecting larger portions of the Interconnection. WECC_URE1 also implemented procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection, provided its operating personnel with sabotage response guidelines, established contacts with local FBI officials and developed appropriate reporting procedures. WECC_URE1 submitted its sabotage recognition and reporting procedure to WECC as evidence of its Mitigation Plan completion. | 2010-08-20 | 2011-02-08 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002056 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification and determined that WECC_URE1 failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. | CIP-002-1 | R1 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R1. | The date on which WECC_URE1 documented and implemented its methodology document. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002057 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification submittal and determined that WECC_URE1failed to develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology (RBAM) required in R1. | CIP-002-1 | R2 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R2. | The date on which WECC_URE1 documented and implemented its methodology document, including a list of Critical Assets. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002058 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification submittal and determined that WECC_URE1failed to develop a list of its associated Critical Cyber Assets that are essential to the operation of the Critical Assets. | CIP-002-1 | R3 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R3. | The date on which WECC_URE1 documented and implemented its methodology document, including a list of associated Critical Cyber Assets. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002059 | Settlement Agreement | WECC notified WECC_URE1 that WECC was initiating a semi-annual CIP Self-Certification process. WECC_URE1 filed a Self-Certification statement and reported that its compliance status for CIP-002-1 R1-R4 was "Not Started." WECC reviewed WECC_URE1's Self-Certification submittal and determined that WECC_URE1failed to have a senior manager or delegate approve annually the list of WECC_URE1's Critical Assets or Critical Cyber Assets. | CIP-002-1 | R4 | Lower | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because after WECC_URE1 provided and implemented its RBAM following WECC's audit, it became apparent that WECC_URE1 did not have any Critical Assets or Critical Cyber Assets on its system and, therefore, WECC concluded that there had been no actual risk to the BPS. Also, WECC_URE1's size minimizes the risk to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with CIP-002-1 R4. | The date on which WECC_URE1 documented and implemented its methodology document, including senior manager or delegate approval. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Self-Certification | WECC_URE1 submitted a Mitigation Plan covering the violations of CIP-002-1 R1-R4. According to the Mitigation Plan, WECC_URE1 developed and implemented a formal Critical Asset Identification Methodology to be applied in identifying Critical Assets and Critical Cyber Assets. WECC_URE1 also will annually update its list of Critical Assets and Critical Cyber Assets. The methodology document submitted as evidence of compliance included documentation of WECC_URE1's application of its methodology for the purpose of assessing whether WECC_URE1 owns, operates, or controls Critical Assets and Critical Cyber Assets as well as the corresponding asset lists and designated senior manager approvals. | 2010-11-15 | 2011-02-02 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001893 | Settlement Agreement | On December 4, 2009, WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC, WECC determined that WECC_URE1 failed to provide evidence that it had documented its Facility Rating Methodology, as required by FAC-008-1 R1. | FAC-008-1 | R1 | Lower | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because of its limited size and a single interconnection to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with FAC-008-1 R1. | The date on which WECC_URE1 documented its Facility Ratings Methodology. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for FAC-008-1 R1. According to the Mitigation Plan, WECC_URE1 documented a Facility Rating Methodology for facilities and equipment at the WECC_URE1 generating facility, including the generator, transmission conductors, transformers, relay protective devices and terminal equipment. As evidence of compliance, WECC_URE1 submitted its Facility Rating Methodology. | 2010-09-08 | 2011-04-05 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001896 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that it had established Ratings for its Facilities that are consistent with its associated Facility Ratings Methodology. | FAC-009-1 | R1 | Medium | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS) because of its limited size and a single interconnection to the BPS. WECC_URE1 operates a facility with a small nameplate capacity of less than 30 MW. In addition, the risk was substantially mitigated by the fact that WECC_URE1 has only one interconnection to the BPS. WECC_URE1 sells its entire output to another entity and has no significant impact on the other entity's electricity supply or any other facilities connected to the BPS due to its limited size. | The date on which WECC_URE1 was subject to compliance with FAC-009-1 R1. | The date on which WECC_URE1 documented Facility Ratings consistent with its associated Facility Ratings Methodology. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for FAC-009-1 R1. According to the Mitigation Plan, WECC_URE1 documented Facility Ratings as required by this Standard and submitted to WECC its Facility Rating Methodology spreadsheet as evidence of compliance. | 2010-09-08 | 2011-04-12 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001917 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that its operating personnel were familiar with the purpose and limitations of Protection System schemes applied in WECC_URE1's area. | PRC-001-1 | R1 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 operates a small facility of less than 30 MW, and therefore, an unintended trip or a failure to trip could only impact WECC_URE1's equipment but would not have broader implications on the BPS. | The date on which WECC_URE1 was subject to compliance with PRC-001-1 R1. | The date on which WECC_URE1 implemented appropriate training. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-001-1 R1 and R3. According to the Mitigation Plan, WECC_URE1 developed and implemented procedures and provided associated training to ensure that its operating personnel are familiar with the purposes and limitations of the Protection Systems applied in WECC_URE1's area. WECC_URE1 also implemented training to ensure that new Protection Systems or changes in the existing Protection Systems are coordinated with all appropriate entities. WECC_URE1 submitted a copy of the relevant procedures and training materials as evidence of compliance. | 2010-09-24 | 2010-11-16 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001919 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that it coordinated all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | PRC-001-1 | R3 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE1 confirmed that it had not experienced any protective system changes that would require Protection System changes by others, including the Transmission Operator and the Host Balancing Authority. In addition, the risk to the BPS was further mitigated by the limited size of the entity and the fact that it has only one interconnection point with the BPS. | The date on which WECC_URE1 was subject to compliance with PRC-001-1 R3. | The date on which WECC_URE1 implemented appropriate training. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-001-1 R1 and R3. According to the Mitigation Plan, WECC_URE1 developed and implemented procedures and provided associated training to ensure that its operating personnel are familiar with the purposes and limitations of the Protection Systems applied in WECC_URE1's area. WECC_URE1 also implemented training to ensure that new Protection Systems or changes in the existing Protection Systems are coordinated with all appropriate entities. WECC_URE1 submitted a copy of the relevant procedures and training materials as evidence of compliance. | 2010-09-24 | 2010-11-16 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001922 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence that it had a Protection System maintenance and testing program for Protection Systems that affect the reliability of the bulk power system (BPS), specifically addressing maintenance and testing intervals and their basis and a summary of maintenance and testing procedures. | PRC-005-1 | R1 | High | Severe | WECC determined that the violation did not pose a serious or substantial risk and posed a moderate risk to the reliability of the BPS because WECC_URE1 had acquired outside technical support to perform Protection System maintenance and testing but the documentation of this maintenance and testing did not completely address all of the elements that comprise its Protection System. The relay devices are documented but WECC determined that additional effort was needed to document maintenance and testing of DC circuitry, station batteries, associated communication equipment and voltage and current sensing devices. In addition, the risk to the BPS was further mitigated by the limited size of the entity and the fact that it has only one interconnection point with the BPS. | The date on which WECC_URE1 was subject to compliance with PRC-005-1 R1. | The date on which WECC_URE1 documented its Protection System maintenance and testing program. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-005-1 R1 and R2.1. According to the Mitigation Plan, WECC_URE1 developed and implemented a documented Protection System maintenance and testing program (Program). The Program includes maintenance and testing intervals and their basis, and addresses relay protective devices, station batteries, voltage and current sensing devices, associated communication systems and DC control circuitry, as appropriate. The Program also includes a summary of maintenance and testing procedures for all BPS elements that comprise WECC_URE1's generator Protection System. As evidence of compliance, WECC_URE1 submitted a copy of the relevant program documents, a list of Protection System components, the schedule for maintenance and testing and documentation regarding testing and maintenance of its Protection System devices. | 2010-08-19 | 2011-03-22 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201001923 | Settlement Agreement | WECC sent WECC_URE1 a Notice of Off-Site Compliance Audit directing WECC_URE1 to provide evidence demonstrating compliance with the Reliability Standards. WECC_URE1 failed to submit audit evidence following the notice. Subsequently, WECC sent three additional notices, directing WECC_URE1 to submit the requested evidence but the entity did not respond. Based on WECC_URE1's failure to submit audit evidence as requested by WECC on several occasions, WECC determined that WECC_URE1 failed to provide evidence of its Protection System maintenance and testing program and the implementation of that program, including evidence that the Protection Systems were maintained and tested within the defined intervals, and the date each Protection System was last tested or maintained. | PRC-005-1 | R2.1 | High | Severe | WECC determined that the violation did not pose serious or substantial risk and posed a moderate risk to the reliability of the bulk power system (BPS) because although WECC_URE1 did not provide evidence that its Protection Systems were maintained and tested within defined intervals, WECC_URE1 subsequently provided evidence, as part of its Mitigation Plan completion, demonstrating that its Protection System devices had been tested and maintained. | The date on which WECC_URE1 was subject to compliance with PRC-005-1 R2. | The date on which WECC_URE1 documented testing and maintenance of its Protection System devices. | $90,000 (for WECC201001887, WECC201001888, WECC201001889, WECC201001890, WECC201002056, WECC201002057, WECC201002058, WECC201002059, WECC201001893, WECC201001896, WECC201001917, WECC201001919, WECC201001922, WECC201001923) | Off-Site Compliance Audit | WECC_URE1 submitted a Mitigation Plan for PRC-005-1 R1 and R2.1. According to the Mitigation Plan, WECC_URE1 developed and implemented a documented Protection System maintenance and testing program (Program). The Program includes maintenance and testing intervals and their basis, and addresses relay protective devices, station batteries, voltage and current sensing devices, associated communication systems and DC control circuitry, as appropriate. The Program also includes a summary of maintenance and testing procedures for all BPS elements that comprise WECC_URE1's generator Protection System. As evidence of compliance, WECC_URE1 submitted a copy of the relevant program documents, a list of Protection System components, the schedule for maintenance and testing and documentation regarding testing and maintenance of its Protection System devices. | 2010-08-19 | 2011-03-22 | Agree and stipulate to the facts. | Mitigating Factors: WECC_URE1 developed and implemented an internal compliance program (ICP), designed to govern WECC_URE1's future compliance efforts. Aggravating Factors: 1) WECC_URE1 was not cooperative with WECC and did not demonstrate a culture of compliance during the compliance auditing process, and 2) WECC_URE1 did not timely complete its mandatory Self-Certification.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002367 | Notice of Confirmed Violation | On January 26, 2010, WECC_URE2 submitted Self-Reports to WECC concerning violations of CIP-007-1 R3 and R6. On November 22, 2010, a WECC subject matter expert (SME) conducted an interview with WECC_URE2 personnel, and determined that WECC_URE2’s CIP-007 Self-Reports involved one server used for controlling physical access (doors) at three Physical Security Perimeters (PSPs). Then, the SME determined that CIP-007 does not cover such devices. Therefore, on December 30, 2010, WECC_URE2 replaced its CIP-007 Self-Reports with a single Self-Report addressing a violation of CIP-006-1 R1.8. In its new Self-Report, WECC_URE2 clarified that the server is used for physical access and monitoring its primary control center. A WECC SME reviewed WECC_URE2’s CIP-006-1 R1 Self-Report, and determined WECC_URE2 did not assess available security patches for the server and did not review the server’s system event logs. WECC determined that WECC_URE2’s failure to assess the available security patches or review the server’s system event logs did not afford the server the protective measures specified in CIP-007. | CIP-006-1 | R1 | Medium | Moderate | WECC determined that the violation of CIP-006-1 R1 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE2 stated that the access control and monitoring assets to its primary control center, including the server at issue, were in a facility that logged, detected, and alarmed for unauthorized physical and electronic access. | The date on which WECC_URE2 was subject to compliance with CIP-006-1 R1. | The date on which WECC_URE2 implemented an appropriate patch management system and enabled logging. | $20,400 (for WECC201002367, WECC201002323, and WECC201002324) | Self-Report | WECC_URE2 combined the update service of the cyber systems to the current server updated services database to better manage, audit, and report security patch management. WECC_URE2 enabled logging and is performing weekly log reviews as defined in its CIP-007 R6 cyber security event procedure. | 2010-03-01 | 2011-07-21 | Does Not Contest | WECC_URE2 had a documented internal compliance program (ICP) at the time of the violation that WECC considered as a mitigating factor in determining the penalty. WECC determined that the WECC_URE2 ICP has been reviewed and approved by an Authorized Entity Officer or equivalent, is fully documented, reviewed and approved by an Authorized Entity Officer or equivalent, and has an oversight position identified and staffed.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002323 | Notice of Confirmed Violation | WECC notified WECC_URE2 that WECC was initiating the semi-annual CIP Self-Certification process for the year ending 2009. On January 28, 2010, WECC_URE2 submitted a Self-Report to WECC concerning a violation of CIP-006-1 R6 due to WECC_URE2’s failure to implement a maintenance and testing program to ensure the functionality of WECC_URE2’s physical security systems. Although WECC_URE2 self-reported this violation, because WECC_URE2 self-reported during the Self-Certification submission period, WECC classified the discovery method for this violation as Self-Certification. On November 22, 2010, a WECC SME conducted an interview with WECC_URE2 personnel where WECC_URE2 clarified that it did not perform baseline testing prior to or on its mandatory compliance date. The SME determined that WECC_URE2 did not conduct testing on its system, which is comprised of a server, workstations, card readers, and door readers in order to provide locking and opening controls at access points. In addition, WECC_URE2’s system provides alarms and alerts to a centralized database, and is associated with three Physical Security Perimeters (PSPs), including WECC_URE2’s (1) data center, (2) primary control center, and (3) back-up control center. WECC determined, by not performing baseline testing, WECC_URE2 failed to implement a maintenance and testing program to ensure that WECC_URE2 physical security systems under CIP-006-1 R2-R4 function properly. | CIP-006-1 | R6 | Medium | Moderate | WECC determined that the violation of CIP-006-1 R6 posed a moderate risk to the reliability of the bulk power system (BPS) because WECC_URE2 failed to implement a maintenance and testing program for the physical security systems for three PSPs, including the primary control center, backup control center and a data center. The physical security system was used for access control, monitoring and logging at these PSPs, and the failure to implement the maintenance and testing program could allow physical security systems to malfunction and potential unauthorized access to the PSPs. WECC determined, however, that the violation did not pose a serious or substantial risk to the BPS because the facilities had physical and electronic access logging, were continuously monitored including video monitoring of access points and weekly log reviews were conducted by WECC_URE2. In addition, WECC_URE2 has an incident response plan, and hardware alerts for a physical security device failure. | The date on which WECC_URE2 was subject to compliance with CIP-006-1 R6. | The date on which WECC_URE2 performed and documented baseline testing. | $20,400 (for WECC201002367, WECC201002323, and WECC201002324) | Self-Certification | WECC_URE2 performed a test in accordance with its CIP physical security maintenance test program in order to provide evidence to establish a documented baseline. | 2010-02-10 | 2010-12-15 | Does Not Contest | WECC_URE2 had a documented internal compliance program (ICP) at the time of the violation that WECC considered as a mitigating factor in determining the penalty. WECC determined that the WECC_URE2 ICP has been reviewed and approved by an Authorized Entity Officer or equivalent, is fully documented, reviewed and approved by an Authorized Entity Officer or equivalent, and has an oversight position identified and staffed.
2011-09-30 | FERC | NP11-270-000 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201002324 | Notice of Confirmed Violation | On October 21, 2010, WECC_URE2 discovered a possible violation of CIP-007-1 R5. Then, on November 10, 2010, WECC_URE2 submitted a Self-Report to WECC concerning a violation of CIP-007-1 R5 due to WECC_URE2’s failure to document procedural controls that enforce access authentication and accountability for all user activity for 31 devices, including switches, firewalls, and servers. On November 22, 2010, a WECC SME conducted an interview with WECC_URE2 personnel who clarified information from its Self-Report stating that where WECC_URE2 could not use automated software to enforce password complexity, WECC_URE2 has a procedure for doing annual password changes in manual fashion. WECC_URE2’s procedure calls for password cracking tools to validate if a password met the complexity requirements outlined in CIP-007 R5.3. The SME determined that after WECC_URE2 installed such password cracking/validation tools pursuant to WECC_URE2’s account management procedure, WECC_URE2’s test machines crashed. Therefore, WECC_URE2 created a process to maintain password complexity through accountability and witness documentation of password changes and complexity based on the requirements. Both WECC_URE2 and the SME determined that WECC_URE2 had to institute this accountability and witness process on 31 devices, including switches, firewalls, and servers located in WECC_URE2’s control center and data center, that were Critical Cyber Assets or Cyber Assets within the Electronic Security Perimeter. Nevertheless, WECC determined WECC_URE2 did not document the manual process associated with the 31 devices. | CIP-007-1 | R5 | Lower | Moderate | WECC determined that the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because while WECC_URE2 did not update its documented account management procedures to reflect procedural controls, WECC_URE2 did in fact follow its manual process of annually changing passwords with manual authentication and witness controls. In addition, WECC_URE2 did enforce authentication and accountability of all user activity for systems access by establishing and implementing technical controls as required by the standard. | The date on which WECC_URE2 was subject to compliance with CIP-007-1 R5. | TBD | $20,400 (for WECC201002367, WECC201002323, and WECC201002324) | Self-Report | WECC_URE2 rewrote procedures to address manual processes that were occurring internally, and drafted additional procedures dealing with default, administrative and shared accounts to assist in sustaining compliance. WECC_URE2 completed a scheduled upgrade to its Energy Management System (EMS) to eliminate system dependencies on shared accounts. WECC_URE2 changed its accounts to the normal password expiration required by CIP-007 R5 password management procedure. WECC_URE2 documented previously undocumented user IDs as shared accounts and the domain automated password complexity and aging was enabled for these accounts as well. WECC_URE2 provided additional training of its CIP-007 R5 shared account management procedure in order to utilize automated task management solutions to schedule and escalate tasks. WECC_URE2 began adhering to and follow its existing procedures and tasks associated to changing shared accounts passwords when employees with access retire, leave employment or change job responsibilities. WECC_URE2 began adhering to and following its existing procedures and tasks associated to changing accounts passwords. WECC_URE2 generated unique user IDs for management personnel and follow complexity and aging requirements set forth within the procedure. WECC_URE2 began utilizing task management programs to alert the responsible personnel of specific tasks needing to be performed. WECC_URE2 began issuing, tracking and escalating tasks based on the relative due date of the task. WECC_URE2 began revising its CIP-007 R1 testing procedure to better align with test process and other standard requirement procedures to prevent or minimize overlooked areas. WECC_URE2 began revising its password procedures to better align the internal process to prevent or minimize adverse effects on system operations while maintaining compliance. WECC_URE2 began adhering to the procedures as well as automated task management, escalation and auditing in order to assist in sustaining future compliance. | 12/30/2011 (approved date) | TBD | Does Not Contest | WECC_URE2 had a documented internal compliance program (ICP) at the time of the violation that WECC considered as a mitigating factor in determining the penalty. WECC determined that the WECC_URE2 ICP has been reviewed and approved by an Authorized Entity Officer or equivalent, is fully documented, reviewed and approved by an Authorized Entity Officer or equivalent, and has an oversight position identified and staffed. WECC determined that WECC_URE2's prior violations of CIP-007-1 R1 and CIP-007-1 R6 should not serve as a basis for aggravating the penalty because the instant violation is sufficiently distinct due to the unique differences between Critical Cyber Assets (protected in accordance with CIP-007).