## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req. | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
2020-12-30 | NOC-2688 | ReliabilityFirst Corporation (ReliabilityFirst) | Michigan Power LP | NCR11409 | GOP | Settlement Agreement | Admits | 0 | RFC2019021748 | VAR-002-4.1 | R2 | Moderate | Medium | Severe | Spot-Check | 2019-06-24 | 2017-11-01 | 2019-01-08 | 2019-01-08 | TBD | On June 24, 2019, ReliabilityFirst determined that the entity, as a Generator Operator (GOP), was in violation of VAR-002-4.1 R2 identified during a Spot-Check conducted from December 21, 2018 through January 4, 2019. While gathering evidence during the Spot-Check, the entity discovered that it failed to maintain the reactive power schedule as prescribed by its Transmission Operator, and also failed to satisfy the notification requirements from November 1, 2017, through the end of 2018. The entity entered into a reduced dispatch agreement (RDA) with Consumers Energy on November 1, 2017, which required the entity to reduce its output at various times, as directed by Consumers. Each day, Consumers would send a schedule to the entity’s control room to reduce MWs at certain hours throughout that day, and the entity was responsible for following that schedule. Although the entity reduced MWs according to the schedule, it did not reduce the output of MVARs as needed to maintain the reactive power schedule. In total, Consumers requested the entity to reduce its MWs 284 times, and the entity failed to maintain its voltage on 245 of those occasions. The root cause of this violation was the entity’s lack of awareness of the constant output of MVARs to the grid and the entity’s misunderstanding that its communications with Consumers regarding reduced generation output satisfied any notification requirements. This root cause involves the management practices of grid operations and workforce management, which includes providing training, education, and awareness to employees. This violation started on November 1, 2017, when the entity was required to comply with VAR-002-4.1 R2 and ended on January 8, 2019, when the entity completed its Mitigation Plan. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is a negative impact on the reliable operation of the BPS by allowing detrimental levels of generator voltage or reactive power output. This risk is not minimal in this case considering the length of time the issue persisted and the number of instances involved. The risk is not serious or substantial in this case based on the following factors. First, the facility at issue is a 125 MW unit, which reduces the potential impact of the noncompliance. Second, although the facility is a cogeneration facility with a high capacity factor, the entity is still inherently lower risk considering the following factors: (a) it does not own a special protection system; (b) it is not a Blackstart Resource; (c) it has no system restoration responsibilities; and, (d) it has never experienced a misoperation. ReliabilityFirst also notes that the Transmission Operator indicated that it did not identify any system voltage issues caused by the entity’s failure to maintain its reactive power schedule, which suggests that any excursions were minor. No harm is known to have occurred. | To mitigate this noncompliance, the entity has: 1) instructed all operations personnel that calls will be placed with ITC and Consumers Energy prior to adjusting MW output. Additionally, entity operations personnel will notify ITC of any variances from the assigned reactive power schedule. These communications will be logged in the control room logbook; 2) implemented an additional graphic monitoring of MVAR at the point of interconnection, to enable operations personnel to visually detect fluctuations of MVAR; 3) made corrections to both the combustion and steam turbine to maintain the -3/+3 MVAR reactive power band; and 4) contacted ITC to discuss the excursions. In a written response, ITC stated that they did not identify any system voltage issues caused by the entity’s failure to maintain the reactive power schedule during Reduced Dispatch Agreement events. | ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. ReliabilityFirst determined that no monetary penalty was warranted due to the lack of any actual harm and the reduced potential for harm. Specifically, ReliabilityFirst considered the following factors: First, the facility at issue is a 125 MW unit, which reduces the potential impact of the noncompliance. Second, the entity is inherently lower risk considering the following factors: (a) it does not own a special protection system; (b) it is not a Blackstart Resource; (c) it has no system restoration responsibilities; and, (d) it has never experienced a misoperation. ReliabilityFirst also notes that the Transmission Operator indicated that it did not identify any system voltage issues caused by the entity’s failure to maintain its reactive power schedule, which suggests that any excursions were minor. As additional support for the $0 penalty amount, ReliabilityFirst notes that the entity has never had a violation prior to the current issue. However, ReliabilityFirst still determined that a Spreadsheet Notice of Penalty was the appropriate disposition method considering (a) the fact that ReliabilityFirst identified the issue during a Spot Check; and (b) the length of time that the issue persisted and the number of instances involved.
2020-12-30 | NOC-2693 | ReliabilityFirst Corporation (ReliabilityFirst) | METC | NCR00820 | TO | Settlement Agreement | Admits | 125000 | RFC2017017946 | FAC-008-1 | R1 | Moderate | Lower | Severe | Self-Report | 2017-07-05 | 2007-06-18 | 12/31/2021 (expected end date) | 12/31/2021 (expected completion date) | TBD | On July 5, 2017, METC submitted a Self-Report to ReliabilityFirst on behalf of ITC Midwest (ITCM) stating that, as a Transmission Owner, ITCM had a possible violation of FAC-008-1 R1. METC submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. During a January 2017 internal control review of the Tiffin to Arnold 345 kV circuit, ITCM reviewed relay thermal limits and discovered that a relay thermal limit associated with the T1 transformer differential scheme did not match the published equipment rating and resulted in reducing the Facility Rating. This lower thermal limit was caused by the combination of the relay limit (which was above five amps) and the impact of the delta-connected Current Transformer (CT), which provides more secondary current to the relays than a wye-connected CT. ITCM identified this relay thermal limit as the most limiting element for both the Duane Arnold-Tiffin 345 kV Facility and the Duane Arnold 345/161 kV Transformer Facility. Subsequently, the planning and relay groups for both ITCM and the ITC Michigan operating companies (i.e., ITCT, METC, ITCGP, and ITCI) conducted a root cause analysis and an extent of condition review. These reviews were designed to identify how ITCM and the Michigan groups calculated, considered, and applied relay thermal limits in the ITC Facility Ratings database. Through this work, ITCM determined that it had not been previously considering the impacts of delta-connected CTs when determining secondary equipment capabilities. Had the impacts been considered, ITCM would have identified this limit in prior reviews. ReliabilityFirst also notes that, in the ITCM footprint, a conservative rating philosophy was applied to secondary equipment. Specifically, ITCM rated secondary equipment at a maximum of five amps or the nameplate rating, whichever was lower. Also through this work, ITC Holdings determined that, in the Michigan operating companies, relay thermal limits were not historically calculated for transformers. The previous Rating Methodology for relays did not consider the need to calculate relay thermal limits on transformers and only addressed transmission lines. CTs on bulk power transformers in Michigan were historically included in the rating of the bulk power transformers, but not explicitly identified on Facility Rating sheets because it was assumed that the relay thermal limits were included in the bulk power transformer ratings. In light of these findings, ITC Holdings committed to review all 254 substations across its entire footprint. ITC Holdings employed a risk-based strategy in planning this work in order to minimize risk while the work is completed. Specifically, ITC Holdings prioritized breaker and half and ring bus configurations because there was a higher likelihood that devices in these circuits were not properly rated, especially when open breaker ratings were considered. ITC Holdings was able to narrow down the list of 254 substations and begin with those which have open breaker configurations. Moreover, as it proceeds through this review, ITC Holdings also approves any identified rating changes the same day, and enters them into its transmission management system within two business days. In total, ITC Holdings projected that this work would take approximately three years to complete, establishing an expected end date of late 2021. ITC Holdings has provided ReliabilityFirst with periodic updates on the progress of this work, and so far has been completing the work on schedule. As of August 2020, ITC Holdings has completed reviews of 184 out of the 254 total substations (i.e., 72%). During the course of this extent of condition, ITC Holdings has been reducing the thermal limit at approximately seven percent of facilities (i.e., 55 out of 813 facilities reviewed). The percentage change that ITC Holdings was required to make to these facilities ranges from 1-67% lower. The ITC Holdings group responsible for performing this extent of condition has been coordinating its review with ITC Holdings’ planning department. The root cause of this matter was ITC Holdings’ omitting to properly consider relay thermal limits in its Facility Rating Methodology. ITC incorrectly assumed that this information was being captured in its methodology, when, in fact, it was not. This root cause involves the management practice of asset and configuration management, which includes defining asset and configuration item attributes. The violation began on June 18, 2007, the date ITC Holdings was required to comply with FAC-008-1 R1. The violation is scheduled to end by December 31, 2021, the date ITC Holdings committed to complete its extent of condition review. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by not having accurate Facility Ratings is that the entity may operate equipment above its maximum ratings without the operators being aware, potentially causing equipment degradation and failure. Operating below the correct rating in emergencies can also cause undue load shedding and result in incorrect post contingency planning. The risk is not minimal in this case because the entity has had to lower Facility Ratings at approximately seven percent of its facilities with an average percentage decrease of 18 percent. The risk is not serious or substantial in this case based on the following factors. First, in the last five years, the entity has never exceeded the corrected Facility Ratings at any of the Facilities with decreased ratings. Second, in the last five years, the entity has never operated above 90 percent of the corrected Facility Ratings at those locations. Third, the entity self-identified this issue through a regularly-occurring, detailed review of its Facility Ratings Methodology. No harm is known to have occurred. | To mitigate this noncompliance, the entity has: 1) reviewed ITCM for delta configured secondary circuits and updated relay thermal limits in Facility Ratings Database and published new ratings; 2) updated Facility Ratings Methodology to include all Facilities including Transformers and the impacts of delta connected CTs secondary circuit; 3) calculated and published, if appropriate, relay thermal and overall facility limits on first 1/3 Transformers; 4) calculated and published if appropriate relay thermal and overall facility limits on second 1/3 Transformers; 5) calculated and published if appropriate relay thermal and overall facility limits on third 1/3 Transformers; 6) reviewed, corrected and published if appropriate relay thermal and overall facility limits for facilities at 42 substations; 7) reviewed, corrected and published if appropriate relay thermal and overall facility limits for facilities at 40 substations; 8) reviewed, analyzed and determined if 10% threshold has been exceeded for ITCT, METC, ITCGP and ITCI group; and 9) reviewed, analyzed and determined if 10% threshold has been exceeded for ITCM. ReliabilityFirst has verified the completion of all mitigation activity in steps 1-9 above. Additionally, ITC Holdings committed to complete an extent of condition review by the end of 2021 that will include all 254 substations and correct any incorrect Facility Ratings. | ReliabilityFirst considered ITC Holdings' compliance history with FAC-008-1 R1 (subsequently determined to have arisen under FAC-009-1 R1) in determining the penalty. ReliabilityFirst considered ITC Holdings' FAC-009-1 R1 compliance history to be an aggravating factor in the penalty determination. ITC Holdings has been highly cooperative throughout the entire enforcement process. Following the self-report of the violation, ITC Holdings met with the Regions on a regular basis to discuss progress on mitigation, the effectiveness of its extent of condition review, reliability, and other related activities. Throughout the enforcement process, ITC Holdings voluntarily provided the Regions with an abundance of information regarding the violation in a manner that was detailed, well-organized and timely. ITC Holdings has been transparent with the Regions regarding the violation and ITC Holdings’ processes and systems, and this insight has allowed the Regions to better analyze the violation and assist ITC Holdings with resolving the same. ITC Holdings’ level of cooperation throughout the enforcement process has been exemplary and the Regions awarded mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. Effective oversight of the reliability of the bulk power system depends on robust and timely self-reporting by Registered Entities. METC self-reported the violation and the issue was identified prior to the occurrence of any harm. The Regions considered that ITC Holdings initially discovered the ITC Holdings violation through a Self-Report and applied some mitigating credit. Under coordinated oversight, METC’s penalty will be divided among the Regional Entities as follows. ITC Holdings shall pay $125,000 to ReliabilityFirst and ReliabilityFirst shall divide that penalty amount in two parts based on the relative net energy for load (“NEL”) for each Region and shall distribute NEL-based proportional allocation to MRO. Of the total penalty remitted, ReliabilityFirst shall distribute $41,250 to MRO.