## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2021-04-29 | NOC-2710 | Western Electricity Coordinating Council (WECC) | Valley Electric Association, Inc. (VEA) | NCR05447 | TO | Settlement Agreement | Admits | 50000 | WECC2019021035 | FAC-008-3 | R6. | Moderate | Medium | High | Compliance Audit | 2019-01-31 | 2013-01-01 | Present | 2021-05-01 | TBD | During a Compliance Audit conducted January 21, 2019 through January 31, 2019, WECC determined VEA, as a Transmission Owner, had a potential noncompliance with FAC-008-3 R6. Specifically, seven of VEA’s 13 138 transmission Facilities were sampled for a detailed review. VEA provided the requested Facility Ratings database spreadsheet. During their review, WECC Auditors found discrepancies across the sampled transmission line Facilities. One of the 138kV transmission lines had three different Facility Ratings, which included the Facility Rating from VEA’s original database spreadsheet (196 MVA), one Facility Rating from a data request (143 MVA), and one Facility Rating from the WECC base case (191 MVA). VEA verified that the element causing the discrepancy at one switching station was owned by Department of Energy (DOE) and DOE had released a new rating for the switch, but the ratings from DOE engineering drawings were not communicated internally at VEA or used to update the Facility Rating. In addition, several circuit breakers and disconnect switches were missing from the database that were on the one-line diagrams, and elements that were in the database were not on the one-line diagrams. As well, conductor jumper ratings were not included in the database for one substation. Bus work was not included for two substations but were added to the database during the audit. VEA provided a revised database during the audit with the noted corrections herein, however the revised database was compared to the one-line diagrams dated November 20, 2018 and CTs were missing from the revised database. VEA later provided the CTs for each circuit breaker in subsequent data requests. The root cause of the violation was attributed to an incomplete understanding of the Standard as well of a lack of formal written and verbal internal procedures, communication, training and coordination between internal departments. This violation began on January 1, 2013, when the Standard became mandatory and enforceable, and will end on May 1, 2021, when mitigation is complete. | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In this instance, VEA failed to have Facility Ratings for its nine solely and three jointly owned Facilities that were consistent with the associated Facility Ratings Methodology (FRM), for determining its Facility Ratings, as required by FAC-008-3 R6. VEA operated 191 miles of 138 kV transmission lines and 164 miles of 230 kV transmission lines mainly to serve VEA’s 130 MW load. VEA owned the 138 kV transmission lines and another Transmission Owner (TO) owned the 230 kV transmission lines. VEA had three jointly owned Facilities, one with an entity at 230 kV and two with an entity at 138 kV and 230 kV. Such failure could have resulted in operating the transmission Facilities above normal, emergency or load-shed System Operating Limits (SOLs), potentially resulting in permanent or premature damage to the equipment if SOLs were exceeded. VEA did not implement effective detective or preventative controls. However, as compensation, VEA’s FRM adhered to the requirements of the Standard, including coordination with its joint Facility owners, thus reducing the risk to the BPS. In addition, VEA’s 130MW of load would not have a significant impact on the BPS, thus reducing the risk. VEA’s mitigation is not yet complete. VEA will complete the following measures to reduce failure points and reduce the risk to the BPS, based on recommendation by WECC Auditors: 1) schedule weekly meetings with its Compliance Team and its Engineering and Operations staff. During these meetings, VEA reviews planned system changes to identify potential changes to Facility Ratings; 2) update the Facility Ratings spreadsheet timely during mitigation upon changes to equipment or infrastructure that could change Facility Ratings or evidence of ratings; 3) establish a schedule to coordinate with joint owners on Facility and equipment ratings to ensure that the Facility ratings for jointly owned Facilities are reviewed on a regular schedule; and 4) update its FRM to ensure that it accurately generates the equipment and Facility Ratings; this includes clarifying confusing language and spelling out specific steps that may otherwise have been assumed. | To mitigate this violation, VEA has performed the following actions: 1) gathered evidence for equipment rating sources; 2) requested equipment ratings from joint owners; 3) completed updated Facility Ratings spreadsheet for VEA Facilities; and 4) confirm VEA equipment ratings and supporting evidence. To remediate and mitigate this violation, VEA will: 1) identify and resolve inconsistencies with joint owners; 2) update its FRM, as necessary; 3) coordinate final Facility Ratings with joint owners; 4) update VEA documentation with Facility Ratings; 5) organize and store all evidence; 6) schedule annual review of FRM and Facility Ratings spreadsheet; and 7) develop Facility Ratings training materials and train VEA engineering. | WECC reviewed VEA's Internal Compliance Program (ICP) and considered it to be a neutral factor in the penalty determination. Although VEA does have a documented ICP, WECC determined that it was not effective in preventing or detecting this violation. WECC provided credit for VEA's cooperation and for agreeing to settle and admit to the violation. WECC determined that VEA's compliance history should not serve as a basis for aggravating the penalty because the previous violation was a result of the NERC Standards becoming mandatory and enforceable and did not indicate a systemic issue or programmatic failure.
2021-04-29 | NOC-2711 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | GOP | Settlement Agreement | Neither Admits nor Denies | No Penalty | SERC2019021816 | PRC-001-1 | R2; R2.1 | Moderate | Medium | Severe | Self-Report | 2019-07-12 | 2012-10-19 | 2019-04-17 | 2021-03-31 | TBD | On July 12, 2019, TVA submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of PRC-001-1 R2.1. TVA failed to notify its Transmission Operator (TOP) and Host Balancing Authority (BA) of a relay failure for a single 500 kV relay. SERC determined this violation spanned to TOP-003-3 R5. On April 15, 2019 while troubleshooting a ground at the Brownsville Combustion Turbine (CT) plant, TVA personnel identified labels on the 500 KV main transformer multifunction relay that said “Failed”. These “Failed” labels were dated 2012 and 2017. TVA analyzed the October 19, 2012 and April 20, 2017 preventative maintenance (PM) information and identified the relay data indicated an A phase sensing failure. On April 17, 2019 , TVA made notifications to the TOP and BA. During both the October 19, 2012 and April 20, 2017 calibration and functional testing of the 500 kV main transformer multifunction relay at the Brownsville CT plant, the relay calibration identified an A phase sensing failure. TVA personnel flagged the relay for repair or replacement in both instances. On both occasions, TVA failed to repair or replace the relay. PRC-001-1 R2.1 was the enforceable Standard at the time of the October 19, 2012 occurrence. PRC-001-1 R2.1 requires the GOP to notify the TOP and BA if a protective relay or equipment failure reduces system reliability, and take corrective action as soon as possible. TOP-003-3 R5 was the enforceable Standard at the time of the April 20, 2017 occurrence. TOP-003-3 R5 requires the GOP to satisfy the obligations of the documented specifications provided by the TOP and BA as specified in TOP-003-3 R2, R3, and R4. The specification provided by the TOP required TVA to notify the TOP of current Protection System and Remedial Action Scheme status or degradation that impact System reliability in real-time in a phone call and followed by a submittal to the Consolidated Outage Portal. Since TVA did not notify the TOP of the degradation which would impact System reliability in real-time, the TOP, in turn, was unable to pass the information along to the BA, as required by the specification provided by the BA. The 500 kV main transformer multifunction relay at the Brownsville CT plant is a redundant relay and is associated with Brownsville CT 3 and Brownsville CT 4, each a 135 MW generator. The TVA TOP does not allow TVA to run these units without redundant relay protection. However, TVA failed to meet its TOP’s redundant relay protection requirement in this case. Brownsville CT 3 had a 2018 annual capacity factor of 7% and Brownsville CT 4 had a 2018 annual capacity factor of 5%. The cause of this violation was management oversight. TVA management failed to implement a documented process and internal controls to ensure the PM reports were adequately reviewed and required action was taken. The relay failure documented on the PM reports should have triggered TVA to notify its TOP and Host BA, and then either repair or replace the relay. In both 2012 and 2017, the relay failure was documented in the PM reports. For the 2012 package, the note was on page 131 of a 364 page document. For the 2017 package, the note was on page 249 of a 505 page document. TVA personnel overlooked the documented failed relay in both the 2012 report and the 2017 report. TVA did not have a documented procedure for this process at the time of the violation . TVA could not provide a response to explain how this failure could occur on the same relay, on two different occasions. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, TVA’s failure to notify the TOP and BA, and take corrective action to repair or replace a faulty relay could result in unplanned loss of generation, transmission, or load. TVA operated the Brownsville CT 3 and Brownsville CT 4 units without the TOP required redundant relay on the 500 kV main transformer from at least October 19, 2012 until April 17, 2019, and did not notify the TOP and BA until April 17, 2019. On two occasions, TVA failed to take action on the same defective relay which raises concerns as to the effectiveness of TVA’s review of maintenance and testing records. In addition, TVA completed an extent of condition review - for 243 of TVA’s 243 generating units (100%), TVA reviewed, verified, and documented the listed devices and either reported to SERC that such devices are in service with no known deficiencies that would prevent them from performing their intended function, or reported to SERC on deficiencies that were found and the status of work orders for reconciling the deficiencies. There were no significant deficiencies. | To mitigate this noncompliance, the entity has performed the following actions: 1) notified its TOP and BA of the relay failure affecting reliability; 2) replaced the failed relay; 3) updated its PRC-005 compliance procedure. TVA updated its PRC-005 compliance procedure to give the field services organization the exclusive action to be responsible for execution and review of PRC-005 Relay PM; 4) updated its evidence checklist to include a deficiency summary. This evidence checklist is a coversheet for persons performing Relay PMs to check that all requirements for the PM are met. TVA added a box to the checklist requesting that "For any unsatisfactory results or unresolved maintenance issues, document a brief description and the follow-up work order number(s) below:" TVA implemented this checklist and created a formal procedure for it; 5) updated its site notification matrix to include a notification to the reliability analysis group on a relay failure. The reliability analysis group performs relay analysis for the TVA TOP. Site notification matrices are internal documents that direct who to contact for particular events. For relay failures that compromise reliability, TVA added a telephone number for reliability analysis and the Transmission Operator and direction for the plants to call reliability analysis; 6) provided training on revised procedures; and 7) performed an extent-of-condition review to ensure there are no other instances of unresolved PM deficiencies and reporting findings to SERC. TVA used the lists of devices verified under its on-going PRC-005 verification efforts (SERC2015014914) to complete this extent-of-condition review to ensure all PRC-005 relays are correctly identified. For 243 of TVA’s 243 generating units (100%), TVA reviewed, verified, and documented the listed devices and either reported to SERC that such devices are in service with no known deficiencies that would prevent them from performing their intended function, or reported to SERC on deficiencies that were found and the status of work orders for reconciling the deficiencies. | SERC reviewed TVA's internal compliance program and considered it to be a neutral factor in determining the disposition. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as SERC, could not impose monetary penalties against federal governmental entities such as SWPA. TVA is a federal governmental entity, and SERC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, SERC has assessed no monetary penalty for this violation. SERC considered TVA’s compliance history and determined there were no relevant instances of noncompliance. SERC determined that sending a message via a settlement agreement is appropriate given the long duration of this violation and TVA’s failure on two occasions to take action on the same defective relay which raises concerns as to the effectiveness of TVA’s review of maintenance and testing records.