## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2021-09-30 | NOC-2725 | ReliabilityFirst Corporation (RF) | Covanta Delaware | NCR00743 | GO | Settlement Agreement | Admits | 0 | RFC2019021205 | VAR-002-4.1 | R2 | Moderate | Medium | Severe | Compliance Audit | 2019-02-27 | 2017-09-26 | 2020-10-01 | 2020-10-01 | TBD | On February 27, 2019, ReliabilityFirst identified as part of a Compliance Audit that the entity, as a Generator Owner, was in violation of VAR-002-4.1 R2. The Compliance Audit was conducted from January 17, 2019, through February 19, 2019. The entity was unable to produce any evidence that the generator was consistently maintained within the voltage schedule provided to them by the applicable Transmission Operator (TOP). For the duration of the noncompliance, the facility lacked the ability to store such evidence using existing facility historians and data recorders and therefore could not demonstrate that the TOP-supplied voltage schedule had been maintained. The entity provides that based on their knowledge, and limited documentation, the entity did not receive notifications from their Transmission Planner (TP) or TOP of any voltage schedule deviation. Starting in August of 2016, the entity’s real-time information and emergency notifications were monitored by a contractor that served as an intermediary between the entity and PJM (TOP). If PJM directed any action, the contractor would notify the facility of the directed action via phone and email. The entity provided that for the duration of the noncompliance, no direction related to voltage schedule deviations was received. The entity indicated that an internal procedure in place for the duration of the noncompliance directed the facility to maintain the TOP-supplied voltage schedule and record all applicable operator communications, including those with the TP and TOP, within the control room log book. The entity performed a sample review of its log books for the duration of the noncompliance comparing them against the PJM emergency procedure systems overall directed alerts for relevant systems. For the duration of the violation, for the TP region in which the entity resides, there were no low voltage alerts, voltage reduction actions, or voltage reduction alerts. However, there were a number of high system voltage actions in the TP region. The entity then sampled 12 high system voltage actions a year for the duration against their internal log books, and found that for all the actions reviewed, there were no communications with the facility from the TOP, TP, or contract intermediary including regarding voltage schedule issues or deviations. The root cause of this noncompliance was that the entity lacked the procedures and data capture capabilities to assure that the generator documented and retained all deviation information, and notified the TOP as required. This noncompliance involves the management practice of reliability quality management. Reliability quality management is involved because the entity did not develop necessary procedural documents or a programmatic approach to compliance with VAR-002-4.1 R2. The violation began on September 26, 2017, the date the entity was required to comply with VAR-002-4.1 R2. The violation ended October 1, 2020, the date the entity completed its Mitigation Plan. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that the failure to identify and notify the TOP of voltage deviations places the TOP in an informational disadvantage and adversely impacts situational awareness, potentially resulting in harm to the BPS. Additionally, failing to identify and manage voltage deviations can result in harm to equipment. The risk posed here is not minimal because of the duration of approximately three years. The risk here is not serious because the facility’s capacity is just 90 MW, and plays a limited role in voltage regulation and support relative to the PJM generator system. ReliabilityFirst notes that while the entity is unable to provide necessary data, there is significant circumstantial evidence that points to there being no significant, alertable voltage schedule deviations for the duration (i.e., the entity did not have evidence of receiving notification from its contract intermediary notifying them of a voltage directive, and the entity’s sampled log book review based on TP region high system voltage events). Additionally, for the duration of the violation, for the TP region in which the entity resides, there were no low voltage alerts, voltage reduction actions, or voltage reduction alerts. | To mitigate this violation, the entity has performed the following actions: 1) performed a root cause study to determine the source of the noncompliance; 2) performed an extent of condition analysis to identify the full scope of the noncompliance; 3) identified activities to mitigate the noncompliance and implement steps to prevent recurrence; 4) replaced the existing AVR (Automatic Voltage Regulator) system to provide enhanced operational controls, and data capture capabilities. Additionally, the entity configured the recording of generator and system parameters to create evidence of voltage support consistent with the voltage schedule provided by the TOP; 5) updated internal procedures to improve operational guidance on voltage control and schedules; and 6) performed training for relevant personnel on the changes made to existing voltage control procedures. | ReliabilityFirst reviewed Covanta Delaware’s internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. This violation was disposed of as a $0 SNOP instead of an FFT for the following reasons. First, the duration of approximately three years was significant, and the issue was identified via Compliance Audit, suggesting that the violation would likely have persisted for an even longer duration. Second, the evidence related to the existence/non-existence of potential deviations, while strong, was circumstantial.
2021-09-30 | NOC-2731 | Texas Reliability Entity, Inc. (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | DP, TO, TOP | Settlement Agreement | Neither Admits nor Denies | 0 | TRE2019022038 | IRO-010-2 | R3 | Minimal | Medium | Severe | Compliance Audit | 6/10/2019 - 8/8/2019 | 2020-01-01 | 2020-03-31 | 1/13/2023 (Expected Completion Date) | TBD | Texas RE determined Oncor was noncompliant with IRO-010-2 R3. Specifically, Oncor failed to satisfy the obligations of its Reliability Coordinator’s (RC’s) documented data specification. The RC requires that 92% of telemetry deemed important by the RC achieve a quarterly reliability of 90%. Texas RE determined that Oncor failed to meet the telemetry reliability criteria for important telemetry for the fourth quarter of 2019, with 89% of important telemetry achieving the RC's quarterly reliability requirements. Oncor ended this instance of noncompliance by achieving the reliability criteria for important telemetry for the first quarter of 2020. The root cause of this noncompliance is Oncor’s use of analog communications technology, which is not adequately supported by Oncor’s telecommunications providers, to provide connectivity to its telemetry devices. This noncompliance started on January 1, 2020, which is the day after the end of the fourth quarter of 2019, and ended on March 31, 2020, which is the last day of the first quarter of 2020. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk of this noncompliance is that Oncor’s RC had decreased situational awareness due to the incorrect and missing telemetry data and a reduction in the capability of the RC’s state estimator to handle the loss of other telemetry points. This is compounded by Oncor’s status as the largest single provider of important telemetry points to its RC, providing 28% of the important telemetry points received by the RC. The risk is lessened by several factors. First, Oncor still had 89% of important telemetry achieve the RC’s quarterly reliability requirements, relatively close to the requirement that 92% of all telemetry achieve the RC’s quarterly reliability requirements. Second, given its role in the ERCOT Interconnection, Oncor communicates with RC personnel on a daily basis. Had a significant issue occurred that impacted overall system operations, Oncor and RC personnel could have quickly coordinated a response. Third, RC operator logs during the duration of the noncompliance did not reveal any evidence that the telemetry failures impacted the RC’s Network Security Analysis or caused invalid State Estimator solutions. Fourth, Oncor’s work with its current communications provider to maintain its existing communications links as much as possible while they are awaiting replacement also reduces the risk, as Oncor maintains a SCADA ticketing system for logging telemetry issues and tracking its coordination with its current communications providers while it works to ensure issues with its existing communications links are addressed in a timely fashion. Finally, the risk is further reduced by Oncor’s internal process for reviewing and addressing the monthly telemetry statistics report from its RC, along with Oncor’s automated tool that alerts Oncor personnel if any important telemetry point has an abnormal quality code for 30 minutes, indicating the presence of internal controls. No harm is known to have occurred. | To mitigate this noncompliance, Oncor has or will perform the following actions: 1) ended the noncompliance by achieving the reliability criteria required by its RC; and 2) prevent reoccurrence by replacing its analog copper-based communications technology, which was provided through several different telecommunications providers, with an updated, more reliable solution that uses communication technology based primarily on Oncor-owned fiber, microwave, and radio frequency-based data links as well as cellular data links, which rely on outside service providers, in instances that are currently out of range of those private solutions. | Texas RE reviewed Oncor’s internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered Oncor’s IRO-010-2 R3 compliance history in determining the disposition track. Texas RE determined that Oncor’s compliance history should not serve as a basis for aggravating the risk due to the differing nature and root cause of the instant noncompliance compared to the compliance history. NERC Violation ID TRE2016015568 was the only potentially relevant compliance history that was located. TRE2016015568 involved a failure to provide accurate information to the RC, and had a root cause of insufficient processes for ensuring the Oncor group tasked with providing that information to Oncor’s RC adequately tracked and verified changes to that information. This is in contrast to the instant noncompliance of failure to maintain adequately reliable telemetry links with the RC due to a reliance on analog communications technology. Although the violation resolved by this agreement involves a minimal risk issue that would otherwise be eligible for a streamlined disposition, Texas RE determined that such streamlined treatment was not appropriate because the expected completion date for the mitigation activities Oncor is undertaking to prevent reoccurrence of this violation will be more than 12 months after the posting of the disposition.