## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2021-10-28 | NOC-2734 | SERC Reliability Corporation (SERC) | Performance Materials NA, Inc. (PerfMat) | NCR09008 | GOP | Settlement Agreement | Neither Admits nor Denies | $0 (for SERC2020024299 and SERC2021024528) | SERC2020024299 | VAR-002-1 | R1. | Minimal | Medium | Severe | Self-Report | 2020-12-10 | 2007-08-02 | 2019-10-28 | 2020-01-10 | TBD | PerfMat notified SERC that it was noncompliant with VAR-002-4.1 R1. PerfMat failed to operate one generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator (TOP). On April 1, 2019, PerfMat became the new owner and operator of a 420 MW Cogeneration Qualifying Facility (QF) that has two gas turbine units and one steam turbine unit (STG), connected at 138 kV. These units primarily provide power and steam to the site, but PerfMat also sells excess generation to the electric power market. When PerfMat acquired the QF, it assumed the registration date and the NCR number of the QF’s previous owners. On October 11, 2019, PerfMat’s testing contractor performed MOD-026 testing and discovered that the STG was operating with the Automatic Voltage Regulator (AVR) in power factor mode. Upon discovery, PerfMat determined that plant personnel knew it was operating with the AVR in power factor mode, but incorrectly believed it was a form of automatic voltage control and met the requirements of VAR-002-4.1. Additionally, PerfMat confirmed with the TOP that it had not given the previous owner any exemptions to operate the STG in power factor mode. On October 28, 2019, during an outage, PerfMat placed the STG’s AVR in automatic voltage control mode. PerfMat reviewed its two gas turbine units and verified that they were operating with the AVR in automatic voltage control mode. The cause of this noncompliance was a deficient process. PerfMat’s process did not detail the difference between automatic voltage control mode and power factor mode. As a result, plant staff erroneously believed that operating the AVR in power factor mode met the requirements of automatic voltage control. When the testing contractor called that into question, PerfMat immediately sought guidance and confirmed power factor mode does not meet the requirement of VAR-002. This noncompliance started on August 2, 2007, when the STG began operating in power factor mode and was required to comply with VAR-002 R1, and ended on October 28, 2019, when PerfMat operated the STG with the AVR in automatic voltage control mode. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PerfMat’s failure to operate the AVR in automatic voltage control mode could have resulted in the TOP making incorrect assumptions regarding its control of reactive capability and taking actions that could adversely affect the reliability of the BPS. However, PerfMat was still controlling voltage with the AVR, even though it was in a different control mode. Additionally, the primary purpose of PerfMat’s generators is to produce steam for a steam host. The STG has a nameplate rating of 145 MW, but is typically operated at approximately 90 MW in order to support the steam demands of its chemical process operation. No harm is known to have occurred. | To mitigate this violation, PerfMat has performed the following actions: 1) updated the process in its Management of Change (MOC) document and all associated VAR procedures to reinforce R1, R2, and R3’s requirement to operate in automatic voltage control mode and provide additional guidance on how to operate within the required parameters; 2) trained operational staff on the updated process and documents including training on the difference between power factor and automatic voltage control mode; 3) completed a review of its policies and procedures with regards to the NERC standard compliance program to ensure there were no other gaps; 4) removed the ability to change the AVR control mode on the STG by removing the option on the control system’s HMI for switching to power factor mode so that it is no longer an option and automatic voltage control is the only mode permitted; and 5) completed the MOC notifying all plant personnel of the change. | SERC reviewed PerfMat’s internal compliance program and considered it to be a neutral factor in the disposition method. SERC considered PerfMat’s compliance history and determined there were no relevant instances of noncompliance. This violation is being disposed of as a $0 Spreadsheet Notice of Penalty. Even though PerfMat, as a new owner, assumed the registration of the facility and is responsible for its compliance liability, SERC acknowledges that these violations were not discovered and reported until PerfMat acquired the facility. SERC encourages PerfMat’s commitment to compliance and its assessment of the facility’s legacy compliance program by reviewing its inherited processes and reporting historical noncompliances. Additionally, despite PerfMat being a small entity and the long duration, the risk remained minimal.
2021-10-28 | NOC-2734 | SERC Reliability Corporation (SERC) | Performance Materials NA, Inc. (PerfMat) | NCR09008 | GOP | Settlement Agreement | Neither Admits nor Denies | $0 (for SERC2020024299 and SERC2021024528) | SERC2021024528 | VAR-002-1 | R2. | Moderate | Medium | Severe | Self-Report | 2021-02-09 | 2007-08-02 | 2020-12-06 | 2021-04-29 | TBD | PerfMat notified SERC that it was noncompliant with VAR-002-4.1 R2. PerfMat failed to maintain its Transmission Operator (TOP) supplied voltage schedule and notification requirements. SERC later determined that this noncompliance began under VAR-002-1 and continued to VAR-004-4.1. On April 1, 2019, PerfMat became the new owner and operator of a 420 MW Cogeneration Qualifying Facility (QF) that has two gas turbine units and one steam turbine unit (STG). While these units primarily provide power and steam to the site, PerfMat also sells excess generation to the electric power market. When PerfMat acquired the QF, it assumed the June 28, 2007, registration date and NCR number of the generator’s previous owners. On January 22, 2021, while responding to a request for information for a related noncompliance, PerfMat determined that it failed to meet the requirements of the TOP’s voltage schedule 53 times between April 9, 2019, and December 6, 2020. The TOP’s issued voltage schedule required PerfMat to operate within a band of 138 kV +2 kV to -2 kV and required PerfMat to notify them within 30 minutes of a failure to meet the voltage schedule. The maximum under voltage excursion was 133.437 kV for 3 hours, and the maximum upper limit exceedance was 140.698 kV for 11 hours. Additionally, the longest under voltage excursion was 134.254 kV for 48 hours. PerfMat’s initial review included all voltage data beginning on the date it acquired the facility, through February 25, 2021. Due to the limitations of obtaining data from the prior owners, PerfMat was unable to perform a more extensive extent-of-condition review for actions prior to its ownership. However, SERC believes that the evidence PerfMat presented is indicative of the historical actions of the facility’s previous owners and operators. The cause of this violation was a deficient procedure. Specifically, PerfMat’s procedure failed to contain information requiring specific adherence to the TOP’s voltage schedule and notification requirements. Its prior procedure only stated that the site needed to maintain a positive flow of VARS to the TOP at all times and did not reference the TOP’s voltage schedule or notification requirement. This violation started on August 2, 2007, when the Standard became mandatory and enforceable, and ended on December 6, 2020, when PerfMat met its voltage schedule. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PerfMat’s failure to maintain the assigned voltage schedule in 53 instances from April 1, 2019, through February 25, 2021, could have resulted in equipment damage or insufficient reactive resource for reliable system operation. However, PerfMat is QF connected at 138 kV in the Midcontinent Independent System Operator Balancing Authority area. Thus, PerfMat would likely have a nominal impact to the grid when operating outside of the assigned voltage schedule. No harm is known to have occurred. | To mitigate this violation, PerfMat has performed the following activities: 1) updated its operating procedures and annual training module to address voltage schedule adherence requirement; 2) added voltage limit alarms; and 3) trained operators on the required response to meet the TOP’s voltage schedule requirements including its new procedure and alarms. | SERC reviewed PerfMat’s internal compliance program and considered it to be a neutral factor in the disposition method. SERC considered PerfMat’s compliance history and determined there were no relevant instances of noncompliance. This violation is being disposed of as a $0 Spreadsheet Notice of Penalty. Even though PerfMat, as a new owner, assumed the registration of the facility and is responsible for its compliance liability, SERC acknowledges that these violations were not discovered and reported until PerfMat acquired the facility. SERC encourages PerfMat’s commitment to compliance and its assessment of the facility’s legacy compliance program by reviewing its inherited processes and reporting historical noncompliances. Additionally, despite PerfMat being a small entity and the long duration, the risk remained moderate.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | PA, TP | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019022408 | TPL-001-4 | R2 | Minimal | High | Severe | Self-Report | 2019-10-19 | 2/28/2018 | 6/24/2020 | 6/24/2020 | 9/17/2020 | BHP notified WECC that it was noncompliant with TPL-001-4 R2. Specifically, the 2017 and 2018 Transmission Coordinating Planning Committee (TCPC) studies, previously thought to be complete, did not include all the requirements of its Planning Assessment, as required by the Standard. BHP’s practice had previously been to complete the Planning Assessment once its external Sub Regional Planning Group had finished compiling, verifying and sending the needed dynamic data for the neighboring entities and base cases in December of each year. However, BHP’s process that fed into the creation of the annual Planning Assessment was only partially completed by previous employees in 2017 who left the company and was completed late for the 2018 TCPC studies. The employees responsible for that part of the process vacated their positions before completing the study work in 2017 and writing the corresponding Planning Assessments. The root cause was attributed to BHP not implementing adequate controls to track the progress of the annual Planning Assessments and a misunderstanding of associated timing requirements. BHP had employee turnover that resulted in not having the required Subject Matter Experts (SMEs) to complete, nor track the progress of the Planning Assessments. The 2017, 2018, and 2019 annual Planning Assessments were due February 2018, 2019, and 2020, respectively. Though incomplete, BHP completed its 2017 Planning Assessment on November 4, 2019 and its 2018 Planning Assessment on December 17, 2019. The noncompliance began on February 28, 2018, when BHP’s 2017 Planning Assessment should have been completed, and ended on June 24, 2020, when BHP completed its 2019 Planning Assessment. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BHP failed to prepare an annual Planning Assessment timely, for its portion of the BES in 2017, 2018, and 2019, as required by TPL-001-4 R2. Such failures could have resulted in BHP’s inability to identify weaknesses in its system and an inability to implement action plans for identified system deficiencies or make needed system improvements. Had an event occurred on BHP’s system, it could have resulted in minor overloading on its local 115kV network or 230kV transmission line overloads. However, as compensation, for one of BHP’s local 115kV networks, if an event were to occur, it would not have adversely affected the BPS. For BHP’s 230kV transmission lines, BHP had a Remedial Action Scheme in place to curtail transfers across the tie for specified contingency events, thereby mitigating the potential overloads. As well, recent system upgrades had mitigated local voltage concerns and transmission facility additions and rating increases have mitigated local thermal loading issues. In addition, the possibility of BHP islanding its system from the main grid would not have had a significant impact to the BPS. Thereby, limiting the potential harm within BHP’s system, reducing the risk to the BPS. | To mitigate this violation, BHP has or will perform the following actions: 1) finalized its Planning Assessments for 2017 and 2018 with available study work and completed its Planning Assessments for 2019; 2) created a TPL-001-4 process checklist that is updated throughout the process of completing the study. These review checkpoints on the TPL-001-4 process checklist prompt the TP to send an email update to the supervisor to ensure that the checklist is being completed and it will provide the supervisor an opportunity to review the major tasks. In addition, the TPL-001-4 process checklist is updated throughout each annual study process to ensure each requirement of the Standard is being addressed. The TPL-001-4 process checklist provides a structured format for assessing TPL-001-4 deliverables and provides guidance and documentation for new employee training; and 3) acquired in-house technical expertise by hiring new qualified employees to complete Planning Assessments required by the Standard; and within its TPL-001-4 process checklist implemented a contingency plan to ensure Planning Assessments are completed timely; specifically if base case information is not available from its sub-regional planning group on a timely basis BHP will use the most recent valid and available studies to ensure timely completion and the forward looking nature of its Planning Assessments. | BHP’s issues with its planning assessments were considered systemic due to the number of Requirements violated, multiple instances, duration and incorrect process for completing the Planning Assessments. Further, the systemic nature of BHP’s issues with TPL-001 also warranted alleging the violations and assessing a penalty. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | PA, TP | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019022409 | TPL-001-4 | R3, R3.2, R3.4. R3.5 | Minimal | Medium | Severe | Self-Report | 2019-10-19 | 2018-02-28 | 2020-06-24 | 2020-06-24 | 2020-09-17 | BHP notified WECC that it was noncompliant with TPL-001-4 R3. Specifically, the 2017 and 2018 Transmission Coordinating Planning Committee (TCPC) studies, previously thought to be complete, did not include all the requirements of the steady state portion of its Planning Assessment, as required by the Standard. BHP’s TCPC studies for 2017 did not include the studies that assess the impact of the extreme events for the steady state portion of the Planning Assessment for one of the utilities that comprises its footprint, as required by TPL-001-4 R3.2. In addition, although BHP’s 2017 TCPC studies included a contingency list, the studies did not include a documented rationale for P0-P7 and extreme events that were expected to have more severe system impacts, as required by TPL-001-4 R3.4 and R3.5. BHP’s practice had previously been to complete the Planning Assessment once its Planning Group had finished compiling, verifying and sending the needed dynamic data for the neighboring entities and base cases in December of each year. However, BHP’s process that fed into the creation of the annual Planning Assessment was only partially completed by previous employees in 2017 who left the company and was completed late for 2018. The employees responsible for that part of the process vacated their positions before completing the study work in 2017 and writing the corresponding Planning Assessments. The root cause was attributed to BHP not implementing adequate controls to track the progress of the annual Planning Assessments and a misunderstanding of associated timing requirements. BHP had employee turnover that resulted in not having the required Subject Matter Experts (SMEs) to complete nor track the progress of the Planning Assessments. The 2017, 2018, and 2019 annual Planning Assessment were due February 2018, 2019, and 2020, respectively. Though incomplete, BHP completed its 2017 Planning Assessment on November 4, 2019 and its 2018 Planning Assessment on December 17, 2019. The noncompliance began on February 28, 2018, when BHP’s 2017 Planning Assessment should have been completed, and ended on June 24, 2020, when BHP completed its 2019 Planning Assessment. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, BHP failed to complete timely its steady state portion of the Planning Assessment for 2017, 2018 and 2019 by performing studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2, as required by TPL-001-4 R3. Such failures could have resulted in BHP’s inability to identify weaknesses in its system and an inability to implement action plans for identified system deficiencies or make needed system improvements. Had an event occurred on BHP’s system, it could have resulted in minor overloading on its local 115kV network or 230kV transmission line overloads. However, as compensation, for one of BHP’s local 115kV networks, if an event were to occur, it would not have adversely affected the BPS. For BHP’s 230kV transmission lines, BHP had a Remedial Action Scheme in place to curtail transfers across the tie for specified contingency events, thereby mitigating the potential overloads. As well, recent system upgrades had mitigated local voltage concerns and transmission facility additions and rating increases have mitigated local thermal loading issues. In addition, the possibility of BHP islanding its system from the main grid would not have had a significant impact to the BPS. Thereby limiting the potential harm within BHP’s system, reducing the risk to the BPS. | To mitigate this violation, BHP has or will perform the following actions: 1) finalized the steady state portion of the 2017 Planning Assessment by performing studies for the Near-Term and Long-Term Transmission Planning Horizons and for 2019 Planning Assessments to include all extreme events; 2) created a TPL-001-4 process checklist that is updated throughout the process of completing the study. These review checkpoints on the TPL-001-4 process checklist prompt the transmission planner to send an email update to the supervisor to ensure that the checklist is being completed and it will provide the supervisor an opportunity to review the major tasks. In addition, the TPL-001-4 process checklist will be updated throughout each annual study process to ensure each requirement of the Standard is being addressed. The process checklist provides a structured format for assessing TPL-001-4 deliverables and provides guidance and documentation for new employee training; and 3) acquired in-house technical expertise by hiring new qualified employees to complete Planning Assessments required by the Standard; and within its TPL-001-4 process checklist implemented a contingency plan to ensure Planning Assessments are completed timely; specifically if base case information is not available from its sub-regional planning group on a timely basis, BHP will use the most recent valid and available studies to ensure timely completion and the forward looking nature of its Planning Assessments. | BHP’s issues with its planning assessments were considered systemic due to the number of Requirements violated, multiple instances, duration and incorrect process for completing the Planning Assessments. Further, the systemic nature of BHP’s issues with TPL-001 also warranted alleging the violations and assessing a penalty. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | PA, TP | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019022410 | TPL-001-4 | R4, R4.2, R4.3, R4.3.1, R4.3.1.1, R4.3.1.2 | Minimal | Medium | Severe | Self-Report | 2019-10-19 | 2018-02-28 | 2020-06-24 | 2020-06-24 | 2020-07-22 | BHP notified WECC that it was noncompliant with TPL-001-4 R4. Specifically, the 2017 and 2018 Transmission Coordinating Planning Committee (TCPC) studies, previously thought to be complete, did not include all the requirements of the steady state portion of its Planning Assessment, as required by the Standard. As well, BHP did not complete its 2019 TCPC studies timely. Specifically, BHP did not include the impacts of high-speed reclosing or relay models that would trip generators when they surpass their voltage ride through capabilities for the 2017 and 2018 TCPC studies, as required by TPL-001-4 R4.3.1.1 and R4.3.1.2. Furthermore, the modeling details described in R4.3 were not included as required for BHP’s 2018 TCPC studies. BHP did not realize that portions of the 2018 TCPC studies did not have high speed reclosing nor the impact of subsequent tripping of generators where simulations showed generator bus voltages or high side of the generation step up (GSU) voltages were less than known or assumed generator steady state or ride through voltage limitations programmed into the study files when the reports were sent to third-party consultants. Consequently, BHP’s 2018 TCPC study did not include impacts of high-speed reclosing or relay models that would trip generators when they surpass their voltage ride through capabilities, as required by TPL-001-4 R4.3.1.1 and TPL-001-4 R4.3.1.2. BHP’s practice had previously been to complete the Planning Assessment once its Planning Group had finished compiling, verifying and sending the needed dynamic data for the neighboring entities and base cases in December of each year. However, BHP’s process that fed into the creation of the annual Planning Assessment was only partially completed by previous employees in 2017 who left the company and completed late in 2018. The employees responsible for that part of the process vacated their positions before completing the study work in 2017 and writing the corresponding Planning Assessments. The root cause was attributed to BHP not implementing adequate controls to track the progress of the annual Planning Assessments and a misunderstanding of associated timing requirements. BHP had employee turnover that resulted in not having the required Subject Matter Experts (SMEs) to complete nor track the progress of the Planning Assessments and TCPC studies. The 2017, 2018, and 2019 annual Planning Assessment were due February 2018, 2019, and 2020, respectively. Though incomplete, BHP completed its 2017 Planning Assessment on November 4, 2019 and its 2018 Planning Assessment on December 17, 2019. The noncompliance began on February 28, 2018, when BHP’s 2017 Planning Assessment should have been completed, and ended on June 24, 2020, when BHP completed its 2019 Planning Assessment timely. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, BHP failed to complete all the requirements of the Stability portion of its Planning Assessment in 2017, 2018 and 2019, as described in Requirement R2, Parts 2.4 and 2.5, BHP failed to perform the Contingency analyses listed in Table 1. The studies were not completed based on computer simulation models using data provided in Requirement R1, as required by TPL-001-4 R4. Such failures could have resulted in BHP’s inability to identify weaknesses in its system and an inability to implement action plans for identified system deficiencies or make needed system improvements. Had an event occurred on BHP’s system, it could have resulted in minor overloading on its local 115kV network or 230kV transmission line overloads. However, as compensation, for one of BHP’s local 115kV networks, if an event were to occur, it would not have adversely affected the BPS. For BHP’s 230kV transmission lines, BHP had a Remedial Action Scheme in place to curtail transfers across the tie for specified contingency events, thereby mitigating the potential overloads. As well, recent system upgrades had mitigated local voltage concerns and transmission facility additions and rating increases have mitigated local thermal loading issues. BHP completed certain portions of the Stability portion of its 2017 and 2018 TCPC studies. In addition, the possibility of BHP islanding its system from the main grid would not have had a significant impact to the BPS. The limiting the potential harm remained within BHP’s system, reducing the risk to the BPS. No harm is known to have occurred. | To mitigate this violation, BHP has or will perform the following actions: 1) completed all requirements of the Stability portion of its Planning Assessment for the annual 2019 studies; 2) created a TPL-001-4 process checklist that is updated throughout the process of completing the study. These review checkpoints on the TPL-001-4 checklist prompt the TP to send an email update to the supervisor to ensure that the checklist is being completed and it will provide the supervisor an opportunity to review the major tasks. In addition, process checklist will be updated throughout each annual study process to ensure each requirement of the Standard is being addressed. The TPL-001-4 process checklist provides a structured format for assessing TPL-001-4 deliverables and provides guidance and documentation for new employee training; 3) acquired in-house technical expertise by hiring new qualified employees to complete Planning Assessments required by the Standard; and within its TPL-001-4 process checklist implemented a contingency plan to ensure Planning Assessments are completed timely; specifically, if base case information is not available from its sub-regional planning group on a timely basis BHP will use the most recent valid and available studies to ensure timely completion and the forward-looking nature of its Planning Assessments. | BHP’s issues with its planning assessments were considered systemic due to the number of Requirements violated, multiple instances, duration and incorrect process for completing the Planning Assessments. Further, the systemic nature of BHP’s issues with TPL-001 also warranted alleging the violations and assessing a penalty. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | TO | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019021408 | PRC-005-1 | R2, R2.1 | Moderate | Lower | Moderate | Self-Report | 2019-04-25 | 2007-06-18 | 2019-04-02 | 2019-04-02 | 2019-09-18 | BHP notified WECC that it was noncompliant with PRC-005-1 R2. Specifically, during an internal compliance certification process, BHP discovered it did not verify battery terminal connection resistance and battery interval or unit-to-unit connection resistance every 15 calendar months as stated in its Protection System Maintenance Program (PSMP) for two battery banks at its DC tie 230kV converter substation. Specifically, BHP discovered that from the mandatory and enforceable date of the Standard, the battery banks involved had not been correctly verified, as required by PSMP. BHP’s third-party contractor was unable to perform the necessary testing because the batteries were designed with protective covers that could not be removed and prevented access to the battery’s posts and straps. In an effort to address the involved batteries design limitations BHP referenced the PRC-005-6 Supplementary Reference and FAQ document which led BHP to incorrectly believe the deferral of tone component of the required testing was acceptable. The root cause of the violation was attributed to the original design of the two battery banks that prevented testing for the battery terminal connection resistance and battery interval or unit-to-unit connection resistance from being completed, as prescribed by its PSMP. Additionally, a contributing cause of this violation was attributed to BHP's lack of a process or procedure for assuring adequate quality of third-party contract services prior to 2017. This noncompliance began on June 18, 2007, when the Standard became mandatory and enforceable, and ended on April 2, 2019, when BHP tested the battery banks in accordance with its PSMP and the current version of the Standard. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BHP failed to verify battery terminal connection resistance and battery interval, or unit-to-unit connection resistance every 15 calendar months as stated in its PSMP, for two battery banks at its DC tie 230kV converter substation, as required by PRC-005-1 R2. Such failure could have resulted in the breakers failing to trip which could have caused equipment damage due to high currents during abnormal system conditions. However, as compensation, the substation involved in the first violation was designed to include redundant battery systems, and each was designed to fully support the battery backup needs of the entire substation reducing the risk to the BPS. | To mitigate this violation, BHP has: 1) performed and verified the terminal connection resistance and battery interval, or unit-to-unit connection resistance on the involved battery banks; replaced the bolts used to connect the straps to the individual jars on the battery banks allowing for the full completion of the maintenance activities as specified in its PSMP; and 2) staff continued to use the testing templates to ensure the correct testing and verification is being performed. | BHP’s systemic issues with PRC-005 were considered an aggravating factor in determining to allege the violations and assess a penalty due to the violations’ VTH expectation for remediation and overlapping duration of the violations. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | TO | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2020023613 | PRC-005-6 | R3 | Moderate | High | Lower | Self-Report | 2020-06-30 | 2017-04-01 | 2019-12-12 | 2020-06-17 | 2020-10-20 | BHP notified WECC that it was noncompliant with PRC-005-6 R3. BHP discovered it did not verify that the communications system at one Bulk Electric System (BES) substation was functional every four calendar months, as prescribed within Table 1-2. Specifically, the involved substation consists of a 115kV ring bus and a non-BES three winding transformer that steps down to 34.5kV and 13.8kV. BHP discovered that its internal BES review committee did not analyze and recategorize the substation as containing BES elements once the addition of a new substation was interconnected on the BHP system on November 7, 2016. This addition caused the involved substation to no longer meet exclusion E1.b and instead met inclusion I4.b making the involved substation subject to PRC-005-6. The root cause of the violation was attributed to BHP’s BES review committee’s lack of a formal process to evaluate the effects of all projects on BHP’s system, including BES reclassifications. Additionally, the contributing cause of this violation was attributed to BHP’s BES review committee’s lack of a formal procedure to communicate the identification or reclassification of BES elements to the PRC-005 review team. This noncompliance began on April 1, 2017, when BHP failed to maintain communication systems within four calendar months of its substation being reclassified as BES, and ended on December 12, 2019, when BHP verified that the communications system at the involved substation was functional. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BHP failed to verify that the communications system at one Bulk Electric System (BES) substation was functional every four calendar months, as prescribed within Table 1-2, as required by PRC-005-6 R3. Such failure could have resulted in a protection system device misoperation leading to the loss of BHP’s 115kV ring bus. However, as compensation, the involved battery banks had all other required testing performed every six months, including: supply voltage, electrolyte level, unintentional grounding, float voltage, battery continuity, cell condition, physical condition of rack, and cell/unit measurements against the station battery baseline, reducing the risk to the BPS. Additionally, the redundancy of the 115kV ring bus topology and the low voltage of the ring bus reduce the risk to the BPS. | To mitigate this violation, BHP has: 1) completed maintenance testing on the communication system at the involved substation; 2) conducted an extent of condition review and found no other instances of potential noncompliance; 3) replaced the informal BES review committee with a more formal chartered group, called the BES Definition Applicability Team (BESDAT), that includes members from the PRC-005 review team, to be responsible for the following: i. identifying BES applicability and/or impacts to facilities based on system configuration, equipment replacement or facility additions; and ii. reviewing and documenting BES designations for impacted facilities. | BHP’s systemic issues with PRC-005 were considered an aggravating factor in determining to allege the violations and assess a penalty due to the violations’ VTH expectation for remediation and overlapping duration of the violations. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2739 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | TO | Settlement Agreement | Admits | $110,000 (for WECC2019021484, WECC2019021482) | WECC2019021484 | FAC-501-WECC-2 | R3 | Moderate | Medium | Severe | Self-Report | 2019-05-07 | 2019-01-01 | 2019-06-05 | 2020-07-14 | TBD | On May 7, 2019, SCEC submitted a Self-Report stating, as a Transmission Owner, it was noncompliant with FAC-501-WECC-2 R3. SCEC did not maintain and inspect three series capacitors and three circuit breakers (CBs) that were elements of three Major WECC Transfer Paths all operated at 500 kV, in accordance with its Transmission Maintenance and Inspection Program (TMIP). Prior to 2019, regarding the series capacitors, SCEC’s TMIP required a visual inspection and SCEC maintained documents that the inspection occurred, although they were not detailed. Specifically, in 2018, SCEC revised its TMIP to include requirements for more detailed inspections for series capacitors; however, it missed those detailed inspections in 2018. For the CBs, SCEC’s TMIP had not changed, yet the inspections were still not performed in 2018. The root cause of the violation was attributed to the progress of the inspections not being adequately tracked and lack of communication between responsible parties. For the first Major WECC Transfer Path, planned maintenance outages were rescheduled due to reliability constraints and new maintenance was not approved until after the end of the calendar year, thus exceeding the compliance deadline. For the second Major WECC Transfer Path, there was a lack of communication between SCEC compliance staff and field personnel. The series capacitors were out of service because they were being replaced and the field personnel assumed that they did not have to maintain the CBs associated with the out-of-service capacitors. The two groups did not effectively communicate to clarify the expectation that the CBs were still required to be maintained. For the third Major WECC Transfer Path, there was a lack of formal review to ensure that the scheduled work had been completed. SCEC’s workload template was manually populated with a task that did not roll over onto the next workload template, so personnel did not realize that the work had not been performed. This noncompliance began on January 1, 2019, when all the equipment was required to be inspected, per SCEC’s TMIP, and ended on June 5, 2019, when SCEC completed the inspections for all the affected equipment. | This violation posed a moderate risk to the reliability of the bulk power system (BPS). In this instance, SCEC failed to adhere to its TMIP for three series capacitors and three CBs, as required by FAC-501-WECC-2 R3, which were elements of three Major WECC Transfer Paths, all operated at 500 kV. SCEC’s series capacitors were utilized to improve power transfer capability of a transmission line and to improve system stability by reducing the phase angle of the line. Additionally, its series capacitors were used to share the load between parallel lines and control voltage. The series capacitor reduced the overall line reactance and allowed a larger stable transfer of power. As well, the series capacitors could have been applied to obtain better load division on parallel lines in the event there were different conductor resistances. A failure to maintain the series capacitors could have resulted in an improper operation of the capacitors failing to support the associated 500 kV transmission line capacity, thereby reducing stability to SCEC's system. This could have resulted in potential instability issues with three Major WECC Transfer Paths and one 500 kV Substation and a derating of the line. The failure to maintain the CBs associated with the series capacitors could have caused the CBs to prematurely open or fail to open, which could have resulted in a loss of the line or damaged equipment if the CB failed to isolate the series capacitor. The failure could have resulted in potential instability issues with the Major WECC Transfer Paths that have a potential of carrying 4,888 MW, depending on the directional flow. The Transfer Path losses could have triggered a Remedial Action Scheme (RAS) to trip 1,400 MW and 600 MW of load in the area to control the instabilities. Per the WECC Transfer Path Catalog, this particular area is considered sensitive. However, as compensation, all three of the Major WECC Transfer Paths had parallel lines and the operations of the RAS would have opened the appropriate other paths to reduce the loading. In addition, the three CBs are only capable of being operated as switchers, due to their configuration, thus during an emergency, other CBs (all of which were timely inspected per the TMIP) could have de-energized the associated transmission line. Two of the series capacitors were being replaced and out of service during the period of the violation. As well, SCEC had performed visual monthly inspections including a measurement of three electrodes that are used in back up protection for the capacitors from the ground and the series capacitors were actively monitored through internal alarms that identify potential degradation of series capacitors through the Energy Management System, reducing the risk to the BPS. | To mitigate this violation, SCEC has performed the following actions: 1) Completed maintenance and testing for the series capacitors and CBs; 2) Updated its monthly workload planning checklist to review with the Subject Matter Experts (SMEs) to ensure all aspects of its TMIP were completed and the responsible party was aware of its responsibilities and update as needed; 3) Finalized monthly workload planning checklist including obtaining management approval and validating the checklist with all the stakeholders; 4) Documented scheduling process project plan by creating a detailed project plan; 5) Documented previous scheduling processes; 6) Documented improved scheduling processes with an emphasis on the communications between responsible parties to address gaps in the monthly and annual scheduling process, changes or additions of inspections types (new equipment types) and annual review processes; and 7) Finalized the scheduling process changes and communicated them to affected personnel. | WECC reviewed SCEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination because it was effective in establishing controls to detect the noncompliance with FAC-501-WECC R3. WECC considered SCEC's compliance history and determined there were no relevant instances of noncompliance.
2021-10-28 | NOC-2739 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | TO | Settlement Agreement | Admits | $110,000 (for WECC2019021484, WECC2019021482) | WECC2019021482 | FAC-501-WECC-1 | R1 | Moderate | Medium | Severe | Self-Report | 2019-05-07 | 2016-01-02 | 2018-02-07 | 2019-12-11 | 4/17/2020 | On May 7, 2019, SCEC submitted a Self-Report stating, as a Transmission Owner, it was noncompliant with FAC-501-WECC-1 R1. Specifically, during SCEC’s review of its potential noncompliance with FAC-501-WECC-2 R3 (NERC Violation ID WECC2019021484), SCEC discovered it did not have documentation that it had not completed the 2016 and 2017 annual reviews of its TMIP. SCEC was late in completing its review for the 2018 TMIP. The root cause of the violation was attributed to poorly defined management policy guidance and expectations. SCEC had no formal process to initiate the annual review of its TMIP, thus there is not documentation to confirm if it was completed timely. Further, when the reviews occurred, SCEC did not appropriately store the documents to demonstrate compliance. This noncompliance began on January 2, 2016, when the TMIP review was due, and ended on February 7, 2018, when SCEC completed the annual review of its TMIP. | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the BPS. In this instance, SCEC failed to annually review its TMIP, as required by FAC-501-WECC-1 R1.1. Such failure could have resulted in SCEC missing maintenance intervals for new equipment or changed equipment which could have led to equipment not operating properly, resulting in equipment failures and causing unplanned outages. However, as compensation, if new equipment were to be added or changed, it would have been added to the TMIP because SCEC compliance personnel and responsible transmission personnel would have been aware of the changes, as these tasks were part of their main job functions. In addition, Major WECC transfer paths would not have changed without SCEC’s knowledge and it would be unlikely that the designation of addition lines would have resulted in SCEC missing their addition in the TMIP. Thus, it would have been unlikely that equipment maintenance would have been missed because of a missed annual review of SCEC’s TMIP. In addition, no changes to SCEC’s TMIP were required during the period of the violation, thereby lessoning the actual risk. | To mitigate this violation, SCEC has performed the following actions: 1) performed a review of its TMIP and found no updates were needed; 2) documented a process for annual review of its TMIP; and 3) trained responsible employees on the new process and the review requirements for the TMIP. | WECC reviewed SCEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination because it was effective in establishing controls to detect the noncompliance with FAC-501-WECC R3. WECC considered SCEC's compliance history and determined there were no relevant instances of noncompliance.