## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2021-11-30 | NOC-2687 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | GO, TO | Settlement Agreement | Neither Admits nor Denies | 0 | SERC2017018352 | PRC-005-1 | R2 | Moderate | High | High | Self-Report | 2017-09-18 | 2007-06-18 | 2019-07-09 | 2021-07-25 | TBD | LGE and KU notified SERC that it was in violation of PRC-005-6 R3 for failing to maintain its Protection System in accordance with the minimum maintenance and testing (M&T) activities and maximum maintenance intervals. SERC later determined that the violation extended back to PRC-005-1 R2. Around May 8, 2017, LGE and KU alerted SERC about this issue, stating that misrepresentations had occurred, that an extent-of condition assessment was underway to determine the scope of the issue, and a Self-Report would be forthcoming once the assessment was completed. Additionally, on October 29, 2019, LGE and KU submitted an expansion of scope for its Transmission Owner (TO) function for five battery banks where testing was outside the required intervals. In March 2017, a Generation Services employee (EE-A), was terminated due to performance issues, including the failure to complete tasks as assigned. In March/April 2017, EE-A’s manager undertook a review of EE-A’s projects, including tasks associated with generation M&T status and performance of controls. On April 17, 2017, during this review, the manager discovered that LGE and KU’s PRC-005-6 M&T program had not been extended to include its Blackstart Resources at two substations by July 1, 2016 in accordance with the Implementation Plan for Phase 2 of the revised Bulk Electric System (BES) definition. Additionally, there were no M&T results for these Blackstart Resources. Both substations connect at less than 100kV and were not BES components prior to the revised BES definition. LGE and KU discovered that EE-A had misrepresented the status of work activities for the Protection System devices associated with the Blackstart units by providing numerous inaccurate verbal updates to the manager that required M&T activities were on schedule and all required activities associated with Protection System devices associated with the Blackstart Resources would be completed prior to July 1, 2016. From April 17 through mid-July 2017, an extent-of-condition review was performed to identify if there were any other instances in which EE-A failed to perform required Generation Owner (GO) related tasks. LGE and KU discovered that EE-A failed to review battery test results at one substation to ensure they were completed as required and entered into Cascade (data repository being used at the time by the department). Specifically, EE-A had been entering information into the internal control (Cascade) to make it appear as though EE-A had completed reviews of the data, when in fact EE-A had not. From mid-July 2017 through September 2017, LGE and KU began completing M&T for the GO devices that had been identified as noncompliant and submitted a Self-Report and mitigation plan, which included steps for identifying if there were additional noncompliant devices. From late 2017 through June 2018, LGE and KU contracted a third-party consultant to perform a walk-down and print review of all generation assets to ensure that all generation assets that should be in scope for PRC-005 were accurately identified. From June 2018 through November 2018, during the review of the data provided by the third-party consultant, LGE and KU GO identified several inaccuracies with the information the consultant provided, including errors such as listing duplicate assets, inclusion of retired assets, assets missing from the vendor’s list that the LGE and KU GO knew should have been on the list. Thus, LGE and KU GO determined that it could not rely on the consultant’s review and that internal resources were needed to conduct another walk-down and review of generation assets. From November 2018 through May 2019, LGE and KU GO conducted an extensive internal review that included a combination of walk downs and in-depth DC schematics review to identify and verify the inventory of generation assets within scope for PRC-005. LGE and KU identified a total of 82 noncompliant Protection System devices that were directly attributed to EE-A, which includes the 78 Protection System devices associated with the LGE and KU Blackstart Resources and the 4 battery banks. LGE and KU’s extensive review identified 159 additional noncompliant Protection System devices on the generation side, 24 of which were attributable to missed devices. All M&T activities associated with these 159 Protection System devices occurred during the time period EE-A had primary responsibility for the GO’s PRC-005 compliance. However, during LGE and KU’s performance of the mitigation activities, it did not dedicate resources to track, or attempt to verify, which additional violations were directly attributable to EE-A’s actions/inactions. Notwithstanding, although EE-A did not perform the actual M&T activities, the EE-A’s responsibilities included notifying plant personnel of the required M&T, reviewing results, ensuring complete and appropriate documentation of the M&T activities, tracking completion of maintenance and testing activities, and updating management as to the status of the testing and maintenance activities. After EE-A’s termination, EE-A’s manager discovered that EE-A was not performing several of these tasks. Specifically: (1) EE-A was not properly notifying plant personnel of the required testing; (2) when testing results were submitted to EE-A, he was not reviewing the results and ensuring that there was appropriate documentation to demonstrate that all the required M&T activities had been properly completed; and (3) EE-A was falsifying information in an internal control (Cascade) that the company utilized to track the completion of PRC-005 M&T activities. Specifically, EE-A had been entering information that indicated that the EE-A had reviewed the testing records and verified everything was compliant, when in fact EE-A had not. On October 29, 2019, LGE and KU as a TO submitted an expansion of scope for three Vented Lead-Acid (VLA) battery banks and two Valve-Regulated Lead-Acid (VRLA) battery banks. The five instances of non-compliance were identified during a review by the LGE and KU TO of its PRC-005 testing records. Three of the instances were tied to the transition to PRC-005-6 and the associated 18-month and 6-month testing intervals for batteries. In each of these cases, the devices were tested just slightly outside the required window due to an error with the macro that tracks completion. One of the instances was tied to an individual inadvertently entering the wrong testing interval, and the last one was tied to a missing work order. From November 2019 through March 2020, in response to a SERC RFI, LGE and KU TO performed a walk-down of four transmission substations. The walk-down did not identify any additional instances of non-compliance. Because no other issues were identified, SERC did not require any additional walk-downs of the TO facilities. From February 13, 2018 to June 4, 2018, SERC conducted an on-site Compliance Audit of the GO and TO functions of LGE and KU. SERC included PRC-005-6 R3 in the 2018 Compliance Audit scope and did not identify any issues for either transmission or generation assets. The cause of the issues identified in the Self-Report involved the management practice of asset and configuration management, which includes validation processes and internal controls. Specifically, LGE and KU lacked effective internal controls to verify verbal reports on M&T activities and to verify the accuracy of its system diagrams, which resulted in LGE and KU failing to identify all Protection System devices. LGE and KU also lacked effective internal controls to verify the monthly review list was complete, i.e., missing Blackstart units, which resulted in not identifying the employee misrepresentation issue until April 2017. Further, LGE and KU did not conduct a walk-down of the facilities prior to the implementation of PRC-005-1 and lacked documented asset and configuration management processes. The cause of the Scope Expansion was tied to the transition to PRC-005-6 and the associated 18-month and 6-month testing intervals for the batteries. The other instances were due to human error for inadvertently entering the wrong testing interval and a missing work order. The noncompliance identified in the Self-Report started on June 18, 2007, when Version 1 of the Standard and Requirement became mandatory and enforceable on LGE and KU, and ended on July 31, 2017, when LGE and KU completed the last of its battery M&T for generation assets. The noncompliance identified in the expansion of scope started on February 1, 2018, the first instance that LGE and KU failed to perform M&T activities within the required interval, and ended on July 9, 2019, when LGE and KU completed the last of the M&T activities for transmission assets. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). LGE and KU’s failure to perform M&T activities with the defined intervals could have caused Protection System relays to operate prematurely and trip a unit, fail to operate and cause the next Protection System relay to operate to clear the fault, or unnecessarily trip a transmission line. LGE and KU did maintain and test the Blackstart units as a part of general plant maintenance, but did not perform the M&T of the associated Protection System devices in accordance with the PRC-005 requirements. LGE and KU work orders for the M&T activities at both plants were performed in accordance with good utility practices, however, the test frequency or extent of testing did not fulfill the periodicity or types of testing required by PRC-005. LGE and KU also failed to perform M&T, within the defined intervals, for some devices associated with 27 of its 34 generators (79.41%) and five batteries on the Transmission system. The impacted generators ranged from a net nameplate rating of 529 MVA to 10 MVA with annual capacity factors ranging from 76% to 0.7%. An unexpected trip of any of these generators would not have a significant impact as entities are required to carry spinning reserves, which would be available if needed. The majority of the units impacted were around 200 MVA. The Blackstart units ranged from 11 MVA to 38 MVA and three were hydro. The gas-fired Blackstart units had annual capacity factors of less than 1%. In addition, of the 218 devices LGE and KU GO failed to maintain in accordance with PRC-005, 155 (71%) were CTs and PTs, which have 12 year intervals and the only maintenance activity required is to verify that current and voltage signal values are provided to the protective relay. PT or CT failure would typically be identified prior to the 12 year verification activity. In addition, LGE and KU Transmission Operations would have been notified via an alarm regarding the loss of DC power or the Loss of a Remote terminal unit if there were issues associated with the five TO batteries. The Quarterly Substation Inspections that follow LGE and KU PRC-005 Protection System Maintenance Program (PSMP) were completed on time for all of the affected batteries. The Quarterly Substation Inspection included verifying the station DC supply voltage, inspecting the electrolyte level of the batteries, and checking the DC supply system unintentional grounds. The test results for all affected TO batteries confirmed Protection Systems were operating as designed, thus, minimizing any potential impact to the BPS had a system disturbance occurred and there were no misrepresentations during the duration of the violation. No harm is known to have occurred. | To mitigate the noncompliance for the generation assets, LGE and KU: 1) terminated the employee who misrepresented maintenance and testing records; 2) developed, trained, and implemented a process to review current and future generation projects, as well as scopes of work, to assess if there are compliance impacts to applicable standards; 3) conducted an internal review, a combination of re-walk down and an in-depth DC schematics review, to identify and verify inventory of generation PRC-005 assets; 4) confirmed test records are available for PRC-005 generation devices; 5) submitted noncompliant PRC-005 generation assets list(s) for testing to plant personnel;. 6) developed and implemented compliance preventive maintenance work orders utilizing Maximo (a fleet-wide Enterprise maintenance management system) to provide a consistent and reliable approach to scheduling compliance work orders; 7) developed and implemented Protection Systems training; 8) implemented and enforced a repository of PRC-005 generation assets and a tool that automates and standardizes testing processes; 9) developed and implemented training on its generation change management program; and 10) ensured maintenance and testing was completed, and appropriate maintenance and testing records were maintained, for all PRC-005 generation devices and ensured adequate evidence was maintained to demonstrate compliance, such as including actual voltage, current, and resistance values measured during the required testing to demonstrate that the test was performed. To mitigate the noncompliance for the transmission assets, LGE and KU: 1) performed the required tests to bring the noncompliant devices into compliance with PRC-005-6 requirements; 2) counseled the parties responsible for performing the work where the potential compliance issues were found of the PRC-005 maintenance and testing expectations; 3) conducted a PRC-005 overview with each operation center and Transmission Asset Management; 4) created and distributed jobs aides for Cascade data entry to each PRC-005 Protection System Component; 5) updated report logic to generate alerts based on PRC-005 test intervals that will include an ongoing reconciliation of total, outstanding, and completed work orders; and 6) reviewed all Cascade records for LGE and KU’s TO PRC-005 Communications Systems, Voltage & Current Sensing Devices, and Control Circuitry to ensure test intervals are accurate and test records support compliance with PRC-005. | LGE and KU’s relevant prior noncompliance with PRC-005-1 R2 includes NERC Violation Identification Numbers: SERC200800135, SERC2011006699, and SERC2013012951. In SERC200800135, LGE and KU had gaps in its documentation to support completion of maintenance testing activities for some components of its Generation and Transmission Protection Systems as defined in the NERC Glossary of Terms. This violation was under different managers and ownership at the time and was mitigated eight years prior to the start of the instant violation. Therefore, this violation does not warrant aggravation of the instant violation. In SERC2011006699, Protection System devices were not compliant with PRC-005 due to a lack of clarity with the division of responsibility at the GO/TO boundary. After identifying the noncompliant Protection System devices, LGE and KU undertook a review that identified other noncompliant generation devices associated with the inclusion of auxiliary equipment devices and missed testing intervals which were incorporated into SERC2011006699. The internal controls implemented to address the noncompliance were designed to: (i) ensure proper identification and assignment of responsibility for Protection System devices located at GO/TO boundaries within LGE and KU, and (ii) to improve the generation data management. A portion of the mitigation plan was focused on the development of an internal control designed to ensure the correct allocation of responsibility between the GO and TO, which would not have come into play with regard to the devices identified in the instant violation. In addition, as a part of the mitigation plan for SERC2011006699, the LGE and KU GO adopted Cascade, which was also used by the LGE and KU TO, for data management and the implementation of internal controls for tracking and reporting Protection System maintenance and testing. However, the GO subsequently identified that Cascade was unable to properly interact with other systems used by generation undermining the ability to use Cascade as a sole control for all of generation’s Protection System devices’ testing and maintenance records. To address this gap, the LGE and KU GO implemented manual processes to track, check and follow-up with plant personnel to ensure required PRC-005 maintenance and tests had occurred. It is these manual processes that EE-A in this instant issue failed to perform. As noted in the mitigation plan for the current Self-Report, LGE and KU is addressing this issue by implementing a new data management system that better aligns with generation’s systems and relies less on manual internal controls. In addition, changes to the PRC-005 standard and the BES definition resulted in an expansion of the scope of devices that needed to be included in the LGE and KU GO PRC-005 program. For example, the Blackstart Resources did not meet the BES definition until it was revised in 2014 and compliance was not required for the devices associated with these Blackstart Resources until July 1, 2016. While LGE and KU had a plan intended to track the compliance activity associated with integrating these devices into the PRC-005 program by July 1, 2016, this plan was undermined by the actions of the terminated employee in this Self-Report. SERC201106699 should not be attributed to this instant violation because three of the instances of non-compliance were tied to the change in intervals associated with the implementation of PRC-005-6. Specifically, the macros for the reports that identified overdue testing and maintenance were not updated to reflect the new testing intervals, and therefore the overdue testing and maintenance was not flagged on the reports. As for the remaining two instances of non-compliance, one tied to a data entry error and one to a missing work order, neither was an issue that would have been caught by the internal controls implemented in 2011. In SERC2013012951, the instances of non-compliance were associated with the change management process, namely, the failure to test devices prior to placing them in service, and missed test intervals for TO Protection System devices. The controls implemented in the mitigation plan for SERC2013012951 were focused on change management for transmission assets and an increased emphasis on and visibility of upcoming test deadlines. The change management process enhancements that were developed to mitigate SERC2013012951 are unrelated to the instances of non-compliance reported in 2019. The monthly report was involved, but only to the extent that there was a failure to update the macros that produce the monthly report as further described below. The expansion of the scope was for five non-compliant TO devices VLA batteries and VRLA batteries). The controls implemented to mitigate SERC2013012951 would not have been able to detect or prevent the instances of non-compliance for these five devices due to the nature of the issues that led to the non-compliance. Specifically, the non-compliance stemmed from a failure to update the macros contained in the monthly report from the prior requirement to test the Protection System DC Supply once per calendar year to the new mandatory test intervals in PRC-005-6 of eighteen-month VLA battery test interval (impacting one device) and the six-month VRLA battery test interval (impacting two devices). The two other instances of non-compliance, one tied to a data entry error and one to a missing work order, were not issues that would have been caught by the internal controls implemented in 2013.
2021-11-30 | NOC-2742 | SERC Reliability Corporation (SERC) | South Carolina Public Service Authority (SCPSA) | NCR01312 | GO, TO | Settlement Agreement | Neither Admits nor Denies | 40000 | SERC2018019136 | FAC-009-1 | R1 | Moderate | Medium | Severe | Compliance Audit | 2018-02-08 | 2007-06-18 | 2021-03-18 | 12/1/2021 (expected completion date) | TBD | SERC determined that SCPSA was noncompliant with FAC-008-3 R6. SCPSA had 21 Facility Ratings that were not consistent with its associated Facility Ratings methodology (FRM). SERC later determined that this violation started under FAC-009-1 R1 and spanned to FAC-008-3 R6. When preparing documentation for a SERC audit data request, SCPSA discovered four instances of incorrect element ratings at one substation, which resulted in Facility Ratings that did not match the FRM. Correction of the element ratings resulted in three Facility Rating increases and one Facility Rating decrease. As part of the on-site audit, SERC completed a walk-down of the substation and discovered seven additional incorrect element ratings; however, none of these incorrect element ratings impacted the Facility Rating. After the Audit, SCPSA performed an extent-of-condition review and conducted a walk-down of all of its generation and transmission facilities. As a result, SCPSA discovered incorrect Facility Ratings at 18 of its 319 transmission facilities, inclusive of the one found during SCPSA’s audit preparation. Of the 18 transmission facilities identified, 12 of the Facility Ratings decreased when corrected. Specifically, the maximum summer Facility Rating decrease was 50% and the maximum winter Facility Rating decrease was 84%. Both maximum Facility Rating changes occurred as a result of an incorrect switch rating at the same 115kV Facility. Furthermore, SCPSA identified incorrect Facility Ratings at nine of its 27 generating units. Six generating units had a single incorrect Facility Rating and three units each had two incorrect Facility Ratings. Of the generating Facility Rating changes, two instances were de-rates of 21.25%, and the remainder were increases with a maximum increase of 4.6%. During the period of noncompliance, SCPSA’s loads did not exceed the correct Facility Rating in any instance of a Facility Rating decrease at its transmission or generating facilities. During its walk-down, SCPSA determined that the oldest incorrect Facility Rating occurred prior to the Standard’s June 18, 2007 effective date. On March 18, 2021, SCPSA revised all incorrect element and Facility Ratings. The causes of the violation were a deficient procedure at its generating facilities and inadequate training at its transmission facilities. The procedure associated with its generation facilities was deficient because it did not specify the specific instances when SCPSA should use a calculation instead of manufacturer nameplate values or when multiple elements could be considered in a single rating. Additionally, at its transmission facilities, some business units lacked awareness of SCPSA’s established process for communicating changes made to the transmission system. During the period of noncompliance, these business units had significant changes to its organization and inadequate training of new employees. This violation started on June 18, 2007, when the Standard became Mandatory and enforceable, and ended on March 18, 2021, when SCPSA revised the incorrect element and Facility Ratings. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCPSA’s failure to establish Facility Ratings consistent with its FRM could result in violations of System Operating Limits, unnecessary facility trips, damage to facilities, and erroneous planning. Additionally, this violation affected 33% of its generating units and 5.6% of its transmission facilities. SCPSA reviewed the operating records for all of the de-rated facilities and found that none operated at loads greater than the revised Facility Ratings during the period of noncompliance. No harm is known to have occurred. | To mitigate this violation, SCPSA has or will perform the following actions: 1) corrected the element and Facility Ratings; 2) increased the Transmission Project Management and Area Engineering business units’ visibility into the facility rating process by adding their representation to the Model Validation and Dynamics Review Team (MVDRT), so that the team includes representation from all areas that have a key role in the facility ratings process; 3) established a Continuous Improvement Project Team, consisting of representation from Power System Engineering & Control, NERC Compliance, Generation, Customer Service, and Technology & Innovation, to focus on minimizing physical and electrical facility characteristics data discrepancies between Transmission Planning’s database and field assets/equipment; 4) implement a standardization of database and filed asset/equipment inputs through checklists for suppliers and field personnel for its transmission facilities; 5) implemented an annual internal control to target verification of 20% of its transmission facilities each calendar year; 6) revise the Generation Facility Ratings Methodology procedure to provide clarity on the rating methodology of generation facilities, including guidance on when nameplate ratings versus calculations can be used and clearly indicate that the generator step-up transformer is evaluated for both the low and high-side and train annually on the new procedure; and 7) implement comprehensive training programs for both its transmission and generation personnel that include annual facility rating training for MVDRT; training to personnel that have a role in the established process for communicating changes made to the transmission system and generating units; training for personnel that conduct work activities on the transmission system on a day-to-day basis; training for personnel responsible for electrical maintenance at the generating units; annual training for the Generation Lead Team; and a computer-based training module on FAC-008 to provide to employees that have a role in making changes to the transmission system as part of their on-boarding process as a new employee. | SERC reviewed SCPSA’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SCPSA's ICP includes strong oversight and an ongoing internal control to walk down 20% of its facilities every year. SERC considered SCPSA’s compliance history and determined there were no relevant instances of noncompliance.
2021-11-30 | NOC-2746 | ReliabilityFirst Corporation (RF) | Southern Indiana Gas & Electric Company d/b/a CenterPoint Energy Indiana South | NCR00917 | TOP | Settlement Agreement | Admits | 0 | RFC2019022724 | TOP-002-4 | R6 | Moderate | Medium | Severe | Self-Report | 2019-12-19 | 2018-06-26 | 2018-06-27 | 2019-09-05 | 2020-04-10 | On December 19, 2019, the entity submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-002-4 R6. The entity failed to provide its Reliability Coordinator (RC), MISO, with an Operating Plan for next-day operations addressing potential SOL exceedances identified as a result of its Operational Planning Analysis. Specifically, on June 26, 2018, as the result of performing its next-day operations study, the entity identified two post-contingent SOL exceedances. the entity created an Operating Plan for next-day operations to address the identified SOL exceedances as required by TOP-002-4 R2. However, the entity, as a TOP, did not notify its RC, MISO, as required by TOP-002-4 R6. The noncompliance was discovered as the result of an entity review of all next-day operations studies between April 1, 2017 and September 5, 2019. The next-day operations study revealed the following potential SOL exceedances: a. For the loss of the Francisco to Duff 345kV line, the study indicated an 8.23% post-contingent MVA overload on the Z80 Francisco to Toyota Tap 138kV line; and b. For the loss of the Francisco to Duff 345kV line, the study indicated a 7.43% post-contingent MVA overload on the Z80 Elliott to Toyota Tap 138kV line. The root cause of this noncompliance was inadequate training of entity Transmission Operators on their notification responsibilities when an SOL exceedance is identified via a next-day operations study. This noncompliance involves the management practice of grid operations. Grid operations management is involved because grid operations involves maintaining situational awareness of the grid, and in this instance by failing to report its findings of a potential SOL exceedance and an accompanying Operating Plan to MISO, the entity potentially adversely impacted the situational awareness of the grid. The violation started on June 26, 2018, when the entity failed to notify MISO of potential SOL exceedances for June 27, 2018, and ended on June 27, 2018, when the entity performed its daily next-day operations study. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by the failure to notify the RC of possible exceedances could result in the RC operating based on inaccurate and different risk and transmission assumptions, potentially causing adverse impacts on the BPS. Specifically, where the entity fails to share the results of next-day studies with the RC before the next day, the RC would be relying on internal BPS studies without knowledge of all relevant or identified contingencies, increasing the probability of miscoordination. The risk here is not minimal because the two potential exceedances identified and not communicated involved a 345 kV line that supported a 138 kV network. Additionally, the study identified two potential MVA rating overloads over 7%, which are sizable overages. The risk here is not serious because MISO has real-time procedures for congestion management to mitigate the risk of the affected lines. Further, the entity created an Operating Plan for next-day operations to address the potential SOL exceedances. Additionally, the entity has extensive internal procedures for collaborating with MISO in the event of an SOL exceedance or an instance approaching an SOL exceedance during real time operations. ReliabilityFirst also notes that the MISO Reliable Operations Working Group (ROWG) Report for June 2018 did not identify any actual SOL exceedances for the entity during the month of June 2018. | To mitigate this violation, the entity has performed the following actions: 1) notified TSO Operators of the procedure; and 2) updated the next-day study form to include a button to automatically produce an email to MISO Transmission Security Planning. | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst granted mitigating credit for cooperation and Self-Reporting. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. TOP-002-4 R6 was developed in response to findings relating to the September 8, 2011, Southwest Outage, with the intent being to improve communication between TOPs and their RC. This specific communication is essential for both TOPs and the RC so as to improve their ability to identify and plan for potential contingencies. The only available Violation Severity Level for TOP-002-4 R6 is Severe. Due to the criticality and regulatory intent of TOP-002-4 R6, and the fact that the type of issue in this case contributed to the September 8, 2011, Southwest Outage, this violation is disposed of in a Settlement. However, this specific violation does not rise to the level of warranting a monetary penalty. The violation is limited in scope. It includes a single instance where a single next-day study identified two potential SOL exceedances, and the entity did not communicate its Operating Plan to the RC as required. Additionally, this violation was identified as the result of an extensive two year review of next-day studies where the entity identified only this single, narrow instance. Based on the foregoing, ReliabilityFirst is not levying a monetary penalty.