## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2021-12-30 | NOC-2749 | ReliabilityFirst Corporation (RF) | ITC Transmission (ITCT) | NCR00803 | TO | Settlement Agreement | Admits | $20,000 (for RFC2019022365 and RFC2019022362) | RFC2019022365 | PRC-005-6 | R3 | Moderate | High | Severe | Self-Report | 2019-10-04 | 2018-07-02 | 2021-12-03 | 2021-12-03 | TBD | On October 4, 2019, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-005-6 R3. This violation relates to the entity’s acquisition of the Dearborn Industrial Generation (DIG) site Protection System assets. On July 2, 2018, the entity acquired the six substations at issue from Ford, Cleveland-Cliffs, and DIG. The Assets include 230 kV and 120 kV Protection Systems that also interconnect with 844 MW of generation. After reviewing the Protection System maintenance and testing data provided by the prior owners of the Assets, the entity concluded that there were 29 Protection Systems that were not compliant with PRC-005-6 R3 and required mitigation. More specifically, the entity concluded that the prior owners did not perform relay scheme maintenance for 44 relay schemes. The entity has now performed all of the overdue relay scheme maintenance. The process to remediate the PRC-005-6 R3 violation took an extended amount of time because it is difficult to get outages for the industrial customers approved to perform the overdue maintenance. The root cause of this violation is that the prior owners did not perform maintenance on any of the aforementioned relay schemes and their components. This violation involves the management practice of external independencies. The violation began on July 2, 2018, the date the entity acquired the assets at issue in this Self-Report. The violation ended on December 3, 2021, the date the entity completed all of the overdue relay scheme maintenance. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by not performing relay scheme maintenance for 44 relay schemes across six substations is that the relays could fail to operate as expected, which could reduce the reliability of the BPS. The risk is not minimal because of the long duration of the violation. The risk is not serious because these substations primarily serve industrial load, meaning that if the relays failed to operate, the impact on the BPS would likely be minimal. ReliabilityFirst notes that there have been no failures at the DIG site due to insufficient maintenance on the relays. | To mitigate this violation, the entity has performed the following actions: 1) completed maintenance at Dearborn Sub 41 DC Supply; 2) completed maintenance at Dearborn 48/49 DC Supply; 3) completed protection system maintenance on the equipment associated with the Ford #1, including Dearborn Generation 48/49 Breaker P; 4) completed protection system maintenance on Substation 42 breakers; 5) completed maintenance on Double Eagle #1 line and Dearborn Generation 41 Transformer E (including breakers at 99 and 41); and 6) completed maintenance on Warren-Navarre-Dig lines Dearborn Generation 42 Transformer N protection and breaker 42005. 7) completed maintenance on Double Eagle #2 line and Dearborn Generation 41 Transformer F (including breakers at 99 and 41); 8) completed maintenance on Ford #2 and Transformer M; and 9) completed maintenance on Bus Relaying at Dearborn Generation 99. In addition, the entity integrated the relays into its NERC Compliance Program to prevent recurrence of the violation. | When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered the presence and operation of a quality compliance program as well as other indicators of a culture of compliance at the entity. This was evidenced by the fact that the violations at issue in this Agreement were proactively identified and reported by the entity after acquiring the Assets. The entity’s internal controls helped identify the violations and the entity ran thorough extent of conditions for the violations to determine the scope of each violation. The entity has spent considerable resources to identify all of the violations, to mitigate the violations, and to integrate the Assets into its NERC Compliance Program which will help prevent recurrence. The entity’s actions identified, addressed, and eliminated longstanding Bulk Electric System (BES) risk for these Assets. Therefore, ReliabilityFirst is awarding a significant amount of internal compliance program credit to encourage this sort of behavior by ITCT and other Registered Entities in the future. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance.
2021-12-30 | NOC-2749 | ReliabilityFirst Corporation (RF) | ITC Transmission (ITCT) | NCR00803 | TO | Settlement Agreement | Admits | $20,000 (for RFC2019022365 and RFC2019022362) | RFC2019022362 | PRC-023-4 | R1 | Moderate | High | Severe | Self-Report | 2019-10-04 | 2018-07-02 | 2019-07-30 | 2019-07-30 | 2020-08-20 | On October 4, 2019, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-023-4 R1. This violation relates to the entity’s acquisition of the DIG site Protection System assets. On July 2, 2018, the entity acquired the six substations at issue from Ford, Cleveland-Cliffs and DIG. The Assets include 230 kV and 120 kV Protection Systems that also interconnect with 844 MW of generation. The entity’s purchase of the Assets resulted in the acquisition of Protection Systems subject to PRC-023. Upon purchasing the Assets, the entity conducted a compliance review for all Protection Systems subject to PRC-023. After reviewing the applied relay settings and Facility Ratings, there were a total of six schemes that had relay settings that were not compliant with any criteria of PRC-023-4 R1. The root cause of this violation is that the prior owners of the Assets did not have internal controls in place to ensure that all schemes have relay settings that are compliant with PRC-023-4 R1. This violation involves the management practice of external independencies. The violation began on July 2, 2018, the date the entity acquired the assets at issue in this Self-Report. The violation ended on July 30, 2019, the date the entity brought all six relay settings into compliance by performing a settings reset. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by having six schemes that have relay settings that are not compliant with any criteria of PRC-023-4 R1 is limiting transmission loadability and interfering with system operators’ ability to take remedial actions to protect system reliability. The risk is not minimal because of the more than one year duration. The risk is not serious because these substations primarily serve industrial load meaning that if the relays failed to operate, the impact on the BPS would likely be minimal. ReliabilityFirst notes that no operations due to the noncompliant relay settings occurred during the violation. | To mitigate this violation, the entity brought all six relays into compliance with a settings reset. The entity implements multiple controls in the setting process to detect and prevent non-compliant settings from being applied to relays. The entity detected the non-compliant settings on the relays it purchased through the use of these controls and created compliant settings within the same process. | When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered the presence and operation of a quality compliance program as well as other indicators of a culture of compliance at the entity. This was evidenced by the fact that the violations at issue in this Agreement were proactively identified and reported by the entity after acquiring the Assets. The entity’s internal controls helped identify the violations and the entity ran thorough extent of conditions for the violations to determine the scope of each violation. The entity has spent considerable resources to identify all of the violations, to mitigate the violations, and to integrate the Assets into its NERC Compliance Program which will help prevent recurrence. The entity’s actions identified, addressed, and eliminated longstanding Bulk Electric System (BES) risk for these Assets. Therefore, ReliabilityFirst is awarding a significant amount of internal compliance program credit to encourage this sort of behavior by ITCT and other Registered Entities in the future. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance.