## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2022-02-28 | NOC-2755 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | TOP | Settlement Agreement | Does Not Contest | No penalty (WECC2020024012, WECC2020024013, and WECC2020024014) | WECC2020024012 | TOP-001-4 | R1 | Moderate | High | Severe | Self-Report | 2020-10-01 | 6/3/2020 | 6/3/2020 | 5/12/2021 | 5/12/2021 | On October 1, 2020, WACM submitted a Self-Report notifying WECC as the Lead Regional Entity under an existing multi-region registered entity coordinated oversight agreement with MRO as the Affected Regional Entity, that as a Transmission Operator (TOP), it was in violation with TOP-001-4 R1. On June 3, 2020, at 2:02 AM a phase to ground fault occurred on a 115kV transmission line, that tripped a breaker, which resulted in the loss of that breaker and the open ended terminal of a multi-terminal 115kV transmission line. The breaker attempted to reclose automatically at 2:02 AM, but it tripped again. A SCADA alarm was generated and documented the trip and attempted reclosing of the breaker. However, the night shift System Operator (SO) was distracted did not recognize the visual and audible alarms for over two hours. At 4:17 AM, the SO attempted to close the breaker via SCADA control, but was unsuccessful. Maintenance was called to investigate the cause and a broken jumper was found approximately three miles from the terminal of the 115kV transmission line where the breaker tripped. The night shift SO completed the verbal shift change with the two incoming morning shift SOs. However, an internal interruption report and transmission log entry was not completed during the night shift SO’s shift. At 7:53 AM, WACM sent its Reliability Coordinator (RC) and affected TOP a notification of the event and the status of the unavailable Bulk Electric System (BES) equipment by sending a Clearance Switching Request Form and WACM initiated the process of switching to electrically isolate the faulted equipment. WACM completed the repairs, and the clearance was released at 3:08 PM. Removal switching was also completed, and the equipment was returned to service at 3:30 PM on June 3, 2020. During the thirteen hour and 28 minute outage of the 115kV transmission line, there was no loss of the potential 35 MW of load or less, depending on loading conditions during the event; nor were there any interruption of customer service. By not recognizing the SCADA alarms in a timely manner, the night shift SO did not act to maintain the reliability of its TOP via its own actions, as required by TOP-001-4 R1. The TOP-001-4 R1 violation began on June 3, 2020, at 2:33 AM, when the night shift SO should have responded to the SCADA alarms and ended on June 3, 2020, at 4:17 AM, when night shift SO took action by attempting to close the breaker via SCADA control, for a total of one hour and 44 minutes. The root cause of the violations was attributed to lack of situational awareness in that the situation was not being properly managed by the night shift SO. The SO thought that since the tripping of the breaker didn’t result in any customer outages, the notifications to the RC and affected TOP were not required to be sent, nor did the SO send the forced outage notification to its RC. | These violations posed a moderate risk in aggregate and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In these instances, WACM failed to act to maintain the reliability of its TOP Area via its own actions or by issuing Operating Instructions, for one hour and 44 minutes, as required by TOP-001-4 R1; inform its RC and one impacted TOP of its actual operations that could result in an Emergency, for five hours and 20 minutes, as required by TOP-001-4 R8; and to perform the 30 minute notification specified in its RC’s outage coordination process, for five hours and 20 minutes, as required by IRO-017-1 R2. The 115kV transmission line associated with the thirteen hour and 28-minute forced outage was open-ended so the line through flow was diverted to parallel paths and the failure of one breaker could have de-energized two of the adjacent TOP’s substations. The failures described herein resulted in the RC and one affected TOP not being aware of the forced outage. Such failures could have resulted in the loss of up to 35 MW of load, based on the transformers that could have been affected by the outage. The failures could also have resulted in the RC and affected TOP performing inaccurate Operating Planning Analysis if either used an off-line power flow model or the outage components were not modeled in an on-line power flow tool, which could have delayed maintenance. However, as compensation, WACM’s SO shift turnover resulted in the next shift SO taking steps to resolve the issue. The issue was isolated to the action of the one night shift SO. In Real-time the on-line power flow tools would have identified actual and potential line exceedances, load loss and generation loss, based on the current status of the transmission system. As well, the open breaker would not have caused any additional loss of load compared to the loss of the line. An on-line power flow study would have indicated a distribution factor higher than normal for loss of parallel lines due to no flow-through of this line. Based on the line rating of 109 MVA, it is unlikely it would have a significant distribution factor compared to the parallel 230kV lines. In addition, no load was lost as a result of this failure or event. | To mitigate this violation, WACM has performed the following actions: 1) attempted to restore the transmission line; 2) called field maintenance personnel to investigate the cause of the line operation; 3) restored the 115 kV transmission line to service; 4) reviewed and updated the applicable internal procedures including: 115kV Line Restoration Guide; Emergency Line Restoration Standard Operating Procedure (SOP); Event Reporting Plan; WACM Desk Procedures and System Operator Shift Change Procedure; 5) ensured SOs reviewed the updated procedures; and 6) reviewed the event and discussed lessons learned at SO meetings. | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. WACM is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation.
2022-02-28 | NOC-2755 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | TOP | Settlement Agreement | Does Not Contest | No penalty (WECC2020024012, WECC2020024013, and WECC2020024014) | WECC2020024013 | TOP-001-4 | R8 | Moderate | High | Severe | Self-Report | 2020-10-01 | 6/3/2020 | 6/3/2020 | 5/12/2021 | 5/12/2021 | On October 1, 2020, WACM submitted a Self-Report notifying WECC as the Lead Regional Entity under an existing multi-region registered entity coordinated oversight agreement with MRO as the Affected Regional Entity, that as a Transmission Operator (TOP), it was in violation with TOP-001-4 R8. On June 3, 2020, at 2:02 AM a phase to ground fault occurred on a 115kV transmission line, that tripped a breaker, which resulted in the loss of that breaker and the open ended terminal of a multi-terminal 115kV transmission line. The breaker attempted to reclose automatically at 2:02 AM, but it tripped again. A SCADA alarm was generated and documented the trip and attempted reclosing of the breaker. However, the night shift System Operator (SO) was distracted did not recognize the visual and audible alarms for over two hours. At 4:17 AM, the SO attempted to close the breaker via SCADA control, but was unsuccessful. Maintenance was called to investigate the cause and a broken jumper was found approximately three miles from the terminal of the 115kV transmission line where the breaker tripped. The night shift SO completed the verbal shift change with the two incoming morning shift SOs. However, an internal interruption report and transmission log entry was not completed during the night shift SO’s shift. At 7:53 AM, WACM sent its Reliability Coordinator (RC) and affected TOP a notification of the event and the status of the unavailable Bulk Electric System (BES) equipment by sending a Clearance Switching Request Form and WACM initiated the process of switching to electrically isolate the faulted equipment. WACM completed the repairs, and the clearance was released at 3:08 PM. Removal switching was also completed, and the equipment was returned to service at 3:30 PM on June 3, 2020. During the thirteen hour and 28 minute outage of the 115kV transmission line, there was no loss of the potential 35 MW of load or less, depending on loading conditions during the event; nor were there any interruption of customer service. The night shift SO did not inform the RC and impacted TOP of its actual or expected operations that could have resulted in an Emergency, as required by TOP-001-4 R8. The TOP-001-4 R8 violation began on June 3, 2020 at 2:33 AM, when the night shift SO should have notified its RC and affected TOP of an abnormal system condition and ended at 7:53 AM when the morning shift SO notified the RC and affected TOP of the abnormal system condition, for a total of five hours and 20 minutes. The root cause of the violations was attributed to lack of situational awareness in that the situation was not being properly managed by the night shift SO. The SO thought that since the tripping of the breaker didn’t result in any customer outages, the notifications to the RC and affected TOP were not required to be sent, nor did the SO send the forced outage notification to its RC. | These violations posed a moderate risk in aggregate and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In these instances, WACM failed to: act to maintain the reliability of its TOP Area via its own actions or by issuing Operating Instructions, for one hour and 44 minutes, as required by TOP-001-4 R1; inform its RC and one impacted TOP of its actual operations that could result in an Emergency, for five hours and 20 minutes, as required by TOP-001-4 R8; and to perform the 30 minute notification specified in its RC’s outage coordination process, for five hours and 20 minutes, as required by IRO-017-1 R2. The 115kV transmission line associated with the thirteen hour and 28-minute forced outage was open-ended so the line through flow was diverted to parallel paths and the failure of one breaker could have de-energized two of the adjacent TOP’s substations. The failures described herein resulted in the RC and one affected TOP not being aware of the forced outage. Such failures could have resulted in the loss of up to 35 MW of load, based on the transformers that could have been affected by the outage. The failures could also have resulted in the RC and affected TOP performing inaccurate Operating Planning Analysis if either used an off-line power flow model or the outage components were not modeled in an on-line power flow tool, which could have delayed maintenance. However, as compensation, WACM’s SO shift turnover resulted in the next shift SO taking steps to resolve the issue. The issue was isolated to the action of the one night shift SO. In Real-time the on-line power flow tools would have identified actual and potential line exceedances, load loss and generation loss, based on the current status of the transmission system. As well, the open breaker would not have caused any additional loss of load compared to the loss of the line. An on-line power flow study would have indicated a distribution factor higher than normal for loss of parallel lines due to no flow-through of this line. Based on the line rating of 109 MVA, it is unlikely it would have a significant distribution factor compared to the parallel 230kV lines. In addition, no load was lost as a result of this failure or event. | To mitigate this violation, WACM has performed the following actions: 1) informed the RC and known impacted TOP of the forced outage; 2) provided an informal training to remind system operators of the need to make timely notifications to the RC and any potentially affected TOP and Balancing Authority (BA) within 30 minutes or as soon as possible; 3) designed and delivered a compliance related training activity for SOs that identified the required reporting to the RC; 4) reviewed and updated the applicable internal procedures including: 115kV Line Restoration Guide; Emergency Line Restoration SOP; Event Reporting Plan; WACM Desk Procedures and System Operator Shift Change Procedure; 5) ensured SOs reviewed the updated procedures; and 6) reviewed the event and discussed lessons learned at SO meetings. | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. WACM is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation.
2022-02-28 | NOC-2755 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | TOP | Settlement Agreement | Does Not Contest | No penalty (WECC2020024012, WECC2020024013, and WECC2020024014) | WECC2020024014 | IRO-017-1 | R2 | Moderate | Medium | Severe | Self-Report | 2020-10-01 | 6/3/2020 | 6/3/2020 | 5/12/2021 | 5/12/2021 | On October 1, 2020, WACM submitted a Self-Report notifying WECC as the Lead Regional Entity under an existing multi-region registered entity coordinated oversight agreement with MRO as the Affected Regional Entity, that as a Transmission Operator (TOP), it was in violation with IRO-017-1 R2 . On June 3, 2020, at 2:02 AM a phase to ground fault occurred on a 115kV transmission line, that tripped a breaker, which resulted in the loss of that breaker and the open ended terminal of a multi-terminal 115kV transmission line. The breaker attempted to reclose automatically at 2:02 AM, but it tripped again. A SCADA alarm was generated and documented the trip and attempted reclosing of the breaker. However, the night shift System Operator (SO) was distracted did not recognize the visual and audible alarms for over two hours. At 4:17 AM, the SO attempted to close the breaker via SCADA control, but was unsuccessful. Maintenance was called to investigate the cause and a broken jumper was found approximately three miles from the terminal of the 115kV transmission line where the breaker tripped. The night shift SO completed the verbal shift change with the two incoming morning shift SOs. However, an internal interruption report and transmission log entry was not completed during the night shift SO’s shift. At 7:53 AM, WACM sent its Reliability Coordinator (RC) and affected TOP a notification of the event and the status of the unavailable Bulk Electric System (BES) equipment by sending a Clearance Switching Request Form and WACM initiated the process of switching to electrically isolate the faulted equipment. WACM completed the repairs, and the clearance was released at 3:08 PM. Removal switching was also completed, and the equipment was returned to service at 3:30 PM on June 3, 2020. During the thirteen hour and 28 minute outage of the 115kV transmission line, there was no loss of the potential 35 MW of load or less, depending on loading conditions during the event; nor were there any interruption of customer service. The night shift SO did not perform the 30-minute forced outage notification specified in its RC’s Outage Coordination Methodology, as required by IRO-017-1 R2. The IRO-017-1 R2 violation began on June 3, 2020 at 2:33 AM when the SO was required to submit a forced outage notification to its RC and ended on June 3, 2020 at 7:53 AM when the morning shift SO submitted the forced outage notification to the RC, for a total of five hours and 20 minutes. The root cause of the violations was attributed to lack of situational awareness in that the situation was not being properly managed by the night shift SO. The SO thought that since the tripping of the breaker didn’t result in any customer outages, the notifications to the RC and affected TOP were not required to be sent, nor did the SO send the forced outage notification to its RC. | These violations posed a moderate risk in aggregate and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In these instances, WACM failed to: act to maintain the reliability of its TOP Area via its own actions or by issuing Operating Instructions, for one hour and 44 minutes, as required by TOP-001-4 R1; inform its RC and one impacted TOP of its actual operations that could result in an Emergency, for five hours and 20 minutes, as required by TOP-001-4 R8; and to perform the 30 minute notification specified in its RC’s outage coordination process, for five hours and 20 minutes, as required by IRO-017-1 R2. The 115kV transmission line associated with the thirteen hour and 28-minute forced outage was open-ended so the line through flow was diverted to parallel paths and the failure of one breaker could have de-energized two of the adjacent TOP’s substations. The failures described herein resulted in the RC and one affected TOP not being aware of the forced outage. Such failures could have resulted in the loss of up to 35 MW of load, based on the transformers that could have been affected by the outage. The failures could also have resulted in the RC and affected TOP performing inaccurate Operating Planning Analysis if either used an off-line power flow model or the outage components were not modeled in an on-line power flow tool, which could have delayed maintenance. However, as compensation, WACM’s SO shift turnover resulted in the next shift SO taking steps to resolve the issue. The issue was isolated to the action of the one night shift SO. In Real-time the on-line power flow tools would have identified actual and potential line exceedances, load loss and generation loss, based on the current status of the transmission system. As well, the open breaker would not have caused any additional loss of load compared to the loss of the line. An on-line power flow study would have indicated a distribution factor higher than normal for loss of parallel lines due to no flow-through of this line. Based on the line rating of 109 MVA, it is unlikely it would have a significant distribution factor compared to the parallel 230kV lines. In addition, no load was lost as a result of this failure or event. | To mitigate this violation, WACM has performed the following actions: 1) submitted a forced outage notification tool to the RC; 2) provided an informal training to remind system operators of the need to make timely notifications to the RC and any potentially affected TOP and BA within 30 minutes or as soon as possible; 3) designed and delivered a compliance related training activity for SOs that identified the required reporting to the RC; 4) designed and delivered a compliance related training activity for SOs relating to the RC's Outage Coordination Methodology and submission requirements; 5) reviewed and updated the applicable internal procedures including: 115kV Line Restoration Guide; Emergency Line Restoration SOP; Event Reporting Plan; WACM Desk Procedures and System Operator Shift Change Procedure; 6) ensured SOs reviewed the updated procedures; and 7) reviewed the event and discussed lessons learned at SO meetings. | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. WACM is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation.
2022-02-28 | NOC-2763 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | TOP | Settlement Agreement | Admits | 132000 | WECC2019021942 | TOP-001-4 | R13 | Moderate | High | Severe | Self-Report | 2019-07-29 | 4/17/2019 | 4/17/2019 | 8/31/2019 | 2/4/2020 | AZPS notified WECC that it was noncompliant with TOP-001-4 R13. On April 16, 2019, AZPS replaced a pair of non-CIP Energy Management System (EMS) frame firewalls as part of a planned outage change at the primary Control Center (PCC). Due to configuration issues, and uncoordinated troubleshooting efforts, on April 17, 2019, at 7:38 PM, the EMS lost visibility to remote thermal unit (RTU) and Inter-Control Center Communications Protocol (ICCP) data between AZPS and its Reliability Coordinator (RC) and neighboring entities. The data lapse impacted the performance of the Real-time Contingency Analysis (RTCA) tool which stopped solving due to the loss of the RTU data. The RTCA is an aspect of AZPS’s Real Time Assessment (RTA), and AZPS System Operators (SOs) and RC lost the ability to perform a manual RTA in accordance with its procedures. Thus, AZPS was unable to perform a Real-time assessment (RTA) which required an examination of existing and expected system conditions, conducted by collecting and reviewing immediately available data. In addition, AZPS notified its neighboring entities of the condition and specifically confirmed the loss of the ICCP data with its RC and other neighboring entities. AZPS’s Balancing Authority (BA) function notified its generation units to change to local control and maintain their current output. Since the SOs did not have visibility of the system including RTCA, the PCC monitored the system in Real-time via field personnel and managed the BA responsibilities through manual checkout every 15 minutes along with adjacent BAs. AZPS activated its CIP-009-6 Recovery Plan and identified lessons learned and updated the Recovery Plan to include a peer check. AZPS completed the required steps for CIP-009-6 R2 and R3, thus CIP-009-6 R1-R3 were not at issue. AZPS used a CIP head end firewall as an attempt to troubleshoot during the instant violation, but the failover did not require Change Management protocols. Therefore, WECC determined that AZPS did not have any additional instances of potential noncompliance with CIP-009-6 R1-R3 nor CIP-010-2 R1 associated with the instant violation. At 8:21 PM, AZPS restored connectivity between the router and the new EMS frame firewalls. At 9:44 PM, the EMS regained visibility and the RTCA began solving with the return of the RTU data. At 10:30 PM, the ICCP services were restored for EMS, improving the functionality of the RTCA solution. The EMS outage began at 7:38 PM and ended at 9:44 PM for a total of two hours and six minutes. The ICCP outage began at 7:38 PM and ended at 10:29 PM for a total of two hours and 51 minutes. The RTCA did not solve during the EMS outage of 2 hours and six minutes and the RTCA results were not verified during the ICCP outage of 2 hours and 51 minutes. The root cause of the violation was attributed to a lack of coordinated efforts in AZPS’s incident response when it did not follow established decision trees and its incident management procedure, which resulted in an EMS outage, ICCP outage and RTCA not solving. The violation began on April 17, 2019 at 8:09 PM, when AZPS did not ensure that an RTA was performed through its RTCA, and ended on April 17, 2019 at 11:35 PM, when AZPS was able to perform an RTA, for a total of three hours and 26 minutes (206 minutes over the 30-minute requirement). | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AZPS failed to ensure that an RTA was performed at least once every 30 minutes for a total of 206 minutes, as required by TOP-001-4 R13. AZPS’s primary Control Center and Real-time monitoring capabilities via SCADA were impacted by the issue. AZPS had peak demand greater than 7,000 MW, and nearly 3,000 miles of BES transmission lines. The data lapse failure resulted in AZPS losing its EMS visibility to the RTU, ICCP data and RTCA, which prevented the SOs from performing a manual RTA nor could the RC perform an RTA for AZPS. Further, the failure could have resulted in the unintended loss of BPS elements following a contingency. Additionally, during the outage, AZPS was also unable to fully perform BA functions for its stakeholders. However, as compensation, AZPS notified its neighboring entities of the condition and specifically confirmed the loss of the ICCP data with its RC and other neighboring entities. AZPS’s Balancing Authority (BA) function notified its generation units to change to local control and maintain their current output. Since the SOs did not have visibility of the system including RTCA, the PCC monitored the system in Real-time via field personnel and managed the BA responsibilities through manual checkout every 15 minutes along with adjacent BAs. | To mitigate this violation, AZPS has performed the following actions: 1) restored its data capabilities and ensured AZPS’ ability to perform a successful RTA; 2) held a Stand Down on the IT Computer Event Response Plan and the new IT End User communication plan to reinforce staff expectations which included the implementation of a Standing Order that all infrastructure changes to "Mission / Business / Safety critical systems must have change command;" 3) conducted formal cross-training between all parties involved in supporting the EMS application; 4) created an asset change management process to include: i. verify and document for an in-service device, its current function and configuration; ii. map the existing configuration for the in-service device with the replacing device iii. develop and/or update applicable System Test Plan and Test cases to meet the new device requirements and exercise of intended functionality iv. identify the monitoring and alerting functionality for the new device v. quality assurance process for all key tasks associated with this process and procedure(s) 5) moved outdated host files out of the primary directory; and 6) developed a procedure for when host files are to be pushed, which requires: i. a peer check be performed within the Real-Time System Support team ii. a peer check be performed with the EMS Duty Engineer. iii. once the push is complete, the RTSS validates push is successful iv. EMS Duty Engineer validates push is successful. | WECC reviewed AZPS's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination because it was effective in detecting the violation. WECC considered AZPS's compliance history and determined there were no relevant instances of noncompliance.