## non-CIP SNOP
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2022-04-28 | NOC-2770 | Texas RE | American Electric Power Service Corp as agent for AEP Texas Inc. and Public Service Company of Oklahoma (AEPSC) | NCR04006 | TOP | Settlement Agreement | Neither Admits nor Denies | 0 | TRE2019021504 | TOP-001-3 | R8 | Moderate | High | Severe | Compliance Audit | 2019-05-09 | 2018-03-20 | 3/20/2018 | 2020-11-17 | 2021-01-15 | During a compliance audit, Texas RE initially determined AEPSC was noncompliant with TOP-001-3 R1. However, based on the description of the issues provided, Texas RE subsequently determined that AEPSC was noncompliant with TOP-001-3 R8. In particular, on March 20, 2018, at 12:20 PM, AEPSC identified a consistent, non-converged solution in its Real-Time Contingency Analysis (RTCA). AEPSC did not communicate this information to its Reliability Coordinator (RC) in violation of TOP-001-3 R8, which requires that each Transmission Operator (TOP) shall inform its RC of its actual or expected operations that result in, or could result in, an Emergency. Prior to March 20, 2018, several transmission lines were out of service for approved construction and maintenance activities in the Del Rio, San Angelo, and Mesa Verde area. An additional forced outage on another transmission line resulted in only two 138 kV lines serving the area on March 20, 2018. Beginning at 10:58, the RC’s required RTCA indicated several thermal limit exceedances. As the available wind generation in the area declined, the RC was unable to automatically resolve the identified post-contingency thermal exceedances through a generation solution. Over the next few hours, AEPSC, the RC, and a neighboring TOP continuously coordinated to bring transmission facilities back into service to address the issue. Specifically, these ongoing communications occurred at 11:35, 11:46, 11:49, 12:11, 12:26, 14:08, and 14:24. In addition to these actions, AEPSC and its RC communicated regarding the development of a post-contingency load shed Transmission Outage Action Plan (TOAP) during the 11:46 call. While these communications were ongoing, at 10:29 and 14:29, AEPSC also placed a number of capacitor banks into service to bring up voltages in the area. Under the Coordinated Function Registration (CFR) agreement between AEPSC and its RC, the RC is the sole entity responsible for performing Real-time Assessments. Although the RC’s State Estimator and RTCA applications showed potential issues in the area, they did not specifically indicate post-contingency voltage collapse. While not required to perform periodic RTCAs, AEPSC’s process is to perform an RTCA for its TOP Area as an additional check on its system. As AEPSC worked with its RC and neighboring TOP to address transmission issues, AEPSC’s optional RTCA began to indicate a consistent, non-converged solution at 12:20. During its various, on-going communications regarding the issue, however, AEPSC did not specifically communicate complete information regarding the actual operational status of its system to its RC derived from its local RTCA information. At 14:33, a fault occurred due to ionized smoke from a nearby grass fire that resulted in a local voltage collapse and the loss of approximately 140 MW of load. The root cause of this noncompliance was inadequate processes and training regarding the need to communicate non-converged RTCA solutions to AEPSC’s RC. Specifically, although AEPSC had established communication protocols for communicating actual operational information regarding its system, such as RTCA results, it lacked specific, detailed steps for operators to track and communicate unsolved RTCA contingencies to its RC. This noncompliance started on March 20, 2018 at 12:20, when AEPSC first identified and then failed to communicate its optional RTCA’s non-converged RTCA solution to its RC, and ended on March 20, 2018 at 14:33, when a fault occurred resulting in a local voltage collapse. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. AEPSC failed to communicate the existence of the non-converged RTCA solution to its RC, depriving the RC of complete information about the actual operations of AEPSC’s system. However, AEPSC and its RC were in continuous communication throughout the event and taking actions to address post-contingency thermal exceedances in the area. Specifically, the RC and AEPSC were communicating to place transmission facilities back into service to alleviate identified post-contingency thermal exceedances in the area. In addition, AEPSC was in communication with its RC regarding contingency overload issues and had taken action to address them by placing a number of capacitor banks in service to increase system voltages in the area. Finally, the loss of load was caused by a combination of approved transmission outages in the area, a forced outage on an additional transmission facility, and a fault resulting from ionized smoke from a nearby grass fire. Throughout the issue, AEPSC, its RC, and neighboring TOP repeatedly communicated to attempt to address the specific capacity issues on the area’s transmission system. Conversely, AEPSC’s failure to communicate the specific results of its optional RTCA to its RC did not cause the event in question. | To mitigate this violation, AEPSC has: 1) Updated its processes to require that every unsolved contingency in the state estimator be logged in the Daily Operating Log (DOL), and created a standardized text template in the DOL to outline specific actions to be taken for RTCA unsolved contingencies in regards to notifications to the RC and time requirements; 2) Provided additional guidance to its reliability personnel during a staff meeting; 3) Provided on the job training task verifications for its reliability operators, including the assessment methodology for Real-time operations and notifications to RCs. The applicable training must be completed before an operator can perform System Control Center (SCC) functions independently; and 4) Conducted an extent of condition review of communication protocols notifications and actions taken with its RC for instances of invalid base case, unsolved contingency, or non-convergence with the RTCA tool; this extent of condition review did not detect any additional instances of noncompliance. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed AEPSC’s internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered AEPSC’s compliance history and determined there were no relevant instances of noncompliance. In addition to the moderate risk of the violation, Texas RE determined that although this violation did not cause a loss of load, the issue occurred during a load loss event and therefore it was inappropriate to process this violation through a streamlined disposition method. Texas RE further concluded, however, that a zero-dollar penalty is appropriate because AEPSC’s failure to communicate the results of its optional RTCA did not cause the loss of load event. In addition, AEPSC is not obligated to run an RTCA, and AEPSC’s decision to run an RTCA as an additional check enhances reliability. Because this violation stems from AEPSC’s failure to communicate complete information regarding its actual operations derived from its optional RTCA, AEPSC would not have a violation if it had elected not to run its optional RTCA altogether. Texas RE also considered the fact that AEPSC elected to address this violation by further enhancing its internal RTCA procedures, including communication processes with its RC, in lieu of terminating such activities in response to this issue.