## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2022-05-31 | NOC-2772 | SERC Reliability Corporation (SERC) | USACE - Savannah District (USACE-SAV) | NCR01361 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020861 and SERC2018020862) | SERC2018020861 | MOD-026-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-12-19 | 7/1/2018 (when USACE-SAV failed to meet the Implementation Plan of MOD-026-1 R2) | 12/30/2022 (when USACE-SAV will complete the excitation and turbine/governor control system model verification for the 20 generators and submits the data to its TP) | 12/30/2022 (when USACE-SAV will verify 100% of its units and submit model verification data to its TP) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-SAV was in violation of MOD-026-1 R2. USACE-SAV did not provide its Transmission Planner (TP) with verified generator excitation control system or plant volt/var control function model in accordance with the NERC Implementation Plan. USACE-SAV owns 20 hydro units, which range from 57.5 MVA to 85 MVA, with capacity factors ranging from .08 to .29. The total nameplate value of all USACE-SAV generation is 1,450 MVA. The MOD-026-1 R2 Implementation Plan required 30% of USACE-SAV’s applicable nameplate generation, or 447 MVA, be compliant on July 1, 2018. USACE-SAV did not have sufficient documentation to show any compliance. This violation started on July 1, 2018, when USACE-SAV failed to meet the Implementation Plan of MOD-026-1 R2 and, will end on December 30, 2022, when USACE-SAV completes the excitation and turbine/governor control system model verification for the 20 generators and submits that data to its TP. The cause of this violation was ineffective resource management (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-SAV is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, USACE-SAV, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineers’ South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed by this noncompliance is that the TP would not have accurate information on the generator excitation control system or plant volt/var control function to use for its planning models to assess BPS reliability. USACE-SAV owns and manages three hydro-electric dams that consist of 20 hydroelectric units that range from 57.5 MVA to 85 MVA, with a total output of 1,450 MVA and a low average annual capacity factor of 22%. Therefore, a failure to verify generator excitation control system or plant volt/var control function models of units this size would have limited impact on the reliability of the BPS. No harm is known to have occurred. | To mitigate this violation, USACE-SAV has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. This reorganization has been completed, the dedicated compliance team established, and communicated to relevant staff; 2) implemented a secure central repository for electronic evidence and documentation. The requirement to store compliance evidence and/or documents within this repository was communicated to the compliance team members; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-SAV hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-SAV hydropower generators. | SERC considered USACE-SAV’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-SAV was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-SAV was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-SAV requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2772 | SERC Reliability Corporation (SERC) | USACE - Savannah District (USACE-SAV) | NCR01361 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020861 and SERC2018020862) | SERC2018020862 | MOD-027-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-12-19 | 7/1/2018 (when USACE-SAV failed to meet the Implementation Plan of MOD-027-1 R2) | 12/30/2022 (when USACE-SAV will complete the turbine/governor control system model verification for the 20 generators and submits the data to its TP) | 12/30/2022 (when USACE-SAV will verify 100% of its units and submit model verification data to its TP) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-SAV was in violation of MOD-027-1 R2. USACE-SAV did not provide its Transmission Planner (TP) with verified turbine/governor and load control or active power/frequency control model in accordance with the NERC Implementation Plan. USACE-SAV owns 20 hydro units, which range from 57.5 MVA to 85 MVA, with capacity factors ranging from .08 to .29. The total nameplate value of all USACE-SAV generation is 1,450 MVA. The MOD-027-1 R2 Implementation Plan required 30% of USACE-SAV’s applicable nameplate generation, or 447 MVA, be compliant on July 1, 2018. USACE-SAV did not have sufficient documentation to show any compliance. This violation started on July 1, 2018, when USACE-SAV failed to meet the Implementation Plan of MOD-027-1 R2 and, will end on December 30, 2022, when USACE-SAV completes the turbine/governor control system model verification for the 20 generators and submits that data to its TP. The cause of this violation was ineffective resource management (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-SAV is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, the USACE-SAV, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineers’ South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This risk posed by this noncompliance is that the TP would not have accurate information on the turbine/governor and load control or active power/frequency control for its planning models to assess BPS reliability. USACE-SAV owns and manages three hydro-electric dams that consist of 20 hydroelectric units that range from 57.5 MVA to 85 MVA, with a total output of 1,450 MVA and a low average annual capacity factor of 22%. Therefore, a failure to verify the turbine/governor and load control or active power/frequency control of units this size would have limited impact on the reliability of the BPS. No harm is known to have occurred. | To mitigate this violation, USACE-SAV has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. This reorganization has been completed, the dedicated compliance team established, and communicated to relevant staff; 2) implemented a secure central repository for electronic evidence and documentation. The requirement to store compliance evidence and/or documents within this repository was communicated to the compliance team members; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-SAV hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-SAV hydropower generators. | SERC considered USACE-SAV’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-SAV was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-SAV was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-SAV requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2773 | SERC Reliability Corporation (SERC) | USACE - Mobile District (USACE-MOB) | NCR01359 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020181 and SERC2018020182) | SERC2018020181 | MOD-026-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-08-02 | 7/1/2018 (when USACE-MOB failed to meet the 30% NERC Implementation Plan requirement) | 12/30/2022 (when USACE-MOB will complete verification for 100% of its applicable units) | 12/30/2022 (when USACE-MOB will verify 100% of its units and submit model verification data to its TP) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-MOB was in violation of MOD-026-1 R2. USACE-MOB failed to provide its Transmission Planner (TP) with verified generator excitation control system or plant volt/var control function model in accordance with the NERC Implementation Plan. The MOD-026-1 R2 Implementation Plan required USACE-MOB to provide its TP with generator excitation control system or plant volt/var control function model, including documentation and data model, for 30% of its applicable units, or 305 MVA, by July 1, 2018, or 50% of its applicable units, or 508 MVA, by July 1, 2020. USACE-MOB failed to meet either of the milestones and is scheduled to perform the verification of all of its applicable units by December 20, 2022. This violation started on July 1, 2018, when USACE-MOB failed to meet the 30% NERC Implementation Plan requirements, and will end on December 30, 2022, when USACE-MOB completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-MOB is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, USACE-MOB, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, USACE-MOB’s failure to provide its TP with verified model data for 30% of its applicable generation, or 305 MVA, or 50% of its applicable generation, or 508 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-MOB is a small facility and total affected generation for this noncompliance is fourteen units, totaling 1,017 MVA, with a low average capacity factor of 32%. USACE-MOB will meet the requirement to provide its verified model data of 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-MOB has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation; 3) perform the MOD-026-1 model verification testing; and 4) submit model verification data to Transmission Planner for the applicable USACE-MOB hydropower generators. | SERC considered USACE-MOB’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-MOB was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-MOB was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-MOB requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2773 | SERC Reliability Corporation (SERC) | USACE - Mobile District (USACE-MOB) | NCR01359 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020181 and SERC2018020182) | SERC2018020182 | MOD-027-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-08-02 | 7/1/2018 (when USACE-MOB failed to meet the 30% NERC Implementation Plan requirement) | 12/30/2022 (when USACE-MOB will complete verification for 100% of its applicable units) | 12/30/2022 (when USACE-MOB will verify 100% of its units and submit model verification data to its TP) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-MOB was in violation of MOD-027-1 R2. USACE-MOB failed to provide its Transmission Planner (TP) with verified turbine/governor and load control or active power/frequency control model in accordance with the NERC Implementation Plan. The MOD-027-1 R2 Implementation Plan required USACE-MOB to provide its TP with turbine/governor and load control or active power/frequency control model, including documentation and data model, for 30% of its applicable units, or 305 MVA, by July 1, 2018, or 50% of its applicable units, or 508 MVA, by July 1, 2020. USACE-MOB failed to meet either of the milestones and is scheduled to perform the verification of all of its applicable units by December 30, 2022. This violation started on July 1, 2018, when USACE-MOB failed to meet the 30% NERC Implementation Plan requirements, and will end on December 30, 2022, when USACE-MOB completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-MOB is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, USACE-MOB, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, USACE-MOB’s failure to provide its TP with verified model data for 30% of its applicable generation, or 305 MVA, or 50% of its applicable generation, or 508 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-MOB is a small facility and total affected generation for this noncompliance is fourteen units, totaling 1,017 MVA, with a low average annual capacity factor of 32%. USACE-MOB will meet the requirement to provide its verified model data of 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-MOB has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation; 3) perform the MOD-027-1 model verification testing; and 4) submit model verification data to Transmission Planner for the applicable USACE-MOB hydropower generators. | SERC considered USACE-MOB’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-MOB was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-MOB was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-MOB requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2774 | SERC Reliability Corporation (SERC) | USACE - Wilmington District (USACE-WILM) | NCR01364 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2020023113 and SERC2020023114) | SERC2020023113 | MOD-027-1 | R2 | Minimal | Medium | Severe | Self-Report | 2/25/2020 | 7/1/2018 (when USACE-WILM failed to meet the 30% NERC Implementation Plan requirement) | 12/30/2022 (when USACE-WILM will complete verification for 100% of its applicable units) | 12/30/2022 (when USACE-WILM will verify 100% of its units and submit model verification data to its TP) | TBD | USACE-WILM notified SERC that it was in violation of MOD-027-1 R2. USACE-WILM failed to provide its Transmission Planner (TP) a verified turbine/governor and load control or active power/frequency control model in accordance with the NERC Implementation Plan. The MOD-027-1 R2 Implementation Plan required USACE-WILM to provide its TP with a verified turbine/governor and load control or active power/frequency control model, including documentation and data model, for 30% of its total applicable units, or 99 MVA, by July 1, 2018, or 50% of its applicable units, or 164 MVA, by July 1, 2020. USACE-WILM is scheduled to perform the verification of all its applicable units by December 30, 2022 and will meet the 100% requirement prior to the NERC Implementation Plan deadline of July 1, 2024. This violation started on July 1, 2018, when USACE-WILM failed to meet the 30% NERC Implementation Plan requirement, and will end on December 30, 2022, when USACE-WILM completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-WILM is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, the USACE-WILM, along with the U.S. Army Corps of Engineer’s South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). USACE-WILM’s failure to provide its TP verified model data for 30% of its applicable generation, or 99 MVA, or 50% of its applicable generation, or 164 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-WILM is a small hydropower facility and the total affected generation for this noncompliance is seven units totaling 327 MVA of applicable units with a low average annual capacity factor of 16%. USACE-WILM will meet the requirement to provide verified model data for 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-WILM has or will complete the following actions: 1) reorganized its technical manpower, to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation, which was communicated to the compliance team members on October 10, 2018; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-WILM hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-WILM hydropower generators. | SERC considered USACE-WILM’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 1, 2021. However, USACE-WILM was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-WILM was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-WILM requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2774 | SERC Reliability Corporation (SERC) | USACE - Wilmington District (USACE-WILM) | NCR01364 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2020023113 and SERC2020023114) | SERC2020023114 | MOD-026-1 | R2 | Minimal | Medium | Severe | Self-Report | 2/25/2020 | 7/1/2018 (when USACE-WILM failed to meet the 30% NERC Implementation Plan requirement) | 12/30/2022 (when USACE-WILM will complete the verification for 100% of its applicable units) | 12/30/2022 (when USACE-WILM will verify 100% of its units and submit model verification data to its TP) | TBD | USACE-WILM notified SERC that it was in violation of MOD-026-1 R2. USACE-WILM failed to provide, for each applicable unit, a verified generator excitation control system or plant volt/var control function model including documentation and data to its Transmission Planner (TP) in accordance with the NERC Implementation Plan. The MOD-026-1 R2 Implementation Plan required USACE-WILM to provide its TP with a verified generator excitation control system or plant volt/var control function model, for 30% of its total applicable units, or 99 MVA, by July 1, 2018, or 50% of its applicable units, or 164 MVA, by July 1, 2020. USACE-WILM is scheduled to perform the verification of all its applicable units by December 30, 2022 and will meet the 100% requirement prior to the NERC Implementation Plan deadline of July 1, 2024. This violation started on July 1, 2018, when USACE-WILM failed to meet the 30% NERC Implementation Plan requirement, and will end on December 30, 2022, when USACE-WILM completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-WILM is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, the USACE-WILM, along with the U.S. Army Corps of Engineer’s South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). USACE-WILM’s failure to provide its TP verified model data for 30% of its applicable generation, or 99 MVA, or 50% of its applicable generation, or 164 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-WILM is a small hydropower facility and the total affected generation for this noncompliance is seven units totaling 327 MVA of applicable units with a low average annual capacity factor of 16%. USACE-WILM will meet the requirement to provide verified model data for 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-WILM has or will complete the following actions: 1) reorganized its technical manpower, to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation, which was communicated to the compliance team members on October 10, 2018; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-WILM hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-WILM hydropower generators. | SERC considered USACE-WILM’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 1, 2021. However, USACE-WILM was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-WILM was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-WILM requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2775 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC or the Entity) | NCR00824 | TO | Settlement Agreement | Admits | $82,000 | MRO2018020131 | FAC-009-1 | R1 | Moderate | Medium | Severe | Self-Report | 2018-06-18 | 2007-06-18 | 2020-02-04 | 2021-03-30 | 2021-04-30 | On June 18, 2018, the Entity submitted a Self-Report stating that, as a Transmission Owner, it was noncompliant with FAC-009-1 R1. The Entity reported that it had ratings documentation errors for components of its Facilities that constituted a noncompliance with FAC-009-1 R1, as the Facility Ratings (FR) were not consistent with its associated Facility Ratings Methodology (FRM). The Entity identified 21 FRs errors during an internal review. The Entity subsequently performed an Extent of Condition (EOC), discovering an additional 68 FRs errors, for a total of 89 FRs errors. Those errors affected the most limiting element of a Facility, causing the overall FRs to be either higher or lower than the rating of the most limiting element. The cause of the noncompliance was the Entity’s inadequate process for reviewing ratings and facility components. For its affected jumper components, the Entity failed to consider industry standards for substation bus design (IEEE Std. 605-2008) and for reducing equipment loss of life (IEEE Std. C57.19) as required by its FRM. Additionally, for its other affected Facility components, the Entity failed to update the primary drawings used for FRs after changes to the equipment were made in the field. The noncompliance began on June 18, 2007, the date the standard became enforceable, and ended on February 4, 2020, when the Entity corrected all of the component and FRs. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Operating a Facility at a rating that is above the rating of the most limiting element could result in damage to the limiting element and possible failure, leading to an outage of the Facility. Upon review of the EOC and other information provided by the Entity, MRO determined the risk is moderate. The Entity identified 89 transmission lines with Facility component rating errors that resulted in a FR change. Of the 89 Facilities, 62 had erroneous FRs that were higher than the actual rating of the most limiting element, resulting in a FR decrease when the error was corrected. Six of the 62 Facilities with ratings decreases were 345-kV Facilities. The most significant of these six was a Facility with a 5% summer normal and 20% winter normal rating decrease. Additionally, the duration of the issues was over 12 years. However, MRO determined that the issue did not pose a serious or substantial risk to the BPS. Of the six years of historical power flows and four years of temperature data (for dynamic ratings) that were reviewed, none of the flows exceeded any of the 89 adjusted FRs, limiting the actual risk posed to the BES. Also, 55 of the 62 FR decreases were caused by jumper component ratings issues. The jumper ratings used by the Entity allowed for operation up to 100 degrees Celsius and were consistent with the manufacturer documentation for the conductor. However, the Entity’s FRM required consideration of industry standards for substation bus design (IEEE Std. 605-2008) and for reducing equipment loss of life (IEEE Std. C57.19). The consideration of those two industry standards resulted in a reduction of the operating temperature limit to 90 degrees Celsius. The risk associated with these 55 ratings decreases is limited as the jumper conductor ratings were valid per manufacturer specifications. The jumper issue was the cause of three of the six 345-kV facility ratings decreases. Further, the 27 FR increases did not pose any risk of overloading the Facilities as they resulted in overly conservative operation of the Facilities. No harm is known to have occurred. | To mitigate this violation, the Entity: 1) adjusted all FRs changes for BES facilities with its Control Center and Reliability Coordinator; 2) enhanced substation engineering quality assurance review checklists were developed and complete; 3) trained personnel on the enhanced quality assurance review checklist; 4) completed historical documentation reviews for all remaining BES Transmissions Facilities; 5) completed nameplate reviews for all 161kV and 345kV substations; 6) completed pre-commission checklists to identify and actively communicate design changes during construction; and 7) instituted annual field reviews and completed reviews for 2018 and 2019. MRO has verified the completion of all mitigation activity. | MRO considered the Entity’s compliance history and determined that there were no relevant instances of noncompliance. MRO provided mitigating credit for cooperation, self-reporting, admission, settlement, and the internal compliance program.