## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2022-06-30 | NOC-2776 | Texas Reliability Entity (Texas RE) | Bryan Texas Utilities (BTU) | NCR04022 | TO | Settlement Agreement | Neither Admits nor Denies | $39,000 (for TRE2020023338 and TRE2020023339) | TRE2020023338 | FAC-009-1 | R2 | Moderate | Medium | Severe | Compliance Audit | 2020-04-30 | 2007-06-28 | 2021-10-28 | 2022-01-19 | 2022-02-03 | Texas RE determined BTU was noncompliant with FAC-009-1 R2. Specifically, BTU failed to provide accurate Facility Ratings data to its associated Reliability Coordinator (RC), the Electric Reliability Council of Texas, Inc. (ERCOT). After inconsistencies were identified in Facility Ratings data sampled during a Compliance Audit, BTU conducted an Extent of Condition (EOC) review, and a total of nine Facilities were identified with a Facility Rating that was inconsistent with the Rating reported to ERCOT. During the noncompliance, FAC-009-1 R2 was replaced by FAC-008-3 R8 and FAC-008-5 R8, which are both also applicable to the noncompliance. The root cause of this violation was an overreliance on stale field verifications, and a failure to adequately communicate with neighboring utilities regarding equipment Ratings for jointly owned Facilities. More specifically, BTU did not have a policy of checking and verifying Facility Ratings, including verification of conductor type, when the opportunity was available such as during additional construction and maintenance and when coordinating with neighboring utilities. This noncompliance began June 28, 2007, when BTU registered as a Transmission Owner, and ended October 28, 2021, when BTU recalculated all applicable Facility Ratings in accordance with its FRM and reported the correct Ratings to ERCOT. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A lack of accurate Facility Ratings and Equipment Ratings could result in overloading on equipment, potentially damaging the affected Facilities, and resulting in unanticipated outages. BTU is a municipally-owned electric utility that serves the citizens of Bryan, rural Brazos County, and portions of Burleson and Robertson Counties. BTU serves approximately 48,500 electric customers, has approximately 2,039 miles of distribution line, and 129 miles of Transmission line. BTU’s Transmission system represents approximately 0.5% of the ERCOT system peak load. Despite BTU’s small size and overall small potential impact to the BPS, this violation is aggravated by the length of time for which these instances of noncompliance occurred, and by the high percentage of Facilities affected. BTU had a total of nine of 29 Facilities (29%) with erroneous Ratings recorded with the RC, representing violations of FAC-009-1 R2. For five of these nine Facilities, BTU was unable to identify the date the erroneous Rating was provided to ERCOT. However, the risk was mitigated by the extent of the discrepancies between the reported and actual Rating. In particular, of these nine erroneous ratings, in only two instances the Rating reported to ERCOT was higher than the actual Rating. In the first of those instances, the discrepancy was 120 MVA (32%), and in the second, it was 31 MVA (14.4%). In the remaining seven instances of noncompliance, the Facility Rating reported to ERCOT was lower than the actual Rating by an average by -40.3 MVA (13.9%). No harm is known to have occurred. | To mitigate this violation, BTU has performed the following actions: 1) submitted revised information to ERCOT to correct the erroneous Facility Ratings in the ERCOT Network Operations Model; 2) conducted a full EOC review of all of BTU’s Transmission Facilities and associated elements; 3) revised its most limiting series element (MLSE) spreadsheet to present a single column for MLSE ratings to avoid confusion; 4) implemented Facility Ratings Checklists for Facility Rating submissions and/or changes to BTU’s MLSE spreadsheet; and 5) implemented a policy that field verifications will be performed during future construction, maintenance activities, and periodically in accordance with BTU’s Facility Rating process. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed BTU's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. BTU did not receive mitigating credit for self-reporting because the violation was discovered during a Compliance Audit. Texas RE considered BTU’s compliance history and determined there were no relevant instances of noncompliance.
2022-06-30 | NOC-2776 | Texas Reliability Entity (Texas RE) | Bryan Texas Utilities (BTU) | NCR04022 | TO | Settlement Agreement | Neither Admits nor Denies | $39,000 (for TRE2020023338 and TRE2020023339) | TRE2020023339 | FAC-009-1 | R1 | Moderate | Medium | Severe | Compliance Audit | 2020-04-30 | 2011-04-25 | 2021-10-28 | 2022-01-19 | 2022-02-03 | Texas RE determined BTU was noncompliant with FAC-009-1 R1. Specifically, BTU failed to calculate Facility Ratings for its solely and jointly owned Facilities in accordance with BTU’s Facility Ratings Methodology (FRM). After inconsistencies were identified regarding the Equipment Ratings provided with Facility Ratings data sampled during a Compliance Audit, BTU conducted an Extent of Condition (EOC) review, and a total of nine Facilities were identified with Facility Rating that were inconsistent with the FRM due to a misidentification of the most limiting series element (MLSE). During the noncompliance, FAC-009-1 R1 was replaced by FAC-008-3 R6 and FAC-008-5 R6, which are both also applicable to the noncompliance. The root cause of this violation was an overreliance on stale field verifications, and a failure to adequately communicate with neighboring utilities regarding equipment Ratings for jointly owned Facilities. More specifically, BTU did not have a policy of checking and verifying Facility Ratings, including verification of conductor type, when the opportunity was available such as during additional construction and maintenance and when coordinating with neighboring utilities. This noncompliance began on April 25, 2011, when BTU first incorrectly calculated the applicable Facility Ratings for its solely and jointly owned Facilities, and ended on October 28, 2021, when BTU recalculated and recorded all applicable Facility Ratings in accordance with its FRM. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A lack of accurate Facility Ratings and Equipment Ratings could result in overloading on equipment, potentially damaging the affected Facilities, and resulting in unanticipated outages. BTU is a municipally-owned electric utility that serves the citizens of Bryan, rural Brazos County, and portions of Burleson and Robertson Counties. BTU serves approximately 48,500 electric customers, has approximately 2,039 miles of distribution line, and 129 miles of Transmission line. BTU’s Transmission system represents approximately 0.5% of the Electric Reliability Council of Texas, Inc. (ERCOT) system peak load. Despite BTU’s small size and overall small potential impact to the BPS, this violation is aggravated by the length of time for which these instances of noncompliance occurred, and by the high percentage of Facilities affected. BTU had a total of nine of 29 Facilities (29%) with erroneous Ratings recorded in BTU’s internal MLSE Spreadsheet, representing violations of R6. However, the risk was mitigated by the fact that the discrepant Facility Ratings were lower than the corrected Facility Ratings and that the Reliability Coordinator received the correct Facility Ratings for five out of the nine Facilities at issue. Specifically, in all nine of these instances, the Facility Rating recorded in BTU’s MLSE Spreadsheet was lower than the actual Facility Rating. The greatest deviation between the value in BTU’s MLSE Spreadsheet and the actual Facility Rating occurred in two instances that were each 247.6 MVA (50%), and the average deviation of all of the deviations was 137.7 MVA (34%). Despite the fact that BTU’s internal MLSE Spreadsheet contained erroneous Ratings for these nine Facilities, the correct rating was nevertheless reported to the Reliability Coordinator, ERCOT, for five of these nine Facilities. No harm is known to have occurred. | To mitigate this violation, BTU has performed the following actions: 1) modified its internal MLSE spreadsheet to identify the correct element and rating for each of the previously incorrect Facility Ratings; 2) conducted a full EOC review of all of BTU’s Transmission Facilities and associated elements; 3) revised its MLSE spreadsheet to present a single column for MLSE ratings to avoid confusion; 4) implemented Facility Ratings Checklists for Facility Ratings submissions, and/or changes to BTU’s MLSE spreadsheet; and 5) implemented a policy that field verifications will be performed during future construction, maintenance activities, and periodically in accordance with BTU’s Facility Rating process. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed BTU's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. BTU did not receive mitigating credit for self-reporting because the violation was discovered during a Compliance Audit. Texas RE considered BTU’s compliance history and determined there were no relevant instances of noncompliance.