## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2022-10-31 | NOC-2786 | SERC Reliability Corporation (SERC) | Ameren Missouri | NCR10248 | GO | Settlement Agreement | Neither Admits nor Denies | 63000 | SERC2020024093 | FAC-008-3 | R6 | Moderate | Medium | Severe | Compliance Audit | 2020-10-16 | 2020-03-09 | 2021-01-27 | 2022-01-12 | TBD | SERC determined that Ameren Missouri, as a Generator Owner, was in violation of FAC-008-3 R6. Ameren Missouri failed to have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology (FRM). During a Compliance Audit conducted from June 1, 2020 to October 16, 2020, SERC auditors requested evidence of compliance for five generating units in its initial sampling request. Of the five units provided, Ameren Missouri made element rating changes after receiving the sampling request for three of the units. Because Ameren Missouri had identified element rating errors and made changes on three out of five units, the audit team sampled five more generation Facilities. Of the five generation units sampled in the additional request, four of the units had element rating errors and Ameren Missouri made element rating changes after receiving the additional sampling request. None of the element rating errors reviewed affected the Most Limiting Element and Facility Rating. The errors occurred during the implementation of the mitigation plan for SERC2017018436. In that mitigation plan, Ameren Missouri completed a walk-down of 100% of its Facilities to ensure that it correctly identified all elements and established element ratings and the overall Facility Rating in accordance with its FRM. After the walk-down was completed on December 14, 2018, Ameren Missouri engaged a contractor in June 2019 to strengthen its internal controls as an additional step in the mitigation plan in SERC2017018436. The contractor was hired to conduct a review of Ameren Missouri’s compliance with various NERC Standards including FAC-008. The contractor recommended that Ameren Missouri implement two programmatic changes. The first recommendation was to adopt the same ratings methodology used by its affiliated registered entity for the appropriate temperature rise for exposed, outdoor conductors. The second recommendation was to add the MVA rating for each element on all of the documents. Given the number of units involved and the number of elements per unit, Ameren Missouri hired an engineering consulting firm to calculate the new ratings, update all of the one line diagrams, and to perform an independent review of these calculations and updates. In preparing the revised documentation for submittal to the SERC audit team for review as part of the sampling request, Ameren Missouri discovered the engineering consultant made a number of errors in performing the work. If Ameren Missouri had conducted its own independent review of the documentation upon receipt from the engineering consultant, Ameren Missouri should have identified the errors prior to implementation. On August 13, 2020, upon discovery of the incorrect ratings, Ameren Missouri began a two phased review of the Facilities Rating documentation for all 63 facilities. The two independent review teams included experienced Ameren Missouri employees. The first team consisted of two employees responsible for reviewing the documentation to identify element or rating discrepancies between the Visio diagrams and the Maximum Equipment Ratings one line diagrams. The other team of two employees verified that the elements depicted on the documentation matched the photographs taken during previous site walk downs and that the ratings were correct based on calculations, nameplates, and tables. Ameren Missouri identified errors in the documentation at 53 of the 63 generating units. Ameren Missouri identified 225 incorrect element ratings. Two of the incorrect ratings resulted in the identification of incorrect Facility Ratings. In each instance, the Facility Rating increased by 16.3%. Ameren Missouri changed both ratings to an incorrect rating on March 9, 2020 and corrected the ratings on October 21, 2020. This violation started on March 9, 2020, when Ameren Missouri changed both Facility Ratings to an incorrect rating, and ended on January 27, 2021, when Ameren Missouri corrected all of the incorrect element ratings. The cause of the violation was ineffective contractor oversight (A4B1). Ameren Missouri failed to review the contractor’s work prior to the implementation of changes deemed necessary by the contractor. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. Ameren Missouri’s failure to accurately document the most limiting Facility Ratings increased the potential for it to operate generation Facilities in excess of their capacity rating, thereby creating the opportunity for equipment damage and Facility outages. The risk was elevated because Ameren Missouri failed to have an effective process for collecting, calculating, tracking, and validating Facility Rating information. At the time of the violation, Ameren Missouri did not have any processes or procedures for contractor oversight. Ameren Missouri accompanied the contractor during site walk downs and held regular meetings with the contractor to review progress and address questions. Ameren Missouri performed spot checks of the data during the engagement but did not conduct a review of the final documentation. Ameren Missouri trusted the contractor's attestation that the contractor accurately performed an independent review. Ameren Missouri identified errors in the documentation at 53 of the 63 generating units. Ameren Missouri identified 225 incorrect element ratings. Two of the incorrect ratings resulted in the identification of incorrect Facility Ratings. In each instance, the Facility Rating increased by 16.3%. | To mitigate this violation, Ameren Missouri has performed the following actions: 1) corrected all incorrect element ratings and Facility Ratings; 2) updated Facility Ratings procedure to add a control to require an independent review of changes to Facilities Ratings documentation by a qualified Ameren Missouri Engineer which will enable Ameren Missouri to identify and correct any errors prior to implementing changes to Facility Rating documentation and notified affected personnel via email of the changes in the revised FAC-008 procedure documents. The review will consist of 100% review of changes that are made/performed after the documents are completed; 3) developed and implemented a guide for performing FAC-008 independent review; 4) included a provision in its FAC-008 Procedure where after the independent review, it will provide feedback to the contractor or Ameren engineer on their performance; 5) communicated/provided training on the guide for performing FAC-008 independent review and the FAC-008 post independent review feedback to corporate and business line personnel with responsibility for compliance with FAC-008; 6) performed a Lessons Learned on this FAC-008 matter that will be communicated to corporate and business line personnel with responsibility for compliance with Reliability Standards across Ameren to all registrations; 7) conducted refresher training/communication on its NERC and Regional Entity Mandatory Reliability Standards Compliance Policy re-emphasizing the obligations for corporate and business line personnel with responsibility for compliance with Reliability Standards. This action will be performed electronically and will require the recipient to acknowledge that they have read and understand said policy; 8) developed and implemented a process to outline expectations for change management within the enterprise Reliability Standards compliance program; and 9) communicated/provided training on expectations for change management process to corporate and business line personnel with responsibility for compliance with Reliability Standards. | SERC reviewed Ameren Missouri’s internal compliance program and considered it to be a neutral factor in the penalty determination. SERC applied mitigating credit for cooperation because Ameren Missouri was cooperative throughout the investigation and enforcement process relating to this violation by providing timely, detailed, thoughtful, organized and thorough responses to its inquiries. SERC encourages this behavior and the level of cooperation demonstrated by Ameren Missouri. SERC considered Ameren Missouri’s FAC-008-3 R6 compliance history in determining the penalty. SERC considered Ameren Missouri’s compliance history to be an aggravating factor in the penalty determination. This violation is a repeat of NERC Violation ID SERC2017018436. Specifically, in SERC2017018436, Ameren Missouri failed to implement a change control process to verify element changes and that such changes were reflected in its ratings database and substation one-line diagrams. As part of the mitigating activities in the prior instance, Ameren Missouri revised its procedure to include a verification process to validate Facility Ratings, required an Independent Review to verify accuracy of Ratings, and bolstered its existing change management process to better define the types of design changes that warrant facility rating document updates. As part of the change management mitigating step, Ameren Missouri hired a contractor which miscalculated the new ratings that resulted in this violation. The prior mitigation was unsuccessful because Ameren Missouri accepted the contractor’s recommendations and implemented the changes to the ratings without independently reviewing and validating the contractor’s work, which resulted in this violation.