## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2023-06-29 | NOC-2812 | SERC Reliability Corporation (SERC) | Associated Electric Cooperative, Inc. (AECI) | NCR01177 | TO | Settlement Agreement | Neither Admits nor Denies | $42,000 | 2021-00393 | FAC-009-1 | R1 | Moderate | Medium | Lower | Self-Report | 2021-05-27 | 2007-06-18 | 2022-07-11 | 11/29/2023 (Expected Completion Date) | TBD | Instance 1: AECI notified SERC that it was in violation of FAC-008-3 R6. AECI failed to have a Facility Rating that was consistent with its associated Facility Ratings methodology for a single Facility. SERC determined that this noncompliance began under FAC-009-1 R1 and spanned to FAC-008-5 R6. On April 13, 2021, AECI placed a 161 kV network transmission circuit back in service following the completion of part of a substation rebuild project. The rebuild project consists of several phases of construction, with completion scheduled for July 2022. During weekly meetings to review details of the project and prior to the April 13, 2021 energization, AECI personnel contacted the member Generation and Transmission Cooperative (G&T) and verified that the G&T would reuse existing bus work and jumpers for this phase of the project. On May 5, 2021, after energization, AECI requested confirmation that there had been no changes to any bus conductors and jumpers during this phase of construction. The project did not include jumper modifications for this Facility. Personnel went out in the field and incorrectly verified that the jumper size matched the specification identified by the contractor that provided engineering services for the project. Once G&T personnel received confirmation that the jumpers matched the engineer’s specifications, the G&T responded to AECI that it made no changes to the Facility's jumpers. However, on May 27, 2021, during a review of engineering drawings, the G&T identified a possible issue related to the conductor size, which led the G&T to question the jumpers installed by the contractor. The G&T discovered that the third-party contractor hired for construction and inspection of the Facilities did replace a jumper. The contractor deviated from the plans and installed a jumper with a slightly larger physical diameter and lower temperature rating than the existing jumper. The replacement jumper wire installed by the contractor became the most limiting element of the transmission circuit and reduced Facility capacity by 4%. AECI did not exceed the correct Facility Rating. For the extent of condition (EOC) assessment, AECI and the G&T verified all Facility Ratings associated with equipment impacted during the substation rebuild via a field verification. The high temperature conductor is unique to the specific circuit of the noncompliance and is not present at any other location on the AECI transmission system. The cause of the noncompliance was ineffective project management. The contractor failed to install the jumper that the project documentation specified and AECI failed to review the changes before implementation. Instances 2-6: On February 14, 2022, AECI submitted finding updates for four additional instances. Instance 2: On September 27, 2021, during construction, a contractor hired by one of the G&Ts identified a discrepancy between drawings and existing bus work at the same substation described in Instance 1. The legacy drawings correctly identified the 3.5” bus work. The Facility Rating issue occurred due to an error in the grouping of a pair of transformers and a section of bus in the asset management system. The bus work that carries both transformers was incorrectly identified as 5” for the equipment group in the asset management system but was confirmed as 3.5” in the field. The in-service date of the 3.5” bus work was prior to June 18, 2007. On September 27, 2021, AECI corrected the rating within AECI's asset management system. AECI uses ambient adjusted ratings. The incorrect Facility Rating included temperature breakpoints from 68 to 104 degrees Fahrenheit. The incorrect Facility Rating was limited by another piece of equipment that was rated at 836 MVA for those breakpoints. The correct Facility Rating was limited by the 3.5” bus work which ranged from 790 MVA at the 68 degree breakpoint to 649 MVA at the 104 degree breakpoint. The percent derate for the normal rating ranged from 5.5% to 22.4% at those breakpoints. AECI did not exceed the correct Facility Rating. For the EOC assessment, AECI and the G&T personnel reviewed other substations with dual transformer groups and did not identify any that converge to a single section of bus work similar to the identified noncompliance. The cause of the noncompliance was inadequate controls. There was not an internal control in place that would have detected the incorrect entry in the G&T’s asset management system. Instance 3: On August 23, 2021, during a review of spare equipment for certain transmission Facilities, a G&T identified a switch at a substation for a 161 kV network line that had an inaccurate rating in the G&T’s asset management system. The rating established in the database was 4000 amps, however, the nameplate was 3000 amps. The updated equipment rating derated the line by 2.6%. The G&T did not exceed the correct Facility Rating. For the EOC assessment, G&T personnel inspected the substation in its entirety for equipment rating deviations. Personnel did not identify any additional deviations. The cause of the noncompliance was a deficient process. Personnel entered the incorrect rating into the Facility Ratings database during the previous FAC-009 mitigation plan. This led to an incorrect equipment rating in the asset management database. AECI's process lacked steps for verifying equipment rating change impacts before making changes, steps for communicating and coordinating temporary rating changes with System Operations, and quarterly reviews of Facility Rating database requests. Instance 4: On October 1, 2021, during a review of spare equipment, a G&T identified five inaccurate equipment ratings that impacted overall Transmission Facility Ratings. The five incorrect Facility Ratings resulted in a 21% derate and uprates of 5%, 18%, 30%, and 41%. The incorrect Facility Ratings date back to before June 18, 2007. AECI did not exceed the correct Facility Rating. For the EOC assessment, the G&T conducted a field verification of all current transformers (CT) of the G&T’s Bulk Electric System (BES) Transmission Facilities. The G&T’s errors identified during the Transmission resiliency project were limited to CTs. During the previous mitigation plan, the G&T performed walkdowns with substation personnel which may not have had the correct skill set to verify how CTs were wired in the field and thus did not identify these issues during the prior walkdown. The G&T reviewed drawings and equipment manuals to determine the full ratings of the CT’s and the ratio being used. All other equipment was field verified by appropriate substation personnel. The cause of the noncompliance was inadequate internal controls. G&T personnel entered the data into the G&T’s asset management system from drawings that contained inaccurate information. There were drafting errors and copy and paste issues when creating record drawings from field drawings. When these errors occurred, the G&T hand drew most system protection drawings and handed them over to a drafter to be entered into computer-aided design (CAD) system. The G&T’s post review process was lacking during that time. In 2015, the G&T began to create drawings in CAD and would then send those to the drafters electronically. As part of this new process, the G&T implemented a post drawing review process control to catch these types of errors. Instance 5: AECI maintains a Modeling and Network Transmission Information System (MANTIS) database of transmission equipment. On August 19, 2019, a transmission planner running the annual TPL dynamics assessment notified the MANTIS team that a G&T owns two circuit breakers at a neighboring entity's substation. The notification included a recommendation to confirm this information either internally or with the G&T. The G&T verified that it owned two breakers, four switches, and associated equipment at that substation. AECI and the G&T had not modeled this equipment as AECI-owned equipment in MANTIS or the system model. On November 5, 2020, the MANTIS team requested the G&T to provide the equipment ratings in the asset management system and on December 3, 2020, the MANTIS team confirmed the proper equipment was in the asset management system. On January 13, 2021, the MANTIS team reached out to the neighboring entity to coordinate the required modeling changes to address the ownership issue. On August 29, 2021, the neighboring entity replied to the MANTIS team to coordinate ratings for the modeling changes. On October 25, 2021, the MANTIS team pushed the ratings changes, which included derates, to the production MANTIS environment. At that time, the G&T discovered that the MANTIS team did not account for the CTs associated with this equipment from the time the G&T provided the data in November 2020, until October 25, 2021. AECI uses ambient adjusted ratings. The normal rating derate percentage ranged from 40% at the lowest temperature breakpoint to 20% at the highest temperature breakpoint. AECI did not exceed the correct Facility Rating. The cause of the noncompliance was an inadequate asset identification process. The process did not include steps that the database team would coordinate and confirm ownership with the G&T and neighboring entity on ties and jointly owned facilities when they are being updated or modified in the database. For the EOC assessment, all AECI BES ties in which equipment in a substation is owned by more than one entity will be reviewed with the G&Ts and neighboring entities to ensure the proper ownership is documented and a determination of correct Facility Ratings if additional G&T owned equipment is identified. Instance 6: On July 28, 2022, AECI submitted another finding update. On May 4, 2022, during a quarterly meeting, AECI and the G&Ts determined that G&T personnel were providing PRC-023 relay loadability settings in their asset management systems that the G&Ts calculated at 0.85 per unit (P.U.) which deviates from the 1.0 P.U. voltage identified in AECI's Facility Ratings Methodology (FRM). Using the 0.85 P.U. relay calculations artificially lowered the equipment ratings for applicable relays in AECI's Facility Ratings database. The group initiated a project to update all applicable ratings to 1.0 P.U. as designated in the FRM. The cause of the noncompliance was inadequate internal controls. AECI lacked a control that required applicable personnel to review how relay settings should be evaluated and entered into AECI’s equipment ratings database. AECI performed a review of relay settings in the Facility Rating database to determine the extent of condition. The incorrect equipment ratings were 17.65% below the correct values and impacted 78 Facilities. G&T personnel corrected the Facility Ratings by June 22, 2022. The relay loadability settings were correct and were not modified. The G&T adjusted impacted Facility Ratings to 1.0 P.U. voltage. During the relay settings review, G&T personnel identified 20 additional discrepancies. The discrepancies consisted of five Facility Ratings that were higher than the correct values (ranging from a 7.0-33.9% deviation), eleven Facility Ratings that were lower than the correct values (ranging from a 13.0-153.0% deviation), three missing relay settings that did not impact the Facility Rating, and one wave trap that had been removed from service by October 2, 2019 but had not been removed from the database. AECI reviewed three years of historical data for the five Facility Ratings that were rated higher than the correct rating. None of the identified Elements exceeded the correct normal or short-term Facility Ratings during that time. Lastly, AECI completed the mitigating activity to perform a field verification of current transformers at G&T’s BES transmission facilities and identified 18 additional incorrect equipment ratings that resulted in five incorrect Facility Ratings. Of the five incorrect Facility Ratings, four were derates ranging from 16.37% to 19.86%, and one uprate of 6.94%. This noncompliance started on June 18, 2007, when FAC-009-1 became mandatory and enforceable, and ended on June 22, 2022, when AECI made the last equipment and Facility Rating correction. The individual Instances had durations of 44 days, 5,215 days, 1,040 days, 5,134 days, 358 days, and 4,393 days, respectively. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failure to establish accurate Facility Ratings and accurately identify equipment rating changes increases the potential risk for AECI to operate the Facilities in excess of their operating limits, thereby creating the opportunity for equipment damage and Facility outages. However, AECI never exceeded the correct Facility Rating in any instance. The noncompliance was limited to a small number of incorrect Facility Ratings (18 out of 495 total solely and jointly owned Facilities had inconsistent normal or emergency ratings compared). Additionally, AECI performed an analysis to determine the worst-case scenario. Transmission Planning personnel used historical data from the last three years for each of the monitored and contingent elements with the worst combination. They identified the absolute maximum flow across those Facilities, regardless of direction or time and performed an evaluation to determine the impact of losing the contingent Facility to the monitored element. The results were compared against the derated ratings to determine if an overload would have occurred. For the identified contingencies, overloads could have occurred in two areas. An operating guide is already in place that mitigates overloads in one area. For overloads at the other area, the solution is to derate the generating units at that Facility. No harm is known to have occurred. | To mitigate this noncompliance, AECI has performed the following actions: 1) derated the Facility Rating in the original Self-Report to reflect the lower capacity jumper wires (Instance 1); 2) replaced the jumper wires on the transmission line with parallel jumpers of a higher ampacity and updated the Facility Ratings to reflect the change (Instance 1); 3) convened the G&T Operations Committee to review potential activities that will reduce the likelihood of reoccurrence of a similar FAC-008 R6 noncompliance. After review, the Committee directed AECI staff to develop Facility Ratings awareness materials for applicable personnel. The Committee also directed AECI to coordinate with the Asset Management Working Group to review facility rating verification practices (Instance 1); 4) developed and distributed Facility Ratings awareness material, inclusive of the SERC online Facility Ratings training module, and deployed it to applicable personnel (all Instances); 5) revised existing processes/procedures to explicitly require field verification steps to ensure that correct equipment has been installed and associated Equipment Ratings are captured prior to energization (Instance 1); 6) trained applicable personnel on the revised processes/procedures. AECI implemented an internal control in AECI’s compliance management system to ensure that training had been reviewed by applicable personnel annually (Instance 1); 7) implemented Facility Rating Database Process Enhancements including adding steps to AECI’s database update process which include verifying equipment rating change impacts before making changes, adding steps to the database update process for communicating and coordinating temporary rating changes with System Operations, and quarterly reviews of Facility Rating database requests; Transmission Planning trained applicable personnel on the revised process (Instances 2 and 3); 8) performed a field verification of current transformers at the specific G&T’s BES transmission facilities. AECI will report any additional potential noncompliance identified during this review to SERC (Instance 4); 9) reviewed relay settings in the Facility Ratings database to verify that ratings were entered at 1.0 per unit voltage, in accordance with AECI’s Facility Rating Methodology (Instance 6); 10) implemented a recurring annual internal control in AECI’s compliance management system that will require applicable personnel to review how relay settings should be evaluated and entered into AECI’s equipment ratings database (Instance 6); and 11) developed and documented a process to perform field verifications of all AECI Joint Registration Organization BES substations every five years. The process will also address field verification of BES substations where a facility has been modified during restoration or maintenance activities performed outside the scope of planned projects (all Instances). To mitigate this noncompliance, AECI will perform the following actions: 1) train applicable AECI and G&T personnel on the new periodic field verification process (all Instances); 2) perform an initial field verification of 50% of applicable substations operated at 200 kV and above. AECI will submit quarterly reports to SERC detailing any additional potential noncompliance identified during this review (all Instances); 3) perform a field verification of all M&A Electric Power Cooperative BES substations. AECI will submit quarterly reports to SERC detailing any additional potential noncompliance identified during this review (all Instances); 4) perform a field verification of 100% of applicable substations operated at 200 kV and above. AECI will submit quarterly reports to SERC detailing any additional potential noncompliance identified during this review (all Instances); 5) add a Facility Rating database update process step in which the database team will coordinate and confirm ownership with the G&T and neighboring entity on ties and jointly owned facilities when they are being updated or modified in the database. Applicable personnel will be trained on the new process (Instance 5); and 6) all BES ties, in which equipment in a substation is owned by more than one entity, will be reviewed with the G&Ts and neighboring entities to ensure that proper ownership is documented. AECI will submit quarterly reports to SERC detailing any additional potential noncompliance identified during this review (Instance 5). | SERC reviewed AECI’s internal compliance program and considered it to be a neutral factor in the penalty determination. SERC applied mitigating credit for cooperation because AECI was cooperative throughout the investigation and enforcement process relating to this violation by providing timely, detailed, thoughtful, organized and thorough responses to its inquiries. SERC encourages this behavior and the level of cooperation demonstrated by AECI. SERC awarded AECI penalty credit because it agreed to settle the violation resolved by this Agreement thereby avoiding a hearing on this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that SERC, NERC, and the Commission time would otherwise expend to resolve these violation. Additionally, it is important to promote prompt resolution of enforcement actions so that AECI can focus on mitigation and reducing risks to reliability. SERC awarded AECI penalty credit for self-identifying and self-reporting the violation. Effective oversight of the reliability and resilience of the BES depends upon self-reporting by Registered Entities as it reduces the probability of unknown risks going undetected and unmitigated for longer durations. Additionally, AECI willfully submitted mitigation for the violation. SERC considered AECI’s FAC-008 R6 compliance history to be an aggravating factor for four instances (2-4 and 6) and non-aggravating for two instances (1 and 5). For Instance 1, AECI self-identified the violation as part of its project management control and before the internal control review cycle cadence of the other controls established in the mitigation for the prior violation. Implementation of controls for the prior violation would not have prevented Instance 1. For Instance 2, AECI identified the discrepancy while performing walk downs during mitigation for the prior violation; however, AECI failed to update the discrepancy in the G&T’s asset management system. For Instance 3, a nameplate picture was mislabeled during the initial phases of the prior mitigation plan which led to an incorrect rating in the G&T’s asset management system. For Instance 4, during the prior mitigation plan, the G&T performed walkdowns with substation personnel which may not have had the correct skill set to verify how CTs were wired in the field. The G&T reviewed drawings and equipment manuals to determine the full ratings of the CT’s and the ratio being used. Those drawings were found to contain inaccuracies. For Instance 5, the issue involved an ownership issue that would not have been mitigated during the prior mitigation. Finally, for Instance 6, AECI failed to properly review and evaluate relay settings which should have been identified and remediated during mitigation for the prior noncompliance.