## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date Regional Entity Verified Completion of Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2023-07-31 | NOC-2813 | SERC Reliability Corporation (SERC) | Cooperative Energy (CoEn) | NCR01315 | TO, GO | Settlement Agreement | Neither Admits nor Denies | 0 | 2021-00605 | FAC-009-1 | R1 | Moderate | Medium | Moderate | Compliance Audit | 8/25/2021 | 6/18/2007 | 12/22/2021 | 2022-04-30 | 4/20/2022 | 4/26/2022 | SERC determined that CoEn was noncompliant with FAC-008-3 R6. CoEn failed to include current transformers (CTs) in the development of the Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology (FRM) or documentation for determining its Facility Ratings. SERC determined that the noncompliance extended back to FAC-009-1 R1. On August 25, 2021, during a data request evidence review for an off-site O&P compliance audit, the audit team discovered that CoEn, as the Transmission Owner (TO) and Generator Owner (GO), did not include CTs in the development of the Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated FRM or documentation for determining its FRs. Specifically, the FR for a 230kV line L231 with a Facility Rating of 325 MVA was inaccurate once the CT Ratio of (500:5) was considered. The CT ratio (500:5) limits the Facility Rating for instances when two circuit breakers (CB1735 or CB1752) are opened. The Facility Rating for L231 should have been de-rated to 200 MVA for this configuration and coordinated with the operations and planning contingency lists for analysis. On October 13, 2021, CoEn completed its extent of condition assessment. CoEn reviewed (print review and walk-down) all of its Bulk Electric System (BES) Facility Ratings to determine if CoEn considered the CTs in the FRM. After a review of 53 BES Facilities (lines and transformers), CoEn determined that the CT ratio was not considered in calculating ratings for 27 BES Facilities (51%). Of these Facilities, three experienced a historical loading during the audit period in excess of the newly calculated Facility Rating with CTs as the limiting element. Of the 27 affected BES Facilities, 17 (63%) required a derate. This noncompliance started on June 18, 2007, when the Standard became enforceable and CoEn failed to include CTs in the development of the Facility Ratings, and ended on December 22, 2021, when CoEn completed field work to eliminate CT ratio limitations, and de-rated all remaining affected lines that were identified in the extent of condition. The cause for this noncompliance was a lack of internal controls. Specifically, CoEn lacked an internal control, i.e., checklist, to ensure it included all equipment documented in the FRM in the development of Facility Ratings. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. CoEn’s failure to establish Facility Ratings that were consistent with its FRM could have resulted in exceedance of System Operating Limits, unnecessary Facility trips, damage to Facilities, and erroneous planning. During CoEn’s review of the operating records for all of the derated Facilities, it found three that operated at loads greater than the revised Facility Ratings. During the Audit Period of June 20, 2018 through April 16, 2021, the MVA flow on the 161kV Line 165 reached a maximum of 125.9 MVA, which is 12% above the calculated 111 MVA CT rating. The MVA flow on 161kV Line 172 reached a maximum of 177.5 MVA, which is 6% above the calculated 167 MVA. Lastly, 230/161kV transformer TT3 reached a maximum of 196 MVA, which is 19% above the calculated 159 MVA. The Line 231 circuit breaker #1752 or #1732 was in an open status resulting in flow through a single breaker, which enhances the potential risk of exceeding the CT rating in question. During the Audit Period, the MVA flow on Line 231 reached a max of 42.49 MVA, which is below the calculated 200 MVA CT rating. The risk was reduced because although there were three exceedances, they were small (all under 20%). Also, CoEn is a small entity with only 1,824 miles of transmission line and the total nameplate of its generation capacity is 2,261 MVA. Further, the issue was limited in that it involved CoEn's failure to consider the CT ratio in the development of its ratings. No harm is known to have occurred. | To mitigate this noncompliance, CoEn performed the following actions: 1) performed an extent of condition assessment; 2) updated System Information Database (SID) to include CT ratio data for incorporation into Facility Rating calculations; 3) performed field work on identified high priority facilities to eliminate CT ratio limitations, and derated all remaining affected lines that were identified in the extent of condition. Derated facilities were communicated in accordance with CoEn’s SID Policy; 4) implemented an internal control (a Facilities checklist) to the Facility Ratings process. The checklist provides better visibility for required Facilities data in the development of Facility Ratings and prevents recurrence; and 5) trained all applicable personnel on process improvements including the Facilities checklist to incorporate into the Facility Rating process. | CoEn did not receive mitigating credit for self-reporting because the violation was discovered during a Compliance Audit. SERC reviewed CoEn’s Internal Compliance Program and considered it to be a neutral factor in the penalty determination. CoEn did not identify the FAC-009-1 R1 violation, and the violation existed for over 14 years. This, as well as the percentage of mis-rated Facilities, demonstrates a need for stronger preventative and detective controls. Accordingly, SERC determined that CoEn’s compliance program that existed at the time of the violation was a neutral factor. The disposition of this violation was escalated from an FFT to an SNOP because of the violation's duration (about 14 years), the percentage of mis-rated facilities (51%), and the number of exceedances (three). For those reasons, SERC determined that this violation was more appropriate as a SNOP. SERC determined that CoEn’s compliance history should not serve as a basis for applying a penalty. CoEn’s relevant prior noncompliance with FAC-008-3 R6 includes NERC Violation ID SERC2018020065. In the prior instance, CoEn (as the TO) failed to update the thermal ratings of the three lines in accordance with the NERC Alert within the System Information Spreadsheet, which CoEn maintains in accordance with its FRM. Its procedure failed to include steps to identify and flag foreseeable occurrences to ensure continued accuracy during re-evaluations, which led to the inconsistency within the System Information Spreadsheet. In contrast, the current instance CoEn (as the TO and GO) failed to include CTs within its FRM. The cause of the current issue was the lack of a checklist to ensure CoEn documented all equipment in the FRM in the development of Facility Ratings. The current issue does not involve recurring conduct that was the same or similar to the conduct in the prior(s), prompt self-reporting and mitigation, and mitigating activities for the prior instance would not have prevented the current instance. SERC awarded penalty credit for the level of cooperation demonstrated by CoEn. CoEn was fully cooperative throughout the entire enforcement process relating to the violation. CoEn cooperated in SERC’s investigation of the violation by timely providing detailed and organized information and dates in response to information requests. Additionally, CoEn mitigated the violation and openly shared information, including any potential weaknesses, regarding its internal compliance program, organizational structure, and applicable processes, procedures, internal controls, systems, and assets. SERC awarded penalty credit because CoEn agreed to settle the violation resolved by the Settlement Agreement thereby avoiding a hearing on this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that SERC, NERC, and the Commission time would otherwise expend to resolve this violation. Additionally, it is important to promote prompt resolution of enforcement actions so that CoEn can focus on mitigation and reducing risks to reliability.