## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | Conetoe II Solar, LLC (Conetoe) | NCR11622 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-00401 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-03-10 | 2019-06-16 | 2022-06-15 |  | 2023-10-02 | TBD | Conetoe notified SERC that it was noncompliant with MOD-032-1 R2. Conetoe failed to submit its steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) annually, as required in the reporting procedures developed by its TP and PC in R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered Conetoe did not submit the steady-state, dynamics, or short circuit modeling data to its TP and PC, as required. Specifically, the PC and TP are the same entity, and require Conetoe to submit the modeling data between May 1st and June 15th of each year. Conetoe submitted the required modeling data for the 2016, 2017, and 2018 calendar years. Conetoe first missed its annual submission that was required to by reported on or before June 15, 2019. In addition, Conetoe did not submit the required data for the 2020 or 2021 calendar years. On June 15, 2022, Conetoe submitted the required data to the TP and PC. There were no changes in the modeling data between the 2018 and 2022 submissions. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on June 16, 2019, when Conetoe failed to submit the required modeling data to its PC and TP by the submission due date, and ended on June 15, 2022, when Conetoe submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). Conetoe’s failure to submit its steady-state, dynamics, and short circuit modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because Conetoe submitted the site’s steady-state, dynamics, and short circuit modeling data to the TP and PC for the 2016, 2017, and 2018 calendar years. Since the 2018 submission, no changes have occurred in the modeling data. Additionally, Conetoe is an 80 MW solar facility with an annual capacity factor of 23%. Moreover, there were no misoperations, emergencies, or other adverse impacts to the BPS as a result of this violation. | To mitigate this noncompliance, Conetoe performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022 as required; 2) defined formal roles and responsibilities for all groups involved in producing & submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go in the tool, the frequency of the tasks, and the owners of tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained. | The Regions considered Conetoe and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. The Regions reviewed Conetoe’s internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. Conetoe did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, Conetoe did receive mitigating credit for cooperation and agreeing to settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in four parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF) and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF, and WECC.
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | Cimarron Windpower II, LLC (CWII) | NCR11240 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-01053 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-07-12 | 2016-07-01 | 2022-09-19 |  | 2023-10-02 | TBD | CWII notified SERC that it was noncompliant with MOD-032-1 R2. CWII failed to submit its steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) annually, as required in the reporting procedures developed by its TP and PC in R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered CWII did not submit the steady-state, dynamics, or short circuit modeling data to its TP and PC, as required. Specifically, the PC requires CWII to submit the data by a particular date each year, and the TP requires CWII to follow the PC’s process. CWII did not submit the initial modeling data to the PC or TP by the July 1, 2016, effective date of the standard, nor did it submit the modeling data for the 2017, 2018, 2019, or 2021 calendar years. CWII submitted the modeling data for 2020 on March 12, 2020, and for 2022 on March 10, 2022, and September 19, 2022, as required. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on July 1, 2016, when the standard became mandatory and enforceable and CWII failed to submit the required modeling data to its PC and TP, and ended on September 19, 2022, when CWII submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). CWII’s failure to submit its steady-state, dynamics, and short circuit modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because CWII submitted the site’s initial steady-state, dynamics, and short circuit modeling data to the TP and PC on May 6, 2011, and no changes in the dynamic data occurred during the period of noncompliance. Additionally, there were no significant changes to the site since construction, and the change in the steady-state and short circuit data that occurred in 2018, would have had a minimal impact on the BPS, as CWII is a 131.1 MW wind generation facility with a rolling 12-month net capacity factor of 24.28%. Additionally, there were no misoperations, emergencies, or other adverse impacts to the BPS as a result of this violation. | To mitigate this violation, CWII performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022, as required; 2) defined formal roles and responsibilities for all groups involved in producing and submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go into the tool, the frequency of the tasks, and the owners of the tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained | The Regions reviewed CWII’s internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. The Regions considered CWII and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. CWII did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, CWII did receive mitigating credit for cooperation and agreeing to settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in four parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF) and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF, and WECC.
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | Frontier Windpower, LLC (FRW) | NCR11692 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-01054 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-07-12 | 2017-02-04 | 2022-09-19 |  | 2023-10-02 | TBD | FRW notified SERC it was noncompliant with MOD-032-1 R2. FRW failed to submit its steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) annually, as required in the reporting procedures developed by its TP and PC in R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered FRW did not submit the steady-state, dynamics, or short circuit modeling data to its TP and PC, as required. Specifically, the PC requires FRW to submit the data by a particular date each year, and the TP requires FRW to copy them on the submission. FRW submitted all its initial modeling data on April 24, 2016, prior to its October 18, 2016, NERC registration date. However, FRW did not submit all the required data for the 2017, 2018, 2019, or 2021 calendar years. In 2019 FRW did submit the steady-state and short circuit data, and on March 12, 2020, FRW submitted the required data for the 2020 calendar year. FRW submitted the modeling data for 2022 on March 10, 2022, and September 19, 2022, as required. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on February 4, 2017, when FRW missed the first 2017 due date for the required model data, and ended on September 19, 2022, when FRW submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). FRW’s failure to submit its steady-state, dynamics, and short circuit modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because FRW submitted the site’s initial steady-state, dynamics, and short circuit modeling data to the TP and PC on April 24, 2016, and no changes in any of the modeling data occurred during the period of noncompliance. Additionally, FRW is a 210 MW solar facility with an annual capacity factor of 31%, and there were no misoperations, emergencies, or other adverse impacts to the BPS because of this violation. | To mitigate this noncompliance, FRW performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022 as required; 2) defined formal roles and responsibilities for all groups involved in producing & submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go in the tool, the frequency of the tasks, and the owners of tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained. | The Regions considered FRW and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. The Regions reviewed FRW’s internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. FRW did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, FRW did receive mitigating credit for cooperation and agreeing to settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in three parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF) and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF, and WECC.
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | Frontier Windpower II, LLC (FRW2) | NCR12088 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-01056 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-07-20 | 2021-08-11 | 2022-09-19 |  | 2023-10-02 | TBD | FRW2 notified SERC that it was noncompliant with MOD-032-1 R2. FRW2 failed to submit its dynamics modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) annually, as required in the reporting procedures developed by its TP and PC in R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered FRW2 did not submit the dynamics, modeling data to its TP and PC, as required. Specifically, the PC requires FRW2 to submit the data by a particular date each year, and the TP requires FRW2 to copy them on the submission. FRW2 submitted all of its initial modeling data on December 20, 2019, prior to its February 12, 2021, NERC registration date. However, FRW2 did not submit the dynamics modeling data for the 2021 calendar year. FRW2 submitted the modeling data for 2022 on March 10, 2022, and September 19, 2022, as required. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on August 11, 2021, when FRW2 failed to submit the required modeling data to its PC and TP by the submission due date, and ended on September 19, 2022, when FRW2 submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). FRW2’s failure to submit its dynamics modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because FRW2 submitted the site’s initial steady-state, dynamics, and short circuit modeling data to the TP and PC on December 20, 2019, and no changes in any of the modeling data occurred during the period of noncompliance. Additionally, FRW2 is a 352 MW solar facility with an annual capacity factor of 15%, and there were no misoperations, emergencies, or other adverse impacts to the BPS because of this violation. | To mitigate this noncompliance, FRW2 performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022 as required; 2) defined formal roles and responsibilities for all groups involved in producing & submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go in the tool, the frequency of the tasks, and the owners of tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained. | The Regions considered FRW2 and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. The Regions reviewed FRW2’s internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. FRW2 did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, FRW2 did receive mitigating credit for cooperation and agreeing to settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in four parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF) and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF and WECC.
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | Ironwood Windpower, LLC (IW) | NCR11257 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-01057 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-07-20 | 2016-07-01 | 2022-09-19 |  | 2023-10-02 | TBD | IW notified SERC pursuant to an existing multi-region registered entity agreement that it was in violation of MOD-032-1 R2. IW failed to provide modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) according to the data requirements and reporting procedures developed by its TP and PC in Requirement R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered IW did not submit the steady-state, dynamics, or short circuit modeling data to its TP and PC, as required. Specifically, the PC requires IW to submit the data by a particular date each year, and the TP requires IW to follow the PC’s process. IW did not submit the required modeling data to the PC or TP by the July 1, 2016, effective date of the standard, nor did it submit the modeling data for the 2017, 2018, 2019, or 2021 calendar years. IW submitted the modeling data for 2020 on March 12, 2020, and for 2022 on March 10, 2022, and September 19, 2022, as required. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on July 1, 2016, when the standard became mandatory and enforceable and IW failed to submit the required modeling data to its PC and TP, and ended on September 19, 2022, when IW submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). IW’s failure to submit its dynamics modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because IW submitted the site’s initial steady-state, dynamics, and short circuit modeling data to the TP and PC on or before March 31, 2011, prior to the inception of the NERC requirement to submit this data, and no changes in any of the modeling data occurred during the period of noncompliance. Additionally, IW is a 168 MW wind generation facility with a rolling 12-month Net Capacity Factor of 20.87%, and there were no misoperations, emergencies, or other adverse impacts to the BPS because of this violation. | To mitigate this noncompliance, IW performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022 as required; 2) defined formal roles and responsibilities for all groups involved in producing & submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go in the tool, the frequency of the tasks, and the owners of tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained. | The Regions considered IW and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. The Regions reviewed IW’s internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. IW did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, IW did receive mitigating credit for cooperation and agreeing to the settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in three parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF), and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF, and WECC.
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | North Allegheny Wind, LLC (NAW) | NCR12040 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-01058 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-07-20 | 2021-06-16 | 2022-06-15 |  | 2023-10-02 | TBD | NAW notified SERC that it was noncompliance with MOD-032-1 R2. NAW failed to submit its steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) annually, as required in the reporting procedures developed by its TP and PC in R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered NAW did not submit the dynamics, modeling data to its TP and PC, as required. Specifically, the PC and TP are the same entity and require NAW to submit the modeling data between May 1st and June 15th of each year. NAW submitted all of its initial modeling data on May 16, 2020, prior to its September 28, 2020, NERC registration date. However, NAW did not submit the modeling data for the 2021 calendar year, which was due on June 15, 2021. NAW submitted the modeling data for 2022 on the June 15, 2022 due date. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on June 16, 2021, when NAW failed to submit the required modeling data to its PC and TP by the submission due date, and ended on June 15, 2022, when NAW submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). NAW’s failure to submit its steady-state, dynamics, and short circuit modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because NAW submitted the site’s initial steady-state, dynamics, and short circuit modeling data to the TP and PC on May 16, 2020, and there were no changes in the modeling data between the 2020 initial submission and the missed 2021 submission. Additionally, NAW is a 70 MW wind generation facility with a rolling 12-month Net Capacity Factor of 20.96%, and there were no misoperations, emergencies, or other adverse impacts to the BPS because of this violation. | To mitigate this noncompliance, NAW performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022 as required; 2) defined formal roles and responsibilities for all groups involved in producing & submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go in the tool, the frequency of the tasks, and the owners of tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained. | The Regions considered NAW and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. The Regions reviewed NAW’s internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. NAW did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, NAW did receive mitigating credit for cooperation and agreeing to settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in three parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF) and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF, and WECC.
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | North Rosamond Solar, LLC (NROS) | NCR11927 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-01059 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-07-20 | 2021-05-01 | 2022-12-13 |  | 2023-10-02 | TBD | NROS notified SERC it was noncompliant with MOD-032-1 R2. NROS failed to submit its steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) annually, as required in the reporting procedures developed by its TP and PC in R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered NROS did not submit the steady-state, dynamics, or short circuit modeling data to its TP and PC, as required. Specifically, the PC requires NROS to submit the data by a particular date each year, and the TP requires NROS to follow the PC’s process. NROS submitted the required data for the 2018, 2019, and 2020 calendar years. NROS missed its first annual submission period on May 1, 2021. NROS submitted the required modeling data on December 13, 2022. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on May 1, 2021, when NROS failed to submit the required modeling data to its PC and TP by the submission due date, and ended on December 13, 2022, when NROS submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). NROS’ failure to submit its steady-state, dynamics, and short circuit modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because NROS submitted the prior years’ data and there were no changes between the last submission in 2020 and the missed submission in 2021. Additionally, NROS is a 150 MW solar generation facility with a rolling 12-month Net Capacity Factor of 26.90%, and there were no misoperations, emergencies, or other adverse impacts to the BPS because of this violation. | To mitigate this noncompliance, NROS performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022 as required; 2) defined formal roles and responsibilities for all groups involved in producing & submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go in the tool, the frequency of the tasks, and the owners of tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained. | The Regions considered NROS and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. The Regions reviewed NROS’ internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. NROS did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, NROS did receive mitigating credit for cooperation and agreeing to settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in three parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF) and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF, and WECC.
2023-11-30 | NOC-2818 | SERC Reliability Corporation (SERC) | Top of the World (TOW) | NCR11090 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00401, 2023-01053, 2023-01054, 2023-01056, 2023-01057, 2023-01058, 2023-01059, 2023-01061) | 2023-01061 | MOD-032-1 | R2 | Minimal | Medium | Severe | Self-Report | 2023-07-20 | 2016-07-01 | 2022-08-31 |  | 2023-10-02 | TBD | TOW notified SERC that it was noncompliant with MOD-032-1 R2. TOW failed to submit its steady-state, dynamics, and short circuit modeling data to its Transmission Planner (TP) and Planning Coordinator (PC) annually, as required in the reporting procedures developed by its TP and PC in R1. On October 6, 2022, while gathering historical MOD-032 compliance evidence for an upcoming audit, Duke Energy Renewable Services (DERS) NERC Compliance discovered TOW did not submit the dynamics, modeling data to its TP and PC, as required. Specifically, the PC and TP are the same entity and require TOW to submit the modeling data by a particular date each year. TOW, which was registered with NERC on September 3, 2010, did not have evidence that it submitted its modeling data to the TP and PC by the July 1, 2016, effective date of the standard. TOW submitted all the modeling data for the 2017, 2018, 2019, and 2020 calendar years. However, TOW did not submit the modeling data for the 2021 calendar year, which was due on September 28, 2021. On August 31, 2022, TOW submitted the modeling data for 2022. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-032 R2 submission data across the Multi-Region Registered Entity (MRRE) Group 15b DERS fleet and for applicable sites within the Duke Energy Enterprise Transmission, Regulated Renewable Energy, and Nuclear business areas. This review included data beginning in 2016, when the standard became mandatory and applicable. The EOC identified additional noncompliances associated with the MRRE Group 15b DERS fleet, which were individually self-reported to SERC. No instances of noncompliance were identified with the other Duke Energy Enterprise business areas. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-032. Personnel responsible for the oversight of compliance activities lacked training and awareness on MOD-032, which resulted in deficient procedures, a lack of controls, and inadequate compliance training across multiple Generator Owners. The roles and responsibilities were not clearly defined for all groups involved in producing and submitting MOD-032 modeling data, and there was not a written procedure for submitting data to its TP and PCs. Rather, compliance personnel relied upon email notifications from its TP and PC as submission reminders; however, when personnel turned over, replacements were not added to the TP and PC distribution list, and no notifications occurred to instruct new personnel to submit the modeling data. This noncompliance started on July 1, 2016, when the standard became mandatory and enforceable and TOW failed to submit the required modeling data to its PC and TP, and ended on August 31, 2022, when TOW submitted all required model data to its TP and PC. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). TOW’s failure to submit its dynamics modeling data to its PC and TP as required could have resulted in inaccurate data being used in planning models and studies, which could have prevented the PC and TP from adequately analyzing the system to support the reliability of the BPS. However, in this instance, the risk is reduced and is not serious or substantial because the missed submission periods were limited to two nonconsecutive years, and no changes in the modeling data occurred during between the prior years and the missed submissions. Additionally, TOW is a 200.2 MW wind generation facility with a rolling 12-month Net Capacity Factor of 14.47%, and there were no misoperations, emergencies, or other adverse impacts to the BPS because of this violation. | To mitigate this noncompliance, TOW performed the following actions: 1) submitted the MOD-032 steady-state, dynamics, and short circuit modeling data to the PC and TP for 2022 as required; 2) defined formal roles and responsibilities for all groups involved in producing & submitting MOD‑032 model data. This information and training was incorporated into the MOD procedure developed as part of this mitigation; 3) cataloged the MOD‑032-1 R1 requirements for all applicable TP and PCs including annual submission due dates, and set-up an annual task to review the MOD-032 R1 requirements from the TP and PCs to ensure compliance personnel have the most current requirements; 4) developed a fleet-wide procedure that sets standards for more structured document controls as it applies to model evidence applicable to the NERC MOD standards, including organization details and roles and responsibilities to maintain an ongoing documentation control program for model data; 5) developed one fleet-wide procedure for all MOD standards that includes documented roles and responsibilities, periodicity, and the process for managing compliance. It was developed in conjunction with Renewables project Engineering and Electrical Engineering, which addresses managing compliance in new NERC sites and existing NERC sites. Compliance personnel will provide annual training to applicable Subject Matter Experts to maintain awareness and consistency; 6) implemented MOD tracking tool to track upcoming modeling requirements with preventative maintenance work orders and associated job plans. Upon completion of modeling tasks, evidence will be attached to the work orders to provide necessary reporting and evidence storage; 7) implemented the newly developed organizational approach for model data evidence, which includes new folder structures and archived historical evidence; 8) trained applicable personnel on MOD roles and responsibilities, the new procedure, and the new evidence approach. This initial training was conducted as a part of this mitigation plan and will be repeated on an annual basis; 9) configured the tracking tool to track and manage all MOD submittal due dates, including determining and setting up the tasks that will go in the tool, the frequency of the tasks, and the owners of tasks; 10) implemented tracking tool and began using as system of record for tracking MOD compliance deadlines, communicated tool deployment to stakeholder groups, and conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; and 11) developed internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control to prevent issues where a system is setup initially but not adequately maintained. | The Regions considered TOW and its affiliates’ compliance history and determined there were no relevant instances of noncompliance. The Regions reviewed TOW’s internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. TOW did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. However, TOW did receive mitigating credit for cooperation and agreeing to settle. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC and SERC shall divide the penalty amount in three parts based on the relative Net Energy Load (NEL) for SERC, Midwest Reliability Organization (MRO), ReliabilityFirst (RF) and Western Electricity Coordinating Council (WECC). SERC will then distribute a NEL based proportional allocation to MRO, RF, and WECC.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Conetoe II Solar, LLC (Conetoe) | NCR11622 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00395 | MOD-025-2 | R1;R1.2 | Minimal | Medium | Severe | Self-Report | 2023-03-09 | 2022-01-18 | 2023-01-04 |  | 2023-10-02 | TBD | Conetoe notified SERC that it was noncompliant with MOD-025-2 R1; R1.2. Conetoe failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On October 19, 2021, Conetoe performed the required five-year staged verification of its Real Power Capability. As such, it was required to submit the Attachment 2 information to the TP on or before January 17, 2022. However, Conetoe did not submit the results to the TP until January 4, 2023, 442 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Real Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Real Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on January 18, 2022, when Conetoe exceeded the 90-calendar day submission requirement, and ended on January 4, 2023, when Conetoe submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). Conetoe’s failure to provide Real Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because Conetoe did not have any significant changes since construction, and thus, no significant changes in Real Power capability occurred since the last Real Power verification data submittal to the TP on April 5, 2017. In addition, Conetoe has limited impact to the BPS as it is an 80 MW solar facility with a 23% annual capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90 day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, Conetoe performed the following actions: 1) completed the MOD-025 Real Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed Conetoe's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. Conetoe did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered Conetoe and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Conetoe II Solar, LLC (Conetoe) | NCR11622 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00397 | MOD-025-2 | R2;R2.2 | Minimal | Medium | Severe | Self-Report | 2023-03-09 | 2022-01-18 | 2023-01-04 |  | 2023-10-02 | TBD | Conetoe notified SERC that it was noncompliant with MOD-025-2 R2; R2.2. Conetoe failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On October 19, 2021, Conetoe performed the required five-year staged verification of its Reactive Power Capability. As such, it was required to submit the Attachment 2 information to the TP on or before January 17, 2022. However, Conetoe did not submit the results to the TP until January 4, 2023, 442 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Reactive Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Reactive Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on January 18, 2022, when Conetoe exceeded the 90-calendar day submission requirement, and ended on January 4, 2023, when Conetoe submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). Conetoe’s failure to provide Reactive Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk is reduced because Conetoe did not have any significant changes since construction, and thus, no significant changes in Reactive Power capability occurred since the last Reactive Power verification data submittal to the TP on April 5, 2017. In addition, Conetoe has limited impact to the BPS as it is an 80 MW solar facility with a 23% annual capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90 day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, Conetoe performed the following actions: 1) completed the MOD-025 Reactive Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed Conetoe's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. Conetoe did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered Conetoe and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Los Vientos Windpower III, LLC (LVWPIII) | NCR11538 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00432 | MOD-025-2 | R1;R1.2 | Minimal | Medium | Severe | Self-Report | 2023-03-14 | 2022-03-17 | 2022-12-20 |  | 2023-10-02 | TBD | LVWPIII notified SERC that it was noncompliant with MOD-025-2 R1.2. LVWPIII failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On December 16, 2021, LVWPIII performed the required five-year staged verification of its Real Power Capability. As such, it was required to submit the Attachment 2 information to the TP on or before March 16, 2022. However, LVWPIII did not submit the results to the TP until December 20, 2022, 369 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Real Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Real Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on March 17, 2022, when LVWPIII exceeded the 90-calendar day submission requirement, and ended on December 20, 2022, when LVWPIII submitted the results to the TP | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). LVWPIII’s failure to provide Real Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because LVWPIII did not have any significant changes since construction, and thus, no significant changes in Real Power capability since the last Real Power verification data submittal to the TP on April 4, 2017. In addition, LVWPIII has limited impact to the BPS as it is a 200 MW wind facility with a 30% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90-day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, LVWPII performed the following actions: 1) completed the MOD-025 Real Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed LVWPIII's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. LVWPIII did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered LVWPIII and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the LVWPIII’s prior compliance exception to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exception was considered when determining the disposition method as the internal control implemented in the prior mitigation should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Los Vientos Windpower III, LLC (LVWPIII) | NCR11538 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00438 | MOD-025-2 | R2;R2.2 | Minimal | Medium | Severe | Self-Report | 2023-03-15 | 2022-03-17 | 2022-12-20 |  | 2023-10-02 | TBD | LVWPIII notified SERC that it was noncompliant with MOD-025-2 R2; R2.2. LVWPIII failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On December 16, 2021, LVWPIII performed the required five-year staged verification of its Reactive Power Capability. As such, it was required to submit the results to the TP on or before March 16, 2022. However, LVWPIII did not submit the results to the TP until December 20, 2022, 369 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Reactive Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Reactive Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on March 17, 2022, when LVWPIII exceeded the 90-calendar day submission requirement, and ended on December 20, 2022, when LVWPIII submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). LVWPIII’s failure to provide Reactive Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because LVWPIII did not have any significant changes since construction, and thus, no significant changes in Reactive Power capability occurred since the last Reactive Power verification data submittal to the TP on April 4, 2017. In addition, LVWPIII has limited impact to the BPS as it is a 200 MW wind facility with a 30% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90 day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, LVWPIII performed the following actions: 1) completed the MOD-025 Reactive Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed LVWPIII's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. LVWPIII did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered LVWPIII and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the LVWPIII’s prior compliance exception to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exception was considered when determining the disposition method as the internal control implemented in the prior mitigation should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Los Vientos Windpower IV, LLC (LVIV) | NCR11635 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00433 | MOD-025-2 | R1;R1.2 | Minimal | Medium | Severe | Self-Report | 2023-03-14 | 2022-03-17 | 2022-12-07 |  | 2023-10-02 | TBD | LVIV notified SERC that it was noncompliant with MOD-025-2 R1; R1.2. LVIV failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On December 16, 2021, LVIV performed the required five-year staged verification of its Real Power Capability. As such, it was required to submit the Attachment 2 information to the TP on or before March 16, 2022. However, LVIV did not submit the results to the TP until December 7, 2022, 266 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Real Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Real Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on March 17, 2022, when LVIV exceeded the 90-calendar day submission requirement, and ended on December 7, 2022, when LVIV submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). LVIV’s failure to provide Real Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because LVIV did not have any significant changes since construction, and thus, no significant changes in Real Power capability occurred since the last Real Power verification data submittal to the TP on November 15, 2016. In addition, LVIV has limited impact to the BPS as it is a 200 MW wind facility with a 39% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90-day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, LVIV performed the following actions: 1) completed the MOD-025 Real Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed LVIV's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. LVIV did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered LVIV and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Los Vientos Windpower IV, LLC (LVIV) | NCR11635 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00440 | MOD-025-2 | R2;R2.2 | Minimal | Medium | Severe | Self-Report | 2023-03-16 | 2022-03-17 | 2022-12-07 |  | 2023-10-02 | TBD | LVIV notified SERC that it was noncompliant with MOD-025-2 R2; R2.2. LVIV failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On December 16, 2021, LVIV performed the required five-year staged verification of its Reactive Power Capability. As such, it was required to submit the results to the TP on or before March 16, 2022. However, LVIV did not submit the results to the TP until December 7, 2022, 266 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Reactive Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Reactive Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on March 17, 2022, when LVIV exceeded the 90-calendar day submission requirement, and ended on December 7, 2022, when LVIV submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). LVIV’s failure to provide Reactive Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because LVIV did not have any significant changes since construction, and thus, no significant changes in Reactive Power capability occurred since the last Reactive Power verification data submittal to the TP on November 15, 2016. In addition, LVIV has limited impact to the BPS as it is a 200 MW wind facility with a 39% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90-day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, LVIV performed the following actions: 1) completed the MOD-025 Reactive Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed LVIV's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. LVIV did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered LVIV and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Los Vientos Windpower V, LLC (LVWPV) | NCR11603 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00437 | MOD-025-2 | R1;R1.2 | Minimal | Medium | Severe | Self-Report | 2023-03-14 | 2021-12-22 | 2022-07-06 |  | 2023-10-02 | TBD | LVWPV notified SERC that it was noncompliant with MOD-025-2 R1; R1.2. LVWPV failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On September 22, 2021, LVWPV performed the required five-year staged verification of its Real Power capability. As such, it was required to submit the Attachment 2 information to the TP on or before December 21, 2021. However, LVWPV did not submit the results to the TP until July 6, 2022, 287 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Real Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Real Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on December 22, 2021, when LVWPV exceeded the 90-calendar day submission requirement, and ended on July 6, 2022, when LVWPV submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). LVWPV’s failure to provide Real Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because LVWPV did not have any significant changes since construction, and thus, no significant changes in Real Power capability occurred since the last Real Power verification data submittal to the TP on December 21, 2016. In addition, LVWPV has limited impact to the BPS as it is a 110 MW wind facility with a 36% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90 day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, LVWPV performed the following actions: 1) completed the MOD-025 Real Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed LVWPV's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. LVWPV did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered LVWPV and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Los Vientos Windpower V, LLC (LVWPV) | NCR11603 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00442 | MOD-025-2 | R2;R2.2 | Minimal | Medium | Severe | Self-Report | 2023-03-16 | 2021-12-22 | 2022-07-06 |  | 2023-10-02 | TBD | LVWPV notified SERC that it was noncompliant with MOD-025-2 R2; R2.2. LVWPV failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On September 22, 2021, LVWPV performed the required five-year staged verification of its Reactive Power Capability. As such, it was required to submit the results to the TP on or before December 21, 2021. However, LVWPV did not submit the results to the TP until July 6, 2022, 287 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Reactive Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Reactive Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on December 22, 2021, when LVWPV exceeded the 90-calendar day submission requirement, and ended on July 6, 2022, when LVWPV submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). LVWPV’s failure to provide Reactive Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because LVWPV did not have any significant changes since construction, and thus, no significant changes in Reactive Power capability occurred since the last Reactive Power verification data submittal to the TP on December 21, 2016. In addition, LVWPV has limited impact to the BPS as it is a 110 MW wind facility with a 36% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90 day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, LVWPV performed the following actions: 1) completed the MOD-025 Reactive Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed LVWPV's internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. LVWPV did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered LVWPV and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (Texas RE). SERC will then distribute a NEL based proportional allocation to Texas RE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00439 | MOD-025-2 | R1;R1.2 | Minimal | Medium | Severe | Self-Report | 2023-03-14 | 2022-01-18 | 2022-12-19 |  | 2023-10-02 | TBD | NOTWIN001 notified SERC that it was noncompliant with MOD-025-2 R1; R1.2. NOTWIN001 failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On October 19, 2021, NOTWIN001 performed the required five-year staged verification of its Real Power Capability. As such, it was required to submit the Attachment 2 information to the TP on or before January 17, 2022. However, NOTWIN001 did not submit the results to the TP until December 19, 2022, 426 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Real Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Real Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on January 18, 2022, when NOTWIN001 exceeded the 90-calendar day submission requirement, and ended on December 19, 2022, when NOTWIN001 submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). NOTWIN001’s failure to provide Real Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because NOTWIN001 did not have any significant changes since construction, and thus, no significant changes in Real Power capability occurred since the last Real Power verification data submittal to the TP on July 13, 2017. In addition, NOTWIN001 has limited impact to the BPS as it is a 153 MW wind facility with a 23% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90-day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, NOTWIN001 performed the following actions: 1) completed the MOD-025 Real Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed NOTWIN00's1 internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. NOTWIN001 did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered NOTWIN001 and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (TexasRE). SERC will then distribute a NEL based proportional allocation to TexasRE.
2023-11-30 | NOC-2819 | SERC Reliability Corporation (SERC) | Notrees Windpower, LP (NOTWIN001) | NCR10276 | GO | Settlement Agreement | Neither Admits Nor Denies | $20,000 (for 2023-00395, 2023-00397, 2023-00432, 2023-00433, 2023-00439, 2023-00436, 2023-00443, 2023-00438, 2023-00440, 2023-00442) | 2023-00443 | MOD-025-2 | R2;R2.2 | Minimal | Medium | Severe | Self-Report | 2023-03-15 | 2022-01-18 | 2022-12-19 |  | 2023-10-02 | TBD | NOTWIN001 notified SERC that it was noncompliant with MOD-025-2 R2; R2.2. NOTWIN001 failed to submit a completed Attachment 2, or a form containing the same information, to its Transmission Planner (TP) within 90 calendar days of the date the data was recorded for a staged test. On October 6, 2022, while gathering historical MOD-025 compliance evidence for an upcoming audit, Duke Energy Renewable Services’ (DERS) NERC Compliance discovered it did not submit the Attachment 2 information to its TP, as required. On October 19, 2021, NOTWIN001 performed the required five-year staged verification of its Reactive Power Capability. As such, it was required to submit the results to the TP on or before January 17, 2022. However, NOTWIN001 did not submit the results to the TP until December 19, 2022, 426 days after the staged test. For the extent-of-condition (EOC) assessment, DERS reviewed MOD-025-2 documentation across the DERS fleet from 2016 through March 2023. DERS confirmed initial Reactive Power verification test dates and secondary test dates, where applicable, for all MRRE Group #15b Generator Owners, and verified whether submission of the verification data occurred within 90 days of the Reactive Power verification test. The EOC identified six additional registered entities that did not meet the compliance requirements, all of which were individually self-reported to SERC. As part of its mitigation, DERS will also conduct an Enterprise-wide EOC on evidence submitted to TPs/Planning Coordinators (PCs) including registration date and implementation date information and report any additional findings to SERC. The cause of this noncompliance was an inadequate fleet-wide compliance management approach to MOD-025. Personnel responsible for the oversight of the compliance activities lacked training and awareness on MOD-025, which resulted in the deficient procedures, unmaintained controls, and inadequate compliance training across multiple Generator Owners. The MOD-025 procedure did not have clearly defined roles and responsibilities for all groups involved in producing and submitting MOD‑025 model data. Additionally, there was a deficient compliance tracking tool that included a narrative reminding personnel of upcoming submission deadlines and the requirement to notify the TP, but did not include a follow-up method to make sure all compliance activities were completed. This resulted in the tool being effective for performing the MOD-025 testing, but deficient in ensuring personnel communicated those test results to the TP within 90 days. This noncompliance started on January 18, 2022, when NOTWIN001 exceeded the 90 calendar day submission requirement, and ended on December 19, 2022, when NOTWIN001 submitted the results to the TP. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). NOTWIN001’s failure to provide Reactive Power capability information to the TP within 90 days of verification could have resulted in incorrect modelling of unit capabilities, which could have affected the proper identification of adverse reliability impacts in the long-term planning and operating processes. However, the risk was reduced because NOTWIN001 did not have any significant changes since construction, and thus, no significant changes in Reactive Power capability occurred since the last Reactive Power verification data submittal to the TP on July 13, 2017. In addition, NOTWIN001 has limited impact to the BPS as it is a 153 MW wind facility with a 23% rolling 12- month capacity factor. Moreover, there were no misoperations as a result of this noncompliance, and DERS was not contacted by the TP to provide updated MOD-025 data following the missed 90 day notification deadline. Also, DERS was not made aware of any adverse consequences or impacts that were a result of the TP not receiving recent data. No harm is known to have occurred. | To mitigate this violation, NOTWIN001 performed the following actions: 1) completed the MOD-025 Reactive Power verification submission to the TP; 2) revised the existing MOD-025 procedure to include the defined formal Roles & Responsibilities for all groups involved in producing and submitting MOD‑025 model data and documented annual training frequency on the Roles & Responsibilities in the MOD-025 procedure; 3) reviewed DERS’ MOD-025 procedure and evaluated ways to promote consistency fleetwide; 4) developed and implemented an organizational approach for model data evidence that supports the evidence gathering process by defining a standard for evidence folder structure, file naming and version control as well as identify a single repository for evidence. The organizational approach, including training frequency, will be documented in the MOD procedure; 5) trained impacted groups on updates to MOD‑025 procedure to ensure new processes are understood and implemented. This training addressed the MOD roles & responsibilities, procedure updates, and new evidence approach. An initial training will be conducted as a part of this mitigation plan and repeated on an annual basis; 6) selected, configured, and implemented a long term tracking tool to use for MOD submittal due dates/compliance; 7) communicated tracking tool deployment to stakeholder groups, including the "Go Live" date for the new tool. DERS conducted an initial training for impacted groups on the new controls and communicated cutover to the new system. Training on the tracking tool will be repeated on an annual basis; 8) developed an internal control to ensure that prior mitigation plan activities were effective and ongoing compliance is met. DERS will ensure ongoing maintenance and functionality of the control as to prevent issues where a system is setup initially but not adequately maintained; and 9) conducted a more thorough EOC for the DERS NERC fleet, during which DERS reviewed submittal evidence to TP/PCs including registration date and implementation date information. | SERC reviewed NOTWIN00's1 internal compliance program and considered it to be a neutral factor in the penalty determination due to a lack of annual reviews of the program and lack of training for mandatory compliance requirements. NOTWIN001 did not receive mitigating credit for self-reporting because the self-report was submitted after receiving notice of an upcoming Compliance Audit. SERC considered NOTWIN001 and its affiliates’ compliance history in determining the penalty. On February 19, 2015, the Federal Energy Regulatory Commission (FERC) ruled that compliance exceptions shall not be included in a registered entity’s compliance history for penalty purposes unless the later violation is classified as “serious” and/or “substantial”, occurs because of the entity’s unsuccessful or partial remediation of the compliance exception, or remediation of the compliance exception reasonable could have enabled the entity to prevent the later serious or substantial violation, but did not. 150 FERC ¶61, 108 at P 44. Thus, SERC did not consider the affiliates’ prior compliance exceptions to be an aggravating factor in determining the penalty. However, SERC notes that the prior compliance exceptions were considered when determining the disposition method as the internal control implemented in the mitigation for the affiliates’ prior noncompliance should have prevented the instant noncompliance. Specifically, prior mitigating actions directly addressed a control that reminded staff to provide the TP with verification of the Real and Reactive Power capability results in the prior mitigation. Under coordinated oversight, the penalty will be divided among the Regional Entities as follows. The $20,000 shall be paid to SERC, and SERC shall divide the penalty amount in two parts based on the relative Net Energy Load (NEL) for SERC and Texas Reliability Entity (TexasRE). SERC will then distribute a NEL based proportional allocation to TexasRE.
2023-11-30 | NOC-2820 | SERC Reliability Corporation (SERC) | Louisiana Energy & Power Authority (LEPA) | NCR01116 | BA | Settlement Agreement | Admits | 0 | 2023-00767 | EOP-008-2 | R6. | Moderate | Medium | Severe | Self-Report | 2023-05-08 | 2007-06-18 | 2026-01-30 | 2026-01-30 | TBD | TBD | LEPA notified SERC that it was noncompliant with EOP-008-2 R6. LEPA failed to have primary and backup functionality that does not depend on each other for the control center functionality required to maintain compliance with Reliability Standards. SERC staff determined that this violation began under EOP-008-0 R1 and spanned to EOP-008-2 R6. On May 2, 2023, during the on-site review by the SERC certification team, the SERC certification team identified that LEPA did not meet the requirements for a back-up control center (BCC). LEPA was unable to demonstrate the required capabilities associated with Primary Control Center (PCC) and BCC independence. Since its original certification in 2007, LEPA operated with the same PCC and BCC functionality. The LEPA BCC has a primary and secondary internet connection via a wireless hotspot, voice communication via a land line for primary and cellular service for secondary, a satellite phone, a dedicated laptop, the capability to receive generation setpoints through extensible markup language, and an inter-control center communications protocol (ICCP) pass through connection r review by SERC staff with three entities. The PCC provides energy management servers, an ICCP server, real-time meter data, and automatic generation dispatch to the BCC. LEPA's BA contains 10 members all located throughout the state of Louisiana. LEPA's BA Area has only 83 MW of generation. LEPA is subject to a Coordinated Functional Registration (BA CFR00001) with MISO. Therefore, it does not have responsibility for all BA functions and Standard Requirements. In other words, although LEPA is registered as a BA, MISO generally handles BA responsibilities. For the extent of condition assessment, LEPA identified the functionality the BCC depended on the PCC to provide for its operation. The cause of the violation was ineffective management oversight. LEPA management did not implement an internal control, i.e., assessment, to ensure that it could meet the obligations of the applicable Standards. This violation started on June 18, 2007, when LEPA failed to have a BCC that met the independence requirements from the PCC, and will end on January 30, 2026, when LEPA will complete a BCC that meets all of the requirements of EOP-008 R6. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). Loss of the PCC would result in an inability to monitor and control certain Bulk Electric System elements. The loss of functional control could create an unknown operating condition for the LEPA footprint and a possible inability to respond to conditions identified by the Reliability Coordinator. However, LEPA is party to BA CFR00001 with MISO. Therefore, LEPA has limited BA responsibilities. MISO generally handles BA responsibilities. LEPA has only 10 members, which are all located throughout the state of Louisiana. LEPA’s BA Area has only 83 MWs of generation. Also, LEPA is considered to have only a low impact Control Center with primarily monitoring responsibilities and functional control over the 83 MW generator connected at 138 kV. No harm is known to have occurred. | To mitigate this violation, LEPA will perform the following actions: 1) obtain budget approval for BCC project; 2) purchase or secure a building lease, energy management system, remote terminal units, meters, and access controls; 3) update existing procedures to include new BCC processes and train system operators and support personnel on revised procedures; 4) establish a new, independent BCC; 5) implement an internal controls program (ICP) where LEPA will assess compliance of all applicable Standards on an annual basis. LEPA will document this annual assessment requirement in its ICP. It will present the results of the compliance assessment to LEPA executive management for awareness and approval of any corrective actions that may be required; 6) track and monitor compliance by sending a compliance survey monthly to the Energy Control Center Manager (ECCM). The survey requires the ECCM to check-off on prewritten survey questions for all applicable Standards. The ECCM is responsible for ensuring the answers to the survey are true and complete. Once the LEPA compliance consultant receives the survey, LEPA will schedule a meeting with the ECCM to review answers and concerns, as well as address any compliance deficiencies identified. It will discuss corrective action including self-reporting for any compliance deficiency. LEPA management can attend the post-survey meetings. Survey results will be an agenda item during LEPA staff meetings, which are called in and attended by LEPA upper management; and 7) train system operators and support personnel at the time it conducts the annual PER-005 required training. The LEPA ECCM coordinates and conducts the training with assistance from senior system operators. Training will include an overview of the LEPA ICP, the monitoring process, the surveys, and the annual compliance assessment process. | SERC determined that LEPA’s compliance history should not serve as a basis for applying a penalty. LEPA’s relevant compliance history includes SPP2011008479. However, that violation involved LEPA’s lack of a procedure regarding testing the loss of its primary functionality plan. Therefore, the prior violation did not involve the BCC, and the mitigation plan would not have detected or prevented the instant violation. LEPA self-reported the violation. However, LEPA only self-reported the violation after SERC identified the violation and suggested that LEPA self-report it. Effective oversight of the reliability and resilience of the BES depends upon self-reporting by Registered Entities. Since LEPA did not identify the violation, and only self-reported it due to SERC’s suggestion, SERC is not awarding mitigating credit for self-reporting. LEPA has been highly cooperative throughout the entire enforcement process relating to this violation. Throughout the enforcement process, LEPA voluntarily provided SERC with information that was timely, detailed, thoughtful, organized, and thorough. LEPA fully cooperated in SERC’s investigation of the violation and all associated mitigating activities and openly shared information regarding its processes, procedures, internal controls, assets, systems, and organization. SERC reviewed LEPA’s Internal Compliance Program and considered it to be a neutral factor in the penalty determination. LEPA did not identify the EOP-008 violation, and the violation is expected to last for over 18 years. This demonstrates a need for stronger preventative and detective controls. Accordingly, SERC determined that LEPA’s compliance program was a neutral factor. LEPA agreed to settle the violation. SERC is applying mitigating credit because it is important to promote prompt resolution of enforcement actions so that the LEPA’s focus is on mitigation and reducing risks to reliability.