## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2024-08-29 | NOC-2835 | Northeast Power Coordinating Council, Inc. (NPCC) | Constellation Energy Generation, LLC – Constellation Nuclear (Constellation) | NCR00778 | GO | Settlement Agreement | Neither Admits nor Denies | $90,000 (for NPCC2020023661, 2024-01241, and 2024-01242) | NPCC2020023661 | PRC-023-4 | R1 | Moderate | High | Severe | Self-Report | 2020-07-14 | 2019-11-07 | 2017-03-31 |  | 2022-10-08 | 2024-06-24 | Constellation submitted a Self-Report to NPCC stating that, as a Generation Owner, it was potentially in violation of PRC-023-4 R1 for failing to use one of the thirteen (13) criteria to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the Bulk Electric System (BES) for all fault conditions. Constellation discovered the potential violation on November 7, 2019, during a fleet-wide post-implementation review of PRC-023-4. During this review it was identified that two protective relays at the Constellation’s nuclear facility, James A. Fitzpatrick (“JAF”), were misclassified by the previous owner and that the relays in question were load responsive relays and therefore applicable under PRC-023-4 R1. Constellation performed an extent of condition (EOC), which found that one other relay, a Nine Mile Point, Unit 1 (“NMP1”) 115kV line overcurrent relay was also noncompliant, bringing the total number of potential noncompliant relays to three. The JAF 345kV line overcurrent relay and the JAF and NMP1 115kV line overcurrent relays were intended to be set using Criterion 1 from R1 of the Standard. Due to the EOC and scope clarification completed by Constellation, the originally planned remediation date was extended by approximately one year. Particularly, the discovery of the additional noncompliant NMP1 overcurrent relay during the EOC required that both ends of the 115kV line 4 be updated. In addition, the JAF 345kV line FS-10 is shared with another entity. With the logistics of coordinating with another entity between NMP1 and JAF, and emergent work associated with nuclear safety, mitigation of the violation was delayed. For NMP1 the violation began April 1, 2018, and, for JAF, March 31, 2017, and both ended on October 8, 2022, when Constellation changed the last noncompliant relay setting on the JAF 345kV line overcurrent relay to come back into compliance. The root cause was ineffective preventative controls, including Constellation’s failure to recognize the previous owner’s inadequate preventative controls when purchasing the generation plants. | NPCC determined that the violation of R1 posed a moderate risk to the reliability of the Bulk Power System (“BPS”) based on the following factors. Failing to use one of the stated criteria in R1 to prevent its phase protective relay settings from limiting transmission system loadability could lead to lines tripping due to loadability, which could interfere with system operators’ ability to take remedial action to protect system reliability. Specifically, by not having the three overcurrent relays within the scope of any criterion listed, the relays could trip outside the bounds of their required setpoints, resulting in a misoperation of their associated lines. Either of the in-scope lines tripping could result in an overload of a subsequent line or trip the attached nuclear plants, JAF and NMP1, which have an aggregate nameplate rating of 1,525 MW. Constellation’s Reliability Coordinator (NYISO), by comparison, is required to have operating reserves of approximately 1965MW. This violation also had a long duration of approximately 5.5 years, beginning the date Constellation registered JAF. The 345kV FS-10 line overcurrent relay was set at 478 MVA, which is approximately 33% of the normal line rating. Historical loading from 2020 shows that the 345kV FS-10 line reached a maximum of 661 MVA and demonstrates that the historical loading of the line can reach above the relay setpoint and potentially cause the line to trip due to loadability if not for Constellation’s communication-aided blocking scheme (described further below). Criterion 1 states that an entity must set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). Using Criterion 1, the original relay setpoint was set to trip at 33% of the highest seasonal Facility Rating as described in Criterion 1 (LTE), making the original setpoint 117% of the line rating lower than the required setpoint. The 115kV line 4 overcurrent relays were set at 79.7 and 95.6 MVA, respectively. This is approximately 66% of the normal line rating using the lowest setting. Historical loading from 2020 shows that the peak for that year was approximately 48 MVA. This would indicate that even if the communication scheme had failed during the noncompliant period, the line would not have tripped due to loadability. Nevertheless, the relay being set well below the normal line rating may not permit a system operator or generation control room operator to take action in an emergency situation when the communication is down. Using Criterion 1, the original relay setpoint was set to trip at 66% of the highest seasonal Facility Rating as described in Criterion 1 (LTE), making the original setpoint 84% of the line rating lower than the required setpoint. Constellation had a reduced risk of the lines inadvertently tripping due to a communication-aided protective control. The relays themselves were used in conjunction with a communication-aided line differential relay, which would trip the protected line or equipment should a failure of the communication circuit occur while there is sufficient emergency load on the circuit. The subject relays phase overcurrent supervisory elements (i.e., phase fault detectors) were associated with current-based, communication-assisted schemes (i.e., pilot wire), and therefore, the scheme was only capable of tripping in the event of a loss of communications. There were alarms in the JAF control room associated with both schemes, which also included monitoring of the integrity of the pilot wires. There have been no actual consequences to date as no pilot wire communication circuit failure or actual emergency line loading events have occurred that would trigger any of these in-scope relays. No event or harm occurred during the timeframe of the violation. | To mitigate the violation, Constellation has completed the following actions: 1) Outlined the strategy to modify the protective relay settings. 2) Outlined the strategy to perform a thorough Extent of Condition review. 3) Generated and distributed a Lessons Learned Communication (Nuclear Event Bulletin) to address the technical human performance behaviors. 4) Enhanced the applicable procedures to provide clearer guidance for implementation of NERC Standards. 5) Performed the setting changes for JAF 115kV Line 4 line overcurrent relay 50FDP-1ZL2N03 and NMP1 115 kV Line 4 line overcurrent relay RLY-(3D)50FDP. 6) Performed the setting change for JAF 345 kV Line FS-10 line overcurrent relay 50-1YL2N24. 7) Provided an interim status update on the line outage and status for Lines 10 and 4. 8) Completed Extent of Condition Review. | NPCC considered the following factors in its penalty determination: 1) Compliance History When assessing the penalty for the violations at issue in this Agreement, NPCC considered whether the facts of the violations constitute repetitive infractions and determined that Constellation had no relevant prior noncompliance with PRC-023-4. 2) Cooperation Constellation was cooperative throughout the entire enforcement process and provided requested information to NPCC that was detailed, organized, and thorough. 3) Self-Disclosure Constellation self-reported the violations described in this Agreement. Effective oversight of the BPS reliability depends on Registered Entities self-reporting. As such, NPCC seeks to encourage self-reporting of violations, and therefore, is applying mitigating credit in the instant case. 4) Settlement Constellation agreed to settle this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that NPCC, NERC, and the Federal Energy Regulatory Commission would otherwise expend to resolve the R1 violation. Additionally, it is important to promote prompt resolution of enforcement actions so that Constellation can focus on mitigation and reducing risks to reliability.
2024-08-29 | NOC-2835 | Northeast Power Coordinating Council, Inc. (NPCC) | Constellation Energy Generation, LLC – Constellation Nuclear (Constellation) | NCR00778 | GO | Settlement Agreement | Neither Admits nor Denies | $90,000 (for NPCC2020023661, 2024-01241, and 2024-01242) | 2024-01241 | PRC-023-4 | R3 | Minimal | Medium | Severe | Self-Report | 2020-07-14 | 2019-11-07 | 2017-04-01 |  | 2019-11-19 | 2024-06-24 | Constellation submitted a Self-Report to NPCC stating that it was potentially in violation of PRC-023-4 R3 because it failed to obtain agreement with its Planning Coordinator on two 115kV lines at Nine Mile Point, Unit 2 (“NMP2”) that use R1, criterion 8. The Standard requires Constellation to obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator regarding its use of the calculated circuit capability. The violation started on April 1, 2017, when Constellation failed to remain compliant with PRC-023-4 R3. The violation ended on November 19, 2019, when Constellation made the written R3 notification to the Planning Coordinator and the Planning Coordinator confirmed the agreement. The root cause was ineffective preventative controls, including Constellation’s failure to recognize the previous owner’s inadequate preventative controls when purchasing the generation plants. | The PRC-023-4 R3 violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. Violations of R3 are administrative noncompliances that could limit transmission loadability, interfere with system operators’ ability to take remedial action to protect system reliability, or impact reliable detection of and protection from all fault conditions by not having the same ratings or awareness of the applicable relays impacted by loadability. Constellation had a reduced risk of this occurring due to the fact that it did have a written agreement from the prior owner. Therefore, Constellation only needed to confirm the agreement. Constellation indicated there were no reported events due to this violation. No event or harm occurred during the timeframe of the violation. | To mitigate the violation, Constellation completed the following: 1) Enhanced the applicable procedures to provide clearer guidance for implementation of NERC Standards. 2) Restored compliance with R3. | NPCC considered the following factors in its penalty determination: 1) Compliance History When assessing the penalty for the violations at issue in this Agreement, NPCC considered whether the facts of the violations constitute repetitive infractions and determined that Constellation had no relevant prior noncompliance with PRC-023-4. 2) Cooperation Constellation was cooperative throughout the entire enforcement process and provided requested information to NPCC that was detailed, organized, and thorough. 3) Self-Disclosure Constellation self-reported the violations described in this Agreement. Effective oversight of the BPS reliability depends on Registered Entities self-reporting. As such, NPCC seeks to encourage self-reporting of violations, and therefore, is applying mitigating credit in the instant case. 4) Settlement Constellation agreed to settle this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that NPCC, NERC, and the Federal Energy Regulatory Commission would otherwise expend to resolve the R1 violation. Additionally, it is important to promote prompt resolution of enforcement actions so that Constellation can focus on mitigation and reducing risks to reliability.
2024-08-29 | NOC-2835 | Northeast Power Coordinating Council, Inc. (NPCC) | Constellation Energy Generation, LLC – Constellation Nuclear (Constellation) | NCR00778 | GO | Settlement Agreement | Neither Admits nor Denies | $90,000 (for NPCC2020023661, 2024-01241, and 2024-01242) | 2024-01242 | PRC-023-4 | R4 | Minimal | Lower | Severe | Self-Report | 2020-07-14 | 2019-11-07 | 2018-01-01 |  | 2022-04-19 | 2024-06-24 | Constellation submitted a Self-Report to NPCC stating that it was potentially in violation of PRC-023-4 R4 because it failed to provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with the applicable JAF transmission line relays. R4 requires that each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1, criterion 2 as the basis for verifying transmission line relay loadability provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. In this case, there were two instances of violation associated with the requirement. After coming back into compliance in 2019 and making the required 2020 submission, Constellation experienced a failure in the notification system it used, resulting in Constellation missing the 2021 notification. A third-party engineering firm was contracted to evaluate relays subject to PRC-023-4. The resulting evaluation completed in January 2021 showed that only one JAF relay, the 345kV line overcurrent relay 50-1YL1N06, was subject to PRC-023-4 R4. The first instance of violation started on January 1, 2018, when Constellation failed to remain in compliance with PRC-023-4 R4. The violation ended on November 22, 2019, when Constellation provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with the in-scope JAF transmission line relays. The second instance started on January 1, 2022, when Constellation failed to remain in compliance. The violation ended on April 19, 2022, when Constellation provided its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits. The root cause was ineffective preventative controls, including Constellation’s failure to recognize the previous owner’s inadequate preventative controls when purchasing the generation plants. | The PRC-023-4 R4 violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. Violations of R4 are administrative noncompliances that could limit transmission loadability, interfere with system operators’ ability to take remedial action to protect system reliability, or impact reliable detection of and protection from all fault conditions by not having the same ratings or awareness of the applicable relays impacted by loadability. Constellation had a reduced risk of this occurring due to the fact the Planning Coordinator could use the previously calculated circuit capability. Additionally, the scope of the R4 violation was limited to one relay. Constellation indicated there were no reported events due to this violation. No event or harm occurred during the timeframe of the violation. | To mitigate the violation, Constellation completed the following actions: 1) Outlined the strategy to perform a thorough Extent of Condition review. 2) Completed Extent of Condition Review. 3) Generated a recurring activity to track the annual Requirement R4 submittal for JAF. 4) Restored compliance with R4. | NPCC considered the following factors in its penalty determination: 1) Compliance History When assessing the penalty for the violations at issue in this Agreement, NPCC considered whether the facts of the violations constitute repetitive infractions and determined that Constellation had no relevant prior noncompliance with PRC-023-4. 2) Cooperation Constellation was cooperative throughout the entire enforcement process and provided requested information to NPCC that was detailed, organized, and thorough. 3) Self-Disclosure Constellation self-reported the violations described in this Agreement. Effective oversight of the BPS reliability depends on Registered Entities self-reporting. As such, NPCC seeks to encourage self-reporting of violations, and therefore, is applying mitigating credit in the instant case. 4) Settlement Constellation agreed to settle this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that NPCC, NERC, and the Federal Energy Regulatory Commission would otherwise expend to resolve the R1 violation. Additionally, it is important to promote prompt resolution of enforcement actions so that Constellation can focus on mitigation and reducing risks to reliability.
2024-08-29 | NOC-2836 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | GO, TO, DP | Settlement Agreement | Neither Admits nor Denies | No penalty | 2022-00732 | PRC-005-6 | R3 | Moderate | High | Lower | Self-Report | 2022-05-10 | 2016-11-01 | present (expected to end when mitigation is completed on 11/20/2025) | 2025-11-20 | TBD | TBD | TVA notified SERC that it was noncompliant with PRC-005-6 R3. TVA failed to maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5 and Table 5. After the initial discovery, TVA submitted nine Finding Updates. SERC dismissed one of the Finding Updates leaving the total number of instances at nine, the initial Self-Report and eight accepted finding updates. The nine instances are spread across different business units of TVA that correlate to the Generator Owner (GO), Transmission Owner (TO), and Distribution Provider (DP) functions. The method of discovery, root causes, and mitigating activities vary widely from instance to instance. With such a high number of instances spread across different business areas with different causes, SERC has concluded that TVA has a systemic issue in its Preventative Maintenance (PM) related to Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. TVA submitted the initial PRC-005-6 R3 Self-Report. TVA’s non-nuclear generation Power Operations (PO) business unit, under the GO function, discovered that a work order was closed on April 30, 2018 without documentation of required maintenance activities for four overcurrent relays at the Raccoon Pumped Storage generation facility (RPS). This noncompliance was discovered while executing a periodic evidence review, which is part of TVA’s internal control program. During the evidence review, which occurred in September of 2021, TVA determined that the RPS PM work order was closed with required maintenance activities for three phase-overcurrent (51T) relays and one neutral overcurrent (50TN) relay missing. On July 13, 2022, TVA performed relay maintenance and testing on the four-station service transformer overcurrent relays bringing them back into compliance. While TVA was performing an extent of condition (EOC) review, it submitted eight additional Finding Updates. TVA submitted a second instance. On June 29, 2022, TVA discovered an issue while reviewing a random sample of maintenance records. TVA discovered that the Bull Run Fossil (BRF) 250V direct current (DC) battery bank four calendar month testing interval was not completed in accordance with Table 1-4. According to the test records, the last four calendar month maintenance and testing was performed on January 5, 2022. The next maintenance and testing interval should have occurred on or before May 31, 2022. On June 1, 2022, TVA performed the maintenance and testing bringing the battery back into compliance one day late. TVA had an internal control designed to prevent such a noncompliance, but it failed. The control, an automated email with preventative maintenance reminders, worked as intended but no action was taken on receipt of the email. For the EOC, TVA utilized the random sampling method that had close to a 100% equipment review rate from November 2019 to June 2022. TVA submitted a third instance. On June 23, 2022, during a battery maintenance review of local power company (LPC), under TVA’s DP functionality, TVA discovered that a four calendar month testing interval for Ebenezer 161kV substation was not completed in accordance with Table 1-4. According to the test records, the last four calendar month maintenance and testing was performed on February 27, 2020. The next maintenance and testing interval should have occurred on or before June 30, 2020. On August 28, 2020, TVA performed the maintenance and testing, bringing the battery back into compliance 58 days late. On January 23, 2023, TVA completed an EOC consisting of a review of LPC battery maintenance and testing records to ensure tests have been performed on the proper interval on all LPC battery assets. The review determined there were no additional instances of noncompliance. TVA submitted a fourth instance. On December 20, 2022, while TVA TO was performing an internal review of PRC‐005 maintenance records, it discovered an error in a design drawing. The design drawing incorrectly identified the breaker from Watt Rd substation to the high side of the transformer bank as non‐Bulk Electric System (BES). Due to this design drawing error, Protection System components, and DC supply at Watt Rd substation were not identified as BES and requiring PRC‐005 maintenance and testing. As a result of the implementation of the revised BES definition on July 1, 2016, Protection System components previously not subject to the testing and maintenance requirements of PRC‐005 were brought into scope. The first PRC‐005 activities due after the July 1, 2016, effective date would be the Table 1‐4(a) vented lead acid (VLA) battery 4 calendar month maintenance and testing activities. The battery maintenance and testing should have occurred on or before November 30, 2016. On January 31, 2023, TVA completed the VLA battery maintenance and testing, bringing the battery back into compliance. On December 13, 2023, TVA completed the Table 1-1 and Table 1-5 maintenance and testing activities to bring the protective relay and control circuitry associated with protective functions back into compliance. On May 18, 2023, TVA completed its EOC review. The EOC reviewed all looped 69kV systems to verify PRC-005 applicable equipment has been the PM program. The EOC did not identify any additional instances of noncompliance. TVA submitted a fifth instance. On May 16, 2023, a TVA TO reviewed the measurement software form that TVA transmission was using to meet compliance for PRC-005-6 Table 1-4. It discovered that the software was providing only the battery intercell connection resistance, and not the battery terminal connection resistance required by PRC-005-6 Table 1-4. TVA transmission started using the software prior to enforcement of PRC-005-2 for measurements required and missed that an upgrade was required in 2019 to verify the additional measurements for the battery terminal connection resistance. The PRC-005-6 Table 1-4(a) required maintenance activity to verify battery terminal connection resistance within the maximum maintenance interval of 18 calendar months was never completed. As such, the PRC-005-2 Implementation Plan milestone was due on or before October 31, 2016. All 18 calendar month requirements per PRC-005-6 Table 1-4 for 226 batteries were not met since the battery terminal connection resistance were not verified. TVA performed an EOC review and determined all TVA transmission PRC-005-6 stations had PMs performed under the current measurement software version. Additionally, there have been reviews of the totality of the current measurement software form to ensure all PRC-005-6 Table 1-4 requirements were met, except for the battery terminal connection resistance. TVA submitted a sixth instance. On June 12, 2023, while performing scheduled PRC-005 maintenance activities, TVA PO, under the GO function, discovered that the static frequency converter (SFC) protective relays at RPS, also subject to the initial Self-Report, were not identified as PRC-005 assets despite having generator trip capability. The Protection Systems had been incorrectly assumed to be de-energized during generation and thus excluded. TVA completed an EOC by reviewing Protection System components associated with BES generators in the PO fleet with pump mode operation capability and did not discover any additional instances of noncompliance. TVA submitted a seventh instance. On July 5, 2023, TVA PO, under the GO function, was notified by Gallatin Combustion Turbine Plant (GCT) personnel that a new PRC-005 battery bank was installed as part of an upgrade to the GCT power distribution system. GCT inquired about who was responsible for initiating the NERC PMs to track maintenance activities. After further investigation, it was found that the battery bank had exceeded the required PRC-005 Table 1-4(a) 4-calendar months maximum maintenance interval. The GCT Station Service Building 125V DC battery bank exceeded the maximum maintenance interval of 4 calendar months per PRC-005 Table 1-4(a). The asset was installed and placed in service on August 8, 2022. The next maintenance interval should have occurred on or before December 31, 2022. On July 18, 2023, GCT maintenance personnel completed battery maintenance and testing, bringing the battery back into compliance. On August 22, 2023, TVA completed its EOC review. The review consisted of a verification check to determine if any other similarly classified upgrade projects had any missing battery system installations not listed within the Maximo database. The review determined there were no additional instances of noncompliance. TVA submitted an eighth instance. On July 10, 2023, TVA LPC, part of the DP function, discovered that various required maintenance activities were not being performed for the vented lead-acid batteries (VLA) at the Blountville substation. According to test records, the 4-calendar month maintenance performance did not include the inspection for unintentional grounds. This inspection for unintentional grounds is documented on the 18 calendar month inspection. According to test records, the 18 calendar month maintenance performed did not include: battery terminal connection resistance, battery intercell or unit-to-unit connection resistance, or physical condition of battery rack. Test records also show that, comparisons of cell/unit measurements to a baseline have not been performed and a battery performance capacity test has not been performed. On August 7, 2023, TVA completed all 4-four calendar month maintenance activities bring the Blountville battery back into compliance with 4-four calendar month activities (2470 days late). On November 8, 2023, TVA completed all 18 calendar month maintenance activities bring the Blountville battery back into compliance with 18 calendar month activities (2563 days late). On November 9, 2023, TVA completed the 6 six calendar year performance testing activities bring the Blountville battery back into compliance with the six calendar year activities (2563 days late). On October 27, 2023, TVA completed its EOC review. The review was performed on PRC-005-6 applicable LPC-owned batteries to determine if additional noncompliance existed. The population size of LPC-owned batteries is nine elements. A population of eight PRC-005-6 applicable LPC-owned batteries was reviewed, excluding the Blountville noncompliance. The EOC reviewed the last maintenance performance for both 4-month and 18-month maintenance activities to ensure adequate forms are used to support evidence of compliance with PRC-005 requirements. The results from the EOC determined there was no additional noncompliance outside of the reported Blountville noncompliance. TVA submitted a ninth instance. On September 26, 2023, while reviewing PRC-005 design change impacts, TVA PO, under the GO function, discovered that Shawnee Fossil Plant (SHF) unit station service transformer #5 (USST-5) had active Buchholz protection capable of tripping a BES generator that was not identified as a PRC-005 device. After further investigation, no maintenance records could be located for the Buchholz relay needed to satisfy the PRC-005-6 100% implementation milestone for 6-calendar year Sudden Pressure Relaying Components. SHF USST-5 Buchholz relay did not satisfy PRC-005-6 Table 5 maintenance activity requirements by the PRC-005-6 100% implementation deadline of January 1, 2023. On November 12, 2023, TVA performed maintenance and testing per Table 5 maintenance activities on the USST-5 Buchholz relay bringing it back into compliance. TVA is currently performing the EOC review as part of mitigation. The EOC consists of reviewing all Buchholz protection systems across the fossil, hydro, and gas generation fleet to determine if similar issues exist. This violation started on November 1, 2016, (Instance 4 and Instance 8), when TVA failed to maintain its Protection System batteries within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals; and is expected to end on November 20, 2025, (Instance 5), when TVA completes its 18 calendar month battery maintenance activities. The duration is predicted to be 3306 days, or about 9 years. As the issues related to PM are systemic, a total of five distinct root causes have been identified. They are a deficient procedure or process, lack of or ineffective internal control, change management, lack of understanding, and training. Specifically, for Instance 1, TVA’s procedure failed to include a verification of evidence packages prior to the closing of a work order. TVA will implement a PM work order evidence checklist. Instance 2 was due to a failure to have an internal control in place for management to review quarterly PM performance for timely completion, proper documentation, and work order closure. TVA will revise its internal control to include a better method of communication and clarity of due dates. Instance 3 was caused by a lack of understanding of the LPC on the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals. Instance 4 was caused by a deficient PRC-005 applicability procedure. Radial systems are not considered BES and so are not in scope of PRC‐005. This led to the Protection System being excluded as applicable to PRC‐005. The procedure did not specifically address situations where a potential 69kv loop causes the 161kV feeder to the transformer to be BES. Instance 5 was caused by poor change management. When the software measurement was upgraded, TVA failed to verify and validate the accuracy of the change. Instance 6 was caused by a deficient procedure. The procedure did not include specific language instructing TVA plant operations personnel to obtain plant or regional engineering concurrence before excluding or removing devices from the PRC-005 Protection System Maintenance Program (PSMP). Instance 7 was caused by a deficient process. The PO Design Change process did not have adequate roles, responsibilities, or timeliness expectations to verify that PMs are created for new PRC-005 assets. Instance 8 was caused by using an inadequate or inaccurate form to document maintenance activities. Also, the frequency of the training for personnel was insufficient to maintain the required knowledge and skill to perform the job. Instance 9 was caused by a lack of understanding of documents relied upon for determining applicability of PRC-005. TVA PO’s utilizes station electrical drawings to identify PRC-005 applicable components throughout its generation fleet. While reviewing the SHF Protection System for PRC-005 applicability, TVA PO NERC Reliability staff overlooked the USST-5 Buchholz relay because of unconventional ANSI device numbering used in the drawings—labeled “97T” which is a non-specific relay designation instead of the standard “63” for fault pressure relays. As a result, the Buchholz relay was never enrolled into the TVA PO PRC-005 program inventory and not assigned a NERC PM work order to ensure that it was maintained in accordance with PRC-005-6, Table 5 requirements. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). For those instances related to relay maintenance (instances 1, 5, 6, and 9), the primary risk was the unintended tripping of generation stations with the missed maintenance. Specifically: For Instance 1, TVA’s failure to complete the required maintenance and testing activities within the defined interval could result in Protection System failures and misoperations impacting a larger portion of the transmission and generation system than necessary when downstream Protection System devices would be required to operate due to the failures, potentially impacting 476 MVA of generation. However, differential relays are the primary protection for the station service transformer B. If the overcurrent relays failed to respond to a fault within their zone of protection, differential protection is available to address the fault. Further, fault current is limited through the Station Service Transformer B due to a neutral resistor. For Instance 4, a fault not cleared by primary protection could result in damage to TVA equipment in the 69kV system and possible instability at Melton Hill and possibly Fort Loudoun. However, the protection includes a modern microprocessor protective relay and a breaker failure backup scheme that would reduce the probability of a complete failure of the protection system. Further, a review of misoperations shows that no issues have been discovered due to lack of maintenance at this point. For Instance 6, a Misoperation of the SFC protective relays may have been possible while RPS Units 1 and 3 were online generating. Failure of the relays to operate during a fault condition or unnecessary operation during generation are possible scenarios, thus impacting 952 MVA of generation. However, the SFC Protection System has overlapping zones of protection such that if one of the SFC relays fails to operate for a fault on an equipment within its protective zone, one of the other relays can detect and clear the fault. For Instance 9, a false operation of the Buchholz relay due to overdue maintenance could have removed SHF Unit 5 generator from the BPS. However, TVA PO's protection philosophy where Sudden Pressure (63SP) and Buchholz Relays are installed, is to set Sudden Pressure Relays (63SP) to trip and Buchholz relays to alarm-only operation. SHF USST-5 is protected by both 63SP and Buchholz Relays. Maintenance records show that the 63SP has been maintained in accordance with PRC-005-6 Table 5 requirements. Additionally, SHF Unit 5 is rated at 175 MVA and makes up only 0.5% of TVA’s total generating capacity. For those instances related to battery maintenance (instances 2, 3, 5, 7, and 8), the primary risk was equipment associated with the batteries in question failing to operate correctly. Specifically: For Instance 2, the four calendar month battery maintenance was only exceeded by one day, thus posing a minimal risk to the BES. For Instance 3, the relay powered by the battery detects faults on a 161kV transmission line only when in alternate configurations of a local network. During the period of noncompliance, the local network was not in an alternate configuration, therefore, the relay powered by the subject battery was not required to detect faults on the BES. Failure of the battery could not have resulted in an impact to the BES. For Instance 5, although the 18 calendar month maintenance and testing was never performed. The chance of impact occurring is negligible because the TVA engineering design specifies for bolted battery terminal connections and any issues or problems i.e., degradation of the terminal connections from corrosion or heat, would be identified during quarterly or annual substation preventative maintenance visual and Infrared (IR) inspections. For Instance 7, the GCT Station Service Building 125VDC Battery Bank supplies backup DC power to Balance of Plant (BOP) protection systems which can act to trip generators of GCT Units 1-8. During the duration of noncompliance, Units 1-3 and 5-8 were connected to the BES for generation while Unit 4 remained in outage. Loss of normal power without available backup DC power would have prevented operation of the BOP protection system during fault and other abnormal system conditions, potentially leading to damage to BES equipment. However, this risk was minimized because the GCT battery system is installed with monitoring and alarming capability. It has the ability to detect charger overvoltage, charger failure, and unintentional DC grounds, along with alarm outputs to the plant control room for immediate corrective response. Furthermore, commissioning tests were performed on the new battery bank per PO's protocol for new protection system assets which would have revealed any defects or potential issues. For Instance 8, the loss of battery would result in loss of relaying and tripping capability for two 161kV BES breakers at Blountville. Backup protection schemes would result in backup tripping at Sullivan and N Bristol, with no loss of load. However, maintenance activities and inspection of the battery/charger were being performed on a monthly basis. No harm is known to have occurred. | To mitigate this violation, TVA has or will perform the following actions: 1) [Instance 1] updated Program Documents to establish NERC compliance responsibilities; 2) [Instance 1] implemented PM work order (WO) procedure and evidence checklist to verify required activities are completed and documented; 3) [Instance 1] revised program to sample PRC-005 PM WOs to validate compliance and quality documentation (Internal Control PO.PRC-005.R3.007); 4) [Instance 1] completed remediation testing to bring overcurrent relay protection for SST B into compliance; 5) [Instance 2] distributed a Data Sharing Operational Experience (OE) stating the Maximo field WO Actual Finish Date should be used to set the next performance date; 6) [Instance 2] established a recurring action for BRF leadership to review BRF Quarterly PM performance for timely completion, proper documentation, and WO closure; 7) [Instance 2] evaluated and revised the failed internal control; 8) [Instance 3] lead discussion with battery owner regarding maintenance activities and maximum maintenance intervals; 9) [Instance 3] distributed an OE to all LPC's with PRC-005 applicable batteries; 10) [Instance 3] enhanced PRC-005 tracking process with applicable LPC for Ebenezer 161; 11) [Instance 3] completed PRC-005-6 R3 Table 1-4(a) activities to bring Protection System Station dc Supply Using Vented Lead Acid (VLA) Batteries back into compliance; 12) [Instance 4] revised PRC-005 applicability procedure TVA-SPP-30.028 Attachment 2 for BES applicability showing that Radial configurations should be checked for looped configurations to verify Looped 69kV BES configurations are screened as applicable; 13) [Instance 5] completed training on updated procedure TVA-SPP-30.028; 14) [Instance 4] completed PRC-005-6 R3 Table 1-1 and Table 1-5 activities to bring Protective Relay and Control Circuitry Associated with Protective Functions back into compliance; 15) [Instance 5] updated Measurement software form; 16) [Instance 5] revised TVA Transmission & Power Supply (TPS) program document(s) to require a PRC-005 compliance review to verify changes to the regulatory standard, testing procedures, field test manuals, or test equipment comply with the PRC-005 standard when any of those items change; 17) [Instance 5] upgraded measurement test equipment; 18) [Instance 5] will train Stakeholders of Program Documents on content of changes; 19) [Instance 5] will train employees to use new form and updated test equipment; 20) [Instance 5] will complete 100% of 18-calendar month PMs to meet all requirements at PRC-005 Stations; 21) [Instance 6] enrolled PRC-005 assets identified in the EOC into Maximo for documentation and corrective maintenance. Revise equipment UNIDs, add devices to the PRC-005 Collection, and establish PMs; 22) [Instance 6] revised procedure for PO NERC Reliability to obtain Plant or Regional Engineering concurrence before excluding or removing device from PRC-005 PSMP; 23) [Instance 6] completed one-time training of impacted staff on the revision of procedure; 24) [Instance 6] will perform remediation testing for the SFC protective relays to end the potential noncompliance; 25) [Instance 7] created NERC PMs for GCT Station Service Building 125VDC Battery Bank in Maximo; 26) [Instance 7] completed 4-month preventive maintenance testing for GCT PM 164798 WO 123854907 and verified that WO evidence is in accordance with PRC-005 Table 1-4(a); 27) [Instance 7] reviewed PO NERC Reliability PRC-005 Guidance Document and enhanced instructions about NERC PM requirement for new PRC-005 assets. Identified responsible party and timeline for completion; 28) [Instance 7] completed one-time training of Design Change Notice (DCN) Project Managers on the revised NERC PM creation requirement in the PRC-005 Guidance Document; 29) [Instance 8] completed 4 calendar month and 18 month activities; 30) [Instance 8] ensured proper forms are updated and utilized for maintenance activities; 31) [Instance 8] provided coaching and training to owner of Blountville TN Batteries; 32) [Instance 8] completed 6-year performance test; 33) [Instance 9] documented SHF USST-5 Buchholz relay in Maximo inventory and assignment to NERC PM; 34) [Instance 9] completed test SHF USST-5 Buchholz relay per PRC-005-6 Table 5; 35) [Instance 9] will revise plant drawing(s) to show SHF USST-5 Buchholz relay with proper ANSI device numbering; 36) [Instance 9] will review applicable Buchholz protection at all BES Fossil generating facilities to ensure compliance with PRC-005-6 maintenance requirements; 37) [Instance 9] will review applicable Buchholz protection at all BES Hydro generating facilities to ensure compliance with PRC-005-6 maintenance requirements; and 38) [Instance 9] will review applicable Buchholz protection at all BES Gas generating facilities to ensure compliance with PRC-005-6 maintenance requirements. | SERC considered TVA’s PRC-005-6 R3 compliance history not to be an aggravating factor in the penalty determination because TVA is a federal entity. TVA has submitted a comprehensive Mitigation Plan. To ensure the potentially complex mitigation is effective, SERC needs additional insight into the internal controls of the plan. As a nonmonetary sanction, TVA will be required to provide a demonstration of the controls that failed, any newly created and/or modified controls, and how both fit into the overall TVA internal control program related to preventative maintenance. The intention of this demonstration is to inform SERC about TVA’s mitigating activities to their internal controls and related program, not to review or evaluate TVA’s programs that are outside the scope of this Settlement Agreement.
2024-08-29 | NOC-2837 | SERC Reliability Corporation (SERC) | Louisiana Energy & Power Authority (LEPA) | NCR01116 | GO | Settlement Agreement | Admits | 0 | 2023-00112 | PRC-005-6 | R3 | Moderate | High | High | Self-Report | 2023-01-30 | 2020-01-01 | 2022-11-17 |  | 2024-03-15 | 2024-07-31 | On January 17, 2023, SERC sent LEPA an audit notification letter notifying it of a compliance audit scheduled for May 15, 2023 through May 19, 2023. On January 30, 2023, LEPA notified SERC that it was noncompliant with PRC-005-6 R3. LEPA failed to maintain its Protection System Relaying, Sudden Pressure Relaying, and associated Control Circuitry Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1, 1-5, and 5 for a total of 15 devices. This noncompliance affects LEPA Unit 1, which is a 83 MW generator and is the only generator owned by LEPA. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. LEPA has a single 75 MW generating unit that it has failed to maintain compliance obligations for since its registration date of April 27, 2016 as shown by the multiple instances of noncompliance since the registration date. LEPA’s failure to maintain the 15 devices, which account for 12% of its PRC-005-6 devices, within the defined six-calendar-year interval could have resulted in the unit unnecessarily tripping or devices failing to trip which would require down stream devices to operate unnecessarily. This also would have been a lesser risk level if LEPA hadn't had as many compliance-related issues relating to the one unit as it has had. The risk from the noncompliance is reduced because LEPA unit 1 is the only facility owned by LEPA and is only a 75 MW facility. In addition, LEPA does not utilize LEPA unit 1 to meet native load obligations. LEPA sells the output to the MISO market. If a trip occurred, it most likely would have only resulted in an economic harm to the purchaser and not a reliability harm since LEPA sells the output from one 75 MW facility to the market. The purchaser would most likely be able to produce enough generation to make up for the lost generation and would only likely be affected in that way for about two hours until it can purchase generation from another source. Contingency reserves would have been available in the event of a trip to offset loss of generation for any reason. Finally, LEPA is a minimal sized entity that has only 10 members, which are all located throughout the state of Louisiana. No harm is known to have occurred. | To mitigate this violation, LEPA has or will perform the following actions: 1) created an accurate PRC-005 spreadsheet to manage and track PRC-005-6 obligations; 2) utilize a monthly compliance questionnaire sent to the Energy Control Center Operations Manager and CIP Senior Manager to answer compliance related questions including if any unresolved maintenance activities have occurred. This will require the Energy Control Center Operations Manager and CIP Senior Manager to be familiar with the new spreadsheet and be aware of any upcoming or unresolved maintenance. The Energy Control Center Operations Manager & CIP Senior Manager will also consult and direct the LEPA Unit 1 Plant personnel on maintenance activities. Plant personnel will be made aware of the PRC-005-6 spreadsheet and any upcoming maintenance activities; 3) the LEPA Energy Control Center Manager will schedule a reoccurring meeting with plant personnel when four-month battery testing is due and the DC Power Supply report is received; and 4) the Energy Control Center Operations Manager will review records with plant personnel and review the Protection System tracking spreadsheet to ensure there is a plan in place to cover any upcoming PRC-005 related maintenance and any other NERC related plant items or activities. | SERC considered LEPA’s compliance history to be an aggravating factor. SERC is considering two separate prior noncompliances as aggravating the disposition track: SPP2017018290 and 2021-00574. Although SPP2017018290 was a Compliance Exception, SERC is elevating the disposition track in part because of this prior due to the fact that the mitigating activities included the creation of a spreadsheet list of all PRC-005 devices. LEPA either failed to maintain this spreadsheet from 2019 forward or failed to identify all required PRC-005 devices in 2019. This list should have directly prevented the instant noncompliance. For 2021-00574, LEPA stated that it failed to conduct a thorough walk-down for the previous noncompliance’s EOC as LEPA was unable to conduct a comprehensive walk-down while the unit was online, which is why it did not discover these occurrences during the prior noncompliance. LEPA failed to complete the walk-down when the unit was offline. Therefore, SERC is elevating the filing track for both SPP2017018290 and 2021-00574. In addition, SERC is imposing a non-monetary sanction on LEPA. LEPA's Chief Executive Officer must sign the settlement agreement as a direct sanction. It is critical for the executive leadership to continue to support and be fully engaged in LEPA's effort to improve its security and compliance posture. This continued involvement will ensure continued success in its compliance program. Other Factors: Although LEPA self-reported the Alleged Violation, LEPA only self-reported the Alleged Violation after receiving an audit notification letter from SERC. Effective oversight of the reliability and resilience of the BES depends upon self-reporting by Registered Entities. Since LEPA identified the Alleged Violation on June 27, 2022, but did not timely self-report the Alleged Violation to SERC until January 30, 2023, which was after it received notice of an upcoming audit, SERC is not providing self-reporting credit. Although LEPA has been cooperative with SERC throughout the enforcement process relating to this Alleged Violation, it inhibited the timely processing of this Alleged Violation by providing SERC with incorrect information and evidence containing numerous discrepancies. Therefore SERC is not providing cooperation credit.