## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2025-04-24 | NOC-2858 | SERC | Florida Power & Light Co. (FPL) | NCR00024 | GO, TO | Settlement Agreement | Admits | 120000 | 2022-01063 | FAC-008-5 | R6. | Moderate | Medium | Moderate | Audit | 2022-07-19 | 2007-06-18 | Present | 2025-06-01 | TBD | TBD | SERC determined that FPL was noncompliant with FAC-008-5 R6. FPL failed to have Facility Ratings for its Facilities that are consistent with the associated Facility Ratings methodology (FRM). SERC determined that this noncompliance began under FAC-009-1 R1 and spanned to FAC-008-5 R6. On February 21, 2022, SERC sent FPL an audit notification letter for an onsite audit of FAC-008-5 R1, R2, R3, and R6. SERC conducted the on-site audit from June 20, 2022 through June 24, 2022. The audit team walked down four transmission substations and identified incorrect Facility Ratings at three of the four substations. The stations with incorrect Facility Ratings were 138 kV, 230 kV, and 500 kV. To determine an initial scope of the noncompliance, SERC identified and required FPL to walk-down eight Transmission Facilities and eight Generation Facilities and report the findings to SERC. Of the eight Transmission Facilities, FPL identified one incorrect rating on a 230 kV line that resulted in a 25% derate. Of the eight Generation Facilities, FPL identified incorrect Facility Ratings at one generation station and incorrect equipment ratings or missing equipment ratings at two additional generation stations, and one with an incomplete walk-down where an outage is required to field verify current transformers. For the complete extent of condition assessment, FPL completed a walk-down of all of its Transmission Facilities and Generation Facilities. For the Transmission Facilities, FPL identified that, out of 1822 Facilities, it had 153 incorrect Facility Ratings (8.4%) that did impact the Most Limiting Element (MLE) and Facility Rating. Specifically, for the 230kV class, it had 86 incorrect Facility Ratings with one exceedance (one time exceeded). The maximum exceedance was 67 MVA on a 568 MVA line with a 25% derate. For the 230kV class of incorrect Facility Ratings, there were 32 derates ranging from 0.41%-10%, 26 derates ranging from 10.92%-19%, 25 derates ranging from 20.84%-26%, 1 derate at 37%, 1 derate at 40% and 1 derate at 45%. For the 138kV class, it had 37 incorrect Facility Ratings and there were no exceedances of the correct Facility Ratings. For the 138kV class of incorrect Facility Ratings, there were 16 derates ranging from 1%-9%, 11 derates ranging from 12%-20%, 9 derates ranging from 20.73%-25%, and 1 derate at 48% (jumper). For the 115kV class of incorrect Facility Ratings, there were 30 incorrect Facility Ratings and there were no exceedances of the correct Facility Rating. For the 115kV class of incorrect Facility Ratings, there were 12 derates ranging from 1%-10%, 7 derates ranging from 12%-20%, 3 derates ranging from 23%-28%, 3 derates ranging from 31%-36%, 4 derates ranging from 43%-46%, and 1 derate at 93% (line – jumper/metering PT/CT). FPL found that it did not have any incorrect ratings that did not impact the MLE or Facility Rating. For the Generation Facilities, FPL has completed the walk-down assessment of all of its 180 Generation Facilities. FPL identified that it had 12 Facility derates and 3 Facility uprates. The derates ranged from 0.4%-8.65% and the uprates were 1.5%. FPL did not exceed the correct Facility Rating in any instance. The causes of this noncompliance were ineffective controls to manage required training, ineffective validation control and ineffective controls to prevent failure to initiate the Management of Change (MOC) process. While FPL tracked its FAC-008 General Training through its Learning Management System, it did not track completion of the FAC-008 worksheet training and as a result, FPL did not train some of the individuals that should have taken the FAC-008 worksheet training. FPL’s post construction inspection review was not documented and resulted in failures to identify some differences in construction versus design. FPL personnel failed to initiate the MOC process due to a gap in understanding of when to apply for a like-for-like change. This noncompliance started on June 18, 2007, when FAC-009-1 R1 was enforceable on FPL and FPL failed to rate its Facilities in accordance with the FRM, and is scheduled to end by April 30, 2025, when FPL completes its mitigating activities to revise all incorrect element ratings and Facility Ratings identified during the walk-down assessment. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. FPL’s failure to establish Facility Ratings consistent with its FRM could result in violations of System Operating Limits, unnecessary facility trips, damage to facilities, and erroneous planning. The risk is reduced as FPL identified only one exceedance of the correct Facility Rating after a complete walk-down of its transmission and generation facilities. The one exceedance (exceeded only one time) for the 230kV class and had a maximum exceedance at 67 MVA on a 568 MVA line with a 25% derate. In addition, of the derated Facilities, 60 of the 153 derates were 10% or less (39% of all derated Facilities) and 104 of the 153 derates were 20% or less (68% of all derated Facilities). In the case of the 93% derate, the Facility in question did not exceed the correct Facility Rating. Its purpose is to be used as an alternate way to feed two substations. The Facility was only used twice in the last 12 months for this purpose and had a maximum load of 5 MVA on the first date and 13 MVA on the second date, below the correct Facility Rating of 15 MVA. No harm is known to have occurred. | To mitigate this noncompliance, FPL has or will perform the following actions: 1) added a FAC-008 Power Delivery (PD) worksheet training course to the Learning Management System (LMS), so that accurate training records for each individual could be tracked; 2) identified and trained the individuals involved in the PD FAC worksheet process and tracked the training to ensure personnel understood responsibilities and the need to comply with FAC-008; 3) performed a detailed walkdown of the 26 transmission facilities and identified that the problem areas were related to: (i) Inadequate tracking and controls of PD FAC training; (ii) PD FAC Worksheet not matching the as-built; and (iii) PD FAC Workflow Process Breakdowns, and (iv) As-built drawing not reflective of installed equipment; 4) implemented a walkdown procedure to standardize and ensure accurate results of the transmission and substation facility walkdowns; 5) finalized the walkdown schedule of Transmission Facilities operated at 100kV and above (includes transmission lines and stations) and Generation facilities for FPL, including the former service area known as Gulf Power. FPL will walkdown 100% of applicable transmission facilities subject to FAC-008; 6) developed an enhanced training plan (e.g., timing of training, tracking of completions) for training of the individuals involved in the PD FAC worksheet process; 7) complete walkdowns with an aggregate completion of 100% of transmission facilities transmission and generation per FPL’s walkdown schedule utilizing Power Delivery’s and Power Generation’s respective Walkdown Procedure. Collect and identify all discrepancies found and discrepancies will be addressed as needed. FPL will submit the SERC quarterly reporting template within thirty (30) days of quarter end; 8) review all existing FAC-008 controls and will revise based on the lessons learned from the walkdown of 100% of transmission and generation facilities; 9) developed an instruction sheet for use as a job aid in generating facility walkdowns to be utilized for self-performing walkdowns across FPL fleet; 10) developed and documented work practices for capturing changes as a result of emergency repairs or changes following post-storm or extreme weather restoration; 11) trained employees on Extreme Weather Restoration – Change Management Process. 12) developed and implemented the following controls to prevent additional instances of non-compliance: a) For generation: (i) reviewed what constitutes “like-for-like” change in field process and taking action to ensure FAC-008 SME notification for any inverter swaps fleetwide. b) For transmission: (i) changed engineering drawing standards for future projects to simplify field construction in order to reduce as-builts; (ii) developed and documented an enhanced training program; (iii) enhanced training to add emphasis to MLE identified during FAC-008 walkdowns; (iv) issued internal field bulletins to raise awareness; (v) provided engagement and support from business unit senior management as part of a monthly meeting (FAC-008 Steering Committee). c) Note – As a result of lessons learned during the physical walkdowns, FPL is revising its controls iteratively as necessary. Post walkdown completion analysis will result in these controls going from ‘interim’ to ‘permanent/final’; 13) developed and implemented the following controls to ensure controls are implemented and working as designed: a) For Generation: (i) a cross-functional team is now responsible for ensuring an independent validation of project construction by reviewing applicable elements (including MLE) of the project to ensure consistency between as-constructed conditions and worksheets. This review process will confirm that MLE(s) are properly identified following the completion of a construction project. b) For Transmission: (i) FAC-008 related trainings are reviewed and validated by the PD’s Engineering Technical Services (ETS) team on an annual basis. As part of that review, the ETS team will review the assignment of the courses to the appropriate personnel, considering factors such as new hires and transfers in. (ii) While the distribution and tracking of the training is automated, the manual testing (confirmation) will occur prior to the commencement of peak hurricane season for FPL (Q2/early Q3) to ensure appropriate personnel are ready to follow the Company’s FAC-008 process; (iii) To ensure completion of this training completeness validation on an annual basis, an automatic reminder has been setup; (iv) A cross functional team is now responsible for an independent validation of project construction, by sending engineering personnel to review all the applicable elements (including MLE) of the project match field vs worksheets. This manual control will allow the testing (confirmation) that MLE(s) are properly identified following the completion of a construction project. c) Note – As a result of lessons learned during these physical walkdowns, FPL is revising its controls iteratively as necessary. Post walkdown completion analysis will result in these controls going from ‘interim’ to ‘permanent/final’; 14) Generation action to ensure Solar Fleet team shares with FAC-008 SME nameplate info for “Like for Like” inverter changes fleetwide, ensuring FAC-008 SME has opportunity to review for consistency with current Facility Rating; and 15) review all existing FAC-008 testing processes and will revise based on the lessons learned from the walkdown of 100% of transmission and generation facilities. | SERC considered FPL’s compliance history and determined there were no relevant instances of noncompliance. SERC awarded penalty credit for settlement because FPL agreed to settle the Alleged Violation resolved by this Agreement thereby avoiding a hearing on this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that SERC, NERC, and the Commission time would otherwise expend to resolve these Alleged Violations. Additionally, it is important to promote prompt resolution of enforcement actions so that FPL can focus on mitigation and reducing risks to reliability. SERC also awarded penalty credit for admission. FPL recognized and affirmatively accepted responsibility for its conduct by admitting to the violations resolved by the Agreement. SERC is applying mitigating credit because there is independent value in FPL accepting responsibility for its violations.
2025-04-24 | NOC-2862 | SERC | Cooperative Energy (CoEn) | NCR01315 | GO, TO | Settlement Agreement | Admits | 20000 | 2024-00064 | FAC-008-5 | R6 | Moderate | Medium | Lower | Self-Report | 2024-01-30 | 2007-06-18 | 2023-11-08 |  | 2024-05-13 | TBD | CoEn notified SERC that it was noncompliant with FAC-008-5 R6. CoEn failed to have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings Methodology (FRM) or documentation for determining its Facility Ratings. This noncompliance began under FAC-009-1 R1 and spanned to FAC-008-5 R6. On October 13, 2023, during the substation facility walkdown, CoEn observed 161 kV gas circuit breaker (GCB) 1592 did not have a Current Transformer Rating Factor (CT RF) on the CT nameplate. In addition, the group noted the GCB did not have the same manufacture date as the other four 161 kV circuit breakers at the facility. The four newer 161 kV GCBs had a CT RF of 1.5 stamped on the CT nameplates. Transmission Planning reviewed the walkdown notes and sent CT nameplate pictures of GCB 1592 for review and confirmation. On October 18, 2023, CoEn reviewed the nameplate and electronic documentation. The group located electronic documentation for GCB 1592. This documentation did not provide a CT RF. Due to lack of information for CT RF on GCB 1592, a conservative CT RF of 1.0 must be utilized instead of the CT RF of 1.5 that was in the system information database (SID) for GCB 1592. CoEn made a request to the manufacturer to provide the CT RF of the circuit breaker CTs. The manufacturer couldn’t verify the CT RF based on the information available. On October 31, 2023, the Transmission Planning group notified CoEn Compliance of the potential noncompliance. CoEn failed to properly calculate the rating of Line 173 due to the CT RF used in the CT Rating calculation for GCB 1592 CTs in its SID. Line 173 required a derate from 273 MVA to 223 MVA. Reducing GCB 1592 CT RF from 1.5 to 1.0 while using the CT ratio 800:5 made GCB 1592 CTs the most limiting equipment rating on Line 173. This reduced the true rating on Line 173 from 273 MVA to 223 MVA. On November 8, 2023, CoEn changed the CT tap settings from 800:5 to 1200:5 to return to compliance. Using the 1200:5 CT ratio with an assumed CT RF 1.0, the most limiting equipment rating is the designed temperature of the line. Currently, Line 173 has a rating of 273 MVA. There were no exceedances. On February 6, 2024, Transmission Planning completed 100% of the substation walkdowns. It did not discover any additional CT RF issues that affected the MLE. CoEn also determined that reverification should be completed of elements that were previously walked down but since then had field work performed necessitating an in-person verification of the equipment. CoEn determined elements at five Facilities needed to be reverified. On May 13, 2024, CoEn completed its extent of condition (EOC) assessment and confirmed that it did not discover any additional CT RF issues that affected the MLE. The assessment consisted of physically walking down Facilities and confirming that it used the correct CT RF Ratio values in the calculation of the Facility Ratings. This violation started on June 18, 2007, when CoEn failed to have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings, and ended on November 8, 2023, when CoEn changed the CT tap settings from 800:5 to 1200:5. The duration was 5,987 days (16 years, four months, and three weeks). The cause for this violation was an ineffective training program. Specifically, CoEn did not provide staff with appropriate training to recognize that the breaker in question, while manufactured by the same company, was an older model breaker based on electronic documentation. Thus, the SME attributed the wrong RF value/CT Ratio to GCB 1592. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System (BPS). CoEn’s failure to establish Facility Ratings that were consistent with its FRM could result in exceedance of System Operating Limits, unnecessary Facility trips, damage to Facilities, and erroneous planning. Additionally, the length of time this issue went unmitigated increased the risk. The risk was reduced because the maximum flow recorded on Line 173 from Q1 2016 to October 2023 was 78 MVA. This is well below 223 MVA. No harm is known to have occurred. | To mitigate this violation, CoEn performed the following actions: 1) made field changes to increase the CT ratios from 800:5 to 1200:5 on GCB 1592; 2) updated the SID to reflect the assumed 1.0 CT RF and 1200:5 field changes on the substation GCB 1592; 3) completed the substation walkdowns that uncovered this potential noncompliance of all Bulk Electric System (BES) substations; 4) provided training to responsible personnel to review the event and the mitigation activities implemented to prevent a reoccurrence; 5) revised current SID Training (currently required on an annual basis for all staff with Facility Ratings responsibilities) to include additional slides to emphasize the importance of accurate data when calculating Facility Ratings; and 6) ensured new elements that have been added since the walkdowns began have been properly walked down. | SERC considered CoEn’s repeated compliance failures involving FAC-008-5 R6 and FAC-009-1 R1 to be an aggravating factor in the penalty determination. Although one prior noncompliance is distinguishable from the current issue because the cause of this issue was different than that of the earlier prior noncompliance (procedural deficiency), SERC is aggravating for CoEn’s other relevant prior violation. Following the 2021 SERC audit finding, CoEn updated its SID to include CT Ratio data for incorporation into Facility Rating calculations, completed field work to eliminate CT Ratio limitations, and de-rated all remaining affected lines that it identified in the EOC. During the 2021 EOC assessment, CoEn determined the CT on GCB 1592 was the most limiting equipment for Line 173 at the 400:5 tap setting. During relay upgrades, the System Protection group moved from the 400:5 to the 800:5 on GCB 1592. This mitigating action was flawed because of the CT RF used to calculate the CT Rating on GCB 1592. The CT RF cannot be verified for GCB 1592 by the manufacturer or any nameplate or documentation. The CT RF value used in the calculation was obtained from electronic documentation for newer 161 kV GCBs located at the substation. CoEn moved to a more conservative CT RF for GCB 1592 due to the CT RF being unverifiable. Since the initial EOC, CoEn revised its policy for making changes to the SID. The changes, including a new data validation process, could have potentially caught the issue. Therefore, SERC is aggravating the penalty because the results of the prior mitigation plan failed to detect or further prevent the instant violation. SERC reviewed CoEn’s Internal Compliance Program and considered it to be a neutral factor in the penalty determination. CoEn has been highly cooperative throughout the entire enforcement process relating to this violation. Throughout the enforcement process, CoEn voluntarily provided SERC with information that was timely, detailed, thoughtful, organized, and thorough. CoEn fully cooperated in SERC’s investigation of the violation and all associated mitigating activities and openly shared information regarding its processes, procedures, internal controls, assets, systems, and organization. Thus, SERC applied cooperation credit. CoEn self-reported the violation. Effective oversight of the reliability and resilience of the BES depends upon self-reporting by Registered Entities. SERC seeks to encourage self-reporting of offenses and, therefore, is applying mitigating credit for the violation. SERC awarded penalty credit because CoEn agreed to settle the violation resolved by this Agreement thereby avoiding a hearing on this matter. A willingness to resolve cases without the need for a trial-type hearing reduces the amount of time and resources that SERC, NERC, and the Commission time would otherwise expend to resolve these violations. Additionally, it is important to promote prompt resolution of enforcement actions so that CoEn can focus on mitigation and reducing risks to reliability. CoEn recognized and affirmatively accepted responsibility for its conduct by admitting to the Alleged Violations resolved by this Agreement. SERC is applying mitigating credit since there is independent value in organizations accepting responsibility for their violations.