## non-CIP SNOPs
Filed_Date | NOC_ID | Region | Registered_Entity_Name | NCR | Reliability_Functions | Notice_of_Confirmed_Violation_or_Settlement_Agreement | Admits_OR_Agrees_and_Stipulates_OR_Neither_Admits_nor_Denies_OR_Does_Not_Contest | Total_Penalty | NERC_Violation_ID | Reliability_Standard | Requirement | Risk_Assessment | Violation_Risk_Factor | Violation_Severity_Level | Discovery_Method | Reported_to_Region_Date | Noncompliance_Start_Date | Noncompliance_End_Date | Mitigation_Expected_Completion_Date | Mitigation_Completion_Date | Date_Regional_Entity_Verified_Completion_of_Mitigation | Description_of_Noncompliance | Description_of_Risk_Assessment | Description_of_Mitigation | Other_Factors_and_Compliance_History_Discussion
2025-06-30 | NOC-2863 | NPCC | Orange and Rockland Utilities, Inc. (ORU) | NCR07186 | TO | Settlement Agreement | Admits | $102,000 (for NPCC2020024042, NPCC2020024044, and NPCC2020024045) | NPCC2020024042 | FAC-008-1 | R1 | Moderate | Lower | Severe | Self-Report | 2020-10-09 | 2007-06-18 | 2024-02-14 |  | 2025-03-31 | TBD | On October 9, 2020, ORU submitted a Self-Report to NPCC, as a Transmission Owner (TO), stating a potential FAC-008-1 R1 violation. ORU’s Facility Ratings Methodology (FRM) failed to include consideration for operating limitations, such as a topology change. ORU conducted an Extent of Condition (EOC) assessment, and no additional issues were found. However, a subsequent joint NPCC/ReliabilityFirst (RF) self-certification review, completed in March 2023, determined that ORU failed to include in its FRM the following topics associated with activities performed by its affiliate, Rockland Electric Company (RECO), which operates its system within the PJM Control Area, under the RF compliance jurisdiction. ORU is in coordinated oversight with RECO and therefore this noncompliance applies to both ORU and RECO. a) RECO uses a wind speed assumption of 3 ft/sec when establishing thermal ratings of stranded conductors utilized for breaker drops and other connections located outside of and inside its substations. This rating practice is inconsistent with ORU’s existing FRM document, which only supports a 2 ft/sec wind speed for rating equipment/connections located within substations. b) RECO uses ambient temperatures of 85, 95, and 105 degrees Celsius, respectively for establishing the Normal, long term emergency (LTE), and short term emergency (STE) ratings of bare copper tubular bus sections. ORU’s rating standard referenced in the FRM titled “Transmission Overhead Conductor Thermal Ratings Methodology” uses another set of temperature values (75, 100, and 125 degrees Celsius) for overhead conductor ratings. ORU’s FRM failed to reflect values of maximum equipment temperatures utilized in rating its electrical equipment. c) Above and beyond ambient temperature assumptions for summer (95 degrees Fahrenheit and winter 50 degrees Fahrenheit), RECO is required by PJM Interconnection LLC (“PJM”) to establish Facility Ratings for ambient temperatures of 59 degrees Fahrenheit, 68 degrees Fahrenheit, 77 degrees Fahrenheit, and 86 degrees Fahrenheit. However, ORU’s existing FRM document only supports the use of summer (95 degrees Fahrenheit) and winter (50 degrees Fahrenheit) ambient temperatures. d) RECO uses a 25/75 split assumption for ring buses and breaker-and-a-half schemes. However, ORU’s existing FRM only identifies a consideration for breaker-and-a-half substation configuration without a defined split when assessing the impact of operating limitations. NPCC determined that the duration of the violation spans multiple versions of the Reliability Standard, as follows: FAC-008-1 R1 from June 18, 2007, until December 31, 2012 (the Standard’s retirement date); and FAC-008-3 R3 from January 1, 2013, until February 14, 2024, when ORU updated its FRM to address the topic of operating limitations and discrepancies in rating calculations between RECO and ORU. NPCC further determined that, for purposes of this violation, there was no substantive change in ORU’s compliance obligations under the applicable Standards and Requirements. The root cause of this violation was determined to be an inaccurate interpretation of the Standard, which caused ORU’s Transmission & Substation (T&S) Engineering to fail to create a sufficiently comprehensive FRM. Contributing factors include a lack of internal controls, inconsistent methodologies, administrative errors, and inadequate documentation. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, this violation had a long duration (approximately seventeen (17) years). Second, ORU determined, based on historical records that seventy-six (76) instances of operating limitations all caused by breaker outages have occurred since June 18, 2007, where ORU failed to derate fifteen (15) affected Facilities. Two (2) of the affected Facilities (power transformers) are used in the derivation of a single Interconnection Reliability Operating Limit (IROL), the NYISO Total East Interface, which was established by ORU’s Reliability Coordinator (RC). The risk of the violation is reduced by the fact that short term deratings due to equipment outages were in effect for no longer than a few days during each of the seventy-six (76) occurrences, and the affected Facilities were restored to their full design ratings upon mitigation of the anomalous operating conditions. Historical records have also shown that derated Facilities’ loadings did not exceed their reduced ratings in real time when operated during breaker outages. ORU also relies on multiple compensating controls including Supervisory Control and Data Acquisition (SCADA) visual/audible alarming, Primate enhanced visual alarming, SCADA Transmission Security Management (TSM) state estimator and contingency analysis. Priority 1 alarms are audible, visual, and color coded for thermal thresholds, requiring acknowledgement by the operator. In addition, ORU sends telemetry data to the visualization software tool that drives the main “map board” located at ORU’s Primary and Backup control centers. This enhanced situational awareness tool will bold and highlight the equipment/Facility when loadings exceed Normal/LTE/STE ratings and will remain in that state until Facility loadings fall below the applicable rating(s). The SCADA TSM application performs predictive contingency analysis for voltage and thermal constraints to enable system operators to plan for contingencies caused by a multitude of operational events, including potential forced outages of thermally stressed Facilities when overloaded above their true ratings. No harm is known to have occurred. | To mitigate this violation, ORU and RECO: 1) Updated its main FRM document with language that addresses the topic of operating limitations with respect to the calculation of Facility Ratings. The updated FRM document specifically addresses the topics set forth in the description a – d. 2) Updated four additional equipment-specific rating methodologies relating to Transmission feeders (Overhead and Underground), Substations and Transformers with language addressing, as appropriate, the impact of operating limitations. 3) Provided training on all FAC-008 compliance topics, including Most Limiting Element (MLE) identification/verification, to responsible staff. 4) Consolidated all FRM-related documents and procedures into one master FRM document. 5) Reformatted how ratings data is organized in a new Facility Ratings spreadsheet, which was shared with all stakeholders, including System Operations for calculating SOLs. 6) Implemented a new Compliance Tracking tool to monitor and organize compliance-related information and activities and facilitate sending automatic reoccurring reminder emails to responsible staff. 7) Implemented a T&S Notification system control to ensure that all changes (i.e., topology, discrepancies) in the BES are captured and notifications are sent to all stakeholders, thus ensuring timely updates of equipment and their rating in the Facility Ratings spreadsheet. 8) Conducted Facility Ratings trainings on an annual basis. A training session was held on July 24, 2023, that provided personnel with an overview of the FAC-008 Facility Ratings process. The Archer Action Tracking System will track and maintain evidence of the training and provide a reminder notification to ensure training is met annually for all stakeholders. 9) After working with a consultant from July to September 2023 on a phase 1 project to evaluate its Facility Ratings methodology and tools, ORU will continue working with the consultant on developing and implementing a phase 2 proposal to continue the engagement. | NPCC considered ORU and RECO’s compliance history and determined there were no relevant prior instances of noncompliance. ORU has been cooperative throughout the entire enforcement process relating to these violations. Throughout the enforcement process, ORU provided requested information to NPCC that was detailed, organized, and thorough. ORU recognized and affirmatively accepted responsibility for its conduct by admitting the violations resolved by this Agreement. NPCC is applying mitigating credit because there is independent value in ORU accepting responsibility for its violations. ORU self-reported the violations. Effective oversight of the reliability and resilience of the BPS depends on self-reporting by Registered Entities. NPCC seeks to encourage self-reporting of noncompliance and, therefore, is applying mitigating credit for the following violations: NPCC2020024044 and NPCC2020024045. Although ORU self-reported all three violations in this Agreement, NPCC recognized that RECO’s Facility Ratings issues were discovered because of the NPCC/ReliabilityFirst Self-Certification process. Therefore, NPCC did not apply mitigating credit to the following violation: NPCC2020024042. Under coordinated oversight, ORU's penalty will be divided among the Regional Entities as follows. ORU shall pay $102,000 to the Regions. ORU shall pay $102,000 to NPCC, and NPCC shall divide that penalty amount in two parts based on the relative net energy for load (NEL) for each Region. For purposes of penalty allocation, NPCC shall pay $59,177.07 to RF.
2025-06-30 | NOC-2863 | NPCC | Orange and Rockland Utilities, Inc. (ORU) | NCR07186 | TO | Settlement Agreement | Admits | $102,000 (for NPCC2020024042, NPCC2020024044, and NPCC2020024045) | NPCC2020024044 | FAC-008-3 | R6 | Moderate | Medium | Severe | Self-Report | 2020-10-09 | 2007-06-18 | 2022-05-26 |  | 2025-03-31 | TBD | On October 9, 2020, ORU submitted a Self-Report to NPCC, as a TO, stating a potential violation of FAC-008-3 R6. ORU is in coordinated oversight with RECO and therefore this noncompliance applies to both ORU and RECO. Based on the internal compliance review, which began in the fall of 2019, ORU and RECO determined that Facility Ratings had been developed that were inconsistent with its FRM for seventeen (17) applicable Facilities, consisting of four (4) 345/138kV transformers and thirteen (13) 138kV transmission lines. ORU determined that 12 Facilities required a change in Facility Ratings. Specifically, 8 Facilities requiring a reduction of at least one of the following ratings: Normal Summer (NS), Long Term Emergency Summer (LTES), Short Term Emergency Summer (STES), Normal Winter (NW), Long Term Emergency Winter (LTEW), and Short Term Emergency Winter (STEW). In addition, 1 Facility required at least one increase in one of the ratings, and 3 Facilities required a mix of reduction and increases in the ratings. Similarly, RECO determined that 5 Facilities required a change in Facility Ratings. Specifically, 1 Facility required at least one increase in the ratings, and 4 Facilities required a mix of reduction and increases in the ratings. The changes for ORU resulted in derates ranging from 1-34%, with 75% of the derates being less than 11%, and increases in ratings ranging from 1-17%, with 83% of the increases being less than 9%. The changes for RECO resulted in derates ranging from 3-40%, with 75% of the derates being less than 13%, and increases in ratings ranging from 1-6%. NPCC determined that the duration of the violation spans multiple versions of the Reliability Standard, as follows: FAC-009-1 R1, from June 18, 2007, until December 31, 2012 (the Standard’s retirement date). FAC-008-3 R6, from January 1, 2013, until September 30, 2021 (the Standard’s retirement date); and FAC-008-5 R6, from October 1, 2021, until May 26, 2022, when ORU revised its Facility Ratings by reflecting the rating of the correct MLE for each noncompliant Facility. NPCC further determined that, for purposes of this violation, there was no substantive change in ORU’s compliance obligations under the applicable Standards and Requirements. The root cause of this violation was ORU’s failure to consider all series components during the establishment of the overall Facility Ratings. Contributing factors include: 1) failure to verify whether the actual completed work on a Facility (including work completed on an emergency basis) reflected the design documentation of the Facility; 2) failure to have a process to periodically verify and review historical Facility Ratings and associated documentation; and 3) failure to develop a formal process to train responsible staff (T&S Engineering employees) on ORU’s FRM. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS based on the following factors. To start, this noncompliance had a long duration, approximately fifteen (15) years. Mitigation of the violation resulted in rating reductions for fifteen (15) Facilities (equivalent to 88% of the noncompliant Facilities), with 75% of the derates being less than 13%. Conversely, the remaining two (2) noncompliant Facilities experienced modest increases in their ratings (up to 34 MVA, equivalent to a 7% increase). The rating changes were caused by the identification of fifteen (15) new MLEs and two computational errors. None of the derates resulted in ORU or RECO operating above the correct Facility Ratings in the past three (3) years. No harm is known to have occurred. | To mitigate this violation, ORU and RECO: 1) Identified and revised (per ORU’s FRM) seventeen (17) Facility Ratings to reflect all applicable series components, and communicated them to System Operations, Substation Operations, Distribution Engineering, as well as to its two RCs, NYISO and PJM. 2) Developed a FAC-008 BES Facility Ratings spreadsheet as a compliance tool to identify all individual equipment that comprises a Facility, and to also record all system changes that may affect Facility Ratings. 3) Implemented a new process checklist to be completed and signed off prior to energization of BES system additions, BES system modifications, and/or BES facility enhancement projects in order to resolve conflicts between elements in the field and drawing documentation; the checklist will include a process flow that confirms the validation of the associated drawings and, as applicable, a requirement for T&S Engineering to notify System Operations, NYISO, and PJM with revised ratings. 4) Instituted a requirement for T&S Engineering to conduct an annual review to validate all changes on BES Facilities or affecting BES Facilities that occurred within the previous twelve (12) months. 5) Instituted, as part of its annual review of the rating methodologies, a requirement for T&S Engineering to verify that any changes in its methodologies which could impact the BES Facilities are reflected accordingly in the Facility Ratings. 6) Tasked T&S Engineering to formalize Facility Ratings training for T&S Engineering personnel. 7) Hired an independent consultant to assess ORU’s overall processes and procedure(s) related to the current NERC FAC-008 Reliability Standard. | NPCC considered ORU and RECO’s compliance history and determined there were no relevant prior instances of noncompliance. ORU has been cooperative throughout the entire enforcement process relating to these violations. Throughout the enforcement process, ORU provided requested information to NPCC that was detailed, organized, and thorough. ORU recognized and affirmatively accepted responsibility for its conduct by admitting the violations resolved by this Agreement. NPCC is applying mitigating credit because there is independent value in ORU accepting responsibility for its violations. ORU self-reported the violations. Effective oversight of the reliability and resilience of the BPS depends on self-reporting by Registered Entities. NPCC seeks to encourage self-reporting of noncompliance and, therefore, is applying mitigating credit for the following violations: NPCC2020024044 and NPCC2020024045. Although ORU self-reported all three violations in this Agreement, NPCC recognized that RECO’s Facility Ratings issues were discovered because of the NPCC/ReliabilityFirst Self-Certification process. Therefore, NPCC did not apply mitigating credit to the following violation: NPCC2020024042. Under coordinated oversight, ORU's penalty will be divided among the Regional Entities as follows. ORU shall pay $102,000 to the Regions. ORU shall pay $102,000 to NPCC, and NPCC shall divide that penalty amount in two parts based on the relative NEL for each Region. For purposes of penalty allocation, NPCC shall pay $59,177.07 to RF.
2025-06-30 | NOC-2863 | NPCC | Orange and Rockland Utilities, Inc. (ORU) | NCR07186 | TOP | Settlement Agreement | Admits | $102,000 (for NPCC2020024042, NPCC2020024044, and NPCC2020024045) | NPCC2020024045 | FAC-014-2 | R2 | Moderate | Medium | Severe | Self-Report | 2020-10-09 | 2016-05-26 | 2022-05-26 |  | 2023-07-31 | 2023-10-27 | On October 9, 2020, ORU submitted a Self-Report, to NPCC, as a Transmission Operator (TOP), stating a potential violation of FAC-014-2 R2. Based on the compliance review completed in June 2022, ORU determined the System Operating Limits (SOLs) of ORU’s fourteen (14) out of thirty-two (32) Facilities had been incorrectly calculated during sixty-four (64) breaker outages (no longer than a few days for each instance). This violation started on May 26, 2016, ORU’s registration date as a TOP, and ended on May 26, 2022, when ORU revised the last noncompliant SOL. The root cause of this violation was a failure to develop temporary SOLs that reflect anomalous temporary configurations at the substation level due to breaker outages. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS based on the following factors. This violation had a six (6) year duration. Only two (2) of the affected facilities—two (2) power transformers— are used in the derivation of a single IROL, the NYISO Total East Interface, which was established by ORU’s RC. None of the affected Facilities are critical or part of blackstart resources. All SOLs reductions were temporary (no longer than a few days for each instance), and all affected Facilities would be immediately restored to their full normal SOLs upon mitigation of the anomalous operating conditions. Historical records have also shown that derated Facilities’ loadings have never exceeded the newly calculated SOLs in real time operation. In addition, ORU operates its system within the boundaries of established SOLs/IROLs and consistent with the NYISO SOL Methodology, which stipulates that thermally constrained non-NYISO Controlled BES Facilities shall: (a) be operated in real time with the objective to be within the normal thermal limit; and (b) be operated in real time with the objective to be within emergency limits for projected post-contingency flows. Lastly, ORU’s RC within the NPCC footprint, the NYISO, carries required Operating Reserves of approximately 1,965 MW and, in collaboration with ORU’s other RC (PJM, which is the RC, TOP and Balancing Authority for RECO), could have adequately compensated for potential reliability gaps arising from this violation. No harm is known to have occurred. | To mitigate this violation, ORU: 1) Issued revised SOLs for fourteen (14) Facilities affected by temporary breaker outages in the noncompliant period. 2) Developed a Facilities Ratings training program and provided initial training to existing employees (including System Operations staff) and provided training to new hires. 3) Implemented an annual refresher training program for all responsible staff. | NPCC considered ORU and RECO’s compliance history and determined there were no relevant prior instances of noncompliance. ORU has been cooperative throughout the entire enforcement process relating to these violations. Throughout the enforcement process, ORU provided requested information to NPCC that was detailed, organized, and thorough. ORU recognized and affirmatively accepted responsibility for its conduct by admitting the violations resolved by this Agreement. NPCC is applying mitigating credit because there is independent value in ORU accepting responsibility for its violations. ORU self-reported the violations. Effective oversight of the reliability and resilience of the BPS depends on self-reporting by Registered Entities. NPCC seeks to encourage self-reporting of noncompliance and, therefore, is applying mitigating credit for the following violations: NPCC2020024044 and NPCC2020024045. Although ORU self-reported all three violations in this Agreement, NPCC recognized that RECO’s Facility Ratings issues were discovered because of the NPCC/ReliabilityFirst Self-Certification process. Therefore, NPCC did not apply mitigating credit to the following violation: NPCC2020024042. Under coordinated oversight, ORU's penalty will be divided among the Regional Entities as follows. ORU shall pay $102,000 to the Regions. ORU shall pay $102,000 to NPCC, and NPCC shall divide that penalty amount in two parts based on the relative NEL for each Region. For purposes of penalty allocation, NPCC shall pay $59,177.07 to RF.