## Public CIP SNOP Posting
Region | Registered EntityName | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017018149 | Settlement Agreement | During a Compliance Audit, Texas RE determined that TRE_URE1 was in violation of CIP-010-2 R1, Parts 1.5, 1.5.1, and 1.5.2. Texas RE subsequently determined that the duration pertaining to TRE_URE1's testing procedure issues started earlier than July 1, 2016. Accordingly, Texas RE determined that TRE_URE1 was in violation of CIP-007-3a R1, and TRE_URE1 was then in violation of CIP-010-2 R1, Parts 1.5, 1.5.1, and 1.5.2. Texas RE further determined that, for purposes of this issue, there was no substantive change in TRE_URE1's compliance obligations under the Standards at issue. TRE_URE1 implemented a new Information Technology Change Management (ITCM) tool and related processes to better control its change authorization process, security testing, and baseline configuration tracking as part of its overall efforts to transition to the CIP Version 5/6 Standards. TRE_URE1 personnel implemented changes to a number of Cyber Assets using an incorrect workflow option embedded in the new ITCM tool that did not include a step for performing security controls testing. TRE_URE1 discovered the issue during a review of change records. The following day, TRE_URE1 issued instructions to personnel on the steps necessary to select the proper workflows to ensure all required security controls testing activities for NERC Cyber Assets were performed prior to implementing any changes to those assets. TRE_URE1 provided additional training to its personnel regarding the need to perform security controls testing and the proper process for ensuring its timely completion within the new ITCM tool environment. TRE_URE1 sent an email to Texas RE disclosing known issues related to security controls testing. Over the next few months, TRE_URE1 worked to resolve the security controls testing issues associated with the transition to its ITCM tool. TRE_URE1 personnel performed the final required security controls testing for all approved changes, ending the issue. The root cause of these noncompliance instances was an insufficient understanding of the new change management process implemented as part of the CIP Version 5/6 transition. In particular, TRE_URE1 failed to implement its new ITCM tool in a manner that would prevent TRE_URE1 employees from choosing a workflow that bypassed required security testing prior to placing changes to Cyber Assets into production. | CIP-007-3a | R1 | Medium | Severe | This issue posed a moderate risk to the reliability of the bulk power system. Failure to perform security controls testing prior to implementing changes in a production environment could create vulnerabilities in affected systems or cause those systems to fail. The changes at issue involved less than five percent of the overall changes related to BES Cyber Assets during the issue period. However, the risk posed by this issue was also mitigated by the following factors. TRE_URE1's established process is to apply any system changes or updates to hardware and/or software in its passive data center first to determine if there are any adverse impacts. This process includes ongoing operational monitoring to identify any failures with the systems and active security event monitoring to identify any security anomalies that would then be investigated, reducing any potential risks that vulnerabilities or adverse impacts could occur on TRE_URE1's system. When TRE_URE1 performed the appropriate security controls testing on all applicable Cyber Assets, it did not identify any adverse effect of security controls with any of the changes to its production systems. In addition, TRE_URE1 had a number of cyber security systems in place, including automated security event monitoring controls, intrusion detection systems, application whitelisting, full packet capture, vulnerability assessments, and antivirus software. In particular, TRE_URE1 has invested heavily in an email protection architecture in which incoming emails are scanned through multiple sandbox technologies and all URLs are re-written and passed through a security analysis gateway. TRE_URE1 personnel also apply various threat analysis perspectives to categorize different advanced actor campaigns to continuously detect and prevent attacks. Throughout the violation period, these controls did not detect any anomalies, malicious traffic, or malicious code, and TRE_URE1 did not have any Reportable Cyber Security Incidents during the audit period. Based upon review of documents provided during the audit and observation of the data centers during the audit, the compliance audit team further concluded that the changes applied did not negatively impact Control Center or data operations. Finally, TRE_URE1's established process requires that as part of submission of the production change request, submitters are required to provide information regarding functional testing performed. By providing this information during the change authorization process, TRE_URE1 reduced the potential risk that the changes at issue could have an adverse impact on its system. | when TRE_URE1 first placed changes to Cyber Assets into production without ensuring that the changes would not adversely affect existing cyber security controls | when TRE_URE1 completed security controls testing for the last affected Cyber Assets | $45,000 (for TRE2017018149 and TRE2017017741) | Compliance Audit | To mitigate this violation, TRE_URE1: 1) completed security controls testing in accordance with all applicable NERC Reliability Standard requirements; 2) completed implementation of modifications to the automated workflow forms to prevent employees from selecting incorrect workflows bypassing required security controls testing, including implementing a process to require all change and deployment requests to be reviewed and validated by change coordinators before the change is allowed to progress through the selected workflows and precluding any change and deployment requests from progressing further in the workflow process until the security controls testing is successfully performed; 3) implemented a new checklist to ensure that NERC assets are correctly identified and are tested in compliance with NERC Reliability Standards; 4) conducted training pertaining to CIP-010 configuration change management for affected employees; and 5) instituted disciplinary actions for a single employee that did not follow the prescribed change management process. Additionally, TRE_URE1 will complete the following mitigation actions: 1) enhance change management and new project processes to improve compliance involvement and oversight of project development activities, including directly assigning compliance staff to applicable project development teams; 2) revise the existing ITCM workflows or processes to require confirmation that all applicable security controls testing has occurred prior to closing out an ITCM change ticket; 3) establish a process to ensure correct workflows have been selected and appropriate Cyber Security tasks have been performed before Cyber Assets are placed into the production environment; 4) establish an explicit requirement that any omitted security controls testing will be designated as a high priority task and performed as soon as reasonably practicable; and 5) conduct additional training on the ITCM workflow process, the process changes made as part of the mitigation of this issue, and the requirement to perform all cyber security testing activities prior to placing Cyber Assets into production. | 12/31/2018 (approved completion date) | TBD | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered TRE_URE1's compliance history in connection with CIP-007-3a R1 and CIP-010-2 R1. TRE_URE1's relevant prior noncompliance includes TRE2016016600 (CIP-010-2 R1). Regarding the current instances of noncompliance pertaining to TRE2017018149 (CIP-007-3a R1) and TRE2017017741 (CIP-010-2 R1), Texas RE noted the fact that both violations stemmed from common issues in implementing TRE_URE1's new ITCM tool. However, both instances involved distinct aspects of the new tool and distinct reliability tasks (security controls testing and baselining). In addition, the noncompliance described in TRE2017017741 occurred concurrently with a number of TRE_URE1's activities to fully mitigate its issues with the ITCM tool. Based on these factors, Texas RE did not consider the issues described in TRE2017017741 to constitute a repeat violation or aggravating factor. Similarly, Texas RE did not consider the noncompliance described in TRE2016016600 to constitute an aggravating factor in this instance. In TRE2016016600, TRE_URE1 did not have clear documented processes specifying that TRE_URE1 personnel will update baseline configurations within 30 days of completing a change. Texas RE did not consider this previous issue to be aggravating because the prior root cause was distinct from the current issues. In particular, Texas RE determined that the previous issue related solely to TRE_URE1's documentation and that personnel had in practice completed all baselining updates within the required 30-day time frame. In addition, the current baselining issues stemmed from TRE_URE1 personnel not properly identifying PACS panels as NERC Cyber Assets, not issues completing baselining updates within 30 days. Based on the reasons set forth above, Texas RE determined that the previous violation pertaining to TRE_URE1 does not constitute a repeat violation and therefore was not considered an aggravating factor in the overall penalty determination.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017017741 | Settlement Agreement | TRE_URE1 submitted a Self-Report stating that it was in violation of CIP-010-2 R1. In particular, TRE_URE1 discovered that it had failed to add multiple newly installed physical access control system (PACS) panels to its baseline configurations within 30 days, as required under CIP-010-2 R1, part 1.1. TRE_URE1 began the process to install a new PACS for its primary and backup Control Centers. As part of this process, IT personnel began to install a number of PACS access control panels at various Control Center locations. IT personnel selected an incorrect workflow that was not intended for new NERC Cyber Assets. As such, the following month, TRE_URE1 personnel placed the panels at issue into production without completing the baseline configurations within 30 days for the panels as required. TRE_URE1 discovered the issue during a cross-functional meeting. Following this meeting, TRE_URE1 personnel created the proper build request tickets to ensure that baseline configurations of the panels would be completed. TRE_URE1 personnel then established the initial baseline configurations for the panels at issue ending the noncompliance for this issue. The root cause of these instances of noncompliance was an insufficient understanding of the new change management process. Specifically, TRE_URE1 lacked a documented process to ensure its personnel properly identified all new NERC Cyber Assets, and did not provide an explicit location option for PACS panels in the correct new build workflow. | CIP-010-2 | R1; P1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system for several reasons. First, the panels at issue were locked and tamper protected, and only two TRE_URE1 staff members had access to the panels. Second, the panels at issue were all configured in an encrypted mode, which helps ensure the integrity of the data and prevent the introduction of malicious code. Third, the BES Cyber Systems for TRE_URE1 are located inside an Electronic Security Perimeter (ESP) and are protected by firewall(s), which control access to the ESP systems, as well as additional layers of firewalls specific to the PACS network restricting any unauthorized access by the panels to the BES Cyber Systems. Fourth, in the event of a breach of the panels, the devices would not accept invalid data formats. In the event the data was sent in an unrecognizable format, the panels would initiate a reboot, which would send an alert to TRE_URE1 security operations console. No alerts were sent during the time period at issue. Fifth, if the panels were to fail, the biometric readers at the door would fail to close and use the access credentials stored locally. Sixth, all access points to the Physical Security Perimeters (PSPs) are monitored by cameras and TRE_URE1 security personnel at all times. Finally, TRE_URE1 possessed a number of cyber security systems, including automated security event monitoring controls, intrusion detection systems, and antivirus software. Throughout the violation period, these controls did not detect any anomalies, malicious traffic, or malicious code. TRE_URE1 confirmed that during the time period at issue, there were no changes to the three panels that would have resulted in a deviation to the baseline and TRE_URE1 did not have any Reportable Cyber Security Incidents during the issue duration. | when the panels at issue were placed into production | when the baselines for the panels at issue were completed | $45,000 (for TRE2017018149 and TRE2017017741) | Self-Report | To mitigate this violation, TRE_URE1: 1) completed the baseline configuration for the panels at issue; 2) modified the ITCM tool to provide an explicit option for PACS panel location within the designated new build workflow; and 3) shared responses to a lessons learned questionnaire that identified problems regarding this issue during the project delivery portion of the PACS installation project. Additionally, TRE_URE1 will complete the following mitigation actions: 1) enhance change management and new project processes to improve compliance involvement and oversight of project development activities, including directly assigning compliance staff to applicable project development teams; 2) revise the process document for building new Cyber Assets; 3) revise the technical architecture documents to include a decision tree for the project to evaluate Cyber Assets and determine applicability to NERC CIP standards; 4) modify the documented processes for new Cyber Assets, to include explicit guidelines for identifying all NERC Cyber Assets during the new build process; 5) revise the applicable new build workflow processes in the ITCM tool to preclude closing new build requests until all applicable baselining activities are performed; and 6) conduct additional training on the revised new build processes, the other process changes made as part of the mitigation of this issue, and the requirement to perform baselining activities on new NERC Cyber Assets. | 12/31/2018 (approved completion date) | TBD | Neither Admits nor Denies | Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered TRE_URE1's compliance history in connection with CIP-007-3a R1 and CIP-010-2 R1. TRE_URE1's relevant prior noncompliance includes TRE2016016600 (CIP-010-2 R1). Regarding the current instances of noncompliance pertaining to TRE2017018149 (CIP-007-3a R1) and TRE2017017741 (CIP-010-2 R1), Texas RE noted the fact that both violations stemmed from common issues in implementing TRE_URE1's new ITCM tool. However, both instances involved distinct aspects of the new tool and distinct reliability tasks (security controls testing and baselining). In addition, the noncompliance described in TRE2017017741 occurred concurrently with a number of TRE_URE1's activities to fully mitigate its issues with the ITCM tool. Based on these factors, Texas RE did not consider the issues described in TRE2017017741 to constitute a repeat violation or aggravating factor. Similarly, Texas RE did not consider the noncompliance described in TRE2016016600 to constitute an aggravating factor in this instance. In TRE2016016600, TRE_URE1 did not have clear documented processes specifying that TRE_URE1 personnel will update baseline configurations within 30 days of completing a change. Texas RE did not consider this previous issues to be aggravating because the prior root cause was distinct from the current issues. In particular, Texas RE determined that the previous issue related solely to TRE_URE1's documentation and that TRE_URE1 personnel had in practice completed all baselining updates within the required 30-day time frame. In addition, the current baselining issues stemmed from personnel not properly identifying PACS panels as NERC Cyber Assets, not issues completing baselining updates within 30 days. Based on the reasons set forth above, Texas RE determined that the previous violation pertaining to TRE_URE1 does not constitute a prior violation and therefore was not considered an aggravating factor in the overall penalty determination.