## Public CIP SNOP Posting
Region | Registered EntityName | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015884 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R2. During its annual review of baseline documentation conducted as part of the Cyber Vulnerability Assessment (CVA), the entity discovered that a service not required for normal or emergency operations was incorrectly enabled. The main purpose of that service is to allow the sharing of an internet connection for devices using a modem over dial-up. The issue was identified on two devices during the execution of a CVA. An extent of condition review determined that the configurations were duplicated across several terminal servers. The systems at issue do not have modems and the entity has disabled dial-up access by default. In fact, none of these devices have any internet access at all. The root cause of this violation was the failure to properly review an incorrect justification for the service at issue, which was previously needed under a prior operating system. This major contributing factor involves the management practice of asset and configuration management, which includes establishing inventory and configuration baselines and performing assessments. | CIP-007-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by leaving the internet connection sharing service enabled could allow threat vectors into an Electronic Security Perimeter (ESP) via the affected terminal servers. This risk was mitigated by the fact that the systems at issue do not have any internet access at all. This fact reduces the likelihood that this service could be successfully exploited because a connection to the internet would be required for any potential exploitation to be successful. | when the service at issue was no longer necessary | when the service at issue was disabled across all affected systems | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) provided training on change management tools and procedures for Version 5 compliance; 2) disabled Internet Connection Sharing Service from impacted terminal servers initially identified; 3) adopted a procedure requiring a review of the baseline configuration at least once over thirty-five days; 4) disabled Internet Connection Sharing Service on remaining impacted terminal servers; 5) validated implementation of baseline monitoring procedure; 6) validated implementation of baseline monitoring procedure for the following month; and 7) assessed for any lessons learned from the first two cycles and created a plan to implement. | 2016-08-19 | 2017-08-16 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015930 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R3. During regular patch management quality assurance activities related to CIP Version 5 implementation, the entity discovered that security patch reviews for two server management devices were not conducted within 30 days of their release as required by CIP-007-3 R3.1 and entity procedures. Several patches for two server management devices were not reviewed. Additionally, these patches were neither installed nor were compensating measures applied as specified CIP-007-3 R3.2 and entity procedures. After self-reporting this issue with the server management devices, the entity identified two additional patching issues that were also identified during the quality assurance review of the patch management program. One related to antivirus patching, and the other involved the late assessment of patches for the operating system of Physical Access Control System (PACS) devices. With respect to the antivirus patching issue, during the entity’s initial run of its new CIP Version 5 process for historical patch discovery, IT personnel identified that entity business units were running different version of the antivirus client installed in their respective environments. Most of the devices containing the antivirus client had up-to-date versions of the client and did not pose a compliance issue. However, the entity determined that about 5% of the devices had missed four antivirus client version upgrades, another 3% had missed three version upgrades, another 1% had missed two version upgrades, and the remaining 6% had missed one antivirus client version upgrade. In total, there were four antivirus client patches involved. With respect to the PACS patching issue, as part of the entity’s new patch management processes, an automatic Patch Source Review (PSR) is generated within the entity’s primary patch management system. The patch management system receives patch source information, identifies relevant security patches for particular devices, and generates an automated Device Patch Notification (DPN) to each asset owner to trigger the patch assessment process in a timely manner. During the early deployment of the patch management system, the entity discovered that due to a failure to correctly identify the devices in software/firmware libraries, DPNs were not generated for the operating system of multiple PACS devices for which patches were identified. As a result of not receiving these DPNs, the relevant asset owners did not assess the applicability of several unique patches within the 30-day requirement. However, the due diligence of the patch management system project team support by patch tracking tools and internal controls caught the error quickly, so that the patches in question were assessed 20 days late, and compensating measures were put into place. The root causes of this violation are as follows: a. With respect to the server management device issue, the names of the devices had not been correctly entered into the entity’s previous patch tracking systems. As a result the prior patch tracking systems did not flag the devices for security patch management. This problem was compounded by the device names also appearing incorrectly on other related tools, such as the central Shared Services Master Asset List, which hindered the detection of the error. b. With respect to the antivirus issue, the major contributing factor was a lack of clarity and specificity in the entity’s CIP Version 3 patch management procedures. Those procedures state that the responsible party for patch identification, assessment, and deployment is the asset owner. The asset owner includes the operating system owner and the application owner. This fact caused a difference of interpretation between business units as to who was performing the assessments and record keeping for patching the antivirus client. Additionally, at the time of the violation, entry into the patch tool was a manual process which lacked clarity as to who would perform the entry. c. With respect to the patch management system issue, the major contributing factor was the failure to correctly identify the devices in software/firmware libraries. All of these root causes involve the management practice of asset and configuration management, which includes establishing assets and configuration items inventory, controlling changes, and verifying the integrity of such items. | CIP-007-3a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, with respect to the devices involved in the server management device and patch management system issues, those devices were protected by multiple network infrastructure layers with separate two factor authentication and do not directly affect Bulk Electric Systems. Rather, they support backup and update functions of other systems. Second, with respect to the antivirus issue, the fact that some of the software clients were running older versions of the application did not increase the risk of this noncompliance because newer versions of the software concern the addition of new features, not the library or index of malicious files that the application uses to identify malware. In other words, the fact that some software clients were running older versions of the application did not affect the entity’s ability to identify and prevent malware because the library of threats was kept current. | when the server management devices were put into production | Mitigation Plan completion | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) updated CIP Version 3 procedure documentation with the CIP Version 5 procedure, which better defines the process; 2) completed patch reviews of all outstanding patches and entered into the current patch tracking system; 3) verified all device names as correct in the current patch tracking system; 4) verified devices are included in patch review cycles; 5) developed Patching Job Aid to further specify roles and responsibilities and workflow required by the unique nature of the environment; 6) updated software/firmware library for impacted devices; 7) distributed and communicated issuance of the Patching Job Aid to all business units; 8) completed an initial review to compare expected DPNs vs. Actual DPNs generated by the entity’s primary patch management system. Where discrepancies were discovered, Compliance Operations manually generated the missing DPNs; 9) deployed Patch Redesign code in production to ensure that no changes occur in the library records during the generation of Patch Source Reviews (PSRs); 10) reviewed and compared, on a monthly cycle, expected DPN vs. Actual DPNs generated by the patch management system. If any discrepancies are identified, Compliance Operations manually generates the missing DPNs; and 11) installed current applicable clients to all machines necessary | 2017-01-10 | 2017-12-06 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014717 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R5. Following an internal compliance review, the entity identified a single user account on its Energy Control System (ECS) that was not afforded sufficient password complexity controls in accordance with CIP-007 R5.3.1. When the account in question was created, it was inadvertently configured to require a minimum password length of zero characters instead of the minimum eight characters that the entity’s own procedural controls require. The eight character minimum is more stringent than the six character minimum requirement in CIP-007 R5.3.1. The root cause of this violation was that the entity uses a phase review process to identify and remediate these types of issues. In this case, the reviewing employee failed to identify this discrepancy and reset the technical control accordingly. Upon discovering the discrepancy, the entity immediately changed the password length configuration from zero to eight characters. This noncompliance involves the management practice of workforce management through ineffective training. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The account user of the password without sufficient password complexity controls complied with entity procedural controls by creating a password that met the entity’s eight character requirement even though the entity did not correctly implement the technical control to enforce the eight character requirement. ReliabilityFirst also notes that the account was otherwise properly configured for a user with valid training and personnel risk assessment credentials and no one other than the designated employee at the entity used the account. Additionally, ReliabilityFirst notes that no harm occurred because the account was not used for any purpose other than its intended purpose. | when the entity inadvertently created an account that required a minimum password length of zero characters | when the entity changed the password length configuration to require a minimum password length of eight characters | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) corrected the account user’s password length. The entity changed the password length configuration on the ECS account to require a minimum password length of eight characters; 2) updated entity training and reference material to include detailed instructions on what to do if an incorrect password length value is entered. The entity revised this procedure to address this issue and implemented changes to its technical controls to reduce the risk of human error during the user account configuration process. The entity training and reference material was enhanced to provide more explicit guidance on performing the periodic review of the ECS password age report; and 3) modified the ECS password age report to display special characters if an incorrect password length value is entered. | 2015-01-21 | 2015-07-16 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014718 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R5. Following an internal compliance review, the entity identified certain accounts that were not afforded sufficient password change controls in accordance with CIP-007-3a R5.3.3. Specifically, the entity discovered a local account on three assets within the Private Network (PN) managed by the entity’s IT infrastructure & operations group for which passwords were not changed at least annually. The required password changes were made on these three accounts 5 years after being put into production. The root cause of this violation was the manual oversight performed in the account monitoring process, which resulted in IT infrastructure and operations not identifying the required password changed for these accounts. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets and configuration items and baselines. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The entity’s secure network architecture and its use of a defense-in-depth strategy to minimize the risk of unauthorized access helps minimize the risk posed by this violation. Additionally, the entity utilizes redundant controls to minimize the risk of unauthorized access, including password complexity and length requirements. Entity passwords must be at least eight characters in length. The entity also has monitoring controls in place to alert the appropriate CIP asset owner when multiple failed logon attempts are made on a single asset. For an outside intruder to exploit these accounts, that intruder would need to infiltrate several layers of firewalls or obtain physical access to a protected Physical Security Perimeter before that intruder could gain access to any of these three accounts. Finally, the assets are in a separate demilitarized zone (DMZ), have a separate domain from the Electronic Security Perimeter devices, and have a limited number of administrators. In each case, the account on the asset expired and was not used again. If any user had attempted to access any of the accounts, that user would have been forced to change the password on the asset. | when the entity was first required to make an annual password change for one of the three assets at issue | when the entity executed the required password changes for all three assets | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) ensured that all local accounts identified received a password change and where possible, removed local accounts. On behalf of the entity, the entity’s IT infrastructure and operations group executed the required password changes on these three accounts; 2) created a report to query the assets in the PN and associated zones for local administrator account password ages; 3) identified any additional local accounts that have not had their passwords changed within the 365 day timeframe; 4) refined the scripted process, which will execute the password change for all in-scope servers within the PN and associated zones and documented a process for updating local administrator account passwords for servers hosted within protected zones. The process can include assets which are out of scope to maintain consistency in the password value. The process will log the date, asset name, account name and status of the password change (pass/fail). Any attempt that fails will be manually addressed by the team; and 5) updated the procedure for monitoring user account password ages to include local accounts in the PN. | 2015-03-06 | 2015-08-17 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015885 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R2. Following a review of its Cyber Vulnerability Assessment (CVA), the entity identified open ports on three switches that were not required for normal or emergency operations. The entity was unable to determine the reason why the ports were open because they were not justified in the device baselines. Further analysis revealed one open port on one switch and two open ports on another switch and a Bulk Power Operations switch that were not justified in the device baselines. These ports were closed as part of the CVA remediation efforts. The root cause of this violation was the failure to appropriately apply change management procedures. This major contributing factor involves the management practice of asset and configuration management, which includes establishing inventory and configuration baselines and performing assessments. | CIP-007-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected devices are protected by two layers of firewalls along with intrusion detection devices in the corresponding Electronic Security Perimeters, which would monitor and alert for any network intrusion and create a dashboard for any potential events reducing the risk. | when the ports were most likely opened | when the ports at issue were closed | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) provided training on entity change management tools and procedures for Version 5 compliance; 2) closed open ports during CVA remediation efforts; 3) adopted a procedure requiring a review of the baseline configuration at least once every 35 days; 4) validated implementation of baseline monitoring procedure; 5) validated implementation of baseline monitoring procedure for the following month; and 6) assessed for any lessons learned from the first two cycles and created a plan to implement. | 2016-07-13 | 2016-10-06 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015888 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R2. During its annual review of baseline documentation conducted as part of the Cyber Vulnerability Assessment (CVA), the entity discovered that a service not required for normal or emergency operations was incorrectly enabled. The main purpose of that service is to allow the sharing of an internet connection for devices using a modem over dial-up. The issue was identified on two devices during the execution of a CVA. An extent of condition review determined that the configurations were duplicated across all server devices. The systems at issue do not have modems and the entity has disabled dial-up access by default. In fact, none of these devices have any internet access at all. The root cause of this violation was the failure to properly review an incorrect justification for the service at issue, which was previously needed under a prior operating system. This major contributing factor involves the management practice of asset and configuration management, which includes establishing inventory and configuration baselines and performing assessments. | CIP-007-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk is that leaving the internet connection sharing service enabled could allow threat vectors into an Electronic Security Perimeter (ESP) via the affected terminal servers. This risk was mitigated by the fact that the systems at issue do not have any internet access at all. This fact reduces the likelihood that this service could be successfully exploited because a connection to the internet would be required for any potential exploitation to be successful. | when the service at issue was no longer necessary | when the service at issue was disabled across all affected systems | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) provided training on entity change management tools and procedures for Version 5 compliance; 2) disabled Internet Connection Sharing Service from impacted terminal servers initially identified; 3) adopted a procedure requiring a review of the baseline configuration at least once over thirty-five days; 4) disabled Internet Connection Sharing Service on remaining impacted terminal servers; 5) validated implementation of baseline monitoring procedure; 6) validated implementation of baseline monitoring procedure for the following month ; and 7) assessed for any lessons learned from first two cycles and created a plan to implement. | 2016-08-31 | 2017-08-16 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016015933 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R3. During regular patch management quality assurance activities related to CIP Version 5 implementation, the entity discovered that security patch reviews for two server management devices were not conducted within 30 days of their release as required by CIP-007-3 R3.1 and entity procedures. Several patches for two server management devices were not reviewed. Additionally, these patches were neither installed nor were compensating measures applied as specified CIP-007-3 R3.2 and entity procedures. After self-reporting this issue with the server management devices, the entity identified two additional patching issues that were also identified during the quality assurance review of the patch management program. One related to antivirus patching, and the other involved the late assessment of patches for the operating system of Physical Access Control System (PACS) devices. With respect to the antivirus patching issue, during the entity’s initial run of its new CIP Version 5 process for historical patch discovery, IT personnel identified that entity business units were running different version of the antivirus client installed in their respective environments. Most of the devices containing the antivirus client had up-to-date versions of the client and did not pose a compliance issue. However, the entity determined that about 5% of the devices had missed four antivirus client version upgrades, another 3% had missed three version upgrades, another 1% had missed two version upgrades, and the remaining 6% had missed one antivirus client version upgrade. In total, there were four antivirus client patches involved. With respect to the PACS patching issue, as part of the entity’s new patch management processes, an automatic Patch Source Review (PSR) is generated within the entity’s primary patch management system. The patch management system receives patch source information, identifies relevant security patches for particular devices, and generates an automated Device Patch Notification (DPN) to each asset owner to trigger the patch assessment process in a timely manner. During the early deployment of the patch management system, the entity discovered that due to a failure to correctly identify the devices in software/firmware libraries, DPNs were not generated for the operating system of multiple PACS devices for which patches were identified. As a result of not receiving these DPNs, the relevant asset owners did not assess the applicability of several unique patches within the 30-day requirement. However, the due diligence of the patch management system project team support by patch tracking tools and internal controls caught the error quickly, so that the patches in question were assessed 20 days late, and compensating measures were put into place. The root causes of this violation are as follows: a. With respect to the server management device issue, the names of the devices had not been correctly entered into the entity’s previous patch tracking systems. As a result the prior patch tracking systems did not flag the devices for security patch management. This problem was compounded by the device names also appearing incorrectly on other related tools, such as the central Shared Services Master Asset List, which hindered the detection of the error. b. With respect to the antivirus issue, the major contributing factor was a lack of clarity and specificity in the entity’s CIP Version 3 patch management procedures. Those procedures state that the responsible party for patch identification, assessment, and deployment is the asset owner. The asset owner includes the operating system owner and the application owner. This fact caused a difference of interpretation between business units as to who was performing the assessments and record keeping for patching the antivirus client. Additionally, at the time of the violation, entry into the patch tool was a manual process which lacked clarity as to who would perform the entry. c. With respect to the patch management system issue, the major contributing factor was the failure to correctly identify the devices in software/firmware libraries. All of these root causes involve the management practice of asset and configuration management, which includes establishing assets and configuration items inventory, controlling changes, and verifying the integrity of such items. | CIP-007-3a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, with respect to the devices involved in the server management device and patch management system issues, those devices were protected by multiple network infrastructure layers with separate two factor authentication and do not directly affect Bulk Electric Systems. Rather, they support backup and update functions of other systems. Second, with respect to the antivirus issue, the fact that some of the software clients were running older versions of the application did not increase the risk of this noncompliance because newer versions of the software concern the addition of new features, not the library or index of malicious files that the application uses to identify malware. In other words, the fact that some software clients were running older versions of the application did not affect the entity’s ability to identify and prevent malware because the library of threats was kept current. | when the server management devices were put into production | Mitigation Plan completion | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) updated CIP Version 3 procedure documentation with the CIP Version 5 procedure, which better defines the process; 2) completed patch reviews of all outstanding patches and entered into the current patch tracking system; 3) verified all device names as correct in the current patch tracking system; 4) verified devices are included in patch review cycles; 5) developed Patching Job Aid to further specify roles and responsibilities and workflow required by the unique nature of the environment; 6) updated software/firmware library for impacted devices; 7) distributed and communicated issuance of the Patching Job Aid to all business units; 8) completed an initial review to compare expected DPNs vs. Actual DPNs generated by the entity’s primary patch management system. Where discrepancies were discovered, Compliance Operations manually generated the missing DPNs; 9) deployed Patch Redesign code in production to ensure that no changes occur in the library records during the generation of Patch Source Reviews (PSRs); 10) reviewed and compared, on a monthly cycle, expected DPN vs. Actual DPNs generated by the patch management system. If any discrepancies are identified, Compliance Operations manually generates the missing DPNs; and 11) installed current applicable clients to all machines necessary | 2017-01-31 | 2017-03-23 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014719 | Settlement Agreement | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R6. The entity identified instances in which certain Cyber Assets did not perform continuous monitoring and logging functions as required by CIP-007-3a R6. As part of remediation efforts under a prior mitigation plan, the entity and the entity's corporate information security services team brought a number of Electronic Access Control and Monitoring Systems (EACMS) into CIP compliance including a class of firewall managers used to manage checkpoint firewalls. All activity for these checkpoint firewalls are collected and logged to a security event management system either directly, or by way of the firewall managers. The entity discovered that logs from the firewall managers were not consistently collected by the security event management system. Upon further investigation and discussion, the entity determined a software issue was the apparent cause for the logging issue. Logs with larger file sizes interfered with the firewall agent’s ability to process such logs. The root cause of this violation involves the management practice of verification. The entity did not have an effective internal control in place to ensure that the firewall manager’s logs were consistently collected and logged as required by CIP-007-3a R6. A technical issue with the security event management system software interfered with the firewall agent’s ability to process such logs. This meant that all logs from the firewall manager were not consistently collected and logged by the security event management system. This system was not able to resolve this technical issue and the entity found another software, which was able to process the larger file sizes that caused the problems. | CIP-007-3a | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The entity utilizes a defense-in-depth strategy that reduces the risk of unauthorized access attempts. The entity monitors Electronic Security Perimeter access through active intrusion detection systems. Access to Critical Cyber Assets (CCAs) requires the potential user to pass through multiple layers of firewalls before accessing the CCA. These protections mean that changes to the configuration of a single firewall would not, on its own, provide access to an unauthorized user. Aside from the logging issue, the firewall was functioning properly in that it was effectively controlling what can pass through the device. Therefore, any changes to the configuration of a single firewall would not, on its own, provide access to an authorized user. The entity also has other redundant controls in place such as required two-factor authentication and that serves as an alternative mechanism for logging, monitoring, and alerting via Remote Secure Access logs. | when the firewall manager's logs were first not being collected by the security event management system | when the entity implemented a manual monitoring process for the logs at issue | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) obtained and implemented the vendor-developed coding solution for the firewall agent in order to re-enable logging to the automated system; 2) validated the efficacy and accuracy of the vendor-developed coding solution through monitoring and testing; 3) performed a comprehensive review of in-scope checkpoint firewalls for adequacy in supporting NERC compliance in the entity environment; 4) developed new and revised the old NERC CIP project management processes to address how projects are managed through the entire project life cycle; 5) evaluated any alternative solution based on the completed review; 6) deployed the new monitoring software to replace and mitigate the issues with logging of in-scope checkpoint devices which included the managers, loggers and firewalls; and 7) performed a comprehensive review of in-scope checkpoint firewall devices to ensure that logging, monitoring and alerting are meeting both security and compliance functions. | 2016-03-24 | 2016-04-19 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2017016759 | Settlement Agreement | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-6 R4. The entity conducted an internal self-assessment of compliance with CIP-007-6 R4, including gathering evidence of reviewing a summary of logged events. The entity discovered that for sample dates of the 1st and 15th of two months, the records associated with the summary reviews for certain firewalls at the entity were incomplete, meaning that the reviews were not completed properly. Further review determined that stored security event logs had not been consistently reviewed, and, therefore, the reviews were not documented as required by the entity’s procedure and by CIP-007-6 R4, Part 4.4, which requires a review at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. The root cause of this noncompliance was an insufficient procedure for performing the reviews and a lack of quality control for verifying the completeness of the reviews. First, the procedure failed to establish a backup performer for this activity. The heavy and unbalanced workload for the employee responsible for performing the summary reviews prevented all reviews from being completed in a timely manner. Second, the procedure for performing these reviews was unclear regarding which reports were required to be completed for the review. Finally, the entity did not have adequate internal preventative controls in place to ensure that the reviews were completed in a timely manner. These major contributing factors involve the management practice of work management, which includes managing organizational work, and verification, which includes establishing verification procedures and criteria. | CIP-007-6 | R4 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the summary review of logs associated with these firewalls was not the only method by which the entity sought to identify security threats. The monitoring team also reduced the risk associated with potential malicious actions by monitoring events on a network as well as on an asset level. For instance, the monitoring team performs summary reviews of the Cyber Assets within the Electronic Security Perimeters as well to ensure awareness of its systems. Second, during the time period in question, at no time was the capability of performance of logging interrupted. ReliabilityFirst also notes that no actual harm occurred because there were no undetected Cyber Security Incidents and negative impacts to any Bulk Electric System Cyber Systems during the time period in question. | when the first summary review was missed | when the entity generated the missing summary review reports and conducted the reviews | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) reassigned the summary reviews to a primary and backup performer who did not have the same workload imbalance; 2) generated the missing summary review reports and conducted an analysis to determine if there had been any undetected Cyber Security Incidents. The result of the industrial control system security operations center analysis confirmed there had been no undetected Cyber Security Incidents; 3) updated the NERC CIP Security Event Monitoring job aid to: (i) document the specific roles and responsibilities for the primary and back-up performers; (ii) document more specificity for recording the performance of the required summary reviews; and (iii) document a complete list of reports to be reviewed as part of the summary reviews; 4) documented, tested and implemented an internal control job aid to have a compliance liaison from the Real-time Security and Compliance section support the performance of the summary reviews by the security operations center. The compliance liaison will periodically review the performance records for accuracy and completeness according to a checklist and record the review using the same checklist. Additionally, an automated prompt will serve as a reminder of the review; 5) conducted internal training with the Real-time System Security and Compliance performers related to the new internal control job aid; and 6) conducted internal training with the security operations center performers related to the updated NERC CIP Security Event Monitoring job aid. | 2017-07-07 | 2017-08-09 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015886 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R2. During its annual review of baseline documentation conducted as part of the Cyber Vulnerability Assessment (CVA), the entity discovered that a service not required for normal or emergency operations was incorrectly enabled. The main purpose of that service is to allow the sharing of an internet connection for devices using a modem over dial-up. The issue was identified on two devices during the execution of a CVA. An extent of condition review determined that the configurations were duplicated across several devices. The systems at issue do not have modems and the entity has disabled dial-up access by default. In fact, none of these devices have any internet access at all. The root cause of this violation was the failure to properly review an incorrect justification for the service at issue, which was previously needed under a prior operating system. This major contributing factor involves the management practice of asset and configuration management, which includes establishing inventory and configuration baselines and performing assessments. | CIP-007-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk is that leaving the internet connection sharing service enabled could allow threat vectors into an Electronic Security Perimeter (ESP) via the affected terminal servers. This risk was mitigated by the fact that the systems at issue do not have any internet access at all. This fact reduces the likelihood that this service could be successfully exploited because a connection to the internet would be required for any potential exploitation to be successful. | when the service at issue was no longer necessary | when the service at issue was disabled across all affected systems | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) provided training on change management tools and procedures for Version 5 compliance; 2) disabled Internet Connection Sharing Service from impacted terminal servers initially identified; 3) adopted a procedure requiring a review of the baseline configuration at least once over thirty-five days; 4) disabled Internet Connection Sharing Service on remaining impacted terminal servers; 5) validated implementation of baseline monitoring procedure; 6) validated implementation of baseline monitoring procedure for the following month; and 7) assessed for any lessons learned from the first two cycles and created a plan to implement. | 2017-08-07 | 2017-08-16 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016015932 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R3. During regular patch management quality assurance activities related to CIP Version 5 implementation, the entity discovered that security patch reviews for two server management devices were not conducted within 30 days of their release as required by CIP-007-3 R3.1 and entity procedures. Several patches for two server management devices were not reviewed. Additionally, these patches were neither installed nor were compensating measures applied as specified CIP-007-3 R3.2 and entity procedures. After self-reporting this issue with the server management devices, the entity identified two additional patching issues that were also identified during the quality assurance review of the patch management program. One related to antivirus patching, and the other involved the late assessment of patches for the operating system of Physical Access Control System (PACS) devices. With respect to the antivirus patching issue, during the entity’s initial run of its new CIP Version 5 process for historical patch discovery, IT personnel identified that entity business units were running different version of the antivirus client installed in their respective environments. Most of the devices containing the antivirus client had up-to-date versions of the client and did not pose a compliance issue. However, the entity determined that about 5% of the devices had missed four antivirus client version upgrades, another 3% had missed three version upgrades, another 1% had missed two version upgrades, and the remaining 6% had missed one antivirus client version upgrade. In total, there were four antivirus client patches involved. With respect to the PACS patching issue, as part of the entity’s new patch management processes, an automatic Patch Source Review (PSR) is generated within the entity’s primary patch management system. The patch management system receives patch source information, identifies relevant security patches for particular devices, and generates an automated Device Patch Notification (DPN) to each asset owner to trigger the patch assessment process in a timely manner. During the early deployment of the patch management system, the entity discovered that due to a failure to correctly identify the devices in software/firmware libraries, DPNs were not generated for the operating system of multiple PACS devices for which patches were identified. As a result of not receiving these DPNs, the relevant asset owners did not assess the applicability of several unique patches within the 30-day requirement. However, the due diligence of the patch management system project team support by patch tracking tools and internal controls caught the error quickly, so that the patches in question were assessed 20 days late, and compensating measures were put into place. The root causes of this violation are as follows: a. With respect to the server management device issue, the names of the devices had not been correctly entered into the entity’s previous patch tracking systems. As a result the prior patch tracking systems did not flag the devices for security patch management. This problem was compounded by the device names also appearing incorrectly on other related tools, such as the central Shared Services Master Asset List, which hindered the detection of the error. b. With respect to the antivirus issue, the major contributing factor was a lack of clarity and specificity in the entity’s CIP Version 3 patch management procedures. Those procedures state that the responsible party for patch identification, assessment, and deployment is the asset owner. The asset owner includes the operating system owner and the application owner. This fact caused a difference of interpretation between business units as to who was performing the assessments and record keeping for patching the antivirus client. Additionally, at the time of the violation, entry into the patch tool was a manual process which lacked clarity as to who would perform the entry. c. With respect to the patch management system issue, the major contributing factor was the failure to correctly identify the devices in software/firmware libraries. All of these root causes involve the management practice of asset and configuration management, which includes establishing assets and configuration items inventory, controlling changes, and verifying the integrity of such items. | CIP-007-3a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, with respect to the devices involved in the server management device and patch management system issues, those devices were protected by multiple network infrastructure layers with separate two factor authentication and do not directly affect Bulk Electric System operations. Rather, they support backup and update functions of other systems. Second, with respect to the antivirus issue, the fact that some of the software clients were running older versions of the application did not increase the risk of this noncompliance because newer versions of the software concern the addition of new features, not the library or index of malicious files that the application uses to identify malware. In other words, the fact that some software clients were running older versions of the application did not affect the entity’s ability to identify and prevent malware because the library of threats was kept current. | when the server management devices were put into production | Mitigation Plan completion | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) updated CIP Version 3 procedure documentation with the CIP Version 5 procedure, which better defines the process; 2) completed patch reviews of all outstanding patches and entered into the current patch tracking system; 3) verified all device names as correct in the current patch tracking system; 4) verified devices are included in patch review cycles; 5) developed Patching Job Aid to further specify roles and responsibilities and workflow required by the unique nature of the environment; 6) updated software/firmware library for impacted devices; 7) distributed and communicated issuance of the Patching Job Aid to all business units; 8) completed an initial review to compare expected DPNs vs. Actual DPNs generated by the entity’s primary patch management system. Where discrepancies were discovered, Compliance Operations manually generated the missing DPNs; 9) deployed Patch Redesign code in production to ensure that no changes occur in the library records during the generation of Patch Source Reviews (PSRs); 10) reviewed and compared, on a monthly cycle, expected DPN vs. Actual DPNs generated by the patch management system. If any discrepancies are identified, Compliance Operations manually generates the missing DPNs; and 11) installed current applicable clients to all machines necessary | 2017-01-10 | 2017-04-13 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015328 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R4. During an internal log review process, the entity discovered an instance where an antivirus definitions package was not tested on like devices prior to its installation in the production environment as required by the entity’s NERC CIP Malicious Software Prevention Procedure. That procedure requires the testing of definition signature packages performed on development assets prior to the testing of the corresponding production assets. The lack of testing involved the entity's generation control system. For the assets at issue, there are four groups: Development Workstations, Development Servers, Production Workstations, and Production Servers. The log review revealed that corporate securty services inadvertently installed an antivirus definitions package on the generation control system development servers in the east Private Network (PN) for testing rather than the appropriate definition package. This occurred at the same time the appropriate definition package was installed on the generation control system development workstations. An employee inadvertently selected the wrong definitions package from the drop down tool to push to the development servers. The tool requires users to manually select the correct package for definition updates. This lack of attention to detail caused the wrong definitions package to be pushed to the development server group. During the testing period, the entity observed no impacts on any assets. Virus signatures are deployed to Development Assets with the current day’s virus signature. The signatures are tested for a week and then are applied to the Production Environment following testing. The policy for the virus signatures has to be changed manually and this requirement leaves it open to human error. The entity’s analyst picked the current date’s signatures for application to Development Assets and then accidently picked the same package for the Production Assets instead of picking the package that had been tested the week before. An internal log review confirmed that a subsequent definition push was successfully accomplished which brought all definitions up to the current, tested sequence number. This noncompliance involves the management practice of verification. In this noncompliance, an entity analyst inadvertently picked the wrong set of virus signatures to apply to Production Assets. The root cause was that the entity did not have an effective process in place to ensure that these types of human errors were corrected before any impact came from them. A contributing cause of this noncompliance was a lack of an effective verification process. | CIP-007-3a | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk is minimal because the entity had tested all of the signatures performed on the generation control system Development Workstations before deploying the signatures to the production system. The devices received the most current virus definition files that were tested within the entity. The files had just not been tested on like devices prior to deployment. Corporate security services monitors and has visibility into the production environment to determine if there were any adverse impacts to the development workstation from the deployment of incorrect virus signatures as part of the entity’s standard operating process. The entity witnessed no impact to the production environment. There was no performance or functional impact to the assets during the one week the package was in place to either the generation control system server assets, the generation control system, or the BPS. Lastly, the incorrect package of signatures was in place for a short amount of time: only one week. | when the entity deployed incorrect virus signatures to Production Assets | when the entity updated all virus signatures which brought all definitions up to current, tested sequence number | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) created a checklist and conducted a meeting to review the developed checklist and reinforced attention to detail while working through the manual process; 2) installed the new antivirus protection live update server; 3) pre-tested and post-tested the system. With the new automated system, definitions are updated automatically every week without human intervention, which ensures that testing is done properly and that the proper package is deployed in the correct sequence; 4) implemented the new virus signature incrementing process; 5) updated its procedure document to reflect all changes; and 6) performed a quality assessment of the new process to ensure the process is operating as designed. | 2016-02-26 | 2016-04-06 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015014720 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R5. Following an internal compliance review, the entity identified certain accounts that were not afforded sufficient password change controls in accordance with CIP-007 R5.3.3. Specifically, the entity discovered five accounts in which passwords for certain accounts were not changed at least annually. For four of these accounts, existing controls required the account user to change the account password every 90 days per entity procedures. However, users that did not log on to the account never received such a prompt to change the password. The users for these four accounts did not log onto the accounts again after their last password change. The passwords for these four accounts were not changed within the annual timeframe. For the fifth and final account, a shared account did not have a control in place to prompt the user to change the password when the password expired. The fifth account was set up incorrectly, which resulted in the account being configured with a non-expiring password and the account not being included in any entity password management tracking system. All five of these accounts, including the shared account with the non-expiring password were active on the Generation Control System (GCS). The entity retired the GCS and this retirement disabled all five accounts at issue. The root cause of this violation was that the process associated with password changes did not include a notification to employees who had not logged into an account in over a year. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets and configuration items and baselines. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The entity’s secure network architecture and use of a defense-in-depth strategy minimized the risk posed by this noncompliance. The entity utilizes redundant controls for its systems such as password complexity and length requirements. Furthermore, the entity has monitoring controls in place to alert the appropriate CIP asset owners when failed logon attempts are made for certain assets. For an outside intruder to exploit these accounts, the intruder would need to infiltrate several layers of firewalls or obtain physical access to a protected Physical Security Perimeter before the intruder could gain access to these accounts. Lastly, four of the five accounts had prompts in place to force the user to change the password the next time the user logged in; the only issue was that the user did not log back into any of the four accounts and thus did not annually change the passwords on those four accounts. | when the first password was required to be changed | when the entity disabled all five accounts with expired passwords | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) retired the GCS system and, as a result, disabled the five individual user and shared accounts; 2) installed a replacement new generation control system; 3) implemented steps to proactively monitor the new environment for password aging and to send notifications to users and their supervisors should a user fail to change their password in a timely manner or fail to login to the system altogether. This practice was expanded to include local accounts; 4) finalized a new procedure for changing shared account passwords on the new generation control system; 5) tested the new procedure in the new generation control development system; 6) implemented the new procedure in the new generation control production environment; and 7) completed a quality assessment to confirm that all shared account passwords on the new generation control system have been changed. | 2016-01-29 | 2016-05-17 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015071 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R5. This Self-Report involves three separate noncompliances. The entity, in its Self-Report, initially discovered an instance where, as a result of improperly elevated access, an IT employee inadvertently patched a generation dispatch system terminal server. Specifically, while installing patches on servers and workstations, an IT employee inadvertently installed server patches to this particular terminal server. Prior to installing these incorrect patches, the entity incorrectly granted the IT employee elevated access that gave him the credentials to patch this terminal server. The patches the IT employee incorrectly installed had not yet been scheduled for deployment to the server meaning that the patches had also not yet undergone significant change testing. The entity removed the inadvertently installed patches and notified the Remote Access team of the IT employee’s error and improper elevated access rights. Following this first issue, while reviewing the patching history of the IT employee at issue in the first instance of noncompliance, the same IT employee applied patches to the generation dispatch production system that were not scheduled for production testing and deployment. The IT employee was only meant to deploy a certain number of update patches to the Quality Assurance (QA) environment and not the production environment. While attempting to deploy those patches to the QA environment, the IT employee mistyped the name. As a result of mistyping the letter “P” instead of the letter “Q”, the patches were installed on a single production server. Unaware that the patch had been applied to the production environment, the IT employee manually rebooted the system, causing the primary server to be offline while rebooting. This reboot triggered a successful failover from the primary to a backup server, as designed, and this failover prevented any operational impact from the patching mistake. Following this second issue, the entity expanded its extent of condition to review and fully re-evaluate the consistency and completeness of patching efforts that impact the generation dispatch system. Through this review, the entity identified additional instances of noncompliance pertaining to the entity’s patching of the generation dispatch system. As part of the extent of condition review which began after the first issue and was expanded after the second issue, the entity conducted a review of patch assessments performed after the commissioning of the generation dispatch system. This review identified instances where patches relevant to the generation dispatch system were either incorrectly categorized or assessed. The root cause of this violation involves the management practice of workforce management through ineffective training and verification through a lack of effective verification processes and procedures. For the first issue, ineffective training resulted in the IT employee improperly getting elevated access and the IT employee deploying the wrong patches to the wrong server. For the second issue, a contributing cause was a lack of attention detail through human error in executing patching by the IT employee. For the third issue, contributing causes were human performance error in the execution of patching assessment activities and a lack of sufficient procedural documentation and training on the proper patch identification and assessment processes. The entity discovered that the documentation and training that supports patching lacked sufficient substantive detail to guide individuals on how to perform patch assessments. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. For the first issue, the IT employee’s elevated access was limited to certain assets and did not extend into the Bulk Electric System (BES) applications. Additionally, the server to which the patch was improperly applied is a jump server into the entity’s Private Network (PN). The jump server does not have administrative access into BES applications. For the second issue, the reboot to a generation dispatch server resulting from the inadvertently applied patches was addressed within two minutes when a backup server was moved to primary status automatically to account for the server that was taken off-line unexpectedly. ReliabilityFirst notes that no actual harm occurred because the lapse in the data feed resulted in no loss of data to the generation dispatch system. Additionally, the entity had completed some testing on the inadvertently installed patches prior to their deployment. For the third issue, access to the generation dispatch system assets is limited and is protected either by physical access protections such as locked cabinets or electronic access protections such as 2-factor authentication. ReliabilityFirst notes that no actual harm occurred because the entity experienced no generation dispatch system interruptions or security breaches stemming from any of these issues. Overall, the entity utilizes secure network architecture and a layer security model based on a defense-in-depth design. | when the entity inadvertently installed patches on the wrong server | when the entity removed the inadvertently installed patches from the server | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) removed unintentional patches from the device, notified the device support group, and removed elevated access from the IT employee; 2) reinforced the entity’s Account Management Policies with server support personnel; 3) reassigned personnel duties of the IT employee who performed repeated incidents; 4) performed an extent of condition analysis of patching activities; 5) required all generation dispatch system support staff to take a human performance error awareness training module to increase focus on attention to deal; 6) developed job aids to reinforce process and procedures for patch identification, assessment, and deployment on the generation dispatch system production environment for CIP Version 3 and CIP Version 5; 7) developed and implemented training to impacted personnel to reinforce the performance and documentation requirements for patch identification, assessment, and deployment in the generation dispatch production environment; 8) engaged a team external to IT to perform a quality assurance assessment of patch management performance and the effectiveness of the job aids developed in Milestone 2; and 9) engaged a team external to IT to perform a quality assurance assessment of patch management performance following transition to the CIP Version 5 patching program. | 2016-06-02 | 2016-09-12 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015015311 | Settlement Agreement | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R6. The entity identified instances in which certain Cyber Assets did not perform continuous monitoring and logging functions as required by CIP-007-3a R6. As part of remediation efforts under a prior mitigation plan, the entity and the entity's corporate information security services team brought a number of Electronic Access Control and Monitoring Systems (EACMS) into CIP compliance including a class of firewall managers used to manage checkpoint firewalls. All activity for these checkpoint firewalls are collected and logged to a security event management system either directly, or by way of the firewall managers. The entity discovered that logs from the firewall managers were not consistently collected by the security event management system. Upon further investigation and discussion, the entity determined a software issue was the apparent cause for the logging issue. Logs with larger file sizes interfered with the firewall agent’s ability to process such logs. The root cause of this violation involves the management practice of verification. The entity did not have an effective internal control in place to ensure that the firewall manager’s logs were consistently collected and logged as required by CIP-007-3a R6. A technical issue with the security event management system software interfered with the firewall agent’s ability to process such logs. This meant that all logs from the firewall manager were not consistently collected and logged by the security event management system. This system was not able to resolve this technical issue and the entity found another software, which was able to process the larger file sizes that caused the problems. | CIP-007-3a | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The entity utilizes a defense-in-depth strategy that reduces the risk of unauthorized access attempts. The entity monitors Electronic Security Perimeter access through active intrusion detection systems. Access to Critical Cyber Assets (CCAs) requires the potential user to pass through multiple layers of firewalls before accessing the CCA. These protections mean that changes to the configuration of a single firewall would not, on its own, provide access to an unauthorized user. Aside from the logging issue, the firewall was functioning properly in that it was effectively controlling what can pass through the device. Therefore, any changes to the configuration of a single firewall would not, on its own, provide access to an authorized user. The entity also has other redundant controls in place such as required two-factor authentication and that serves as an alternative mechanism for logging, monitoring, and alerting via Remote Secure Access logs. | when the entity brought the devices at issue into production | Mitigating activities completion | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) successfully and fully deployed the solution to fully remediate any logging issues with the security event management system; 2) finished the reclassification of the replaced checkpoint firewall managers out of CIP scope; 3) finished decommissioning activities for those firewall managers; and 4) manually monitored the devices at issue until the firewall managers were replaced by a new solution. | 2015-05-28 | 2017-03-21 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016015887 | Settlement Agreement | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R2. During its annual review of baseline documentation conducted as part of the Cyber Vulnerability Assessment (CVA), the entity discovered that a service not required for normal or emergency operations was incorrectly enabled. The main purpose of that service is to allow the sharing of an internet connection for devices using a modem over dial-up. The issue was identified on two devices during the execution of a CVA. An extent of condition review determined that the configurations were duplicated across several devices. The systems at issue do not have modems and the entity has disabled dial-up access by default. In fact, none of these devices have any internet access at all. The root cause of this violation was the failure to properly review an incorrect justification for the service at issue, which was previously needed under a prior operating system. This major contributing factor involves the management practice of asset and configuration management, which includes establishing inventory and configuration baselines and performing assessments. | CIP-007-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk is that leaving the internet connection sharing service enabled could allow threat vectors into an Electronic Security Perimeter (ESP) via the affected terminal servers. This risk was mitigated by the fact that the systems at issue do not have any internet access at all. This fact reduces the likelihood that this service could be successfully exploited because a connection to the internet would be required for any potential exploitation to be successful. | when the service at issue was no longer necessary | when the service at issue was disabled across all affected systems | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) provided training on change management tools and procedures for Version 5 compliance; 2) disabled Internet Connection Sharing Service from impacted terminal servers initially identified; 3) adopted a procedure requiring a review of the baseline configuration at least once over thirty-five days; 4) disabled Internet Connection Sharing Service on remaining impacted terminal servers; 5) validated implementation of baseline monitoring procedure; 6) validated implementation of baseline monitoring procedure for the following month; and 7) assessed for any lessons learned from the first two cycles and created a plan to implement. | 2016-08-19 | 2017-08-16 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014723 | Settlement Agreement | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R3. During an internal CIP compliance review, the entity’s IT compliance unit determined that a CIP-Cyber Asset patch was not timely assessed within 30 days of its availability as required by CIP-007 R3.1. The entity utilizes a management tool administered by the entity’s IT compliance unit to provide a greater degree of automation in the patch management monitoring and assessment process. Once a patch is entered in that tool as needing assessment, the the IT compliance unit notifies the responsible personnel to perform the required assessment. In this case, an internal compliance review revealed that a vendor patch was assessed nine days late. The untimely assessment did not result in any security vulnerability because the patch was ultimately deemed to be inapplicable. The internal compliance review was performed to verify the effectiveness of a newly implemented compliance tool and associated processes. The root cause of this violation was internal miscommunication between teams regarding the identification of personnel responsible for performing the required assessment, which prevented the patch from being timely assessed. Moreover, the patch management tool relies on a properly configured Master Asset List (MAL). In this case, there was confusion as to the proper formatting and correct methods for data entry into the MAL, which made it difficult for the patch management tool to function optimally. These major contributing factors involve the management practices of work management, which includes managing organizational work, and asset and configuration management, which includes establishing assets and configuration items inventory and controlling changes. | CIP-007-3a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The entity utilizes a secure network architecture by employing a layered security model with hardened devices. This architecture minimizes the risk posed by assessing a patch’s applicability late. The devices affected by the patch in question are not Internet facing and reside behind several layers of protection and firewalls. The most common type of attacks occur when a firewall or device is in a demilitarized zone (DMZ) that is Internet facing. In this case, a would-be attacker would need to first infiltrate two to three layers of firewalls before even being able to attempt an attack on the devices, thus reducing the risk. | when the entity was required to assess the patch at issue | when the entity actually assessed the patch | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) determined which individuals will serve as trainers/Subject Matter Experts (SMEs). These individuals will serve as local patch assessment/patch tool SMEs and will train additional entity users as necessary; 2) determined which individuals and groups have responsibilities for patch management and assigned specific individuals or groups to the work. The entity will have each individual or group confirm that they are aware of their obligations; 3) identified all individuals that needed access to the Patch Management Tool, submitted tickets for all impacted individuals, and ensured tickets are completed properly. The entity also provided evidence to show all impacted associates have confirmed their access is enabled; 4) developed/enhanced existing training requirements to demonstrate the essential information fields for the Patch Management Tool are formatted properly. Training procedure should include a template for MAL format that is used by the entity and all entity Business Units; 5) held discussions with all business units using the patch management tool and determined and documented resolutions to issues; 6) improved existing training by creating interactive training materials to more clearly show how a user should complete common tasks, how to assess and document a patch, how to enter assessments into the tool, and how to manually verify patch releases; 7) had key manager and operational compliance contacts review and approve training; and 8) conducted training sessions to “train the trainer,” which focused on the fact that training should be interactive. | 2015-06-10 | 2016-01-04 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2016015934 | Settlement Agreement | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R3. During regular patch management quality assurance activities related to CIP Version 5 implementation, the entity discovered that security patch reviews for two server management devices were not conducted within 30 days of their release as required by CIP-007-3 R3.1 and entity procedures. Several patches for two server management devices were not reviewed. Additionally, these patches were neither installed nor were compensating measures applied as specified CIP-007-3 R3.2 and entity procedures. After self-reporting this issue with the server management devices, the entity identified two additional patching issues that were also identified during the quality assurance review of the patch management program. One related to antivirus patching, and the other involved the late assessment of patches for the operating system of Physical Access Control System (PACS) devices. With respect to the antivirus patching issue, during the entity’s initial run of its new CIP Version 5 process for historical patch discovery, IT personnel identified that entity business units were running different version of the antivirus client installed in their respective environments. Most of the devices containing the antivirus client had up-to-date versions of the client and did not pose a compliance issue. However, the entity determined that about 5% of the devices had missed four antivirus client version upgrades, another 3% had missed three version upgrades, another 1% had missed two version upgrades, and the remaining 6% had missed one antivirus client version upgrade. In total, there were four antivirus client patches involved. With respect to the PACS patching issue, as part of the entity’s new patch management processes, an automatic Patch Source Review (PSR) is generated within the entity’s primary patch management system. The patch management system receives patch source information, identifies relevant security patches for particular devices, and generates an automated Device Patch Notification (DPN) to each asset owner to trigger the patch assessment process in a timely manner. During the early deployment of the patch management system, the entity discovered that due to a failure to correctly identify the devices in software/firmware libraries, DPNs were not generated for the operating system of multiple PACS devices for which patches were identified. As a result of not receiving these DPNs, the relevant asset owners did not assess the applicability of several unique patches within the 30-day requirement. However, the due diligence of the patch management system project team support by patch tracking tools and internal controls caught the error quickly, so that the patches in question were assessed 20 days late, and compensating measures were put into place. The root causes of this violation are as follows: a. With respect to the server management device issue, the names of the devices had not been correctly entered into the entity’s previous patch tracking systems. As a result the prior patch tracking systems did not flag the devices for security patch management. This problem was compounded by the device names also appearing incorrectly on other related tools, such as the central Shared Services Master Asset List, which hindered the detection of the error. b. With respect to the antivirus issue, the major contributing factor was a lack of clarity and specificity in the entity’s CIP Version 3 patch management procedures. Those procedures state that the responsible party for patch identification, assessment, and deployment is the asset owner. The asset owner includes the operating system owner and the application owner. This fact caused a difference of interpretation between business units as to who was performing the assessments and record keeping for patching the antivirus client. Additionally, at the time of the violation, entry into the patch tool was a manual process which lacked clarity as to who would perform the entry. c. With respect to the patch management system issue, the major contributing factor was the failure to correctly identify the devices in software/firmware libraries. All of these root causes involve the management practice of asset and configuration management, which includes establishing assets and configuration items inventory, controlling changes, and verifying the integrity of such items. | CIP-007-3a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, with respect to the devices involved in the server management device and patch management system issues, those devices were protected by multiple network infrastructure layers with separate two factor authentication and do not directly affect Bulk Electric Systems. Rather, they support backup and update functions of other systems. Second, with respect to the antivirus issue, the fact that some of the software clients were running older versions of the application did not increase the risk of this noncompliance because newer versions of the software concern the addition of new features, not the library or index of malicious files that the application uses to identify malware. In other words, the fact that some software clients were running older versions of the application did not affect the entity’s ability to identify and prevent malware because the library of threats was kept current. | when the server management devices were put into production | Mitigation Plan completion | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) updated CIP Version 3 procedure documentation with the CIP Version 5 procedure, which better defines the process; 2) completed patch reviews of all outstanding patches and entered into the current patch tracking system; 3) verified all device names as correct in the current patch tracking system; 4) verified devices are included in patch review cycles; 5) developed Patching Job Aid to further specify roles and responsibilities and workflow required by the unique nature of the environment; 6) updated software/firmware library for impacted devices; 7) distributed and communicated issuance of the Patching Job Aid to all business units; 8) completed an initial review to compare expected DPNs vs. Actual DPNs generated by the entity’s primary patch management system. Where discrepancies were discovered, Compliance Operations manually generated the missing DPNs; 9) deployed Patch Redesign code in production to ensure that no changes occur in the library records during the generation of Patch Source Reviews (PSRs); 10) reviewed and compared, on a monthly cycle, expected DPN vs. Actual DPNs generated by the patch management system. If any discrepancies are identified, Compliance Operations manually generates the missing DPNs; and 11) installed current applicable clients to all machines necessary | 2017-02-06 | 2017-04-13 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014738 | Settlement Agreement | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R5. Following an internal compliance review, the entity identified several accounts that were not afforded sufficient password change controls in accordance with CIP-007 R5.3.3. Specifically, these accounts included shared accounts, user accounts, administrator accounts, and read-only user accounts. The root cause of this violation was the fact that the entity had gaps in its inventory of local, shared, and administrator accounts, which resulted in the entity not identifying certain accounts for which annual CIP password changes must be applied. Other causal factors included a lack of internal controls for the management of the entity’s Supervisory Control and Data Acquisition (SCADA) system device accounts and required password changes and the failure to configure device accounts to permit password changes and logging prior to the entity putting those accounts into service. This major contributing factor involves the management practice of asset and configuration management, which includes controlling changes to assets and configuration items and baselines. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The entity’s secure network architecture and use of a defense-in-depth strategy minimizes the risk of unauthorized access. The entity utilizes redundant controls for its systems including monthly audits of shared and default account usage. The entity manages knowledge of account passwords on a need-to-know basis and the number of individuals with knowledge of account passwords is extremely limited. Furthermore, the entity has monitoring controls in place to alert the appropriate CIP asset owners when multiple failed logon attempts are made on NERC CIP assets. For an unauthorized intruder to exploit these accounts, the intruder would need to infiltrate several layers of firewalls to reach the segregated and isolated Electronic Security Perimeter with 2-factor authentication required or obtain unescorted physical access to a protected Physical Security Perimeter before they could gain access to these accounts. To get to the servers, one would need to first log in successfully to the corresponding SCADA nodes, which have limited accessibility, using completely different credentials. The accounts used to log into the SCADA nodes are in full compliance in following password change requirements and the passwords are unique to each device, providing protection. The risk of unauthorized access to the EMS Time Clock is also limited by the fact that access itself to the EMS Time Clock does not provide a significant threat vector. There is no protected information residing on the device, and there exists no functionality to connect from the EMS Time Clock to another device. | The first date that one of the account's passwords had not been changed in more than one year | when the entity finished changing passwords on all the accounts at issue | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) changed the passwords on all of the involved systems and accounts; 2) identified and implemented corrective actions and internal controls to track account password change tasks and to review account password age monthly; 3) completed and documented a formal inventory of application accounts; 4) created TFEs for accounts identified that do not currently have TFEs issued; 5) developed a job aid that specified methods for device and application account identification, management, and password change requirements for the entity’s SCADA system devices; 6) completed training on the newly developed IT entity job aid and reinforced existing processes on account and password management; and 7) completed an extent of-condition and validated its inventory of local, shared, and administrator accounts and had a qualified third party conduct an independent audit to validate the entity’s inventory and to provide additional recommendations on corrective actions and internal controls. | 2015-08-12 | 2016-01-18 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2015014722 | Settlement Agreement | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R6. The entity identified instances in which certain Cyber Assets did not perform continuous monitoring and logging functions as required by CIP-007-3a R6. As part of remediation efforts under a prior mitigation plan, the entity brought a number of Electronic Access Control and Monitoring Systems (EACMS) into CIP compliance, including a class of firewall managers used to manage checkpoint firewalls. All activity for these checkpoint firewalls are collected and logged to a security event management system either directly, or by way of the firewall managers. The entity discovered that logs from the firewall managers were not consistently collected by the security event management system. Upon further investigation and discussions with the vendor, the entity determined that a software issue was the apparent cause for the logging issue. Logs with larger file sizes interfered with the firewall agent’s ability to process such logs. While the entity was moving forward with the mitigation involving the security event management system and the checkpoint devices, it discovered issues arising from the deployment of the system to perform monitoring and logging on servers and workstations. The entity attempted to connect multiple servers and workstations to the security event management system for continuous monitoring and logging. The Cyber Assets were to be placed into the Energy Management System (EMS) production environment. While trying to configure the security event management system in the test environment, the entity unsuccessfully attempted off-boarding the old devices and on-boarding the new devices to log to the security event management system. Following this unsuccessful attempt, the entity relied on manual monitoring to be compliant with CIP-007 R6 when the devices were moved into production. Once in production, however, the default policy size for storage of log files on the devices was too small to hold all necessary security logs to facilitate manual monitoring, and eventually, logs were overwritten once the storage was full. The entity adjusted the log storage size for the devices to properly capture adequate logs. As a result of the technical issues deploying the security event management system and the default log storage size on the devices, logs were not available. The root cause of this violation involves the management practice of verification. The entity did not have an effective internal control in place to ensure that the firewall manager’s logs were consistently collected and logged as required by CIP-007-3a R6. A technical issue with the security event management system software interfered with the firewall agent’s ability to process such logs. This meant that all logs from the firewall manager were not consistently collected and logged by the security event management system. The security event management system was not able to resolve this technical issue and the entity found another software, which was able to process the larger file sizes that caused the problems. For the servers and workstations instance of noncompliance, a contributing cause was a failure of personnel to follow procedures to continue work to resolve technical issues with the security event management system in the test environment. | CIP-007-3a | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The entity utilizes a defense-in-depth strategy that reduces the risk of unauthorized access attempts. The entity monitors Electronic Security Perimeter access through active intrusion detection systems. Access to Critical Cyber Assets (CCAs) requires the potential user to pass through multiple layers of firewalls before accessing the CCA. These protections mean that changes to the configuration of a single firewall would not, on its own, provide access to an unauthorized user. Aside from the logging issue, the firewall was functioning properly in that it was effectively controlling what can pass through the device. Therefore, any changes to the configuration of a single firewall would not, on its own, provide access to an authorized user. The entity also has other redundant controls in place such as required two-factor authentication and that serves as an alternative mechanism for logging, monitoring, and alerting via Remote Secure Access logs. | when the firewall manager's logs were first not being collected by the security event management system | when the entity successfully implemented a monitoring process for all of the logs and assets at issue | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) implemented a manual monitoring process for the firewall managers until a permanent fix was applied to the firewall agent to fix the issues logging to the automated system; 2) obtained and implemented the vendor-developed coding solution for the firewall agent in order to re-enable logging to the automated system; 3) validated the efficacy and accuracy of the vendor-developed coding solution through monitoring and testing; 4) performed a comprehensive review of in-scope checkpoint firewalls for adequacy in supporting NERC compliance in the entity environment; 5) developed new and revised the old NERC CIP project management processes to address how projects are managed through the entire project life cycle; 6) provided training to all necessary entity staff to ensure proper understanding and adherence to the entity’s NERC Cyber Security Controls Test Procedure when transitioning supported assets; 7) reinforced the Requirements Engineering Fundamentals procedure by providing training for project team members to ensure all requirements, including compliance requirements, are identified, understood, and tested for each project; 8) evaluated any alternative solution based on the completed review performed earlier; 9) deployed the new Security Event Management solution to replace and mitigate the issues with logging of in-scope checkpoint devises including managers, loggers and firewalls; and 10) performed a comprehensive review of in-scope checkpoint firewall devices to ensure that logging, monitoring and alerting are meeting both security and compliance functions. | 2016-02-22 | 2016-04-19 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2017016756 | Settlement Agreement | RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-007-6 R4. The entity conducted an internal self-assessment of compliance with CIP-007-6 R4, including gathering evidence of reviewing a summary of logged events. The entity discovered that for sample dates of the 1st and 15th of two months, the records associated with the summary reviews for certain firewalls at the entity were incomplete, meaning that the reviews were not completed properly. Further review determined that stored security event logs had not been consistently reviewed, and, therefore, the reviews were not documented as required by the entity’s procedure and by CIP-007-6 R4, Part 4.4, which requires a review at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. The root cause of this noncompliance was an insufficient procedure for performing the reviews and a lack of quality control for verifying the completeness of the reviews. First, the procedure failed to establish a backup performer for this activity. The heavy and unbalanced workload for the employee responsible for performing the summary reviews prevented all reviews from being completed in a timely manner. Second, the procedure for performing these reviews was unclear regarding which reports were required to be completed for the review. Finally, the entity did not have adequate internal preventative controls in place to ensure that the reviews were completed in a timely manner. These major contributing factors involve the management practice of work management, which includes managing organizational work, and verification, which includes establishing verification procedures and criteria. | CIP-007-6 | R4 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the summary review of logs associated with these firewalls was not the only method by which the entity sought to identify security threats. The monitoring team also reduced the risk associated with potential malicious actions by monitoring events on a network as well as on an asset level. For instance, the monitoring team performs summary reviews of the Cyber Assets within the Electronic Security Perimeters as well to ensure awareness of its systems. Second, during the time period in question, at no time was the capability of performance of logging interrupted. ReliabilityFirst also notes that no actual harm occurred because there were no undetected Cyber Security Incidents and negative impacts to any Bulk Electric System Cyber Systems during the time period in question. | when the first summary review was missed | when the entity generated the missing summary review reports and conducted the reviews | $0 (for RFC2016015884, RFC2016015885, RFC2016015886, RFC2016015887, RFC2016015888, RFC2015014723. RFC2016015930, RFC2016015932, RFC2016015933, RFC2016015834, RFC2015015328, RFC2015014717, RFC2015014718, RFC2015014720, RFC2015014738, RFC2015015071, RFC2015014719, RFC2015014722, RFC2015015311, RFC2017016756, and RFC2017016759) | Self-Report | To mitigate this violation, the entity: 1) reassigned the summary reviews to a primary and backup performer who did not have the same workload imbalance; 2) generated the missing summary review reports and conducted an analysis to determine if there had been any undetected Cyber Security Incidents. The result of the industrial control system security operations center analysis confirmed there had been no undetected Cyber Security Incidents; 3) updated the NERC CIP Security Event Monitoring job aid to: (i) document the specific roles and responsibilities for the primary and back-up performers; (ii) document more specificity for recording the performance of the required summary reviews; and (iii) document a complete list of reports to be reviewed as part of the summary reviews; 4) documented, tested and implemented an internal control job aid to have a compliance liaison from the Real-time Security and Compliance section support the performance of the summary reviews by the security operations center. The compliance liaison will periodically review the performance records for accuracy and completeness according to a checklist and record the review using the same checklist. Additionally, an automated prompt will serve as a reminder of the review; 5) conducted internal training with the Real-time System Security and Compliance performers related to the new internal control job aid; and 6) conducted internal training with the security operations center performers related to the updated NERC CIP Security Event Monitoring job aid. | 2017-07-14 | 2017-08-09 | Neither Admits nor Denies | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. The major factors contributing to the causes of these violations relate to two overarching themes: (a) incorrect configuration of tools used to automate or otherwise enhance certain processes; and, (b) gaps or inadequacies in certain processes and procedures. These themes involve the management practices of asset and configuration management, workforce management, and verification. The entity's mitigating actions demonstrate a commitment to maturing in these management practices and better position the entity to be more reliable and secure in the future. ReliabilityFirst considered the entity's compliance history to be an aggravating factor in the disposition determination. The entity has been highly cooperative throughout the entire enforcement process. Following the self-reporting of the violations, the entity met with ReliabilityFirst on a regular basis to discuss progress on mitigation, the effectiveness of its CIP Compliance Program, reliability, and other related activities. Throughout the enforcement process, the entity voluntarily provided ReliabilityFirst with an abundance of information regarding the violations in a manner that was detailed, well organized and timely. The entity has been transparent with ReliabilityFirst regarding its violations, processes, and systems, and this insight has allowed ReliabilityFirst to better analyze the violations and assist the entity with resolving the same. The entity's level of cooperation throughout the enforcement process has been exemplary and ReliabilityFirst awarded a significant amount of mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. As explained above, the entity has committed to effective mitigating actions designed to both bring the entity back into compliance and to effectively transition the entity into compliance with CIP Version 5. The entity crafted these mitigating actions to include both what is legally required to mitigate each discrete violation (both addressing the issue and preventing recurrence), as well as going even farther by implementing broad changes (such as overhauling numerous procedures and adding or refining automation tools) to enhance the CIP Compliance culture at the entity. ReliabilityFirst awarded mitigating credit for the thoroughness of the entity's mitigation.