## Public CIP SNOP Posting
Region | Registered EntityName | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017018459 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-6 R2 Parts 2.1, 2.2, 2.3, and 2.4. Specifically, WECC_URE1 reported that it was instructed by the designer, manufacturer, and warranty provider of the high voltage direct current protection and control system (HVDC PCS) at a substation, that its patches and updates for software and firmware provided during the warranty period would be functional patches rather than security patches and only for the designer's proprietary devices. The designer's position was that because the substation Station Control and Monitoring (SCM) network for the HVDC PCS was a private network with no External Routable Connectivity (ERC), it did not perform security patching because of the potential to disrupt operations. Due to a setting in a single device being incorrect, the SCM network suffered a failure during the trial operation phase. The designer's position was not to apply security patches to the system devices because those security patches could pose a risk to system reliability without providing a tangible security benefit. As a term of purchase, the designer had approving authority for implementation of patches for third-party manufactured devices that were utilized by the designer in the system design. Because of this agreement between WECC_URE1 and the designer, the responsibility of evaluating security patches for the third-party devices and Operating System platforms had yet to be defined. The HVDC PCS at the substation was an engineered high speed, real time, closed loop, protection and control system. This engineered system consists of multiple devices running multiple software packages that are closely integrated by the manufacturer, to meet the protection and control requirements. The manufacturer and designer sold the engineered system to WECC_URE1 and retained the knowledge of how the software and hardware integrations work. As required by CIP-007-6 R2 Part 2.1, WECC_URE1 had identified the manufacturer as the patch source for the HVDC PCS at the substation. However, since the manufacturer does not have a website with patching information for the HVDC PCS, it was required to notify WECC_URE1 when new security patches were available. The evaluation of security patches for the BES Cyber Assets (BCAs) and Protected Cyber Assets (PCAs) at the substation and the creation of mitigation plan(s), had not taken place since the requirement became effective on July 1, 2016 as required by CIP-007-6 R2 Parts 2.1, 2.2, 2.3, and 2.4. Additionally, WECC_URE1 was performing its CIP-007-6 R2 security patch management program for the other CIP devices by different manufacturers within this substation. This violation was discovered during WECC_URE1’s preparation for a WECC audit. WECC determined that WECC_URE1 failed to implement a program or process for tracking (2.1), evaluating (2.2), and installing cyber security patches or creating a mitigation plan to address the vulnerabilities addressed by each security patch that was not installed (2.3) and implementing the mitigation plan (2.4) for its designer devices at its substation, designated as a Medium Impact BES Cyber Systems (MIBCS), consisting of BCAs and PCAs. WECC determined that this violation began when the Standard and Requirement became mandatory and enforceable for WECC_URE1, and ended when WECC_URE1 implemented a security patch management program for the designer's devices in its MIBCS located at its substation, for a total of 502 days of noncompliance. The root cause of this violation was WECC_URE1's not integrating the substation HVDC PCS into the field patch management process. Specifically, WECC_URE1 underestimated the resources needed and effort required to establish and operate a compliant security patch management program at its substation. | CIP-007-6 | R2; P2.1, 2.2, 2.3, and 2.4 | High | Severe | WECC determined this noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE1 failed to implement or document a security patch management program for its manufacturer's devices within its MIBCS consisting of BCAs and PCAs, located at the substation, as required by CIP-007-6 R2. Such failure could potentially result in unauthorized electronic access to the vulnerable systems within WECC_URE1's substations. Unauthorized electronic access, due to unpatched software, could result in complete control of the unpatched devices due to malware infection or other successful intrusion into the network locations of the unpatched systems. The result could be complete control (installation of software, exfiltration of data, remote control, etc.) of the affected system and an anchor point for reconnaissance and spreading through the environment, which could result in significant negative effects to the BPS, including neighboring entities via interties. The substation monitors and controls a WECC major path. However, the substation has no ERC to the substation; therefore, any compromise would have to be performed at the physical site itself. WECC_URE1 implemented weak controls to detect this violation. Vendor-approved security patches are applied on an annual basis for vendor-owned CIP assets. All other CIP assets are managed under WECC_URE1's security patch management program. Based on this, WECC determined that the potential harm had a moderate likelihood of occurring. | when the Standard and Requirement became mandatory and enforceable | when a security patch management program was implemented for the devices in scope | No penalty | Self-Report | To mitigate this violation, WECC_URE1: 1) enrolled the BCAs and PCAs at the substation into its firmware tracker; 2) utilized its existing patch mitigation plan process to document all designer-released security patches that needed to be deployed to the devices in scope; and 3) documented changes to the baseline for firmware or software as a result of deploying patches during a maintenance outage. | 2017-11-15 | 2017-12-07 | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although WECC_URE1 does have a documented ICP, WECC determined that WECC_URE1 did not implement effective controls to detect this violation in a timely manner. WECC considered WECC_URE1's CIP-007-6 R2 compliance history in determining the disposition track. WECC considered WECC_URE1's compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017974 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R2.4. Specifically, WECC_URE1 reported that during a routine audit, it was discovered one Cyber Asset at a substation with External Routable Connectivity (ERC) containing Medium Impact BES Cyber Systems (MIBCS) that allowed access to a relay without any authentication procedure. The investigation showed that the device had been set to allow access without a password. Because this violated the approved configuration for these devices, technical services issued an inspection of all in-service devices to review and correct any devices which were not set up correctly (remote authentication enabled and all ports set to require authentication). WECC_URE1 determined there were no additional devices configuration issues. The improperly configured device had one port where the access control default was not changed to require a password. This setting was changed on the day it was found. This setting change is required in the configuration manual utilized by WECC_URE1 . The manual was also reviewed and additional language was added to reinforce the requirement to enable passwords. WECC determined that WECC_URE1 failed to implement strong procedural or technical access controls at the access point of an Electronic Security Perimeter (ESP) to ensure authenticity of the accessing party for one device that allowed access to a relay. The root cause of this violation was the accuracy or effectiveness of changes were not verified or validated. Specifically, the configuration of the device was never completely validated to ensure accuracy. | CIP-005-1 | R2; R2.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE1 failed to ensure authentication at the device access point for all user access into WECC_URE1’s substation containing MIBCS as required by CIP-005-1 R2.4. Such failure could result in inappropriate access via a compromised or misused remote access account resulting in significant negative effects on the reliability and stability of the Bulk Electric System (BES), including but not limited to disruption, manipulation, or compromise of the MIBCS for reconnaissance. WECC_URE1 implemented weak detective controls in that the issue was identified as a result of an audit 8 years after the device should have been compliant with the CIP-005-1 R2.4. However, access to device was limited to a small number of personnel who were authorized to have said access. The improper setting allowed direct access to the device from WECC_URE1’s network The network requires privileges and authentication to access. This is a local WECC_URE1 network for supporting field BES Cyber Systems that does not have direct access to the Internet. A detailed configuration review of devices revealed no additional misconfigurations. Based on this, the potential harm had a minimal likelihood of occurring. | when access point authentication should have been implemented | when WECC_URE1 implemented access point authentication | No penalty | Self-Report | To mitigate this violation, WECC_URE1 1) changed the configuration on the device to require authentication; 2) reviewed all device configuration to ensure authentication was configured prior to accessing any ESP; 3) updated the device configuration procedure to provide additional emphasis on the setting of port passwords; 4) added an additional control to the device configuration procedure requiring discovered instances of device configuration inconsistent with configuration document to be presorted to the Subject Matter Expert; and 5) sent an email notification to applicable personnel communicating the change to the device configuration procedure. | 2017-08-14 | 2018-01-29 | Does Not Contest | WECC did not give credit for WECC_URE1’s internal compliance program (ICP). Although WECC_URE1 does have a documented ICP, WECC determined that WECC_URE1 did not implement effective controls to detect this violation in a timely manner. WECC considered WECC_URE1’s CIP-005-1 R2.4 compliance history in determining the disposition track. WECC considered WECC_URE1's CIP-005-1 R2 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015839 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R3.1. Specifically, WECC_URE1 reported that in preparation an audit, WECC_URE1 determined that it was not able to confirm that it documented the assessment of security patches and security upgrades for applicability within 30 calendars days of the availability of the patches or upgrades for seven Critical Cyber Assets (CCAs). The CCAs included two Remedial Action Schemes (RAS) within its Control Centers and five network servers. During an internal investigation of this noncompliance, WECC_URE1 determined that after experiencing network connection issues, one of its technicians saved evidence of security patch assessment to his computer’s hard drive, which was subsequently wiped clean without saving a copy when the technician’s employment ended; resulting in a gap in security patch management documentation from. After reviewing all relevant information, WECC determined an increase of scope from the initial Self-Report. During scheduled maintenance, WECC_URE1 performed a full investigation which identified 58 additional RAS system devices, and 6 RAS servers. WECC_URE1 failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of the availability of the patches or upgrades for a total of 71 CCAs. The root cause of the first device issue was the improper identification and classification of a device in the PACS systems. The root cause of the network equipment issue was the poor transition of duties between personnel. The root cause of the RAS system issue was the lack of written communication. Specifically, a specific security patch fix was not documented on WECC_URE1’s patch discovery list. | CIP-007-3a | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, WECC_URE1 failed to document the assessment of security patches within 30 days for 71 CCAs. Such failure may lead to security exposures that could result in serious adverse effects on WECC_URE1’s operations, including the installation of potentially harmful software on the CCAs. Installation of malware or other harmful software could lead to unintended access and eventually to control of systems and software. Given that this violation involved several different locations containing the CCAs, a widespread coordinated attack would be conceivable. As such, the failure to adequately protect devices and resources could affect the reliability of the BPS. However, the controls implemented by WECC_URE1 reduced the likelihood of the potential harm from occurring. Specifically, none of the network equipment has internet access and was secured in server rooms with limited authorized physical access. Additionally, antivirus was maintained on all network applicable devices. The RAS equipment does not have ERC and is also located in locked cabinets within Controls Centers, with alarming for access attempts. | when security patches and security upgrade assessments should have been documented. | Mitigation Plan completion | No penalty | Self-Report | To mitigate this violation, WECC_URE1: 1) updated its patch management plan; 2) assessed for applicability all security patches and security upgrades for the devices in scope; 3) initiated change tickets for security patches and security upgrades assessed as applicable for the devices in scope; 4) updated its processes and procedures for RAS systems patch discovery, evaluation, testing, and installation; 5) ensured all installed software on RAS systems in scope are on the patch source list for monthly discovery and evaluation; and 6) ensured all applicable security patches are part of its RAS system upgrade. | 2017-05-15 | 2017-10-12 | Does Not Contest | WECC did not give credit for WECC_URE1’s internal compliance program (ICP). Although WECC_URE1 does have a documented ICP, WECC determined that WECC_URE1 did not implement effective controls to detect this violation in a timely manner. WECC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit. WECC considered WECC_URE1's CIP-007-3a R3 compliance history in determining the disposition track. WECC considered WECC_URE1's CIP-007-3a R3 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2017017706 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-6 R2 part 2.2. Specifically, WECC_URE1 reported that as part of its reliability compliance monitoring efforts, during an internal spot check of visitor logs it discovered that an entry made on a specific date did not include a last exit time for one visitor as required by CIP-006-6 R2 Part 2.2. WECC determined that WECC_URE1 failed to include all the required elements of CIP-006-6 R2 Part 2.2 specific to one visitor on its visitor log. The root cause of this violation was due to a mental lapse that lead to an incorrect performance. Specifically, the visitor escort was trained appropriately in the process; however, did not follow that process. WECC determined that this violation began when WECC_URE1 did not fill in the last exit time on a visitor log, and ended when WECC_URE1 mitigated this violation, for a total of 372 days of noncompliance. | CIP-006-6 | R2; P2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to include all the required elements of CIP-006-6 R2 Part 2.2 specific to one visitor on its visitor log. Such failure could lead to the visitor being allowed back in without knowledge; without justifiable cause; and potentially without a visitor escort. In addition, ensuring that visitors are logged out provides closure of the visitor management process and clarification that the individual is still not somewhere in the facility, which during an emergency could create an issue for security personnel attempting to locate the individual for safety concerns. However, WECC_URE1 implemented good preventive controls. Specifically, WECC_URE1 maintained a visitor escort for the visitor while in the Physical Security Perimeter (PSP), and performed all required duties with the exception of ensuring final logout of the visitor. The PSP which was protecting the control center was manned 24 hours a day, seven days a week by system operators and physical security personnel. Additionally, cards issued to visitors must be turned back in to Security prior to final exit, and the cards do not actually open any access points; thereby, reducing the likelihood of re-entrance without an escort. WECC determined the potential harm had a remote likelihood of occurring. | when the visitor log was not filled in completely | Mitigation Plan completion | No Penalty | Self-Report | To mitigate this violation, WECC_URE1: 1) reiterated to the escort involved with this violation, and other applicable personnel, of the requirement to fill out the visitor log in its entirety when acting as an escort; 2) updated the visitor procedures for its control center to be consistent with the visitor procedures at its other control center, which changes the log from being a physical book that used handwritten updates to log visitors to a digital SharePoint list; 3) modified its procedures to standardize the roles and responsibilities at the control centers; 4) updated the PSP plan to include the revised visitor process that is applicable to both control centers; and 5) sent communications to applicable personnel to establish the revised visitor process at its control center. | 2017-06-29 | 2018-01-31 | Does Not Contest | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. It was through the internal control of monitoring that this violation was discovered. WECC considered WECC_URE1’s CIP-006-6 R2 compliance history in determining the disposition track. WECC considered WECC_URE1’s compliance history to be an aggravating factor in the penalty determination.