## Public CIP SNOP Posting
Region | Registered EntityName | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2017017596 | Settlement Agreement | NPCC_URE1 submitted a Self-Report stating that it had three instances of noncompliance with CIP-006-6 R1. As part of NPCC_URE1’s NERC Reliability Standards compliance program, a compliance concern was submitted by NPCC_URE1 staff and in accordance with NPCC_URE1’s procedures, an internal investigation was conducted of the reported incident that revealed a potential noncompliance. The violation started when NPCC_URE1 failed to follow its NERC CIP Physical Security Plan to restrict physical access, monitor and issue an alarm or alert to personnel identified in its Bulk Electric System (BES) Cyber Security response plan within 15 minutes of detecting unauthorized physical access to one (1) Physical Access Control System (PACS). As a result, there was potential unauthorized access to one (1) PACS for multiple periods of time due to the failure to meet Parts 1.6, and 1.7 of CIP-006-6 R1. Specifically, a room door was propped open for approximately 1 hour and 54 minutes. The timeline is as follows: • 0623: Technician #1 with authorized access enters the room • 0624: PACS generated a propped door alarm • 0628: Security Guard acknowledged propped door alarm and cleared from system • 0815: Security Guard noticed door was open on video camera monitoring system and notified security manager • 0818: Security Guard secured the door In another instance, a room door latch was disabled for approximately 7 hours and 38 minutes. During that time, there were seven (7) forced door alarms generated by the PACS signaling the detection of potential unauthorized physical access (entry/exit without the use of the card reader). Security failed to monitor the alarms and notify a member of the incident response team within 15 minutes of detecting unauthorized access. The timeline is as follows: • 0858: Technician #2 with authorized access disabled lock by stuffing material into the communications’ room door lock strike plate, which inhibited the door latch from engaging. • 0858 – 1636: Seven (7) forced door alarms were generated by the PACS, signaling the detection of physical entry without the use of the card reader (potential unauthorized access). Security did not respond as required by NPCC_URE1 procedure and failed to notify a member of the incident response team within 15 minutes of detecting unauthorized access. • 1636: Security Guard discovered the disabled latch during a regular patrol and returned the latch to proper service. In another instance, the room door was propped open for approximately 3 hours and 7 minutes. The timeline is as follows: • 0802 – 0845: Five (5) Technicians with authorized access entered the room • 0845: PACS generated a propped door alarm. The Security Guard acknowledged the propped door alarm, and began to investigate via the CCTV system and site intrusion detection system. The Security Guard cleared the alarm. • 1152: Security Guard who was dispatched to investigate found the propped door and secured it. The Security Guard spoke with a NPCC_URE1 electrician (who has authorized unescorted physical access) in the room. The electrician stated that the door was propped open when he arrived and no one else was in the room. The root cause is lack of awareness and failure to follow documented procedures. In the three instances, NPCC_URE1 Technicians violated the documented NERC CIP Physical Security Plan, NPCC_URE1 Security failed to monitor for unauthorized access to a PACS, and NPCC_URE1 Security failed to issue an alarm or alert in response to detected unauthorized physical access to a PACS. | CIP-006-6 | R1: P1.6; P1.7 | Medium | Severe | The violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PACS network switch within the room permits network communication between card reader control panels and the various PACS servers. It could have been physically damaged or taken out of service by not following the proper access process and/or failing to respond to unauthorized access. If this PACS network switch became unavailable, the primary security monitoring workstation location would be unable to communicate with the PACS server/PSP related card panels. However, all panels would continue to be operational using the last known configuration and an alternate PACS monitoring workstation would provide the monitoring capability. The PACS network switch is not in the direct communications path between the PSP related card panels, PACS servers and the alternate PACS monitoring workstation. The entity reduced the risk of a malicious attacker causing harm to the exposed PACS’ core network switch by implementing a defense-in-depth security strategy. The PACS core network switch has no graphical user interface and only provides administrative access through a physical console connection and has its unused physical ports disabled. It also has a secure shell configuration requiring appropriate log-in credentials that are maintained as per NERC CIP requirements. The PACS core network switch is located behind three separate restricted physical access control points, which include a perimeter intrusion detection system, vehicle barriers, and CCTV cameras. Security systems are monitored 24x7 by onsite security personnel. Card readers are used to enter the perimeter and the building containing the room at issue. All personnel who can facilitate their own access through the permiter and building must have a valid Personnel Risk Assessment (PRA). All others entering this area are accompanied by personnel having access rights. No other CIP assets are located in the room. During the first two incidents, approximately 30 persons carded into the building. Of those 30, only three (3) did not have access to the room. All three (3) have valid PRAs. During the third incident, approximately 13 persons carded into the building. Of those 13, only four (4) did not have access to the room. All four (4) have valid PRAs, with three (3) having authorized access to other NPCC_URE1 PSPs. NPCC_URE1 performed an investigation and found no evidence of any physical tampering with or unauthorized electronic access attempts during the timeframe of the incidents. Had an unauthorized person been successful in physically disabling the switch, the PACS would have sent communications failure messages to NPCC_URE1’s operations center and security. No harm is known to have occurred. | The date the entity failed to follow its NERC CIP Physical Security Plan to restrict physical access, monitor and issue an alarm or alert to personnel identified in its BES Cyber Security response plan within 15 minutes of detecting unauthorized physical access to one PACS. | The date the entity resumed following its NERC CIP Physical Security Plan to restrict physical access, monitor and issue an alarm or alert to personnel identified in its BES Cyber Security response plan within 15 minutes of detecting unauthorized physical access to one PACS. | 0 | Self-Report | To mitigate this violation, NPCC_URE1: 1) Management conducted an ‘on the job briefing’ with technicians to reinforce the importance of maintaining physical security; 2) Security conducted refresher training with security management staff to reinforce physical security policies and procedures, including physical access controls; 3) Compliance department referred this matter to NPCC_URE1’s labor and law department for employee disciplinary consideration for staff involved in incidents; 4) Security identified and implemented system improvements for forced and propped door alarm notifications and response to unauthorized access to PSPs, specifically, Security worked with an outside vendor to create a PDF window pop-up with specific instructions on when and how to respond to an alarm to help the operator to detect, assess, and respond to alarms; 5) Security and compliance conducted a presentation of physical security policies and procedures during an all-hands meeting; 6) Security implemented new signage for all PSPs at NPCC_URE1’s BES facilities to include language related to adherence to NPCC_URE1’s physical security procedures; 7) Physical Infrastructure Security increased CCTV recording retention capabilities at all NPCC_URE1 BES facilities; and 8) Physical Infrastructure Security implemented a system for forced and propped door alarm notifications and response to unauthorized access. | 2017-12-19 | 2018-06-25 | Does Not Contest | NPCC reviewed NPCC_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. NPCC_URE1 self-reported this particular potential non-compliance and continued to be highly cooperative throughout the entire process. Although the violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system, NPCC determined that Compliance Exception treatment was not appropriate here based on the underlying conduct, which included deliberate and repetitive actions to prop open a door and/or disable locks in violation of the NPCC_URE1 procedure.