## non-CIP SNOPs
Filing Date | NOC ID | Region | Registered Entity Name | NCR | Reliability Functions | Notice of Confirmed Violation or Settlement Agreement | Admits OR Agrees and Stipulates OR Neither Admits nor Denies OR Does Not Contest | Total Penalty or Sanction ($) | NERC Violation ID | Reliability Standard | Req | Risk Assessment | Violation Risk Factor | Violation Severity Level | Method of Discovery | Discovery Date | Violation Start Date | Violation End Date | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | Description of Noncompliance | Description of the Risk Assessment | Description and Status of Mitigation Activity | Other Factors Affecting the Penalty Determination which includes Compliance History and Internal Compliance Program and Compliance Culture
2022-08-31 | NOC-2783 | Texas Reliability Entity, Inc. (Texas RE) | Buffalo Gap Wind Farm, LLC (AES Buffalo Gap) | NCR04025 | GO | Settlement Agreement | Admits | $105,000 | TRE2020023422 | FAC-009-1 | R1 | Moderate | Medium | Severe | Compliance Audit | 2020-05-14 | 2009-04-30 | 2021-08-26 | 2021-08-26 | 2021-10-01 | Texas RE determined that AES Buffalo Gap was in violation of FAC-009-1 R1. Specifically, AES Buffalo Gap did not establish Facility Ratings that are consistent with the statement in its Facility Ratings Methodology that "the ratings for all AES Buffalo Gap, LLC, generating units, including turbine-generators, lines, transformers, and series and shunt compensation devices, shall, in all cases, be equal to the most limiting applicable equipment rating of the individual equipment that comprises the facility." AES Buffalo Gap did not consider all applicable equipment in its Facility Ratings documentation. This issue was discovered during a Compliance Audit engagement from April 6, 2020 to May 14, 2020. This violation started on April 30, 2009, when Buffalo Gap made its original Facility Ratings Methodology in response to a FAC-008-1 and FAC-009-1 filed violation. AES Buffalo Gap updated its ratings documentation and established Facility Ratings consistent with its most limiting element on August 26, 2021, ending the violation. This issue began when FAC-009-1 R1 was applicable, which was replaced by FAC-008-3 R6 during the duration of the violation. AES Buffalo Gap has one Facility with two substations. The one-line diagram shows four buses at the Facility, which are grouped in the Appendices in the Methodology document, with three total build phases, BG1, BG2 (with 2 buses), and BG3. The Methodology document calculates the Facility Ratings of BG1 at 117.8 MW, BG2A and B at 115.5 MW, and BG3 at 170.2 MW, for a total of approximately 520MW/547MVA. However, these documents did not consider all applicable equipment. Texas RE identified two series elements on the one-line diagrams that were not included in the Facility Ratings calculations, Switch 89-1B and a Wave Trap. The one-line diagram showed switch 89-1B and a Wave Trap equipment as AEP owned. AES Buffalo Gap originally believed this equipment belonged to another Transmission Owner, however a review of the interconnection agreement revealed this equipment to actually be owned and installed by AES Buffalo Gap. The Wave Trap had an installed rating of 3,000 amps, and Switch 89-1B had a nameplate rating of 2,000 amps (478 MVA). As Switch 89-1B is located after the site aggregation and before the point of interconnection, this 478 MVA rating is limiting the total rating of the aggregate Facility relative to the original Facility Rating of 547 MVA, and is therefore the most limiting element. AES Buffalo Gap's Facility Rating Methodology, referencing certain IEEE standards, allows AES Buffalo Gap, based on certain ambient and operating conditions, to increase the Equipment Rating of the switch that is the most limiting series element. Due to the location of Switch 89-1B and the assumed ambient temperature, the applicable multiplier is 1.03. Applying this multiplier increased the Facility Rating from 478 MVA to 492 MVA. This limiting factor was incorporated into the Facility Ratings documentation and Methodology by August 26, 2021, ending this part of the violation. In addition, AES Buffalo Gap did not document the consideration of certain additional equipment in its Facility Ratings documentation, which is inconsistent with the Facility Ratings Methodology for the Facility. Information on these elements was later provided in the Compliance Audit and incorporated into Facility Ratings documents by August 26, 2021, ending this part of the violation. None of this additional equipment was the most limiting or second most limiting equipment. The root cause for not including the most limiting element in the Facility Ratings was due to a misunderstanding of the Reliability Standard. AES Buffalo Gap was not aware that the series elements should have been included in the Facility Ratings regardless of which entity owned them. The root cause for not including the additional relevant equipment in the Facility Ratings documents was due to a Methodology document that was insufficient in describing necessary inclusions and sources of ratings. This violation started on April 30, 2009, when AES Buffalo Gap made its original Facility Ratings Methodology, and ended on August 26, 2021, when AES Buffalo Gap updated its ratings documentation and established Facility Ratings consistent with its most limiting element. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to document accurate Facility Ratings could have resulted in operators relying on incorrect Facility Ratings, which could lead to overloading, damage to equipment, or unexpected outages. If the switch fails due to exceeding its ampacity rating, it will likely be when the wind farm is operating at or near its full capacity, meaning that approximately 500 MW of capacity would unexpectedly trip offline. This risk is aggravated by several factors. First, AES Buffalo Gap is a relatively large wind farm at approximately 492 MVA. Second, the actual Facility Rating was found to be lower than previously documented, and the violation spanned over 11 years. Third, during that span, Buffalo Gap operated at or over its 492 MVA capacity on 1,522 separate occasions for a total of 5,016 hours, about 5% of the total time period, with the average exceedance being 21 MW per occasion. Fourth, the violation period started immediately following the conclusion of a filed violation regarding the failure to have a Methodology for Facility Ratings, causing this Facility to have missing or incomplete Facility Ratings since its registration. This did not pose a serious or substantial risk due to several factors. First, no trips or Misoperations occurred as a result of the violation. Second, Buffalo Gap owns the Transmission line connecting it to the nearby American Electric Power (AEP) substation, and there are no other Facilities on the line that could have been impacted. Buffalo Gap’s Facility’s connection to the AEP substation is isolated and is unlikely to affect neighboring entities. AEP also monitors the Facility output and provides notifications if tolerances are near to or exceed system limits. Third, Buffalo Gap conducts periodic infrared temperature scans while operating at a minimum of 80% operational capacity twice per year and detected no abnormal temperatures from the misrated or unlisted equipment. If the equipment had been heated to abnormal temperatures during periods of high loading, AES Buffalo Gap’s proactive measurement program would likely have identified the issue sooner and led to replacement of the equipment or revision of the documented Facility Ratings. Finally, the portion of the violation relating to a failure to document the consideration of certain equipment in the development of the Facility Ratings documentation was mainly a documentation issue, as these records were later incorporated and did not change the identification of the most limiting or second most limiting equipment. No harm is known to have occurred. | To mitigate this violation, AES Buffalo Gap has performed the following actions: 1) verified and revised one-line diagrams to as-built conditions; 2) revised Facility Ratings documentation; 3) revised Facility Ratings Methodology to properly describe rating sources and processes used to derive ratings; 4) utilize a third-party to perform compliance verifications or mock audits consistent with FAC-008-3; and 5) AES Buffalo Gap completed an extent of condition review in order to develop a revised Methodology and documentation. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed AES Buffalo Gap's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. AES Buffalo Gap did not receive mitigating credit for self-reporting because the issue arose from a Compliance Audit. AES Buffalo received mitigating credit for admitting to the violation. Texas RE considered AES Buffalo Gap’s FAC-009-1 R1, FAC-008-1 R1, and FAC-008-3 R6 compliance history in determining the penalty. Texas RE considered AES Buffalo Gap’s FAC-009-1 R1 compliance history to be an aggravating factor in the penalty determination. Specifically, AES Buffalo Gap was previously penalized for violations of FAC-008-1 R1 and FAC-009-1 R1 under Violation IDs TRE201000118 and TRE201000119, which both relate to a single set of facts and are considered to be a single previous violation for the purposes of calculating the penalty. These cases involved violations due to not having a Facility Ratings Methodology from the time AES Buffalo Gap was registered as a Generator Owner on June 28, 2007 until April 30, 2009, when a Facility Ratings Methodology was adopted. This compliance history should be considered aggravating because the current violation is a direct result of the incorrect Methodology created to end the previous violation. Texas RE also evaluated other related FAC-009-1 R1 and FAC-008-1 R1 violations for AES Buffalo Gap’s affiliates during the violation duration, which were filed under Violation IDs RFC200800043, RFC200800044, RFC200800046, RFC200800047, RFC200800053, RFC200800054, SPP201000410, and SPP201000411. However, Texas RE did not consider these affiliate’s compliance history to be aggravating relevant compliance history because they did not involve shared personnel or compliance programs and because the mitigation in these issues would not have prevented the instant violation.
2022-07-28 | NOC-2778 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas, LLC (DEC) | NCR01219 | TO, GO | Settlement Agreement | Neither Admits nor Denies | 210000 | SERC2018020332 | FAC-009-1 | R1. | Moderate | Medium | High | Self-Report | 2018-08-29 | 2007-06-18 | 2022-06-27 | 2022-06-27 | TBD | Multi-Region Regional Entity (MRRE) group 15a includes Duke Energy Carolinas, LLC (DEC), Duke Energy Florida, LLC (DEF), Duke Energy Corporation (DECorp), and Duke Energy Progress, LLC (DEP) (collectively referred to as “Duke” or the “Duke Companies”). This violation consists of instances where DEC, DEF, and DECorp were noncompliant with FAC-009-1 R1 (extending to FAC-008-3 R6) for failing to have Facility Ratings that were consistent with their respective Facility Ratings Methodology (FRM). This violation involves instances of noncompliance that were self-reported, identified during a subsequent SERC-led audit, and during the extent of condition. SERC was first notified of this violation when DEF through DEC, pursuant to an existing MRRE Agreement, notified SERC in a Self-Report on August 28, 2018, that it had discovered three instances where it had Facility Ratings that were not consistent with its FRM. All three instances occurred at a single 500 kV substation and each impacted a separate 500 kV line segment. The three line segments were incorrectly inputted into the Facility Ratings Database (FRD) as bundled line conductors rather than single line conductors because at the time of the substation energization, there were no approved Facility Rating Spreadsheets (FRSs) available. In the absence of approved FRSs, personnel defaulted to the bundled line conductor ratings, which drove the conductor ratings higher. However, the conductors were the most Limiting Element and caused Facility Rating derations of 7.8%. On February 8, 2019, while completing walk-downs in preparation for the SERC-led audit, DEC and DECorp discovered potential instances of noncompliance with FAC-008-3 R6, and submitted one Self-Report designated NERC ID SERC2019021040, which was dismissed and consolidated with the original Self-Report. Additionally, during the SERC-led audit, SERC conducted sample walk-downs for all Duke Companies. While no issues were identified for DEP or DEF, the walk-downs identified that DEC had additional instances where Facility Ratings were not consistent with the respective FRM. The audit finding was initially designated as NERC ID SERC2019021764, but was dismissed and consolidated with the original Self-Report. Following the SERC-led audit, SERC requested walk-downs from all Duke Companies to determine the extent of condition. The results of these walk-downs caused SERC to request that DECorp complete a walk-down of all Bulk Electric System (BES) transmission and generation Facilities, with an expected completion date in June 2022. DEC, DEF, and DEP later informed SERC that they would voluntarily complete 100% walk-downs of all their BES Transmission station and substation Facilities. As of November 2021, the results of all walk-downs performed (prior, during, and post-audit) for each Duke Company are as follows: Of 326 DEC Facilities walked-down, DEC has a total of 65 instances where DEC failed to have Facility Ratings consistent with its FRM. A total of 22 of the 65 were subject to a Facility Ratings deration, resulting in a deration percentage of 6.7% for DEC. The 22 Facilities subject to derations had derates ranging from 4.39% to 82.82%. The derations occurred at Facilities between voltages of 100 kV to 230 kV. DEC’s issues consisted of instances where Elements were missing from its Facility Ratings documentation; instances where the wrong equipment was utilized in the ratings calculations; and instances where DEC did not correctly define its Facilities in it Facility Ratings documentation at one substation. Of 96 DEF Facilities walked-down, DEF has a total of 26 instances (including the three instances that were initially self-reported) where DEF failed to have Facility Ratings consistent with its FRM. Of those 26 instances, four Facilities were subject to a Facility Ratings deration, resulting in a deration percentage of 4.2%. Three of the four Facilities subject to Facility Rating derations had derates of 7.8% at a 500 kV bus. The fourth Facility was subject to a 31.7% derate on a 230 kV transmission line. DEF’s issues were generally related to discrepancies between field ratings and Facility Ratings documentation as a result of major equipment changes or asset commissioning. Of 725 DECorp Facilities walked-down, DECorp has a total of 69 instances where DECorp failed to have Facility Ratings consistent with its FRM. Of the 69 Facilities, 61 Facilities were subject to a Facility Rating deration, resulting in a derate percentage of 8.4%. DECorp’s Facility derations range from 2.3% to 35.1% in voltage ranges from 138 kV to 345 kV. The largest derate at a 345 kV Facility was 13.8%. DECorp’s issues center around a design practice in its FRM since the effective date of the Standard Requirement. The design practice did not allow for bus work or CTs to be the most Limiting Element. Thus, when a design mistake was made and the bus work and/or CT was in fact the most Limiting Element, none of the internal controls downstream could have identified the issues. DEP has walked-down a total of 69 Facilities and has not identified any instances where a Facility Rating was not consistent with its FRM. The cause of this violation was rooted in the presence of vertical organizational silos, which created challenges to implementing Facility Ratings programs that were consistent and equally effective across the Duke Companies. The silos resulted primarily from the 2006 merger of Duke Energy and Cinergy in the Midwest footprint, now DECorp. Specifically, when the merger occurred, DECorp left a good portion of Cinergy’s Facility Ratings program in place, including an FRM that included the above-mentioned design practice. The combined FRM was different from the FRMs utilized by DEC, DEF, and DEP. In 2013, DECorp and DEC merged their FRMs and that design practice was removed from the newly combined FRM. However, DEF and DEP still had their own programs and FRMs. Around the same time, DECorp had already begun its efforts to correct the Facilities that were missing bus work and CTs. Those efforts were suspended prior to completion. Thus, although DECorp and DEC were using the same FRM, the two entities continued working in silos over the years. As a result of the silos, the Duke Companies had been working independently from one another, which resulted in a lack of uniformity and coordination over the years. This further contributed to a lack of awareness of the Facility Ratings program challenges that existed within the Duke Companies, including lack of or inadequate change management controls for equipment changes/replacements; inadequate controls in the asset commissioning process; and lack of documented procedures and controls to ensure that Equipment Ratings information and calculations used matched the corresponding ratings documentation. This violation began on June 18, 2007, when the Standard became enforceable and DECorp first failed to have Facility Ratings that were consistent with the FRM, and will end on June 27, 2022 once all walk-downs have been completed by Duke and all identified issues have been addressed. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). DEC, DEF, and DECorp’s failure to have Facility Ratings that were consistent with their respective FRMs could have caused equipment damage and/or unplanned outages. While the timeframe for the violation was multi-year, historical review found no exceedances, either pre or post contingent, of the corrected actual ratings using 15 minute flow data from November 2020 to November 2021. Additionally, the deration percentage for each (DEC, DEF, and DECorp) was less than 10%. Lastly, a large percentage of the Facility derations for each of the violating Duke Companies occurred on lower voltage (e.g., sub-230 kV) Facilities. No harm is known to have occurred. While DECorp has the highest number of ratings issues and derate percentage, approximately 75% of the DECorp walk-downs have been completed and the percentage of derates has been consistently lower than the walk-downs result data that was first reported in 2019. Also, during the 2019 walk-downs, DEF and DEC had significantly lower percentages of derates, and there have been no Facility Ratings issues reported by DEP as of November 2021. | To mitigate this violation, Duke has or will perform the following actions: 1) form region-specific teams to define walk-down process and timelines, and complete 100% field walk-downs of Bulk Electric System Transmission substations for all Duke Companies, reporting walk-down results to the Regions every 90 days until completion, including the percentage of Facilities with discrepancies between field conditions and the component/equipment listing in the FRD; 2) correct Facility discrepancies as identified (including derates, uprates, and missing elements), including coordination with neighboring entities as necessary, and utilizing the FRM and operational needs to determine necessary corrective actions (e.g., accept new rating, replace equipment, or temporary rating change); 3) identify and assign additional staff to support FRM related processes; 4) create and distribute lessons learned and conduct training to relevant personnel as necessary to communicate cause analysis findings and corrective actions; 5) develop and update processes, guidelines, and procedures to address any identified gaps for Duke Generation and Transmission, and develop a single Duke Transmission Enterprise approach to ensure accurate Facility Ratings; 6) develop and implement enhanced enterprise level internal controls to prevent future occurrence and detect discrepancies, including, checklists, administrative controls, independent reviews, team/peer reviews, work orders, an internal controls tracking sheet, a spot check procedure, and a NERC Compliance Internal Control Program; and 7) train affected personnel on updated FRM processes, procedures, and methods. Training to include initial training for new employees and contractors and ongoing (biannual) refresher training for employees and contractors in Transmission Asset Management Technical Support, as well training to Line and Substation Engineers concerning point of ownership between Line Engineering and Substation Engineering components. | The Regions acknowledge that Duke has continuously worked to dismantle silos within its business units over the past several years, including the creation of an overarching ICP with centralized oversight. Duke implemented enhanced oversight of its Operations and Planning (O&P) program by implementing an O&P Corporate Compliance group, which has the authority to conduct oversight activities such as reviews, internal audits, and observations to validate effective implementation of enterprise and business area procedures. While the Regions recognize and value Duke’s continuous commitment and resources expended in the creation and implementation of its overarching ICP, the issues that comprise this violation existed long before the ICP enhancements were implemented. Additionally, the Regions determined that the ICP continues to be hindered by the presence of vertical silos, which resulted in a lack of Facility Ratings program uniformity and coordination across the Duke Companies. As such, the Regions considered Duke’s ICP to be a neutral factor in the penalty determination. Effective oversight of the reliability of the BPS depends on robust and timely self-reporting by Registered Entities. While Duke submitted two Self-Reports reporting some of the instances that comprise this violation, the majority of the instances were identified as a result of the field walk-downs performed, at the request of the Regions, to determine the extent of condition. Notably, the instances identified in the initial Self-Report were identified during a routine internal compliance verification. As such, the Regions are awarding Duke some mitigating credit for self-reporting. The Regions considered DEF’s, DEC’s, DECorp’s, and DEP’s compliance history in determining the penalty. The Regions considered that Duke’s relevant compliance history did not serve to aggravate the penalty because although the prior instance involved similar conduct as the instant violation, mitigation activities for the prior instance would not have likely prevented the instant violation from occurring. Additionally, the prior violation involved one instance and was a minimal risk issue filed as a Compliance Exception. The Regions are awarding some mitigating credit for the level of cooperation demonstrated by Duke. Duke has been highly cooperative with the Regions during the investigation and enforcement processing of the violation by providing the Regions with timely, detailed, and organized evidence in response to Requests for Information. Duke fully cooperated in the Regions’ assessment of the violation and all associated mitigating activities, and openly shared information regarding relevant processes, procedures, internal controls, and organizational oversight of its compliance program. Duke staff and Executives have engaged with the Regions’ staff and Executives throughout the enforcement process by having open and transparent discussions regarding the facts and circumstances of the violation, progress on mitigation, and any potential noncompliance issues identified as a result of the mitigating activities. This is behavior that the Regions highly encourage. Additionally, when the Regions requested field walk-downs to determine the extent of condition, each Duke Company walked-down at least 50 Facilities, well above the minimum required. Further, while only DECorp was required to complete full walk-downs of all of its Facilities based on the initial walk-down findings, DEC, DEF, and DEP voluntarily committed to do the same for their Transmission stations and substation Facilities within the same aggressive timeline used by DECorp. This behavior demonstrates Duke’s level of cooperation with the Regions and overall commitment to reducing risks to the BPS. Duke agreed to settle the violation resolved by this Agreement, thereby avoiding a hearing on this matter. The Regions applied mitigating credit because it is important to promote prompt resolution of enforcement actions so that Duke’s focus is on mitigation and reducing risks to reliability. Under Coordinated Oversight, the penalty will be divided among the Regional Entities as follows: Duke shall pay $210,000 to SERC, and SERC shall divide that penalty amount in two parts based on the relative net energy for load (NEL) for each Region and shall distribute the NEL-based proportional allocation to ReliabilityFirst in the amount of $85,260.
2022-06-30 | NOC-2776 | Texas Reliability Entity (Texas RE) | Bryan Texas Utilities (BTU) | NCR04022 | TO | Settlement Agreement | Neither Admits nor Denies | $39,000 (for TRE2020023338 and TRE2020023339) | TRE2020023338 | FAC-009-1 | R2 | Moderate | Medium | Severe | Compliance Audit | 2020-04-30 | 2007-06-28 | 2021-10-28 | 2022-01-19 | 2022-02-03 | Texas RE determined BTU was noncompliant with FAC-009-1 R2. Specifically, BTU failed to provide accurate Facility Ratings data to its associated Reliability Coordinator (RC), the Electric Reliability Council of Texas, Inc. (ERCOT). After inconsistencies were identified in Facility Ratings data sampled during a Compliance Audit, BTU conducted an Extent of Condition (EOC) review, and a total of nine Facilities were identified with a Facility Rating that was inconsistent with the Rating reported to ERCOT. During the noncompliance, FAC-009-1 R2 was replaced by FAC-008-3 R8 and FAC-008-5 R8, which are both also applicable to the noncompliance. The root cause of this violation was an overreliance on stale field verifications, and a failure to adequately communicate with neighboring utilities regarding equipment Ratings for jointly owned Facilities. More specifically, BTU did not have a policy of checking and verifying Facility Ratings, including verification of conductor type, when the opportunity was available such as during additional construction and maintenance and when coordinating with neighboring utilities. This noncompliance began June 28, 2007, when BTU registered as a Transmission Owner, and ended October 28, 2021, when BTU recalculated all applicable Facility Ratings in accordance with its FRM and reported the correct Ratings to ERCOT. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A lack of accurate Facility Ratings and Equipment Ratings could result in overloading on equipment, potentially damaging the affected Facilities, and resulting in unanticipated outages. BTU is a municipally-owned electric utility that serves the citizens of Bryan, rural Brazos County, and portions of Burleson and Robertson Counties. BTU serves approximately 48,500 electric customers, has approximately 2,039 miles of distribution line, and 129 miles of Transmission line. BTU’s Transmission system represents approximately 0.5% of the ERCOT system peak load. Despite BTU’s small size and overall small potential impact to the BPS, this violation is aggravated by the length of time for which these instances of noncompliance occurred, and by the high percentage of Facilities affected. BTU had a total of nine of 29 Facilities (29%) with erroneous Ratings recorded with the RC, representing violations of FAC-009-1 R2. For five of these nine Facilities, BTU was unable to identify the date the erroneous Rating was provided to ERCOT. However, the risk was mitigated by the extent of the discrepancies between the reported and actual Rating. In particular, of these nine erroneous ratings, in only two instances the Rating reported to ERCOT was higher than the actual Rating. In the first of those instances, the discrepancy was 120 MVA (32%), and in the second, it was 31 MVA (14.4%). In the remaining seven instances of noncompliance, the Facility Rating reported to ERCOT was lower than the actual Rating by an average by -40.3 MVA (13.9%). No harm is known to have occurred. | To mitigate this violation, BTU has performed the following actions: 1) submitted revised information to ERCOT to correct the erroneous Facility Ratings in the ERCOT Network Operations Model; 2) conducted a full EOC review of all of BTU’s Transmission Facilities and associated elements; 3) revised its most limiting series element (MLSE) spreadsheet to present a single column for MLSE ratings to avoid confusion; 4) implemented Facility Ratings Checklists for Facility Rating submissions and/or changes to BTU’s MLSE spreadsheet; and 5) implemented a policy that field verifications will be performed during future construction, maintenance activities, and periodically in accordance with BTU’s Facility Rating process. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed BTU's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. BTU did not receive mitigating credit for self-reporting because the violation was discovered during a Compliance Audit. Texas RE considered BTU’s compliance history and determined there were no relevant instances of noncompliance.
2022-06-30 | NOC-2776 | Texas Reliability Entity (Texas RE) | Bryan Texas Utilities (BTU) | NCR04022 | TO | Settlement Agreement | Neither Admits nor Denies | $39,000 (for TRE2020023338 and TRE2020023339) | TRE2020023339 | FAC-009-1 | R1 | Moderate | Medium | Severe | Compliance Audit | 2020-04-30 | 2011-04-25 | 2021-10-28 | 2022-01-19 | 2022-02-03 | Texas RE determined BTU was noncompliant with FAC-009-1 R1. Specifically, BTU failed to calculate Facility Ratings for its solely and jointly owned Facilities in accordance with BTU’s Facility Ratings Methodology (FRM). After inconsistencies were identified regarding the Equipment Ratings provided with Facility Ratings data sampled during a Compliance Audit, BTU conducted an Extent of Condition (EOC) review, and a total of nine Facilities were identified with Facility Rating that were inconsistent with the FRM due to a misidentification of the most limiting series element (MLSE). During the noncompliance, FAC-009-1 R1 was replaced by FAC-008-3 R6 and FAC-008-5 R6, which are both also applicable to the noncompliance. The root cause of this violation was an overreliance on stale field verifications, and a failure to adequately communicate with neighboring utilities regarding equipment Ratings for jointly owned Facilities. More specifically, BTU did not have a policy of checking and verifying Facility Ratings, including verification of conductor type, when the opportunity was available such as during additional construction and maintenance and when coordinating with neighboring utilities. This noncompliance began on April 25, 2011, when BTU first incorrectly calculated the applicable Facility Ratings for its solely and jointly owned Facilities, and ended on October 28, 2021, when BTU recalculated and recorded all applicable Facility Ratings in accordance with its FRM. | This noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A lack of accurate Facility Ratings and Equipment Ratings could result in overloading on equipment, potentially damaging the affected Facilities, and resulting in unanticipated outages. BTU is a municipally-owned electric utility that serves the citizens of Bryan, rural Brazos County, and portions of Burleson and Robertson Counties. BTU serves approximately 48,500 electric customers, has approximately 2,039 miles of distribution line, and 129 miles of Transmission line. BTU’s Transmission system represents approximately 0.5% of the Electric Reliability Council of Texas, Inc. (ERCOT) system peak load. Despite BTU’s small size and overall small potential impact to the BPS, this violation is aggravated by the length of time for which these instances of noncompliance occurred, and by the high percentage of Facilities affected. BTU had a total of nine of 29 Facilities (29%) with erroneous Ratings recorded in BTU’s internal MLSE Spreadsheet, representing violations of R6. However, the risk was mitigated by the fact that the discrepant Facility Ratings were lower than the corrected Facility Ratings and that the Reliability Coordinator received the correct Facility Ratings for five out of the nine Facilities at issue. Specifically, in all nine of these instances, the Facility Rating recorded in BTU’s MLSE Spreadsheet was lower than the actual Facility Rating. The greatest deviation between the value in BTU’s MLSE Spreadsheet and the actual Facility Rating occurred in two instances that were each 247.6 MVA (50%), and the average deviation of all of the deviations was 137.7 MVA (34%). Despite the fact that BTU’s internal MLSE Spreadsheet contained erroneous Ratings for these nine Facilities, the correct rating was nevertheless reported to the Reliability Coordinator, ERCOT, for five of these nine Facilities. No harm is known to have occurred. | To mitigate this violation, BTU has performed the following actions: 1) modified its internal MLSE spreadsheet to identify the correct element and rating for each of the previously incorrect Facility Ratings; 2) conducted a full EOC review of all of BTU’s Transmission Facilities and associated elements; 3) revised its MLSE spreadsheet to present a single column for MLSE ratings to avoid confusion; 4) implemented Facility Ratings Checklists for Facility Ratings submissions, and/or changes to BTU’s MLSE spreadsheet; and 5) implemented a policy that field verifications will be performed during future construction, maintenance activities, and periodically in accordance with BTU’s Facility Rating process. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed BTU's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. BTU did not receive mitigating credit for self-reporting because the violation was discovered during a Compliance Audit. Texas RE considered BTU’s compliance history and determined there were no relevant instances of noncompliance.
2022-05-31 | NOC-2772 | SERC Reliability Corporation (SERC) | USACE - Savannah District (USACE-SAV) | NCR01361 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020861 and SERC2018020862) | SERC2018020861 | MOD-026-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-12-19 | 2018-07-01 | 2022-12-30 | 12/30/2022 (Expected Completion Date) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-SAV was in violation of MOD-026-1 R2. USACE-SAV did not provide its Transmission Planner (TP) with verified generator excitation control system or plant volt/var control function model in accordance with the NERC Implementation Plan. USACE-SAV owns 20 hydro units, which range from 57.5 MVA to 85 MVA, with capacity factors ranging from .08 to .29. The total nameplate value of all USACE-SAV generation is 1,450 MVA. The MOD-026-1 R2 Implementation Plan required 30% of USACE-SAV’s applicable nameplate generation, or 447 MVA, be compliant on July 1, 2018. USACE-SAV did not have sufficient documentation to show any compliance. This violation started on July 1, 2018, when USACE-SAV failed to meet the Implementation Plan of MOD-026-1 R2 and, will end on December 30, 2022, when USACE-SAV completes the excitation and turbine/governor control system model verification for the 20 generators and submits that data to its TP. The cause of this violation was ineffective resource management (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-SAV is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, USACE-SAV, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineers’ South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk posed by this noncompliance is that the TP would not have accurate information on the generator excitation control system or plant volt/var control function to use for its planning models to assess BPS reliability. USACE-SAV owns and manages three hydro-electric dams that consist of 20 hydroelectric units that range from 57.5 MVA to 85 MVA, with a total output of 1,450 MVA and a low average annual capacity factor of 22%. Therefore, a failure to verify generator excitation control system or plant volt/var control function models of units this size would have limited impact on the reliability of the BPS. No harm is known to have occurred. | To mitigate this violation, USACE-SAV has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. This reorganization has been completed, the dedicated compliance team established, and communicated to relevant staff; 2) implemented a secure central repository for electronic evidence and documentation. The requirement to store compliance evidence and/or documents within this repository was communicated to the compliance team members; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-SAV hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-SAV hydropower generators. | SERC considered USACE-SAV’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-SAV was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-SAV was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-SAV requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2772 | SERC Reliability Corporation (SERC) | USACE - Savannah District (USACE-SAV) | NCR01361 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020861 and SERC2018020862) | SERC2018020862 | MOD-027-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-12-19 | 2018-07-01 | 2022-12-30 | 12/30/2022 (Expected Completion Date) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-SAV was in violation of MOD-027-1 R2. USACE-SAV did not provide its Transmission Planner (TP) with verified turbine/governor and load control or active power/frequency control model in accordance with the NERC Implementation Plan. USACE-SAV owns 20 hydro units, which range from 57.5 MVA to 85 MVA, with capacity factors ranging from .08 to .29. The total nameplate value of all USACE-SAV generation is 1,450 MVA. The MOD-027-1 R2 Implementation Plan required 30% of USACE-SAV’s applicable nameplate generation, or 447 MVA, be compliant on July 1, 2018. USACE-SAV did not have sufficient documentation to show any compliance. This violation started on July 1, 2018, when USACE-SAV failed to meet the Implementation Plan of MOD-027-1 R2 and, will end on December 30, 2022, when USACE-SAV completes the turbine/governor control system model verification for the 20 generators and submits that data to its TP. The cause of this violation was ineffective resource management (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-SAV is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, the USACE-SAV, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineers’ South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This risk posed by this noncompliance is that the TP would not have accurate information on the turbine/governor and load control or active power/frequency control for its planning models to assess BPS reliability. USACE-SAV owns and manages three hydro-electric dams that consist of 20 hydroelectric units that range from 57.5 MVA to 85 MVA, with a total output of 1,450 MVA and a low average annual capacity factor of 22%. Therefore, a failure to verify the turbine/governor and load control or active power/frequency control of units this size would have limited impact on the reliability of the BPS. No harm is known to have occurred. | To mitigate this violation, USACE-SAV has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. This reorganization has been completed, the dedicated compliance team established, and communicated to relevant staff; 2) implemented a secure central repository for electronic evidence and documentation. The requirement to store compliance evidence and/or documents within this repository was communicated to the compliance team members; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-SAV hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-SAV hydropower generators. | SERC considered USACE-SAV’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-SAV was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-SAV was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-SAV requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2773 | SERC Reliability Corporation (SERC) | USACE - Mobile District (USACE-MOB) | NCR01359 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020181 and SERC2018020182) | SERC2018020181 | MOD-026-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-08-02 | 2018-07-01 | 2022-12-30 | 12/30/2022 (Expected Completion Date) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-MOB was in violation of MOD-026-1 R2. USACE-MOB failed to provide its Transmission Planner (TP) with verified generator excitation control system or plant volt/var control function model in accordance with the NERC Implementation Plan. The MOD-026-1 R2 Implementation Plan required USACE-MOB to provide its TP with generator excitation control system or plant volt/var control function model, including documentation and data model, for 30% of its applicable units, or 305 MVA, by July 1, 2018, or 50% of its applicable units, or 508 MVA, by July 1, 2020. USACE-MOB failed to meet either of the milestones and is scheduled to perform the verification of all of its applicable units by December 20, 2022. This violation started on July 1, 2018, when USACE-MOB failed to meet the 30% NERC Implementation Plan requirements, and will end on December 30, 2022, when USACE-MOB completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-MOB is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, USACE-MOB, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, USACE-MOB’s failure to provide its TP with verified model data for 30% of its applicable generation, or 305 MVA, or 50% of its applicable generation, or 508 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-MOB is a small facility and total affected generation for this noncompliance is fourteen units, totaling 1,017 MVA, with a low average capacity factor of 32%. USACE-MOB will meet the requirement to provide its verified model data of 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-MOB has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation; 3) perform the MOD-026-1 model verification testing; and 4) submit model verification data to Transmission Planner for the applicable USACE-MOB hydropower generators. | SERC considered USACE-MOB’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-MOB was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-MOB was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-MOB requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2773 | SERC Reliability Corporation (SERC) | USACE - Mobile District (USACE-MOB) | NCR01359 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2018020181 and SERC2018020182) | SERC2018020182 | MOD-027-1 | R2 | Minimal | Medium | Severe | Compliance Audit | 2018-08-02 | 2018-07-01 | 2022-12-30 | 12/30/2022 (Expected Completion Date) | TBD | During the Compliance Audit conducted by SERC, SERC determined that USACE-MOB was in violation of MOD-027-1 R2. USACE-MOB failed to provide its Transmission Planner (TP) with verified turbine/governor and load control or active power/frequency control model in accordance with the NERC Implementation Plan. The MOD-027-1 R2 Implementation Plan required USACE-MOB to provide its TP with turbine/governor and load control or active power/frequency control model, including documentation and data model, for 30% of its applicable units, or 305 MVA, by July 1, 2018, or 50% of its applicable units, or 508 MVA, by July 1, 2020. USACE-MOB failed to meet either of the milestones and is scheduled to perform the verification of all of its applicable units by December 30, 2022. This violation started on July 1, 2018, when USACE-MOB failed to meet the 30% NERC Implementation Plan requirements, and will end on December 30, 2022, when USACE-MOB completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-MOB is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, USACE-MOB, along with the U.S. Army Corps of Engineers’ South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, USACE-MOB’s failure to provide its TP with verified model data for 30% of its applicable generation, or 305 MVA, or 50% of its applicable generation, or 508 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-MOB is a small facility and total affected generation for this noncompliance is fourteen units, totaling 1,017 MVA, with a low average annual capacity factor of 32%. USACE-MOB will meet the requirement to provide its verified model data of 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-MOB has or will perform the following actions: 1) reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation; 3) perform the MOD-027-1 model verification testing; and 4) submit model verification data to Transmission Planner for the applicable USACE-MOB hydropower generators. | SERC considered USACE-MOB’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 31, 2021. However, USACE-MOB was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-MOB was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-MOB requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2774 | SERC Reliability Corporation (SERC) | USACE - Wilmington District (USACE-WILM) | NCR01364 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2020023113 and SERC2020023114) | SERC2020023113 | MOD-027-1 | R2 | Minimal | Medium | Severe | Self-Report | 2020-02-25 | 2018-07-01 | 2022-12-30 | 12/30/2022 (Expected Completion Date) | TBD | USACE-WILM notified SERC that it was in violation of MOD-027-1 R2. USACE-WILM failed to provide its Transmission Planner (TP) a verified turbine/governor and load control or active power/frequency control model in accordance with the NERC Implementation Plan. The MOD-027-1 R2 Implementation Plan required USACE-WILM to provide its TP with a verified turbine/governor and load control or active power/frequency control model, including documentation and data model, for 30% of its total applicable units, or 99 MVA, by July 1, 2018, or 50% of its applicable units, or 164 MVA, by July 1, 2020. USACE-WILM is scheduled to perform the verification of all its applicable units by December 30, 2022 and will meet the 100% requirement prior to the NERC Implementation Plan deadline of July 1, 2024. This violation started on July 1, 2018, when USACE-WILM failed to meet the 30% NERC Implementation Plan requirement, and will end on December 30, 2022, when USACE-WILM completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-WILM is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, the USACE-WILM, along with the U.S. Army Corps of Engineer’s South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). USACE-WILM’s failure to provide its TP verified model data for 30% of its applicable generation, or 99 MVA, or 50% of its applicable generation, or 164 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-WILM is a small hydropower facility and the total affected generation for this noncompliance is seven units totaling 327 MVA of applicable units with a low average annual capacity factor of 16%. USACE-WILM will meet the requirement to provide verified model data for 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-WILM has or will complete the following actions: 1) reorganized its technical manpower, to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation, which was communicated to the compliance team members on October 10, 2018; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-WILM hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-WILM hydropower generators. | SERC considered USACE-WILM’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 1, 2021. However, USACE-WILM was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-WILM was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-WILM requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2774 | SERC Reliability Corporation (SERC) | USACE - Wilmington District (USACE-WILM) | NCR01364 | GO | Settlement Agreement | Neither Admits nor Denies | No Penalty (for SERC2020023113 and SERC2020023114) | SERC2020023114 | MOD-026-1 | R2 | Minimal | Medium | Severe | Self-Report | 2020-02-25 | 2018-07-01 | 2022-12-30 | 12/30/2022 (Expected Completion Date) | TBD | USACE-WILM notified SERC that it was in violation of MOD-026-1 R2. USACE-WILM failed to provide, for each applicable unit, a verified generator excitation control system or plant volt/var control function model including documentation and data to its Transmission Planner (TP) in accordance with the NERC Implementation Plan. The MOD-026-1 R2 Implementation Plan required USACE-WILM to provide its TP with a verified generator excitation control system or plant volt/var control function model, for 30% of its total applicable units, or 99 MVA, by July 1, 2018, or 50% of its applicable units, or 164 MVA, by July 1, 2020. USACE-WILM is scheduled to perform the verification of all its applicable units by December 30, 2022 and will meet the 100% requirement prior to the NERC Implementation Plan deadline of July 1, 2024. This violation started on July 1, 2018, when USACE-WILM failed to meet the 30% NERC Implementation Plan requirement, and will end on December 30, 2022, when USACE-WILM completes the verification for 100% of its applicable units. The cause for this violation was management oversight (A4B2). Management failed to allocate sufficient manpower and resources dedicated to track and maintain NERC compliance. Each District of the U.S. Army Corps of Engineers, which USACE-WILM is a part of, had an individual responsible for maintaining NERC compliance. The individual was typically responsible for other tasks, along with NERC compliance, which caused noncompliances to occur depending on the individual’s workload. Going forward, to minimize the risk of noncompliance with current and future enforceable Compliance Standards and Requirements, the USACE-WILM, along with the U.S. Army Corps of Engineer’s South Atlantic Division (SAD), reorganized its technical manpower to establish a dedicated team to monitor and track NERC compliance. The U.S. Army Corps of Engineer’s South Atlantic Division’s compliance team assessed the overall status of compliance and/or non-compliance for each of its Districts with their applicable NERC Reliability Standards and discovered previously approved documents were not readily available for some of the districts and the documents were not being stored in a central location that was periodically backed up. Therefore, the U.S. Army Corps of Engineers implemented a secure central repository for electronic documentation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). USACE-WILM’s failure to provide its TP verified model data for 30% of its applicable generation, or 99 MVA, or 50% of its applicable generation, or 164 MVA, by the Implementation Plan dates could result in inaccurate system models. However, USACE-WILM is a small hydropower facility and the total affected generation for this noncompliance is seven units totaling 327 MVA of applicable units with a low average annual capacity factor of 16%. USACE-WILM will meet the requirement to provide verified model data for 100% of its units by December 30, 2022, which is prior to the NERC Implementation deadline of July 1, 2024. No harm is known to have occurred. | To mitigate this violation, USACE-WILM has or will complete the following actions: 1) reorganized its technical manpower, to establish a dedicated team to monitor and track NERC compliance; 2) implemented a secure central repository for electronic evidence and documentation, which was communicated to the compliance team members on October 10, 2018; 3) perform the MOD-026-1 and MOD-027-1 model verification testing for the applicable USACE-WILM hydropower generators; and 4) submit model verification data to Transmission Planner for the applicable USACE-WILM hydropower generators. | SERC considered USACE-WILM’s compliance history and determined that there were no relevant instances of noncompliance. SERC initially filed a Compliance Exception disposition to resolve this violation, with an initial mitigation completion date of December 1, 2021. However, USACE-WILM was unable to complete the mitigation plan within the required 12 months from filing the Compliance Exception because USACE-WILM was not successful in awarding a contract to complete the required model testing and validation. Therefore, USACE-WILM requested an extension of a mitigation completion date of December 30, 2022. As a result, SERC elevated this minimal risk violation to an SNOP settlement agreement.
2022-05-31 | NOC-2775 | Midwest Reliability Organization (MRO) | MidAmerican Energy Company (MEC or the Entity) | NCR00824 | TO | Settlement Agreement | Admits | 82000 | MRO2018020131 | FAC-009-1 | R1 | Moderate | Medium | Severe | Self-Report | 2018-06-18 | 2007-06-18 | 2020-02-04 | 2021-03-30 | 2021-04-30 | On June 18, 2018, the Entity submitted a Self-Report stating that, as a Transmission Owner, it was noncompliant with FAC-009-1 R1. The Entity reported that it had ratings documentation errors for components of its Facilities that constituted a noncompliance with FAC-009-1 R1, as the Facility Ratings (FR) were not consistent with its associated Facility Ratings Methodology (FRM). The Entity identified 21 FRs errors during an internal review. The Entity subsequently performed an Extent of Condition (EOC), discovering an additional 68 FRs errors, for a total of 89 FRs errors. Those errors affected the most limiting element of a Facility, causing the overall FRs to be either higher or lower than the rating of the most limiting element. The cause of the noncompliance was the Entity’s inadequate process for reviewing ratings and facility components. For its affected jumper components, the Entity failed to consider industry standards for substation bus design (IEEE Std. 605-2008) and for reducing equipment loss of life (IEEE Std. C57.19) as required by its FRM. Additionally, for its other affected Facility components, the Entity failed to update the primary drawings used for FRs after changes to the equipment were made in the field. The noncompliance began on June 18, 2007, the date the standard became enforceable, and ended on February 4, 2020, when the Entity corrected all of the component and FRs. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Operating a Facility at a rating that is above the rating of the most limiting element could result in damage to the limiting element and possible failure, leading to an outage of the Facility. Upon review of the EOC and other information provided by the Entity, MRO determined the risk is moderate. The Entity identified 89 transmission lines with Facility component rating errors that resulted in a FR change. Of the 89 Facilities, 62 had erroneous FRs that were higher than the actual rating of the most limiting element, resulting in a FR decrease when the error was corrected. Six of the 62 Facilities with ratings decreases were 345-kV Facilities. The most significant of these six was a Facility with a 5% summer normal and 20% winter normal rating decrease. Additionally, the duration of the issues was over 12 years. However, MRO determined that the issue did not pose a serious or substantial risk to the BPS. Of the six years of historical power flows and four years of temperature data (for dynamic ratings) that were reviewed, none of the flows exceeded any of the 89 adjusted FRs, limiting the actual risk posed to the BES. Also, 55 of the 62 FR decreases were caused by jumper component ratings issues. The jumper ratings used by the Entity allowed for operation up to 100 degrees Celsius and were consistent with the manufacturer documentation for the conductor. However, the Entity’s FRM required consideration of industry standards for substation bus design (IEEE Std. 605-2008) and for reducing equipment loss of life (IEEE Std. C57.19). The consideration of those two industry standards resulted in a reduction of the operating temperature limit to 90 degrees Celsius. The risk associated with these 55 ratings decreases is limited as the jumper conductor ratings were valid per manufacturer specifications. The jumper issue was the cause of three of the six 345-kV facility ratings decreases. Further, the 27 FR increases did not pose any risk of overloading the Facilities as they resulted in overly conservative operation of the Facilities. No harm is known to have occurred. | To mitigate this violation, the Entity: 1) adjusted all FRs changes for BES facilities with its Control Center and Reliability Coordinator; 2) enhanced substation engineering quality assurance review checklists were developed and complete; 3) trained personnel on the enhanced quality assurance review checklist; 4) completed historical documentation reviews for all remaining BES Transmissions Facilities; 5) completed nameplate reviews for all 161kV and 345kV substations; 6) completed pre-commission checklists to identify and actively communicate design changes during construction; and 7) instituted annual field reviews and completed reviews for 2018 and 2019. MRO has verified the completion of all mitigation activity. | MRO considered the Entity’s compliance history and determined that there were no relevant instances of noncompliance. MRO provided mitigating credit for cooperation, self-reporting, admission, settlement, and the internal compliance program.
2022-04-28 | NOC-2770 | Texas Reliability Entity, Inc. (Texas RE) | American Electric Power Service Corp as agent for AEP Texas Inc. and Public Service Company of Oklahoma (AEPSC) | NCR04006 | TOP | Settlement Agreement | Neither Admits nor Denies | 0 | TRE2019021504 | TOP-001-3 | R8 | Moderate | High | Severe | Compliance Audit | 2019-05-09 | 2018-03-20 | 2018-03-20 | 2020-11-17 | 2021-01-15 | During a compliance audit, Texas RE initially determined AEPSC was noncompliant with TOP-001-3 R1. However, based on the description of the issues provided, Texas RE subsequently determined that AEPSC was noncompliant with TOP-001-3 R8. In particular, on March 20, 2018, at 12:20 PM, AEPSC identified a consistent, non-converged solution in its Real-Time Contingency Analysis (RTCA). AEPSC did not communicate this information to its Reliability Coordinator (RC) in violation of TOP-001-3 R8, which requires that each Transmission Operator (TOP) shall inform its RC of its actual or expected operations that result in, or could result in, an Emergency. Prior to March 20, 2018, several transmission lines were out of service for approved construction and maintenance activities in the Del Rio, San Angelo, and Mesa Verde area. An additional forced outage on another transmission line resulted in only two 138 kV lines serving the area on March 20, 2018. Beginning at 10:58, the RC’s required RTCA indicated several thermal limit exceedances. As the available wind generation in the area declined, the RC was unable to automatically resolve the identified post-contingency thermal exceedances through a generation solution. Over the next few hours, AEPSC, the RC, and a neighboring TOP continuously coordinated to bring transmission facilities back into service to address the issue. Specifically, these ongoing communications occurred at 11:35, 11:46, 11:49, 12:11, 12:26, 14:08, and 14:24. In addition to these actions, AEPSC and its RC communicated regarding the development of a post-contingency load shed Transmission Outage Action Plan (TOAP) during the 11:46 call. While these communications were ongoing, at 10:29 and 14:29, AEPSC also placed a number of capacitor banks into service to bring up voltages in the area. Under the Coordinated Function Registration (CFR) agreement between AEPSC and its RC, the RC is the sole entity responsible for performing Real-time Assessments. Although the RC’s State Estimator and RTCA applications showed potential issues in the area, they did not specifically indicate post-contingency voltage collapse. While not required to perform periodic RTCAs, AEPSC’s process is to perform an RTCA for its TOP Area as an additional check on its system. As AEPSC worked with its RC and neighboring TOP to address transmission issues, AEPSC’s optional RTCA began to indicate a consistent, non-converged solution at 12:20. During its various, on-going communications regarding the issue, however, AEPSC did not specifically communicate complete information regarding the actual operational status of its system to its RC derived from its local RTCA information. At 14:33, a fault occurred due to ionized smoke from a nearby grass fire that resulted in a local voltage collapse and the loss of approximately 140 MW of load. The root cause of this noncompliance was inadequate processes and training regarding the need to communicate non-converged RTCA solutions to AEPSC’s RC. Specifically, although AEPSC had established communication protocols for communicating actual operational information regarding its system, such as RTCA results, it lacked specific, detailed steps for operators to track and communicate unsolved RTCA contingencies to its RC. This noncompliance started on March 20, 2018 at 12:20, when AEPSC first identified and then failed to communicate its optional RTCA’s non-converged RTCA solution to its RC, and ended on March 20, 2018 at 14:33, when a fault occurred resulting in a local voltage collapse. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. AEPSC failed to communicate the existence of the non-converged RTCA solution to its RC, depriving the RC of complete information about the actual operations of AEPSC’s system. However, AEPSC and its RC were in continuous communication throughout the event and taking actions to address post-contingency thermal exceedances in the area. Specifically, the RC and AEPSC were communicating to place transmission facilities back into service to alleviate identified post-contingency thermal exceedances in the area. In addition, AEPSC was in communication with its RC regarding contingency overload issues and had taken action to address them by placing a number of capacitor banks in service to increase system voltages in the area. Finally, the loss of load was caused by a combination of approved transmission outages in the area, a forced outage on an additional transmission facility, and a fault resulting from ionized smoke from a nearby grass fire. Throughout the issue, AEPSC, its RC, and neighboring TOP repeatedly communicated to attempt to address the specific capacity issues on the area’s transmission system. Conversely, AEPSC’s failure to communicate the specific results of its optional RTCA to its RC did not cause the event in question. | To mitigate this violation, AEPSC has: 1) Updated its processes to require that every unsolved contingency in the state estimator be logged in the Daily Operating Log (DOL), and created a standardized text template in the DOL to outline specific actions to be taken for RTCA unsolved contingencies in regards to notifications to the RC and time requirements; 2) Provided additional guidance to its reliability personnel during a staff meeting; 3) Provided on the job training task verifications for its reliability operators, including the assessment methodology for Real-time operations and notifications to RCs. The applicable training must be completed before an operator can perform System Control Center (SCC) functions independently; and 4) Conducted an extent of condition review of communication protocols notifications and actions taken with its RC for instances of invalid base case, unsolved contingency, or non-convergence with the RTCA tool; this extent of condition review did not detect any additional instances of noncompliance. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed AEPSC’s internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered AEPSC’s compliance history and determined there were no relevant instances of noncompliance. In addition to the moderate risk of the violation, Texas RE determined that although this violation did not cause a loss of load, the issue occurred during a load loss event and therefore it was inappropriate to process this violation through a streamlined disposition method. Texas RE further concluded, however, that a zero-dollar penalty is appropriate because AEPSC’s failure to communicate the results of its optional RTCA did not cause the loss of load event. In addition, AEPSC is not obligated to run an RTCA, and AEPSC’s decision to run an RTCA as an additional check enhances reliability. Because this violation stems from AEPSC’s failure to communicate complete information regarding its actual operations derived from its optional RTCA, AEPSC would not have a violation if it had elected not to run its optional RTCA altogether. Texas RE also considered the fact that AEPSC elected to address this violation by further enhancing its internal RTCA procedures, including communication processes with its RC, in lieu of terminating such activities in response to this issue.
2022-02-28 | NOC-2755 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | TOP | Settlement Agreement | Does Not Contest | No penalty (WECC2020024012, WECC2020024013, and WECC2020024014) | WECC2020024012 | TOP-001-4 | R1 | Moderate | High | Severe | Self-Report | 2020-10-01 | 2020-06-03 | 2020-06-03 | 2021-05-12 | 2021-05-12 | On October 1, 2020, WACM submitted a Self-Report notifying WECC as the Lead Regional Entity under an existing multi-region registered entity coordinated oversight agreement with MRO as the Affected Regional Entity, that as a Transmission Operator (TOP), it was in violation with TOP-001-4 R1. On June 3, 2020, at 2:02 AM a phase to ground fault occurred on a 115kV transmission line, that tripped a breaker, which resulted in the loss of that breaker and the open ended terminal of a multi-terminal 115kV transmission line. The breaker attempted to reclose automatically at 2:02 AM, but it tripped again. A SCADA alarm was generated and documented the trip and attempted reclosing of the breaker. However, the night shift System Operator (SO) was distracted did not recognize the visual and audible alarms for over two hours. At 4:17 AM, the SO attempted to close the breaker via SCADA control, but was unsuccessful. Maintenance was called to investigate the cause and a broken jumper was found approximately three miles from the terminal of the 115kV transmission line where the breaker tripped. The night shift SO completed the verbal shift change with the two incoming morning shift SOs. However, an internal interruption report and transmission log entry was not completed during the night shift SO’s shift. At 7:53 AM, WACM sent its Reliability Coordinator (RC) and affected TOP a notification of the event and the status of the unavailable Bulk Electric System (BES) equipment by sending a Clearance Switching Request Form and WACM initiated the process of switching to electrically isolate the faulted equipment. WACM completed the repairs, and the clearance was released at 3:08 PM. Removal switching was also completed, and the equipment was returned to service at 3:30 PM on June 3, 2020. During the thirteen hour and 28 minute outage of the 115kV transmission line, there was no loss of the potential 35 MW of load or less, depending on loading conditions during the event; nor were there any interruption of customer service. By not recognizing the SCADA alarms in a timely manner, the night shift SO did not act to maintain the reliability of its TOP via its own actions, as required by TOP-001-4 R1. The TOP-001-4 R1 violation began on June 3, 2020, at 2:33 AM, when the night shift SO should have responded to the SCADA alarms and ended on June 3, 2020, at 4:17 AM, when night shift SO took action by attempting to close the breaker via SCADA control, for a total of one hour and 44 minutes. The root cause of the violations was attributed to lack of situational awareness in that the situation was not being properly managed by the night shift SO. The SO thought that since the tripping of the breaker didn’t result in any customer outages, the notifications to the RC and affected TOP were not required to be sent, nor did the SO send the forced outage notification to its RC. | These violations posed a moderate risk in aggregate and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In these instances, WACM failed to act to maintain the reliability of its TOP Area via its own actions or by issuing Operating Instructions, for one hour and 44 minutes, as required by TOP-001-4 R1; inform its RC and one impacted TOP of its actual operations that could result in an Emergency, for five hours and 20 minutes, as required by TOP-001-4 R8; and to perform the 30 minute notification specified in its RC’s outage coordination process, for five hours and 20 minutes, as required by IRO-017-1 R2. The 115kV transmission line associated with the thirteen hour and 28-minute forced outage was open-ended so the line through flow was diverted to parallel paths and the failure of one breaker could have de-energized two of the adjacent TOP’s substations. The failures described herein resulted in the RC and one affected TOP not being aware of the forced outage. Such failures could have resulted in the loss of up to 35 MW of load, based on the transformers that could have been affected by the outage. The failures could also have resulted in the RC and affected TOP performing inaccurate Operating Planning Analysis if either used an off-line power flow model or the outage components were not modeled in an on-line power flow tool, which could have delayed maintenance. However, as compensation, WACM’s SO shift turnover resulted in the next shift SO taking steps to resolve the issue. The issue was isolated to the action of the one night shift SO. In Real-time the on-line power flow tools would have identified actual and potential line exceedances, load loss and generation loss, based on the current status of the transmission system. As well, the open breaker would not have caused any additional loss of load compared to the loss of the line. An on-line power flow study would have indicated a distribution factor higher than normal for loss of parallel lines due to no flow-through of this line. Based on the line rating of 109 MVA, it is unlikely it would have a significant distribution factor compared to the parallel 230kV lines. In addition, no load was lost as a result of this failure or event. | To mitigate this violation, WACM has performed the following actions: 1) attempted to restore the transmission line; 2) called field maintenance personnel to investigate the cause of the line operation; 3) restored the 115 kV transmission line to service; 4) reviewed and updated the applicable internal procedures including: 115kV Line Restoration Guide; Emergency Line Restoration Standard Operating Procedure (SOP); Event Reporting Plan; WACM Desk Procedures and System Operator Shift Change Procedure; 5) ensured SOs reviewed the updated procedures; and 6) reviewed the event and discussed lessons learned at SO meetings. | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. WACM is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation.
2022-02-28 | NOC-2755 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | TOP | Settlement Agreement | Does Not Contest | No penalty (WECC2020024012, WECC2020024013, and WECC2020024014) | WECC2020024013 | TOP-001-4 | R8 | Moderate | High | Severe | Self-Report | 2020-10-01 | 2020-06-03 | 2020-06-03 | 2021-05-12 | 2021-05-12 | On October 1, 2020, WACM submitted a Self-Report notifying WECC as the Lead Regional Entity under an existing multi-region registered entity coordinated oversight agreement with MRO as the Affected Regional Entity, that as a Transmission Operator (TOP), it was in violation with TOP-001-4 R8. On June 3, 2020, at 2:02 AM a phase to ground fault occurred on a 115kV transmission line, that tripped a breaker, which resulted in the loss of that breaker and the open ended terminal of a multi-terminal 115kV transmission line. The breaker attempted to reclose automatically at 2:02 AM, but it tripped again. A SCADA alarm was generated and documented the trip and attempted reclosing of the breaker. However, the night shift System Operator (SO) was distracted did not recognize the visual and audible alarms for over two hours. At 4:17 AM, the SO attempted to close the breaker via SCADA control, but was unsuccessful. Maintenance was called to investigate the cause and a broken jumper was found approximately three miles from the terminal of the 115kV transmission line where the breaker tripped. The night shift SO completed the verbal shift change with the two incoming morning shift SOs. However, an internal interruption report and transmission log entry was not completed during the night shift SO’s shift. At 7:53 AM, WACM sent its Reliability Coordinator (RC) and affected TOP a notification of the event and the status of the unavailable Bulk Electric System (BES) equipment by sending a Clearance Switching Request Form and WACM initiated the process of switching to electrically isolate the faulted equipment. WACM completed the repairs, and the clearance was released at 3:08 PM. Removal switching was also completed, and the equipment was returned to service at 3:30 PM on June 3, 2020. During the thirteen hour and 28 minute outage of the 115kV transmission line, there was no loss of the potential 35 MW of load or less, depending on loading conditions during the event; nor were there any interruption of customer service. The night shift SO did not inform the RC and impacted TOP of its actual or expected operations that could have resulted in an Emergency, as required by TOP-001-4 R8. The TOP-001-4 R8 violation began on June 3, 2020 at 2:33 AM, when the night shift SO should have notified its RC and affected TOP of an abnormal system condition and ended at 7:53 AM when the morning shift SO notified the RC and affected TOP of the abnormal system condition, for a total of five hours and 20 minutes. The root cause of the violations was attributed to lack of situational awareness in that the situation was not being properly managed by the night shift SO. The SO thought that since the tripping of the breaker didn’t result in any customer outages, the notifications to the RC and affected TOP were not required to be sent, nor did the SO send the forced outage notification to its RC. | These violations posed a moderate risk in aggregate and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In these instances, WACM failed to: act to maintain the reliability of its TOP Area via its own actions or by issuing Operating Instructions, for one hour and 44 minutes, as required by TOP-001-4 R1; inform its RC and one impacted TOP of its actual operations that could result in an Emergency, for five hours and 20 minutes, as required by TOP-001-4 R8; and to perform the 30 minute notification specified in its RC’s outage coordination process, for five hours and 20 minutes, as required by IRO-017-1 R2. The 115kV transmission line associated with the thirteen hour and 28-minute forced outage was open-ended so the line through flow was diverted to parallel paths and the failure of one breaker could have de-energized two of the adjacent TOP’s substations. The failures described herein resulted in the RC and one affected TOP not being aware of the forced outage. Such failures could have resulted in the loss of up to 35 MW of load, based on the transformers that could have been affected by the outage. The failures could also have resulted in the RC and affected TOP performing inaccurate Operating Planning Analysis if either used an off-line power flow model or the outage components were not modeled in an on-line power flow tool, which could have delayed maintenance. However, as compensation, WACM’s SO shift turnover resulted in the next shift SO taking steps to resolve the issue. The issue was isolated to the action of the one night shift SO. In Real-time the on-line power flow tools would have identified actual and potential line exceedances, load loss and generation loss, based on the current status of the transmission system. As well, the open breaker would not have caused any additional loss of load compared to the loss of the line. An on-line power flow study would have indicated a distribution factor higher than normal for loss of parallel lines due to no flow-through of this line. Based on the line rating of 109 MVA, it is unlikely it would have a significant distribution factor compared to the parallel 230kV lines. In addition, no load was lost as a result of this failure or event. | To mitigate this violation, WACM has performed the following actions: 1) informed the RC and known impacted TOP of the forced outage; 2) provided an informal training to remind system operators of the need to make timely notifications to the RC and any potentially affected TOP and Balancing Authority (BA) within 30 minutes or as soon as possible; 3) designed and delivered a compliance related training activity for SOs that identified the required reporting to the RC; 4) reviewed and updated the applicable internal procedures including: 115kV Line Restoration Guide; Emergency Line Restoration SOP; Event Reporting Plan; WACM Desk Procedures and System Operator Shift Change Procedure; 5) ensured SOs reviewed the updated procedures; and 6) reviewed the event and discussed lessons learned at SO meetings. | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. WACM is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation.
2022-02-28 | NOC-2755 | Western Electricity Coordinating Council (WECC) | Western Area Power Administration - Rocky Mountain Region (WACM) | NCR05464 | TOP | Settlement Agreement | Does Not Contest | No penalty (WECC2020024012, WECC2020024013, and WECC2020024014) | WECC2020024014 | IRO-017-1 | R2 | Moderate | Medium | Severe | Self-Report | 2020-10-01 | 2020-06-03 | 2020-06-03 | 2021-05-12 | 2021-05-12 | On October 1, 2020, WACM submitted a Self-Report notifying WECC as the Lead Regional Entity under an existing multi-region registered entity coordinated oversight agreement with MRO as the Affected Regional Entity, that as a Transmission Operator (TOP), it was in violation with IRO-017-1 R2 . On June 3, 2020, at 2:02 AM a phase to ground fault occurred on a 115kV transmission line, that tripped a breaker, which resulted in the loss of that breaker and the open ended terminal of a multi-terminal 115kV transmission line. The breaker attempted to reclose automatically at 2:02 AM, but it tripped again. A SCADA alarm was generated and documented the trip and attempted reclosing of the breaker. However, the night shift System Operator (SO) was distracted did not recognize the visual and audible alarms for over two hours. At 4:17 AM, the SO attempted to close the breaker via SCADA control, but was unsuccessful. Maintenance was called to investigate the cause and a broken jumper was found approximately three miles from the terminal of the 115kV transmission line where the breaker tripped. The night shift SO completed the verbal shift change with the two incoming morning shift SOs. However, an internal interruption report and transmission log entry was not completed during the night shift SO’s shift. At 7:53 AM, WACM sent its Reliability Coordinator (RC) and affected TOP a notification of the event and the status of the unavailable Bulk Electric System (BES) equipment by sending a Clearance Switching Request Form and WACM initiated the process of switching to electrically isolate the faulted equipment. WACM completed the repairs, and the clearance was released at 3:08 PM. Removal switching was also completed, and the equipment was returned to service at 3:30 PM on June 3, 2020. During the thirteen hour and 28 minute outage of the 115kV transmission line, there was no loss of the potential 35 MW of load or less, depending on loading conditions during the event; nor were there any interruption of customer service. The night shift SO did not perform the 30-minute forced outage notification specified in its RC’s Outage Coordination Methodology, as required by IRO-017-1 R2. The IRO-017-1 R2 violation began on June 3, 2020 at 2:33 AM when the SO was required to submit a forced outage notification to its RC and ended on June 3, 2020 at 7:53 AM when the morning shift SO submitted the forced outage notification to the RC, for a total of five hours and 20 minutes. The root cause of the violations was attributed to lack of situational awareness in that the situation was not being properly managed by the night shift SO. The SO thought that since the tripping of the breaker didn’t result in any customer outages, the notifications to the RC and affected TOP were not required to be sent, nor did the SO send the forced outage notification to its RC. | These violations posed a moderate risk in aggregate and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In these instances, WACM failed to: act to maintain the reliability of its TOP Area via its own actions or by issuing Operating Instructions, for one hour and 44 minutes, as required by TOP-001-4 R1; inform its RC and one impacted TOP of its actual operations that could result in an Emergency, for five hours and 20 minutes, as required by TOP-001-4 R8; and to perform the 30 minute notification specified in its RC’s outage coordination process, for five hours and 20 minutes, as required by IRO-017-1 R2. The 115kV transmission line associated with the thirteen hour and 28-minute forced outage was open-ended so the line through flow was diverted to parallel paths and the failure of one breaker could have de-energized two of the adjacent TOP’s substations. The failures described herein resulted in the RC and one affected TOP not being aware of the forced outage. Such failures could have resulted in the loss of up to 35 MW of load, based on the transformers that could have been affected by the outage. The failures could also have resulted in the RC and affected TOP performing inaccurate Operating Planning Analysis if either used an off-line power flow model or the outage components were not modeled in an on-line power flow tool, which could have delayed maintenance. However, as compensation, WACM’s SO shift turnover resulted in the next shift SO taking steps to resolve the issue. The issue was isolated to the action of the one night shift SO. In Real-time the on-line power flow tools would have identified actual and potential line exceedances, load loss and generation loss, based on the current status of the transmission system. As well, the open breaker would not have caused any additional loss of load compared to the loss of the line. An on-line power flow study would have indicated a distribution factor higher than normal for loss of parallel lines due to no flow-through of this line. Based on the line rating of 109 MVA, it is unlikely it would have a significant distribution factor compared to the parallel 230kV lines. In addition, no load was lost as a result of this failure or event. | To mitigate this violation, WACM has performed the following actions: 1) submitted a forced outage notification tool to the RC; 2) provided an informal training to remind system operators of the need to make timely notifications to the RC and any potentially affected TOP and BA within 30 minutes or as soon as possible; 3) designed and delivered a compliance related training activity for SOs that identified the required reporting to the RC; 4) designed and delivered a compliance related training activity for SOs relating to the RC's Outage Coordination Methodology and submission requirements; 5) reviewed and updated the applicable internal procedures including: 115kV Line Restoration Guide; Emergency Line Restoration SOP; Event Reporting Plan; WACM Desk Procedures and System Operator Shift Change Procedure; 6) ensured SOs reviewed the updated procedures; and 7) reviewed the event and discussed lessons learned at SO meetings. | WECC reviewed WACM's internal compliance program (ICP) and considered it to be a neutral factor in the disposition determination. WECC considered WACM's compliance history and determined there were no relevant instances of noncompliance. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. WACM is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation.
2022-02-28 | NOC-2763 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | TOP | Settlement Agreement | Admits | 132000 | WECC2019021942 | TOP-001-4 | R13 | Moderate | High | Severe | Self-Report | 2019-07-29 | 2019-04-17 | 2019-04-17 | 2019-08-31 | 2020-02-04 | AZPS notified WECC that it was noncompliant with TOP-001-4 R13. On April 16, 2019, AZPS replaced a pair of non-CIP Energy Management System (EMS) frame firewalls as part of a planned outage change at the primary Control Center (PCC). Due to configuration issues, and uncoordinated troubleshooting efforts, on April 17, 2019, at 7:38 PM, the EMS lost visibility to remote thermal unit (RTU) and Inter-Control Center Communications Protocol (ICCP) data between AZPS and its Reliability Coordinator (RC) and neighboring entities. The data lapse impacted the performance of the Real-time Contingency Analysis (RTCA) tool which stopped solving due to the loss of the RTU data. The RTCA is an aspect of AZPS’s Real Time Assessment (RTA), and AZPS System Operators (SOs) and RC lost the ability to perform a manual RTA in accordance with its procedures. Thus, AZPS was unable to perform a Real-time assessment (RTA) which required an examination of existing and expected system conditions, conducted by collecting and reviewing immediately available data. In addition, AZPS notified its neighboring entities of the condition and specifically confirmed the loss of the ICCP data with its RC and other neighboring entities. AZPS’s Balancing Authority (BA) function notified its generation units to change to local control and maintain their current output. Since the SOs did not have visibility of the system including RTCA, the PCC monitored the system in Real-time via field personnel and managed the BA responsibilities through manual checkout every 15 minutes along with adjacent BAs. AZPS activated its CIP-009-6 Recovery Plan and identified lessons learned and updated the Recovery Plan to include a peer check. AZPS completed the required steps for CIP-009-6 R2 and R3, thus CIP-009-6 R1-R3 were not at issue. AZPS used a CIP head end firewall as an attempt to troubleshoot during the instant violation, but the failover did not require Change Management protocols. Therefore, WECC determined that AZPS did not have any additional instances of potential noncompliance with CIP-009-6 R1-R3 nor CIP-010-2 R1 associated with the instant violation. At 8:21 PM, AZPS restored connectivity between the router and the new EMS frame firewalls. At 9:44 PM, the EMS regained visibility and the RTCA began solving with the return of the RTU data. At 10:30 PM, the ICCP services were restored for EMS, improving the functionality of the RTCA solution. The EMS outage began at 7:38 PM and ended at 9:44 PM for a total of two hours and six minutes. The ICCP outage began at 7:38 PM and ended at 10:29 PM for a total of two hours and 51 minutes. The RTCA did not solve during the EMS outage of 2 hours and six minutes and the RTCA results were not verified during the ICCP outage of 2 hours and 51 minutes. The root cause of the violation was attributed to a lack of coordinated efforts in AZPS’s incident response when it did not follow established decision trees and its incident management procedure, which resulted in an EMS outage, ICCP outage and RTCA not solving. The violation began on April 17, 2019 at 8:09 PM, when AZPS did not ensure that an RTA was performed through its RTCA, and ended on April 17, 2019 at 11:35 PM, when AZPS was able to perform an RTA, for a total of three hours and 26 minutes (206 minutes over the 30-minute requirement). | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, AZPS failed to ensure that an RTA was performed at least once every 30 minutes for a total of 206 minutes, as required by TOP-001-4 R13. AZPS’s primary Control Center and Real-time monitoring capabilities via SCADA were impacted by the issue. AZPS had peak demand greater than 7,000 MW, and nearly 3,000 miles of BES transmission lines. The data lapse failure resulted in AZPS losing its EMS visibility to the RTU, ICCP data and RTCA, which prevented the SOs from performing a manual RTA nor could the RC perform an RTA for AZPS. Further, the failure could have resulted in the unintended loss of BPS elements following a contingency. Additionally, during the outage, AZPS was also unable to fully perform BA functions for its stakeholders. However, as compensation, AZPS notified its neighboring entities of the condition and specifically confirmed the loss of the ICCP data with its RC and other neighboring entities. AZPS’s Balancing Authority (BA) function notified its generation units to change to local control and maintain their current output. Since the SOs did not have visibility of the system including RTCA, the PCC monitored the system in Real-time via field personnel and managed the BA responsibilities through manual checkout every 15 minutes along with adjacent BAs. | To mitigate this violation, AZPS has performed the following actions: 1) restored its data capabilities and ensured AZPS’ ability to perform a successful RTA; 2) held a Stand Down on the IT Computer Event Response Plan and the new IT End User communication plan to reinforce staff expectations which included the implementation of a Standing Order that all infrastructure changes to "Mission / Business / Safety critical systems must have change command;" 3) conducted formal cross-training between all parties involved in supporting the EMS application; 4) created an asset change management process to include: i. verify and document for an in-service device, its current function and configuration; ii. map the existing configuration for the in-service device with the replacing device iii. develop and/or update applicable System Test Plan and Test cases to meet the new device requirements and exercise of intended functionality iv. identify the monitoring and alerting functionality for the new device v. quality assurance process for all key tasks associated with this process and procedure(s) 5) moved outdated host files out of the primary directory; and 6) developed a procedure for when host files are to be pushed, which requires: i. a peer check be performed within the Real-Time System Support team ii. a peer check be performed with the EMS Duty Engineer. iii. once the push is complete, the RTSS validates push is successful iv. EMS Duty Engineer validates push is successful. | WECC reviewed AZPS's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination because it was effective in detecting the violation. WECC considered AZPS's compliance history and determined there were no relevant instances of noncompliance.
2021-12-30 | NOC-2749 | ReliabilityFirst Corporation (RF) | ITC Transmission (ITCT) | NCR00803 | TO | Settlement Agreement | Admits | $20,000 (for RFC2019022365 and RFC2019022362) | RFC2019022365 | PRC-005-6 | R3 | Moderate | High | Severe | Self-Report | 2019-10-04 | 2018-07-02 | 2021-12-03 | 2021-12-03 | TBD | On October 4, 2019, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-005-6 R3. This violation relates to the entity’s acquisition of the Dearborn Industrial Generation (DIG) site Protection System assets. On July 2, 2018, the entity acquired the six substations at issue from Ford, Cleveland-Cliffs, and DIG. The Assets include 230 kV and 120 kV Protection Systems that also interconnect with 844 MW of generation. After reviewing the Protection System maintenance and testing data provided by the prior owners of the Assets, the entity concluded that there were 29 Protection Systems that were not compliant with PRC-005-6 R3 and required mitigation. More specifically, the entity concluded that the prior owners did not perform relay scheme maintenance for 44 relay schemes. The entity has now performed all of the overdue relay scheme maintenance. The process to remediate the PRC-005-6 R3 violation took an extended amount of time because it is difficult to get outages for the industrial customers approved to perform the overdue maintenance. The root cause of this violation is that the prior owners did not perform maintenance on any of the aforementioned relay schemes and their components. This violation involves the management practice of external independencies. The violation began on July 2, 2018, the date the entity acquired the assets at issue in this Self-Report. The violation ended on December 3, 2021, the date the entity completed all of the overdue relay scheme maintenance. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by not performing relay scheme maintenance for 44 relay schemes across six substations is that the relays could fail to operate as expected, which could reduce the reliability of the BPS. The risk is not minimal because of the long duration of the violation. The risk is not serious because these substations primarily serve industrial load, meaning that if the relays failed to operate, the impact on the BPS would likely be minimal. ReliabilityFirst notes that there have been no failures at the DIG site due to insufficient maintenance on the relays. | To mitigate this violation, the entity has performed the following actions: 1) completed maintenance at Dearborn Sub 41 DC Supply; 2) completed maintenance at Dearborn 48/49 DC Supply; 3) completed protection system maintenance on the equipment associated with the Ford #1, including Dearborn Generation 48/49 Breaker P; 4) completed protection system maintenance on Substation 42 breakers; 5) completed maintenance on Double Eagle #1 line and Dearborn Generation 41 Transformer E (including breakers at 99 and 41); and 6) completed maintenance on Warren-Navarre-Dig lines Dearborn Generation 42 Transformer N protection and breaker 42005. 7) completed maintenance on Double Eagle #2 line and Dearborn Generation 41 Transformer F (including breakers at 99 and 41); 8) completed maintenance on Ford #2 and Transformer M; and 9) completed maintenance on Bus Relaying at Dearborn Generation 99. In addition, the entity integrated the relays into its NERC Compliance Program to prevent recurrence of the violation. | When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered the presence and operation of a quality compliance program as well as other indicators of a culture of compliance at the entity. This was evidenced by the fact that the violations at issue in this Agreement were proactively identified and reported by the entity after acquiring the Assets. The entity’s internal controls helped identify the violations and the entity ran thorough extent of conditions for the violations to determine the scope of each violation. The entity has spent considerable resources to identify all of the violations, to mitigate the violations, and to integrate the Assets into its NERC Compliance Program which will help prevent recurrence. The entity’s actions identified, addressed, and eliminated longstanding Bulk Electric System (BES) risk for these Assets. Therefore, ReliabilityFirst is awarding a significant amount of internal compliance program credit to encourage this sort of behavior by ITCT and other Registered Entities in the future. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance.
2021-12-30 | NOC-2749 | ReliabilityFirst Corporation (RF) | ITC Transmission (ITCT) | NCR00803 | TO | Settlement Agreement | Admits | $20,000 (for RFC2019022365 and RFC2019022362) | RFC2019022362 | PRC-023-4 | R1 | Moderate | High | Severe | Self-Report | 2019-10-04 | 2018-07-02 | 2019-07-30 | 2019-07-30 | 2020-08-20 | On October 4, 2019, the entity submitted a Self-Report to ReliabilityFirst stating that, as a Transmission Owner, it was in violation of PRC-023-4 R1. This violation relates to the entity’s acquisition of the DIG site Protection System assets. On July 2, 2018, the entity acquired the six substations at issue from Ford, Cleveland-Cliffs and DIG. The Assets include 230 kV and 120 kV Protection Systems that also interconnect with 844 MW of generation. The entity’s purchase of the Assets resulted in the acquisition of Protection Systems subject to PRC-023. Upon purchasing the Assets, the entity conducted a compliance review for all Protection Systems subject to PRC-023. After reviewing the applied relay settings and Facility Ratings, there were a total of six schemes that had relay settings that were not compliant with any criteria of PRC-023-4 R1. The root cause of this violation is that the prior owners of the Assets did not have internal controls in place to ensure that all schemes have relay settings that are compliant with PRC-023-4 R1. This violation involves the management practice of external independencies. The violation began on July 2, 2018, the date the entity acquired the assets at issue in this Self-Report. The violation ended on July 30, 2019, the date the entity brought all six relay settings into compliance by performing a settings reset. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by having six schemes that have relay settings that are not compliant with any criteria of PRC-023-4 R1 is limiting transmission loadability and interfering with system operators’ ability to take remedial actions to protect system reliability. The risk is not minimal because of the more than one year duration. The risk is not serious because these substations primarily serve industrial load meaning that if the relays failed to operate, the impact on the BPS would likely be minimal. ReliabilityFirst notes that no operations due to the noncompliant relay settings occurred during the violation. | To mitigate this violation, the entity brought all six relays into compliance with a settings reset. The entity implements multiple controls in the setting process to detect and prevent non-compliant settings from being applied to relays. The entity detected the non-compliant settings on the relays it purchased through the use of these controls and created compliant settings within the same process. | When assessing the penalty for the violations at issue in this Agreement, ReliabilityFirst considered the presence and operation of a quality compliance program as well as other indicators of a culture of compliance at the entity. This was evidenced by the fact that the violations at issue in this Agreement were proactively identified and reported by the entity after acquiring the Assets. The entity’s internal controls helped identify the violations and the entity ran thorough extent of conditions for the violations to determine the scope of each violation. The entity has spent considerable resources to identify all of the violations, to mitigate the violations, and to integrate the Assets into its NERC Compliance Program which will help prevent recurrence. The entity’s actions identified, addressed, and eliminated longstanding Bulk Electric System (BES) risk for these Assets. Therefore, ReliabilityFirst is awarding a significant amount of internal compliance program credit to encourage this sort of behavior by ITCT and other Registered Entities in the future. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance.
2021-11-30 | NOC-2687 | SERC Reliability Corporation (SERC) | LG&E and KU Services Company as agent for Louisville Gas and Electric Company and Kentucky Utilities Company (LGE and KU) | NCR01223 | GO, TO | Settlement Agreement | Neither Admits nor Denies | 0 | SERC2017018352 | PRC-005-1 | R2 | Moderate | High | High | Self-Report | 2017-09-18 | 2007-06-18 | 2019-07-09 | 2021-07-25 | TBD | LGE and KU notified SERC that it was in violation of PRC-005-6 R3 for failing to maintain its Protection System in accordance with the minimum maintenance and testing (M&T) activities and maximum maintenance intervals. SERC later determined that the violation extended back to PRC-005-1 R2. Around May 8, 2017, LGE and KU alerted SERC about this issue, stating that misrepresentations had occurred, that an extent-of condition assessment was underway to determine the scope of the issue, and a Self-Report would be forthcoming once the assessment was completed. Additionally, on October 29, 2019, LGE and KU submitted an expansion of scope for its Transmission Owner (TO) function for five battery banks where testing was outside the required intervals. In March 2017, a Generation Services employee (EE-A), was terminated due to performance issues, including the failure to complete tasks as assigned. In March/April 2017, EE-A’s manager undertook a review of EE-A’s projects, including tasks associated with generation M&T status and performance of controls. On April 17, 2017, during this review, the manager discovered that LGE and KU’s PRC-005-6 M&T program had not been extended to include its Blackstart Resources at two substations by July 1, 2016 in accordance with the Implementation Plan for Phase 2 of the revised Bulk Electric System (BES) definition. Additionally, there were no M&T results for these Blackstart Resources. Both substations connect at less than 100kV and were not BES components prior to the revised BES definition. LGE and KU discovered that EE-A had misrepresented the status of work activities for the Protection System devices associated with the Blackstart units by providing numerous inaccurate verbal updates to the manager that required M&T activities were on schedule and all required activities associated with Protection System devices associated with the Blackstart Resources would be completed prior to July 1, 2016. From April 17 through mid-July 2017, an extent-of-condition review was performed to identify if there were any other instances in which EE-A failed to perform required Generation Owner (GO) related tasks. LGE and KU discovered that EE-A failed to review battery test results at one substation to ensure they were completed as required and entered into Cascade (data repository being used at the time by the department). Specifically, EE-A had been entering information into the internal control (Cascade) to make it appear as though EE-A had completed reviews of the data, when in fact EE-A had not. From mid-July 2017 through September 2017, LGE and KU began completing M&T for the GO devices that had been identified as noncompliant and submitted a Self-Report and mitigation plan, which included steps for identifying if there were additional noncompliant devices. From late 2017 through June 2018, LGE and KU contracted a third-party consultant to perform a walk-down and print review of all generation assets to ensure that all generation assets that should be in scope for PRC-005 were accurately identified. From June 2018 through November 2018, during the review of the data provided by the third-party consultant, LGE and KU GO identified several inaccuracies with the information the consultant provided, including errors such as listing duplicate assets, inclusion of retired assets, assets missing from the vendor’s list that the LGE and KU GO knew should have been on the list. Thus, LGE and KU GO determined that it could not rely on the consultant’s review and that internal resources were needed to conduct another walk-down and review of generation assets. From November 2018 through May 2019, LGE and KU GO conducted an extensive internal review that included a combination of walk downs and in-depth DC schematics review to identify and verify the inventory of generation assets within scope for PRC-005. LGE and KU identified a total of 82 noncompliant Protection System devices that were directly attributed to EE-A, which includes the 78 Protection System devices associated with the LGE and KU Blackstart Resources and the 4 battery banks. LGE and KU’s extensive review identified 159 additional noncompliant Protection System devices on the generation side, 24 of which were attributable to missed devices. All M&T activities associated with these 159 Protection System devices occurred during the time period EE-A had primary responsibility for the GO’s PRC-005 compliance. However, during LGE and KU’s performance of the mitigation activities, it did not dedicate resources to track, or attempt to verify, which additional violations were directly attributable to EE-A’s actions/inactions. Notwithstanding, although EE-A did not perform the actual M&T activities, the EE-A’s responsibilities included notifying plant personnel of the required M&T, reviewing results, ensuring complete and appropriate documentation of the M&T activities, tracking completion of maintenance and testing activities, and updating management as to the status of the testing and maintenance activities. After EE-A’s termination, EE-A’s manager discovered that EE-A was not performing several of these tasks. Specifically: (1) EE-A was not properly notifying plant personnel of the required testing; (2) when testing results were submitted to EE-A, he was not reviewing the results and ensuring that there was appropriate documentation to demonstrate that all the required M&T activities had been properly completed; and (3) EE-A was falsifying information in an internal control (Cascade) that the company utilized to track the completion of PRC-005 M&T activities. Specifically, EE-A had been entering information that indicated that the EE-A had reviewed the testing records and verified everything was compliant, when in fact EE-A had not. On October 29, 2019, LGE and KU as a TO submitted an expansion of scope for three Vented Lead-Acid (VLA) battery banks and two Valve-Regulated Lead-Acid (VRLA) battery banks. The five instances of non-compliance were identified during a review by the LGE and KU TO of its PRC-005 testing records. Three of the instances were tied to the transition to PRC-005-6 and the associated 18-month and 6-month testing intervals for batteries. In each of these cases, the devices were tested just slightly outside the required window due to an error with the macro that tracks completion. One of the instances was tied to an individual inadvertently entering the wrong testing interval, and the last one was tied to a missing work order. From November 2019 through March 2020, in response to a SERC RFI, LGE and KU TO performed a walk-down of four transmission substations. The walk-down did not identify any additional instances of non-compliance. Because no other issues were identified, SERC did not require any additional walk-downs of the TO facilities. From February 13, 2018 to June 4, 2018, SERC conducted an on-site Compliance Audit of the GO and TO functions of LGE and KU. SERC included PRC-005-6 R3 in the 2018 Compliance Audit scope and did not identify any issues for either transmission or generation assets. The cause of the issues identified in the Self-Report involved the management practice of asset and configuration management, which includes validation processes and internal controls. Specifically, LGE and KU lacked effective internal controls to verify verbal reports on M&T activities and to verify the accuracy of its system diagrams, which resulted in LGE and KU failing to identify all Protection System devices. LGE and KU also lacked effective internal controls to verify the monthly review list was complete, i.e., missing Blackstart units, which resulted in not identifying the employee misrepresentation issue until April 2017. Further, LGE and KU did not conduct a walk-down of the facilities prior to the implementation of PRC-005-1 and lacked documented asset and configuration management processes. The cause of the Scope Expansion was tied to the transition to PRC-005-6 and the associated 18-month and 6-month testing intervals for the batteries. The other instances were due to human error for inadvertently entering the wrong testing interval and a missing work order. The noncompliance identified in the Self-Report started on June 18, 2007, when Version 1 of the Standard and Requirement became mandatory and enforceable on LGE and KU, and ended on July 31, 2017, when LGE and KU completed the last of its battery M&T for generation assets. The noncompliance identified in the expansion of scope started on February 1, 2018, the first instance that LGE and KU failed to perform M&T activities within the required interval, and ended on July 9, 2019, when LGE and KU completed the last of the M&T activities for transmission assets. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). LGE and KU’s failure to perform M&T activities with the defined intervals could have caused Protection System relays to operate prematurely and trip a unit, fail to operate and cause the next Protection System relay to operate to clear the fault, or unnecessarily trip a transmission line. LGE and KU did maintain and test the Blackstart units as a part of general plant maintenance, but did not perform the M&T of the associated Protection System devices in accordance with the PRC-005 requirements. LGE and KU work orders for the M&T activities at both plants were performed in accordance with good utility practices, however, the test frequency or extent of testing did not fulfill the periodicity or types of testing required by PRC-005. LGE and KU also failed to perform M&T, within the defined intervals, for some devices associated with 27 of its 34 generators (79.41%) and five batteries on the Transmission system. The impacted generators ranged from a net nameplate rating of 529 MVA to 10 MVA with annual capacity factors ranging from 76% to 0.7%. An unexpected trip of any of these generators would not have a significant impact as entities are required to carry spinning reserves, which would be available if needed. The majority of the units impacted were around 200 MVA. The Blackstart units ranged from 11 MVA to 38 MVA and three were hydro. The gas-fired Blackstart units had annual capacity factors of less than 1%. In addition, of the 218 devices LGE and KU GO failed to maintain in accordance with PRC-005, 155 (71%) were CTs and PTs, which have 12 year intervals and the only maintenance activity required is to verify that current and voltage signal values are provided to the protective relay. PT or CT failure would typically be identified prior to the 12 year verification activity. In addition, LGE and KU Transmission Operations would have been notified via an alarm regarding the loss of DC power or the Loss of a Remote terminal unit if there were issues associated with the five TO batteries. The Quarterly Substation Inspections that follow LGE and KU PRC-005 Protection System Maintenance Program (PSMP) were completed on time for all of the affected batteries. The Quarterly Substation Inspection included verifying the station DC supply voltage, inspecting the electrolyte level of the batteries, and checking the DC supply system unintentional grounds. The test results for all affected TO batteries confirmed Protection Systems were operating as designed, thus, minimizing any potential impact to the BPS had a system disturbance occurred and there were no misrepresentations during the duration of the violation. No harm is known to have occurred. | To mitigate the noncompliance for the generation assets, LGE and KU: 1) terminated the employee who misrepresented maintenance and testing records; 2) developed, trained, and implemented a process to review current and future generation projects, as well as scopes of work, to assess if there are compliance impacts to applicable standards; 3) conducted an internal review, a combination of re-walk down and an in-depth DC schematics review, to identify and verify inventory of generation PRC-005 assets; 4) confirmed test records are available for PRC-005 generation devices; 5) submitted noncompliant PRC-005 generation assets list(s) for testing to plant personnel;. 6) developed and implemented compliance preventive maintenance work orders utilizing Maximo (a fleet-wide Enterprise maintenance management system) to provide a consistent and reliable approach to scheduling compliance work orders; 7) developed and implemented Protection Systems training; 8) implemented and enforced a repository of PRC-005 generation assets and a tool that automates and standardizes testing processes; 9) developed and implemented training on its generation change management program; and 10) ensured maintenance and testing was completed, and appropriate maintenance and testing records were maintained, for all PRC-005 generation devices and ensured adequate evidence was maintained to demonstrate compliance, such as including actual voltage, current, and resistance values measured during the required testing to demonstrate that the test was performed. To mitigate the noncompliance for the transmission assets, LGE and KU: 1) performed the required tests to bring the noncompliant devices into compliance with PRC-005-6 requirements; 2) counseled the parties responsible for performing the work where the potential compliance issues were found of the PRC-005 maintenance and testing expectations; 3) conducted a PRC-005 overview with each operation center and Transmission Asset Management; 4) created and distributed jobs aides for Cascade data entry to each PRC-005 Protection System Component; 5) updated report logic to generate alerts based on PRC-005 test intervals that will include an ongoing reconciliation of total, outstanding, and completed work orders; and 6) reviewed all Cascade records for LGE and KU’s TO PRC-005 Communications Systems, Voltage & Current Sensing Devices, and Control Circuitry to ensure test intervals are accurate and test records support compliance with PRC-005. | LGE and KU’s relevant prior noncompliance with PRC-005-1 R2 includes NERC Violation Identification Numbers: SERC200800135, SERC2011006699, and SERC2013012951. In SERC200800135, LGE and KU had gaps in its documentation to support completion of maintenance testing activities for some components of its Generation and Transmission Protection Systems as defined in the NERC Glossary of Terms. This violation was under different managers and ownership at the time and was mitigated eight years prior to the start of the instant violation. Therefore, this violation does not warrant aggravation of the instant violation. In SERC2011006699, Protection System devices were not compliant with PRC-005 due to a lack of clarity with the division of responsibility at the GO/TO boundary. After identifying the noncompliant Protection System devices, LGE and KU undertook a review that identified other noncompliant generation devices associated with the inclusion of auxiliary equipment devices and missed testing intervals which were incorporated into SERC2011006699. The internal controls implemented to address the noncompliance were designed to: (i) ensure proper identification and assignment of responsibility for Protection System devices located at GO/TO boundaries within LGE and KU, and (ii) to improve the generation data management. A portion of the mitigation plan was focused on the development of an internal control designed to ensure the correct allocation of responsibility between the GO and TO, which would not have come into play with regard to the devices identified in the instant violation. In addition, as a part of the mitigation plan for SERC2011006699, the LGE and KU GO adopted Cascade, which was also used by the LGE and KU TO, for data management and the implementation of internal controls for tracking and reporting Protection System maintenance and testing. However, the GO subsequently identified that Cascade was unable to properly interact with other systems used by generation undermining the ability to use Cascade as a sole control for all of generation’s Protection System devices’ testing and maintenance records. To address this gap, the LGE and KU GO implemented manual processes to track, check and follow-up with plant personnel to ensure required PRC-005 maintenance and tests had occurred. It is these manual processes that EE-A in this instant issue failed to perform. As noted in the mitigation plan for the current Self-Report, LGE and KU is addressing this issue by implementing a new data management system that better aligns with generation’s systems and relies less on manual internal controls. In addition, changes to the PRC-005 standard and the BES definition resulted in an expansion of the scope of devices that needed to be included in the LGE and KU GO PRC-005 program. For example, the Blackstart Resources did not meet the BES definition until it was revised in 2014 and compliance was not required for the devices associated with these Blackstart Resources until July 1, 2016. While LGE and KU had a plan intended to track the compliance activity associated with integrating these devices into the PRC-005 program by July 1, 2016, this plan was undermined by the actions of the terminated employee in this Self-Report. SERC201106699 should not be attributed to this instant violation because three of the instances of non-compliance were tied to the change in intervals associated with the implementation of PRC-005-6. Specifically, the macros for the reports that identified overdue testing and maintenance were not updated to reflect the new testing intervals, and therefore the overdue testing and maintenance was not flagged on the reports. As for the remaining two instances of non-compliance, one tied to a data entry error and one to a missing work order, neither was an issue that would have been caught by the internal controls implemented in 2011. In SERC2013012951, the instances of non-compliance were associated with the change management process, namely, the failure to test devices prior to placing them in service, and missed test intervals for TO Protection System devices. The controls implemented in the mitigation plan for SERC2013012951 were focused on change management for transmission assets and an increased emphasis on and visibility of upcoming test deadlines. The change management process enhancements that were developed to mitigate SERC2013012951 are unrelated to the instances of non-compliance reported in 2019. The monthly report was involved, but only to the extent that there was a failure to update the macros that produce the monthly report as further described below. The expansion of the scope was for five non-compliant TO devices VLA batteries and VRLA batteries). The controls implemented to mitigate SERC2013012951 would not have been able to detect or prevent the instances of non-compliance for these five devices due to the nature of the issues that led to the non-compliance. Specifically, the non-compliance stemmed from a failure to update the macros contained in the monthly report from the prior requirement to test the Protection System DC Supply once per calendar year to the new mandatory test intervals in PRC-005-6 of eighteen-month VLA battery test interval (impacting one device) and the six-month VRLA battery test interval (impacting two devices). The two other instances of non-compliance, one tied to a data entry error and one to a missing work order, were not issues that would have been caught by the internal controls implemented in 2013.
2021-11-30 | NOC-2742 | SERC Reliability Corporation (SERC) | South Carolina Public Service Authority (SCPSA) | NCR01312 | GO, TO | Settlement Agreement | Neither Admits nor Denies | 40000 | SERC2018019136 | FAC-009-1 | R1 | Moderate | Medium | Severe | Compliance Audit | 2018-02-08 | 2007-06-18 | 2021-03-18 | 12/1/2021 (Expected Completion Date) | TBD | SERC determined that SCPSA was noncompliant with FAC-008-3 R6. SCPSA had 21 Facility Ratings that were not consistent with its associated Facility Ratings methodology (FRM). SERC later determined that this violation started under FAC-009-1 R1 and spanned to FAC-008-3 R6. When preparing documentation for a SERC audit data request, SCPSA discovered four instances of incorrect element ratings at one substation, which resulted in Facility Ratings that did not match the FRM. Correction of the element ratings resulted in three Facility Rating increases and one Facility Rating decrease. As part of the on-site audit, SERC completed a walk-down of the substation and discovered seven additional incorrect element ratings; however, none of these incorrect element ratings impacted the Facility Rating. After the Audit, SCPSA performed an extent-of-condition review and conducted a walk-down of all of its generation and transmission facilities. As a result, SCPSA discovered incorrect Facility Ratings at 18 of its 319 transmission facilities, inclusive of the one found during SCPSA’s audit preparation. Of the 18 transmission facilities identified, 12 of the Facility Ratings decreased when corrected. Specifically, the maximum summer Facility Rating decrease was 50% and the maximum winter Facility Rating decrease was 84%. Both maximum Facility Rating changes occurred as a result of an incorrect switch rating at the same 115kV Facility. Furthermore, SCPSA identified incorrect Facility Ratings at nine of its 27 generating units. Six generating units had a single incorrect Facility Rating and three units each had two incorrect Facility Ratings. Of the generating Facility Rating changes, two instances were de-rates of 21.25%, and the remainder were increases with a maximum increase of 4.6%. During the period of noncompliance, SCPSA’s loads did not exceed the correct Facility Rating in any instance of a Facility Rating decrease at its transmission or generating facilities. During its walk-down, SCPSA determined that the oldest incorrect Facility Rating occurred prior to the Standard’s June 18, 2007 effective date. On March 18, 2021, SCPSA revised all incorrect element and Facility Ratings. The causes of the violation were a deficient procedure at its generating facilities and inadequate training at its transmission facilities. The procedure associated with its generation facilities was deficient because it did not specify the specific instances when SCPSA should use a calculation instead of manufacturer nameplate values or when multiple elements could be considered in a single rating. Additionally, at its transmission facilities, some business units lacked awareness of SCPSA’s established process for communicating changes made to the transmission system. During the period of noncompliance, these business units had significant changes to its organization and inadequate training of new employees. This violation started on June 18, 2007, when the Standard became Mandatory and enforceable, and ended on March 18, 2021, when SCPSA revised the incorrect element and Facility Ratings. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCPSA’s failure to establish Facility Ratings consistent with its FRM could result in violations of System Operating Limits, unnecessary facility trips, damage to facilities, and erroneous planning. Additionally, this violation affected 33% of its generating units and 5.6% of its transmission facilities. SCPSA reviewed the operating records for all of the de-rated facilities and found that none operated at loads greater than the revised Facility Ratings during the period of noncompliance. No harm is known to have occurred. | To mitigate this violation, SCPSA has or will perform the following actions: 1) corrected the element and Facility Ratings; 2) increased the Transmission Project Management and Area Engineering business units’ visibility into the facility rating process by adding their representation to the Model Validation and Dynamics Review Team (MVDRT), so that the team includes representation from all areas that have a key role in the facility ratings process; 3) established a Continuous Improvement Project Team, consisting of representation from Power System Engineering & Control, NERC Compliance, Generation, Customer Service, and Technology & Innovation, to focus on minimizing physical and electrical facility characteristics data discrepancies between Transmission Planning’s database and field assets/equipment; 4) implement a standardization of database and filed asset/equipment inputs through checklists for suppliers and field personnel for its transmission facilities; 5) implemented an annual internal control to target verification of 20% of its transmission facilities each calendar year; 6) revise the Generation Facility Ratings Methodology procedure to provide clarity on the rating methodology of generation facilities, including guidance on when nameplate ratings versus calculations can be used and clearly indicate that the generator step-up transformer is evaluated for both the low and high-side and train annually on the new procedure; and 7) implement comprehensive training programs for both its transmission and generation personnel that include annual facility rating training for MVDRT; training to personnel that have a role in the established process for communicating changes made to the transmission system and generating units; training for personnel that conduct work activities on the transmission system on a day-to-day basis; training for personnel responsible for electrical maintenance at the generating units; annual training for the Generation Lead Team; and a computer-based training module on FAC-008 to provide to employees that have a role in making changes to the transmission system as part of their on-boarding process as a new employee. | SERC reviewed SCPSA’s internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SCPSA's ICP includes strong oversight and an ongoing internal control to walk down 20% of its facilities every year. SERC considered SCPSA’s compliance history and determined there were no relevant instances of noncompliance.
2021-11-30 | NOC-2746 | ReliabilityFirst Corporation (RF) | Southern Indiana Gas & Electric Company d/b/a CenterPoint Energy Indiana South | NCR00917 | TOP | Settlement Agreement | Admits | 0 | RFC2019022724 | TOP-002-4 | R6 | Moderate | Medium | Severe | Self-Report | 2019-12-19 | 2018-06-26 | 2018-06-27 | 2019-09-05 | 2020-04-10 | On December 19, 2019, the entity submitted a Self-Report stating that, as a Transmission Operator (TOP), it was in violation of TOP-002-4 R6. The entity failed to provide its Reliability Coordinator (RC), MISO, with an Operating Plan for next-day operations addressing potential SOL exceedances identified as a result of its Operational Planning Analysis. Specifically, on June 26, 2018, as the result of performing its next-day operations study, the entity identified two post-contingent SOL exceedances. the entity created an Operating Plan for next-day operations to address the identified SOL exceedances as required by TOP-002-4 R2. However, the entity, as a TOP, did not notify its RC, MISO, as required by TOP-002-4 R6. The noncompliance was discovered as the result of an entity review of all next-day operations studies between April 1, 2017 and September 5, 2019. The next-day operations study revealed the following potential SOL exceedances: a. For the loss of the Francisco to Duff 345kV line, the study indicated an 8.23% post-contingent MVA overload on the Z80 Francisco to Toyota Tap 138kV line; and b. For the loss of the Francisco to Duff 345kV line, the study indicated a 7.43% post-contingent MVA overload on the Z80 Elliott to Toyota Tap 138kV line. The root cause of this noncompliance was inadequate training of entity Transmission Operators on their notification responsibilities when an SOL exceedance is identified via a next-day operations study. This noncompliance involves the management practice of grid operations. Grid operations management is involved because grid operations involves maintaining situational awareness of the grid, and in this instance by failing to report its findings of a potential SOL exceedance and an accompanying Operating Plan to MISO, the entity potentially adversely impacted the situational awareness of the grid. The violation started on June 26, 2018, when the entity failed to notify MISO of potential SOL exceedances for June 27, 2018, and ended on June 27, 2018, when the entity performed its daily next-day operations study. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by the failure to notify the RC of possible exceedances could result in the RC operating based on inaccurate and different risk and transmission assumptions, potentially causing adverse impacts on the BPS. Specifically, where the entity fails to share the results of next-day studies with the RC before the next day, the RC would be relying on internal BPS studies without knowledge of all relevant or identified contingencies, increasing the probability of miscoordination. The risk here is not minimal because the two potential exceedances identified and not communicated involved a 345 kV line that supported a 138 kV network. Additionally, the study identified two potential MVA rating overloads over 7%, which are sizable overages. The risk here is not serious because MISO has real-time procedures for congestion management to mitigate the risk of the affected lines. Further, the entity created an Operating Plan for next-day operations to address the potential SOL exceedances. Additionally, the entity has extensive internal procedures for collaborating with MISO in the event of an SOL exceedance or an instance approaching an SOL exceedance during real time operations. ReliabilityFirst also notes that the MISO Reliable Operations Working Group (ROWG) Report for June 2018 did not identify any actual SOL exceedances for the entity during the month of June 2018. | To mitigate this violation, the entity has performed the following actions: 1) notified TSO Operators of the procedure; and 2) updated the next-day study form to include a button to automatically produce an email to MISO Transmission Security Planning. | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst granted mitigating credit for cooperation and Self-Reporting. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. TOP-002-4 R6 was developed in response to findings relating to the September 8, 2011, Southwest Outage, with the intent being to improve communication between TOPs and their RC. This specific communication is essential for both TOPs and the RC so as to improve their ability to identify and plan for potential contingencies. The only available Violation Severity Level for TOP-002-4 R6 is Severe. Due to the criticality and regulatory intent of TOP-002-4 R6, and the fact that the type of issue in this case contributed to the September 8, 2011, Southwest Outage, this violation is disposed of in a Settlement. However, this specific violation does not rise to the level of warranting a monetary penalty. The violation is limited in scope. It includes a single instance where a single next-day study identified two potential SOL exceedances, and the entity did not communicate its Operating Plan to the RC as required. Additionally, this violation was identified as the result of an extensive two year review of next-day studies where the entity identified only this single, narrow instance. Based on the foregoing, ReliabilityFirst is not levying a monetary penalty.
2021-10-28 | NOC-2734 | SERC Reliability Corporation (SERC) | Performance Materials NA, Inc. (PerfMat) | NCR09008 | GOP | Settlement Agreement | Neither Admits nor Denies | $0 (for SERC2020024299 and SERC2021024528) | SERC2020024299 | VAR-002-1 | R1. | Minimal | Medium | Severe | Self-Report | 2020-12-10 | 2007-08-02 | 2019-10-28 | 2020-01-10 | TBD | PerfMat notified SERC that it was noncompliant with VAR-002-4.1 R1. PerfMat failed to operate one generator connected to the interconnected transmission system in the automatic voltage control mode or in a different control mode as instructed by the Transmission Operator (TOP). On April 1, 2019, PerfMat became the new owner and operator of a 420 MW Cogeneration Qualifying Facility (QF) that has two gas turbine units and one steam turbine unit (STG), connected at 138 kV. These units primarily provide power and steam to the site, but PerfMat also sells excess generation to the electric power market. When PerfMat acquired the QF, it assumed the registration date and the NCR number of the QF’s previous owners. On October 11, 2019, PerfMat’s testing contractor performed MOD-026 testing and discovered that the STG was operating with the Automatic Voltage Regulator (AVR) in power factor mode. Upon discovery, PerfMat determined that plant personnel knew it was operating with the AVR in power factor mode, but incorrectly believed it was a form of automatic voltage control and met the requirements of VAR-002-4.1. Additionally, PerfMat confirmed with the TOP that it had not given the previous owner any exemptions to operate the STG in power factor mode. On October 28, 2019, during an outage, PerfMat placed the STG’s AVR in automatic voltage control mode. PerfMat reviewed its two gas turbine units and verified that they were operating with the AVR in automatic voltage control mode. The cause of this noncompliance was a deficient process. PerfMat’s process did not detail the difference between automatic voltage control mode and power factor mode. As a result, plant staff erroneously believed that operating the AVR in power factor mode met the requirements of automatic voltage control. When the testing contractor called that into question, PerfMat immediately sought guidance and confirmed power factor mode does not meet the requirement of VAR-002. This noncompliance started on August 2, 2007, when the STG began operating in power factor mode and was required to comply with VAR-002 R1, and ended on October 28, 2019, when PerfMat operated the STG with the AVR in automatic voltage control mode. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). PerfMat’s failure to operate the AVR in automatic voltage control mode could have resulted in the TOP making incorrect assumptions regarding its control of reactive capability and taking actions that could adversely affect the reliability of the BPS. However, PerfMat was still controlling voltage with the AVR, even though it was in a different control mode. Additionally, the primary purpose of PerfMat’s generators is to produce steam for a steam host. The STG has a nameplate rating of 145 MW, but is typically operated at approximately 90 MW in order to support the steam demands of its chemical process operation. No harm is known to have occurred. | To mitigate this violation, PerfMat has performed the following actions: 1) updated the process in its Management of Change (MOC) document and all associated VAR procedures to reinforce R1, R2, and R3’s requirement to operate in automatic voltage control mode and provide additional guidance on how to operate within the required parameters; 2) trained operational staff on the updated process and documents including training on the difference between power factor and automatic voltage control mode; 3) completed a review of its policies and procedures with regards to the NERC standard compliance program to ensure there were no other gaps; 4) removed the ability to change the AVR control mode on the STG by removing the option on the control system’s HMI for switching to power factor mode so that it is no longer an option and automatic voltage control is the only mode permitted; and 5) completed the MOC notifying all plant personnel of the change. | SERC reviewed PerfMat’s internal compliance program and considered it to be a neutral factor in the disposition method. SERC considered PerfMat’s compliance history and determined there were no relevant instances of noncompliance. This violation is being disposed of as a $0 Spreadsheet Notice of Penalty. Even though PerfMat, as a new owner, assumed the registration of the facility and is responsible for its compliance liability, SERC acknowledges that these violations were not discovered and reported until PerfMat acquired the facility. SERC encourages PerfMat’s commitment to compliance and its assessment of the facility’s legacy compliance program by reviewing its inherited processes and reporting historical noncompliances. Additionally, despite PerfMat being a small entity and the long duration, the risk remained minimal.
2021-10-28 | NOC-2734 | SERC Reliability Corporation (SERC) | Performance Materials NA, Inc. (PerfMat) | NCR09008 | GOP | Settlement Agreement | Neither Admits nor Denies | $0 (for SERC2020024299 and SERC2021024528) | SERC2021024528 | VAR-002-1 | R2. | Moderate | Medium | Severe | Self-Report | 2021-02-09 | 2007-08-02 | 2020-12-06 | 2021-04-29 | TBD | PerfMat notified SERC that it was noncompliant with VAR-002-4.1 R2. PerfMat failed to maintain its Transmission Operator (TOP) supplied voltage schedule and notification requirements. SERC later determined that this noncompliance began under VAR-002-1 and continued to VAR-004-4.1. On April 1, 2019, PerfMat became the new owner and operator of a 420 MW Cogeneration Qualifying Facility (QF) that has two gas turbine units and one steam turbine unit (STG). While these units primarily provide power and steam to the site, PerfMat also sells excess generation to the electric power market. When PerfMat acquired the QF, it assumed the June 28, 2007, registration date and NCR number of the generator’s previous owners. On January 22, 2021, while responding to a request for information for a related noncompliance, PerfMat determined that it failed to meet the requirements of the TOP’s voltage schedule 53 times between April 9, 2019, and December 6, 2020. The TOP’s issued voltage schedule required PerfMat to operate within a band of 138 kV +2 kV to -2 kV and required PerfMat to notify them within 30 minutes of a failure to meet the voltage schedule. The maximum under voltage excursion was 133.437 kV for 3 hours, and the maximum upper limit exceedance was 140.698 kV for 11 hours. Additionally, the longest under voltage excursion was 134.254 kV for 48 hours. PerfMat’s initial review included all voltage data beginning on the date it acquired the facility, through February 25, 2021. Due to the limitations of obtaining data from the prior owners, PerfMat was unable to perform a more extensive extent-of-condition review for actions prior to its ownership. However, SERC believes that the evidence PerfMat presented is indicative of the historical actions of the facility’s previous owners and operators. The cause of this violation was a deficient procedure. Specifically, PerfMat’s procedure failed to contain information requiring specific adherence to the TOP’s voltage schedule and notification requirements. Its prior procedure only stated that the site needed to maintain a positive flow of VARS to the TOP at all times and did not reference the TOP’s voltage schedule or notification requirement. This violation started on August 2, 2007, when the Standard became mandatory and enforceable, and ended on December 6, 2020, when PerfMat met its voltage schedule. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. PerfMat’s failure to maintain the assigned voltage schedule in 53 instances from April 1, 2019, through February 25, 2021, could have resulted in equipment damage or insufficient reactive resource for reliable system operation. However, PerfMat is QF connected at 138 kV in the Midcontinent Independent System Operator Balancing Authority area. Thus, PerfMat would likely have a nominal impact to the grid when operating outside of the assigned voltage schedule. No harm is known to have occurred. | To mitigate this violation, PerfMat has performed the following activities: 1) updated its operating procedures and annual training module to address voltage schedule adherence requirement; 2) added voltage limit alarms; and 3) trained operators on the required response to meet the TOP’s voltage schedule requirements including its new procedure and alarms. | SERC reviewed PerfMat’s internal compliance program and considered it to be a neutral factor in the disposition method. SERC considered PerfMat’s compliance history and determined there were no relevant instances of noncompliance. This violation is being disposed of as a $0 Spreadsheet Notice of Penalty. Even though PerfMat, as a new owner, assumed the registration of the facility and is responsible for its compliance liability, SERC acknowledges that these violations were not discovered and reported until PerfMat acquired the facility. SERC encourages PerfMat’s commitment to compliance and its assessment of the facility’s legacy compliance program by reviewing its inherited processes and reporting historical noncompliances. Additionally, despite PerfMat being a small entity and the long duration, the risk remained moderate.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | PA, TP | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019022408 | TPL-001-4 | R2 | Minimal | High | Severe | Self-Report | 2019-10-19 | 2018-02-28 | 2020-06-24 | 2020-06-24 | 2020-09-17 | BHP notified WECC that it was noncompliant with TPL-001-4 R2. Specifically, the 2017 and 2018 Transmission Coordinating Planning Committee (TCPC) studies, previously thought to be complete, did not include all the requirements of its Planning Assessment, as required by the Standard. BHP’s practice had previously been to complete the Planning Assessment once its external Sub Regional Planning Group had finished compiling, verifying and sending the needed dynamic data for the neighboring entities and base cases in December of each year. However, BHP’s process that fed into the creation of the annual Planning Assessment was only partially completed by previous employees in 2017 who left the company and was completed late for the 2018 TCPC studies. The employees responsible for that part of the process vacated their positions before completing the study work in 2017 and writing the corresponding Planning Assessments. The root cause was attributed to BHP not implementing adequate controls to track the progress of the annual Planning Assessments and a misunderstanding of associated timing requirements. BHP had employee turnover that resulted in not having the required Subject Matter Experts (SMEs) to complete, nor track the progress of the Planning Assessments. The 2017, 2018, and 2019 annual Planning Assessments were due February 2018, 2019, and 2020, respectively. Though incomplete, BHP completed its 2017 Planning Assessment on November 4, 2019 and its 2018 Planning Assessment on December 17, 2019. The noncompliance began on February 28, 2018, when BHP’s 2017 Planning Assessment should have been completed, and ended on June 24, 2020, when BHP completed its 2019 Planning Assessment. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BHP failed to prepare an annual Planning Assessment timely, for its portion of the BES in 2017, 2018, and 2019, as required by TPL-001-4 R2. Such failures could have resulted in BHP’s inability to identify weaknesses in its system and an inability to implement action plans for identified system deficiencies or make needed system improvements. Had an event occurred on BHP’s system, it could have resulted in minor overloading on its local 115kV network or 230kV transmission line overloads. However, as compensation, for one of BHP’s local 115kV networks, if an event were to occur, it would not have adversely affected the BPS. For BHP’s 230kV transmission lines, BHP had a Remedial Action Scheme in place to curtail transfers across the tie for specified contingency events, thereby mitigating the potential overloads. As well, recent system upgrades had mitigated local voltage concerns and transmission facility additions and rating increases have mitigated local thermal loading issues. In addition, the possibility of BHP islanding its system from the main grid would not have had a significant impact to the BPS. Thereby, limiting the potential harm within BHP’s system, reducing the risk to the BPS. | To mitigate this violation, BHP has or will perform the following actions: 1) finalized its Planning Assessments for 2017 and 2018 with available study work and completed its Planning Assessments for 2019; 2) created a TPL-001-4 process checklist that is updated throughout the process of completing the study. These review checkpoints on the TPL-001-4 process checklist prompt the TP to send an email update to the supervisor to ensure that the checklist is being completed and it will provide the supervisor an opportunity to review the major tasks. In addition, the TPL-001-4 process checklist is updated throughout each annual study process to ensure each requirement of the Standard is being addressed. The TPL-001-4 process checklist provides a structured format for assessing TPL-001-4 deliverables and provides guidance and documentation for new employee training; and 3) acquired in-house technical expertise by hiring new qualified employees to complete Planning Assessments required by the Standard; and within its TPL-001-4 process checklist implemented a contingency plan to ensure Planning Assessments are completed timely; specifically if base case information is not available from its sub-regional planning group on a timely basis BHP will use the most recent valid and available studies to ensure timely completion and the forward looking nature of its Planning Assessments. | BHP’s issues with its planning assessments were considered systemic due to the number of Requirements violated, multiple instances, duration and incorrect process for completing the Planning Assessments. Further, the systemic nature of BHP’s issues with TPL-001 also warranted alleging the violations and assessing a penalty. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | PA, TP | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019022409 | TPL-001-4 | R3, R3.2, R3.4. R3.5 | Minimal | Medium | Severe | Self-Report | 2019-10-19 | 2018-02-28 | 2020-06-24 | 2020-06-24 | 2020-09-17 | BHP notified WECC that it was noncompliant with TPL-001-4 R3. Specifically, the 2017 and 2018 Transmission Coordinating Planning Committee (TCPC) studies, previously thought to be complete, did not include all the requirements of the steady state portion of its Planning Assessment, as required by the Standard. BHP’s TCPC studies for 2017 did not include the studies that assess the impact of the extreme events for the steady state portion of the Planning Assessment for one of the utilities that comprises its footprint, as required by TPL-001-4 R3.2. In addition, although BHP’s 2017 TCPC studies included a contingency list, the studies did not include a documented rationale for P0-P7 and extreme events that were expected to have more severe system impacts, as required by TPL-001-4 R3.4 and R3.5. BHP’s practice had previously been to complete the Planning Assessment once its Planning Group had finished compiling, verifying and sending the needed dynamic data for the neighboring entities and base cases in December of each year. However, BHP’s process that fed into the creation of the annual Planning Assessment was only partially completed by previous employees in 2017 who left the company and was completed late for 2018. The employees responsible for that part of the process vacated their positions before completing the study work in 2017 and writing the corresponding Planning Assessments. The root cause was attributed to BHP not implementing adequate controls to track the progress of the annual Planning Assessments and a misunderstanding of associated timing requirements. BHP had employee turnover that resulted in not having the required Subject Matter Experts (SMEs) to complete nor track the progress of the Planning Assessments. The 2017, 2018, and 2019 annual Planning Assessment were due February 2018, 2019, and 2020, respectively. Though incomplete, BHP completed its 2017 Planning Assessment on November 4, 2019 and its 2018 Planning Assessment on December 17, 2019. The noncompliance began on February 28, 2018, when BHP’s 2017 Planning Assessment should have been completed, and ended on June 24, 2020, when BHP completed its 2019 Planning Assessment. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, BHP failed to complete timely its steady state portion of the Planning Assessment for 2017, 2018 and 2019 by performing studies for the Near-Term and Long-Term Transmission Planning Horizons in Requirement R2, Parts 2.1, and 2.2, as required by TPL-001-4 R3. Such failures could have resulted in BHP’s inability to identify weaknesses in its system and an inability to implement action plans for identified system deficiencies or make needed system improvements. Had an event occurred on BHP’s system, it could have resulted in minor overloading on its local 115kV network or 230kV transmission line overloads. However, as compensation, for one of BHP’s local 115kV networks, if an event were to occur, it would not have adversely affected the BPS. For BHP’s 230kV transmission lines, BHP had a Remedial Action Scheme in place to curtail transfers across the tie for specified contingency events, thereby mitigating the potential overloads. As well, recent system upgrades had mitigated local voltage concerns and transmission facility additions and rating increases have mitigated local thermal loading issues. In addition, the possibility of BHP islanding its system from the main grid would not have had a significant impact to the BPS. Thereby limiting the potential harm within BHP’s system, reducing the risk to the BPS. | To mitigate this violation, BHP has or will perform the following actions: 1) finalized the steady state portion of the 2017 Planning Assessment by performing studies for the Near-Term and Long-Term Transmission Planning Horizons and for 2019 Planning Assessments to include all extreme events; 2) created a TPL-001-4 process checklist that is updated throughout the process of completing the study. These review checkpoints on the TPL-001-4 process checklist prompt the transmission planner to send an email update to the supervisor to ensure that the checklist is being completed and it will provide the supervisor an opportunity to review the major tasks. In addition, the TPL-001-4 process checklist will be updated throughout each annual study process to ensure each requirement of the Standard is being addressed. The process checklist provides a structured format for assessing TPL-001-4 deliverables and provides guidance and documentation for new employee training; and 3) acquired in-house technical expertise by hiring new qualified employees to complete Planning Assessments required by the Standard; and within its TPL-001-4 process checklist implemented a contingency plan to ensure Planning Assessments are completed timely; specifically if base case information is not available from its sub-regional planning group on a timely basis, BHP will use the most recent valid and available studies to ensure timely completion and the forward looking nature of its Planning Assessments. | BHP’s issues with its planning assessments were considered systemic due to the number of Requirements violated, multiple instances, duration and incorrect process for completing the Planning Assessments. Further, the systemic nature of BHP’s issues with TPL-001 also warranted alleging the violations and assessing a penalty. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | PA, TP | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019022410 | TPL-001-4 | R4, R4.2, R4.3, R4.3.1, R4.3.1.1, R4.3.1.2 | Minimal | Medium | Severe | Self-Report | 2019-10-19 | 2018-02-28 | 2020-06-24 | 2020-06-24 | 2020-07-22 | BHP notified WECC that it was noncompliant with TPL-001-4 R4. Specifically, the 2017 and 2018 Transmission Coordinating Planning Committee (TCPC) studies, previously thought to be complete, did not include all the requirements of the steady state portion of its Planning Assessment, as required by the Standard. As well, BHP did not complete its 2019 TCPC studies timely. Specifically, BHP did not include the impacts of high-speed reclosing or relay models that would trip generators when they surpass their voltage ride through capabilities for the 2017 and 2018 TCPC studies, as required by TPL-001-4 R4.3.1.1 and R4.3.1.2. Furthermore, the modeling details described in R4.3 were not included as required for BHP’s 2018 TCPC studies. BHP did not realize that portions of the 2018 TCPC studies did not have high speed reclosing nor the impact of subsequent tripping of generators where simulations showed generator bus voltages or high side of the generation step up (GSU) voltages were less than known or assumed generator steady state or ride through voltage limitations programmed into the study files when the reports were sent to third-party consultants. Consequently, BHP’s 2018 TCPC study did not include impacts of high-speed reclosing or relay models that would trip generators when they surpass their voltage ride through capabilities, as required by TPL-001-4 R4.3.1.1 and TPL-001-4 R4.3.1.2. BHP’s practice had previously been to complete the Planning Assessment once its Planning Group had finished compiling, verifying and sending the needed dynamic data for the neighboring entities and base cases in December of each year. However, BHP’s process that fed into the creation of the annual Planning Assessment was only partially completed by previous employees in 2017 who left the company and completed late in 2018. The employees responsible for that part of the process vacated their positions before completing the study work in 2017 and writing the corresponding Planning Assessments. The root cause was attributed to BHP not implementing adequate controls to track the progress of the annual Planning Assessments and a misunderstanding of associated timing requirements. BHP had employee turnover that resulted in not having the required Subject Matter Experts (SMEs) to complete nor track the progress of the Planning Assessments and TCPC studies. The 2017, 2018, and 2019 annual Planning Assessment were due February 2018, 2019, and 2020, respectively. Though incomplete, BHP completed its 2017 Planning Assessment on November 4, 2019 and its 2018 Planning Assessment on December 17, 2019. The noncompliance began on February 28, 2018, when BHP’s 2017 Planning Assessment should have been completed, and ended on June 24, 2020, when BHP completed its 2019 Planning Assessment timely. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In these instances, BHP failed to complete all the requirements of the Stability portion of its Planning Assessment in 2017, 2018 and 2019, as described in Requirement R2, Parts 2.4 and 2.5, BHP failed to perform the Contingency analyses listed in Table 1. The studies were not completed based on computer simulation models using data provided in Requirement R1, as required by TPL-001-4 R4. Such failures could have resulted in BHP’s inability to identify weaknesses in its system and an inability to implement action plans for identified system deficiencies or make needed system improvements. Had an event occurred on BHP’s system, it could have resulted in minor overloading on its local 115kV network or 230kV transmission line overloads. However, as compensation, for one of BHP’s local 115kV networks, if an event were to occur, it would not have adversely affected the BPS. For BHP’s 230kV transmission lines, BHP had a Remedial Action Scheme in place to curtail transfers across the tie for specified contingency events, thereby mitigating the potential overloads. As well, recent system upgrades had mitigated local voltage concerns and transmission facility additions and rating increases have mitigated local thermal loading issues. BHP completed certain portions of the Stability portion of its 2017 and 2018 TCPC studies. In addition, the possibility of BHP islanding its system from the main grid would not have had a significant impact to the BPS. The limiting the potential harm remained within BHP’s system, reducing the risk to the BPS. No harm is known to have occurred. | To mitigate this violation, BHP has or will perform the following actions: 1) completed all requirements of the Stability portion of its Planning Assessment for the annual 2019 studies; 2) created a TPL-001-4 process checklist that is updated throughout the process of completing the study. These review checkpoints on the TPL-001-4 checklist prompt the TP to send an email update to the supervisor to ensure that the checklist is being completed and it will provide the supervisor an opportunity to review the major tasks. In addition, process checklist will be updated throughout each annual study process to ensure each requirement of the Standard is being addressed. The TPL-001-4 process checklist provides a structured format for assessing TPL-001-4 deliverables and provides guidance and documentation for new employee training; 3) acquired in-house technical expertise by hiring new qualified employees to complete Planning Assessments required by the Standard; and within its TPL-001-4 process checklist implemented a contingency plan to ensure Planning Assessments are completed timely; specifically, if base case information is not available from its sub-regional planning group on a timely basis BHP will use the most recent valid and available studies to ensure timely completion and the forward-looking nature of its Planning Assessments. | BHP’s issues with its planning assessments were considered systemic due to the number of Requirements violated, multiple instances, duration and incorrect process for completing the Planning Assessments. Further, the systemic nature of BHP’s issues with TPL-001 also warranted alleging the violations and assessing a penalty. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | TO | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2019021408 | PRC-005-1 | R2, R2.1 | Moderate | Lower | Moderate | Self-Report | 2019-04-25 | 2007-06-18 | 2019-04-02 | 2019-04-02 | 2019-09-18 | BHP notified WECC that it was noncompliant with PRC-005-1 R2. Specifically, during an internal compliance certification process, BHP discovered it did not verify battery terminal connection resistance and battery interval or unit-to-unit connection resistance every 15 calendar months as stated in its Protection System Maintenance Program (PSMP) for two battery banks at its DC tie 230kV converter substation. Specifically, BHP discovered that from the mandatory and enforceable date of the Standard, the battery banks involved had not been correctly verified, as required by PSMP. BHP’s third-party contractor was unable to perform the necessary testing because the batteries were designed with protective covers that could not be removed and prevented access to the battery’s posts and straps. In an effort to address the involved batteries design limitations BHP referenced the PRC-005-6 Supplementary Reference and FAQ document which led BHP to incorrectly believe the deferral of tone component of the required testing was acceptable. The root cause of the violation was attributed to the original design of the two battery banks that prevented testing for the battery terminal connection resistance and battery interval or unit-to-unit connection resistance from being completed, as prescribed by its PSMP. Additionally, a contributing cause of this violation was attributed to BHP's lack of a process or procedure for assuring adequate quality of third-party contract services prior to 2017. This noncompliance began on June 18, 2007, when the Standard became mandatory and enforceable, and ended on April 2, 2019, when BHP tested the battery banks in accordance with its PSMP and the current version of the Standard. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BHP failed to verify battery terminal connection resistance and battery interval, or unit-to-unit connection resistance every 15 calendar months as stated in its PSMP, for two battery banks at its DC tie 230kV converter substation, as required by PRC-005-1 R2. Such failure could have resulted in the breakers failing to trip which could have caused equipment damage due to high currents during abnormal system conditions. However, as compensation, the substation involved in the first violation was designed to include redundant battery systems, and each was designed to fully support the battery backup needs of the entire substation reducing the risk to the BPS. | To mitigate this violation, BHP has: 1) performed and verified the terminal connection resistance and battery interval, or unit-to-unit connection resistance on the involved battery banks; replaced the bolts used to connect the straps to the individual jars on the battery banks allowing for the full completion of the maintenance activities as specified in its PSMP; and 2) staff continued to use the testing templates to ensure the correct testing and verification is being performed. | BHP’s systemic issues with PRC-005 were considered an aggravating factor in determining to allege the violations and assess a penalty due to the violations’ VTH expectation for remediation and overlapping duration of the violations. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2736 | Western Electricity Coordinating Council (WECC) | Black Hills Corporation (BHP) | NCR05030 | TO | Settlement Agreement | Admits | $46,000 (for WECC2019022408, WECC2019022409, WECC2019022410, WECC2019021408, and WECC2020023613) | WECC2020023613 | PRC-005-6 | R3 | Moderate | High | Lower | Self-Report | 2020-06-30 | 2017-04-01 | 2019-12-12 | 2020-06-17 | 2020-10-20 | BHP notified WECC that it was noncompliant with PRC-005-6 R3. BHP discovered it did not verify that the communications system at one Bulk Electric System (BES) substation was functional every four calendar months, as prescribed within Table 1-2. Specifically, the involved substation consists of a 115kV ring bus and a non-BES three winding transformer that steps down to 34.5kV and 13.8kV. BHP discovered that its internal BES review committee did not analyze and recategorize the substation as containing BES elements once the addition of a new substation was interconnected on the BHP system on November 7, 2016. This addition caused the involved substation to no longer meet exclusion E1.b and instead met inclusion I4.b making the involved substation subject to PRC-005-6. The root cause of the violation was attributed to BHP’s BES review committee’s lack of a formal process to evaluate the effects of all projects on BHP’s system, including BES reclassifications. Additionally, the contributing cause of this violation was attributed to BHP’s BES review committee’s lack of a formal procedure to communicate the identification or reclassification of BES elements to the PRC-005 review team. This noncompliance began on April 1, 2017, when BHP failed to maintain communication systems within four calendar months of its substation being reclassified as BES, and ended on December 12, 2019, when BHP verified that the communications system at the involved substation was functional. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, BHP failed to verify that the communications system at one Bulk Electric System (BES) substation was functional every four calendar months, as prescribed within Table 1-2, as required by PRC-005-6 R3. Such failure could have resulted in a protection system device misoperation leading to the loss of BHP’s 115kV ring bus. However, as compensation, the involved battery banks had all other required testing performed every six months, including: supply voltage, electrolyte level, unintentional grounding, float voltage, battery continuity, cell condition, physical condition of rack, and cell/unit measurements against the station battery baseline, reducing the risk to the BPS. Additionally, the redundancy of the 115kV ring bus topology and the low voltage of the ring bus reduce the risk to the BPS. | To mitigate this violation, BHP has: 1) completed maintenance testing on the communication system at the involved substation; 2) conducted an extent of condition review and found no other instances of potential noncompliance; 3) replaced the informal BES review committee with a more formal chartered group, called the BES Definition Applicability Team (BESDAT), that includes members from the PRC-005 review team, to be responsible for the following: i. identifying BES applicability and/or impacts to facilities based on system configuration, equipment replacement or facility additions; and ii. reviewing and documenting BES designations for impacted facilities. | BHP’s systemic issues with PRC-005 were considered an aggravating factor in determining to allege the violations and assess a penalty due to the violations’ VTH expectation for remediation and overlapping duration of the violations. WECC did not apply mitigating credit for BHP’s Internal Compliance Program (ICP). Although BHP does have a documented ICP, WECC determined that BHP’s ICP was not effective in detecting or preventing these violations. WECC considered BHP’s compliance history and determined there were no relevant instances of noncompliance. WECC determined there were no other aggravating factors.
2021-10-28 | NOC-2739 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | TO | Settlement Agreement | Admits | $110,000 (for WECC2019021484, WECC2019021482) | WECC2019021484 | FAC-501-WECC-2 | R3 | Moderate | Medium | Severe | Self-Report | 2019-05-07 | 2019-01-01 | 2019-06-05 | 2020-07-14 | TBD | On May 7, 2019, SCEC submitted a Self-Report stating, as a Transmission Owner, it was noncompliant with FAC-501-WECC-2 R3. SCEC did not maintain and inspect three series capacitors and three circuit breakers (CBs) that were elements of three Major WECC Transfer Paths all operated at 500 kV, in accordance with its Transmission Maintenance and Inspection Program (TMIP). Prior to 2019, regarding the series capacitors, SCEC’s TMIP required a visual inspection and SCEC maintained documents that the inspection occurred, although they were not detailed. Specifically, in 2018, SCEC revised its TMIP to include requirements for more detailed inspections for series capacitors; however, it missed those detailed inspections in 2018. For the CBs, SCEC’s TMIP had not changed, yet the inspections were still not performed in 2018. The root cause of the violation was attributed to the progress of the inspections not being adequately tracked and lack of communication between responsible parties. For the first Major WECC Transfer Path, planned maintenance outages were rescheduled due to reliability constraints and new maintenance was not approved until after the end of the calendar year, thus exceeding the compliance deadline. For the second Major WECC Transfer Path, there was a lack of communication between SCEC compliance staff and field personnel. The series capacitors were out of service because they were being replaced and the field personnel assumed that they did not have to maintain the CBs associated with the out-of-service capacitors. The two groups did not effectively communicate to clarify the expectation that the CBs were still required to be maintained. For the third Major WECC Transfer Path, there was a lack of formal review to ensure that the scheduled work had been completed. SCEC’s workload template was manually populated with a task that did not roll over onto the next workload template, so personnel did not realize that the work had not been performed. This noncompliance began on January 1, 2019, when all the equipment was required to be inspected, per SCEC’s TMIP, and ended on June 5, 2019, when SCEC completed the inspections for all the affected equipment. | This violation posed a moderate risk to the reliability of the bulk power system (BPS). In this instance, SCEC failed to adhere to its TMIP for three series capacitors and three CBs, as required by FAC-501-WECC-2 R3, which were elements of three Major WECC Transfer Paths, all operated at 500 kV. SCEC’s series capacitors were utilized to improve power transfer capability of a transmission line and to improve system stability by reducing the phase angle of the line. Additionally, its series capacitors were used to share the load between parallel lines and control voltage. The series capacitor reduced the overall line reactance and allowed a larger stable transfer of power. As well, the series capacitors could have been applied to obtain better load division on parallel lines in the event there were different conductor resistances. A failure to maintain the series capacitors could have resulted in an improper operation of the capacitors failing to support the associated 500 kV transmission line capacity, thereby reducing stability to SCEC's system. This could have resulted in potential instability issues with three Major WECC Transfer Paths and one 500 kV Substation and a derating of the line. The failure to maintain the CBs associated with the series capacitors could have caused the CBs to prematurely open or fail to open, which could have resulted in a loss of the line or damaged equipment if the CB failed to isolate the series capacitor. The failure could have resulted in potential instability issues with the Major WECC Transfer Paths that have a potential of carrying 4,888 MW, depending on the directional flow. The Transfer Path losses could have triggered a Remedial Action Scheme (RAS) to trip 1,400 MW and 600 MW of load in the area to control the instabilities. Per the WECC Transfer Path Catalog, this particular area is considered sensitive. However, as compensation, all three of the Major WECC Transfer Paths had parallel lines and the operations of the RAS would have opened the appropriate other paths to reduce the loading. In addition, the three CBs are only capable of being operated as switchers, due to their configuration, thus during an emergency, other CBs (all of which were timely inspected per the TMIP) could have de-energized the associated transmission line. Two of the series capacitors were being replaced and out of service during the period of the violation. As well, SCEC had performed visual monthly inspections including a measurement of three electrodes that are used in back up protection for the capacitors from the ground and the series capacitors were actively monitored through internal alarms that identify potential degradation of series capacitors through the Energy Management System, reducing the risk to the BPS. | To mitigate this violation, SCEC has performed the following actions: 1) Completed maintenance and testing for the series capacitors and CBs; 2) Updated its monthly workload planning checklist to review with the Subject Matter Experts (SMEs) to ensure all aspects of its TMIP were completed and the responsible party was aware of its responsibilities and update as needed; 3) Finalized monthly workload planning checklist including obtaining management approval and validating the checklist with all the stakeholders; 4) Documented scheduling process project plan by creating a detailed project plan; 5) Documented previous scheduling processes; 6) Documented improved scheduling processes with an emphasis on the communications between responsible parties to address gaps in the monthly and annual scheduling process, changes or additions of inspections types (new equipment types) and annual review processes; and 7) Finalized the scheduling process changes and communicated them to affected personnel. | WECC reviewed SCEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination because it was effective in establishing controls to detect the noncompliance with FAC-501-WECC R3. WECC considered SCEC's compliance history and determined there were no relevant instances of noncompliance.
2021-10-28 | NOC-2739 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | TO | Settlement Agreement | Admits | $110,000 (for WECC2019021484, WECC2019021482) | WECC2019021482 | FAC-501-WECC-1 | R1 | Moderate | Medium | Severe | Self-Report | 2019-05-07 | 2016-01-02 | 2018-02-07 | 2019-12-11 | 2020-04-17 | On May 7, 2019, SCEC submitted a Self-Report stating, as a Transmission Owner, it was noncompliant with FAC-501-WECC-1 R1. Specifically, during SCEC’s review of its potential noncompliance with FAC-501-WECC-2 R3 (NERC Violation ID WECC2019021484), SCEC discovered it did not have documentation that it had not completed the 2016 and 2017 annual reviews of its TMIP. SCEC was late in completing its review for the 2018 TMIP. The root cause of the violation was attributed to poorly defined management policy guidance and expectations. SCEC had no formal process to initiate the annual review of its TMIP, thus there is not documentation to confirm if it was completed timely. Further, when the reviews occurred, SCEC did not appropriately store the documents to demonstrate compliance. This noncompliance began on January 2, 2016, when the TMIP review was due, and ended on February 7, 2018, when SCEC completed the annual review of its TMIP. | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the BPS. In this instance, SCEC failed to annually review its TMIP, as required by FAC-501-WECC-1 R1.1. Such failure could have resulted in SCEC missing maintenance intervals for new equipment or changed equipment which could have led to equipment not operating properly, resulting in equipment failures and causing unplanned outages. However, as compensation, if new equipment were to be added or changed, it would have been added to the TMIP because SCEC compliance personnel and responsible transmission personnel would have been aware of the changes, as these tasks were part of their main job functions. In addition, Major WECC transfer paths would not have changed without SCEC’s knowledge and it would be unlikely that the designation of addition lines would have resulted in SCEC missing their addition in the TMIP. Thus, it would have been unlikely that equipment maintenance would have been missed because of a missed annual review of SCEC’s TMIP. In addition, no changes to SCEC’s TMIP were required during the period of the violation, thereby lessoning the actual risk. | To mitigate this violation, SCEC has performed the following actions: 1) performed a review of its TMIP and found no updates were needed; 2) documented a process for annual review of its TMIP; and 3) trained responsible employees on the new process and the review requirements for the TMIP. | WECC reviewed SCEC's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination because it was effective in establishing controls to detect the noncompliance with FAC-501-WECC R3. WECC considered SCEC's compliance history and determined there were no relevant instances of noncompliance.
2021-09-30 | NOC-2725 | ReliabilityFirst Corporation (RF) | Covanta Delaware | NCR00743 | GO | Settlement Agreement | Admits | 0 | RFC2019021205 | VAR-002-4.1 | R2 | Moderate | Medium | Severe | Compliance Audit | 2019-02-27 | 2017-09-26 | 2020-10-01 | 2020-10-01 | TBD | On February 27, 2019, ReliabilityFirst identified as part of a Compliance Audit that the entity, as a Generator Owner, was in violation of VAR-002-4.1 R2. The Compliance Audit was conducted from January 17, 2019, through February 19, 2019. The entity was unable to produce any evidence that the generator was consistently maintained within the voltage schedule provided to them by the applicable Transmission Operator (TOP). For the duration of the noncompliance, the facility lacked the ability to store such evidence using existing facility historians and data recorders and therefore could not demonstrate that the TOP-supplied voltage schedule had been maintained. The entity provides that based on their knowledge, and limited documentation, the entity did not receive notifications from their Transmission Planner (TP) or TOP of any voltage schedule deviation. Starting in August of 2016, the entity’s real-time information and emergency notifications were monitored by a contractor that served as an intermediary between the entity and PJM (TOP). If PJM directed any action, the contractor would notify the facility of the directed action via phone and email. The entity provided that for the duration of the noncompliance, no direction related to voltage schedule deviations was received. The entity indicated that an internal procedure in place for the duration of the noncompliance directed the facility to maintain the TOP-supplied voltage schedule and record all applicable operator communications, including those with the TP and TOP, within the control room log book. The entity performed a sample review of its log books for the duration of the noncompliance comparing them against the PJM emergency procedure systems overall directed alerts for relevant systems. For the duration of the violation, for the TP region in which the entity resides, there were no low voltage alerts, voltage reduction actions, or voltage reduction alerts. However, there were a number of high system voltage actions in the TP region. The entity then sampled 12 high system voltage actions a year for the duration against their internal log books, and found that for all the actions reviewed, there were no communications with the facility from the TOP, TP, or contract intermediary including regarding voltage schedule issues or deviations. The root cause of this noncompliance was that the entity lacked the procedures and data capture capabilities to assure that the generator documented and retained all deviation information, and notified the TOP as required. This noncompliance involves the management practice of reliability quality management. Reliability quality management is involved because the entity did not develop necessary procedural documents or a programmatic approach to compliance with VAR-002-4.1 R2. The violation began on September 26, 2017, the date the entity was required to comply with VAR-002-4.1 R2. The violation ended October 1, 2020, the date the entity completed its Mitigation Plan. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is that the failure to identify and notify the TOP of voltage deviations places the TOP in an informational disadvantage and adversely impacts situational awareness, potentially resulting in harm to the BPS. Additionally, failing to identify and manage voltage deviations can result in harm to equipment. The risk posed here is not minimal because of the duration of approximately three years. The risk here is not serious because the facility’s capacity is just 90 MW, and plays a limited role in voltage regulation and support relative to the PJM generator system. ReliabilityFirst notes that while the entity is unable to provide necessary data, there is significant circumstantial evidence that points to there being no significant, alertable voltage schedule deviations for the duration (i.e., the entity did not have evidence of receiving notification from its contract intermediary notifying them of a voltage directive, and the entity’s sampled log book review based on TP region high system voltage events). Additionally, for the duration of the violation, for the TP region in which the entity resides, there were no low voltage alerts, voltage reduction actions, or voltage reduction alerts. | To mitigate this violation, the entity has performed the following actions: 1) performed a root cause study to determine the source of the noncompliance; 2) performed an extent of condition analysis to identify the full scope of the noncompliance; 3) identified activities to mitigate the noncompliance and implement steps to prevent recurrence; 4) replaced the existing AVR (Automatic Voltage Regulator) system to provide enhanced operational controls, and data capture capabilities. Additionally, the entity configured the recording of generator and system parameters to create evidence of voltage support consistent with the voltage schedule provided by the TOP; 5) updated internal procedures to improve operational guidance on voltage control and schedules; and 6) performed training for relevant personnel on the changes made to existing voltage control procedures. | ReliabilityFirst reviewed Covanta Delaware’s internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity's compliance history and determined there were no relevant instances of noncompliance. This violation was disposed of as a $0 SNOP instead of an FFT for the following reasons. First, the duration of approximately three years was significant, and the issue was identified via Compliance Audit, suggesting that the violation would likely have persisted for an even longer duration. Second, the evidence related to the existence/non-existence of potential deviations, while strong, was circumstantial.
2021-09-30 | NOC-2731 | Texas Reliability Entity, Inc. (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | DP, TO, TOP | Settlement Agreement | Neither Admits nor Denies | 0 | TRE2019022038 | IRO-010-2 | R3 | Minimal | Medium | Severe | Compliance Audit | 6/10/2019 to 8/8/2019 | 2020-01-01 | 2020-03-31 | 1/13/2023 (Expected Completion Date) | TBD | Texas RE determined Oncor was noncompliant with IRO-010-2 R3. Specifically, Oncor failed to satisfy the obligations of its Reliability Coordinator’s (RC’s) documented data specification. The RC requires that 92% of telemetry deemed important by the RC achieve a quarterly reliability of 90%. Texas RE determined that Oncor failed to meet the telemetry reliability criteria for important telemetry for the fourth quarter of 2019, with 89% of important telemetry achieving the RC's quarterly reliability requirements. Oncor ended this instance of noncompliance by achieving the reliability criteria for important telemetry for the first quarter of 2020. The root cause of this noncompliance is Oncor’s use of analog communications technology, which is not adequately supported by Oncor’s telecommunications providers, to provide connectivity to its telemetry devices. This noncompliance started on January 1, 2020, which is the day after the end of the fourth quarter of 2019, and ended on March 31, 2020, which is the last day of the first quarter of 2020. | This noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk of this noncompliance is that Oncor’s RC had decreased situational awareness due to the incorrect and missing telemetry data and a reduction in the capability of the RC’s state estimator to handle the loss of other telemetry points. This is compounded by Oncor’s status as the largest single provider of important telemetry points to its RC, providing 28% of the important telemetry points received by the RC. The risk is lessened by several factors. First, Oncor still had 89% of important telemetry achieve the RC’s quarterly reliability requirements, relatively close to the requirement that 92% of all telemetry achieve the RC’s quarterly reliability requirements. Second, given its role in the ERCOT Interconnection, Oncor communicates with RC personnel on a daily basis. Had a significant issue occurred that impacted overall system operations, Oncor and RC personnel could have quickly coordinated a response. Third, RC operator logs during the duration of the noncompliance did not reveal any evidence that the telemetry failures impacted the RC’s Network Security Analysis or caused invalid State Estimator solutions. Fourth, Oncor’s work with its current communications provider to maintain its existing communications links as much as possible while they are awaiting replacement also reduces the risk, as Oncor maintains a SCADA ticketing system for logging telemetry issues and tracking its coordination with its current communications providers while it works to ensure issues with its existing communications links are addressed in a timely fashion. Finally, the risk is further reduced by Oncor’s internal process for reviewing and addressing the monthly telemetry statistics report from its RC, along with Oncor’s automated tool that alerts Oncor personnel if any important telemetry point has an abnormal quality code for 30 minutes, indicating the presence of internal controls. No harm is known to have occurred. | To mitigate this noncompliance, Oncor has or will perform the following actions: 1) ended the noncompliance by achieving the reliability criteria required by its RC; and 2) prevent reoccurrence by replacing its analog copper-based communications technology, which was provided through several different telecommunications providers, with an updated, more reliable solution that uses communication technology based primarily on Oncor-owned fiber, microwave, and radio frequency-based data links as well as cellular data links, which rely on outside service providers, in instances that are currently out of range of those private solutions. | Texas RE reviewed Oncor’s internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered Oncor’s IRO-010-2 R3 compliance history in determining the disposition track. Texas RE determined that Oncor’s compliance history should not serve as a basis for aggravating the risk due to the differing nature and root cause of the instant noncompliance compared to the compliance history. NERC Violation ID TRE2016015568 was the only potentially relevant compliance history that was located. TRE2016015568 involved a failure to provide accurate information to the RC, and had a root cause of insufficient processes for ensuring the Oncor group tasked with providing that information to Oncor’s RC adequately tracked and verified changes to that information. This is in contrast to the instant noncompliance of failure to maintain adequately reliable telemetry links with the RC due to a reliance on analog communications technology. Although the violation resolved by this agreement involves a minimal risk issue that would otherwise be eligible for a streamlined disposition, Texas RE determined that such streamlined treatment was not appropriate because the expected completion date for the mitigation activities Oncor is undertaking to prevent reoccurrence of this violation will be more than 12 months after the posting of the disposition.
2021-08-31 | NOC-2724 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | GO | Settlement Agreement | Admits | $49,000 (for WECC2020023450 and WECC2020023451) | WECC2020023450 | PRC-019-2 | R1 | Moderate | Medium | Lower | Self-Report | 2020-05-21 | 2016-07-01 | 2020-10-23 | 2020-10-23 | TBD | On May 21, 2020, FEUS submitted a Self-Report stating it was noncompliant with PRC-019-2 R1. Specifically, FEUS did not coordinate an automatic voltage regulator (AVR) with primary and backup Protection System devices for a 104 MVA combined-cycle generating unit. FEUS did not set the in-service limiters to operate before the Protection System of the applicable unit in order to avoid disconnecting the generator unnecessarily. The applicable in-service Protection System devices were not set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. The root cause was attributed to FEUS not reviewing the quality of the settings recommended by a third-party contractor. Thus, when FEUS implemented the recommended settings, the Protection System devices were not coordinated to isolate or de-energize the combined cycle facility to limit the extent of damage when operating conditions exceeded equipment capabilities or stability limits. This violation began on July 1, 2016, when the Standard became mandatory and enforceable, and ended on October 23, 2020, when FEUS adjusted the AVR over-excitation limiter (OEL) and over-excitation monitor (OEM) settings for its 104 MVA combined-cycle generating unit. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, FEUS failed to coordinate the voltage regulating system controls, (including in-service limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions, for one 104 MVA generating unit, as required by PRC-019-2 R1; R1.1; R1.1.2. Such failure could have resulted in equipment damage to FEUS’s combined cycle generation facility due to the applicable Protection System devices not isolating or de-energizing the Facilities when operating conditions exceeded equipment capabilities or stability limits. However, as compensation, the size of the 104 MVA unit reduced the likelihood that failing to coordinate the AVR and Protection System devices would have had a significant impact on the reliability of the BPS. Furthermore, though FEUS did not coordinate the Protection System devices to operate to isolate or de-energize the unit to limit the extent of damage, it did set the AVR to operate before the unit’s Protection System devices to prevent unnecessarily disconnecting the unit, as required by PRC-019-2 R1.1.1. In addition, FEUS confirmed that it has suffered no equipment damage as a result of the instant violation. | To mitigate this violation, FEUS has: 1) contracted two third-party contractors to provide a peer review process and facilitated the review of the settings between the contractors to discuss any differences between the studies; 2) made required setting changes to the OEL and OEM; specifically, FEUS adjusted the AVR OEL and OEM settings to prevent excessive field current from causing thermal damage to the rotor of the steam and combustion turbines and adjust the V/Hz limiters to fall within the transformer and generator V/Hz capability curves; 3) implemented a new plan for hiring third-party contractors including: a) hiring reputable contractors who have experience in the services requested by examining one or more of the following company attributes: years of experience, internal peer review processes; b) if capable, FEUS engineers will review the recommended settings; c) if a potential noncompliance is suggested by the third-party contractor or the review by FEUS engineers shows concerns, another third-party contractor may be hired to provide a more thorough peer review process; and d) concerns will be brought to the third-party contractor's attention and discussed for clarity and possible recalculation. | WECC did not apply mitigating credit for FEUS’s Internal Compliance Program (ICP). Although FEUS did have a documented ICP, WECC determined that it was not effective in remediating the violations herein during previous mitigation efforts. FEUS’s relevant compliance history regarding PRC-019-2 R1 and PRC-024-2 were not remediated. The violations herein demonstrate that some of the generating units that were involved in the previous instances of noncompliance and are involved in the instant violation. Furthermore, though the previous mitigation has thus far prevented new, distinct instances from occurring, the previous remediation and mitigation efforts were not effective in ending the original instance of noncompliance with PRC-019-2 and PRC-024-2.
2021-08-31 | NOC-2724 | Western Electricity Coordinating Council (WECC) | Farmington Electric Utility System (FEUS) | NCR05155 | GO | Settlement Agreement | Admits | $49,000 (for WECC2020023450 and WECC2020023451) | WECC2020023451 | PRC-024-2 | R2 | Moderate | Medium | Severe | Self-Report | 2020-05-21 | 2016-07-01 | 2020-10-23 | 2020-10-23 | TBD | On May 21, 2020, FEUS submitted a Self-Report stating, as a GO, it was noncompliant with PRC-024-2 R2. Specifically, FEUS did not properly set its undervoltage protective relaying setpoints for a 104 MVA combined-cycle generating unit not to trip within the “no trip zone,” as required by Attachment 2 of the Standard. The root cause was attributed to FEUS not reviewing the quality of the settings recommended by a third-party contractor. The third-party contractor used the incorrect Point of Interconnection (POI) leading to incorrect setting recommendations. Thus, when FEUS implemented the recommended settings, the voltage protective relays were not set not to trip within the “no trip zone.” This violation issue began on July 1, 2016, when the Standard became mandatory and enforceable, and ended on October 23, 2020, when FEUS adjusted the undervoltage relay setpoints for its 104 MVA combined-cycle generating unit. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, FEUS failed to set its protective relaying such that the generator voltage protective relaying did not trip the applicable generating unit as a result of a voltage excursion (at the point of interconnection) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. Such failure could have resulted in deteriorated system response following a voltage excursion which could subsequently cause equipment damage, cascading, system instability, or system separation. However, as compensation, the size of the 104 MVA unit reduced the likelihood that tripping within the “no trip zone” during a voltage excursion would have had a significant impact on the reliability of the BPS. Additionally, all the unit’s PRC-024-2 R2 overvoltage relay setpoints were set in accordance with the Standard, therefore the generating unit would have appropriately ridden through an overvoltage excursion. In addition, FEUS confirmed that it has suffered no equipment damage as a result of the instant violation. | To mitigate this violation, FEUS has: 1) contracted two third-party contractors to provide a peer review process and facilitated the review of the settings between the contractors to discuss any differences between the studies; 2) set its undervoltage relays not to trip in the “no trip zone” specifically, FEUS adjusted the undervoltage relay setpoints for the primary relay to 2 seconds/0.7113 pu from 2 seconds/0.75 pu and to 3 seconds/0.8443 pu from 0.90 pu; for the backup relay to disable one level of trip settings and change other settings to 2 seconds/0.713 pu from 2 seconds/0.75 pu, to 0.30 seconds/0.6261 pu from 0.30 seconds/0.65 pu, and to enable an additional level of tripping at 0.15 seconds/0.4348 pu; for another primary relay to 0.15 seconds/0.4368 pu from 0.15 seconds/0.45 pu, to 0.3 seconds/0.622 pu from 0.3 seconds/0.65 pu, to 2 seconds/0.7113 pu from 2 seconds/0.75 pu, and to 3 seconds/0.8443 pu from 3 seconds/0.90 pu; and for its backup relay to disable one level of trip settings and change other settings to 2 seconds/0.7079 pu from 2 seconds/0.75 pu, to 0.5 seconds/0.6175 pu from 0.3 seconds/0.65 pu, and to enable an additional level of tripping at 0.15 seconds/0.4368 pu; 3) implemented new plan for hiring third-party contractors including: a) hiring reputable contractors who have experience in the services requested by examining one or more of the following company attributes: years of experience, internal peer review processes; b) if capable, FEUS engineers will review the recommended settings; c) if a potential noncompliance is suggested by the third-party contractor or the review by FEUS engineers shows concerns, another third-party contractor may be hired to provide a more thorough peer review process; and d) concerns will be brought to the third-party contractor's attention and discussed for clarity and possible recalculation. | WECC did not apply mitigating credit for FEUS’s Internal Compliance Program (ICP). Although FEUS did have a documented ICP, WECC determined that it was not effective in remediating the violations herein during previous mitigation efforts. FEUS’s relevant compliance history regarding PRC-019-2 R1 and PRC-024-2 were not remediated. The violations herein demonstrate that some of the generating units that were involved in the previous instances of noncompliance and are involved in the instant violation. Furthermore, though the previous mitigation has thus far prevented new, distinct instances from occurring, the previous remediation and mitigation efforts were not effective in ending the original instance of noncompliance with PRC-019-2 and PRC-024-2.
2021-08-31 | NOC-2727 | Western Electricity Coordinating Council (WECC) | US Bureau of Reclamation (USBR) | NCR05441 | GOP | Settlement Agreement | Admits | No Penalty (for WECC2018020569, WECC2018020042, and WECC2019022404) | WECC2018020569 | PRC-001-1.1(ii) | R3, R3.1 | Minimal | High | Moderate | Self-Report | 2018-10-19 | 2018-03-16 | 2018-05-25 | 2018-06-04 | 2019-04-25 | USBR submitted a Self-Report stating it was in potential noncompliance with PRC-001-1.1(ii) R3. Specifically, on April 26, 2018 during an internal audit, USBR discovered it did not coordinate with its Transmission Operator (TOP) and Balancing Authority (BA), on two separate occasions, its protective system changes related to one of its generating Facilities comprised of two generating units with a combined capacity of 184 MVA. These instances occurred on March 16, 2018 and April 16, 2018, when USBR made changes to two relay elements on the two affected generating units. The root cause of the violation was attributed to USBR’s job performance standards not being adequately defined. Specifically, USBR’s business practices did not contain a repeatable process for relay setting changes and notification with the TOP and BA with enough task specificity and accountability. This noncompliance began on March 16, 2018, when USBR first failed to coordinate its protective system changes, and ended on May 25, 2018, when it revised its Memorandum of Understanding (MOU) with its TOP and BA to reflect that the relay elements in scope no longer need to be coordinated in the future. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, USBR failed to coordinate changes to two relay elements on two generating units, with its TOP and BA, as required by PRC-001-1.1(ii) R3. In this instance, failure to coordinate relay changes with the TOP and BA would have had no effect to the TOP or BA, as the relay elements at issue only affected protection for the generator and exciter. Additionally, the relay elements did not affect how the TOP or BA would set its own protection relay settings. As such, coordinating with the TOP and BA would have been for informational purposes only, thereby reducing the risk to the BPS. | To mitigate this violation, USBR has or will perform the following actions: 1) updated its MOU with its TOP and BA and updated the list of relays that needed coordination; 2) modified its business practice to clearly define processes that assign specific task responsibilities, deadlines, and safeguards to prevent future noncompliance; 3) modified its PRC-001 relay settings change management process, detailing the steps that needed to be followed when making protection system changes, before the units are put back online; and 4) developed a checklist to incorporate business practice processes and document task completion. | On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. USBR is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation. WECC considered USBR's PRC-001-1.1(ii) R3 compliance history in determining the disposition track. Additionally, USBR's violation duration is beyond the Operations Planning violation time horizon expectation for remediation.
2021-08-31 | NOC-2727 | Western Electricity Coordinating Council (WECC) | US Bureau of Reclamation (USBR) | NCR05441 | GO, TO | Settlement Agreement | Admits | No Penalty (for WECC2018020569, WECC2018020042, and WECC2019022404) | WECC2018020042 | PRC-005-1.1b | R2, R2.1 | Moderate | High | Lower | Self-Report | 2018-07-18 | 2015-04-01 | 2016-05-21 | 2018-10-03 | 2019-02-06 | USBR submitted Self-Report stating it was in potential noncompliance with PRC-005-1.1b R2. Specifically, during an internal review, USBR discovered it did not establish evidence that its Protection System devices were maintained and tested within the defined intervals of its Protection System Maintenance and Testing Program (PSMP), for one lockout relay at its 1,125 MVA total capacity hydroelectric plant. USBR had implemented a quality control review process for tracking the completion of its maintenance tasks and to ensure consistency as personnel changes occurred. However, in this instance, a new employee inadvertently changed the completion date for the relay in scope which resulted in the tracking tool having the incorrect next test date. The root cause of this violation was attributed to a less than adequate check of the work of the new employee. Specifically, the last test date for the relay was entered as February 12, 2011 instead of the actual testing date of September 28, 2008. As such, USBR missed the 6.5 year maintenance and testing interval date of March 31, 2015, as specified in its PSMP. This noncompliance began on April 1, 2015, when USBR missed the maintenance and testing interval for one lockout relay, and ended on May 21, 2016, when USBR completed the maintenance and testing for the lockout relay. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS, due to the overlap in PRC-005 violation duration, the length of the overall instant violation and the same root cause. In this instance, USBR failed to provide evidence that one lockout relay at its 1,125 MVA hydroelectric plant was maintained and tested within the defined intervals of USBR’s PSMP, as required by PRC-005-1.1b R2. Such failure could have resulted in a Misoperation that could have caused the four 13.8 kV generator unit breakers to open, which could have removed 625 MW from Bulk Electric System availability. However, as compensation, the affected lockout relay had no Misoperations during the time of the violations, thereby reducing the risk to the BPS. Additionally, the 1,125 MVA hydroelectric plant involved was not running at full capacity through the duration of the violation, further reducing the risk. | To mitigate this violation, USBR has or will perform the following actions: 1) performed maintenance testing on the one lockout relay; 2) reduced the number of personnel with the capability to make changes in the maintenance tracking tool to only those that are appropriately trained; and 3) implemented a quality control review process for tracking the completion of maintenance tasks. | On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. USBR is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation. WECC considered USBR's PRC-005-1.1b R2 compliance history in determining the disposition track. Additionally, USBR violation duration is beyond the Long Term Planning violation time horizon expectation for remediation. Furthermore, the PRC-005 violations’ have overlapping root causes for the same Standard and Requirement.
2021-08-31 | NOC-2727 | Western Electricity Coordinating Council (WECC) | US Bureau of Reclamation (USBR) | NCR05441 | GO, TO | Settlement Agreement | Admits | No Penalty (for WECC2018020569, WECC2018020042, and WECC2019022404) | WECC2019022404 | PRC-005-1.1b | R2, R2.1 | Moderate | Lower | Lower | Self-Report | 2019-10-18 | 2014-04-01 | 2018-08-28 | 2019-06-12 | 2021-03-02 | USBR submitted Self-Report stating it was in potential noncompliance with PRC-005-1.1b R2. USBR discovered it did not establish evidence that two Protection System microprocessor relays at its 115kV switchyard were maintained and tested within the defined intervals of its PSMP. USBR had implemented a quality control review process for tracking the completion of its maintenance tasks and to ensure consistency as personnel changes occurred. However, in this instance, the frequency of maintenance intervals for the relays involved was erroneously entered into the tracking system which resulted in the tracking tool having the incorrect next test date. The root cause of this violation was attributed to a less than adequate check of the work of the new employee. As such, USBR missed the 5.5 year maintenance and testing interval date of March 31, 2014, as specified in its PSMP. This noncompliance began on April 1, 2014, when USBR missed the maintenance and testing interval for the two microprocessor relays, and ended on August 28, 2018, when USBR completed testing for the two microprocessor relays as specified by its PSMP. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS, due to the overlap in PRC-005 violation duration, the length of the overall instant violation and the same root cause. In this instance, USBR failed to provide evidence that two microprocessor relays at its 115kV switchyard were maintained and tested within the defined intervals of USBR’s PSMP, as required by PRC-005-1.1b R2. Such failure could have resulted in a Misoperation of the relays that could have caused the 115kV main bus to trip. However, as compensation, the affected microprocessor relays had no Misoperations during the time of the violations, thereby reducing the risk to the BPS. | To mitigate this violation, USBR has or will perform the following actions: 1) performed maintenance testing on the two microprocessor relays; 2) updated the interval for maintenance and testing of microprocessor relays to be completed one year prior to what is specified in its PSMP; 3) reduced the number of personnel with the capability to make changes in the maintenance tracking tool to only those that are appropriately trained; and 4) implemented a quality control review process for tracking the completion of maintenance tasks. | On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as WECC, could not impose monetary penalties against federal governmental entities such as SWPA. USBR is a federal governmental entity, and WECC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, WECC has assessed no monetary penalty for this violation. WECC considered USBR's PRC-005-1.1b R2 compliance history in determining the disposition track. Additionally, USBR violation duration is beyond the Long Term Planning violation time horizon expectation for remediation. Furthermore, the PRC-005 violations’ have overlapping root causes for the same Standard and Requirement.
2021-08-31 | NOC-2728 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | TOP | Settlement Agreement | Admits | $85,000 (for WECC2018020295, WECC2018020296, WECC2018020302) | WECC2018020295 | COM-002-4 | R1 | Moderate | Lower | Severe | Compliance Audit | 8/6/2018 to 8/17/2018 | 2016-07-01 | 2021-01-14 | 2021-01-29 | 2021-04-12 | During a Compliance Audit conducted from August 6, 2018 through August 17, 2018, WECC determined that SCEC, as a Transmission Operator, was in potential noncompliance with COM-002-4 R1. Specifically, WECC discovered that SCEC had a Grid Control Center (GCC) Transmission Dispatcher that issued and received Operating Instructions to the Switching Center Operators or to field personnel. SCEC’s Switching Center Operators also received Operating Instructions from the GCC Transmission Dispatcher and issued Operating Instructions for switching to SCEC’s field personnel. SCEC did not identify and include, within its documented communications protocols, Switching Center Operators or field personnel as individuals that could issue and/or receive Operating Instructions. In addition, the documented communications protocol did not require all of its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct or request that the issuer reissue the Operating Instruction, per COM-002-4 R1.3; nor did SCEC specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction, per COM-002-4 R1.6. The root cause of this issue was attributed to SCEC’s misinterpretation of the Standard Requirement. SCEC did not correctly define operating personnel that issue and receive Operating Instructions in its documented communications protocols. This violation began on July 1, 2016, when the Standard became mandatory and enforceable, and ended on January 14, 2021, when SCEC updated its GCC Communication Protocols for issuing and receiving Operating Instructions with an accurate definition of operating personnel. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, SCEC failed to appropriately develop documented communications protocols for its operating personnel that issue and receive Operating Instructions, as required by COM-002-4 R1, affecting nearly 900 employees. Specifically, the documented communications protocol failed to require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct or request that the issuer reissue the Operating Instruction, per COM-002-4 R 1.3; nor did SCEC specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction, per COM-002-4 R 1.6. Failure to include all criteria defined in COM-002-4 R1 could have resulted in a miscommunication between SCEC’s GCC Transmission Dispatchers, Switching Center Operators and field personnel to the issuer or receiver of their Operating Instructions; leading to an action or inaction that could have been harmful to the BPS. However, as compensation, SCEC had separate documented communication protocols that included three-part communications. In addition, SCEC field personnel were trained on three-part communication in a basic operations course; the training focused on receiving the Operating Instructions, not issuing them. Similarly, SCEC had protocols that specified the nomenclature to be used for Transmission interface elements and Facilities, but its protocol for the Switching Center Operations did not specify or reference these documents. | To mitigate this violation, SCEC has performed the following actions: 1) updated its GCC Communication Protocols for issuing and receiving Operating Instructions to include: i. all required operating personnel, with expanded definition to include all personnel who issue and receive Operating Instructions; and ii. specific nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. 2) developed a process designed to identify operating personnel and develop, deliver and track training associated with the documented communications protocols required by the specific requirements of COM-002-4 R1, R2 and R3. This process included roles, responsibilities, as well as future employee and effectiveness assessment and tracking methodologies. | WECC reviewed SCEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination because the ICP was not effective in establishing internal controls to detect the instances of noncompliance with COM-002-4. SCEC's failure of COM-002-4 was considered a systemic problem, given the number of affected individuals, duration of the issue, and number of Requirements violated. WECC considered SCEC's compliance history and determined there were no relevant instances of noncompliance.
2021-08-31 | NOC-2728 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | TOP | Settlement Agreement | Admits | $85,000 (for WECC2018020295, WECC2018020296, WECC2018020302) | WECC2018020296 | COM-002-4 | R2 | Moderate | Lower | High | Compliance Audit | 8/6/2018 to 8/17/2018 | 2016-07-01 | 2020-12-18 | 2021-01-29 | 2021-04-12 | During a Compliance Audit conducted from August 6, 2018 through August 17, 2018, WECC determined that SCEC, as a Transmission Operator, was in potential noncompliance with COM-002-4 R2. Specifically, SCEC had a Grid Control Center (GCC) with personnel responsible for Real-time operations, specifically the GCC Transmission Dispatchers, System Operators and Power System Operations Specialists. SCEC conducted initial training for its 24 GCC Transmission Dispatchers responsible for the Real-time operation regarding the documented communications protocols developed in R1, prior to those individuals issuing an Operating Instruction, but did not conduct the required initial training for its System Operators and Power System Operations Specialists. The root cause of the issue was attributed to SCEC’s misinterpretation of the definition of operating personnel. Specifically, SCEC did not correctly define operating personnel responsible for the Real-time operation of the interconnected Bulk Electric System (BES). SCEC previously trained approximately 24 GCC Transmission Dispatchers but based on its new understanding of COM-002-4 R2 an additional 153 operating personnel were trained for issuing and or receiving Operating Instructions in any situation, as required by the Standard. This violation began on July 1, 2016, when the Standard became mandatory and enforceable and ended on December 18, 2020 when all affected operating personnel received the required initial training. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, SCEC failed to conduct initial training for its System Operators and Power System Operations Specialists responsible for the Real-time operation of the interconnected BES regarding the documented communications protocols developed in Requirement R1, prior to that individual operator issuing an Operating Instruction, as required by COM-002-4 R2. Failure to conduct initial training for operating personnel responsible for the Real-time operation of the interconnected BPS regarding the communication protocols developed in R1 could have resulted in a misunderstanding of instructions by the issuer or receiver of Real-time operating instructions, which could have led to an action or inaction that could have been harmful to the BPS. However, as compensation, SCEC Switching Center Operators were trained on three-part communication in a basic operations course, but the training did not use the correct documented communications protocol and focused on receiving the Operating Instructions, not issuing them, thereby reducing the risk. In addition, the 24 GCC Transmission Dispatchers that performed the majority of the Operating Instructions had been trained in accordance with the Standard. As well, SCEC had communications manuals that clearly stated the objectives from the documented communications protocol. | To mitigate this violation, SCEC has performed the following actions: 1) developed high level process designed to identify operating personnel and develop, deliver and track training associated with the documented communications protocols required by the specific requirements of COM-002-4 R1, R2 and R3. This process included roles, responsibilities, as well as future employee and effectiveness assessment and tracking methodologies; 2) built and tested processes for identifying operating personnel and tracking training by developing and finalizing functional rolls, responsibilities, processes, procedures, and controls; and 3) updated and completed end user training material by developing an updated communication protocol training for all in scope operating personnel; 4) updated its communications protocol to include all required operating personnel, with expanded definition to include all personnel who issue and receive Operating Instructions; and 5) conducted initial training for each of its operating personnel responsible for the Real-time operation on its documented communications protocols. | WECC reviewed SCEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination because the ICP was not effective in establishing internal controls to detect the instances of noncompliance with COM-002-4. SCEC's failure of COM-002-4 was considered a systemic problem, given the number of affected individuals, duration of the issue, and number of Requirements violated. WECC considered SCEC's compliance history and determined there were no relevant instances of noncompliance.
2021-08-31 | NOC-2728 | Western Electricity Coordinating Council (WECC) | Southern California Edison Company (SCEC) | NCR05398 | DP, GOP | Settlement Agreement | Admits | $85,000 (for WECC2018020295, WECC2018020296, WECC2018020302) | WECC2018020302 | COM-002-4 | R3 | Moderate | Lower | High | Compliance Audit | 8/6/2018 to 8/17/2018 | 2016-07-01 | 2020-12-28 | 2021-01-29 | 2021-04-12 | During a Compliance Audit conducted from August 6, 2018 through August 17, 2018, WECC determined that SCEC, as a Distribution Provider and Generator Operator, was in potential noncompliance with COM-002-4 R3. Specifically, at the time of the audit, SCEC had 24 Grid Control Center (GCC) Transmission Dispatchers that issued and received Operating Instructions to the Switching Center Operators or to SCEC field personnel. SCEC’s Switching Center Operators also receive Operating Instructions from the GCC Transmission Dispatcher and issue Operating Instructions for switching to SCEC’s field personnel. SCEC did not correctly define its operating personnel that issue and receive Operating Instructions and therefore did not conduct initial training for all operating personnel who could receive Operating Instructions on receiving an Operating Instructions. Specifically, SCEC did not conduct the required initial training for Switching Center Operators, SCEC Transmission and Distribution field personnel, Power Supply personnel and generator unit operators. The root cause of the issue was attributed to SCEC’s misinterpretation of the definition of operating personnel. SCEC previously trained approximately 24 GCC Transmission Dispatchers, and 697 additional personnel who could possibly issue or receive Operating Instructions in any situation were trained, as a result of this issue. This violation began on July 1, 2016, when the Standard became mandatory and enforceable and ended on December 18, 2020 when all affected operating personnel received the required initial training. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, SCEC failed to conduct initial training for its field personnel and generator unit operators who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or request that the issuer reissue the Operating Instruction, as required by COM-002-4 R3. Failure to conduct three-part communication training for operating personnel who can receive Operating Instructions could have resulted in a misunderstanding of instructions, which could have led to an action or inaction that could have been harmful to the BPS. However, as compensation, the 24 GCC Transmission Dispatchers that were responsible for a majority of the issuing and receiving of the Operating Instructions had been trained according to the requirements of the Standard. In addition, all SCEC field personnel and personnel mentioned herein were trained on three-part communication in a basic operations course, but the training did not use the correct documented communications protocol and the training focused on receiving the Operating Instructions, not issuing them, thereby reducing the risk. As well, SCEC had a power point of the training for generating unit operators but was not able to provide evidence regarding which personnel were trained or when, thus the generator unit operators had received minimal training, thereby reducing the risk to the BPS. | To mitigate this violation, SCEC has performed the following actions: 1) developed a process designed to identify operating personnel and develop, deliver and track training associated with the documented communications protocols required by the specific requirements of COM-002-4 R1, R2 and R3. This process included roles, responsibilities, as well as future employee and effectiveness assessment and tracking methodologies; 2) built and tested processes for identifying operating personnel and tracking training by developing and finalizing functional rolls, responsibilities, processes, procedures, and controls; 3) updated and completed end user training material by developing an updated communication protocol training for all in scope operating personnel; 4) updated its communications protocol to include all required operating personnel, with expanded definition to include all personnel who issue and receive Operating Instructions; and 5) conducted initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction. | WECC reviewed SCEC's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination because the ICP was not effective in establishing internal controls to detect the instances of noncompliance with COM-002-4. SCEC's failure of COM-002-4 was considered a systemic problem, given the number of affected individuals, duration of the issue, and number of Requirements violated. WECC considered SCEC's compliance history and determined there were no relevant instances of noncompliance.
2021-04-29 | NOC-2710 | Western Electricity Coordinating Council (WECC) | Valley Electric Association, Inc. (VEA) | NCR05447 | TO | Settlement Agreement | Admits | 50000 | WECC2019021035 | FAC-008-3 | R6. | Moderate | Medium | High | Compliance Audit | 2019-01-31 | 2013-01-01 | Ongoing | 2021-05-01 | TBD | During a Compliance Audit conducted January 21, 2019 through January 31, 2019, WECC determined VEA, as a Transmission Owner, had a potential noncompliance with FAC-008-3 R6. Specifically, seven of VEA’s 13 138 transmission Facilities were sampled for a detailed review. VEA provided the requested Facility Ratings database spreadsheet. During their review, WECC Auditors found discrepancies across the sampled transmission line Facilities. One of the 138kV transmission lines had three different Facility Ratings, which included the Facility Rating from VEA’s original database spreadsheet (196 MVA), one Facility Rating from a data request (143 MVA), and one Facility Rating from the WECC base case (191 MVA). VEA verified that the element causing the discrepancy at one switching station was owned by Department of Energy (DOE) and DOE had released a new rating for the switch, but the ratings from DOE engineering drawings were not communicated internally at VEA or used to update the Facility Rating. In addition, several circuit breakers and disconnect switches were missing from the database that were on the one-line diagrams, and elements that were in the database were not on the one-line diagrams. As well, conductor jumper ratings were not included in the database for one substation. Bus work was not included for two substations but were added to the database during the audit. VEA provided a revised database during the audit with the noted corrections herein, however the revised database was compared to the one-line diagrams dated November 20, 2018 and CTs were missing from the revised database. VEA later provided the CTs for each circuit breaker in subsequent data requests. The root cause of the violation was attributed to an incomplete understanding of the Standard as well of a lack of formal written and verbal internal procedures, communication, training and coordination between internal departments. This violation began on January 1, 2013, when the Standard became mandatory and enforceable, and will end on May 1, 2021, when mitigation is complete. | This violation posed a moderate risk and did not pose a serious and substantial risk to the reliability of the Bulk Power System (BPS). In this instance, VEA failed to have Facility Ratings for its nine solely and three jointly owned Facilities that were consistent with the associated Facility Ratings Methodology (FRM), for determining its Facility Ratings, as required by FAC-008-3 R6. VEA operated 191 miles of 138 kV transmission lines and 164 miles of 230 kV transmission lines mainly to serve VEA’s 130 MW load. VEA owned the 138 kV transmission lines and another Transmission Owner (TO) owned the 230 kV transmission lines. VEA had three jointly owned Facilities, one with an entity at 230 kV and two with an entity at 138 kV and 230 kV. Such failure could have resulted in operating the transmission Facilities above normal, emergency or load-shed System Operating Limits (SOLs), potentially resulting in permanent or premature damage to the equipment if SOLs were exceeded. VEA did not implement effective detective or preventative controls. However, as compensation, VEA’s FRM adhered to the requirements of the Standard, including coordination with its joint Facility owners, thus reducing the risk to the BPS. In addition, VEA’s 130MW of load would not have a significant impact on the BPS, thus reducing the risk. VEA’s mitigation is not yet complete. VEA will complete the following measures to reduce failure points and reduce the risk to the BPS, based on recommendation by WECC Auditors: 1) schedule weekly meetings with its Compliance Team and its Engineering and Operations staff. During these meetings, VEA reviews planned system changes to identify potential changes to Facility Ratings; 2) update the Facility Ratings spreadsheet timely during mitigation upon changes to equipment or infrastructure that could change Facility Ratings or evidence of ratings; 3) establish a schedule to coordinate with joint owners on Facility and equipment ratings to ensure that the Facility ratings for jointly owned Facilities are reviewed on a regular schedule; and 4) update its FRM to ensure that it accurately generates the equipment and Facility Ratings; this includes clarifying confusing language and spelling out specific steps that may otherwise have been assumed. | To mitigate this violation, VEA has performed the following actions: 1) gathered evidence for equipment rating sources; 2) requested equipment ratings from joint owners; 3) completed updated Facility Ratings spreadsheet for VEA Facilities; and 4) confirm VEA equipment ratings and supporting evidence. To remediate and mitigate this violation, VEA will: 1) identify and resolve inconsistencies with joint owners; 2) update its FRM, as necessary; 3) coordinate final Facility Ratings with joint owners; 4) update VEA documentation with Facility Ratings; 5) organize and store all evidence; 6) schedule annual review of FRM and Facility Ratings spreadsheet; and 7) develop Facility Ratings training materials and train VEA engineering. | WECC reviewed VEA's Internal Compliance Program (ICP) and considered it to be a neutral factor in the penalty determination. Although VEA does have a documented ICP, WECC determined that it was not effective in preventing or detecting this violation. WECC provided credit for VEA's cooperation and for agreeing to settle and admit to the violation. WECC determined that VEA's compliance history should not serve as a basis for aggravating the penalty because the previous violation was a result of the NERC Standards becoming mandatory and enforceable and did not indicate a systemic issue or programmatic failure.
2021-04-29 | NOC-2711 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | GOP | Settlement Agreement | Neither Admits nor Denies | No Penalty | SERC2019021816 | PRC-001-1 | R2; R2.1 | Moderate | Medium | Severe | Self-Report | 2019-07-12 | 2012-10-19 | 2019-04-17 | 2021-03-31 | TBD | On July 12, 2019, TVA submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of PRC-001-1 R2.1. TVA failed to notify its Transmission Operator (TOP) and Host Balancing Authority (BA) of a relay failure for a single 500 kV relay. SERC determined this violation spanned to TOP-003-3 R5. On April 15, 2019 while troubleshooting a ground at the Brownsville Combustion Turbine (CT) plant, TVA personnel identified labels on the 500 KV main transformer multifunction relay that said “Failed”. These “Failed” labels were dated 2012 and 2017. TVA analyzed the October 19, 2012 and April 20, 2017 preventative maintenance (PM) information and identified the relay data indicated an A phase sensing failure. On April 17, 2019 , TVA made notifications to the TOP and BA. During both the October 19, 2012 and April 20, 2017 calibration and functional testing of the 500 kV main transformer multifunction relay at the Brownsville CT plant, the relay calibration identified an A phase sensing failure. TVA personnel flagged the relay for repair or replacement in both instances. On both occasions, TVA failed to repair or replace the relay. PRC-001-1 R2.1 was the enforceable Standard at the time of the October 19, 2012 occurrence. PRC-001-1 R2.1 requires the GOP to notify the TOP and BA if a protective relay or equipment failure reduces system reliability, and take corrective action as soon as possible. TOP-003-3 R5 was the enforceable Standard at the time of the April 20, 2017 occurrence. TOP-003-3 R5 requires the GOP to satisfy the obligations of the documented specifications provided by the TOP and BA as specified in TOP-003-3 R2, R3, and R4. The specification provided by the TOP required TVA to notify the TOP of current Protection System and Remedial Action Scheme status or degradation that impact System reliability in real-time in a phone call and followed by a submittal to the Consolidated Outage Portal. Since TVA did not notify the TOP of the degradation which would impact System reliability in real-time, the TOP, in turn, was unable to pass the information along to the BA, as required by the specification provided by the BA. The 500 kV main transformer multifunction relay at the Brownsville CT plant is a redundant relay and is associated with Brownsville CT 3 and Brownsville CT 4, each a 135 MW generator. The TVA TOP does not allow TVA to run these units without redundant relay protection. However, TVA failed to meet its TOP’s redundant relay protection requirement in this case. Brownsville CT 3 had a 2018 annual capacity factor of 7% and Brownsville CT 4 had a 2018 annual capacity factor of 5%. The cause of this violation was management oversight. TVA management failed to implement a documented process and internal controls to ensure the PM reports were adequately reviewed and required action was taken. The relay failure documented on the PM reports should have triggered TVA to notify its TOP and Host BA, and then either repair or replace the relay. In both 2012 and 2017, the relay failure was documented in the PM reports. For the 2012 package, the note was on page 131 of a 364 page document. For the 2017 package, the note was on page 249 of a 505 page document. TVA personnel overlooked the documented failed relay in both the 2012 report and the 2017 report. TVA did not have a documented procedure for this process at the time of the violation . TVA could not provide a response to explain how this failure could occur on the same relay, on two different occasions. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, TVA’s failure to notify the TOP and BA, and take corrective action to repair or replace a faulty relay could result in unplanned loss of generation, transmission, or load. TVA operated the Brownsville CT 3 and Brownsville CT 4 units without the TOP required redundant relay on the 500 kV main transformer from at least October 19, 2012 until April 17, 2019, and did not notify the TOP and BA until April 17, 2019. On two occasions, TVA failed to take action on the same defective relay which raises concerns as to the effectiveness of TVA’s review of maintenance and testing records. In addition, TVA completed an extent of condition review - for 243 of TVA’s 243 generating units (100%), TVA reviewed, verified, and documented the listed devices and either reported to SERC that such devices are in service with no known deficiencies that would prevent them from performing their intended function, or reported to SERC on deficiencies that were found and the status of work orders for reconciling the deficiencies. There were no significant deficiencies. | To mitigate this noncompliance, the entity has performed the following actions: 1) notified its TOP and BA of the relay failure affecting reliability; 2) replaced the failed relay; 3) updated its PRC-005 compliance procedure. TVA updated its PRC-005 compliance procedure to give the field services organization the exclusive action to be responsible for execution and review of PRC-005 Relay PM; 4) updated its evidence checklist to include a deficiency summary. This evidence checklist is a coversheet for persons performing Relay PMs to check that all requirements for the PM are met. TVA added a box to the checklist requesting that "For any unsatisfactory results or unresolved maintenance issues, document a brief description and the follow-up work order number(s) below:" TVA implemented this checklist and created a formal procedure for it; 5) updated its site notification matrix to include a notification to the reliability analysis group on a relay failure. The reliability analysis group performs relay analysis for the TVA TOP. Site notification matrices are internal documents that direct who to contact for particular events. For relay failures that compromise reliability, TVA added a telephone number for reliability analysis and the Transmission Operator and direction for the plants to call reliability analysis; 6) provided training on revised procedures; and 7) performed an extent-of-condition review to ensure there are no other instances of unresolved PM deficiencies and reporting findings to SERC. TVA used the lists of devices verified under its on-going PRC-005 verification efforts (SERC2015014914) to complete this extent-of-condition review to ensure all PRC-005 relays are correctly identified. For 243 of TVA’s 243 generating units (100%), TVA reviewed, verified, and documented the listed devices and either reported to SERC that such devices are in service with no known deficiencies that would prevent them from performing their intended function, or reported to SERC on deficiencies that were found and the status of work orders for reconciling the deficiencies. | SERC reviewed TVA's internal compliance program and considered it to be a neutral factor in determining the disposition. On August 22, 2014, in Southwestern Power Administration (SWPA) v. Federal Energy Regulatory Commission (FERC), the United States Court of Appeals for the District of Columbia Circuit unanimously ruled that FERC, and by extension, the North American Electric Reliability Corporation (NERC) and the Regional Entities it oversees, such as SERC, could not impose monetary penalties against federal governmental entities such as SWPA. TVA is a federal governmental entity, and SERC is bound to follow SWPA v. FERC in the resolution of this matter. Therefore, SERC has assessed no monetary penalty for this violation. SERC considered TVA’s compliance history and determined there were no relevant instances of noncompliance. SERC determined that sending a message via a settlement agreement is appropriate given the long duration of this violation and TVA’s failure on two occasions to take action on the same defective relay which raises concerns as to the effectiveness of TVA’s review of maintenance and testing records.
2020-12-30 | NOC-2688 | ReliabilityFirst Corporation (RF) | Michigan Power LP | NCR11409 | GOP | Settlement Agreement | Admits | 0 | RFC2019021748 | VAR-002-4.1 | R2 | Moderate | Medium | Severe | Spot Check | 2019-06-24 | 2017-11-01 | 2019-01-08 | 2019-01-08 | TBD | On June 24, 2019, ReliabilityFirst determined that the entity, as a Generator Operator (GOP), was in violation of VAR-002-4.1 R2 identified during a Spot-Check conducted from December 21, 2018 through January 4, 2019. While gathering evidence during the Spot-Check, the entity discovered that it failed to maintain the reactive power schedule as prescribed by its Transmission Operator, and also failed to satisfy the notification requirements from November 1, 2017, through the end of 2018. The entity entered into a reduced dispatch agreement (RDA) with Consumers Energy on November 1, 2017, which required the entity to reduce its output at various times, as directed by Consumers. Each day, Consumers would send a schedule to the entity’s control room to reduce MWs at certain hours throughout that day, and the entity was responsible for following that schedule. Although the entity reduced MWs according to the schedule, it did not reduce the output of MVARs as needed to maintain the reactive power schedule. In total, Consumers requested the entity to reduce its MWs 284 times, and the entity failed to maintain its voltage on 245 of those occasions. The root cause of this violation was the entity’s lack of awareness of the constant output of MVARs to the grid and the entity’s misunderstanding that its communications with Consumers regarding reduced generation output satisfied any notification requirements. This root cause involves the management practices of grid operations and workforce management, which includes providing training, education, and awareness to employees. This violation started on November 1, 2017, when the entity was required to comply with VAR-002-4.1 R2 and ended on January 8, 2019, when the entity completed its Mitigation Plan. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this noncompliance is a negative impact on the reliable operation of the BPS by allowing detrimental levels of generator voltage or reactive power output. This risk is not minimal in this case considering the length of time the issue persisted and the number of instances involved. The risk is not serious or substantial in this case based on the following factors. First, the facility at issue is a 125 MW unit, which reduces the potential impact of the noncompliance. Second, although the facility is a cogeneration facility with a high capacity factor, the entity is still inherently lower risk considering the following factors: (a) it does not own a special protection system; (b) it is not a Blackstart Resource; (c) it has no system restoration responsibilities; and, (d) it has never experienced a misoperation. ReliabilityFirst also notes that the Transmission Operator indicated that it did not identify any system voltage issues caused by the entity’s failure to maintain its reactive power schedule, which suggests that any excursions were minor. No harm is known to have occurred. | To mitigate this noncompliance, the entity has: 1) instructed all operations personnel that calls will be placed with ITC and Consumers Energy prior to adjusting MW output. Additionally, entity operations personnel will notify ITC of any variances from the assigned reactive power schedule. These communications will be logged in the control room logbook; 2) implemented an additional graphic monitoring of MVAR at the point of interconnection, to enable operations personnel to visually detect fluctuations of MVAR; 3) made corrections to both the combustion and steam turbine to maintain the -3/+3 MVAR reactive power band; and 4) contacted ITC to discuss the excursions. In a written response, ITC stated that they did not identify any system voltage issues caused by the entity’s failure to maintain the reactive power schedule during Reduced Dispatch Agreement events. | ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. ReliabilityFirst determined that no monetary penalty was warranted due to the lack of any actual harm and the reduced potential for harm. Specifically, ReliabilityFirst considered the following factors: First, the facility at issue is a 125 MW unit, which reduces the potential impact of the noncompliance. Second, the entity is inherently lower risk considering the following factors: (a) it does not own a special protection system; (b) it is not a Blackstart Resource; (c) it has no system restoration responsibilities; and, (d) it has never experienced a misoperation. ReliabilityFirst also notes that the Transmission Operator indicated that it did not identify any system voltage issues caused by the entity’s failure to maintain its reactive power schedule, which suggests that any excursions were minor. As additional support for the $0 penalty amount, ReliabilityFirst notes that the entity has never had a violation prior to the current issue. However, ReliabilityFirst still determined that a Spreadsheet Notice of Penalty was the appropriate disposition method considering (a) the fact that ReliabilityFirst identified the issue during a Spot Check; and (b) the length of time that the issue persisted and the number of instances involved.
2020-12-30 | NOC-2693 | ReliabilityFirst Corporation (RF) | METC | NCR00820 | TO | Settlement Agreement | Admits | 125000 | RFC2017017946 | FAC-008-1 | R1 | Moderate | Lower | Severe | Self-Report | 2017-07-05 | 2007-06-18 | Ongoing | 12/31/2021 (Expected Completion Date) | TBD | On July 5, 2017, METC submitted a Self-Report to ReliabilityFirst on behalf of ITC Midwest (ITCM) stating that, as a Transmission Owner, ITCM had a possible violation of FAC-008-1 R1. METC submitted the Self-Report to ReliabilityFirst under an existing multi-region registered entity agreement. During a January 2017 internal control review of the Tiffin to Arnold 345 kV circuit, ITCM reviewed relay thermal limits and discovered that a relay thermal limit associated with the T1 transformer differential scheme did not match the published equipment rating and resulted in reducing the Facility Rating. This lower thermal limit was caused by the combination of the relay limit (which was above five amps) and the impact of the delta-connected Current Transformer (CT), which provides more secondary current to the relays than a wye-connected CT. ITCM identified this relay thermal limit as the most limiting element for both the Duane Arnold-Tiffin 345 kV Facility and the Duane Arnold 345/161 kV Transformer Facility. Subsequently, the planning and relay groups for both ITCM and the ITC Michigan operating companies (i.e., ITCT, METC, ITCGP, and ITCI) conducted a root cause analysis and an extent of condition review. These reviews were designed to identify how ITCM and the Michigan groups calculated, considered, and applied relay thermal limits in the ITC Facility Ratings database. Through this work, ITCM determined that it had not been previously considering the impacts of delta-connected CTs when determining secondary equipment capabilities. Had the impacts been considered, ITCM would have identified this limit in prior reviews. ReliabilityFirst also notes that, in the ITCM footprint, a conservative rating philosophy was applied to secondary equipment. Specifically, ITCM rated secondary equipment at a maximum of five amps or the nameplate rating, whichever was lower. Also through this work, ITC Holdings determined that, in the Michigan operating companies, relay thermal limits were not historically calculated for transformers. The previous Rating Methodology for relays did not consider the need to calculate relay thermal limits on transformers and only addressed transmission lines. CTs on bulk power transformers in Michigan were historically included in the rating of the bulk power transformers, but not explicitly identified on Facility Rating sheets because it was assumed that the relay thermal limits were included in the bulk power transformer ratings. In light of these findings, ITC Holdings committed to review all 254 substations across its entire footprint. ITC Holdings employed a risk-based strategy in planning this work in order to minimize risk while the work is completed. Specifically, ITC Holdings prioritized breaker and half and ring bus configurations because there was a higher likelihood that devices in these circuits were not properly rated, especially when open breaker ratings were considered. ITC Holdings was able to narrow down the list of 254 substations and begin with those which have open breaker configurations. Moreover, as it proceeds through this review, ITC Holdings also approves any identified rating changes the same day, and enters them into its transmission management system within two business days. In total, ITC Holdings projected that this work would take approximately three years to complete, establishing an expected end date of late 2021. ITC Holdings has provided ReliabilityFirst with periodic updates on the progress of this work, and so far has been completing the work on schedule. As of August 2020, ITC Holdings has completed reviews of 184 out of the 254 total substations (i.e., 72%). During the course of this extent of condition, ITC Holdings has been reducing the thermal limit at approximately seven percent of facilities (i.e., 55 out of 813 facilities reviewed). The percentage change that ITC Holdings was required to make to these facilities ranges from 1-67% lower. The ITC Holdings group responsible for performing this extent of condition has been coordinating its review with ITC Holdings’ planning department. The root cause of this matter was ITC Holdings’ omitting to properly consider relay thermal limits in its Facility Rating Methodology. ITC incorrectly assumed that this information was being captured in its methodology, when, in fact, it was not. This root cause involves the management practice of asset and configuration management, which includes defining asset and configuration item attributes. The violation began on June 18, 2007, the date ITC Holdings was required to comply with FAC-008-1 R1. The violation is scheduled to end by December 31, 2021, the date ITC Holdings committed to complete its extent of condition review. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by not having accurate Facility Ratings is that the entity may operate equipment above its maximum ratings without the operators being aware, potentially causing equipment degradation and failure. Operating below the correct rating in emergencies can also cause undue load shedding and result in incorrect post contingency planning. The risk is not minimal in this case because the entity has had to lower Facility Ratings at approximately seven percent of its facilities with an average percentage decrease of 18 percent. The risk is not serious or substantial in this case based on the following factors. First, in the last five years, the entity has never exceeded the corrected Facility Ratings at any of the Facilities with decreased ratings. Second, in the last five years, the entity has never operated above 90 percent of the corrected Facility Ratings at those locations. Third, the entity self-identified this issue through a regularly-occurring, detailed review of its Facility Ratings Methodology. No harm is known to have occurred. | To mitigate this noncompliance, the entity has: 1) reviewed ITCM for delta configured secondary circuits and updated relay thermal limits in Facility Ratings Database and published new ratings; 2) updated Facility Ratings Methodology to include all Facilities including Transformers and the impacts of delta connected CTs secondary circuit; 3) calculated and published, if appropriate, relay thermal and overall facility limits on first 1/3 Transformers; 4) calculated and published if appropriate relay thermal and overall facility limits on second 1/3 Transformers; 5) calculated and published if appropriate relay thermal and overall facility limits on third 1/3 Transformers; 6) reviewed, corrected and published if appropriate relay thermal and overall facility limits for facilities at 42 substations; 7) reviewed, corrected and published if appropriate relay thermal and overall facility limits for facilities at 40 substations; 8) reviewed, analyzed and determined if 10% threshold has been exceeded for ITCT, METC, ITCGP and ITCI group; and 9) reviewed, analyzed and determined if 10% threshold has been exceeded for ITCM. ReliabilityFirst has verified the completion of all mitigation activity in steps 1-9 above. Additionally, ITC Holdings committed to complete an extent of condition review by the end of 2021 that will include all 254 substations and correct any incorrect Facility Ratings. | ReliabilityFirst considered ITC Holdings' compliance history with FAC-008-1 R1 (subsequently determined to have arisen under FAC-009-1 R1) in determining the penalty. ReliabilityFirst considered ITC Holdings' FAC-009-1 R1 compliance history to be an aggravating factor in the penalty determination. ITC Holdings has been highly cooperative throughout the entire enforcement process. Following the self-report of the violation, ITC Holdings met with the Regions on a regular basis to discuss progress on mitigation, the effectiveness of its extent of condition review, reliability, and other related activities. Throughout the enforcement process, ITC Holdings voluntarily provided the Regions with an abundance of information regarding the violation in a manner that was detailed, well-organized and timely. ITC Holdings has been transparent with the Regions regarding the violation and ITC Holdings’ processes and systems, and this insight has allowed the Regions to better analyze the violation and assist ITC Holdings with resolving the same. ITC Holdings’ level of cooperation throughout the enforcement process has been exemplary and the Regions awarded mitigating credit for this level of cooperation to encourage this sort of response by other Registered Entities in the future. Effective oversight of the reliability of the bulk power system depends on robust and timely self-reporting by Registered Entities. METC self-reported the violation and the issue was identified prior to the occurrence of any harm. The Regions considered that ITC Holdings initially discovered the ITC Holdings violation through a Self-Report and applied some mitigating credit. Under coordinated oversight, METC’s penalty will be divided among the Regional Entities as follows. ITC Holdings shall pay $125,000 to ReliabilityFirst and ReliabilityFirst shall divide that penalty amount in two parts based on the relative net energy for load (“NEL”) for each Region and shall distribute NEL-based proportional allocation to MRO. Of the total penalty remitted, ReliabilityFirst shall distribute $41,250 to MRO.
2020-11-30 | NOC-2689 | ReliabilityFirst Corporation (RF) | Twin Ridges Wind Farm | NCR11280 | GO | Settlement Agreement | Neither Admits nor Denies | 0 | RFC2019021935 | PRC-019-2 | R1 | Moderate | Medium | Severe | Spot Check | 2019-07-24 | 2016-07-01 | 2020-02-10 | 2020-06-19 | 2020-09-28 | On July 24, 2019, ReliabilityFirst determined that the entity, as a Generator Owner, was in violation of PRC-019-2 R1 identified during a Spot-Check conducted from July 8, 2019 through July 19, 2019. The ReliabilityFirst Spot-Check team determined that the entity did not verify coordination of its Generating Facilities. The entity could not locate evidence of dated documents that would demonstrate that the facility coordinated the voltage regulating system controls, including in-service limiters and protection functions, with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. After PRC-019-2 R1 became effective on July 1, 2016, the entity was sold and acquired by the current owner on February 16, 2018. At the time of the sale, both the prior owner and the current owner were not aware that the entity was not compliant with PRC-019-2 R1. This violation involves the management practices of reliability quality management, planning and implementation. The root cause of this violation was that neither the prior nor current owner confirmed that the entity was compliant with PRC-019-2 R1. The violation began on July 1, 2016, when the entity was required to comply with PRC-019-2 R1 and ended on February 10, 2020, when the entity completed the overdue coordination. | The violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by failing to fully coordinate voltage regulating system controls with the applicable equipment capabilities and settings of the applicable Protection System devices and functions, is that it could result in a generator falsely tripping, or potentially damaging the generator. The risk is not minimal because of the long, more than three year, duration. The risk is lessened because no changes were required when the entity performed the overdue coordination. ReliabilityFirst notes that this is a 139.4 MW wind facility that had an average capacity factor of 35.4% during the violation. No harm is known to have occurred. | To mitigate this noncompliance, the entity has: 1) engaged an engineering firm to perform the required coordination study and to make any necessary adjustments identified during the study. The engineering firm determined that no changes were required; and 2) engaged an outside firm to perform a comprehensive review of its compliance program (a gap analysis) to support its mitigating activities. ReliabilityFirst has verified the completion of all mitigation activity. | ReliabilityFirst reviewed the entity's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. ReliabilityFirst considered the entity’s compliance history and determined there were no relevant instances of noncompliance. ReliabilityFirst determined that no penalty was warranted because of a combination of factors including: the small size of the entity, the moderate risk posed by the violation, the entity's level of cooperation throughout the enforcement process, and the entity's lack of compliance history.
2020-11-30 | NOC-2690 | Texas Reliability Entity, Inc. (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | TO | Settlement Agreement | Neither Admits nor Denies | 192000 | TRE2018019658 | FAC-008-3 | R6 | Moderate | Medium | Moderate | Compliance Audit | 2018-04-30 | 2016-02-25 | 2017-07-11 | 2020-09-08 | 2020-09-28 | During a Compliance Audit conducted from October 30, 2017 through November 10, 2017, Texas RE determined that Oncor Electric Delivery Company LLC (Oncor), as a Transmission Owner (TO), was in noncompliance with FAC-008-3, R6. Specifically, 22 Oncor Facilities had Facilities Ratings that were inconsistent with its associated Facility Ratings methodology. During the Compliance Audit, the audit team reviewed spreadsheets that represented weekly reviews of Facility Ratings performed by Oncor staff. The audit team compared these Ratings to ERCOT Independent System Operator (ERCOT) Model Ratings for the same Facilities and period and noted that some ratings were either higher or lower than the ERCOT Model Ratings. Based on this evidence, the audit team reviewed 199 Oncor Facilities for the period between the previous audit, February 25, 2016, and the time of the current audit. In its review, the audit team noted 22 instances in which Oncor field verifications identified Facility Ratings that altered the Facility’s most limiting applicable Equipment Rating. As such, Oncor’s resulting Facility Ratings for these 22 Facilities were inconsistent with its Facility Rating methodology. The root cause of the noncompliance was a failure of internal controls. In particular, Oncor lacked sufficient processes to track and timely reflect equipment ratings changes in its internal Facility Ratings documentation. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Oncor is the largest regulated electric transmission and distribution service provider in Texas, and the 6th largest in the United States. Oncor's service area is located primarily in the north-central, eastern, and western regions of Texas, and comprises 91 counties and over 400 incorporated municipalities, including Dallas/Fort Worth and surrounding suburbs, as well as Waco, Wichita Falls, Odessa, Midland, Tyler, and Killeen. This service area has an estimated population in excess of ten million, about 37% of the population of Texas. Oncor maintains approximately 70 operations facilities, 1,046 Stations, 16,080 circuit miles of transmission, and more than 105,000 miles of distribution conductor in the state. Oncor’s failure to maintain accurate Facility Ratings within its own record system resulted in erroneous Facility Ratings being used by ERCOT in the planning and operation of the bulk power system, and the System being operated according to incorrect System Operating Limits (SOLs). These erroneous Facility Ratings posed the risk that SOLs for certain Facilities could have been exceeded resulting in damage to those Facilities, or alternatively, that those Facilities could have been unnecessarily tripped Off-line. In particular, the incorrect Facility Ratings for 12 of the 22 Facilities at issue were higher than those Facility’s actual Facility Ratings, increasing the risk of an inadvertent exceedance and associated equipment damage. The most significant Facility Rating discrepancy concerned four 326 MVA rating conductors, which Oncor had incorrectly ratings as 653 MVA Facilities (a 327 MVA rating discrepancy). However, the risk was minimized by several factors. As an initial matter, Oncor’s internal Facility Ratings for 10 of the 22 Facilities at issue were more conservative than the Facilities’ actual Facility Ratings. Moreover, line flow data demonstrates that flow levels remained below the actual Facility Ratings for all Facilities during the audit period. Oncor detected the Facility Rating discrepancies during field verifications associated with new or upgraded transmission projects and corrected its internal Facility Rating documentation. This indicates the presence of detective controls to identify and address Facility Ratings issues associated with equipment changes. No harm is known to have occurred. | To mitigate this noncompliance, the entity has performed the following actions: 1) corrected the 22 incorrect Facility ratings; 2) implemented a weekly comparison of the ratings of Oncor Facilities that are included in the ERCOT Network Operations Model and the ratings of Oncor Facilities that are included in Oncor’s Ratings Model to determine whether there are any instances of ratings in those two models that do not match. This weekly comparison is part of Oncor’s constant monitoring of the ratings being used for its Facilities; 3) implemented a new project tracking and communication application (PETE) that consolidated the three primary systems that were previously used for initiating and executing transmission projects, and integrated those systems with the existing tracking and communication processes for all projects that require submission of a Network Operations Model Change Request (NOMCR); 4) conducted staff training and developed training material for PETE; and 5) revised its rating discrepancy review and commissioning process to ensure that: • rating discrepancies are tracked, reviewed, and resolved quickly; • rating corrections for energized assets are submitted promptly to the ERCOT/Oncor models in time for the next scheduled ERCOT model NOMCR load; and • assets are energized in the field only after a proper ERCOT model topology and rating review. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed Oncor's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered Oncor’s IRO-010-1a R3 compliance history in determining the penalty and disposition track for this violation and determined it to be an aggravating factor. In TRE2016015568, during a previous Compliance Audit conducted February 1, 2016 through February 25, 2016, Texas RE determined that Oncor was in violation of IRO-010-1a, R3. Oncor failed to provide ERCOT with accurate data regarding the Ratings for 10 of its Facilities for the period of October 1, 2011 (the enforceable date for IRO-010-1a) through May 18, 2016. The incorrect ratings in Oncor’s Transmission Management System (TMS) were telemetered to ERCOT via ICCP.
2020-11-30 | NOC-2690 | Texas Reliability Entity, Inc. (Texas RE) | Oncor Electric Delivery Company LLC (Oncor) | NCR04109 | TO | Settlement Agreement | Neither Admits nor Denies | 192000 | TRE2018019659 | FAC-008-3 | R8 | Moderate | Medium | Severe | Compliance Audit | 2018-04-30 | 2013-01-01 | 2017-07-12 | 2020-09-08 | 2020-09-28 | During a Compliance Audit conducted from October 30, 2017 through November 10, 2017, Texas RE determined that Oncor Electric Delivery Company LLC (Oncor), as a Transmission Owner (TO), was in noncompliance with FAC-008-3, R8. Specifically, Oncor did not provide accurate and timely Facility Ratings data to its associated Reliability Coordinator, ERCOT. During the Compliance Audit, the audit team took judgmental samples from a list of Network Operations Model Change Requests (NOMCRs) submitted by Oncor to ERCOT focusing mainly on new and upgraded 138kV and 345kV projects. Based on this review, the audit team identified a number of mismatches between ERCOT model information and information in Oncor’s internal record system. In particular, the audit team identified 29 Facilities for which the Facility Ratings provided to ERCOT differed from the Facility Ratings in Oncor’s internal record system. For 22 Facilities at issue, Oncor detected the Facility Ratings issues during a field verification process, which required Oncor to update both its internal records, as well as the Facility Ratings it had previously provided to ERCOT. For seven additional Facilities, Oncor did not provide the correct Facility Ratings from its internal Facility Rating records to ERCOT as required. Because of the nature of its Facility Rating submission issues, Oncor could not provide documentation when its Facility Rating submissions began. Oncor’s Facility Ratings issues lasted until July 12, 2017, when Oncor submitted the final NOMCR to correct the last erroneous Facility Rating submission at issue. The root cause of the noncompliance was a failure of internal controls. Oncor possessed a process to perform a weekly comparison between Oncor Facility Ratings and the corresponding Facility Ratings set forth in the ERCOT Network Operations Model, a mitigation tool Oncor put into place as a result of the previous audit. However, in implementing this tool, Oncor did not develop sufficient procedures to ensure it timely submitted Facility Rating changes to address identified discrepancies, including discrepancies identified in Oncor’s field verifications. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Oncor is the largest regulated electric transmission and distribution service provider in Texas, and the 6th largest in the United States. Oncor's service area is located primarily in the north-central, eastern, and western regions of Texas, and comprises 91 counties and over 400 incorporated municipalities, including Dallas/Fort Worth and surrounding suburbs, as well as Waco, Wichita Falls, Odessa, Midland, Tyler, and Killeen. This service area has an estimated population in excess of ten million, about 37% of the population of Texas. Oncor maintains approximately 70 operations facilities, 1,046 Stations, 16,080 circuit miles of transmission, and more than 105,000 miles of distribution conductor in the state. Because of the volume of its transmission capacity, any failure by Oncor to timely update ERCOT with accurate Facility Ratings is a risk to the bulk power system. More specifically, Oncor’s failure to provide accurate and timely Facility Ratings to ERCOT resulted in erroneous Facility Ratings being used in the planning and operation of the bulk power system. These erroneous Facility Ratings posed the risk that System Operating Limits (SOLs) for certain Facilities could have been exceeded resulting in damage to those Facilities, or alternatively, that those Facilities could have been unnecessarily tripped Off-line. The most significant Facility Rating discrepancy concerned four 326 MVA rating conductors, which Oncor had incorrectly ratings as 653 MVA Facilities (a 327 MVA rating discrepancy). However, the risk was minimized by several factors. As an initial matter, Oncor’s internal Facility Ratings for 12 of the 29 Facilities at issue were more conservative than the Facilities’ actual Facility Ratings, limiting the overall risk associated with those issues. In addition, Oncor provides approximately 2,437 Facility Ratings to ERCOT. Accordingly, the Facility Rating submission issues impacted only approximately 1.2% of all Oncor Facilities for which Oncor provides Facility Ratings. Moreover, Oncor detected 22 Facility Rating discrepancies during field verifications associated with new or upgraded transmission projects and corrected its internal Facility Rating documentation. This indicates the presence of detective controls to identify and address Facility Ratings issues associated with equipment changes. Further, for all 29 Facilities, line flow data demonstrates that flow levels remained below these Facilities’ actual Facility Ratings during the audit period. No harm is known to have occurred. | To mitigate this noncompliance, the entity has performed the following actions: 1) submitted NOMCRs to correct the ERCOT Model Ratings requiring revision; 2) implemented a weekly comparison of the ratings of Oncor Facilities that are included in the ERCOT Network Operations Model and the ratings of Oncor Facilities that are included in Oncor’s Ratings Model to determine whether there are any instances of ratings in those two models that do not match. This weekly comparison is part of Oncor’s constant monitoring of the ratings being used for its Facilities; 3) implemented a new project tracking and communication application (PETE) that consolidated the three primary systems that were previously used for initiating and executing transmission projects, integrated those systems with the existing tracking and communication processes for all projects that require submission of a NOMCR; 4) conducted staff training and developed training material for PETE; and 5) revised its rating discrepancy review and commissioning process to ensure that: • rating discrepancies are tracked, reviewed, and resolved quickly; • rating corrections for energized assets are submitted promptly to the ERCOT/Oncor models in time for the next scheduled ERCOT model NOMCR load; and • assets are energized in the field only after a proper ERCOT model topology and rating review. Texas RE has verified the completion of all mitigation activity. | Texas RE reviewed Oncor's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Texas RE considered Oncor’s IRO-010-1a R3 compliance history in determining the penalty and disposition track for this violation and determined it to be an aggravating factor. In TRE2016015568, during a previous Compliance Audit conducted February 1, 2016 through February 25, 2016, Texas RE determined that Oncor was in violation of IRO-010-1a, R3. Oncor failed to provide ERCOT with accurate data regarding the Ratings for 10 of its Facilities for the period of October 1, 2011 (the enforceable date for IRO-010-1a) through May 18, 2016. The incorrect ratings in Oncor’s Transmission Management System (TMS) were telemetered to ERCOT via ICCP.
2020-11-30 | NOC-2694 | Western Electricity Coordinating Council (WECC) | Sacramento Municipal Utility District (SMUD) | NCR05368 | GO | Settlement Agreement | Admits | 26000 | WECC2019022212 | FAC-008-3 | R2 | Moderate | Medium | Moderate | Compliance Audit | 9/3/2019 to 9/13/2019 | 2013-01-01 | 2019-11-04 | 2019-12-03 | 2020-01-29 | During a Compliance Audit conducted from September 3, 2019 through September 13, 2019, WECC determined that SMUD, as a Generator Owner (GO), was in violation of FAC-008-3 R2. Specifically, SMUD, as a GO, did not include in its Facility Ratings methodologies that its solely owned equipment for eight generation Facilities defined generation tie-lines as being between the high side terminals of the main step up transformer and the point of interconnection with itself as the Transmission Owner (TO). SMUD’s two Generator Facility Ratings Methodologies directed its generation personnel to use said methodologies for Transmission Facility Ratings to determine ratings beyond the high side terminals of its main step up transformers. Likewise, SMUD’s Transmission Facility Ratings Methodology noted that SMUD’s generation staff were responsible for Facility Ratings of generation tie-lines. Neither Facility Ratings methodologies specifically stated the demarcation for generation Facilities must extend from the high side terminals of the main step up transformers to the point of interconnection with the TO (SMUD), which could have resulted in SMUD’s Facility Ratings having missed elements in its calculations, leading to incorrect Facility Ratings and possibly incorrect System Operating Limits (SOLs). SMUD assumed that generator tie-lines were understood to be from step-up transformer to the point of interconnection, and thus SMUD did not specifically define the demarcation line in its Facility Ratings methodologies. However, despite the oversight in the methodologies, WECC auditors found that SMUD’s eight generator tie-line Facilities were rated appropriately. SMUD’s Facility Ratings methodologies were consistent with the principle that the Facility Ratings do not exceed the most limiting applicable equipment rating of the individual equipment that comprised a Facility. The root cause of the violation was attributed to SMUD’s incorrect interpretation of the requirements of the Standard, SMUD assumed that generator tie-lines were understood to be from step-up transformer to the point of interconnection because SMUD is the GO and TO, thus SMUD did not specifically define the demarcation line in its appropriate Facility Ratings methodologies. This violation began on January 1, 2013, when the Standard became mandatory and enforceable, and ended on November 4, 2019, when SMUD updated its applicable Facility Ratings methodologies to describe the demarcation of generator tie lines for a total of 2,499 days. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, SMUD failed include the definition of generator series elements associated with the tie-lines in its documented methodology for determining its Facility Ratings methodologies, applicable to eight solely owned generation Facilities, including approximately 2,000 MVA and a 140 MVA Blackstart Resource between the location specified in R1 and the point of interconnection with the TO, as required by FAC-008-3 R2. Such failure could have resulted in an improper Facility Rating for a Facility because not all elements in the Facility would have been taken into account if the demarcation of the generator tie-lines had not been accurate. Since Facility Ratings are used to develop SOLs, this could have led to the operation of the system beyond safe and reliable limits and could have resulted in the loss of BPS equipment operated at or above 200 kV. However, as compensation, SMUD’s Facility Ratings Methodologies were consistent with the principle that the Facility Ratings do not exceed the most limiting applicable equipment rating of the individual equipment that comprised a Facility. WECC auditors found that SMUD’s generator tie-line Facilities were rated appropriately even though its methodologies did not specifically define the demarcation of the generator tie-lines. SMUD thought the generator tie-line demarcation was an understood definition and the Facility Ratings were created with the correct generator tie-line definition in mind, though it was not specifically stated per the requirements of the Standard, thus reducing the risk to the BPS. | To remediate and mitigate this violation, SMUD has: 1) revised its two Generator Facility Ratings methodologies and one Transmission Facility Ratings methodology to clearly describe the demarcation for its generator tie-lines, according to the Standard; and 2) conducted two meetings with the relevant SMEs, to address and ensure understanding of how its Facility Ratings methodologies should reflect that Facilities are rated from the high side of the generator step-up transformer to the point of interconnection with the BES (generation tie lines) and address any recommendations for improvements suggested or recommended by the WECC auditors. | WECC did not apply mitigating credit for SMUD’s Internal Compliance Program (ICP). SMUD does have a well-documented ICP, WECC determined that it was not effective in detecting or preventing these particular violations. SMUD’s ICP was effective in creating the compensating measures that prevented SMUD from having incorrect Facility Ratings. WECC considered SMUD’s compliance history and determined there were no relevant compliance history.
2020-11-30 | NOC-2694 | Western Electricity Coordinating Council (WECC) | Sacramento Municipal Utility District (SMUD) | NCR05368 | TO | Settlement Agreement | Admits | 26000 | WECC2019022213 | FAC-008-3 | R3 | Moderate | Medium | Moderate | Compliance Audit | 9/3/2019 to 9/13/2019 | 2013-01-01 | 2019-10-31 | 2019-12-03 | 2020-01-29 | During a Compliance Audit conducted from September 3, 2019 through September 13, 2019, WECC determined that SMUD, as a Transmission Owner (TO), was in violation of FAC-008-3 R3. Specifically, SMUD, as a TO, did not explicitly describe which of its transmission Facilities were jointly owned, thus it did not describe how it rated its jointly owned transmission Facilities with its neighboring entities in its Facility Ratings methodology. SMUD’s jointly owned transmission Facilities consisted of 12 interconnection points at 230kV with two other entities. SMUD provided evidence that all components that make up its jointly owned transmission Facilities were rated appropriately, which included circuit breakers, switches, jumpers, wave traps, revenue meters and any other components of the jointly owned line interconnecting to the SMUD bus. In addition, SMUD coordinated with neighbors to rate all components of the jointly owned transmission Facilities in order to create the Facility Rating that used the most limiting element. The root cause of the violation was attributed to SMUD’s incorrect interpretation of the definition for jointly owned Facilities. SMUD interpreted this to mean actual ownership of facilities. SMUD previously thought the demarcation was the end of its actual ownership of a Facility instead of understanding the definition of joint Facility Ratings to be developed to account for the transmission line and all components from terminal to terminal including terminal circuit breakers. This violation began on January 1, 2013, when the Standard became mandatory and enforceable, and ended on October 31, 2019, when SMUD updated its Facility Ratings Methodology to include its jointly owned Facility Ratings for a total of 2,495 days. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, SMUD failed to name its jointly owned Facilities as jointly owned therefore failed to address how its jointly owned Facilities were rated, such as transmission interconnection lines, in its Facility Ratings Methodology, as required by FAC-008-3 R3. SMUD’s jointly owned transmission Facilities consisted of 12 interconnection points at 230kV with two other entities. Such failure could have resulted in confusion between the joint owners of the Facilities regarding what Facilities are considered jointly owned leading to confusion about sharing Facility Ratings for these jointly owned Facilities thus resulting in incorrect Facility Rating or SOLs for a specific Facility. Since Facility Ratings are used to develop SOLs, this could have led to inaccurate Facility Ratings or SOLs between the joint owners or operation of the system beyond safe and reliable limits and could have resulted in the loss of BPS equipment operated at above 200 kV. However, as compensation, SMUD had an Operating Procedure developed to validate Facility Ratings between Facility owners to share and maintain the most limiting element, thus SMUD’s Facility Ratings Methodologies were consistent with the principle that the Facility Ratings do not exceed the most limiting applicable equipment rating of the individual equipment that comprised a Facility. SMUD provided evidence that all components that make up its jointly owned Transmission Facilities were rated appropriately, which included circuit breakers, switches, jumpers, wave traps, revenue meters and any other components of the jointly owned line interconnecting to the SMUD bus, thus reducing the risk to the BPS. | To remediate and mitigate this violation, SMUD has: 1) revised its Facility Ratings methodology to clearly describe the concept of joint ownership of transmission line Facilities; and 2) updated the applicable Facility Ratings Methodology for interconnection lines that are jointly owned Facilities. The methodology now describes that the interconnection lines are jointly owned Facilities, and Facility Ratings must be developed to account for the transmission line and all components from terminal to terminal, including terminal circuit breakers; 3) added a procedural step to annually request updates of jointly owned transmission line ratings from neighboring entities and review to ensure the ratings are confirmed and verified, or updated as necessary by using the language of the Standard; and 4) conducted two meetings with the relevant SMEs, to address and ensure understanding of how its Facility Rating methodology should address how to identify and rate its jointly owned Facilities and address any recommendations for improvements suggested or recommended by the WECC auditors. | WECC did not apply mitigating credit for SMUD’s Internal Compliance Program (ICP). SMUD does have a well-documented ICP, WECC determined that it was not effective in detecting or preventing these particular violations. SMUD’s ICP was effective in creating the compensating measures that prevented SMUD from having incorrect Facility Ratings. WECC considered SMUD’s compliance history and determined there were no relevant compliance history.
2020-11-30 | NOC-2695 | Western Electricity Coordinating Council (WECC) | sPower Services, LLC (SPS) | NCR11679 | GOP | Settlement Agreement | Admits | 22000 | WECC2017017218 | VAR-002-4 | R3 | Minimal | Medium | Severe | Self-Report | 2017-03-10 | 2017-02-04 | 2017-02-04 | 2017-03-01 | 2017-06-30 | On March 10, 2017, SPS submitted a Self-Report stating that, as a Generator Operator (GOP), it was in violation of VAR-002-4 R3. Specifically, SPS discovered it did not notify its Transmission Operator (TOP) of a status change on the automatic voltage regulation (AVR), within 30 minutes of the change. On February 4, 2017, a single 50 MW solar generating unit started generating with the power factor control function disabled. At 7:17 AM, an alarm was triggered by the site local Supervisory Control and Data Acquisition (SCADA) system indicating that the power factor control was disabled for a generation threshold, but it should not have been active. However, due to degraded external communication with the Facility, the alarm was not transmitted to SPS’s control room at that time. Subsequently, at 8:22 AM, SPS discovered the solar generating unit was generating at approximately a 0.98 power factor and not producing at unity power factor. SPS immediately notified its SCADA vendor of the deviation and started an investigation concurrently with the vendor. At 8:31 AM, SPS notified its TOP of the power factor deviation from unity given the unusual behavior of the solar generating Facility. At 8:45 AM, during troubleshooting with the vendor an alarm was raised in the SPS control room indicating the closed loop power factor control had been disabled and at 8:48 AM, SPS reported the change in status of the power factor controller to its TOP. At 8:50 AM, another alarm was raised in the SPS control room indicating the closed loop power factor control had been reenabled. At 9:06 AM, SPS notified its TOP that the power factor control had been reenabled and the solar generating unit was producing at unity power factor. Further, the SCADA vendor’s internal investigation concluded that the power factor control function was inadvertently disabled during a SCADA software update completed after generating hours the previous evening. This issue began on February 4, 2017 at 7:48 AM, when SPS failed to notify its associated TOP of a status change on the AVR within 30 minutes of the change for its solar generating unit and ended on February 4, 2017 at 8:48 AM, when SPS notified its TOP of the AVR status change of its solar generating unit, for a total of 60 minutes. The root cause of the issue was attributed to an unreliable communications path from the generating unit to the control room. Additionally, a contributing factor to this issue was the breakdown of change control process by the SCADA vendor. As a result, when the SCADA system was restarted after the software upgrade, the power factor control function status was defaulted to disabled and was not corrected before implementation. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SPS failed to notify its TOP of a change in status of its AVR, for a single 50 MW solar generating unit, within 30 minutes of the change, as required by VAR-002-4 R3. Failure to notify its TOP of the status change on the AVR, for a single 50 MW solar generating unit, could have resulted in an inaccurate Operating Plan developed by the TOP that expected the AVR to be in the required mode. Additionally, the inaccurate Operating Plan could have led to delayed system recovery following a voltage transient, load shedding to recover from voltage following a contingency or tripping of the 50 MW generating unit to address an over-voltage condition. However, as compensation, the solar generating unit contributes 50 MW to the grid and does not provide significant voltage support to the Interconnection. No harm is known to have occurred. | To mitigate this violation, the entity has performed the following actions: 1) notified its TOP of the AVR change; 2) verified the AVR controller vendor updated its change control process; and 3) provided alternate communication path for alarms from the generating Facility to the GOP control room. | WECC applied a mitigating credit for the following reasons: 1) SPS self-reported these violations in a timely manner from the date of discovery. 2) SPS accepted responsibility and admitted to the violations. 3) SPS agreed to settle these violations. WECC considered the following as aggravating factors and justification for the escalation of the disposition of these minimal risk violations to an expedited settlement agreement: the violations’ Real-time Operations violation time horizon expectation for remediation, multiple and overlapping root causes at the same Control Center for the same Standard and Requirement, repeated violations demonstrating a system problem.
2020-11-30 | NOC-2695 | Western Electricity Coordinating Council (WECC) | sPower Services, LLC (SPS) | NCR11679 | GOP | Settlement Agreement | Admits | 22000 | WECC2018019434 | VAR-002-4.1 | R3 | Minimal | Medium | Severe | Self-Report | 2018-03-25 | 2017-12-25 | 2017-12-25 | 2018-03-23 | 2018-05-30 | On March 25, 2018, SPS submitted a Self-Report stating that, as a GOP, it was in violation of VAR-002-4.1 R3. Specifically, SPS discovered it did not notify its Transmission Operator (TOP) of a status change on the automatic voltage regulation (AVR), within 30 minutes of the change. On December 25, 2017 at approximately 9:08 AM, the SPS Control Center (CC) received an alarm indicating that a common 220 kV bus, shared by ten solar generating units with a combined capacity of 300 MW, had deviated from the controller deadband, followed by an alarm at 9:11 AM that the power factor had deviated from the schedule set forth by the TOP. At that time, the AVR was still active and controlling to the appropriate power factor target. By approximately, 9:20 AM the power factor had returned to schedule and the associated alarm cleared shortly after. The SPS CC Operator contacted the TOP at 9:23 AM and Balancing Authority (BA) at 9:25 AM to notify that the power factor at the 220 kV bus had deviated from schedule but had since returned. Subsequently, the SPS CC Operator requested that SPS’s SCADA vendor investigate the SCADA to confirm that AVR was active and functioning properly. Shortly thereafter the vendor confirmed that AVR appeared to be functioning normally. At 9:53 AM, the SPS CC received an alarm indicating that the power factor at the 220 kV bus had again deviated from power factor schedule. The SPS CC notified the TOP and BA at 10:03 AM and 10:04 AM, that the power factor at the 220 kV bus had deviated from the schedule. Following a brief observation, the CC Operator and the CC Lead determined that an AVR malfunction had likely occurred and at 10:09 AM and 10:10 AM notified the TOP and BA that an AVR malfunction had occurred and that the SPS CC would take manual control of the connected solar generating units to maintain the power factor schedule at the 220 kV bus. At 10:20 AM, the SPS CC operator notified its TOP that the power factor at the 220 kV bus had been returned to schedule. After monitoring controller performance, the SPS CC operator contacted its TOP at 1:15 PM to inform them that AVR was back in automatic and controlling within schedule. An internal investigation concluded that the master plant controller sent a setpoint to the solar generating units during start up at 7:38 AM which was successfully received and executed by the solar generating units, but the next setpoint sent at 8:14 AM was not processed by the units. In the absence of alarms or indications that a malfunction had occurred, notifications were made to the TOP within fifteen minutes of steady alarms indicating a potential issue, but not within 30 minutes as required by the Standard. This issue began on December 25, 2017 at 9:39 AM, when SPS failed to notify its associated TOP of a status change on the AVR within 30 minutes of the change for the ten solar generating units and ended on December 25, 2017 at 10:09 AM, when SPS’s control room operator notified its TOP of the AVR status change for the aforementioned units, for a total of 30 minutes. The root cause of the issue was attributed to inadequate control design and incomplete consideration of possible failure modes. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SPS failed to notify its TOP of a change in status of its AVR, for ten solar generating units with a combined capacity of 300 MW, within 30 minutes of the change, as required by VAR-002-4.1 R3. Failure to notify the TOP of the status change on the AVR, for the ten solar generating units, could have resulted in a voltage deviation at the substation and caused tripping and the loss of 300 MW of generation. If an emergency event had occurred, SPS would not have been able to support voltage. However, SPS implemented good detective controls. Specifically, SPS had implemented alarms that indicated if the power factor at the substation deviated. Though the alarms did not directly address the performance of the AVR, it led the CC Operator to determine that an AVR malfunction had likely occurred which led to the CC Operator notifying the TOP and BA that the AVR had malfunctioned and that the SPS CC would take manual control of the aforementioned solar generating units to maintain the power factor schedule at the 220 kV bus. Additionally, the affected units contribute a total of 300 MW to the grid and do not provide significant voltage support to the Interconnection. No harm is known to have occurred. | To mitigate this violation, the entity has performed the following actions: 1) notified its TOP of the AVR changes; 2) made several algorithm and alarm changes to its SCADA system to prevent the master plant controller malfunction; a) created algorithm to detect whenever there is a mismatch between the substation master plant controller and any of the individual solar plant controllers, and in response to the mismatch, rebroadcasts the last control setpoint transmitted by the substation master plant controller; b) completed testing and updates of parameter scaling that led to the substation master plant controller stopping the processing of setpoints; c) completed testing and deployment of alarms that detected a variance between the setpoint transmitted between the substation master plant controller and an individual solar plant of greater than the setpoint step size; and d) completed testing and development of an algorithm to reliably detect mismatch between the substation master plant controller and the solar plants, and raise alarms based on this condition. | WECC applied a mitigating credit for the following reasons: 1) SPS self-reported these violations in a timely manner from the date of discovery. 2) SPS accepted responsibility and admitted to the violations. 3) SPS agreed to settle these violations. WECC considered the following as aggravating factors and justification for the escalation of the disposition of these minimal risk violations to an expedited settlement agreement: the violations’ Real-time Operations violation time horizon expectation for remediation, multiple and overlapping root causes at the same Control Center for the same Standard and Requirement, repeated violations demonstrating a system problem.
2020-11-30 | NOC-2695 | Western Electricity Coordinating Council (WECC) | sPower Services, LLC (SPS) | NCR11679 | GOP | Settlement Agreement | Admits | 22000 | WECC2018020372 | VAR-002-4.1 | R3 | Minimal | Medium | Severe | Self-Report | 2018-09-11 | 2018-05-10 | 2018-05-10 | 2018-12-06 | 2019-04-02 | On September 11, 2018, SPS submitted a Self-Report stating that, as a GOP, it was in violation of VAR-002-4.1 R3. Specifically, SPS discovered it did not notify its Transmission Operator (TOP) of a status change on the automatic voltage regulation (AVR), within 30 minutes of the change. On May 10, 2018 at 7:55 AM, the SPS CC noticed that a 56 MW solar generating unit had a power factor that was outside the control deadband. The SPS CC immediately performed a power factor control reset and the power factor returned to within the setpoint deadband. At 8:02 AM, the SPS CC contacted its TOP to inform them that the power factor for the 56 MW solar generating unit had deviated from the setpoint deadband, and even though the power factor controller had been reset and the unit was operating within the power factor deadband at that time, there was still a possibility that the power factor controller had malfunctioned. Subsequently, the SPS CC contacted its SCADA vendor to initiate an investigation. The SCADA vendor confirmed that the 56 MW solar generating unit SCADA controller was in automatic and properly operating in power factor control mode. However, due to the observed behavior of the unit, the SCADA vendor agreed to explore the possible malfunction and report back with any findings. At 8:24 AM, the SPS CC received an Operating Instruction from its TOP to overexcite the power factor of the unit, the command was executed without issue and the unit responded as expected. At 9:50 AM, the SCADA vendor notified the SPS CC that the SCADA controller had stopped sending power factor setpoints automatically for a period prior to the reset performed by the SPS CC. Specifically, the power factor at the solar generating unit stopped sending setpoints automatically due to a SCADA command that failed to execute at 7:19 AM during the morning unit ramp up. It was identified that the power factor controller algorithm had calculated that, based upon the target unit power factor setpoint and current unit feedback, the next power factor setpoint to be issued to the inverters should be 0.9998. However, the parameter to implement that control setpoint had been incorrectly programmed during unit commissioning with a limit of 0.999; therefore, the 0.9998 inverter setpoint was never transmitted to the inverters, and the power factor controller stopped automatically sending any further setpoints. This resulted in the inverters maintaining the last power factor setpoint transmitted, -0.9961, which eventually led to the generating unit power factor deviating from the power factor controller setpoint deadband as the unit real power continued to ramp up with increasing sunlight. As a result, incorrect programming by the SCADA vendor caused the plant control system to malfunction in a way undetectable by existing monitoring and alarming. Although SPS notified its TOP immediately after discovering and restoring the power factor controller to automatic operation, it was not within the 30 minutes of when the issue occurred, as required by the Standard. This issue began on May 10, 2018 at 7:50 AM, when SPS failed to notify its associated TOP of the AVR status change within 30 minutes of the change for its 56 MW solar generating unit and ended on May 10, 2018 at 8:02 AM, when SPS’s control room operator notified its associated TOP of the AVR status change for the aforementioned unit, for a total of 12 minutes. The root cause of the issue was attributed to the controller not being properly commissioned by the vendor. A contributing factor to the root cause was that the SPS did not have a checklist or narrative for the vendor that defined the required settings for the controller, as such, the vendor inputted an incorrect setting that caused this issue. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. In this instance, SPS failed to notify its TOP of a change in status on its AVR, for a 56 MW solar generating unit, within 30 minutes of the change, as required by VAR-002-4.1 R3. Failure to notify the TOP of the status change in the 56 MW solar generating unit’s voltage control device could have resulted in the TOP being unaware of the amount of MVARs the unit was consuming and the TOP developing an Operating Plan with incorrect voltage assumptions. Further, it could have potentially affected the TOP’s ability to recover voltage following a voltage transient which could have resulted in load shedding or tripping of the 56 MW unit to recover voltage in the area. However, as compensation, during the time of noncompliance the maximum VAR contribution to maintain BPS voltage was 5 MVAR, further reducing the risk. Additionally, the Facility contributes 56 MW to the grid and does not provide significant voltage support to the Interconnection. No harm is known to have occurred. | To mitigate this violation, the entity has performed the following actions: 1) notified its TOP of the status change of the 56 MW solar generating unit voltage control device; 2) confirmed the SCADA vendor developed a new configuration file with an updated parameter limit for the solar generating unit; 3) updated to the control logic so that the power factor feedback used in the SCADA control algorithm was based off the last setpoint transmitted, rather than the feedback from the inverters; and 4) developed a formal control system narrative that outlines the required settings and other key configuration elements to ensure that the SCADA system is properly commissioned and operates as designed under all circumstances. | WECC applied a mitigating credit for the following reasons: 1) SPS self-reported these violations in a timely manner from the date of discovery. 2) SPS accepted responsibility and admitted to the violations. 3) SPS agreed to settle these violations. WECC considered the following as aggravating factors and justification for the escalation of the disposition of these minimal risk violations to an expedited settlement agreement: the violations’ Real-time Operations violation time horizon expectation for remediation, multiple and overlapping root causes at the same Control Center for the same Standard and Requirement, repeated violations demonstrating a system problem.
2020-11-30 | NOC-2695 | Western Electricity Coordinating Council (WECC) | sPower Services, LLC (SPS) | NCR11679 | GOP | Settlement Agreement | Admits | 22000 | WECC2019022519 | VAR-002-4.1 | R3 | Minimal | Medium | Severe | Self-Report | 2019-11-15 | 2019-08-11 | 2019-08-12 | 2019-11-12 | 2019-04-16 | On November 15, 2019, SPS submitted a Self-Report stating that, as a GOP, it was in violation of VAR-002-4.1 R3. Specifically, SPS discovered it did not notify its Transmission Operator (TOP) of a status change on the alternative voltage controlling device, within 30 minutes of the change. On August 11, 2019 at 1:27 AM, a meter failure occurred at SPS’s 84 MVA wind generating Facility which caused the meter to provide incorrect grid voltages to the controller resulting in the Facility inappropriately producing or consuming VARs. However, the SPS Control Center (CC) was not aware of the meter failure because no alarms had been set to notify the SPS CC of meter failures thus this has been identified as the root cause of this issue. The meter failure was not identified until August 12, 2019 at 12:34 PM, when the manufacturer site supervisor contacted the SPS Control Center (CC) indicating that the voltage control for the site had malfunctioned causing the Facility to produce and consume VARs erratically. Subsequently, the SPS CC notified its TOP of the status change on the alternative voltage controlling device on August 18, 2019 at 12:49 PM, but not within the 30 minutes required by the Standard. On August 13, 2019, SPS replaced the failed meter and notified its TOP within 30 minutes of the change. This issue began on August 11, 2019 at 1:58 AM, when SPS failed to notify its TOP of a status change on the alternative voltage controlling device within 30 minutes of the change for its 84 MW wind generating Facility and ended on August 12, 2019 at 12:49 PM, when the SPS control room operator notified its TOP of the alternative voltage controlling device status change for the aforementioned Facility, for a total of 1 day, 10 hours, and 51 minutes. The root cause of this issue was that the SPS Control Center (CC) was not aware of the meter failure because no alarms had been set to notify the SPS CC of meter failures. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In this instance, SPS failed to notify its TOP of a change in status of its alternative voltage controlling device, its 84 MVA wind generating Facility, within 30 minutes of the change, as required by VAR-002-4.1 R3. Failure to notify the TOP of the status change on the alternative voltage controlling device, for an 84 MVA wind generating Facility, could have resulted in the TOP having inaccurate alternative voltage controlling device status in its Operating Plan and Real-time Assessment which could have led to voltage schedules not being properly met and reactive support not being provided when needed. However, as compensation, the Facility’s voltage only fell outside the preferred range twice throughout the duration of this issue reducing the risk. Additionally, the Facility contributes 84 MVA to the grid and does not provide significant voltage support to the interconnection. No harm is known to have occurred. | To mitigate this violation, the entity has performed the following actions: 1) notified its TOP of the alternative voltage controlling device change; 2) replaced the failed meter at the wind generating Facility; 3) created alarms to detect improper reactive conditions specifically improper VAR support based on grid voltage and plant real power generation; 4) created alarms to detect a failed meter; and 5) added the following tasks to its internal tracking software: a) verify that the alarm to detect improper reactive conditions and the alarm to detect a failed meter are implemented at new sites; b) test alarms during commissioning. | WECC applied a mitigating credit for the following reasons: 1) SPS self-reported these violations in a timely manner from the date of discovery. 2) SPS accepted responsibility and admitted to the violations. 3) SPS agreed to settle these violations. WECC considered the following as aggravating factors and justification for the escalation of the disposition of these minimal risk violations to an expedited settlement agreement: the violations’ Real-time Operations violation time horizon expectation for remediation, multiple and overlapping root causes at the same Control Center for the same Standard and Requirement, repeated violations demonstrating a system problem.