## Redacted for Public Posting
Reported Quarter and Year | Regional Entity | Registered Function(s) | Nominal Voltage Rating of the Circuit (kV) | Has the reported circuit experienced a previous vegetation-related transmission outage within the last eight reporting quarters? | Element of IROL or Major WECC Transfer Path? | Outage Start Date | Outage Duration (mins) | Detailed Description of the Cause of the Outage | Category Associated with the Sustained Outage | If the vegetation causing the outage was located outside of the ROW, provide the horizontal distance to the edge of the ROW. | If the vegetation causing the outage was located outside of the ROW, provide the horizontal distance to the nearest conductor. | Tree Type | Tree Height (ft) | Tree Condition | Mitigation/remediation actions taken by Registered Entity to address recurrence of the contact/encroachment.
Q1 2025 | SERC | GO, TO | 230 | No | No | 2025-02-17 | 10510 | A 116' tall read oak uprooted and locked a line. Heavy rains saturating the ground and high winds attributed to the oak uprooting. | 3 | 33 | 62 | Red Oak | 116 | Healthy | Forester patrolled adjacent spans and area.
Q1 2025 | SERC | GO, TO | 230 | No | No | 2025-02-16 | 1516 | Large diameter oak tree uprooted and fell across outside conductor | 3 | 26 | 49 | Oak | 85 | Green | The immediate area was ground patrolled to identify any additional hazard trees
Q1 2025 | SERC | GO, TO | 230 | Yes | No | 2025-03-19 | 847 | A large pine tree fell in a high wind event during a frontal storm. The tree was hollow and burned due to forestry control burns. | 3 | 5 | 37 | Pine | 110 | The tree was in poor conditions, hollow and burnt inside, due to forestry control burns. | Tree removed. Surrounding area was patrolled for similar trees and had them removed
Q1 2025 | WECC | GO, TO | 230 | Yes | No | 2025-02-13 | 1496 | Tree broke at stem due to combination of heart rot, wind, and snow | 3 | 35 | 55 | Western Hemlock | 72 | Alive | N/A
Q4 2024 | SERC | GO, TO | 230 | No | No | 2024-10-10 | 236 | An alive hickory tree, off the right of way, made contact and hung on the 230kV line. The tree was remvoed and the line was returned to service. Soil conditions were dry. | 3 | 8 | 49 | Hickory | 81 | The tree was alive | Additional tree trimming was performed.
Q4 2024 | SERC | GO, TO | 230 | Yes | No | 2024-10-05 | 296 | A 70' pine tree broke and fell on the conductor due to a large canker spot approx 8' from ground level. | 3 | 5 | 47 | pine | 70 | A 70' pine tree broke and fell on the conductor due to a large canker spot approx 8' from ground level. | Ground patrol took place and no other diseased trees found.
Q4 2024 | NPCC | GO, TO | 115 | No | Yes | 2024-11-28 | 1130 | Tree uprooted and fell onto the phase. The tree top was caught in conductors. | 3 | 7 | 62 | White Pine | 100 | Tree uprooted during wind and snowy conditions. | The tree was removed and additional trees in area were inspected.
Q4 2024 | WECC | GO, TO | 230 | No | No | 2024-11-19 | 8637 | Trees uprooted in soft soil from high winds | 3 | 65 | 85 | Cottonwood | 95 | The tree was alive | The tree was removed and additional trees in area were inspected.
Q4 2024 | WECC | GO, TO | 230 | Yes | No | 2024-11-19 | 5310 | Trees uprooted in soft soil from high winds | 3 | 100 | 120 | Douglas Fir | 150 | The tree was alive | The tree was removed and additional trees in area were inspected.
Q4 2024 | WECC | GO, TO | 230 | Yes | No | 2024-11-19 | 7451 | Trees uprooted in soft soil from high winds | 3 | 15 | 35 | Douglas Fir | 55 | The tree was alive | The tree was removed and additional trees in area were inspected.
Q4 2024 | WECC | GO, TO | 230 | Yes | No | 2024-12-14 | 308 | A healthy tree outside the ROW fell | 3 | 35 | 37.5 | Western Hemlock | 117 | The tree was in good condition. | Continued to monitor surrounding property for signs of forest decline.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-26 | 709 | A healthy red oak uprooted during a high wind event and fell onto the line from outside the right of way. | 3 | 17 | 54 | Red Oak | 92 | Healthy | Adjacent trees were inspected and no additional concerns were found.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-09-27 | 16812 | A healthy red oak uprooted during Storm Helene and fell on the outside conductor resulting in line locking out. | 3 | 20 | 55 | Red Oak | 86 | Healthy | Location was inspected to identify/mitigate any vegetation concerns
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-13 | 642 | An off the right-of-way an alive pine tree with root rot made contact and hung on the line. The tree was removed and the line was returned to service. The soil conditions were dry. | 3 | 4 | 46 | Sweetgum | 82 | Alive | Removed one dead pine and spot trimmed 2 hardwoods
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-17 | 3699 | An off the right-of-way alive and healthy oak tree made contact and hung on the line. The tree was removed and the line was returned to service. Soil condition were wet and thunderstorms were in the area. | 3 | 21 | 56 | Oak | 98 | Alive | The tree was in a recent cut over. The remaining residual trees, left by the loggers, were cut so they would not fall and hit the line.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-09-17 | 550 | A 100-foot healthy pine tree fell from 29 feet off right-of-way. | 3 | 29 | 89 | Pine | 100 | Healthy | Patrolled and found no other trees that required work at this time.
Q3 2024 | SERC | GO, TO | 230 | no | no | 2024-08-19 | 963 | A healthy willow tree was struck by lightning in a storm fracturing the tree trunk. A limb leaned toward the conductor and made contact due to the high wind. | 3 | 7 | 39 | Willow | 50 | Healthy | The tree was removed and the grounds were patrolled
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-04-10 | 432 | A 20" diameter red oak split and uprooted fell into a three-phase distribution circuit and the top of the tree rested in the line across the outside conductor. The tree was a 3-stem codominant trunk, with the codominant union originating at just below the ground level and extending up to about 3-4 feet above ground. The three stems were each approximately 20"+ and approximately 90-100 feet tall. All 3 stems at the codominant union, with the one trunk that was facing the right of way, falling at a 90-degree angle to the link. There were visible broken roots below the ground. | 3 | 43 | 78 | Red Oak | 100 | Co-Dominant stem | Entity personnel walked adjoining spans on same side of the ROW to inspect the trees. The area is in a residential neighborhood resulting in a limited woodline in that area. Six additional trees have been marked as potential hazard trees and will be taken down.
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-05-27 | 960 | A 22" diameter red oak approximately 85 feet tall failed at roughly 35 feet from the ground fell across the line pinning both phases to the ground. This area experienced sustained and heavy wind for several days leading to several uprooted trees in the surrounding area. The tree was a healthy and full crown and no visible defects from the ground. | 3 | 1 | 36 | Red Oak | 85 | This tree had minor fungal growth about 35 feet up the main stem where it broke and fell into the ROW. Within the tree rot was visible only after the tree broke in half. | Entity personnel performed a visual inspection of the surrounding spans in this area. A tree crew was sent to the area to clean up the fall in, remove a dead tree located outside the ROW, and remove a Virginia Pine that was leaning due to the same wind storm.
Q2 2024 | SERC | GO, TO | 345 | no | no | 2024-05-28 | 93 | A 92ft oak tree fell from outside the right of way (ROW) due to erosion around the roots. | 3 | 17 | 68 | OAK | 92 | Erosion around the root | NA
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-04-03 | 839.53 | A live tree uprooted off right of way (ROW) causing damage to outside conductor. There was storms and high winds 24 hours prior to tree failure. | 3 | 15 | 62.5 | sweet gum | 85 | live, sound | Performed vegetation patrol of the immediate area.
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-05-10 | 12 | A tall oak tree, approximately 100', fell at an angle toward the line in a low area due to the wind and rain from a storm. The tree top brushed against "A" and "C" phase conductors causing the line to trip and lock out. The tree was located approximately 35' off the right of way (ROW) and 100' south of the structure. | 3 | 35 | 61 | Oak | 100 | live and healthy | Lidar and ground inspections performed per Transmission Vegetation Management Plan (TVMP). Additional ground inspection performed for this section of line to identify any additional vegetation concerns.
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-05-30 | 902 | A dead oak tree fell during a thunderstorm with high winds. | 3 | 8 | 40 | Oak | 70 | dead oak tree | Foot patrol the area and no findings
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-06-01 | 735 | A healthy pine tree fell due to high winds in a thunder storm | 3 | 15 | 47 | Pine | 85 | healthy pine tree | Foot patrol the area and no findings
Q2 2024 | SERC | GO, TO | 230 | no | no | 2024-04-11 | 1026 | A small green pine tree with an unhealthy hollow base fell on the conductor in a thunderstorm event. | 3 | 8.5 | 50.5 | Pine | 75 | unhealthy pine tree with hollow base | Foot patrol the area and no findings
Q2 2024 | WECC | GO, TO | 230 | no | no | 2024-06-27 | 273 | A live spruce tree fell into the line during thunderstorm with heavy rains and winds. That cleared itself. The line was tested and returned to service. | 3 | 1 | 41 | Spruce | 110 | Live | Crew investigated the area. This section of the line in on the national forest. The entity plans to work with the authorities to plan for mechanical re-treatment in 2025 or 2026.
Q2 2024 | RF | TO | 345 | no | no | 2024-06-25 | 1650 | Severe thunderstorm knocked down the tree from outside the ROW | 3 | 30 | 80 | Shagbark Hickory (Deciduous, hardwood) | 90 | healthy | Removed tree. The entity's TVMP includes budget for danger tree removal. The entity expects to remove danger trees when they are found during inspections.
Q1 2024 | SERC | GO, TO | 500 | No | yes | 2024-03-20 | 24430 | During a period of sustained wind, a contact between the conductor and a Hickory tree located 23 feet outside of the ROW has occurred. | 3 | 23 | 61 | Hickory | 49 | Healthy | Tree was removed and surrounding area inspected.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-01-14 | 199 | A healthy Pine tree 31 feet outside of the ROW made contact with a 230 kV line. The tree was removed and the line was returned to service. Soil conditions were wet and rain and high winds were in the area. | 3 | 31 | 36 | Pine | 87 | Alive | Two trees next to the tree in question were cut down due to cankers.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-02-28 | 1138 | A live Hickory tree with root rot made contact a 230 kV line. The tree was removed and the line was returned to service. Soil conditions were wet and storms and strong winds were in the area. | 3 | 10 | 53 | Hickory | 80 | Alive | No additional issues observed.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-02-11 | 326 | As a result of winds and saturated soil conditions, several large hardwood trees uprooted and fell on a 40 foot tall hardwood tree located 3 feet outside of the ROW, causing it to uproot and contact the conductor. | 3 | 3 | 31 | Maple | 50 | Healthy | Tree was removed and surrounding area inspected.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-03-17 | 154 | A dead Virginia pine broke about 4 feet from the base and contacted the line. | 3 | 6 | 61 | Virginia pine | 85 | External decay | Tree was removed and surrounding area inspected.
Q1 2024 | SERC | GO, TO | 230 | No | No | 2024-01-09 | 420 | During thunderstorm and high winds, a pine tree between broke off during a thunderstorm and fell into the transmission line. The three was removed off the line. Neither the conductor or structures sustained any damage. | 3 | 8 | 42 | Pine | 74 | The roots of the pine tree showed sign of deterioration due to an old injury at the ground line | Surrounding area was foot patrolled. No findings.
Q1 2024 | WECC | GO, TO | 230 | Yes | No | 2024-01-10 | 480 | A Douglas fir tree uprooted due to high wind and soft soil and fell into the line. | 3 | 20 | 40 | Douglas Fir | 155 | Alive | No additional issues observed.
Q1 2024 | WECC | GO, TO | 230 | Yes | No | 2024-01-13 | 1431 | A Western hemlock uprooted due to high wind and soft soil and fell into the line. | 3 | 23 | 43 | Western Hemlock | 68 | Alive | No additional issues observed.
Q1 2024 | WECC | GO, TO | 230 | Yes | No | 2024-02-16 | 3060 | During high winds. a large cottonwood tree broke off and fell into a Douglas fir, causing it to break off and contact a line. | 3 | 7 | 27 | Douglas Fir | 85 | Alive | No additional issues observed.
Q1 2024 | WECC | GO, TO | 60 | No | Yes | 2024-03-01 | 2981 | During heavy snow, a pine tree broke off and struck line. | 3 | 33 | 43 | Lodgepole pine | 100 | Healthy | Inspection completed. No additional issue was identified.
Q1 2024 | WECC | GO, TO | 230 | No | No | 2024-03-05 | 1 | During heavy snow, a large cedar tree uprooted from outside of the ROW and struck line. | 3 | 53 | 97 | Incense Cedar | 114 | Live and healthy | Inspection conducted to in vicinity of impacted tree to identify any additional trees.
Q1 2024 | WECC | GO, TO | 230 | No | N0 | 2024-01-08 | 630 | During high wind and heavy rain, a hemlock tree 35 feet off the ROW broke and fell into the line. | 3 | 35 | 35 | Western Hemlock | 117 | Good | Surrounding area was inspected for signs of forest decline.
Q4 2023 | SERC | TO | 230 | No | No | 2023-10-14 | 3862 | The top portion of a dead Sweetgum tree that was outside the right-of-way fell into the line. | 3 | 12 | 52 | Sweetgum | 70 | Dead | Tree was removed and surrounding area inspected.
Q3 2023 | NPCC | TO | 115 | No | Yes | 2023-07-15 | 8 | A healthy Cottonwood tree was uprooted on the south side of the right-of-way during a thunderstorm. The saturated ground surrounding the tree and the added wind caused the tree to fall. | 3 | 41 | 78 | Cottonwood | 99 | Healthy | Tree was removed and surrounding area inspected.
Q3 2023 | NPCC | TO | 345 | No | No | 2023-09-07 | 1413 | A Locust tree from outside the right-of-way fell into the conductor during a severe wind and rain storm. | 3 | 10 | 60 | Locust | 80 | Healthy | The tree was removed. No damage was done to the conductor. The entire line was patrolled with no additional issues identified prior to restoring.
Q3 2023 | RF | TO | 230 | No | No | 2023-09-24 | 2928 | An outwardly healthy Virginia Pine tree uprooted during a wind event and fell into the line. Upon further examination, the roots showed signs of potential root decay and may have contributed to the fall. | 3 | 39 | 115 | Virginia Pine | 103 | Outwardly healthy | When investigating the fault, surrounding spans were reviewed to ensure there were no other existing tree conditions related to this incident. No other vegetation concerns were identified.
Q3 2023 | RF | TO | 230 | No | No | 2023-07-22 | 234 | A Hickory tree from outside the right-of-way split out and fell into the conductor. It made contact but self-cleared from the line. | 3 | 30 | 65 | Hickory | 100 | Healthy | Tree was removed and surrounding area inspected.
Q3 2023 | SERC | TO | 230 | No | No | 2023-07-14 | 461 | An oak tree from outside the right-of-way fell into the line during a storm. The tree's root system was damaged when the property owner logged the surrounding area, leavening nothing to sustain the tree's roots during the storm. | 3 | 14 | 60 | Oak | 75 | Good | Two adjacent trees in the same wet area were cut down to avoid similar falls into the right-of-way.
Q3 2023 | SERC | TO | 230 | No | No | 2023-07-30 | 150 | A Pine tree from outside the right-of-way fell into the line during stormy weather conditions. | 3 | 16 | 46 | Pine | 93 | Living and otherwise healthy | Tree was removed and surrounding area inspected.
Q3 2023 | SERC | TO | 230 | No | No | 2023-08-07 | 243 | A Pine tree from outside the right-of-way fell into the line during stormy weather conditions. | 3 | 7 | 45 | Pine | 75 | Green | Tree was removed and surrounding area inspected.
Q2 2023 | SERC | GO, TO | 230 | No | No | 2023-06-03 | 371 | A Hackberry tree from off the right-of-way broke in a thunderstorm and fell into the line. Neither the conductor nor the structures sustained any damage. | 3 | 7 | 39 | Hackberry | 55 | Healthy | The tree was removed off the line. A patrol of the area did not find any other damaged trees.
Q2 2023 | SERC | GO, TO | 230 | Yes | No | 2023-05-27 | 283 | An alive and healthy Sweetgum tree from off the right-of-way made contact and hung on the line during a thunderstorm. | 3 | 24 | 58 | Sweetgum | 86 | Alive and healthy | No additional vegetation issues were observed. The tree was removed and the line returned to service.
Q2 2023 | SERC | TO | 230 | No | No | 2023-04-30 | 200 | A live Northern Red Oak with internal decay fell from off the right-of-way and pinned the line to the ground during a high wind event. | 3 | 1 | 43 | Northern Red Oak | 102 | Live, internal decay not visible from outside | The surrounding area was patrolled for other storm-related hazards.
Q2 2023 | SERC | TO | 230 | No | No | 2023-04-01 | 260 | A Sweetgum tree with decay on the backside of tree fell onto the line from off the right-of-way during a thunderstorm. | 3 | 8 | 39 | Sweetgum | 65 | Decay on backside | The immediate area was patrolled to identify any additional hazardous trees.
Q2 2023 | SERC | TO | 230 | No | No | 2023-04-01 | 275 | A Hickory tree with root decay and a light systemic fungal infection from off the right-of-way fell into the line. | 3 | 25 | 70 | Hickory | 91 | Root decay and a light systemic fungal infection | The line crew patrolled the area and followed up by performing an aerial patrol. No hazards were observed during the patrols.
Q1 2023 | RF | TO | 230 | No | No | 2023-03-03 | 1564 | An off-corridor, outwardly healthy, White Pine tree broke at the trunk 12' from the ground. The tree appeared healthy externally, but upon examination after failure, the tree was found to have some internal decay; however, no internal decay was observed at the point of failure. The tree failed during a high wind weather event and subsequently fell into the ROW contacting the conductor. Radar indicates that the outage location experienced high winds in the range of 41-44 mph at the time of the outage, which exceeds the threshold for the high wind weather exclusion. | 3 | 11 | 65 | White Pine | 94 | Healthy | During the investigation, surrounding spans were reviewed, but no further vegetation threats were identified.
Q1 2023 | WECC | GO, TO | 230 | Yes | No | 2023-01-04 | 1465 | During a high wind event, a healthy Douglas Fir was uprooted and blown into the line. | 3 | 18 | 38 | Douglas Fir | 85 | Alive | Tree was removed and surrounding area inspected.
Q1 2023 | WECC | GO, TO | 230 | Yes | No | 2023-01-09 | 1916 | During a high wind event, a Douglas Fir with root rot was uprooted and blown into the line. | 3 | 30 | 50 | Douglas Fir | 75 | Alive with root rot | Tree was removed and surrounding area inspected.
Q1 2023 | WECC | TO | 230 | No | No | 2023-03-28 | 1346 | A Ponderosa Pine was snow loaded and fell into the line due to a recent atmospheric river event. | 3 | 8 | 60 | Ponderosa Pine | 75 | Healthy | Tree was removed and surrounding area inspected with LiDAR.
Q1 2023 | WECC | TO | 230 | No | No | 2023-03-28 | 373 | A dead Lodgepole Pine off the right-of-way in saturated soil conditions with tree leaning resulted in the roots breaking and the tree landing on the conductor. | 3 | 5 | 38 | Lodgepole Pine | 70 | Dead | The dead tree, as well as an additional tree at the site, were removed The surrounding area was survey for other potential hazards.
Q4 2022 | NPCC | TO | 115 | No | Yes | 2022-12-03 | 1486 | An Ash tree that was dead from the effects of Emerald Ash Borers was uprooted during high winds and fell into the line from outside the right-of-way. | 3 | 18 | 58 | Ash | 80 | Dead from Emerald Ash Borers | Tree was removed and area inspected for other dead trees.
Q4 2022 | SERC | TO | 230 | No | No | 2022-12-23 | 268 | During a thunderstorm, a Red Oak fell onto a conductor from outside the right-of-way. | 3 | 1 | 43 | Red Oak | 90 | Alive and healthy | Tree was removed and surrounding area inspected for other storm-related hazards.
Q4 2022 | SERC | GO, TO | 230 | No | No | 2022-10-18 | 499 | During a thunderstorm, a Red Oak fell into the line from outside the right-of-way. Upon investigation, it was the determined there was internal decay. | 3 | 59 | 99 | Red Oak | 110 | Internal decay | Tree was removed and surrounding area inspected.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-11-04 | 2768 | During a high wind event, a healthy Western Hemlock was blown into the line. | 3 | 25 | 50 | Western Hemlock | 90 | Alive and healthy | Tree was removed and area inspected, at which time a separate 60-foot-tall Western Hemlock also outside the right-of-way was discovered on the line.
Q4 2022 | WECC | GO, TO | 230 | No | No | 2022-11-04 | 2755 | During a high wind event, a healthy Douglas Fir was blown into the line. | 3 | 15 | 36 | Douglas Fir | 120 | Alive and healthy | Tree was removed and area inspected, at which time a separate 110-foot-tall Western Red Cedar also outside the right-of-way was discovered on the line.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-12-08 | 1303 | Heavy snow load caused a tree to break off at the base and fall into the line. | 3 | 10 | 35 | Western Hemlock | 65 | Alive and healthy | Tree was removed and surrounding area inspected.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-11-17 | 1183 | A large Douglas Fir at the edge of the right-of-way lost its codominant tops in gale force winds, one of which made contact with and pinned down the line. | 3 | 1 | 28 | Douglas Fir | 110 | Codominant tops 67 feet up the trunk, otherwise alive and healthy | Tree was removed and surrounding area inspected.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-12-22 | 1419 | A healthy Douglas Fir tree standing on the uphill side of a creek blew over in high gusty winds, compromising two Alder trees. All three trees struck the line. | 3 | 55 | 73.5 | Douglas Fir | 124 | Alive and healthy | Tree was removed. An annual inspection conducted earlier in the year showed no other signs of concern.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-12-27 | 1623 | A healthy Alder tree in sandy soil on a steep hillside was uprooted in heavy rains and gusty winds and fell into the line. | 3 | 19 | 55 | Red Alder | 80 | Alive and healthy | Tree was removed. An inspection occurs on this line every year.
Q4 2022 | WECC | GO, TO | 230 | Yes | No | 2022-11-04 | 631 | The soil around a Douglas Fir became saturated from a wind and rain storm and fell into the line from outside the right-of-way. | 3 | 58 | 95 | Douglas Fir | 110 | Alive and healthy | Tree was removed and surrounding area inspected.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-09-03 | 406 | A dead oak tree broke in a storm and fell through the transmission line. Neither the conductor nor the structures sustained any damage. | 3 | 7 | 40 | Oak | 65 | Dead and decaying (broke into pieces when tree hit the ground) | Tree identified in line patrol and removed. Thorough line patrol to identify potential hazard trees. None identified.
Q3 2022 | SERC | GO, TO | 230 | Yes | No | 2022-07-06 | 473 | A live Loblolly Pine with canker on the trunk made contact with the line. The tree was removed and the line returned to service. The tree was removed and the line returned to service. The soil condition was dry. Thunderstorms and a possible tornado were in the area. | 3 | 24 | 54 | Loblolly Pine | 78 | Alive with canker on trunk | The tree was removed and the line returned to service.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-07-25 | 146 | A live and healthy Sweetgum tree made contact with the line. The tree was cut to ground and removed and the line returned to service. The soil condition was wet. Strong winds and rain was in the area. | 3 | 15 | 47 | Sweetgum | 75 | Alive and healthy | The tree was cut to ground and removed and the line returned to service.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-08-11 | 518 | A live Loblolly Pine tree with some root rot made contact with the line. The tree was removed and the line returned to service. The soil condition was dry. Thunderstorms were in the area. | 3 | 27 | 56 | Loblolly Pine | 80 | Alive with some root rot | The tree was removed and the line returned to service.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-08-10 | 53 | A dead and decaying Hackberry tree fell through the line. | 3 | 10 | 40 | Hackberry | 60 | Dead and decaying | Tree was removed.
Q3 2022 | SERC | GO, TO | 230 | No | No | 2022-07-15 | 174 | Adverse weather from the night before caused a large Red Oak tree with internal decay - possibly due to a lightning strike in the past - to fall into a Pine tree, which fell into the line. | 3 | 22 | 69 | Red Oak, Pine | 73 | Healthy | Tree was removed.
Q3 2022 | SERC | TO | 230 | No | No | 2022-09-30 | 164 | Strong winds from Hurricane Ian caused a live Loblolly Pine tree to break six feet above the base and fall into the line. | 3 | 10 | 40 | Loblolly Pine | 83 | Live | Tree was removed.
Q3 2022 | SERC | TO | 230 | No | No | 2022-09-30 | 325 | Strong winds from Hurricane Ian uprooted a live Loblolly Pine and it fell into the line. | 3 | 2 | 32 | Loblolly Pine | 72 | Live | Tree was removed.
Q2 2022 | NPCC | TO | 115 | No | Yes | 2022-06-17 | 595 | A healthy basswood tree uprooted and fell at an angle toward the line. | 3 | 12 | 68 | Basswood | 79 | Healthy | A small oak tree that was bent over by the fallen basswood is being removed.
Q2 2022 | SERC | GO, TO | 230 | Yes | No | 2022-06-16 | 195 | A tree uprooted and fell on to the northern base of the line pinning it to the ground. The soil was saturated due to recent heavy rains. | 3 | 35 | 47 | Pine | 85 | Healthy | A ground visual inspection of trees in the area didn’t find any others that posed a danger to the line. No further action was required.
Q2 2022 | SERC | GO, TO | 230 | No | No | 2022-06-08 | 148 | A large poplar tree broke off three feet from ground level and fell into another large polar tree that was uprooted and fell into the line. | 3 | 50 | 69 | Poplar | 98 | Healthy | Significant storm came through the area, producing very high wind gusts and rainfall within a matter of an hour.
Q2 2022 | SERC | GO, TO | 230 | No | No | 2022-05-29 | 1 | A palm tree off the right-of-way failed at the base of the tree and made contact with the conductor. | 3 | 19 | 27 | Washingtonian Palm | 53 | Dead | Tree was removed and area inspected.
Q2 2022 | SERC | GO, TO | 230 | No | No | 2022-06-25 | 417.07 | A water oak failed during a major storm event, falling on the outside of the conductor. | 3 | 3 | 38 | Water oak | 66 | Live, internal decay not visible from outside | Local storm event, patrolled area for other storm-related hazards.
Q2 2022 | WECC | TO | 60 | Yes | Yes | 2022-04-04 | 213 | A healthy sugar pine with no visual defects completely uprooted and made contact with the line after the ground became saturated with snow melt. | 3 | 20 | 40 | Sugar Pine | 60 | Healthy | Site inspection that will address high risk trees based on poor taper condition of tree or site conditions identified by LiDAR along the adjacent spans in either direction to the outage span.
Q1 2022 | SERC | GO, TO | 230 | No | No | 2022-01-18 | 1414.57 | A tree uprooted and fell into the line causing an outage, caused by strong winds after an ice storm. | 3 | 2 | 46 | Water oak | 69 | Live tree with internal decay | Tree was removed from line and line was patrolled for any other tree issue.
Q1 2022 | SERC | GO, TO | 230 | Yes | No | 2022-01-12 | 109 | A tree from outside the right-of-way fell into the line, caused by the back side of the trunk base being burned through after a controlled burn. | 3 | 10 | 40 | Pine | 88 | Healthy tree but was still smoldering from a controlled burn the previous day and had a large wound on the base of the trunk at ground level that had burned through | A foot patrol was conducted along the ROW of the controlled burn area to identify other trees that exhibited a similar condition. One live pine was identified as leaning and a canker was noted on another live pine. Both pines were removed.
Q1 2022 | SERC | GO, TO | 230 | No | No | 2022-01-17 | 122 | A tree fell into the line from outside the right-of-way during Winter Storm Izzy. | 3 | 6 | 39 | Pine | 60 | Live | The entire area was air-patrolled and the immediate surrounding area was ground-patrolled to identify any additional threats.
Q1 2022 | SERC | GO, TO | 230 | Yes | No | 2022-01-03 | 3130 | A red oak uprooted and made contact with the line, pinning it to the ground, caused by wet snow built up from the previous day's winter storm. | 3 | 11 | 58 | Red Oak | 85 | Healthy | Line corridor ground was patrolled by line crew and followed up with an aerial patrol. No hazards were observed during the patrols.
Q1 2022 | WECC | GO, TO | 230 | Yes | No | 2022-01-07 | 1562 | A large Douglas Fir from outside the right-of-way uprooted during gusty winds and made contact with the line. | 3 | 100 | 132 | Western Hemlock and Douglas Fir | 155 | Healthy | Annual inspection conducted in spring of 2021. Other trees in the area inspected, but no others showed signs for concern of failure.
Q1 2022 | WECC | GO, TO | 230 | No | No | 2022-01-02 | 1050 | A Douglas Fir was uprooted in a storm with heavy winds and precipitation and fell into the line. | 3 | 19 | 51 | Douglas Fir | 107 | Healthy | Tree was removed.
Q1 2022 | WECC | GO, TO | 230 | Yes | No | 2022-01-06 | 49808 | Heavy snow and high winds caused four trees in separate locations to fall into the line from outside the right-of-way. | 3 | 25 | 35 | Douglas Fir | 80 | Healthy | Additional damaged trees were removed.
Q4 2021 | SERC | TO | 230 | No | No | 2021-12-07 | 222 | A dead pine fell from off the right-of-way into the line. Tree height is estimated because it broke into multiple pieces. | 3 | 5 | 35 | Pine | 65 | Dead, tree height is estimated because it broke into multiple pieces. | The surrounding area was patrolled to determine if any additional threats existed. None were found.
Q4 2021 | WECC | TO | 60 | No | Yes | 2021-12-14 | 1210 | A tall Lodgepole pine with poor taper was snow loaded and bent over the line due to heavy storm and a recent atmospheric river event. | 3 | 3 | 23 | Lodgepole Pine | 65 | Healthy | Tree was removed and area inspected.
Q4 2021 | WECC | TO | 115 | No | Yes | 2021-12-14 | 2136 | A tall lodgepole pine broke off during a heavy snow storm and fell into the line. | 3 | 17 | 32 | Lodgepole Pine | 100 | Healthy | Tree was removed and area inspected.
Q4 2021 | WECC | GO, TO | 230 | NO | No | 2021-10-24 | 586 | A healthy Douglas Fir with no outward signs of failure fell into the line from outside the right-of-way during high winds. | 3 | 35 | 60 | Douglas Fir | 100 | Healthy | Tree was removed and area inspected.
Q4 2021 | WECC | GO, TO | 230 | Yes | No | 2021-11-01 | 2381 | High wind/rain created saturated soils causing whole tree to uproot. | 3 | 20 | 45 | Western Hemlock | 95 | Healthy | Tree was removed.
Q4 2021 | WECC | GO, TO | 230 | Yes | No | 2021-11-15 | 2877 | High wind/rain created saturated soils causing whole tree to uproot. | 3 | 10 | 30 | Douglas Fir | 55 | Healthy | Tree was removed.
Q4 2021 | WECC | GO, TO | 230 | No | No | 2021-12-25 | 4019 | Heavy snow/strong winds caused whole tree to fall. | 3 | 25 | 55 | Douglas Fir | 120 | Healthy | Tree was removed.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-07-14 | 108 | An isolated, severe thunderstorm impacted the area immediately surrounding the outage that included high winds, lightning and heavy rains resulting in many customer outages. A large oak tree from off the right-of-way fell into the line. | 3 | 35 | 86 | Oak | 111 | Live tree before storm damages. Growth defects included rotten center visible after all/split | Area was inspected for other danger trees. None identified.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-08-23 | 615 | During a severe thunderstorm, lightning struck a green slash pine. The tee failed at the base where the sap become overheated and blew out the structure of the tree base. The pine tree fell into the right-of-way and made contact with the conductor. | 3 | 15 | 52 | Slash Pine | 72 | Green, live tree | Tree was removed and area inspected.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-07-19 | 236 | A living pine tree from off the right-of-way broke 20 feet up and fell diagonally towards the line and landed on the line. No visible signs of decay were observed at the breakpoint. Weather at the time of outage was a passing though afternoon thunderstorm. | 3 | 9 | 76 | Pine | 90 | Live, sound | Tree was removed and area inspected.
Q3 2021 | SERC | GO, TO | 230 | No | No | 2021-08-24 | 25 | A tall gum tree fell at the an angle toward the line in a swampy area due to the wind and rain from summer storms. | 3 | 16 | 42 | Sweet gum | 90 | Live | Area was inspected
Q3 2021 | SERC | TO | 230 | No | No | 2021-07-28 | 7929 | A strong storm passed through part the corridor, and strong winds brought a 100 foot tall Sycamore tree down on the line. | 3 | 0 | 43 | American Sycamore | 100 | Tree was sheared 15 foot up the trunk by the wind, no noted damage to remainder of tree | Tree was removed and area inspected.
Q3 2021 | SERC | TO | 230 | No | No | 2021-08-10 | 413 | Extensive decay at the base of and back side of the tree caused the tree to split during the wind load of the storm and fall onto the line. | 3 | 16 | 59 | Red Maple | 75 | Extensive decay at the base of and on the back side of the tree | Tree was removed and area inspected.
Q3 2021 | SERC | TO | 230 | No | No | 2021-08-13 | 410 | The area experienced localized thunderstorms. A small grouping of 3-4 trees that were entangled in vines were uprooted in saturated soil and fell at a 90 degree angle onto the line. | 3 | 12 | 42 | Basswood | 70 | Entangled in vines in saturated soil | Tree was removed and area inspected.
Q3 2021 | SERC | TO | 230 | No | No | 2021-08-22 | 533 | A 75-foot-tall red oak, located off the right-of-way, fell onto the line. It had a crack up and down the main stem. The main stem failed six feet from the ground. | 3 | 11 | 44 | Red Oak | 75 | The tree had a crack up and down the main stem, rot was only visible after the tree fell | Tree was removed and area inspected.
Q3 2021 | WECC | GO, TO | 230 | No | No | 2021-09-18 | 165 | Declining Douglas Fir tree that was outside of the ROW fell onto the line. | 3 | 15 | 77 | Douglas Fir | 85 | Dying | Tree was removed and area inspected.
Q2 2021 | SERC | GO, TO | 230 | No | No | 2021-05-05 | 702 | A tree uprooted and fell onto the line. The tree fell as a result of strong gusty winds and saturated soil due to thunderstorms. There was no damage to either the wires or conductors. | 3 | 7 | 45 | Sweetgum | 65 | Healthy tree with no apparent wounds or insect issues | A ground visual inspection of trees in the area didn’t find any others that pose a danger to the line. No further action was required.
Q2 2021 | SERC | GO, TO | 230 | Yes | No | 2021-06-11 | 289 | A live sycamore tree with rot on the back side broke off and fell onto the line from outside the right-of-way. The tree fell to the ground and damaged the line conductors. The soil condition was dry. The line was repaired and restored to service. | 3 | 14 | 46 | Sycamore | 75 | Alive with rot on the back side (woods side) of the trunk where the tree broke off | No mitigation/remediation actions taken because tree fell to ground and no additional vegetation issues were observed.
Q2 2021 | SERC | GO, TO | 230 | Yes | No | 2021-06-15 | 234 | A live maple tree that appeared healthy fell into the line from outside the right-of-way. The top of the tree broke and made contact with the middle and outside phases, pulling them to the ground and damaging the line conductor. The soil condition was wet. The tree was removed from the line, and the line was returned to service. The damaged wire was later repaired. Storms and high winds were reported in the area. | 3 | 9 | 32 | Maple | 30 | Alive and healthy | Flight patrol was conducted as well as a foot patrol in vicinity of the outage.
Q2 2021 | SERC | TO | 230 | No | No | 2021-06-15 | 383 | A sweet bay magnolia fell onto the transmission conductor from outside the right-of-way. The tree was found to have decay at the base of the trunk causing the failure. | 3 | 2 | 32 | Sweet Bay Magnolia | 60 | Internal decay at base of trunk | Tree fell into the clear and no longer a threat. Surrounding area was patrolled and no other issues were identified.
Q2 2021 | SERC | TO | 500 | No | No | 2021-06-15 | 1149 | Due to local storms and wind conditions, a mature oak tree up-rooted and fell onto the outside conductor causing a transmission line outage. | 3 | 20 | 49 | Water Oak | 96 | Healthy and live with a rotten core that was discovered after tree fell and split | Transmission Vegetation inspected the area of storm impact and no other trees were identified to need maintenance
Q2 2021 | SERC | TO | 230 | No | No | 2021-05-04 | 193 | During a thunderstorm in area, a large hardwood tree uprooted and fell into the transmission line. | 3 | 6 | 40 | Hardwood | 65 | Healthy | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q2 2021 | SERC | TO | 230 | Yes | No | 2021-04-30 | 299 | An 85-foot-tall hickory tree fell over into line 2010 and lodged on a single phase distribution pole. | 3 | 5 | 30 | Hickory | 85 | The tree had a 2 foot area of decay below ground level. No decay was visible above grade. The tree appeared healthy - good leaf flush with good color. The tree did not uproot in the typical manner. Essentially, the tree separated from what should have been the root system. There was a single large root on one side of the stump providing nutrients. | A nearby white oak tree was removed the following day.
Q1 2021 | SERC | GO, TO | 230 | No | No | 2021-02-12 | 308 | A tree uprooted and fell onto the line pinning it to the ground. The soil was saturated due to recent heavy rains. There was no damage to either the wires or conductors. | 3 | 41.5 | 73 | Pine | 109 | Tree was healthy and had a wound approximately 15 feet from the ground with DBH of 23 inches. | A ground visual inspection of trees in the area didn’t find any others that pose a danger to the line. No further action was required.
Q1 2021 | SERC | GO, TO | 230 | Yes | No | 2021-02-16 | 192 | A living loblolly pine tree located outside the right-of-way fell to ground and made contact with the line. The tree had root rot-below grade and strong thunderstorms/winds were in the area. The tree was removed and the line was restored to service. | 3 | 4 | 36 | Loblolly Pine | 80 | Alive, but functional issue included: root rot - below grade | No mitigation/remediation actions taken because tree fell to ground and no additional vegetation issues were observed.
Q1 2021 | SERC | TO | 230 | No | No | 2021-01-26 | 825 | A tree from off the right-of-way fell onto the line. It was very windy and rainy that day. The soil was saturated and the root system appeared to have been damaged by Hurricane Zeta. | 3 | 15 | 59 | Pine | 85 | Healthy, but root system appears to have been weekend by Hurricane Zeta. | We performed an aerial patrol of the area to identify any other trees that appeared to be prone to falling on the line. We sent a vegetation crew to cut all identified trees.
Q1 2021 | SERC | TO | 230 | Yes | No | 2021-01-31 | 267 | Pine tree had been damaged during Hurricane Zeta and was leaning/lodged in another tree. During a thunderstorm, the other tree fell under the strain, and the leaning pine tree fell onto the transmission line. | 3 | 31 | 69 | Pine | 85 | Damaged - leaning on and lodged in another tree. | We performed an aerial patrol to identify danger trees. We then sent a vegetation crew in to remove the identified trees. Due to weather, we were unable to patrol the line until after this incident.
Q1 2021 | SERC | TO | 230 | No | No | 2021-02-18 | 924 | Heavy rainfall in the region associated with the flooding of the Great Pee Dee River swamp undermined a cluster of sycamore trees which floated into the line. | 3 | 5 | 39 | Sycamore | 55 | Healthy | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-14 | 5211 | A healthy Douglas Fir tree fell into the right-of-way during a high wind event. | 3 | 6.5 | 52 | Alder | 71 | Healthy | The tree was removed. A site inspection will be conducted to address high-risk trees in the area using LiDAR.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-19 | 5185 | A healthy Douglas Fir tree fell into the right-of-way during a high wind event. | 3 | 58 | 98 | Douglas Fir | 137 | Healthy | The tree was removed. A site inspection will be conducted to address high-risk trees in the area using LiDAR.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-19 | 2926 | A healthy Alder tree from outside the right-of-way during a high wind event. | 3 | 58 | 98 | Douglas Fir | 137 | Healthy | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 9509 | During a storm with strong winds, a Douglas Fir tree snapped and fell into the right-of-way. Restricted access and crew availability led to the extended outage. | 3 | 40 | 60 | Douglas Fir | 95 | Damaged | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 3679 | A Western Hemlock tree with root decay fell into the right-of-way during a storm with high winds. | 3 | 20 | 45 | Western Hemlock | 75 | Root Decay | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 3679 | A Douglas Fir tree with root decay fell into the right-of-way during a storm with high winds. | 3 | 45 | 65 | Douglas Fir | 104 | Root Decay | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-26 | 1026 | During a high wind event, a Hemlock tree with root rot broke off at ground level and fell into the right-of-way. | 3 | 26 | 46 | Western Hemlock | 65 | Root Rot | The tree was removed.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-02-13 | 1620 | During a high wind event, a healthy Douglas Fir tree fell into the right-of-way. | 3 | 65 | 90 | Douglas Fir | 145 | Healthy | The tree was removed.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-13 | 1127 | A healthy Douglas Fir tree fell into the right-of-way. | 3 | 71 | 105 | Douglas Fir | 135 | Healthy | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-13 | 588 | A damaged Douglas Fir tree fell into the right-of-way. | 3 | 25 | 80 | Douglas Fir | 150 | Damaged | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q1 2021 | WECC | TO | 230 | No | No | 2021-01-13 | 396 | A damaged Douglas Fir tree fell into the right-of-way. | 3 | 25 | 80 | Douglas Fir | 150 | Damaged | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q1 2021 | WECC | TO | 230 | Yes | No | 2021-01-13 | 475 | A damaged Douglas Fir tree fell into the right-of-way. | 3 | 25 | 80 | Douglas Fir | 150 | Damaged | The tree was removed. The surrounding property will continue to be monitored for signs of forest decline.
Q4 2020 | NPCC | TO | 230 | No | Yes | 2020-11-15 | 1105 | A wind event caused two outage events due to a fall-in from outside the right-of-way by one tree at the same location. | 3 | 7 | 31 | White Pine | 99 | Healthy | The tree lot adjacent to the right-of-way had been partially cleared for a new development. Following the event, the entity received permission to remove additional trees that may be susceptible to wind due to the recent clearing on the adjacent lot.
Q4 2020 | NPCC | TO | 115 | No | Yes | 2020-11-15 | 1119 | A wind event caused two outage events due to a fall-in from outside the right-of-way by one tree at the same location. | 3 | 7 | 31 | White Pine | 99 | Healthy | The tree lot adjacent to the right-of-way had been partially cleared for a new development. Following the event, the entity received permission to remove additional trees that may be susceptible to wind due to the recent clearing on the adjacent lot.
Q4 2020 | WECC | TO | 115 | Yes | Yes | 2020-11-08 | 434 | A dead Lodgepole Pine tree fell into the line from outside the right-of-way. | 3 | 10 | 40 | Lodgepole Pine | 75 | Dead | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared right-of-way.
Q4 2020 | WECC | TO | 230 | Yes | No | 2020-10-11 | 2547 | During a storm with high winds, a healthy Western Hemlock tree broke at 15' above the ground and fell from the edge of the right-of-way into the line. | 3 | 32 | 54 | Western Hemlock | 85 | Healthy | Tree was removed.
Q4 2020 | WECC | TO | 230 | Yes | No | 2020-11-25 | 918 | A healthy Birch tree fell into the right-of-way after a beaver gnawed the base of the tree. | 3 | 17.5 | 37.5 | Birch | 85 | Healthy | Continue to monitor surrounding property for signs of forest decline.
Q3 2020 | NPCC | GO | 345 | No | No | 2020-08-30 | 333 | A tree fell from outside the ROW and contacted the line. | 3 | 10 | 60 | Ash | 110 | Healthy appearance, interior rot | Inspection of the area of concern identified additional trees outside ROW but potential hazards; these trees are to be removed.
Q3 2020 | RF | TO | 230 | No | No | 2020-08-04 | 4561 | An off-corridor healthy White Pine tree approximately 71’ tall and 23” diameter at breast height uprooted due to high winds during Tropical Storm Isaias, and subsequently fell into the ROW, coming to rest approximately 7" from the conductor. Upon investigation, the tree was still leaning on fencing and suspended by distribution and communication wires. The White Pine tree was located approximately 9’ from the edge of the maintained ROW. No other trees in the surrounding spans uprooted during the tropical storm, but substantial damage was observed throughout. Radar indicates that the outage location experienced high winds in excess of 50 mph at the time of the outage. The National Weather Service issued a tropical storm warning for Tropical Storm Isaias that was travelling over the outage area, which indicated the storm may contain high winds in excess of 60 mph. | 3 | 9 | 59 | White Pine | 71 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions.
Q3 2020 | RF | TO | 230 | No | No | 2020-08-27 | 284 | An off-corridor healthy Red Oak tree approximately 98’ tall and 29.4” diameter at breast height uprooted due to high winds and subsequently fell into the ROW contacting the conductor. The Red Oak tree was located approximately 20’ from the edge of the maintained ROW. Radar indicates that the outage location experienced high winds in excess of 50-60 mph at the time of the outage. National Weather Service had issued a severe thunderstorm warning for the outage area, which indicated the storm may contain high winds in excess of 55 mph. | 3 | 20 | 75 | Red Oak | 98 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions. As information, three large trees, broken at base, were encountered on the access road and had to be removed to reach outage location.
Q3 2020 | RF | TO | 345 | No | No | 2020-07-12 | 5 | Fall-in from outside the ROW. An off-corridor healthy Red Oak tree approximately 91’ tall and 22” diameter at breast height uprooted due to saturated soil and a root system insufficient for the size of the tree, and subsequently fell into the ROW contacting the line. The Red Oak tree was located approximately 40’ from the edge of the maintained ROW. | 3 | 40 | 80 | Red Oak | 91 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions; one tree was struck by the Red Oak and fell at the time of the outage, and one other tree was identified for removal in the span.
Q3 2020 | SERC | GO, TO | 230 | No | No | 2020-08-06 | 243 | A Loblolly Pine tree from off the ROW, which appeared to be healthy, made contact with the 230 kV line. No damage to facilities. Strong thunderstorms were in the area at the time of event. | 3 | 10 | 42 | Loblolly Pine | 83 | Healthy, no visible signs of decay | Vines were cut and removed and area was sprayed.
Q3 2020 | SERC | TO | 230 | No | No | 2020-07-23 | 990 | A healthy Poplar Tree 90' off the ROW broke off about 8-10 feet up the tree. | 3 | 1 | 43 | Poplar | 74 | Healthy tree sheared off 8-10 feet up tree. | Tree was cut down. Adjacent spans in both directions were evaluated and additional potential danger trees were also mitigated and cut.
Q3 2020 | SERC | TO | 230 | No | No | 2020-07-13 | 56 | Oak tree with root decay fell 35 feet from off the right-of-way. | 3 | 35 | 65 | Oak | 87 | Evidence of root decay. | Tree was cut down and other trees in the adjacent spans were evaluated for potential risk to facilities and cut down as needed.
Q3 2020 | SERC | DP, TO | 230 | No | No | 2020-07-28 | 551 | An 86 foot tall red oak tree uprooted during a storm and hit the line. The tree was outside the right of way, 4 feet from the ROW edge, and 38 feet from the nearest conductor. The tree was a hazard tree, with a small defect on the backside that might have affected root growth and might have contributed to the uprooting. | 3 | 4 | 38 | Red Oak | 86 | The tree had a small defect on the backside at the bottom that might have affected root growth and might have contributed to the uprooting. | Adjacent areas were patrolled for other trees with visible damage. None were found.
Q3 2020 | WECC | TO | 230 | No | No | 2020-08-09 | 474 | A dead Douglas fir tree back in the stand broke about 12 feet from ground level and hit the line. The tree broke from a healthy, unmanaged stand of Douglas firs and big leaf maples. | 3 | 41.5 | 61 | Douglas Fir | 65 | dead | The stand was surveyed and 6 small, suppressed dead Douglas firs were felled.
Q3 2020 | WECC | TO | 230 | Yes | No | 2020-09-08 | 3791 | 24" Hemlock was alive, root failure due to root rot with strong wind out of east. Tree is located on the south side of the ROW, sitting on the west bank of a steep uphill section | 3 | 32 | 52 | Western Hemlock | 124 | Healthy | Tree was removed.
Q3 2020 | WECC | TO | 230 | Yes | No | 2020-09-23 | 401 | Hemlock Tree fell through and contacted the line. | 3 | 27 | 47 | Hemlock | 110 | Healthy | Tree was removed. Continue to monitor surrounding property for signs of forest decline.
Q2 2020 | NPCC | TO | <200 | No | Yes | 2020-06-06 | 1416 | During a strong wind event, a healthy Red Oak tree snapped 6 feet up from the base of the trunk, falling into the transmission line. | 3 | 14 | 62 | Red Oak | 70 | Healthy tree with no evidence of internal decay | The tree was removed and the area was inspected with no findings of additional vegetation issues identified.
Q2 2020 | RF | TO | 345 | No | No | 2020-05-29 | 183 | During a high wind in excess of 55 mph weather condition, a healthy Tulip Poplar tree approximately 20” diameter at breast height (DBH) uprooted, falling into the transmission line and contacting a conductor. | 3 | 8 | 53 | Tulip Poplar | 95 | Healthy | The surrounding spans were reviewed to ensure there were no other existing tree conditions. A total of 20 trees were uprooted or damaged as a result of the severe thunderstorm and high winds. The Tulip Poplar tree and 7 other trees were uprooted. Due to the severity of the storm and winds, an aerial saw was brought in to remove 12 additional trees which were unsafe to climb.
Q2 2020 | SERC | GO, TO | 230 | No | No | 2020-06-27 | 855 | During a strong thunderstorms, a live healthy loblolly pine from outside of the ROW fell and made contact with the transmission line. There was no damage to the facilities. | 3 | 4 | 36 | Loblolly Pine | 84 | Healthy, no visible signs of decay | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2020 | SERC | GO, TO | 230 | No | No | 2020-05-27 | 297 | During strong thunderstorm event, a tree off the ROW broke and pushed a healthy pine tree into the transmission lines. There were no damages to the facilities. | 3 | 22 | 54 | Pine | 86 | Healthy, no visible signs of decay. | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2020 | SERC | GO, TO | 230 | No | No | 2020-06-30 | 329 | An off right-of-way live water oak tree with internal decay broke at base and made contact with the transmission line. Tree had signs of internal decay and root rot, but signs were not externally visible. Strong thunderstorms were in the area at the time of event. | 3 | 10 | 31 | Water Oak | 76 | Tree was alive with root rot | Tree was removed from area and right of way was inspected for any other hazards. There were no damages to the facilities.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-05-16 | 565 | A 103 feet tall oak tree , 28 feet off the ROW split 10 feet from the ground, making contact with the line and causing an outage. | 3 | 28 | 61 | Oak | 103 | Tree appeared healthy from an aerial inspection during the spring helicopter patrol. The large tree had 2 codominant stems that split 10’ from the ground. Age of the tree and the weight of the stem facing the conductor caused the tree to fail. The tree showed signs of internal rot at the split that could not be seen during a visual inspection. | A tree crew was called to site to remove the tree from the conductors and line was restored. Additional off right of way danger trees have been identified and scheduled for removal during the routine vegetation maintenance of this section of line.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-05-01 | 953 | A 115 ft. maple tree fell into 62 ft. sweetgum making the sweetgum to fall on the conductor. | 3 | 12 | 44 | Maple/Sweetgum | 62 | Healthy | Tree cut from conductor and other trees evaluated for condition with additional tree work completed the next day.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-06-22 | 1025 | Off right-of-way poplar tree fell on the conductor during thunderstorm. | 3 | 23 | 55 | Poplar | 98 | Healthy | Tree was cut off the line. The area was inspected and other trees and vegetation observed in the immediate area for additional vegetation threats were removed.
Q2 2020 | WECC | TO | 230 | No | No | 2020-06-01 | 197 | A hemlock tree fell into the transmission line due to laminated root rot disease. | 3 | 26 | 46 | Hemlock | 75 | Dying | Tree was removed off the line. The entity will continue to monitor vegetation for signs of rot.
Q2 2020 | WECC | TO | 230 | No | No | 2020-06-01 | 329 | A cottonwood tree fell from outside of the ROW and made contact with conductor. | 3 | 19 | 60 | Cottonwood | 70 | Healthy | Tree was removed off the line. The entity will continue to monitor surrounding property for signs of forest decline.
Q1 2020 | WECC | TO | 230 | Yes | Yes | 2020-01-12 | 7636 | A Douglas fir tree back in the stand uprooted and fell into the trunk/base of another Douglas fir tree closer to the edge of the ROW, causing this tree to uproot and hit the line. The tree was alive but the now-exposed roots showed evidence of a possible root rot. This occurred during a snow event with an accumulation of approximately 30 inches in 72 hours with sustained winds of 15 to 18 mph and gusts of 35 to 40 mph. | 3 | 8 | 36 | Douglas Fir | 84 | Alive, but some rot present in the roots | The adjacent trees were surveyed for removal.
Q1 2020 | WECC | TO | 230 | Yes | Yes | 2020-01-22 | 17355 | A Douglas fir tree back in the stand uprooted and fell onto the line. The tree was alive and healthy. This occurred during a period in which the area received over 2 inches of rain in a 72 hour period and experienced sustained winds of 13-17mph and gusts of 32mph. | 3 | 34.5 | 83 | Douglas Fir | 95 | Alive/healthy | An adjacent, uprooted tree was removed and the stand surveyed.
Q1 2020 | WECC | TO | 230 | Yes | No | 2020-01-12 | 3058 | A Douglas Fir tree fell into the line due to root failure caused by high water flow undermining the bank. | 3 | 22 | 42 | Douglas Fir | 124 | Healthy | None
Q1 2020 | WECC | TO | 230 | Yes | No | 2020-03-15 | 580 | Large dead tree fell from outside ROW and brushed through circuit and fell to ground. | 3 | 62 | 90 | Western Hemlock | 100 | Dead | Continue to monitor surrounding property for signs of forest decline.
Q4 2019 | SERC | TO | 230 | No | No | 2019-12-22 | 3267 | During a weather event a pine tree located 35 feet off the ROW fell into two structures, breaking insulators and conductors. | 3 | 35 | 77 | Loblolly Pine | 93 | Tree was still green in the top but had beetle damage and was rotten at the trunk. | Forester and contract tree crew checked the area and removed any other danger trees. The line was also patrolled for any other potential danger trees.
Q4 2019 | SERC | TO | 230 | No | No | 2019-10-19 | 583 | During a tropical storm, a live red oak tree located 26 feet off the ROW fell on a transmission structure breaking a cross arm and insulators. The tree had root rot that was not visible during routine inspections. | 3 | 26 | 74 | Red Oak | 94 | The tree had root damage that was not visible during routine inspections | Tree was removed from area and right of way was inspected for any other hazards.
Q4 2019 | WECC | TO | 230 | Yes | Yes | 2019-10-29 | 2109 | A healthy Douglas fir tree on a steep slope that was located nearly 30 feet off the ROW was uprooted and fell into the line during a wind storm. | 3 | 29.5 | 66 | Douglas Fir | 88 | Alive healthy tree with no visible defects | The entity surveyed the outage site and took corrective action the following day to remove 2 additional trees that potentially could fall into the line.
Q3 2019 | RF | TO | 345 | No | Yes | 2019-07-20 | 1621 | A large tree was uprooted by strong wind moving through the area. | 3 | 2 | 40 | Ash | 88 | Live, healthy | Ground patrol was conducted to identify any hazards. The tree was safely removed to remediate the situation.
Q3 2019 | SERC | GO, TO | 230 | No | No | 2019-08-24 | 919 | During a thunderstorm, an off right-of-way live pine tree with internal decay at the base of the trunk broke at base and fell from outside ROW. | 3 | 6 | 38 | Loblolly Pine | 94 | Alive, but with decay at base of trunk. | None
Q2 2019 | RF | TO | 230 | No | No | 2019-06-29 | 1.63 | A healthy Red Oak tree was uprooted due to high winds in the area and subsequently falling into the ROW contacting the conductor, causing two sustained outages. | 3 | 8 | 41 | Red Oak | 65 | Healthy | The surrounding spans were reviewed to ensure there were no other existing tree conditions; no other issues were identified. This corridor is currently being worked for 2019 Maintenance.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-20 | 1077 | During a thundershower, a live pine tree broke approximately 14' above the ground contacting the transmission line. There were no damages to the facilities. | 3 | 5 | 58 | Pine | 78 | Healthy with no visible internal decay. | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-04-19 | 6 | During a weather event, a healthy oak tree fell into the line making contact long enough to cause a sustained outage. | 3 | 30 | 66 | Oak | 86 | Healthy | Checked several spans adjacent to tree location for additional vegetation issues and none were found.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-05-30 | 892 | A double-stemmed poplar tree fell onto the line causing the outage. Tree was found in a wetland area on a section of line where a strip of danger trees adjacent to the right-of-way was left by a logging operation months after routine utility vegetation maintenance had occurred. Area of right-of-way had been previously maintained using side-trimming aerial saw. | 3 | 4 | 38 | Poplar | 68 | Healthy | Tree was cut off of line and several spans adjacent to the location was patrolled for any additional vegetation issues. Additional potential danger trees were found and removed. The removed trees were prone to future wind damage that had been previously left adjacent to the right-of-way by outside logging operations.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-27 | 158 | Recent storms caused the tree to lean towards the line. The tree broke approximately 40’ high resulting in the top falling into the line. | 3 | 1 | 30 | Green Pine | 51 | Healthy green Pine | An inspection of the area was performed and no other hazard tree related issues were identified.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-06-20 | 1 | Tree fell onto the line and fell in the clear during a thunderstorm weather event causing an approximate one-minute outage. | 3 | 27 | 77 | Maple | 95 | Healthy | Line was patrolled for additional vegetation issues in several adjacent spans. No issues were found.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-22 | 411 | A loblolly pine tree fell into the line during thunder storm. | 3 | 2 | 45 | Loblolly Pine | 65 | Dead | Tree was removed from the line. Forester inspected the area and removed other trees as needed.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-22 | 860 | During a thunderstorms in the area, a healthy Sweet Gum tree broke off about six feet from the ground and fell on the conductor. Tree had no visible issues. | 3 | 14 | 57 | Sweet Gum | 85 | Green tree broke with no visible issues. | Forester inspected the area and removed other trees as well.
Q2 2019 | SERC | TO | 230 | No | No | 2019-05-14 | 275 | A Red Oak with root rot uprooted hitting the conductor, causing the outage. | 3 | 30 | 75 | Red Oak | 98 | Tree had root rot causing the failure. | Tree did not have to be removed from the line it brushed the conductor and fell to the ground. Forester inspected the area and removed diseased trees.
Q2 2019 | SERC | TO | 230 | No | Yes | 2019-06-20 | 103 | Strong winds in the area caused green pine tree to break off approximately 10 ft. up from ground falling onto outside conductor closest to edge of right of way. | 3 | 10 | 35 | Pine | 70 | Healthy green pine | An inspection of the area was performed. No other hazard tree were identified.
Q2 2019 | SERC | TO | 230 | No | Yes | 2019-06-22 | 470 | Strong winds in the area caused green oak to be uprooted, falling into the conductor closest to the edge of the right of way. | 3 | 8 | 32 | Oak | 78 | Healthy green oak | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q2 2019 | WECC | TO | 230 | Yes | No | 2019-06-06 | 621 | Wet soils in area caused a cedar tree to be uprooted, falling into a Hemlock and push it into line. | 3 | 25 | 45 | Western Hemlock | 60 | Healthy | An inspection of the area was performed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-05-18 | 6919 | During strong wind gust in the area, an oak tree fell into the line. The tree appeared to be healthy with a dense green canopy and showed no signs of distress such as included bark, disease or decay that would lead to its failure. The area has also experienced tornadoes and record rainfall during the previous months. | 3 | 16 | 76 | Swamp Laurel Oak | 90 | Healthy | Other identified hazard trees off the ROW were removed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-06-03 | 743 | Strong winds caused an oak tree to fall into the line. The area had received nearly 23 inches of rain prior to this event. | 3 | 9 | 60 | Southern Red Oak | 64 | Healthy | Other identified hazard trees off the ROW were removed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-05-26 | 1094 | During severe thunderstorm with wind gust of over 40 mph a healthy oak tree fell into the line causing a sustained outage. The tree was standing in over 12 inches of water due to recent flooding in the area. | 3 | 10 | 47 | Red Oak | 90 | Healthy | Other identified hazard trees off the ROW were removed.
Q1 2019 | WECC | TO | 230 | No | No | 2019-02-15 | 10980 | Due to a 3 days of heavy rain and wind storm in the area, a large healthy tree located 30 feet outside of the ROW fell into the transmission line. The tree was located on property owned by the county. The maintenance crew removed the tree, assessed the area and determined that no further work is necessary. | 3 | 30 | 111 | Ponderosa Pine | 158 | Healthy | None
Q1 2019 | WECC | GO, TO | 230 | Yes | No | 2019-01-06 | 3494 | A healthy tree broke off 18 feet above the ground during high winds and freezing rain-snow, falling into the transmission line. | 3 | 12 | 32 | Western Hemlock | 100 | Healthy | None
Q1 2019 | SERC | TO | 230 | No | No | 2019-01-20 | 1415 | An off right-of-way live pine tree with internal decay at the base of the trunk broke at base and made contact with the 230 kV line. There was no damage to the facilities. Tree had signs of internal decay, but signs were not externally visible. The soil condition was wet. Storms and high winds were recorded in the area. | 3 | 27 | 57 | Loblolly Pine | 81 | Alive with visible signs of decay at the root | None
Q1 2019 | SERC | TO | 230 | No | No | 2019-01-19 | 556 | A healthy tree uprooted and fell onto the east phase of the line pinning it to the ground between two structures. The soil was saturated due to recent heavy rains. There was no damage to either the wires or conductors. A strong storm front was passing though at the time of the outage. | 3 | 31 | 63 | Oak | 93 | Healthy | None
Q4 2018 | WECC | GO, TO | 115 | Yes | Yes | 2018-11-14 | 156 | A 50-foot tall dead Larch tree located 35 feet outside the Right of Way (ROW) fell into a 115 kV transmission line. The contact resulted in a sustained outage that lasted for roughly 2.5 hours. | 3 | 35 | 45 | Larch | 50 | Dead | Proactive analysis of vegetation on this line is constant along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared ROW.
Q4 2018 | WECC | GO, TO | 230 | No | No | 2018-12-14 | 1453 | During high winds and a heavy wet snow storm, a 120-foot tall healthy Western Hemlock tree located 25 feet outside the Right of Way (ROW) fell into a 230 kV transmission line resulting in a sustained outage. The tree uprooted in the heavy storms and the resulting outage lasted approximately 24 hours. There is some indication at the outage site that Phytophthora Root Rot may have been a contributing factor. | 3 | 25 | 45 | Western Hemlock | 120 | Healthy | Contacted property owner to discuss topping or removal of potentially diseased trees adjacent to lines.
Q4 2018 | WECC | GO, TO | 230 | Yes | No | 2018-12-20 | 3780 | During high winds and heavy wet snow storms over the course of several days, a 60-foot tall healthy Western Hemlock tree located 10 feet outside the Right of Way (ROW) fell into a 230 kV transmission line resulting in a sustained outage. The tree uprooted in the storm resulting in an outage that lasted approximately 63 hours. | 3 | 10 | 30 | Western Hemlock | 60 | Healthy | None
Q4 2018 | WECC | GO, TO | 230 | Yes | No | 2018-12-29 | 2437 | A 120-foot tall healthy Douglas Fir uprooted in saturated soils from snow melt fell into a 230 kV transmission line. The location had been battered by high winds and heavy snow storms in the week preceding the outage. The tree uprooted resulting in a sustained outage that lasted approximately 41 hours. | 3 | 25 | 45 | Douglas Fir | 120 | Healthy | None
Q4 2018 | WECC | GO, TO | 230 | Yes | Yes | 2018-12-18 | 2952 | A 95-foot tall healthy Douglas Fir fell into a 230 kV transmission line while being battered by high winds and heavy wet snow storms. The tree uprooted in the storm resulting in a sustained outage that lasted approximately 49 hours. | 3 | 14.5 | 55 | Douglas Fir | 95 | Healthy | The tree was removed.
Q4 2018 | WECC | TO | 230 | Yes | No | 2018-12-16 | 741 | A 90-foot healthy Western Hemlock tree located 28 feet outside the Right of Way (ROW) fell into a 230 kV transmission line during high winds and heavy snow storms. The resulting outage lasted approximately 12.5 hours. The tree top snapped on impact and fell to the ground. | 3 | 28 | 41 | Western Hemlock | 90 | Healthy | Continue to monitor surrounding property for signs of forest decline.
Q4 2018 | WECC | TO | 230 | Yes | No | 2018-12-20 | 1668 | During high winds and heavy snow storms, two healthy Western Hemlock trees fell into the same 230 kV transmission line. One tree snapped on impact and fell to the ground, the other ended up resting on the lines and required additional line deenergization for safety reasons. The Western Hemlock trees were 95 and 70 feet tall and located roughly 28 feet off the Right of Way. | 3 | 28 | 50 | Western Hemlock | 95 and 70 | Healthy and Good | Continue to monitor surrounding property for signs of forest decline.
Q4 2018 | SERC | TO | 230 | No | No | 2018-10-25 | 1160 | A healthy 65-foot Sweet Gum Tree located 20 feet outside the Right of Way (ROW) fell and made contact with a 230 kV transmission line. The tree appeared to be healthy and it was noted that soil conditions were wet. There was no damage to facilities. During the patrol to assess the situation, it was noted that another tree located roughly 75 feet from the ROW initiated the issue. The second tree fell into another tree located 20 feet off the ROW causing it to fall into the line. This transmission line had been scheduled to come out of service on the day the outage occurred (October 25, 2018). This vegetation incident occurred before the line was switched out of service that day. After the patrol was completed, the line was left out-of-service for its scheduled outage which led to an extended outage of approximately 20 hours. | 3 | 20 | 51 | Sweet Gum | 65 | Healthy | The tree was removed from area and Right of Way was inspected for any other hazards. No other risks were identified in the area.
Q4 2018 | SERC | TO | 230 | No | No | 2018-11-12 | 1112 | A 67-foot tall healthy Sweet Gum tree located 15 feet off a 100-foot Right of Way (ROW) fell causing a sustained outage during a rain and thunderstorm event. The soil had suffered from erosion due to recent hurricanes and flooding which weakened the root system and contributed to the event. | 3 | 15 | 47 | Sweet Gum | 67 | Healthy | The tree fell in the clear. Adjacent spans patrolled and no additional risks identified.
Q4 2018 | SERC | TO | 230 | No | No | 2018-12-15 | 409 | A 67-foot tall healthy Oak tree located three feet off a 100-foot Right of Way (ROW) fell causing a sustained outage during a rain and thunderstorm event. The soil had suffered from erosion due to recent hurricanes and flooding which weakened the root system and contributed to the event. | 3 | 3 | 35 | Oak | 67 | Healthy | The tree fell into the clear and is no longer a threat. The surrounding spans were patrolled and no other issues were identified.
Q4 2018 | NPCC | TO | 115 | Yes | Yes | 2018-12-18 | 411 | During a high wind event of 30 mph (47 mph gusts) in the early morning of December 18, 2018, a 115 kV line locked out. A patrol determined that an 80-foot Eastern White Pine tree fell into the easement from eight feet outside the Right of Way. The tree snapped seven feet up from the base and fell downslope, where it landed on the field phase of the 115 kV transmission line. The top of the tree then snapped under the pressure, falling clear of the conductor. A visual examination of the tree found no externally identifiable defects, but internally both decay and insect activity were present. The poor structured pine along with the sustained winds caused the tree to fall resulting in the outage. | 3 | 8 | 42 | Eastern White Pine | 80 | Internal decay and insect activity | The area was inspected with no findings of additional vegetation issues identified. The tree was cut to ground level and the debris cleared.
Q3 2018 | WECC | TO | 230 | No | No | 2018-09-14 | 1002 | The area has been in a steady decline from a widespread infestation of several beetle populations for the past few years. While clearing large numbers of trees as a result of the infestation, a contact tree crew lost control of a live 135-foot tall Red-Fir tree located two feet off the Right-of-Way and it fell onto a 230 kV transmission line. The tree was alive but within a pocket of dead trees along a transmission ROW. The resulting outage lasted approximately 17 hours. | 3 | 50 | 85 | Red Fir | 135 | Alive | Stood down crews and required contractors to perform follow-up tailboards regarding correct tree falling procedures.
Q3 2018 | SERC | TO | 230 | Yes | Yes | 2018-07-04 | 775 | An off right-of-way healthy 96-foot tall Pine tree broke during a localized overnight thunderstorm. The broke top pinned down the outside phase of a 230 kV line. There were no damages to facilities. The tree was located two feet outside the right-of-way. Similar tree damage was observed approximately 100 ft. away from the Pine that caused the outage which remained off the right-of-way and away from the facilities. Location of this outage is almost six miles away from the outage that occurred on this line during Q2 2018. The two events are unrelated as there is no indication to suggest that the storm which caused the outage in Q2 damaged the tree that caused this outage. Due to the high number of strong storms in this area, the entire line was patrolled to identify and remove any potential storm-related threats. | 3 | 2 | 50 | Pine | 96 | Healthy | The tree was removed and the entire line was patrolled to identify and remove any potential storm-related threats.
Q3 2018 | SERC | TO | 500 | No | No | 2018-07-31 | 210 | During a small pop-up thundershower, an off right-of-way live Pine tree with internal decay, broke at the base and made contact with a 500 kV line. The tree was 94 feet tall and located five feet off the right-of-way. There was no damage to facilities. The tree had signs of internal decay but signs were not externally visible. | 3 | 5 | 69 | Pine | 94 | Live tree with not visible signs of internal decay | The tree was removed from the area and the right-of-way was inspected for any other hazards.
Q3 2018 | SERC | GO, TO | 230 | No | No | 2018-07-22 | 795 | An off right-of-way live Water Oak tree, located 19 feet off the ROW broke at roughly six feet from the base and made contact with a 230kV transmission line (likely due to wind). The tree showed root rot signs and numerous indicators were noted on the trunk. Tree had signs of internal decay and they were externally visible. The soil was noted being wet at the time of the patrol next morning. | 3 | 19 | 51 | Water Oak | 68 | Live tree with visible signs of decay | The tree was removed from the area and the right-of-way was inspected for any other hazards. No hazards were identified in the area.
Q3 2018 | SERC | TO | 230 | Yes | Yes | 2018-07-30 | 1948 | A 90-foot tall healthy Oak tree fell onto a transmission line from 30-feet off the right-of-way during a localized thunderstorm/rain event. The resulting outage lasted approximately 32 hours. | 3 | 30 | 62 | Oak | 90 | Healthy | The tree was removed from the line and span plus adjacent spans were checked for at risk trees.
Q3 2018 | SERC | TO | 230 | Yes | Yes | 2018-09-28 | 488 | A healthy 39-foot tall Yellow Poplar tree broke at the root crown and fell into the line from seven feet outside the right-of-way. The tree was rooted on a bank beside a creek bed, and the creek had undercut the bank. Recent heavy rains from remnants of Hurricane Florence saturated the ground and contributed to the breaking of the trunk. It was raining with some wind at the time of the fault. | 3 | 7 | 39 | Yellow Poplar | 95 | Healthy | The tree was removed and the right-of-way was patrolled for additional hazard trees to be removed.
Q3 2018 | FRCC | GO, TO | 230 | No | No | 2018-07-21 | 129 | On July 21, 2018 during a severe thunderstorm, a dead 58-foot tall Black Gum tree fell from outside the right-of-way causing a C phase to ground fault. The fault tripped a 230 kV transmission line. The tree was located in a swamp. Wind gusts were recorded up to 52 mph and wind speed was recorded up to 41 mph. No damage resulted from the falling tree. No notable impact to the BES occurred. The outage lasted approximately two hours. | 3 | 23 | 36 | Black Gum | 58 | Dead | The tree was removed and continued bi-annual work plan.
Q3 2018 | FRCC | TO | 230 | No | No | 2018-07-21 | 43 | A 99-foot tall green Slash Pine tree located 21 feet off the Right of Way failed at the base due to internal rot and fell over into a phase conductor of a 230kV transmission line. The tree was suffering from internal rot. The resulting outage last 43 minutes. The tree was permanently removed afterword. This outage was not related to weather. | 3 | 21 | 42 | Slash Pine | 99 | Green Tree with internal rot | The tree was permanently removed.
Q2 2018 | MRO | GO, TO | 230 | No | No | 2018-06-06 | 491 | A 73-foot dead Poplar tree located 33-feet outside the Right of Way (ROW) fell into a 230 kV transmission line causing an 8 hour outage. The tree was rotting. The root system had been compromised by flooding during the previous year. The ground stopped supporting the tree and it fell into the line from outside the ROW. | 3 | 33 | 64 | Poplar | 73 | Dead with compromised rotting root system | Tree was safely removed by ground crews.
Q2 2018 | NPCC | TO | 230 | No | No | 2018-05-04 | 1251 | During a thunderstorm and high wind event, a healthy 120 foot tall, 29 inch diameter trunk, multi-stem White Pine tree had trunk failure at approximately 30 feet from the base of the tree. Approximately 90 feet of the tree fell and landed on the conductor. The tree was located approximately 4 feet outside of the ROW, 87 feet from the center-line of the ROW. The tree was located 67 feet to the nearest conductor. | 3 | 4 | 67 | White Pine | 120 | Healthy | The ROW sideline was inspected in the area of the fall-in from outside the ROW. No additional issues were identified.
Q2 2018 | NPCC | TO | <200 | No | Yes | 2018-04-04 | 1279 | During a high wind event, a 24 inch diameter multi-stem White Pine tree, that was 94 feet tall and in healthy condition located 8 feet outside the Right of Way (ROW), broke at the trunk and landed on a conductor. The tree was located 8 feet outside of the ROW. The distance from the base of the tree to the conductor was 52 feet. The distance from the center-line of the ROW to the cleared-edge of the ROW is 75 feet. | 3 | 8 | 52 | White Pine | 94 | Healthy | The ROW sideline was inspected in the area of the fall-in from outside the ROW. No additional issues were identified.
Q2 2018 | RF | TO | 230 | No | No | 2018-05-15 | 3196 | On May 15th a 230kV line tripped to lockout during a period of thunderstorms with heavy wind and rain. The cause of this event was determined to be due to an 89 foot tall White Pine tree uprooting from 40 feet outside of the 50 foot centerline Right Of Way edge. The tree made contact with the tower causing the tower to collapse. There were no indications that the tree made any contact with the conductor. The resulting outage lasted approximately 53 hours. | 3 | 40 | 67.5 | White Pine | 89 | Healthy | The entire right of way corridor including this specific area will be patrolled again for hazardous trees as part of the 2018 herbicide cycle. All White Pines will be inspected and evaluated as part of the patrol. These and any other hazard trees will be identified for removal and completed. Future reliability improvements include a data analytics effort to identify areas where hazard trees are most susceptible to fail and cause an outage such that these areas may be prioritized and addressed in a timely matter.
Q2 2018 | SERC | TO | 230 | No | No | 2018-06-08 | 1221 | An off Right of Way (ROW) live 81-foot tall Chestnut Oak tree located 16 feet outside the ROW broke at its base and made contact with a 230 kV line. The tree hung into outside phase causing the line to lock out. No damage to facilities. The tree had signs of root rot, but signs were not externally visible. A small thundershower went through the area at the time of event. The resulting outage lasted approximately 20 hours. | 3 | 16 | 60 | Chestnut Oak | 81 | Live tree with internal decay that was not externally visible upon inspection. | No action needed to address recurrence due to being live tree with internal decay that was not externally visible upon inspection.
Q1 2018 | WECC | GO, TO | 230 | No | Yes | 2018-02-18 | 2157 | A healthy 35-foot Pine tree located just outside the ROW (one foot) fell into a 230 kV transmission line. The location of the failure was initially identified through a helicopter patrol, though the patrol was delayed due to ongoing snow and wind storm conditions in the area. The location of the contact was a remote mountainous area difficult to access, hampering the restoration efforts. The resulting outage lasted nearly 36 hours. Wider inspections of surrounding vegetation are planned for the spring when the ROW is more easily accessible. | 3 | 1 | 33 | Pine | 35 | Healthy | Annual Aerial Assessment to determine Hot Spotting and Programmed Vegetation Management needs
Q1 2018 | SERC | TO | 230 | No | No | 2018-02-07 | 119 | A 100-foot live green Pine tree uprooted and hit a 230 kV transmission line. The tree struck the bottom conductor. The top of the tree broke from the contact with the conductor and passed through to the ground causing the line to lockout. The tree fell out into the right-of-way at a 20-degree angle during significant weather with wind speeds in excess of 20 MPH reported as a storm front passed through area. Heavy rain also occurred in area throughout the day. | 3 | 22 | 74 | Pine | 100 | Healthy | No other tree removal was necessary. In a conservative and precautionary measure, English Ivy that was around the base of the tree was cleared away from tree trunks on adjacent trees.
Q1 2018 | SERC | TO | 230 | No | No | 2018-03-01 | 147 | A live 79-foot Loblolly Pine tree located 23 feet outside the ROW fell during high winds. The tree broke at 23 feet from the ground and made contact with the outside phase of the transmission line. The line operated and locked out resulting in a nearly three hour outage. | 3 | 23 | 54 | Loblolly Pine | 79 | Alive | The tree was removed and the line restored to service at 7:05 pm. Five dead trees were also cut the following day in the area.
Q1 2018 | NPCC | TO | 345 | No | Yes | 2018-03-02 | 708 | During a Nor'easter storm with heavy snow and severe winds, an 85-foot multi-leader White Pine tree outside the northern maintained edge of the ROW split near its base and made contact with the closest phase of a 345 kV transmission line. The tree was located in a slightly uphill configuration. | 3 | 13 | 63 | White Pine | 85 | Healthy | Remainder of the tree was removed. The surrounding area was inspected and no other critical vegetation issues were found. Routine removals identified for removal.
Q1 2018 | NPCC | TO | <200 | No | Yes | 2018-03-02 | 1290 | A 95-foot tall healthy White Pine tree fell from off the ROW into a transmission line. During Nor'easter snowstorm Riley, a 115 kV transmission line locked out. A patrol determined an Eastern White Pine tree made contact from off easement as a "fall-in" as evidenced by one side of the co-dominant split away and came to rest on the 115 kV H-Frame lines. The extreme winds (over 85 mph) in combination with co-dominant pine resulted in the poor structured pine failing and causing an outage. Working the tree during the storm was difficult due to high winds and snowy wet weather. Tree was accessed from hilly wet area. The pine tree was on a ridge. All tree work was performed with manual climbing tree crews. | 3 | 14 | 49 | White Pine | 95 | Healthy | The remainder of the tree was removed. The area was inspected and no other vegetation issues were identified.
Q1 2018 | NPCC | TO | 345 | No | No | 2018-03-02 | 156 | A healthy 105-foot Eastern White Pine tree fell into a transmission line during a storm. During Nor'easter snowstorm "Riley", a 345 kV line tripped, restored, and reclosed several times. Reclosing turned off due to voltage transients at a nearby Nuclear Power Plant. The transmission line tripped out. A vegetation ground patrol determined that an Eastern White Pine tree made contact from off easement as a "blow-in" as evidenced by carbon "burning" at the top of tree. The tree did not break or "wind throw." The extreme winds (over 85 mph) in combination with the tree in a wetland location appears to have caused enough movement of root cap and swaying of trunk of tree to draw an arc. | 3 | 8 | 23 | Eastern White Pine | 105 | Healthy | The tree was removed to prevent potential future contact. Two additional adjacent trees were also removed, being the same distance and having the same site conditions.
Q1 2018 | FRCC | TO | 230 | No | No | 2018-03-21 | 418 | An 85-foot Slash Pine tree located ten feet outside the Right of Way sustained a complete failure at its base due to fresh gale conditions. | 3 | 10 | 35 | Slash Pine | 85 | Failed at base | The tree that caused the vegetation contact has been removed.
Q4 2017 | SERC | TO | 230 | No | No | 2017-11-18 | 2857 | A live 70-foot Sycamore tree uprooted and fell into a 230 kV transmission line during storms and high winds on November 18. Wind and wet soil caused the tree to uproot. Due to the remote location and the weather, aerial patrols were not dispatched until early the following day. Line and vegetation crews worked together to remove the tree off the downed wires and remove the old structure. A new structure was installed and line was returned to service on November 20. The outage lasted approximately 48 hours. | 3 | 4 | 39 | Sycamore | 70 | Alive with no visual defects | Due to the remote location and weather, aerial patrols were dispatched early the next day. The line and vegetation crews worked together to remove the up-rooted tree off the downed wires and wreck out the old structure. At approximately 15:13 on November 20, the line crews completed installation of a new structure and returned the line back to service. No other tree issues were noted from ground inspections of the area.
Q4 2017 | WECC | TO | 115 | Yes | Yes | 2017-11-23 | 277 | During a snowstorm, a 90-foot tall dead Pine tree located 20 feet outside the right-of-way fell into a transmission line. The resulting outage lasted over four hours. | 3 | 20 | 35 | Pine | 90 | Dead | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared Right of Way.
Q4 2017 | WECC | TO | 230 | No | No | 2017-11-13 | 1555 | An 85-foot Douglas Fir tree located 33 feet outside the right-of-way during high winds. The tree broke center phase and was leaning on the bottom phase. The resulting outage lasted approximately 26 hours. Along with the offending tree, additional trees in the immediate area with similar threat profiles were removed. | 3 | 33 | 56 | Douglas Fir | 85 | Tree Alive | Removed additional trees with similar threat-profiles in the immediate area.
Q4 2017 | FRCC | TO | 230 | Yes | No | 2017-09-10 | 1652 | A 65-foot tall healthy Oak tree located ten feet outside the right-of-way leaned in toward a transmission line in a swampy area due to wind and rain from Hurricane Irma. The tree rested against the “A” and “C” phase conductors causing the line to trip and lock out. The resulting outage lasted approximately 27 hours. The tree has been removed from the line. | 3 | 10 | 40 | Oak | 65 | Healthy | Removed the tree from the line.
Q3 2017 | RF | TO | 230 | No | No | 2017-08-05 | 612 | A 91-foot tall healthy Red Maple tree fell in from outside the Right-of-Way (ROW). An off corridor live Red Maple tree approximately 91’ tall and 17” diameter at breast height (DBH) uprooted due to high winds and subsequently fell into the ROW contacting the conductor (Z Phase). The Red Maple tree was located approximately 8’ from the edge of the maintained ROW. The service area experienced high winds and thunderstorms on August 4, 2017. Wind gusts of 40-50 mph were reported in the weather report for the closest location that day. Wind gusts of 30-40 mph were also reported the following day, the day of the outage. The multiple storms, high winds, and heavy rain caused the tree to slowly uproot and fall into the line causing the outage. The outage lasted approximately six hours. | 3 | 8 | 62 | Red Maple | 91 | Healthy | After the initial assessment, there was a thorough review of the surrounding spans via foot patrol to ensure that there were no other tree conditions that could cause any further reliability concerns. Two additional trees were identified for removal as a precaution, but no other issues were identified.
Q3 2017 | RF | TO | 230 | No | No | 2017-08-06 | 798 | Fall-in from outside the Right-of-Way (ROW). An off corridor healthy Basswood tree approximately 105 foot tall and 25 inch diameter at breast height (DBH) uprooted and fell into a Hickory tree, approximately 111 foot tall and 27 inch DBH, which uprooted and both trees fell into the ROW, contacting the conductor (Y Phase), due to high winds. The Basswood tree was located approximately 72 feet from the edge of the maintained ROW. The Hickory tree was located approximately 55 feet from the edge of the maintained ROW. The service area experienced high winds and thunderstorms on August 4th and August 5th. The high winds likely caused the Basswood to uproot into the Hickory and slowly uprooted the Hickory into the conductor on August 6, 2017. A week prior to the event (July 23-24), there was a major wind event in the area of the outage according to the forest service; a couple hundred trees came down but no outages resulted. On August 3, a scheduled aerial patrol was performed, and wind damage was found in the span from the prior wind event. Follow-up ground patrol was scheduled for the following week to remove trees showing signs of damage from the wind, but no reliability issues were found in the field during the patrol. | 3 | 72 | 100 | Basswood | 105 | Healthy Healthy | After the initial assessment, there was a thorough review of the surrounding spans via foot patrol to ensure that there were no other tree conditions that could cause any further reliability concerns. Six additional trees in the same span were identified for removal as a precaution, but no other issues were identified.
Q3 2017 | SERC | TO | 230 | No | No | 2017-08-23 | 1124 | A 65-foot healthy Poplar tree located eight feet outside the Right of Way fell into a 230 kV transmission line as rain and storms passed through the area. The resulting outage lasted approximately 18 hours. | 3 | 8 | 35 | Poplar | 65 | Alive with no external signs of decay. | The tree was removed and surrounding spans were checked on the line to ensure that no other trees in the area were impacted by the storm activity.
Q3 2017 | SERC | TO | 230 | No | No | 2017-07-08 | 109 | A 78-foot tall healthy green Pine tree fell into a 230 kV transmission line during severe winds and thunderstorm. The resulting outage lasted approximately 23 hours. The following day the entire line was patrolled by air and no other hazardous trees were noted. | 3 | 1 | 41 | Pine | 78 | Alive, green and healthy. No obvious defects. | The entire line was patrolled by air the following day and no other tree problems were noted.
Q2 2017 | RF | TO | 345 | No | No | 2017-04-03 | 1170 | A 105-foot Tulip Poplar tree located approximately 54 feet from the edge of the Right-of-Way (ROW) fell into another tree. The second tree was an approximately 99-foot tall Beech tree, which uprooted as a result of the falling Tulip Poplar tree and fell into the ROW contacting the conductor. The Beech tree was located approximately 24 feet from the edge of the ROW. After inspecting the fallen tree, it was determined that though the tree was alive, it had internal decay and was hollow. The inspection also discovered a noticeable water stain on the remaining stub, which began at the point of failure at 25 feet above the ground. Weather was not a contributing factor. An adjacent 345kV line was also affected during the outage from the off-ROW fall-in. At the time of the line trip, the entity was performing planned breaker maintenance on one of the three 345kV breakers in the ring bus configuration at a substation. When the off-ROW fall-in occurred, the two in-service 345kV breakers at the substation opened as designed; however, this open-ended another 345kV line at the substation because the other 345kV breaker was open for maintenance. | 3 | 24 | 75 | Beech | 99 | Healthy with Internal Decay and Hollow | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions; no other issues were identified.
Q2 2017 | RF | TO | 230 | No | No | 2017-05-01 | 1487 | A healthy 92-foot tall Pine tree located 3 feet off the Right-of-Way (ROW) uprooted due to extremely high winds and subsequently fell into the ROW contacting the conductor (B Phase). The service area experienced a severe storm with high winds, thunderstorms, and tornado warnings. Wind gusts of 60-70 mph were reported in the weather report. | 3 | 3 | 58 | Pine | 92 | Healthy | Upon arrival at the site of the outage, it was identified that there were hundreds of trees uprooted and laying on the ground due to severe storms in the area. After the initial assessment found the pine tree on the conductor, there was a thorough review of the surrounding spans via foot patrol to ensure that there were no other tree conditions that could cause any further reliability concerns. None were identified. Following the outage, Emergency Aerial Patrols were performed on this circuit and additional circuits in the area, due to the severe storm. No additional vegetation reliability concerns were identified as a result of the aerial patrols.
Q2 2017 | SERC | TO | 230 | No | No | 2017-05-29 | 944 | An 80-foot apparently healthy Poplar tree located 18 feet outside the Right-of-Way fell on a transmission line during storm activity with high winds. The falling tree resulted in a sustained outage. The weather at the time of the interruption was 71 degrees with severe thunderstorms capable of producing hail, straight line winds and cloud to ground lightning. The outage lasted approximately 16 hours. Though the tree appeared to be healthy externally, internal decay was discovered after the failure. | 3 | 18 | 50 | Poplar | 79 | Healthy with Internal Decay | The remaining stem of the tree was removed and surrounding spans were checked on the line to ensure that no other trees in the area were impacted by the storm activity.
Q2 2017 | SERC | TO | 230 | No | No | 2017-05-22 | 1246 | A 70-foot tall apparently healthy Poplar tree located 8 feet off the Right-of-Way fell into a 230kV transmission line during a thunderstorm. The tree appeared healthy externally but root decay was detected after the failure. The contact resulted in an outage that lasted approximately 21 hours. | 3 | 8 | 40 | Poplar | 70 | Healthy with Root Decay | The tree cleared itself from the line but surrounding spans were checked on the line to ensure that no other trees in the area were impacted by the recent storm activity.
Q2 2017 | SERC | TO | 500 | No | No | 2017-05-20 | 165 | A 100-foot tall healthy Sweetgum tree located near a drain (and located only two feet off the Right-of-Way) fell into the outside phase of a transmission line causing the line to operate. Shallow roots and erosion played a role in creating the conditions for the fall, the soil was rocky and the root structure was shallow, but isolated thunderstorms were in the area with heavy rains and high winds provided the final catalyst. | 3 | 2 | 56 | Sweet Gum | 100 | Healthy | Tree did not have to be removed from line and no damage to the conductor. A Danger Tree crew cut several large trees nearby because of the root structure of the tree that failed and the rocky soil.
Q1 2017 | WECC | TO | 230 | Yes | No | 2017-01-02 | 1430 | A healthy 60-foot Hemlock tree, located 23 feet outside the Right-of-Way, fell south into a line during localized high wind conditions. The resulting outage lasted approximately 24 hours. | 3 | 23 | 39 | Hemlock | 60 | Healthy | Crews inspected the immediate area. No imminent threats were discovered.
Q1 2017 | WECC | TO | 230 | Yes | No | 2017-02-09 | 1888 | A 90-foot tall healthy Douglas Fir tree, located 21 feet off the Right-of-Way, was uprooted by the snow load and high winds resulting in an outage. The outage lasted approximately 31 hours. | 3 | 21 | 37 | Douglas Fir | 90 | Healthy | Crews inspected the immediate area. No imminent threats were discovered.
Q1 2017 | WECC | TO | 120 | No | No | 2017-01-10 | 645 | An apparently healthy 90-foot tall (approximately) Jeffery Pine tree located approximately 25 feet off the Right-of-Way, fell into power lines in January during a snow storm in the area. Though the tree appeared healthy, tree conditions were difficult to measure, the base was buried in snow and the fallen portion of the tree was buried in more than ten feet of snow. | 3 | 25 | 50 | Jeffrey Pine | 90 | Healthy | A contractor cleared the tree from the lines. The tree was on private property. It was deemed impractical to remove every tree within 50’ of the lines on a proactive basis. The area was under 7-8 feet of snow at the time, making difficult conditions.
Q1 2017 | SERC | TO | 230 | No | No | 2017-01-26 | 248 | During storm activity with high winds, a dual-stem 78-foot tall healthy pine tree fell causing a sustained outage. One stem broke about 12 feet above the ground and fell into transmission and distribution lines that share the ROW. The outages lasted a little over four hours. The tree was located 12 feet outside the ROW. | 3 | 12 | 48 | Pine | 78 | Healthy | The remaining stem of the pine tree was removed, and nearby trees and spans were checked on the line to ensure that no other trees in the area were impacted by the local storm event.
Q1 2017 | SERC | TO | 230 | Yes | No | 2017-03-01 | 267 | During weather conditions where wind gusts of 38 mph were reported, an off right-of-way green, 72-foot tall Sweetgum tree broke two feet up from the ground and made contact with a 230kV line. Line construction is on a single pole with three vertical phases. The tree passed through the top conductor and then hung on the middle and bottom phase locking the line out. The line on this right-of-way is built thirty feet from the western edge of the right of way. The tree measured thirty-one feet from the centerline of the stated line so the tree was one foot off right-of-way. The tree was covered with English ivy all around the base and ivy dominates floor cover in the area. The ivy had grown up the entire height of the tree. Though the tree was alive, it had heart rot/decay in the center of the trunk where the break point was located. | 3 | 1 | 31 | Sweetgum | 72 | Live Tree with Internal Decay | Ivy was cleared away from tree trunks on adjacent trees and crews performed detailed trunk inspections. As a result, additional trees off the right-of way were identified to be cut down.
Q1 2017 | SERC | TO | 230 | No | No | 2017-01-06 | 1139 | An apparently healthy 70-foot Water Oak tree, located 37.5 feet off the right of way (in a private backyard) was uprooted during inclement weather and fell into a line. The outage lasted just under 19 hours. | 3 | 37.5 | 47.5 | Water Oak | 70 | Healthy | Tree was removed and surrounding area inspected for similar potential issues.
Q1 2017 | FRCC | TO | 230 | Yes | No | 2017-02-07 | 2890 | A 105-foot Live Oak tree located on the west side of the ROW that appeared healthy caused an outage. The tree was 34 feet off the right of way. When the tree, fell it damaged the H-Frame structure. During the outage a weather station nearby documented wind gusts at 46 MPH. At the location of the outage, there were 8-10 other large trees that were either broken or uprooted. Several trees were entangled in the parallel distribution line on the easement. The outage lasted approximately 48 hours. | 3 | 34 | 67 | Oak | 105 | Tree appeared healthy "full leaf out" from the 2015 fall aerial inspection and when observed during the 2015 maintenance trimming of the entire line. A post job inspection following the 2015 maintenance trimming did not identify this tree as a hazard tree. Fungus was discovered growing on the west facing side of the tree (away from the cleared right of way) during an inspection of the tree following the outage. The tree showed signs of internal rot which could not be seen from the right of way. This line was also patrolled during the 2016 aerial patrols and no hazard trees were identified in this span. | A crew was called to site to remove the tree from the conductors and line was restored. Contractors performed an assessment to better identify where the outages have occurred. This area will have a thorough hazardous tree inspection performed and hazardous trees identified will be removed.
Q4 2016 | FRCC | GO, TO | 230 | Yes | No | 2016-10-07 | 550 | Due to Hurricane Matthew, powerful storms in the area resulted in gale force winds and a healthy 60-foot Water Oak tree growing just outside of the right-of-way falling into phases “A” & “C” of a 230 KV line. | 3 | 1 | 27.5 | Water Oak | 60 | Healthy | Line was de-energized and the tree was removed from the line(s) and disposed.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-16 | 136 | A live 72-foot Pine tree located 26-feet off the right-of-way broke approximately 10' above ground and fell through the line during high winds from a significant thunderstorm event. The surrounding area was inspected to be sure there were no other vegetation-related issues that could cause reliability threats; no other issues were identified. | 3 | 26 | 65 | Pine | 72 | Healthy | No action needed to address recurrence. This was a weather related event involving a Pine tree, located off right-of-way, caused by high winds due to a significant thunderstorm.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-22 | 483 | A 92-foot Poplar tree located 3-feet off the right-of-way appeared to have been uprooted during an afternoon thunderstorm the day before the event. The tree leaned up against a Pine tree and slowly started bowing out toward line and made contact with top and middle conductors. The tree appeared live but was suffering from internal decay that would not have been visible during inspections. | 3 | 3 | 85 | Poplar | 92 | Live tree with internal decay which would not have been evident during a visual inspection. | The surrounding area was inspected to ensure that there were no other vegetation-related issues that could cause reliability threats; no other issues were identified.
Q3 2016 | SERC | TO | 230 | Yes | No | 2016-07-28 | 413 | During an afternoon thunderstorm, an 87-foot Green Sweetgum tree located 22 feet off the right-of-way, broke eight and one-half (8.5) feet up from the ground and fell across all phases of two lines. The surrounding area was inspected for any other vegetation-related issues that could cause reliability threats; during this inspection two declining hardwoods were identified and were subsequently removed the following week. | 3 | 22 | 72 | Sweetgum | 87 | Live tree with internal decay. | The surrounding area was inspected for any other vegetation-related issues that could cause reliability threats; during this inspection two declining hardwoods were identified and were subsequently removed the following week.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-28 | 403 | During an afternoon thunderstorm, an 87-foot Green Sweetgum tree located 22 feet off the right-of-way, broke eight and one-half (8.5) feet up from the ground and fell across all phases of two lines. | 3 | 22 | 72 | Sweetgum | 87 | Live tree with internal decay. | The surrounding area was inspected for any other vegetation-related issues that could cause reliability threats; during this inspection two declining hardwoods were identified and were subsequently removed the following week.
Q3 2016 | SERC | GO, TO | 230 | No | No | 2016-07-05 | 200 | An 88-foot tall Loblolly Pine tree located 18 feet off the right-of-way was found on a transmission line. The tree was alive with some trunk rot causing it to snap 13 feet above the ground. The tree was removed. | 3 | 18 | 50 | Loblolly Pine | 88 | Tree was alive with some trunk rot, causing trunk to snap 13 feet above ground level. | The tree was removed and no additional issues were observed in the area.
Q3 2016 | SERC | GO, TO | 230 | No | No | 2016-07-08 | 606 | A 65-foot Loblolly Pine tree located 7 feet off the right-of-way fell into a transmission line causing an outage during strong winds. The tree was alive but rotted at the stump center. The tree was removed and no additional issues were observed. | 3 | 7 | 35 | Loblolly Pine | 65 | Tree was alive but was rotted at the stump center. | The tree was cut off of the wire and no additional issues were observed in the area.
Q3 2016 | SERC | GO, TO | 230 | No | No | 2016-07-20 | 386 | A healthy 115-foot tall Loblolly Pine tree located 57 feet off the right-of-way fell into the line causing an outage. The tree fell while there high winds in the area. The tree was removed and no additional issues were observed in the area. | 3 | 57 | 88 | Loblolly Pine | 115 | Healthy | The tree was cut off of the wire and no additional issues were observed in the area.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-03 | 322 | A 65-foot tall healthy Maple tree adjacent to the line and located 8 feet off the right-of-way, uprooted and fell into the line during thunderstorm activity and high winds resulting in a sustained outage. The 14 inch (DBH) tree was healthy but located in a wet area (due to recent rains) and fell onto the line during the local storm event. | 3 | 8 | 40 | Maple | 65 | Healthy | The tree that fell and other nearby trees were removed, and nearby spans were checked on the line to ensure that no other trees in the area were impacted by the local storm event.
Q3 2016 | NPCC | TO | <200 | No | Yes | 2016-07-25 | 608 | During a thunderstorm event, one leader of a twin stemmed Black Locust tree approximately 90 feet tall broke approximately 15 feet above ground and fell into the line contacting two phases. The contact resulted in the line locking out. The tree was removed and the line returned to service after approximately 10 hours (delays in switching at the UI Facilities). Upon further examination of the tree base, it appears there was extensive internal decay that was not visible prior to the tree failure. The tree was 16 feet outside the maintained and easement limit of the right-of-way. | 3 | 16 | 37 | Black Locust | 90 | Extensive internal decay that was not visible prior to the tree failure. | The tree and the tree parts that were the cause of the contact have been removed. The remaining locust leader as well as several other white pines in this location have been permissioned and are scheduled for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-04-02 | 569 | A 98-foot Pine tree located 22 feet outside the ROW fell into the line during a localized thunderstorm. The winds of the storm and the saturated soil may have contributed to the outage. | 3 | 22 | 54 | Pine | 98 | Healthy | Tree was cut to the ground. No other danger trees were identified for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-04-07 | 6 | A 104-foot tall Red Oak tree located 40-feet outside the ROW on a creek bank. The healthy tree was weakened due to the flowing water in the creek and a storm in the area. | 3 | 40 | 72 | Red Oak | 104 | Healthy | Tree was cut to the ground. No other danger trees were identified for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-06-12 | 246 | Storms in the area contributed winds and saturated soil causing a pine tree to fall into the line. The 89-foot Pine tree was located 14-feet outside the ROW. | 3 | 14 | 46 | Pine | 89 | Healthy | Tree was cut to the ground. No other danger trees were identified for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-06-17 | 1186 | Strong storms with high winds and heavy rains caused 88-foot Willow Oak tree located 14-feet outside the ROW to fall into a line. This caused the failure of several x-arms and broke several poles. The tree was alive but had some trunk decay. | 3 | 14 | 45 | Willow Oak | 88 | Healthy with some trunk decay | The transmission crew replaced the poles, corrected the associated damage, and returned the line to service. Back side of tree trunk had decay. The tree was removed along with one additional Oak tree that also had decay on its trunk.
Q2 2016 | SERC | TO | 230 | No | No | 2016-04-11 | 1113 | Weather reported to be in the area at time of outage caused a 90-foot Oak tree and a 110-foot Pine tree to fall into the line at the same span. Both trees appeared to be alive and healthy with no visible defects at the time of the outage restorations. Thunderstorms, winds, and wet ground conditions were all contributors to the tree becoming up-rooted. | 3 | 29 | 64 | Pine and Oak | 90 and 110 | Healthy | Patrolled area of outage with no other work actions required.
Q2 2016 | SERC | TO | 230 | No | No | 2016-06-05 | 956 | A healthy 75-foot tall Poplar located 17-feet outside the ROW fell during a supercell thunderstorm moving through the area, with estimated winds of roughly 55 mph. | 3 | 17 | 47 | Poplar | 75 | Healthy | Span 21-22 and adjacent spans were inspected to determine if any other fall-in risks were present, and none were found.
Q2 2016 | SERC | TO | 230 | No | No | 2016-06-17 | 152 | An outage was caused by high winds, generated from a severe thunderstorm event. The storm caused a healthy Pine tree located 15-feet off the ROW to snap 6 feet above ground level and fall into the line. The tree was approximately 60 feet tall and 16" DBH. | 3 | 15 | 47 | Pine | 60 | Healthy | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q2 2016 | SERC | TO | 230 | No | No | 2016-05-10 | 225 | A healthy 54-foot tall Sweet Gum tree (that was located 49 feet from the centerline on a 90' ROW) fell into a line causing an outage during a localized thunderstorm. The Robinson Plant - Rockingham 230kV line was sectionalized, and load was restored from the Robinson Plant in 66 minutes. | 3 | 4 | 31 | Sweet Gum | 54 | Healthy | Adjacent spans where inspected to determine if any other off-ROW trees presented a similar fall-in risk, and none were found.
Q2 2016 | SERC | TO | 230 | No | No | 2016-04-09 | 362 | Winds gusting to 29 mph caused a 74-foot Red Oak tree located 30 feet off the easement to break 10 feet above ground. The tree fell into a Water Oak tree located 6 feet off the easement knocking it into the outside conductor. The terrain was difficult and damage to the conductor extended the outage duration. The Water Oak tree that struck the line was healthy but the larger Red Oak tree that initiated the fall had a hollow in the trunk. | 3 | 6 | 47 | Water Oak | 74 | Water Oak Healthy and Red Oak had a hollow in the trunk. | Other trees on this hillside were inspected by our contract Danger Tree crew. Several trees in this area were removed.
Q2 2016 | WECC | TO | 115 | Yes | Yes | 2016-06-01 | 87 | A 90-foot dead Pine tree located 50 feet outside the ROW fell into the line. | 3 | 50 | 85 | Pine | 90 | Dead | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared ROW.
Q1 2016 | FRCC | TO | 230 | Yes | No | 2016-02-24 | 416 | At 7:07am a thunderstorm hit the area causing a 75 foot Oak tree to break 12’-15’ from the ground. The Oak tree was 10.5’ off the edge of the easement. The easement is 100’ wide (50’ east and west of the center line). No known service interruptions resulted. The outage ended at 14:03 the same day. | 3 | 10.5 | 33.5 | Oak | 75 | Tree appeared healthy "full leaf out" from the 2015 fall aerial inspection and when observed during the 2015 maintenance trimming of the entire line. A post job inspection following the 2015 maintenance trimming by a arborist did not identify this tree as a hazard tree. Fungus was discovered growing on the west facing side of the tree (away from the cleared right of way) during an inspection of the tree following the outage. The tree showed signs of internal rot which could not be seen from the right of way. | A crew was called to site to remove the tree from the conductors and line was restored. The crew also found 3 additional hazardous trees in the same area and those trees were removed.
Q1 2016 | NPCC | TO | 345 | No | No | 2016-03-01 | 727 | During a high wind event, a healthy single stem, 74-foot tall, 18-inch DBH (diameter at breast height) Eastern Hemlock located 22.5 feet outside the northern maintained edge of the ROW, broke near its base and made contact with the closest phase of the 312 transmission line. The base of the tree was 52 feet from the closest phase and the tree was located on the uphill, north side of the ROW. Hazard tree inspections and removals were completed on this section of the line in 2015. | 3 | 22.5 | 52 | Hemlock | 74 | Healthy | The tree that was the cause of the contact has been removed. Area inspected for other problematic conditions and are either being corrected or scheduled for corrective actions.
Q1 2016 | NPCC | TO | <200 | No | Yes | 2016-03-28 | 1079 | During a high wind event, a healthy, approximately 75-foot tall, 22 inch DBH, Eastern Hemlock tree located 25 feet outside the eastern limit of the easement edge of the ROW, broke about 25 feet above the ground and made contact with the outer phase of the transmission line. The base of the tree was 35 feet from the closest phase of the line and located on the east side of the north to south oriented ROW. There was no evidence of defect or decay. | 3 | 25 | 35 | Hemlock | 75 | Healthy | The tree that was the cause of the contact has been removed. Area inspected for other problematic conditions and are either being corrected or scheduled for corrective actions.
Q1 2016 | SERC | TO | 230 | No | No | 2016-02-24 | 592 | During a weather-related event, an 85-foot healthy Pine tree located three feet outside the ROW fell through several conductors. When the tree fell through the conductors, the circuit protection operated. However, a broken limb from the tree hung on the conductor and contacted the grounded structure resulting in the lockout. After the limb was removed the line was placed back in service. There was no conductor damage. The tree appeared healthy from the outside but was suffering from internal decay that would not be visible during routine inspections. | 3 | 3 | 73 | Pine | 85 | Live tree with internal decay that would not have been visible during routine inspections. | It is standard procedure to check multiple spans on either side of the affected span. The crews surveyed the additional spans at the time of the incident and no other issues were found. No other actions were necessary. This occurred during a weather related event in which high straight line wind gusts occurred throughout the day resulting in a large number of outages statewide.
Q1 2016 | SERC | TO | 230 | No | No | 2016-02-24 | 4 | A 102-foot healthy Loblolly Pine tree located in a private backyard uprooted during high winds. Wind gusts were reported at 43 miles per hour. It fell onto a shed and a 115kV de-energized transmission line that shared the same corridor as another 230 KV line. The tree rested just a few inches from the 230 kV middle phase, but close enough to cause the outage. | 3 | 33.5 | 101 | Pine | 102 | Healthy | It is standard procedure to check multiple spans on either side of the affected span. The crews surveyed the additional spans at the time of the incident and no other issues were found. No other actions were necessary. This occurred during a weather related event in which high straight line wind gusts occurred throughout the day resulting in a large number of outages statewide.
Q1 2016 | SERC | GO, TO | 230 | No | No | 2016-03-29 | 639 | A healthy 110-foot Oak tree located 39 feet outside the ROW fell during high winds. The soil condition was wet and the tree fell and came into contact with a 230 kV transmission line during a storm. A recloser failed to operate resulting in the outage. | 3 | 39 | 71 | Oak | 110 | Healthy | It is standard procedure to check multiple spans on either side of the affected span. The crews surveyed the additional spans at the time of the incident and no other issues were found. No additional actions were necessary.
Q1 2016 | SERC | TO | 230 | Yes | No | 2016-02-24 | 2690 | A 71-foot healthy Pine tree (10in. DBH) located 45 feet outside of a ROW corridor broke at ground level and fell into conductor during high winds. Following the outage, the line was sectionalized. The conductor and the cross-arm were damaged, requiring repairs to line prior to re-energizing. The outage lasted approximately 44 hours. | 3 | 45 | 32 | Pine | 71 | Healthy | The fallen tree and three others adjacent to it in the span were removed. Trees in adjacent spans were reviewed and no additional issues were found.
Q4 2015 | SERC | TO | 230 | No | No | 2015-11-09 | 1694 | A 112-foot healthy green Hickory tree located outside the right-of-way uprooted and fell into the outside conductor. The tree was green with no visible faults. The soil was saturated from recent rains. | 3 | 50 | 82 | Carya | 112 | Healthy | Tree was removed from conductor. The danger tree crew and foresters did a survey of all trees in this wetland. We removed several more trees because of the saturated soils and size of the trees.
Q4 2015 | SERC | TO | 230 | No | No | 2015-10-04 | 216 | Crew found a 70-foot green Loblolly Pine tree with root rot from outside the right-of-way on the line. Probable cause was root rot with wet soil and winds from a local storm. | 3 | 2.5 | 42.5 | Loblolly Pine | 70 | Tree was alive some present "root-rot," in wet soil. | Tree was cut down and removed. Line was placed back into service.
Q4 2015 | SERC | TO | 230 | No | No | 2015-10-04 | 271 | An 82-foot Loblolly Pine tree located 25 feet outside the right-of-way fell due to root rot in wet soil. The fallen tree caused an outage on a 230 kV line. A lineman found the tree in contact with a structure. | 3 | 25 | 45.5 | Loblolly Pine | 82 | Alive; some present "root-rot;" wet soil | Tree fell to ground. The line crew cut it away from the structure. No other remediation was necessary in the area.
Q4 2015 | SERC | TO | 230 | No | No | 2015-10-16 | 231 | A 65 foot tall dead Yellow Poplar tree that was rooted 35 feet from the edge of the right-of-way. The tree broke at its base and hit a conductor. Significant rotting was found at the base of the tree. Strong winds are believed to have pushed the tree over. | 3 | 35 | 50 | Yellow Poplar | 65 | Dead. With rotting around the base of the tree. | Other trees in the area were inspected, and no other vegetation/tree issues were found.
Q4 2015 | SERC | TO | 500 | Yes | No | 2015-12-31 | 734 | The area had experienced prolonged flooding and heavy rains that washed away a creek bank resulting in the uprooting of an 87-foot Oak tree located 35 feet outside the right-of-way. The tree fell into a second smaller hardwood, pushing the second tree to within three feet of conductors. The second tree was energized and tripped the line. | 3 | 35 | 90 | Oak | 87 | Healthy | No action needed to address recurrence. This was a weather related event involving two trees, off the right-of-way, which were impacted due to historical prolonged rainfall and flooding.
Q4 2015 | SPP RE | TO | 345 | No | No | 2015-11-17 | 497 | Heavy rains occurred off and on throughout the day with some severe storms and high winds. At the time of the outage, the closest weather station reported heavy thunderstorm and rain including 24-34 mph winds. The storm led to a 78-foot Loblolly Pine tree that was located 83 feet outside the right-of-way falling and causing an outage on a 345 kV line. | 3 | 83 | 58 | Loblolly Pine | 78 | Green tree with root rot | None
Q4 2015 | WECC | TO | 115 | Yes | Yes | 2015-12-24 | 720 | A healthy 80-foot Douglas Fir tree located 15 feet outside the right-of-way broke above the ground line during a snowstorm. The falling tree caused an outage on a 115 kV transmission line. | 3 | 15 | 50 | Douglas Fir | 80 | Healthy | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared R-O-W.
Q4 2015 | WECC | TO | 230 | No | No | 2015-11-13 | 632 | A healthy 110-foot Douglas Fir tree located 55 feet outside the right-of-way uprooted during localized strong winds and fell east into a transmission line. This outage was weather related but did not occur during a major storm. | 3 | 55 | 67.5 | Douglas Fir | 110 | Healthy | None, tree was healthy, failure was due to high winds
Q3 2015 | FRCC | GO, TO | 230 | No | No | 2015-07-04 | 558 | Due to powerful storms in the area and resulting gale force winds, a healthy 80-foot pine tree, growing outside of the right-of-way fell into both a 115kV line as well as a 230kV line from beyond the right-of-way limits. | 3 | 5 | 45 | Pine | 80 | Healthy | Line was de-energized and the tree was removed from the line(s) and disposed of.
Q3 2015 | NPCC | TO | 345 | No | No | 2015-06-23 | 1188 | A major storm with winds in excess of 70 mph (with confirmed Micro-Bursts and Tornado warnings) caused an outage on a 345 kV line. The strong winds appear to have led to a 92-foot tall healthy hickory tree on the cleared edge outside of the ROW to have blown over and caused the top of the tree to come close enough to the conductor to cause a trip. The line reclosed and then tripped out after which the tree must have become free from the line. The line was patrolled and re-energized following the patrol. It was estimated that the tree bent over almost 90 degrees and covered the distance between the conductor and the tree branch, estimated to be over 50 feet. | 3 | 2 | 32 | Hickory | 92 | Healthy | The tree that was the cause of the contact has been removed. Area inspected for other problematic conditions and are either being corrected or scheduled for corrective actions.
Q3 2015 | SERC | TO | 500 | No | No | 2015-07-02 | 859 | During a thunderstorm, a 105-foot oak live tree with internal decay in the trunk, located 37 feet outside the ROW broke at its base and caused an outage on a 500kv line. The tree was approximately 90 feet from the nearest conductor. | 3 | 37 | 90 | Oak | 105 | It was a live tree that had internal decay in the trunk that would not have been visible during routine inspections. | This was a weather related event involving a single tree, and no other trees were endangering the line at this location. The tree was removed and no other action was needed to remediate the situation.
Q3 2015 | SERC | GO, TO | 230 | No | No | 2015-07-02 | 963 | A 57-foot tall maple tree with a rotten trunk due to an old cambium wound that never sealed fell in to a 230kv line causing an outage that lasted approximately 16 hours. The tree was located 7 feet off the ROW and was 37 feet from the nearest conductor. The stump of the tree was approximately 90% rotten. | 3 | 7 | 37 | Maple | 57 | Trunk rotten due to an old cambium wound that never sealed. Stump was approximately 90 % rotten. | Transmission crew removed the tree and returned the line to service. The area was surveyed and no additional action was necessary.
Q3 2015 | SERC | TO | 500 | No | No | 2015-07-01 | 1093 | During a severe thunderstorm strong winds broke a 107-foot green loblolly pine tree located 16 feet outside the ROW fell into the outside phase causing an outage on a 500kv line. The tree had a defect and the winds broke the tree at this spot. Several downed trees were noticed in the area near this outage. | 3 | 16 | 45 | Loblolly Pine | 107 | Tree was green but had a defect about 12 feet off the ground. The strong winds caused the tree to break at this point. | Contract tree crews were sent to the location and removed any damaged trees from the storm. Crews were also instructed to look for any possible hazardous trees off the easement. Several trees were removed in this area.
Q3 2015 | SERC | TO | 230 | No | No | 2015-08-17 | 1291 | A live 65-foot tall hickory tree located 4.5 feet outside the south side of the ROW fell during bad weather causing a line to trip and an outage that lasted approximately 21 hours. Follow-up ground patrols found a tree on the line between structures. The hickory tree had a growth defect approximately 3-feet above the ground level which caused the tree to fail and break during stormy weather. | 3 | 4.5 | 49 | Hickory | 65 | Healthy tree with a growth defect approximately 3-feet above the ground. | Follow-up ground and aerial inspections were performed and no other hazardous trees were noted.
Q3 2015 | SERC | TO | 230 | No | No | 2015-09-29 | 1357 | An approximately 40-inch diameter dead pine tree approximately 90-feet tall broke and hit a 100-feet tall live oak tree causing it to break approximately 20-feet above the ground level. The healthy oak tree fell into the line causing an outage lasting approximately 22 hours. | 3 | 20 | 60 | Oak | 100 | Healthy tree was struck by a dead tree and fell into the line. | Transmission vegetation personnel patrolled and inspected approximately five spans east and west of this outage location and found no other priority tree issues.
Q3 2015 | WECC | TO | 115 | Yes | Yes | 2015-08-22 | 36407.4 | An 80-foot tall healthy Douglas fir located 15 feet outside the ROW broke and caused a 115kv line to trip causing a sustained outage. | 3 | 15 | 50 | Douglas Fir | 80 | Healthy | Service to remove appropriate trees outside of the cleared ROW.
Q2 2015 | SERC | TO | 230 | No | No | 2015-04-27 | 61 | A dead Oak tree 5 feet off the Right-of-Way along a sloped bank up-rooted and fell through the conductors during a high-wind event. The 85-foot tall and 28-inch diameter dead Oak tree fell through the lines and damaged a lower davit arm. | 3 | 5 | 65 | Oak | 85 | Dead | An aerial line patrol was performed and no additional hazardous trees were identified on the line.
Q2 2015 | RF | TO | 138 | No | Yes | 2015-05-07 | 1438 | An 87-foot Black Cherry tree with internal rot in the lower section fell from outside the Right-of-Way into a 138 kV IROL line during a storm. | 3 | 4.5 | 36.5 | Black Cherry | 87 | Fair. Tree had internal rot that was not apparent from outside. Upon removal, rot was located only in bottom 20%. | The line was patrolled to look for other storm-damaged or hazardous trees likely to fall in. One additional tree was identified and removed.
Q2 2015 | FRCC | TO | 230 | No | No | 2015-05-11 | 460 | At 1800 a thunderstorm caused a 70-foot healthy Oak tree to uproot from 15 feet off the Right-of-Way and land on the west and center conductors of the H-frame 230kV line. The Right-of-Way is 100 feet wide and the base of the tree was 65 feet from the center line. | 3 | 15 | 38 | Oak | 70 | Healthy | A tree crew was called to site to remove the tree from the conductors and line was restored.
Q1 2015 | SERC | TO | 230 | Yes | No | 2015-03-18 | 97 | A dead Red Oak tree fell from outside the right of way and made contact with a conductor. There were strong winds in the area at the time. The conductor burned in two, and both burned ends fell to the ground in a swampy area. | 3 | 13 | 41 | Red Oak | 54 | Dead | Another tree near the fallen tree was found charred. The other tree has been removed. Vines in the fall path of the fallen tree were also removed.