Compliance Questionnaire and

Reliability Standard Audit Worksheet

PRC-001-1 — System Protection Coordination

Registered Entity: (Must be completed by the Compliance Enforcement Authority)

NCR Number: (Must be completed by the Compliance Enforcement Authority)

Applicable Function(s):  BA, TOP, GOP

Auditors:

Disclaimer

NERC developed this Reliability Standard Audit Worksheet (RSAW) language in order to facilitate NERC’s and the Regional Entities’ assessment of a registered entity’s compliance with this Reliability Standard.  The NERC RSAW language is written to specific versions of each NERC Reliability Standard.  Entities using this RSAW should choose the version of the RSAW applicable to the Reliability Standard being assessed.  While the information included in this RSAW provides some of the methodology that NERC has elected to use to assess compliance with the requirements of the Reliability Standard, this document should not be treated as a substitute for the Reliability Standard or viewed as additional Reliability Standard requirements.  In all cases, the Regional Entity should rely on the language contained in the Reliability Standard itself, and not on the language contained in this RSAW, to determine compliance with the Reliability Standard.  NERC’s Reliability Standards can be found on NERC’s website at http://www.nerc.com/page.php?cid=2|20.   Additionally, NERC Reliability Standards are updated frequently, and this RSAW may not necessarily be updated with the same frequency.  Therefore, it is imperative that entities treat this RSAW as a reference document only, and not as a substitute or replacement for the Reliability Standard.  It is the responsibility of the registered entity to verify its compliance with the latest approved version of the Reliability Standards, by the applicable governmental authority, relevant to its registration status.

The NERC RSAW language contained within this document provides a non-exclusive list, for informational purposes only, of examples of the types of evidence a registered entity may produce or may be asked to produce to demonstrate compliance with the Reliability Standard.  A registered entity’s adherence to the examples contained within this RSAW does not necessarily constitute compliance with the applicable Reliability Standard, and NERC and the Regional Entity using this RSAW reserves the right to request additional evidence from the registered entity that is not included in this RSAW.  Additionally, this RSAW includes excerpts from FERC Orders and other regulatory references.  The FERC Order cites are provided for ease of reference only, and this document does not necessarily include all applicable Order provisions.  In the event of a discrepancy between FERC Orders, and the language included in this document, FERC Orders shall prevail.

Subject Matter Experts

Identify your company’s subject matter expert(s) responsible for this Reliability Standard.  Include the person's title, organization and the requirement(s) for which they are responsible. Insert additional lines if necessary.

Response: (Registered Entity Response Required)

| SME Name | Title | Organization | Requirement |
| --- | --- | --- | --- |

# Reliability Standard Language

PRC-001-1 — System Protection Coordination

Purpose:

To ensure system protection is coordinated among operating entities.

Applicability:

- Balancing Authorities

- Transmission Operators

- Generator Operators

NERC BOT Approval Date: 11/1/2006

FERC Approval Date: 3/16/2007

Reliability Standard Enforcement Date in the United States: 6/18/2007

Requirements:

Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of protection system schemes applied in its area.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

# R1 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to PRC-001-1 R1.

___	Verify the operator is familiar with relay protection schemes deployed on its system via one of the following:

___	Operator training records indicating training in basic relaying, including any Special Protection Systems within its system.

___	Interview operator(s) to ensure basic knowledge of relaying, including any Special Protection Systems within its system.

Auditors Detailed notes:

Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows:

  - If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority.  The Generator Operator shall take corrective action as soon as possible.

  - If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities.  The Transmission Operator shall take corrective action as soon as possible.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

Question – Did you have an equipment or relay failure during the audit period which reduced system reliability? If yes, provide evidence you notified the proper entities.

Entity Response: (Registered Entity Response Required)

# R2 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to PRC-001-1 R2.

___	Verify the entity notified reliability entities of relay or equipment failure as follows:

___	Verify that if a protective relay or equipment failure reduces system reliability, the Generator Operator notified its Transmission Operator and Host Balancing Authority.

___	Verify the Generator Operator took corrective action as soon as possible.

___	Verify the Transmission Operator took corrective action as soon as possible.

___	Verify that if a protective relay or equipment failure reduces system reliability, the Transmission Operator notified its Reliability Coordinator and affected Transmission Operators and Balancing Authorities.

Auditors Detailed notes:

A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows.

  - Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority.

  - Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

Question: Have you made changes to new or added new protective systems during the audit period? If yes, provide evidence you coordinated with the appropriate entities.

Entity Response: (Registered Entity Response Required)

# R3 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to PRC-001-1 R3.

___	Verify the entity coordinated new and protective systems and changes to protective systems as follows:

___	Verify each Generator Operator coordinated all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority.

___	Verify each Transmission Operator coordinated all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities.

Auditors Detailed notes:

Each Transmission Operator shall coordinate protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

# R4 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to PRC-001-1 R4.

___	Verify each Transmission Operator coordinated protection systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities.

Auditors Detailed notes:

A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others:

  - Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems.

  - Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

Question: Did you experience changes in operating conditions that could require changes of protection systems of other entities? If yes, provide evidence of coordination.

Entity Response: (Registered Entity Response Required)

# R5 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to PRC-001-1 R5.

___	Verify each Generator Operator or Transmission Operator coordinated changes in generation, transmission, load or operating conditions that could require changes in the protection systems of others.

___	Verify the Generator Operator notified its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems.

___	Verify the Transmission Operator notified neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems.

Auditors Detailed notes:

Each Transmission Operator and Balancing Authority shall monitor the status of each Special Protection System in their area, and shall notify affected Transmission Operators and Balancing Authorities of each change in status.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

# R6 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority

Compliance Assessment Approach Specific to PRC-001-1 R6.

___	Verify the entity monitors the status of each Special Protection System in its area.

___	Verify the entity notified affected Transmission Operators and Balancing Authorities of each change in status.

Auditors Detailed notes:

# Supplemental Information

Other - The list of questions above is not all inclusive of evidence required to show compliance with the Reliability Standard. Provide additional information here, as necessary that demonstrates compliance with this Reliability Standard.

Entity Response: (Registered Entity Response)

# Compliance Findings Summary (to be filled out by auditor)

| Req. | C | PV | OEA | NA | Statement |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |

Excerpts from FERC Orders -- For Reference Purposes Only

Updated Through March 31, 2009

PRC-001-1

Order 693

P 1418.  Protection and Control systems (PRC) on Bulk-Power System elements are an integral part of reliable grid operation. Protection systems are designed to detect and isolate faulty elements on a system, thereby limiting the severity and spread of system disturbances, and preventing possible damage to protected elements. The function, settings and limitations of a protection system are critical in establishing SOLs and IROLs. The PRC Reliability Standards apply to transmission operators, transmission owners, generator operators, generator owners, distribution providers and regional reliability organizations and cover a wide range of topics related to the protection and control of power systems.

P 1419.  PRC-001-1 ensures that protection systems are coordinated among operating entities by requiring transmission and generator operators to notify appropriate entities of relay or equipment failures that could affect system reliability. In addition, transmission and generator operators must coordinate with appropriate entities when new protection systems are installed, or when existing protection systems are modified.

P 1433.  The Commission approves PRC-001-1 as mandatory and enforceable….

P 1435.  Protection systems on Bulk-Power System elements are an integral part of reliable operations. They are designed to detect and isolate faulty elements on a power system, thereby limiting the severity and spread of disturbances and preventing possible damage to protected elements. If a protection system can no longer perform as designed because of a failure of its relays, system reliability is reduced or threatened. In deriving SOLs and IROLs, moreover, the functions, settings, and limitations of protection systems are recognized and integrated. Systems are only reliable when protection systems perform as designed. This is what PRC-001-1 means in linking a reduction in system reliability with a protection relay failure or other equipment failure.

P 1436.  … we note that while the PRC Reliability Standards do not specifically require protection systems consisting of redundant and independent protection groups for each critical element in the Bulk-Power System, such requirements are included as one potential solution in the TPL Reliability Standards.

P 1438.  In the case, … of a system element protected by a single protection System with a failed relay that threatens system reliability, that scenario would require the use of appropriate operating solutions including removing a system element from service. Another possible solution is to operate a system at a lower SOL or IROL that recognizes the degraded protection performance.

P 1439.  Corrective actions taken by transmission operators to return a system to a secure operating state when a protective relay or equipment failure reduces system reliability normally refer to “operator control actions”, consisting of operator actions such as removing the facility without protection from service, generation redispatch, transmission re-configuration, etc. Corrective action must be completed as soon as possible, but no longer than 30 minutes after a notice of protection system failure. Failure to complete corrective action within 30 minutes will be considered a violation of the relevant IROL or TOP Reliability Standards. In contrast, troubleshooting or replacing failed relays or equipment are performed by field maintenance personnel and normally take hours or even days to complete. These actions are not normally considered corrective actions in the context of real-time operation of the Bulk-Power System.

P 1440.  We believe that “[t]he transmission operator shall take corrective action as soon as possible” refers to transmission operators taking operator control actions. It does not refer to troubleshooting, repairing or replacing failed relays or equipment, etc., since these time-consuming corrective actions would prolong the risk of cascading failures to the Bulk-Power System.

P 1442.  We agree … that generator operators do not have the same ability as transmission operators to take corrective control actions on the Bulk-Power System…

P 1443.  As explained above, the requirement for system operators to take corrective control action when protective relay or equipment failure reduces system reliability should be treated the same as the requirement for returning a system to a secure and reliable state after an IROL violation, i.e., as soon as possible, but no longer than 30 minutes after a violation. A longer time limit would place an entity in violation of relevant IROL or TOP Reliability Standards.

P 1448.  … The time allowed for mitigating actual IROL violations is very clear: as soon as possible and within 30 minutes. We clarify that our concern is not about “field protection and control personnel not being alerted about failure of relays and protection systems on critical elements.” Our focus, rather, is that upon detection of failure of relays and protection systems on critical elements, field personnel must report the failures promptly to the transmission operators so that corrective operator control actions can be taken as soon as possible and within 30 minutes… with respect to …[concerns] that our proposed directives would result in local-level personnel undermining or not following the instructions of reliability coordinator personnel at a time when the system is unstable, we do not understand how local level personnel, who have no operating control of a transmission operator’s system or a reliability coordinator’s system could do so.

P 1449.  The Commission approves Reliability Standard PRC-001-1 as mandatory and enforceable. …

June 8, 2007 Order Approving Regional Reliability Standards for the Western Interconnection and Directing Modifications, Docket No. RR07-11-000

- P 87.  We note that upon failure of protective relays, NERC Reliability Standard PRC-001-1 requires transmission operators and generator operators to take corrective actions as soon as possible (within thirty minutes as directed by Order No. 693).  Order No. 693 clarifies that “corrective actions” do not refer to the repair of protective relays, but instead to actions that ensure the reliability of the system, such as lowering IROLs and SOLs.  The proposed regional Reliability Standard does not relieve compliance with this requirement but, rather, adds more stringency by defining a maximum timeframe for removal and repair of protective equipment.

Revision History

| Version | Date | Reviewers | Revision Description |
| --- | --- | --- | --- |
| 1 | October 2009 | RSAW Working Group | New Document. |
| 1 | December 2010 | QRSAW WG | Revised Findings Table, modified Supporting Evidence tables, and added Revision History. |
| 1 | January 2011 | Craig Struck | Reviewed for format consistency and content. |