Reliability Standard Audit Worksheet

PRC-005-1b — Transmission and Generation Protection System Maintenance and Testing

This section must be completed by the Compliance Enforcement Authority.

Registered Entity:

NCR Number:

Compliance Assessment Date:

Compliance Monitoring Method:

Applicable Function(s): DP, GO, TO

Names of Auditors:

# Subject Matter Experts

Identify Subject Matter Expert(s) responsible for this Reliability Standard.  (Insert additional rows if necessary)

Registered Entity Response (Required):

| SME Name | Title | Organization | Requirement(s) |
| --- | --- | --- | --- |

# R1 Supporting Evidence and Documentation

R1.  Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES.  The program shall include:

R1.1. Maintenance and testing intervals and their basis.

R1.2. Summary of maintenance and testing procedures.

Registered Entity Response (Required):

Describe, in narrative form, how you meet compliance with this requirement.

Registered Entity Evidence (Required):

Provide the following for all evidence submitted (Insert additional rows if necessary): File Name, File Extension, Document Title, Revision, Date, Page(s), Section(s), Section Title(s), Description

Compliance Assessment Approach Specific to PRC-005-1b R1

This section must be completed by the Compliance Enforcement Authority

Review the evidence to verify the Registered Entity has:

| (R1) Review the evidence provided by the entity to determine if the entity has a transmission Protection System and/or a generation Protection System (see Requirement 2). If yes: |  |
| --- | --- |
|  | Review the evidence provided by the entity to verify the entity has a maintenance and testing program for the Protection System. The maintenance and testing program should include: |
|  | Protective relays which respond to electrical quantities |
|  | Communication systems necessary for correct operation of protective functions |
|  | Voltage and current sensing devices providing inputs to protective relays |
|  | Station DC supply associated with protective functions (including Station batteries, battery chargers, and non battery based DC supply) |
|  | DC control circuitry associated with protective functions through the trip coil(s) of the circuit breakers or other interrupting devices. |
| Review the program and determine if it has the following for each protective system device: |  |
|  | (R1.1) Maintenance and testing intervals |
|  | (R1.1) Basis for those intervals |
|  | (R1.2) Summary of Maintenance and Testing procedures |

Note to Auditor:

All equipment specified by the new definition that was not covered by the old definition must be included in the maintenance and testing program (i.e., a periodicity, basis, and testing/maintenance procedure) by April 1, 2013. The actual test should be completed by the end of the first specified testing cycle. (For example, if quarterly and annual battery charger tests are added, all quarterly battery charger tests should be complete by July 1, 2013 and annual tests by April 1, 2014.)

Auditor  Notes:

# R2 Supporting Evidence and Documentation

R2.   Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days).  The documentation of the program implementation shall include:

R2.1. Evidence Protection System devices were maintained and tested within the defined intervals.

R2.2. Date each Protection System device was last tested/maintained.

Registered Entity Response (Required):

Describe, in narrative form, how you meet compliance with this requirement.

Data Request: Provide a list of all substations 100kV and above and generating stations connected to the BES for use in NERC Sampling Methodology.

TEST RECORDS NOTE: If test records are provided as evidence of compliance with R2 please provide an annotated sample test record for each type of test record provided. The sample test record(s) should include descriptive annotations for each relevant section, heading, cell, etc. The annotations should include an explanation of what each relevant section/heading/cell is and what the test results are indicating. The annotations should be written from the perspective that the person reviewing the test record is unfamiliar with your test record format. Examples of annotations could include cell comments in MS Excel spreadsheets, review comments in MS Word documents, and Sticky Note comments in PDF formatted documents, to name a few.

Registered Entity Evidence (Required):

Provide the following for all evidence submitted (Insert additional rows if necessary): File Name, File Extension, Document Title, Revision, Date, Page(s), Section(s), Section Title(s), Description

Compliance Assessment Approach Specific to PRC-005-1b R2

This section must be completed by the Compliance Enforcement Authority

Review the evidence to verify the Registered Entity has:

| (R2) Review the evidence provided by the entity to determine if the entity is required to have a Protection System maintenance and testing program. If yes: |  |
| --- | --- |
| Review the evidence provided by the entity to determine if the entity provided the above information to its Regional Reliability Organization/Regional Entity within 30 calendar days of the request (Prior to compliance assessment, determine if a 30 day data request was made (the audit notice constitutes a 30 day request)) and that the documentation included: |  |
|  | (R2.1) Evidence Protection System devices were maintained and tested within the defined intervals. |
|  | (R2.2) Date when each Protection System device was last tested/maintained. |

Auditor  Notes:

Supplemental Information

Question: How does your company document and confirm that program implementation is 	on schedule?  Include a discussion of defined maintenance and testing intervals, and your 	process for tracking the dates each protective device was last tested/maintained.

Question: Describe your maintenance program to periodically test protection systems in 	order to ensure proper performance.  Include in your description how your company’s 	program identifies the equipment specified in the NERC Glossary definition of Protection 	Systems (e.g. Protective relays, associated communication systems, voltage and current sensing devices, station batteries/chargers and DC control circuitry).

Other : The list of questions above is not all inclusive of evidence required to show compliance with the Reliability Standard. Provide additional information here, as necessary that demonstrates compliance with this Reliability Standard.

# Compliance Finding Summary  [Author to update table based on number of Requirements in the standard]

This section must be completed by the Compliance Enforcement Authority

| Req. | NF | PV | OEA | NA | Statement |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |

# Additional Information:

Reliability Standard

Introduction

Title:	Transmission  and Generation Protection System Maintenance and Testing

Number:	PRC-005-1b

Purpose:	To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested.

Applicability

  - Transmission Owner.

  - Generator Owner.

  - Distribution Provider that owns a transmission Protection System.

Effective Date:	To be determined

Requirements

R1. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include:

R1.1.  	Maintenance and testing intervals and their basis.

R1.2.  	Summary of maintenance and testing procedures.

R2. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days).  The documentation of the program implementation shall include:

R2.1. 	Evidence Protection System devices were maintained and tested within the defined intervals.

R2.2. 	Date each Protection System device was last tested/maintained.

Measures

Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System that affects the reliability of the BES, shall have an associated Protection System maintenance and testing program as defined in Requirement 1.

Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System that affects the reliability of the BES, shall have evidence it provided documentation of its associated Protection System maintenance and testing program and the implementation of its program as defined in Requirement 2. Compliance

- Compliance Monitoring Process

  - Compliance Monitoring Responsibility

- Regional Reliability Organization.

  - Compliance Monitoring Period and Reset Time Frame

One calendar year.

  - Data Retention

The Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System, shall retain evidence of the implementation of its Protection System maintenance and testing program for three years.

The Compliance Monitor shall retain any audit data for three years.

  - Additional Compliance Information

- The Transmission Owner and any Distribution Provider that owns a transmission Protection System and the Generator Owner that owns a generation Protection System, shall each demonstrate compliance through self-certification or audit (periodic, as part of targeted monitoring or initiated by complaint or event), as determined by the Compliance Monitor.

- Levels of Non-Compliance

  - Level 1:  Documentation of the maintenance and testing program provided was incomplete as required in R1, but records indicate maintenance and testing did occur within the identified intervals for the portions of the program that were documented.

  - Level 2:  Documentation of the maintenance and testing program provided was complete as required in R1, but records indicate that maintenance and testing did not occur within the defined intervals.

  - Level 3:  Documentation of the maintenance and testing program provided was incomplete, and records indicate implementation of the documented portions of the maintenance and testing program did not occur within the identified intervals.

  - Level 4:  Documentation of the maintenance and testing program, or its implementation, was not provided.

Regional Differences

- None identified.

Appendix 1 of PRC-005-1b

Requirement Number and Text of Requirement

R1. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: R1.1. Maintenance and testing intervals and their basis. R1.2. Summary of maintenance and testing procedures. R2. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days). The documentation of the program implementation shall include: R2.1 Evidence Protection System devices were maintained and tested within the defined intervals. R2.2 Date each Protection System device was last tested/maintained.

Question:

Is protection for a radially-connected transformer protection system energized from the BES considered a transmission Protection System subject to this standard?

Response:

The request for interpretation of PRC-005-1 Requirements R1 and R2 focuses on the applicability of the term “transmission Protection System.” The NERC Glossary of Terms Used in Reliability Standards contains a definition of “Protection System” but does not contain a definition of transmission Protection System. In these two standards, use of the phrase transmission Protection System indicates that the requirements using this phrase are applicable to any Protection System that is installed for the purpose of detecting faults on transmission elements (lines, buses, transformers, etc.) identified as being included in the Bulk Electric System (BES) and trips an interrupting device that interrupts current supplied directly from the BES. A Protection System for a radially connected transformer energized from the BES would be considered a transmission Protection System and subject to these standards only if the protection trips an interrupting device that interrupts current supplied directly from the BES and the transformer is a BES element.

Appendix 2 of PRC-005-1b

Requirement Number and Text of Requirement

R1. Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: R1.1. Maintenance and testing intervals and their basis. R1.2. Summary of maintenance and testing procedures.

Question #2

Does R1 require a maintenance and testing program for auxiliary relays and sensing devices? If so, what types of auxiliary relays and sensing devices? (i.e. transformer sudden pressure relays)

Response to Question #2

The existing definition of “Protection System” does not include auxiliary relays; therefore, maintenance and testing of such devices is not explicitly required. Maintenance and testing of such devices is addressed to the degree that an entity’s maintenance and testing program for DC control circuits involves maintenance and testing of imbedded auxiliary relays. Maintenance and testing of devices that respond to quantities other than electrical quantities (for example, sudden pressure relays) are not included within Requirement R1.

Question #3

Does R1 require maintenance and testing of transmission line re-closing relays?

Response to Question #3

No. “Protective Relays” refer to devices that detect and take action for abnormal conditions. Automatic restoration of transmission lines is not a “protective” function.

Question #4

Does R1 require a maintenance and testing program for the DC circuitry that is just the circuitry with relays and devices that control actions on breakers, etc., or does R1 require a program for the entire circuit from the battery charger to the relays to circuit breakers and all associated wiring?

Response to Question #4

PRC-005-1 requires that entities 1) address DC control circuitry within their program, 2) have a basis for the way they address this item, and 3) execute the program. PRC-005-1 does not establish specific additional requirements relative to the scope and/or methods included within the program.

Question #5

For R1, what are examples of "associated communications systems" that are part of “Protection Systems” that require a maintenance and testing program?

Response to Question #5

“Associated communication systems” refer to communication systems used to convey essential Protection System tripping logic, sometimes referred to as pilot relaying or teleprotection. Examples include the following: - communications equipment involved in power-line-carrier relaying - communications equipment involved in various types of permissive protection system applications - direct transfer-trip systems - digital communication systems (which would include the protection system communications - functions of standard IEC 618501 as well as various proprietary systems)

Sampling Methodology

Sampling is essential for auditing compliance with NERC Reliability Standards since it is not always possible

or practical to test 100% of either the equipment, documentation, or both, associated with the full suite of enforceable standards. The Sampling Methodology Guidelines and Criteria, or sample guidelines, provided by the Electric Reliability Organization help to establish a minimum sample set for monitoring and enforcement uses in audits of NERC Reliability Standards.

There are two approaches to sampling: statistical and non-statistical, and choosing which to use depends on the objectives for sampling. (When the population sample to be reviewed is documentation, a statistical approach using RAT‐STATS is expected.) Both are represented in the sample guideline in line with standard practices for their use. The Audit Team Lead may determine if the scope of the audit samples should be reduced to levels below those established in the sample guideline. In doing so, the audit team will document the rationale for reducing the scope of the of sample population in the RSAW or audit report.

Additionally, separate from the audit, the registered entity may use this methodology to determine the sample population to test in order to provide themselves reasonable assurance that management’s expectations are being met by the organization.

Regulatory Language for Reference Purposes Only (through April 1, 2013)

Order No. 693

P 1418.  Protection and Control systems (PRC) on Bulk-Power System elements are an integral part of reliable grid operation. Protection systems are designed to detect and isolate faulty elements on a system, thereby limiting the severity and spread of system disturbances, and preventing possible damage to protected elements. The function, settings and limitations of a protection system are critical in establishing SOLs and IROLs. The PRC Reliability Standards apply to transmission operators, transmission owners, generator operators, generator owners, distribution providers and regional reliability organizations and cover a wide range of topics related to the protection and control of power systems.

P 1470.  PRC-005-1 ensures that all transmission and generation protection systems affecting the reliability of the Bulk-Power System are maintained and tested by requiring the transmission owners, distribution providers, and generator owners to develop, document, and implement a protection system maintenance program that may be reviewed by the regional reliability organization.

P 1474.  For the reasons stated in the NOPR, the Commission approves Reliability Standard PRC-005-1 as mandatory and enforceable.

NOPR on the Interpretation of Protection System Reliability Standard (December 16, 2010)

P 10. The Commission proposes to accept NERC’s proposed interpretation of Reliability Standard PRC-005-1 Requirement R1. As discussed above, NERC’s Glossary defines “Protection System” as: “Protective relays, associated communication systems, voltage and current sensing devices, station batteries and DC control circuitry.” NERC’s proposed interpretation essentially identifies what equipment is considered to be a “protective relay,” “associated communication system,” “sensing device,” or “station battery.” None of these terms or phrases within the NERC definition of “Protection System” are further defined anywhere else. NERC’s interpretation provides further meaning to these phrases, is not inconsistent with the language of the Reliability Standard and, therefore, appears reasonable. Further, the interpretation should assist in providing a consistent understanding of what constitutes a “Protection System” for those entities that must comply with Reliability Standard PRC-005-1. Accordingly, we proposed to approve NERC’s interpretation.

P 11. …[P]ursuant to section 215 (d)(5) of the FPA, we propose to direct NERC to develop a modification to the Reliability Standard to include any component or device that is designed to detect defective lines or apparatuses or other power system conditions of an abnormal or dangerous nature and to initiate appropriate control circuit actions.

P 14. …Specifically, we propose to direct NERC to include any device, including auxiliary and backup protection devices, that is designed to sense or take action against any abnormal system condition that will affect reliable operation.

P 15. …Accordingly, pursuant to section 215 (d)(5) of the FPA, we propose that NERC propose a modification to the Reliability Standard to include the maintenance and testing of reclosing relays affecting the reliability of the Bulk-Power System.

P 16. …Specifically, we propose to direct NERC to develop a modification to the Reliability Standard that explicitly includes maintenance and testing of all DC control circuitry that is necessary to ensure proper operation of the Protection System, including voltage and continuity.

P 17. …To address our concerns, the Commission proposes to direct NERC to develop modifications to the PRC-005-1 Reliability Standards through its Reliability Standards development process.

P 19. As stated above, the Commission previously approved, in Order No. 693, the Reliability Standard that is the subject of the current Notice of Proposed Rulemaking (NOPR). This NOPR accepts an interpretation of the currently approved Reliability Standard and does not change this standard. The interpretation of the current Reliability Standard at issue in this rulemaking is not expected to change the reporting burden nor impose any additional information collection requirements.

Order Approving Interpretation (September 26, 2011)

P 7. NERC interprets “transmission Protection System,” as it appears in Requirements R1 and R3 of PRC-004-1 and Requirements R1 and R2 of PRC-005-1, to mean “any Protection System that is installed for the purpose of detecting faults on transmission elements (lines, buses, transformers, etc.) identified as being included in the Bulk Electric System (BES) and trips an interrupting device that interrupts current supplied directly from the BES.”[Footnote omitted.] In addition, NERC’s proposed interpretation states that “[a] Protection System for a radially connected transformer energized from the BES would be considered a transmission Protection System and subject to these standards only if the protection trips an interrupting device that interrupts current supplied directly from the BES and the transformer is a BES element.”[Footnote omitted.]

P 11. The Commission approves NERC’s interpretation as it is consistent with the intent of Requirements R1 and R3 of PRC-004-1 and Requirements R1 and R2 of PRC-005-1. The interpretation clarifies that the Requirements are “applicable to any Protection System that is installed for the purpose of detecting faults on transmission elements (lines, buses, transformers, etc.) identified as being included in the [BES] and trips an interrupting device that interrupts current supplied directly from the BES.”[Footnote omitted.] This interpretation is consistent with the Commission’s understanding that a “transmission Protection System” is installed for the purpose of detecting and isolating faults affecting the reliability of the bulk electric system through the use of current interrupting devices. The Commission further understands that the “interrupting device” referred to in the interpretation is a device that has the performance capability to interrupt full fault current associated with the protected bulk electric system facilities.

Order Approving Modification of Definition for Protection System (February 3, 2012)

P5. The current definition of Protection System includes protective relays, associated communication systems, voltage and current sensing devices, station batteries and DC control circuitry. The revised definition with the proposed modification states:

“The modified definition approved herein shall supersede the interpretation of Requirement R1 of Reliability Standard PRC-005-1 approved concurrently with this order in Docket No. RM10-5-000 on the effective date of the modified definition (the first day of the first calendar quarter twelve months from approval, i.e., April 1, 2013).

“Protection System –

- Protective relays which respond to electrical quantities,

- Communications systems necessary for correct operation of protective functions,

- Voltage and current sensing devices providing inputs to protective relays,

- Station dc supply associated with protective functions (including station batteries, battery chargers, and non-battery-based dc supply), and

- Control circuitry associated with protective functions through the trip coil(s) of the circuit breaker or other interrupting devices.”

P6. In the Petition, NERC explains that the modification will improve the definition by clearly identifying the essential elements that constitute a Protection System. NERC states that battery chargers are an essential piece of the bulk power system that should be included in the definition since battery chargers function to assure that batteries associated with protection systems are in a continuous state of readiness.

Revision History

| Version | Date | Reviewers | Revision Description |
| --- | --- | --- | --- |
| 1 | December 2009 | RSAW Working Group | New Document |
| 1 | December 2010 | QRSAW WG | Revised Findings Table, modified Supporting Evidence tables, and added Revision History |
| 1 | January 2011 | Craig Struck | Reviewed for format consistency and content. Added test record annotation remarks for R2 evidence. |
| 1.1 | September 2011 | Craig Struck | Format update for 2012. |
| 1.1 | October 2011 | NERC Legal | Updated Excerpts from FERC Orders from March 31, 2009 through and including October 19, 2011. |
| 2 | March 2013 | RSAW WG | Updated template, added interpretation, revised for new definition of protection system, and updated title. |

NERC developed this Reliability Standard Audit Worksheet (RSAW) language in order to facilitate NERC’s and the Regional Entities’ assessment of a registered entity’s compliance with this Reliability Standard.  The NERC RSAW language is written to specific versions of each NERC Reliability Standard.  Entities using this RSAW should choose the version of the RSAW applicable to the Reliability Standard being assessed.  While the information included in this RSAW provides some of the methodology that NERC has elected to use to assess compliance with the requirements of the Reliability Standard, this document should not be treated as a substitute for the Reliability Standard or viewed as additional Reliability Standard requirements.  In all cases, the Regional Entity should rely on the language contained in the Reliability Standard itself, and not on the language contained in this RSAW, to determine compliance with the Reliability Standard.  NERC’s Reliability Standards can be found on NERC’s website at http://www.nerc.com/page.php?cid=2|20.   Additionally, NERC Reliability Standards are updated frequently, and this RSAW may not necessarily be updated with the same frequency.  Therefore, it is imperative that entities treat this RSAW as a reference document only, and not as a substitute or replacement for the Reliability Standard.  It is the responsibility of the registered entity to verify its compliance with the latest approved version of the Reliability Standards, by the applicable governmental authority, relevant to its registration status.

The NERC RSAW language contained within this document provides a non-exclusive list, for informational purposes only, of examples of the types of evidence a registered entity may produce or may be asked to produce to demonstrate compliance with the Reliability Standard.  A registered entity’s adherence to the examples contained within this RSAW does not necessarily constitute compliance with the applicable Reliability Standard, and NERC and the Regional Entity using this RSAW reserves the right to request additional evidence from the registered entity that is not included in this RSAW.  Additionally, this RSAW includes excerpts from FERC Orders and other regulatory references.  The FERC Order cites are provided for ease of reference only, and this document does not necessarily include all applicable Order provisions.  In the event of a discrepancy between FERC Orders, and the language included in this document, FERC Orders shall prevail.

According to the FERC Order issued approving a modified definition of Protection System (RD11-13-000), this interpretation will be superseded by the modified definition of Protection System when the modified definition becomes effective.  The modified definition of Protection System becomes effective on April 1, 2013.