Compliance Questionnaire and

Reliability Standard Audit Worksheet

PRC-005-1 — Transmission and Generation Protection System Maintenance and Testing

Registered Entity: (Must be completed by the Compliance Enforcement Authority)

NCR Number: (Must be completed by the Compliance Enforcement Authority)

Applicable Function(s): TO, GO, DP

Auditors:

Disclaimer

NERC developed this Reliability Standard Audit Worksheet (RSAW) language in order to facilitate NERC’s and the Regional Entities’ assessment of a registered entity’s compliance with this Reliability Standard.  The NERC RSAW language is written to specific versions of each NERC Reliability Standard.  Entities using this RSAW should choose the version of the RSAW applicable to the Reliability Standard being assessed.  While the information included in this RSAW provides some of the methodology that NERC has elected to use to assess compliance with the requirements of the Reliability Standard, this document should not be treated as a substitute for the Reliability Standard or viewed as additional Reliability Standard requirements.  In all cases, the Regional Entity should rely on the language contained in the Reliability Standard itself, and not on the language contained in this RSAW, to determine compliance with the Reliability Standard.  NERC’s Reliability Standards can be found on NERC’s website at http://www.nerc.com/page.php?cid=2|20.   Additionally, NERC Reliability Standards are updated frequently, and this RSAW may not necessarily be updated with the same frequency.  Therefore, it is imperative that entities treat this RSAW as a reference document only, and not as a substitute or replacement for the Reliability Standard.  It is the responsibility of the registered entity to verify its compliance with the latest approved version of the Reliability Standards, by the applicable governmental authority, relevant to its registration status.

The NERC RSAW language contained within this document provides a non-exclusive list, for informational purposes only, of examples of the types of evidence a registered entity may produce or may be asked to produce to demonstrate compliance with the Reliability Standard.  A registered entity’s adherence to the examples contained within this RSAW does not necessarily constitute compliance with the applicable Reliability Standard, and NERC and the Regional Entity using this RSAW reserves the right to request additional evidence from the registered entity that is not included in this RSAW.  Additionally, this RSAW includes excerpts from FERC Orders and other regulatory references.  The FERC Order cites are provided for ease of reference only, and this document does not necessarily include all applicable Order provisions.  In the event of a discrepancy between FERC Orders, and the language included in this document, FERC Orders shall prevail.

# Subject Matter Experts

Identify your company’s subject matter expert(s) responsible for this Reliability Standard.  Include the person's title, organization and the requirement(s) for which they are responsible. Insert additional lines if necessary.

Response: (Registered Entity Response Required)

| SME Name | Title | Organization | Requirement |
| --- | --- | --- | --- |

# Reliability Standard Language

PRC-005-1 — Transmission and Generation Protection System Maintenance and Testing

NOTE: The following is the definition of “protection system” as defined in the NERC Glossary of Terms Used in Reliability Standards:	 “Protective relays, associated communication systems, voltage and current sensing devices, station batteries and DC control circuitry.”

Purpose:

To ensure all transmission and generation Protection Systems affecting the reliability of the Bulk Electric System (BES) are maintained and tested.

Applicability:

Transmission Owner

Generator Owner

Distribution Provider that owns a transmission Protection System

NERC BOT Approval Date: 2/7/2006

FERC Approval Date:  3/16/2007

Reliability Standard Enforcement Date in the United States: 6/18/2007

Requirements:

R1.	Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES.  The program shall include:

R1.1. Maintenance and testing intervals and their basis.

R1.2. Summary of maintenance and testing procedures.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

# R1 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority

Compliance Assessment Approach Specific to PRC-005-1 R1.

___	Review the evidence provided by the entity to determine if the entity has a transmission

Protection System and/or a generation Protection System (see Requirement 2).  If yes:

___ Review the evidence provided by the entity to verify the entity has a maintenance and testing program for the Protection System. The maintenance and testing program should include (see note on page 2):

Protective relays

___	  Associated communication systems

___	Voltage and current sensing devices

___	Station batteries

___	DC control circuitry

___Review the program and determine if it has the following:

___	 Maintenance and testing intervals

___	 Basis for those intervals

___	 Summary of Maintenance and Testing procedures

Detailed notes:

Auditors Detailed notes:

R2. 	Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Reliability Organization on request (within 30 calendar days).  The documentation of the program implementation shall include:

R2.1. Evidence Protection System devices were maintained and tested within the defined intervals.

R2.2. Date each Protection System device was last tested/maintained.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity

Response Required)

Data Request: Provide a list of all substations 100kV and above and generating stations connected to the BES.

Entity Response: (Registered Entity Response Required)

# R2 Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version TEST RECORDS NOTE: If test records are provided as evidence of compliance with R2 please provide an annotated sample test record for each type of test record provided. The sample test record(s) should include descriptive annotations for each relevant section, heading, cell, etc. The annotations should include an explanation of what each relevant section/heading/cell is and what the test results are indicating. The annotations should be written from the perspective that the person reviewing the test record is unfamiliar with your test record format. Examples of annotations could include cell comments in MS Excel spreadsheets, review comments in MS Word documents, and Sticky Note comments in PDF formatted documents, to name a few. |  |  |
| --- | --- | --- | --- |
| Title |  | Date | Version |  |
| Audit Team: Additional Evidence Reviewed: |  |  |  |  |

This section must be completed by the Compliance Enforcement Authority

Compliance Assessment Approach Specific to PRC-005-1 R2.

Review the evidence provided by the entity to determine if the entity is required to have a

Protection System maintenance and testing program.  If yes:

___   Review the evidence provided by the entity to determine if the entity provided the above information to its Regional Reliability Organization/Regional Entity within 30 calendar days of the request (Prior to compliance assessment, determine if a 30 day data request was made (the audit notice constitutes a 30 day request)) and that the documentation included:

___	Evidence Protection System devices were maintained and tested within the defined intervals.

___Date when each Protection System device was last tested/maintained.

Auditors Detailed notes:

# Supplemental Information

PRC-005-1 — Questions

Question: How does your company document and confirm that program implementation is 	on schedule?  Include a discussion of defined maintenance and testing intervals, and your 	process for tracking the dates each protective device was last tested/maintained.

Entity Response: (Registered Entity Response Required)

Question: Describe your maintenance program to periodically test protection systems in 	order to ensure proper performance.  Include in your description how your company’s 	program identifies the equipment specified in the NERC Glossary definition of Protection 	Systems (Protective relays, associated communication systems, voltage and current sensing devices, station batteries and DC control circuitry).

Entity Response: (Registered Entity Response Required)

Other - The list of questions above is not all inclusive of evidence required to show compliance with the Reliability Standard. Provide additional information here, as necessary that demonstrates compliance with this Reliability Standard.

Entity Response: (Registered Entity Response)

# Compliance Findings Summary (to be filled out by auditor)

| Req. | C | PV | OEA | NA | Statement |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |

Excerpts from FERC Orders -- For Reference Purposes Only

Updated Through October 19, 2011

PRC-005-1

Order 693

P 1418.  Protection and Control systems (PRC) on Bulk-Power System elements are an integral part of reliable grid operation. Protection systems are designed to detect and isolate faulty elements on a system, thereby limiting the severity and spread of system disturbances, and preventing possible damage to protected elements. The function, settings and limitations of a protection system are critical in establishing SOLs and IROLs. The PRC Reliability Standards apply to transmission operators, transmission owners, generator operators, generator owners, distribution providers and regional reliability organizations and cover a wide range of topics related to the protection and control of power systems.

P 1470.  PRC-005-1 ensures that all transmission and generation protection systems affecting the reliability of the Bulk-Power System are maintained and tested by requiring the transmission owners, distribution providers, and generator owners to develop, document, and implement a protection system maintenance program that may be reviewed by the regional reliability organization.

P 1474.  For the reasons stated in the NOPR, the Commission approves Reliability Standard PRC-005-1 as mandatory and enforceable.

NOPR on the Interpretation of Protection System Reliability Standard (December 16, 2010)

P 10. The Commission proposes to accept NERC’s proposed interpretation of Reliability Standard PRC-005-1 Requirement R1. As discussed above, NERC’s Glossary defines “Protection System” as: “Protective relays, associated communication systems, voltage and current sensing devices, station batteries and DC control circuitry.” NERC’s proposed interpretation essentially identifies what equipment is considered to be a “protective relay,” “associated communication system,” “sensing device,” or “station battery.” None of these terms or phrases within the NERC definition of “Protection System” are further defined any where else. NERC’s interpretation provides further meaning to these phrases, is not inconsistent with the language of the Reliability Standard and, therefore, appears reasonable. Further, the interpretation should assist in providing a consistent understanding of what constitutes a “Protection System” for those entities that must comply with Reliability Standard PRC-005-1. Accordingly, we proposed to approve NERC’s interpretation.

P 11. …[P]ursuant to section 215 (d)(5) of the FPA, we propose to direct NERC to develop a modification to the Reliability Standard to include any component or device that is designed to detect defective lines or apparatuses or other power system conditions of an abnormal or dangerous nature and to initiate appropriate control circuit actions.

P 14. …Specifically, we propose to direct NERC to include any device, including auxiliary and backup protection devices, that is designed to sense or take action against any abnormal system condition that will affect reliable operation.

P 15. …Accordingly, pursuant to section 215 (d)(5) of the FPA, we propose that NERC propose a modification to the Reliability Standard to include the maintenance and testing of reclosing relays affecting the reliability of the Bulk-Power System.

P 16. …Specifically, we propose to direct NERC to develop a modification to the Reliability Standard that explicitly includes maintenance and testing of all DC control circuitry that is necessary to ensure proper operation of the Protection System, including voltage and continuity.

P 17. …To address our concerns, the Commission proposes to direct NERC to develop modifications to the PRC-005-1 Reliability Standards through its Reliability Standards development process.

P 19. As stated above, the Commission previously approved, in Order No. 693, the Reliability Standard that is the subject of the current Notice of Proposed Rulemaking (NOPR). This NOPR accepts an interpretation of the currently approved Reliability Standard and does not change this standard. The interpretation of the current Reliability Standard at issue in this rulemaking is not expected to change the reporting burden nor impose any additional information collection requirements.

Order Approving Interpretation (September 26, 2011)

P 7. NERC interprets “transmission Protection System,” as it appears in Requirements R1 and R3 of PRC-004-1 and Requirements R1 and R2 of PRC-005-1, to mean “any Protection System that is installed for the purpose of detecting faults on transmission elements (lines, buses, transformers, etc.) identified as being included in the Bulk Electric System (BES) and trips an interrupting device that interrupts current supplied directly from the BES.”[Footnote omitted.] In addition, NERC’s proposed interpretation states that “[a] ProtectionSystem for a radially connected transformer energized from the BES would be considered a transmission Protection System and subject to these standards only if the protection trips an interrupting device that interrupts current supplied directly from the BES and the transformer is a BES element.”[Footnote omitted.]

P 11. The Commission approves NERC’s interpretation as it is consistent with the intent of Requirements R1 and R3 of PRC-004-1 and Requirements R1 and R2 of PRC-005-1. The interpretation clarifies that the Requirements are “applicable to any Protection System that is installed for the purpose of detecting faults on transmission elements (lines, buses, transformers, etc.) identified as being included in the [BES] and trips an interrupting device that interrupts current supplied directly from the BES.”[Footnote omitted.] This interpretation is consistent with the Commission’s understanding that a “transmission Protection System” is installed for the purpose of detecting and isolating faults affecting the reliability of the bulk electric system through the use of current interrupting devices. The Commission further understands that the “interrupting device” referred to in the interpretation is a device that has the performance capability to interrupt full fault current associated with the protected bulk electric system facilities.

Revision History

| Version | Date | Reviewers | Revision Description |
| --- | --- | --- | --- |
| 1 | December 2009 | RSAW Working Group | New Document |
| 1 | December 2010 | QRSAW WG | Revised Findings Table, modified Supporting Evidence tables, and added Revision History |
| 1 | January 2011 | Craig Struck | Reviewed for format consistency and content. Added test record annotation remarks for R2 evidence. |
| 1.1 | September 2011 | Craig Struck | Format update for 2012. |
|  | October 2011 | NERC Legal | Updated Excerpts from FERC Orders from March 31, 2009 through and including October 19, 2011. |