Compliance Questionnaire and

Reliability Standard Audit Worksheet

TPL-003-0a — System Performance Following 
Loss of Two or More Bulk Electric System Elements (Category C)

Registered Entity: (Must be completed by the Compliance Enforcement Authority)

NCR Number: (Must be completed by the Compliance Enforcement Authority)

Applicable Function(s):   PA, TP

Auditors:

Disclaimer

NERC developed this Reliability Standard Audit Worksheet (RSAW) language in order to facilitate NERC’s and the Regional Entities’ assessment of a registered entity’s compliance with this Reliability Standard.  The NERC RSAW language is written to specific versions of each NERC Reliability Standard.  Entities using this RSAW should choose the version of the RSAW applicable to the Reliability Standard being assessed.  While the information included in this RSAW provides some of the methodology that NERC has elected to use to assess compliance with the requirements of the Reliability Standard, this document should not be treated as a substitute for the Reliability Standard or viewed as additional Reliability Standard requirements.  In all cases, the Regional Entity should rely on the language contained in the Reliability Standard itself, and not on the language contained in this RSAW, to determine compliance with the Reliability Standard.  NERC’s Reliability Standards can be found on NERC’s website at http://www.nerc.com/page.php?cid=2|20.   Additionally, NERC Reliability Standards are updated frequently, and this RSAW may not necessarily be updated with the same frequency.  Therefore, it is imperative that entities treat this RSAW as a reference document only, and not as a substitute or replacement for the Reliability Standard.  It is the responsibility of the registered entity to verify its compliance with the latest approved version of the Reliability Standards, by the applicable governmental authority, relevant to its registration status.

The NERC RSAW language contained within this document provides a non-exclusive list, for informational purposes only, of examples of the types of evidence a registered entity may produce or may be asked to produce to demonstrate compliance with the Reliability Standard.  A registered entity’s adherence to the examples contained within this RSAW does not necessarily constitute compliance with the applicable Reliability Standard, and NERC and the Regional Entity using this RSAW reserves the right to request additional evidence from the registered entity that is not included in this RSAW.  Additionally, this RSAW includes excerpts from FERC Orders and other regulatory references.  The FERC Order cites are provided for ease of reference only, and this document does not necessarily include all applicable Order provisions.  In the event of a discrepancy between FERC Orders, and the language included in this document, FERC Orders shall prevail.

# Subject Matter Experts

Identify your company’s subject matter expert(s) responsible for this Reliability Standard.  Include the person's title, organization and the requirement(s) for which they are responsible. Insert additional lines if necessary.

Response: (Registered Entity Response Required)

| SME Name | Title | Organization | Requirement |
| --- | --- | --- | --- |

# Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |
| --- | --- |
| R1 |  |
| R2 |  |
| R3 |  |

# Reliability Standard Language

TPL-003-0a — System Performance Following Loss of Two or More Bulk Electric System Elements (Category C)

Purpose:

System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet present and future System needs.

Applicability:

Planning Authority

Transmission Planner

NERC BOT Approval Date: 2/8/2005

FERC Approval Date: 3/16/2007

Reliability Standard Enforcement Date in the United States: 6/18/2007

Requirements:

R1. 		The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is planned such that the network can be operated to supply projected customer demands and projected Firm (non-recallable reserved) Transmission Services, at all demand levels over the range of forecast system demands, under the contingency conditions as defined in Category C of Table I (attached).  The controlled interruption of customer Demand, the planned removal of generators, or the Curtailment of firm (non-recallable reserved) power transfers may be necessary to meet this standard.  To be valid, the Planning Authority and Transmission Planner assessments shall:

R1.1. Be made annually.

R1.2. 	Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons.

R1.3. 	Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies).  The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s).

R1.3.1. Be performed and evaluated only for those Category C contingencies that would produce the more severe System results or impacts.  The rationale for the contingencies selected for evaluation shall be available as supporting information.  An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information.

R1.3.2. Cover critical system conditions and study years as deemed appropriate by the responsible entity.

R1.3.3. Be conducted annually unless changes to system conditions do not warrant such analyses.

R1.3.4. Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions.

R1.3.5. Have all projected firm transfers modeled.

R1.3.6. Be performed and evaluated for selected demand levels over the range of forecast system demands.

R1.3.7. Demonstrate that System performance meets Table 1 for Category C contingencies.

R1.3.8. Include existing and planned facilities.

R1.3.9. Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance.

R1.3.10. Include the effects of existing and planned protection systems, including any backup or redundant systems.

R1.3.11. Include the effects of existing and planned control devices.

R1.3.12. Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed.

R1.4. Address any planned upgrades needed to meet the performance requirements of Category C.R1.5. Consider all contingencies applicable to Category C.

- Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity Response Required)

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to TPL-003-0 R1.

_____ Determine if entity has completed an Assessment that studies if its portion of the interconnected transmission system is planned to meet the requirements of R1.

______ Confirm that the above Assessment is conducted annually.

______ Confirm that the Assessment is both for the:

______ 1-5 year planning horizon range.

______ 6-10 year planning horizon range.

______ Confirm that the Assessment is supported by one or more current Study(ies) or past Studies and/or system simulations testing that address(es) the following categories showing system performance following Category C of Table I (multiple contingencies)

______ Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information.

______ Cover critical system conditions and study years as deemed appropriate by the responsible entity.

______ Be conducted annually unless changes to system conditions do not warrant such analyses.

______ Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions.

______ Have all projected firm transfers modeled.

______ Be performed and evaluated for selected demand levels over the range of forecast system Demands.

______ Demonstrate that system performance meets Category C of Table I contingencies.

______ Include existing and planned facilities.

______ Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance.

______ Include the effects of existing and planned protection systems, including any backup or redundant systems.

______ Include the effects of existing and planned control devices.

______ Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed.

______ Confirm that the Assessment addressed planned upgrades needed to meet the performance requirements of Category C of Table I.

______ Confirm that the Assessment considers all contingencies applicable to Category C of Table I.

Detailed notes:

Additional Evidence Reviewed:

| Title | Date | Version |
| --- | --- | --- |

R2.						When System simulations indicate an inability of the systems to respond as prescribed in Reliability Standard TPL-003-0_R1, the Planning Authority and Transmission Planner shall each:

R2.1. Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon:

R2.1.1. Including a schedule for implementation.

R2.1.2. Including a discussion of expected required in-service dates of facilities.

R2.1.3. Consider lead times necessary to implement plans.

R2.2. Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities.  Detailed implementation plans are not needed.

- Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity Response Required)

Question: Have your planning assessments ever indicated an inability of the systems to respond as prescribed in Requirement 1 of this standard?  If yes, please describe the actions taken.

Entity Response: (Registered Entity Response Required)

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to TPL-003-0 R2.

______ Determine if system simulations indicate an inability of the system to respond as prescribed in Reliability Standard TPL-003-0_R1.

______ Determine if a written summary of plans to achieve the required system performance has been provided.

______  Determine if the above summary includes:

______ A schedule for implementation.

______ A discussion of expected required in-service dates of facilities.

______ Consideration of the lead times necessary to implement the plans.

______ Determine if the current assessment has reviewed the continuing need for previously identified system facilities.

Detailed notes:

Additional Evidence Reviewed:

| Title | Date | Version |
| --- | --- | --- |

R3. 	The Planning Authority and Transmission Planner shall each document the results of these Reliability Assessments and corrective plans and shall annually provide these results to its respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization.

- Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity Response Required)

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to TPL-003-0 R3.

___   Determine if entity has documented the results of its Reliability Assessments and Corrective Plans per TPL-003-0 Requirement 3.

___   Determine if documentation has been submitted to the entity’s Regional Reliability Organization/Regional Entity per the Regional Reliability Organization’s/Regional Entity’s submission requirements.

Detailed notes:

Additional Evidence Reviewed:

| Title | Date | Version |
| --- | --- | --- |

# Supplemental Information

Other - The list of questions above is not all inclusive of evidence required to show compliance with the Reliability Standard. Provide additional information here, as necessary that demonstrates compliance with this Reliability Standard.

Entity Response: (Registered Entity Response)

# Compliance Findings Summary (to be filled out by auditor)

| Req. | C | PV | NA | Statement |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |

Excerpts from FERC Orders -- For Reference Purposes Only

Updated Through March 31, 2009

TPL-003-0

Order 693

P 1683.  The Transmission Planning (TPL) group of Reliability Standards consists of six Reliability Standards that are applicable to transmission planners, planning authorities and regional reliability organizations. These Reliability Standards are intended to ensure that the transmission system is planned and designed to meet an appropriate and specific set of reliability criteria. Transmission planning is a process that involves a number of stages including developing a model of the Bulk-Power System, using this model to assess the performance of the system for a range of operating conditions and contingencies, determining those operating conditions and contingencies that have an undesirable reliability impact, identifying the nature of potential options, and the need to develop and evaluate a range of solutions and selecting the preferred solution, taking into account the time needed to place the solution in service. The proposed TPL Reliability Standards address: (1) the types of simulations and assessments that must be performed to ensure that reliable systems are developed to meet present and future system needs and (2) the information required to assess regional compliance with planning criteria and for self-assessment of regional reliability.

P 1684.  The TPL group of Reliability Standards contains a table designated “Table 1” (Transmission System Standards – Normal and Emergency Conditions), which is a key part of this group of Reliability Standards. It lays out the system performance requirements for a range of contingencies grouped according to the number of elements forced out of service as a result of the contingency. For example: Category A applies to the normal system with no contingencies; Category B applies to contingencies resulting in the loss of a single element, defined as a generator, transmission circuit, transformer, single DC pole with or without a fault; Category C applies to a contingency resulting in loss of two or more elements, such as any two circuits on a multiple circuit tower line or both poles of a bi-polar DC line; while Category D applies to extreme contingencies resulting in loss of multiple elements, such as a substation or all lines on a right-of-way. The system performance expectations for Category C contingencies are lower than those for Category B contingencies, in that they allow unspecified amounts of planned or controlled loss of load.

P 1798. Reliability Standard TPL-003-0 seeks to ensure that the future Bulk-Power System is planned to meet the system performance requirements of a system with the loss of multiple elements. It does this by requiring that the transmission planner and the planning authority annually evaluate and document the ability of its transmission system to meet the performance requirements of Category C contingencies specified in Table 1 (i.e., events resulting in the loss of two or more elements) for both the near-term and the longer-term planning horizons. TPL-003-0 requires the preparation of a documented plan to achieve the necessary performance requirements if the system is unable to meet the Category C performance criteria.

P 1799.  TPL-003-0 applies to each planning authority and transmission planner. They must demonstrate annually through valid assessments that their portion of the interconnected transmission system is planned to meet the performance requirements of Category C with all transmission facilities in service over a planning horizon that takes into account lead times for corrective plans. The Reliability Standard also requires the applicable entities to consider planned outages of transmission equipment for those demand levels for which they perform such outages. The Reliability Standard defines various categories of conditions to be simulated. The specific study elements selected from each of the categories for assessments, including the subset of Category C contingencies to be evaluated, require approval by the associated regional reliability organization.

P 1816. The Commission approves proposed Reliability Standard TPL-003-0 as a mandatory and enforceable Reliability Standard…

P 1817.  The Commission notes that, like Requirement R1.3.1 of TPL-001-0, Requirement R1.3.2 of TPL-003-0 requires an entity assessing system performance to cover “critical system conditions and study years” as deemed appropriate by the entity performing the study.

P 1825.  Accordingly, the Commission approves Reliability Standard TPL-003-0 as mandatory and enforceable...

Revision History

| Version | Date | Reviewers | Revision Description |
| --- | --- | --- | --- |
| 1 | 5/5/10 | Craig Struck | Added Revision History. Minor editorial changes to reflect Version 0a. Modified compliance assessment approach for R1 & R3. |