Compliance Questionnaire and

Reliability Standard Audit Worksheet

TPL-004-0 — System Performance Following Extreme Events Resulting in

the Loss of Two or More Bulk Electric System Elements (Category D)

Registered Entity:  (Must be completed by the Compliance Enforcement Authority)

NCR Number:  (Must be completed by the Compliance Enforcement Authority)

Applicable Function(s):  PA, TP

Auditors:

Disclaimer

NERC developed this Reliability Standard Audit Worksheet (RSAW) language in order to facilitate NERC’s and the Regional Entities’ assessment of a registered entity’s compliance with this Reliability Standard.  The NERC RSAW language is written to specific versions of each NERC Reliability Standard.  Entities using this RSAW should choose the version of the RSAW applicable to the Reliability Standard being assessed.  While the information included in this RSAW provides some of the methodology that NERC has elected to use to assess compliance with the requirements of the Reliability Standard, this document should not be treated as a substitute for the Reliability Standard or viewed as additional Reliability Standard requirements.  In all cases, the Regional Entity should rely on the language contained in the Reliability Standard itself, and not on the language contained in this RSAW, to determine compliance with the Reliability Standard.  NERC’s Reliability Standards can be found on NERC’s website at http://www.nerc.com/page.php?cid=2|20.   Additionally, NERC Reliability Standards are updated frequently, and this RSAW may not necessarily be updated with the same frequency.  Therefore, it is imperative that entities treat this RSAW as a reference document only, and not as a substitute or replacement for the Reliability Standard.  It is the responsibility of the registered entity to verify its compliance with the latest approved version of the Reliability Standards, by the applicable governmental authority, relevant to its registration status.

The NERC RSAW language contained within this document provides a non-exclusive list, for informational purposes only, of examples of the types of evidence a registered entity may produce or may be asked to produce to demonstrate compliance with the Reliability Standard.  A registered entity’s adherence to the examples contained within this RSAW does not necessarily constitute compliance with the applicable Reliability Standard, and NERC and the Regional Entity using this RSAW reserves the right to request additional evidence from the registered entity that is not included in this RSAW.  Additionally, this RSAW includes excerpts from FERC Orders and other regulatory references.  The FERC Order cites are provided for ease of reference only, and this document does not necessarily include all applicable Order provisions.  In the event of a discrepancy between FERC Orders, and the language included in this document, FERC Orders shall prevail.

# Subject Matter Experts

Identify your company’s subject matter expert(s) responsible for this Reliability Standard.  Include the person's title, organization and the requirement(s) for which they are responsible. Insert additional lines if necessary.

Response: (Registered Entity Response Required)

| SME Name | Title | Organization | Requirement |
| --- | --- | --- | --- |

# Supporting Evidence and Documentation

Response: (Registered Entity Response Required)

|  | Provide the following: Document Title and/or File Name, Page & Section, Date & Version |
| --- | --- |
| R1 |  |
| R2 |  |

# Reliability Standard Language

TPL-004-0 — System Performance Following Extreme Events Resulting in the Loss of Two or More Bulk Electric System Events (Category D)

Purpose:

System simulations and associated assessments are needed periodically to ensure that reliable systems are developed that meet specified performance requirements, with sufficient lead time and continue to be modified or upgraded as necessary to meet present and future System needs.

Applicability:

Planning Authority

Transmission Planner

NERC BOT Approval Date: 2/8/2005

FERC Approval Date: 3/16/2007

Reliability Standard Enforcement Date in the United States: 6/18/2007

Requirements:

R1. 	The Planning Authority and Transmission Planner shall each demonstrate through a valid assessment that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies that are listed under Category D of Table I.  To be valid, the Planning Authority’s and Transmission Planner’s assessment shall:

R1.1. Be made annually.

R1.2. Be conducted for near-term (years one through five).

R1.3. Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I.  The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s).

R1.3.1. Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts.  The rationale for the contingencies selected for evaluation shall be available as supporting information.  An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information.

R1.3.2. Cover critical system conditions and study years as deemed appropriate by the responsible entity.

R1.3.3. Be conducted annually unless changes to system conditions do not warrant such analyses.

R1.3.4. Have all projected firm transfers modeled.

R1.3.5. Include existing and planned facilities.

R1.3.6. Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance.

R1.3.7. Include the effects of existing and planned protection systems, including any backup or redundant systems.

R1.3.8. Include the effects of existing and planned control devices.

R1.3.9. Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed.

R1.4. Consider all contingencies applicable to Category D.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity Response Required)

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to TPL-004-0 R1.

NOTE:  Table D states that the number of extreme contingencies that are judged to be critical by the transmission planning entities will be selected for evaluation.  It is not expected that all possible facility outages under each listed contingency of Category D of Table I will be evaluated.

______ Determine if entity has completed an Assessment that studies if its portion of the interconnected transmission system is evaluated to meet Requirement 1.

______ Confirm that the above Assessment is conducted annually.

______  Confirm that the Assessment looks at the:

______1-5 year planning horizon range.

6-10 year planning horizon range.

______ Confirm that the Assessment is supported by one or more current Study(ies) or past Studies and/or system simulations testing that address(es) the following categories showing system performance following Category D of Table 1:

______  Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information.  An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information.

______  Cover critical system conditions and study years as deemed appropriate by the responsible entity.

______  Be conducted annually unless changes to system conditions do not warrant such analyses.

______  Have all projected firm transfers modeled.

______ Include existing and planned facilities.

______ Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance.

______ Include the effects of existing and planned protection systems, including any backup or redundant systems.

______ Include the effects of existing and planned control devices.

______ Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed.

______ Confirm that the Assessment considers all contingencies applicable to Category D of Table I.

Detailed notes:

Additional Evidence Reviewed:

| Title | Date | Version |
| --- | --- | --- |

R2.	The Planning Authority and Transmission Planner shall each document the results of its reliability assessments and shall annually provide the results to its entities’ respective NERC Regional Reliability Organization(s), as required by the Regional Reliability Organization.

Describe, in narrative form, how you meet compliance with this requirement: (Registered Entity Response Required)

This section must be completed by the Compliance Enforcement Authority.

Compliance Assessment Approach Specific to TPL-004-0 R2.

Determine if entity has documented the results of its reliability Assessments per TPL-004-0 Requirement 2.

______Review the evidence provided to determine if documentation has been submitted to the entity’s Regional Reliability Organization/Regional Entity per the Regional Reliability Organization’s/Regional Entity’s submission requirements.

Detailed notes:

Additional Evidence Reviewed:

| Title | Date | Version |
| --- | --- | --- |

# Supplemental Information

Other - The list of questions above is not all inclusive of evidence required to show compliance with the Reliability Standard. Provide additional information here, as necessary that demonstrates compliance with this Reliability Standard.

Entity Response: (Registered Entity Response)

# Compliance Findings Summary (to be filled out by auditor)

| Req. | C | PV | NA | Statement |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |

Excerpts From FERC Orders—For Reference Purposes Only

Updated as of March 31, 2009

TPL- 004-0

Order 693

- P 1826.  The goal of Reliability Standard TPL-004-0 is to ensure that the future Bulk-Power System is evaluated to assess the risks and consequences of an extreme event involving the loss of multiple elements.  It seeks to do this by requiring the transmission planner and the planning authority to evaluate and document annually the risks and consequences of Category D contingencies (i.e., extreme events resulting in loss of two or more elements or cascading) for the near-term (five-year) planning horizon.

- P 1827.  TPL-004-0 applies to each planning authority and transmission planner.  Each must demonstrate annually through valid assessments that its portion of the interconnected transmission system is evaluated for the risks and consequences of a number of each of the extreme contingencies of Category D with all transmission facilities in service over a planning horizon that takes into account lead times for corrective plans.  TPL-004-0 also requires that planned outages of transmission equipment be considered for those demand levels for which planned outages are performed.  It defines various categories of conditions to be simulated.  The associated regional reliability organization must approve the specific study elements selected from each of the categories for assessment, including the subset of Category D contingencies to be evaluated.

- P 1831.  The Commission approves proposed Reliability Standard TPL-004-0 as mandatory and enforceable.…

- P 1832.  The Commission notes that, like Requirement R1.3.1 of TPL-001-0, Requirement R1.3.2 of TPL-004-0 requires an entity assessing system performance to cover “critical system conditions and study years” as deemed appropriate by the entity performing the study.…

- P 1834.  All commenters that responded on the issue opposed the Commission’s proposal to modify TPL-004-0 to require that, in determining the range of the extreme events to be assessed, the contingency list of Category D be expanded to include recent events such as hurricanes and ice storms.  The Commission is not persuaded by the commenters’ contention that expansion of the extreme events list will lead to an endless list of possibilities.  The two that the Commission used are examples from the general news media.  While the NOPR referred to two recent events, other examples include:  (1) loss of a large gas pipeline into a region or multiple regions that have significant gas-fired generation; (2) a successful cyber attack; (3) regulation that restricts or eliminates the use of a river or lake or other body of water as the cooling source for generation; (4) shutdown of a nuclear power plant and other facilities a day or more prior to a hurricane, tornado or wildfire, or other event and (5) the loss of older transmission lines, which may not be constructed to meet an entity’s present radial ice loading requirements, while the newer or stronger transmission lines remain in service.  The above examples are not an exhaustive list, however, the Commission would not expect the range of scenarios to be much more extensive than this, either….

- P 1836.  Accordingly, the Commission approves Reliability Standard TPL-004-0 as mandatory and enforceable….

Revision History

| Version | Date | Reviewers | Revision Description |
| --- | --- | --- | --- |
| 1 | 5/5/10 | Craig Struck | Added Revision History. Modified compliance assessment approach for R1 & R2. |