## Sheet1
2014-2018 Generating Unit Statistical Brochure -- Units Reporting Events
NOTE: This brochure contains data on units reporting events only. For a review of statistics containing all units that reported , see the brochure "2014-2018 Generating Unit Statistical Brochure -- All Units Reporting".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL All Fuel Types | All Sizes | 1347 | 5734.5 | 168.83 | 98.69 | 44.39 | 72.78 | 53.26 | 82.87 | 80.23 | 8.58 | 11.36 | 8.89 | 12.13 | 5 | 8.42 | 10.32 | 16.62 | 8.7 | 3.42 | 60.99 | 81.86 | 79.25 | 7.7 | 10.31 | 13.05 | 5.09
| FOSSIL All Fuel Types | 001-099 | 326 | 1273 | 123.69 | 99.2 | 29.42 | 64.99 | 42.7 | 85.17 | 82.55 | 10.66 | 13.53 | 9.25 | 9.73 | 5.09 | 8.29 | 9.96 | 19.37 | 6.54 | 3.2 | 45.27 | 85.09 | 82.53 | 9.73 | 12.57 | 10.03 | 4.88
| FOSSIL All Fuel Types | 100-199 | 320 | 1320.75 | 73.39 | 99.34 | 28.29 | 62.56 | 43.6 | 84.14 | 81.35 | 8.55 | 11.54 | 7.62 | 11.78 | 4.08 | 7.34 | 8.99 | 17.45 | 8.52 | 3.26 | 45.22 | 83.87 | 80.98 | 8.21 | 11.22 | 12.09 | 4.04
| FOSSIL All Fuel Types | 200-299 | 157 | 651 | 241.1 | 97.87 | 37.36 | 67.72 | 55.09 | 80.86 | 78.28 | 9.93 | 12.69 | 10.41 | 13.07 | 6.07 | 10.11 | 12.06 | 18.37 | 9.03 | 4.04 | 55.17 | 81.23 | 78.68 | 9.57 | 12.3 | 12.93 | 5.84
| FOSSIL All Fuel Types | 300-399 | 112 | 522.25 | 210.38 | 98.01 | 33.89 | 65.89 | 52.16 | 81.83 | 79.51 | 8.06 | 10.89 | 8.73 | 13.6 | 4.57 | 7.88 | 9.71 | 16.07 | 10.29 | 3.3 | 51.44 | 81.81 | 79.54 | 8.11 | 10.92 | 13.65 | 4.54
| FOSSIL All Fuel Types | 400-599 | 213 | 951 | 326.56 | 97.54 | 45.49 | 72.34 | 62.62 | 81.37 | 78.46 | 8.44 | 11.47 | 10 | 12.86 | 5.77 | 9.21 | 11.53 | 16 | 9.43 | 3.44 | 62.88 | 81.37 | 78.46 | 8.48 | 11.5 | 12.81 | 5.82
| FOSSIL All Fuel Types | 600-799 | 143 | 660.5 | 526.9 | 96.75 | 53.03 | 77.47 | 68.39 | 82.32 | 79.73 | 6.64 | 9.03 | 8.22 | 12.82 | 4.86 | 8.31 | 10.39 | 13.51 | 9.38 | 3.44 | 68.45 | 82.22 | 79.65 | 6.67 | 9.05 | 12.88 | 4.89
| FOSSIL All Fuel Types | 800-999 | 60 | 291 | 271.43 | 97.96 | 49.77 | 75.24 | 65.72 | 82.28 | 80.21 | 6.17 | 8.36 | 7.33 | 13.4 | 4.32 | 7.72 | 9.64 | 13.09 | 10 | 3.4 | 66.14 | 82.39 | 80.33 | 6.1 | 8.26 | 13.31 | 4.3
| FOSSIL All Fuel Types | 1000 Plus | 16 | 60 | 694.46 | 95.43 | 55.32 | 78.58 | 69.56 | 75.2 | 71.99 | 8.98 | 10.71 | 10.2 | 17.94 | 6.87 | 12.38 | 14.2 | 17.3 | 12.42 | 5.51 | 70.4 | 75.45 | 72.38 | 8.7 | 10.39 | 17.84 | 6.71
| FOSSIL Coal Primary | All Sizes | 858 | 3483.5 | 355.19 | 97.83 | 54.69 | 76.07 | 65.47 | 83 | 80.2 | 7.22 | 9.63 | 8.5 | 11.9 | 5.09 | 8.7 | 10.7 | 14.38 | 8.3 | 3.61 | 71.9 | 82.19 | 79.45 | 6.72 | 8.99 | 12.63 | 5.18
| FOSSIL Coal Primary | 001-099 | 146 | 491.67 | 225.11 | 98.69 | 36 | 72.91 | 45.32 | 86.11 | 83.97 | 8.98 | 11.34 | 8.65 | 9.42 | 4.47 | 7.72 | 9.18 | 17.14 | 6.17 | 3.25 | 49.38 | 86.88 | 84.77 | 7.26 | 9.58 | 9.26 | 3.87
| FOSSIL Coal Primary | 100-199 | 215 | 763.42 | 159.66 | 98.89 | 39.7 | 67.98 | 57.93 | 85.15 | 81.74 | 6.73 | 9.48 | 7.54 | 10.67 | 4.18 | 7.79 | 9.76 | 14.75 | 7.05 | 3.62 | 58.41 | 85.06 | 81.62 | 6.58 | 9.45 | 10.83 | 4.12
| FOSSIL Coal Primary | 200-299 | 113 | 455 | 457.05 | 96.82 | 45.62 | 72.57 | 62.93 | 80.15 | 77.3 | 9.8 | 12.2 | 10.86 | 13.01 | 6.84 | 11.23 | 13.19 | 17.73 | 8.62 | 4.39 | 62.86 | 80.74 | 77.89 | 9.42 | 11.82 | 12.72 | 6.54
| FOSSIL Coal Primary | 300-399 | 66 | 306.58 | 465.11 | 96.66 | 48.49 | 72.19 | 67.1 | 81.69 | 78.82 | 7.02 | 9.81 | 8.86 | 13.24 | 5.07 | 8.98 | 11.26 | 14.76 | 9.33 | 3.91 | 67.17 | 81.8 | 78.95 | 7.01 | 9.78 | 13.14 | 5.06
| FOSSIL Coal Primary | 400-599 | 143 | 660.5 | 557.15 | 97.24 | 57.25 | 75.69 | 75.59 | 82.1 | 79.13 | 6.86 | 9.41 | 8.94 | 12.33 | 5.57 | 8.79 | 11.12 | 13.16 | 9.11 | 3.22 | 75.65 | 82.04 | 79.06 | 6.9 | 9.48 | 12.35 | 5.61
| FOSSIL Coal Primary | 600-799 | 118 | 539.33 | 642.66 | 96.75 | 59.62 | 78.55 | 75.8 | 83.34 | 80.77 | 5.78 | 7.82 | 7.4 | 12.01 | 4.65 | 8.03 | 10.04 | 11.96 | 8.63 | 3.38 | 75.9 | 83.34 | 80.77 | 5.78 | 7.82 | 12 | 4.66
| FOSSIL Coal Primary | 800-999 | 43 | 206 | 702.28 | 95.41 | 58.22 | 77.39 | 75.13 | 81.38 | 79.17 | 6.51 | 8.41 | 8.03 | 13.39 | 5.23 | 8.76 | 10.8 | 12.84 | 9.86 | 3.53 | 75.23 | 81.56 | 79.37 | 6.41 | 8.29 | 13.29 | 5.15
| FOSSIL Coal Primary | 1000 Plus | 14 | 56 | 705.56 | 95.19 | 57.49 | 79.7 | 71.72 | 75.78 | 72.85 | 7.91 | 9.33 | 8.99 | 18.06 | 6.16 | 11.85 | 13.37 | 16 | 12.37 | 5.69 | 72.14 | 75.92 | 73.07 | 7.86 | 9.3 | 17.93 | 6.15
| FOSSIL Oil Primary | All Sizes | 89 | 283 | 81.47 | 99.13 | 7.18 | 44.78 | 24.32 | 83.92 | 82.27 | 10.85 | 15.69 | 8.43 | 13.12 | 2.96 | 7.63 | 9.16 | 28.22 | 8.45 | 4.67 | 16.03 | 80.89 | 79.63 | 15.47 | 20.1 | 16.18 | 2.93
| FOSSIL Oil Primary | 001-099 | 27 | 92.42 | 70.78 | 99.63 | 26.68 | 49.42 | 45.25 | 86.65 | 83.67 | 5.25 | 10.64 | 6.6 | 10.85 | 2.51 | 9.35 | 12.26 | 22.18 | 4.01 | 6.84 | 53.99 | 85.47 | 82.09 | 4.41 | 9.59 | 12.04 | 2.49
| FOSSIL Oil Primary | 100-199 | 19 | 65.33 | 161.3 | 97.68 | 10.78 | 54.03 | 17.42 | 85.39 | 84.02 | 19.12 | 24.3 | 14.43 | 10.49 | 4.12 | 7.96 | 9.29 | 35.72 | 6.64 | 3.84 | 19.95 | 84.82 | 83.38 | 16.69 | 21.7 | 11.18 | 4
| FOSSIL Oil Primary | 200-299 | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| FOSSIL Oil Primary | 300-399 | 13 | 47 | 164.32 | 98.66 | 10.89 | 40.77 | 26.16 | 80.86 | 80.33 | 8.61 | 9.81 | 7.1 | 16.67 | 2.46 | 4.93 | 5.32 | 17.01 | 14.2 | 2.47 | 26.7 | 81.05 | 80.5 | 8.04 | 9.24 | 16.62 | 2.34
| FOSSIL Oil Primary | 400-599 | 12 | 33.58 | 23.33 | 98.6 | 1.62 | 41.22 | 3.95 | 85.41 | 84.47 | 49.84 | 56.08 | 23.34 | 10.66 | 3.92 | 7.31 | 8.06 | 69 | 7.28 | 3.39 | 3.93 | 85.35 | 84.42 | 50.41 | 56.53 | 10.66 | 4
| FOSSIL Oil Primary | 600-799 | 7 | 25.42 | 32.14 | 98.64 | 3.2 | 44.43 | 7.43 | 80.37 | 79.79 | 8.37 | 13.1 | 6.17 | 18.95 | 0.68 | 6.7 | 7.16 | 49.56 | 12.93 | 6.02 | 7.19 | 78.49 | 77.88 | 8.76 | 14.03 | 20.82 | 0.69
| FOSSIL Oil Primary | 800-999 | 7 | 12.92 | 53.48 | 87.37 | 0.56 | 28.63 | 1.98 | 77.21 | 76.7 | 5.68 | 22.49 | 5.36 | 22.67 | 0.12 | 3.87 | 4.32 | 68.63 | 18.92 | 3.75 | 1.95 | 77.46 | 76.94 | 5.73 | 22.95 | 22.43 | 0.12
| FOSSIL Gas Primary | All Sizes | 419 | 1540.75 | 54.47 | 98.99 | 11.63 | 42.15 | 25.19 | 81.4 | 79.51 | 17.43 | 21.16 | 10.91 | 13.28 | 5.32 | 8.56 | 9.93 | 28.79 | 10.04 | 3.25 | 27.59 | 79.48 | 77.38 | 16.53 | 20.75 | 15.05 | 5.46
| FOSSIL Gas Primary | 001-099 | 125 | 436.92 | 59.55 | 99.01 | 11.42 | 46.95 | 19.45 | 83.21 | 81.93 | 26.19 | 28.22 | 12.44 | 9.89 | 6.9 | 10.02 | 10.69 | 35.69 | 6.77 | 3.12 | 24.33 | 82 | 80.57 | 23.37 | 25.23 | 10.58 | 7.42
| FOSSIL Gas Primary | 100-199 | 116 | 463.58 | 40.84 | 99.32 | 11.44 | 43.25 | 25.29 | 82.79 | 80.75 | 12.54 | 16.18 | 8 | 13.59 | 3.63 | 6.39 | 7.67 | 23.64 | 10.82 | 2.77 | 26.46 | 82.24 | 80 | 12.1 | 15.65 | 14.12 | 3.64
| FOSSIL Gas Primary | 200-299 | 52 | 171 | 83.37 | 99.05 | 14.92 | 43.7 | 33.6 | 81.43 | 79.41 | 12.11 | 16.57 | 9.97 | 13.95 | 4.63 | 8.22 | 10.16 | 23.69 | 10.36 | 3.59 | 34.14 | 81.32 | 79.4 | 11.72 | 15.93 | 14.15 | 4.53
| FOSSIL Gas Primary | 300-399 | 39 | 153.5 | 54.8 | 98.71 | 10.15 | 39.76 | 25.58 | 81.16 | 79.3 | 15.21 | 19.24 | 10.49 | 14.25 | 4.59 | 7.2 | 8.7 | 25.82 | 11.64 | 2.61 | 25.52 | 80.98 | 79.16 | 15.18 | 19.14 | 14.46 | 4.57
| FOSSIL Gas Primary | 400-599 | 62 | 227.33 | 77.67 | 98.19 | 12.32 | 41.75 | 29.37 | 77.84 | 75.11 | 18.91 | 24.22 | 14.66 | 15.31 | 6.85 | 11.12 | 13.34 | 32.37 | 11.04 | 4.27 | 29.52 | 78.08 | 75.35 | 19 | 24.22 | 14.99 | 6.93
| FOSSIL Gas Primary | 600-799 | 16 | 54.33 | 143.21 | 95.08 | 11.78 | 47.17 | 24.05 | 70.45 | 68.01 | 26.22 | 31.71 | 21.46 | 21.01 | 8.55 | 12.73 | 15.16 | 39.44 | 16.82 | 4.19 | 24.97 | 71.14 | 68.8 | 25.45 | 30.71 | 20.34 | 8.53
| FOSSIL Gas Primary | 800-999 | 9 | 34.08 | 19.89 | 99.44 | 7.81 | 32.71 | 23.76 | 83.08 | 82.64 | 4.94 | 6.16 | 2.86 | 15.68 | 1.24 | 5.47 | 5.89 | 19.9 | 11.45 | 4.23 | 23.88 | 82.96 | 82.51 | 4.81 | 6.05 | 15.83 | 1.21
| FOSSIL Lignite Primary | All Sizes | 35 | 130.25 | 54.05 | 99.52 | 66.39 | 80.43 | 81.87 | 87.31 | 83.06 | 4.55 | 8.5 | 8.01 | 8.79 | 3.9 | 5.4 | 8.96 | 10.27 | 7.29 | 1.5 | 82.55 | 88.05 | 83.77 | 4.67 | 9 | 7.9 | 4.05
| FOSSIL Oil/Gas Primary | 001-099 | 147 | 529.33 | 62.84 | 99.18 | 14.58 | 47.85 | 23.96 | 83.81 | 82.23 | 20.38 | 23.36 | 11.02 | 10.06 | 6.13 | 9.9 | 10.96 | 31.89 | 6.29 | 3.77 | 30.46 | 82.71 | 80.88 | 17.37 | 20.3 | 10.88 | 6.4
| FOSSIL Oil/Gas Primary | 100-199 | 127 | 528.92 | 43.57 | 99.29 | 11.37 | 44.18 | 24.36 | 83.09 | 81.13 | 13.13 | 16.91 | 8.3 | 13.22 | 3.68 | 6.58 | 7.86 | 24.81 | 10.33 | 2.9 | 25.74 | 82.52 | 80.37 | 12.51 | 16.2 | 13.8 | 3.68
| FOSSIL Oil/Gas Primary | 200-299 | 53 | 173.33 | 83.34 | 99.01 | 14.81 | 43.78 | 33.31 | 81.57 | 79.57 | 12.11 | 16.57 | 9.96 | 13.84 | 4.59 | 8.14 | 10.07 | 23.69 | 10.29 | 3.56 | 33.82 | 81.47 | 79.57 | 11.72 | 15.94 | 14.03 | 4.49
| FOSSIL Oil/Gas Primary | 300-399 | 50 | 200.5 | 64.37 | 98.7 | 10.32 | 40 | 25.71 | 81.1 | 79.53 | 13.82 | 17.29 | 9.78 | 14.78 | 4.12 | 6.7 | 7.96 | 24 | 12.2 | 2.58 | 25.79 | 80.99 | 79.47 | 13.59 | 16.97 | 14.95 | 4.06
| FOSSIL Oil/Gas Primary | 400-599 | 69 | 260.92 | 74.08 | 98.23 | 10.9 | 41.73 | 25.89 | 78.87 | 76.39 | 19.94 | 25.32 | 14.72 | 14.68 | 6.45 | 10.6 | 12.62 | 33.94 | 10.53 | 4.15 | 26.12 | 79.05 | 76.56 | 20.02 | 25.3 | 14.42 | 6.54
| FOSSIL Oil/Gas Primary | 600-799 | 21 | 79.75 | 98.16 | 96.55 | 9.13 | 46.85 | 18.55 | 73.73 | 71.91 | 24.26 | 29.69 | 17.83 | 20.33 | 5.94 | 10.74 | 12.51 | 41.03 | 15.53 | 4.79 | 19.48 | 73.41 | 71.61 | 23.87 | 29.12 | 20.48 | 6.11
| FOSSIL Oil/Gas Primary | 800-999 | 11 | 47 | 20.28 | 99.29 | 5.75 | 32.58 | 17.77 | 81.47 | 81.01 | 4.97 | 6.77 | 2.84 | 17.6 | 0.93 | 5.03 | 5.46 | 23.54 | 13.5 | 4.1 | 17.66 | 81.4 | 80.93 | 4.84 | 6.69 | 17.7 | 0.9
| FOSSIL Oil/Gas Primary | All Sizes | 480 | 1823.75 | 57.32 | 98.99 | 10.81 | 42.46 | 25.06 | 81.79 | 79.94 | 16.51 | 20.4 | 10.56 | 13.26 | 4.95 | 8.42 | 9.82 | 28.71 | 9.79 | 3.47 | 25.46 | 79.74 | 77.8 | 16.41 | 20.68 | 15.26 | 5
| NUCLEAR All Types | All Sizes | 105 | 491.75 | 4418.13 | 98.39 | 91.3 | 99 | 92.32 | 92.33 | 90.49 | 1.6 | 2.17 | 2.17 | 6.17 | 1.5 | 1.87 | 2.69 | 2.86 | 5.8 | 0.37 | 92.22 | 92.23 | 90.4 | 1.64 | 2.2 | 6.23 | 1.54
| NUCLEAR All Types | 400-799 | 14 | 63 | 3494.5 | 97.87 | 89.59 | 97.19 | 92.25 | 92.32 | 89.93 | 1.88 | 2.65 | 2.65 | 5.91 | 1.77 | 2.53 | 3.52 | 3.71 | 5.14 | 0.77 | 92.18 | 92.25 | 89.89 | 1.89 | 2.67 | 5.97 | 1.78
| NUCLEAR All Types | 800-999 | 37 | 168.75 | 4760.51 | 97.71 | 92.39 | 99.54 | 92.87 | 92.87 | 91.44 | 1.28 | 1.81 | 1.81 | 5.92 | 1.2 | 1.47 | 2.28 | 2.42 | 5.65 | 0.27 | 92.82 | 92.82 | 91.39 | 1.29 | 1.82 | 5.96 | 1.22
| NUCLEAR All Types | 1000 Plus | 54 | 260 | 4503.28 | 98.35 | 90.98 | 98.97 | 91.97 | 91.97 | 90.01 | 1.74 | 2.29 | 2.29 | 6.4 | 1.63 | 1.97 | 2.76 | 2.94 | 6.06 | 0.34 | 91.93 | 91.94 | 89.97 | 1.78 | 2.33 | 6.4 | 1.67
| NUCLEAR PWR | All Sizes | 62 | 304 | 4495.5 | 97.81 | 91.49 | 99.58 | 91.84 | 91.84 | 90.45 | 1.49 | 1.9 | 1.9 | 6.77 | 1.39 | 1.71 | 2.24 | 2.39 | 6.46 | 0.32 | 91.87 | 91.87 | 90.46 | 1.45 | 1.87 | 6.78 | 1.35
| NUCLEAR PWR | 400-799 | 5 | 22 | 2582.72 | 100 | 89.31 | 99.11 | 90.23 | 90.23 | 88.36 | 2.28 | 2.55 | 2.55 | 7.67 | 2.11 | 3.55 | 3.96 | 4.22 | 6.22 | 1.45 | 90.12 | 90.12 | 88.34 | 2.19 | 2.44 | 7.86 | 2.02
| NUCLEAR PWR | 800-999 | 22 | 109 | 4726.62 | 97.16 | 92.1 | 99.99 | 92.22 | 92.22 | 91.2 | 1.34 | 1.73 | 1.73 | 6.53 | 1.25 | 1.5 | 2.02 | 2.15 | 6.28 | 0.25 | 92.11 | 92.11 | 91.09 | 1.36 | 1.75 | 6.62 | 1.27
| NUCLEAR PWR | 1000 Plus | 35 | 173 | 4761.01 | 98.26 | 91.33 | 99.42 | 91.8 | 91.8 | 90.25 | 1.49 | 1.93 | 1.93 | 6.81 | 1.38 | 1.6 | 2.16 | 2.31 | 6.6 | 0.21 | 91.87 | 91.87 | 90.3 | 1.45 | 1.89 | 6.78 | 1.35
| NUCLEAR BWR | All Sizes | 34 | 155 | 4435.52 | 98.93 | 91.84 | 98.28 | 93.79 | 93.79 | 91.17 | 1.52 | 2.34 | 2.34 | 4.76 | 1.44 | 1.94 | 3.28 | 3.43 | 4.27 | 0.49 | 93.44 | 93.44 | 90.85 | 1.65 | 2.44 | 4.99 | 1.57
| NUCLEAR BWR | 400-799 | 5 | 21 | 3578.16 | 94.24 | 91.17 | 96.29 | 94.79 | 94.79 | 91.76 | 2.2 | 3.51 | 3.51 | 3.07 | 2.14 | 2.61 | 4.47 | 4.59 | 2.6 | 0.47 | 94.69 | 94.69 | 91.68 | 2.28 | 3.57 | 3.11 | 2.2
| NUCLEAR BWR | 800-999 | 11 | 49 | 5675.08 | 98.66 | 94.43 | 99.17 | 95.18 | 95.18 | 92.94 | 0.8 | 1.59 | 1.59 | 4.06 | 0.76 | 1.09 | 2.39 | 2.48 | 3.73 | 0.33 | 95.22 | 95.22 | 93.04 | 0.79 | 1.56 | 4.02 | 0.76
| NUCLEAR BWR | 1000 Plus | 18 | 85 | 4169.14 | 100 | 90.81 | 98.16 | 92.75 | 92.75 | 90.01 | 1.76 | 2.49 | 2.49 | 5.58 | 1.67 | 2.26 | 3.51 | 3.69 | 4.99 | 0.59 | 92.51 | 92.51 | 89.79 | 1.95 | 2.68 | 5.65 | 1.84
| NUCLEAR CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET ENGINE | All Sizes | 315 | 1302.58 | 4.79 | 98.73 | 4.62 | 80.12 | 4.21 | 90.1 | 88.55 | 37.59 | 39.67 | 10.37 | 6.5 | 3.4 | 6.68 | 7.12 | 55.25 | 3.22 | 3.28 | 5.77 | 89.73 | 87.48 | 32.85 | 35.9 | 6.64 | 3.63
| JET ENGINE | 001-019 | 38 | 152.08 | 5.2 | 95.86 | 0.3 | 39.35 | 0.85 | 91.17 | 91.13 | 76.94 | 77.07 | 19.74 | 6 | 2.83 | 5.94 | 5.98 | 87.38 | 2.89 | 3.11 | 0.76 | 90.89 | 90.85 | 79.55 | 79.68 | 6.17 | 2.94
| JET ENGINE | 20 Plus | 277 | 1150.5 | 4.78 | 98.78 | 4.83 | 80.37 | 4.65 | 89.95 | 88.2 | 35.62 | 37.85 | 10.18 | 6.57 | 3.48 | 6.78 | 7.27 | 53.12 | 3.26 | 3.31 | 6.01 | 89.67 | 87.31 | 32.11 | 35.22 | 6.66 | 3.66
| GAS TURBINE | All Sizes | 750 | 3504.25 | 8.16 | 98.28 | 4.27 | 69.66 | 4.25 | 89.65 | 87.49 | 47.1 | 48.58 | 10.75 | 6.54 | 3.81 | 6.23 | 6.46 | 60.18 | 4.12 | 2.41 | 6.13 | 90.1 | 87.88 | 33.47 | 35.08 | 6.8 | 3.1
| GAS TURBINE | 001-019 | 127 | 550 | 3.04 | 96.24 | 0.66 | 73.08 | 0.91 | 88.44 | 87.72 | 84.47 | 84.77 | 17.24 | 6.62 | 4.94 | 8.43 | 8.53 | 90.41 | 3.13 | 3.49 | 0.91 | 88.01 | 87.31 | 84.9 | 85.15 | 6.88 | 5.11
| GAS TURBINE | 020-049 | 158 | 705.25 | 5.47 | 98.76 | 3.26 | 80.87 | 2.71 | 90.5 | 87.06 | 62.29 | 63.06 | 11.08 | 5.03 | 4.48 | 6.23 | 6.36 | 70.22 | 3.27 | 1.76 | 4.03 | 90.44 | 86.88 | 48.97 | 49.97 | 5.69 | 3.87
| GAS TURBINE | 50 Plus | 464 | 2247 | 9.46 | 98.4 | 4.52 | 68.98 | 5.5 | 89.67 | 87.56 | 37.67 | 39.6 | 9.65 | 6.98 | 3.35 | 5.72 | 6.02 | 52.08 | 4.62 | 2.37 | 6.55 | 90.15 | 88 | 30.93 | 32.64 | 6.91 | 2.94
| COMBINED CYCLE | All Sizes | 333 | 1400.58 | 77.7 | 98.71 | 53.59 | 79.92 | 55.5 | 87.91 | 84.9 | 4.05 | 5.09 | 3.94 | 9.75 | 2.34 | 3.92 | 4.71 | 7.89 | 8.17 | 1.58 | 67.05 | 88.5 | 85.17 | 2.49 | 3.57 | 9.79 | 1.72
| HYDRO | All Sizes | 1063 | 4647 | 29.2 | 99.94 | 37.67 | 60.79 | 60.09 | 80.71 | 80.16 | 8.68 | 8.93 | 7.56 | 13.24 | 6.05 | 7.97 | 8.17 | 11.39 | 11.32 | 1.92 | 61.97 | 82.35 | 81.89 | 4.27 | 4.41 | 14.78 | 2.87
| HYDRO | 001-029 | 402 | 1805 | 93.46 | 99.85 | 32.95 | 55.37 | 56.82 | 76.26 | 75.75 | 15.03 | 15.46 | 13.87 | 12.84 | 10.91 | 12.66 | 13 | 17.48 | 11.08 | 1.76 | 59.51 | 82.06 | 81.55 | 7.22 | 7.74 | 12.82 | 5.12
| HYDRO | 30 Plus | 661 | 2842 | 20.91 | 99.95 | 38.01 | 61.16 | 62.15 | 83.52 | 82.95 | 4.4 | 4.52 | 3.72 | 13.49 | 2.99 | 5.01 | 5.12 | 7.31 | 11.47 | 2.02 | 62.14 | 82.37 | 81.91 | 4.05 | 4.16 | 14.92 | 2.71
| PUMPED STORAGE | All Sizes | 111 | 544 | 8.71 | 99.91 | 8.04 | 46.46 | 27.46 | 81.77 | 81.53 | 7.69 | 7.77 | 5.37 | 14.71 | 3.52 | 5.58 | 5.62 | 11.74 | 12.65 | 2.06 | 17.31 | 79.58 | 78.95 | 8.89 | 9.21 | 17.02 | 3.4
| MULTIBOILER/MULTI-TURBINE | All Sizes | 22 | 103 | 373.07 | 99.07 | 37.54 | 63.79 | 68.79 | 87.22 | 79.6 | 3.13 | 9.6 | 8.03 | 10.56 | 2.22 | 4.34 | 9.91 | 13.48 | 8.44 | 2.12 | 58.84 | 84.27 | 79.78 | 2.86 | 6.78 | 13.99 | 1.73
| DIESEL | All Sizes | 166 | 684.17 | 10.21 | 99.29 | 10.35 | 62.47 | 7.57 | 94.11 | 93.49 | 18.91 | 20.5 | 6.23 | 4.12 | 1.76 | 3.64 | 3.86 | 34.04 | 2.24 | 1.88 | 16.57 | 94.72 | 93.46 | 8.6 | 11.23 | 3.72 | 1.56
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.