## Notes
This file contains the Benchmark Geoelectric Field waveshape for the benchmark GMD event associated with proposed Reliability Standard TPL-007-1. A full description of the benchmark GMD event is available at: http://www.nerc.com/pa/Stand/Pages/Project-2013-03-Geomagnetic-Disturbance-Mitigation.aspx.
The Benchmark Geoelectric Field waveshape is calculated from the reference geomagnetic field waveshape for the reference (Quebec) ground model using the plane wave method. The reference geomagnetic field waveshape is based on the measurement record of the March 13-14, 1989 GMD event measured at Natural Resources Canada Ottawa geomagnetic observatory. Analysis of this selection is provided in the benchmark GMD event whitepaper. A description of the reference ground model is also provided in the white paper.
The geomagnetic latitude of the Ottawa geomagnetic observatory is 55°; therefore the amplitude of the geomagnetic field measurement data were scaled up to the 60° reference geomagnetic latitude such that the resulting peak geoelectric field amplitude computed using the reference earth model was 8 V/km. Sampling rate for the geomagnetic field waveshape is 10 seconds. The east-west and north-south components of geomagnetic field are contained in columns E and F respectively.
In the data file, the eastward directional component is indicated by EW (Column B), while the northward directional component is indicated by NS (Column C). Column D is the geoelectric field magnitude (vector sum)

## Reference_geomagnetic_field_Efi
Time(s) | E_EW(mV/km) | E_NS(mV/km) | Emag (mV/km) | dB_EW/dt(nT/s) | dB_NS/dt(nT/s)
5 | 19.1912 | 38.3824 | 42.9128 | 0.658 | -0.329
15 | 15.2473 | 49.6858 | 51.9727 | 0.329 | 0
25 | 28.3599 | 14.3936 | 31.8035 | -0.329 | -0.329
35 | 21.6395 | -31.6765 | 38.3624 | -0.658 | 0
45 | 14.0045 | 14.7828 | 20.3631 | 0.658 | 0
55 | 10.2743 | 18.3648 | 21.0435 | 0 | 0
65 | 27.3425 | -8.0775 | 28.5106 | -0.329 | -0.33
75 | 2.7504 | 12.0803 | 12.3894 | 0.329 | 0.33
85 | 18.9188 | 12.5713 | 22.7147 | 0 | -0.33
95 | 17.6029 | 8.2514 | 19.4409 | 0 | 0
105 | 31.4174 | 6.3466 | 32.052 | 0 | -0.329
115 | 5.7097 | 24.4434 | 25.1014 | 0.329 | 0.329
125 | 2.0273 | 0.60734 | 2.1163 | -0.329 | 0
135 | 4.303 | 17.1777 | 17.7084 | 0.329 | 0
145 | 4.7921 | -3.0145 | 5.6614 | -0.329 | 0
155 | 4.8441 | 34.2325 | 34.5735 | 0.659 | 0
165 | 4.7386 | 10.762 | 11.759 | -0.33 | 0
175 | 4.5753 | -15.2894 | 15.9593 | -0.329 | 0
185 | 4.3941 | -10.1779 | 11.0859 | 0 | 0
195 | 4.2121 | 15.0633 | 15.6412 | 0.329 | 0
205 | 23.2275 | 13.6876 | 26.9605 | 0 | -0.329
215 | 19.1169 | 28.174 | 34.0474 | 0.33 | 0
225 | 12.8815 | 22.1613 | 25.6331 | 0 | 0
235 | 29.2075 | 34.1655 | 44.9484 | 0.33 | -0.33
245 | 23.5573 | -11.7929 | 26.3442 | -0.66 | 0
255 | 16.3771 | -12.0298 | 20.3206 | 0 | 0
265 | 12.8456 | 15.3133 | 19.9877 | 0.33 | 0
275 | 10.7368 | 14.4612 | 18.0113 | 0 | 0
285 | 28.5483 | 9.8699 | 30.2063 | 0 | -0.329
295 | -14.8045 | 27.1147 | 30.8931 | 0.33 | 0.659
305 | 5.5466 | 2.7628 | 6.1966 | -0.33 | -0.33
315 | 10.4288 | -0.1171 | 10.4295 | 0 | 0
325 | -11.3678 | 21.9248 | 24.6967 | 0.33 | 0.33
335 | -8.414 | 37.9925 | 38.913 | 0.329 | 0
345 | 16.3293 | 9.0538 | 18.6713 | -0.329 | -0.33
355 | 14.7333 | 23.3972 | 27.6496 | 0.329 | 0
365 | 9.867 | 21.1658 | 23.3527 | 0 | 0
375 | 7.7651 | 15.2752 | 17.1356 | 0 | 0
385 | 6.5948 | 12.3774 | 14.0247 | 0 | 0
395 | 5.8631 | 10.6091 | 12.1214 | 0 | 0
405 | 5.363 | 28.6721 | 29.1693 | 0.33 | 0
415 | 4.995 | 43.0528 | 43.3416 | 0.329 | 0
425 | 4.7074 | 13.1693 | 13.9854 | -0.329 | 0
435 | 4.4713 | 26.9214 | 27.2902 | 0.329 | 0
445 | 4.2702 | -14.1523 | 14.7825 | -0.659 | 0
455 | 4.0937 | 6.8156 | 7.9505 | 0.33 | 0
465 | 23.1267 | -7.334 | 24.2618 | -0.33 | -0.329
475 | 19.0388 | 32.5817 | 37.7365 | 0.659 | 0
485 | -6.3636 | 10.5877 | 12.353 | -0.329 | 0.329
495 | 13.8716 | 42.8936 | 45.0808 | 0.658 | -0.329
505 | 14.3345 | 36.6199 | 39.3255 | 0 | 0
515 | 9.9702 | 5.5125 | 11.3927 | -0.329 | 0
525 | -11.1684 | 23.0486 | 25.6119 | 0.329 | 0.329
535 | -27.6069 | 21.9257 | 35.2545 | 0 | 0.33
545 | -18.3085 | -2.6543 | 18.4999 | -0.329 | 0
555 | -9.9538 | 37.0713 | 38.3843 | 0.659 | 0
565 | -6.0025 | 33.5927 | 34.1248 | 0 | 0
575 | -3.7967 | 3.802 | 5.3731 | -0.33 | 0
585 | -2.4704 | 22.156 | 22.2933 | 0.33 | 0
595 | -1.6282 | 2.2203 | 2.7533 | -0.33 | 0
605 | 18.1803 | 20.2853 | 27.24 | 0.33 | -0.33
615 | -4.6398 | 0.67479 | 4.6886 | -0.33 | 0.33
625 | -6.5063 | 19.0116 | 20.0941 | 0.33 | 0
635 | -2.9928 | -19.5875 | 19.8148 | -0.659 | 0
645 | -1.6176 | 22.0342 | 22.0935 | 0.659 | 0
655 | -0.89668 | 24.1233 | 24.14 | 0 | 0
665 | -0.47604 | -3.0598 | 3.0966 | -0.33 | 0
675 | -0.21156 | -2.4415 | 2.4507 | 0 | 0
685 | -0.035472 | 1.7895 | 1.7899 | 0 | 0
695 | -19.1039 | 3.3987 | 19.4038 | 0 | 0.329
705 | -34.3206 | 23.3985 | 41.5378 | 0.33 | 0.33
715 | -24.2196 | 19.798 | 31.2818 | 0 | 0
725 | -15.2949 | 13.8551 | 20.6373 | 0 | 0
735 | -10.9134 | 30.3646 | 32.2663 | 0.33 | 0
745 | -8.3665 | 44.0221 | 44.8101 | 0.329 | 0
755 | -6.7592 | 13.7813 | 15.3496 | -0.329 | 0
765 | -44.0608 | -11.0874 | 45.4344 | -0.33 | 0.658
775 | -35.4064 | -5.9096 | 35.8962 | 0 | 0
785 | -3.4887 | -19.2057 | 19.52 | -0.33 | -0.329
795 | -1.4395 | -12.8231 | 12.9036 | 0 | 0
805 | -4.0533 | -5.5548 | 6.8764 | 0 | 0
815 | 14.5582 | -21.3775 | 25.8638 | -0.329 | -0.329
825 | 10.5515 | -15.59 | 18.825 | 0 | 0
835 | 23.8442 | 10.7555 | 26.1578 | 0.329 | -0.33
845 | 17.2997 | 10.2422 | 20.1043 | 0 | 0
855 | 9.8531 | 25.3785 | 27.2241 | 0.33 | 0
865 | -32.12 | -18.5811 | 37.1073 | -0.659 | 0.659
875 | -7.0176 | 20.8968 | 22.0437 | 0.659 | -0.329
885 | -19.1808 | -16.4686 | 25.2808 | -0.659 | 0.329
895 | 2.6689 | -16.9898 | 17.1982 | 0 | -0.329
905 | 4.6327 | -8.3721 | 9.5684 | 0 | 0
915 | 20.58 | 14.4366 | 25.1386 | 0.329 | -0.33
925 | -3.8003 | 12.4344 | 13.0021 | 0 | 0.33
935 | -25.6789 | 7.498 | 26.7512 | 0 | 0.329
945 | -18.6939 | 5.4383 | 19.4688 | 0 | 0
955 | -11.5273 | -14.8361 | 18.7879 | -0.329 | 0
965 | -8.2106 | 26.9211 | 28.1453 | 0.659 | 0
975 | -25.5405 | 5.4587 | 26.1173 | -0.33 | 0.329
985 | -20.4528 | -19.4366 | 28.2152 | -0.329 | 0
995 | -13.6203 | -32.7763 | 35.4937 | -0.329 | 0
1005 | -10.3164 | 16.1115 | 19.1314 | 0.658 | 0
1015 | -8.3713 | -1.945 | 8.5943 | -0.329 | 0
1025 | 12.0732 | -5.7765 | 13.384 | 0 | -0.329
1035 | -10.1967 | 35.6984 | 37.1261 | 0.659 | 0.329
1045 | 7.4918 | 29.0167 | 29.9683 | 0 | -0.329
1055 | -31.1648 | 17.5137 | 35.7488 | 0 | 0.66
1065 | -46.9166 | 12.3652 | 48.5187 | 0 | 0.329
1075 | -32.6339 | -9.7294 | 34.0534 | -0.33 | 0
1085 | -41.1347 | -7.4938 | 41.8117 | 0 | 0.329
1095 | -51.0114 | -40.8925 | 65.3786 | -0.658 | 0.329
1105 | 0.56174 | -30.9827 | 30.9878 | 0 | -0.658
1115 | 42.0619 | -37.0638 | 56.0619 | -0.33 | -0.66
1125 | 27.7213 | -7.7634 | 28.7878 | 0.33 | 0
1135 | 32.6878 | -21.4571 | 39.1011 | -0.33 | -0.329
1145 | 22.4104 | -18.7354 | 29.2103 | 0 | 0
1155 | -6.2198 | 25.9242 | 26.6599 | 0.659 | 0.329
1165 | -6.9656 | -17.3182 | 18.6666 | -0.659 | 0
1175 | -3.5854 | 18.733 | 19.073 | 0.659 | 0
1185 | -2.4679 | -0.49312 | 2.5167 | -0.329 | 0
1195 | -1.9834 | -5.398 | 5.7508 | 0 | 0
1205 | -21.0592 | -22.2673 | 30.6484 | -0.33 | 0.331
1215 | 2.338 | -17.4866 | 17.6422 | 0 | -0.331
1225 | -33.9428 | 46.6794 | 57.7155 | 0.988 | 0.66
1235 | -29.3062 | -0.48844 | 29.3102 | -0.658 | 0
1245 | 0.88785 | -9.1017 | 9.1449 | 0 | -0.329
1255 | -17.2522 | -23.4291 | 29.0957 | -0.33 | 0.329
1265 | 2.626 | 1.4005 | 2.9761 | 0.33 | -0.329
1275 | -15.4573 | 4.325 | 16.051 | 0 | 0.329
1285 | 3.9839 | -17.8031 | 18.2434 | -0.33 | -0.329
1295 | -14.4238 | -33.9958 | 36.9291 | -0.329 | 0.329
1305 | -14.3985 | -24.3811 | 28.3153 | 0 | 0
1315 | -29.0182 | -15.7187 | 33.002 | 0 | 0.329
1325 | -23.0246 | -11.4748 | 25.7255 | 0 | 0
1335 | 3.4342 | 10.1909 | 10.7539 | 0.329 | -0.329
1345 | -54.5957 | -11.3728 | 55.7676 | -0.329 | 0.988
1355 | -46.7343 | 6.7503 | 47.2193 | 0.329 | 0
1365 | -49.0902 | -12.3175 | 50.6119 | -0.329 | 0.329
1375 | -18.2304 | 6.535 | 19.3663 | 0.329 | -0.329
1385 | 7.5688 | 6.9477 | 10.2741 | 0 | -0.33
1395 | -16.1627 | -16.4065 | 23.0305 | -0.329 | 0.33
1405 | 20.7928 | -14.138 | 25.1441 | 0 | -0.659
1415 | -2.2435 | -28.1567 | 28.246 | -0.33 | 0.329
1425 | -8.5655 | -21.882 | 23.4988 | 0 | 0
1435 | 12.3543 | 4.7668 | 13.242 | 0.33 | -0.329
1445 | -10.2585 | -14.8411 | 18.0414 | -0.33 | 0.329
1455 | -12.0829 | -14.8714 | 19.1613 | 0 | 0
1465 | -8.5403 | 9.044 | 12.4391 | 0.33 | 0
1475 | 12.0822 | -12.0074 | 17.0339 | -0.33 | -0.329
1485 | 28.1274 | -12.8667 | 30.9306 | 0 | -0.329
1495 | 18.6174 | -8.7072 | 20.5529 | 0 | 0
1505 | -9.0627 | -6.8784 | 11.3774 | 0 | 0.329
1515 | -9.168 | -5.8153 | 10.8568 | 0 | 0
1525 | -5.3656 | -24.3706 | 24.9542 | -0.33 | 0
1535 | -23.1572 | -19.9213 | 30.5469 | 0 | 0.329
1545 | -37.7849 | -32.6411 | 49.9313 | -0.329 | 0.33
1555 | -46.5729 | -25.6133 | 53.1514 | 0 | 0.329
1565 | -33.5341 | 1.4662 | 33.5662 | 0.329 | 0
1575 | -3.7771 | 20.7179 | 21.0594 | 0.33 | -0.329
1585 | -21.5154 | 13.0537 | 25.1657 | 0 | 0.329
1595 | -1.2382 | -13.5143 | 13.5709 | -0.33 | -0.329
1605 | 0.20314 | -12.8076 | 12.8092 | 0 | 0
1615 | 16.0301 | 10.8356 | 19.3488 | 0.33 | -0.33
1625 | -8.3041 | 8.7151 | 12.0379 | 0 | 0.33
1635 | 27.5643 | -15.6185 | 31.6817 | -0.33 | -0.659
1645 | 3.6558 | 5.4369 | 6.5517 | 0.33 | 0.329
1655 | 15.8509 | 6.4553 | 17.1149 | 0 | -0.329
1665 | -6.082 | -16.736 | 17.8068 | -0.33 | 0.329
1675 | 11.0766 | -14.3715 | 18.1447 | 0 | -0.329
1685 | -8.7898 | -9.098 | 12.6504 | 0 | 0.329
1695 | -9.7512 | -25.9643 | 27.735 | -0.329 | 0
1705 | -25.1294 | -20.7273 | 32.5746 | 0 | 0.33
1715 | -38.8329 | 5.3399 | 39.1983 | 0.329 | 0.329
1725 | -8.8087 | -14.4859 | 16.9539 | -0.329 | -0.329
1735 | 15.8158 | -14.6835 | 21.5811 | 0 | -0.33
1745 | -28.0368 | -10.1397 | 29.814 | 0 | 0.659
1755 | -7.1143 | -8.0658 | 10.755 | 0 | -0.329
1765 | 17.745 | -6.8404 | 19.0178 | 0 | -0.33
1775 | 31.1149 | -6.0347 | 31.6947 | 0 | -0.329
1785 | 1.4789 | 13.7295 | 13.8089 | 0.329 | 0.329
1795 | 15.6739 | 10.2188 | 18.7109 | 0 | -0.329
1805 | -5.6776 | -33.8981 | 34.3703 | -0.658 | 0.329
1815 | 11.7314 | -28.5028 | 30.8226 | 0 | -0.329
1825 | -8.0194 | -17.6602 | 19.3957 | 0 | 0.329
1835 | -8.929 | -32.0411 | 33.262 | -0.329 | 0
1845 | -5.0388 | -6.2305 | 8.013 | 0.329 | 0
1855 | -3.5062 | 16.7388 | 17.1021 | 0.329 | 0
1865 | -21.9731 | -8.6094 | 23.5995 | -0.329 | 0.33
1875 | -17.5772 | -30.3865 | 35.1041 | -0.329 | 0
1885 | -49.6547 | -3.9791 | 49.8139 | 0.329 | 0.659
1895 | -19.549 | -0.5054 | 19.5555 | 0 | -0.33
1905 | -9.6505 | -3.0327 | 10.1158 | 0 | 0
1915 | -28.3937 | 15.4546 | 32.3272 | 0.329 | 0.33
1925 | -23.4127 | -27.0954 | 35.8095 | -0.658 | 0
1935 | 2.7702 | 13.0659 | 13.3563 | 0.658 | -0.33
1945 | 2.2551 | -23.7684 | 23.8751 | -0.658 | 0
1955 | -1.7614 | -23.9468 | 24.0115 | 0 | 0
1965 | -3.1693 | 23.3105 | 23.5249 | 0.658 | 0
1975 | -23.0046 | -19.1194 | 29.9126 | -0.658 | 0.33
1985 | -0.02609 | -2.0566 | 2.0568 | 0.329 | -0.33
1995 | 2.0593 | -17.2625 | 17.3849 | -0.329 | 0
2005 | -1.2235 | -16.0695 | 16.116 | 0 | 0
2015 | 16.816 | 27.4554 | 32.1959 | 0.658 | -0.329
2025 | -6.8309 | 21.9253 | 22.9647 | 0 | 0.329
2035 | -9.1935 | -27.2473 | 28.7565 | -0.658 | 0
2045 | -5.9791 | -24.0346 | 24.7671 | 0 | 0
2055 | -4.7733 | 4.8106 | 6.7769 | 0.329 | 0
2065 | -4.1447 | -33.477 | 33.7326 | -0.659 | 0
2075 | -3.7681 | 28.1914 | 28.4421 | 0.988 | 0
2085 | -22.766 | -11.3073 | 25.4194 | -0.658 | 0.33
2095 | 0.62341 | -16.807 | 16.8186 | 0 | -0.33
2105 | 2.9093 | 8.9647 | 9.4249 | 0.329 | 0
2115 | -19.5319 | -30.8169 | 36.4853 | -0.659 | 0.33
2125 | -16.6952 | -8.3396 | 18.6622 | 0.33 | 0
2135 | 8.1404 | -2.0401 | 8.3921 | 0 | -0.33
2145 | -12.5242 | 34.8198 | 37.0037 | 0.658 | 0.33
2155 | -13.2173 | 7.5266 | 15.21 | -0.329 | 0
2165 | -8.9925 | -0.65422 | 9.0163 | 0 | 0
2175 | -7.1478 | 19.1701 | 20.4594 | 0.329 | 0
2185 | 32.3476 | 15.0189 | 35.6642 | 0 | -0.659
2195 | 25.1217 | -10.4702 | 27.2163 | -0.329 | 0
2205 | 13.4136 | 28.9108 | 31.871 | 0.658 | 0
2215 | -10.9926 | 25.4249 | 27.6995 | 0 | 0.329
2225 | -9.8955 | -4.1838 | 10.7436 | -0.329 | 0
2235 | 13.6852 | -4.9177 | 14.542 | 0 | -0.329
2245 | -7.7381 | 17.7227 | 19.3384 | 0.329 | 0.329
2255 | -9.0213 | 14.9348 | 17.448 | 0 | 0
2265 | -5.2526 | 9.3438 | 10.719 | 0 | 0
2275 | -23.0066 | -12.4151 | 26.1426 | -0.329 | 0.33
2285 | -56.7147 | -9.9467 | 57.5803 | 0 | 0.659
2295 | -3.8312 | -4.8023 | 6.1433 | 0 | -0.659
2305 | 3.5058 | 16.5302 | 16.8979 | 0.329 | 0
2315 | -1.3646 | 13.6855 | 13.7534 | 0 | 0
2325 | -21.9732 | -10.9758 | 24.562 | -0.329 | 0.33
2335 | 0.74666 | 28.9861 | 28.9958 | 0.659 | -0.33
2345 | 2.7379 | 25.8216 | 25.9664 | 0 | 0
2355 | -0.58188 | 15.6006 | 15.6115 | 0 | 0
2365 | -21.0002 | 11.0539 | 23.7318 | 0 | 0.33
2375 | -17.567 | 8.5101 | 19.5197 | 0 | 0
2385 | -50.0899 | 6.9441 | 50.5689 | 0 | 0.658
2395 | -39.5154 | -13.3411 | 41.7067 | -0.33 | 0
2405 | -64.2637 | -29.303 | 70.6292 | -0.329 | 0.659
2415 | -30.592 | -0.60709 | 30.598 | 0.329 | -0.33
2425 | -37.8483 | 3.8992 | 38.0486 | 0 | 0.33
2435 | -32.0413 | 1.8277 | 32.0934 | 0 | 0
2445 | -4.7456 | 1.2915 | 4.9182 | 0 | -0.33
2455 | -23.6578 | -18.1064 | 29.7915 | -0.329 | 0.33
2465 | -3.8201 | 4.935 | 6.2408 | 0.329 | -0.33
2475 | -2.581 | -31.3636 | 31.4696 | -0.658 | 0
2485 | 13.1182 | -7.6204 | 15.171 | 0.329 | -0.329
2495 | 8.0588 | -19.8453 | 21.4192 | -0.329 | 0
2505 | -17.5879 | 2.1372 | 17.7173 | 0.329 | 0.329
2515 | 21.906 | 4.2563 | 22.3157 | 0 | -0.658
2525 | -0.55647 | 1.0903 | 1.2241 | 0 | 0.329
2535 | 12.4099 | 0.025485 | 12.41 | 0 | -0.329
2545 | -9.0701 | -0.43478 | 9.0806 | 0 | 0.329
2555 | -10.8104 | -19.831 | 22.5861 | -0.329 | 0
2565 | -7.3373 | -15.9731 | 17.5778 | 0 | 0
2575 | -25.2023 | -29.1132 | 38.5063 | -0.329 | 0.329
2585 | -1.3767 | -22.3907 | 22.433 | 0 | -0.329
2595 | -37.2704 | -33.9884 | 50.441 | -0.33 | 0.659
2605 | -32.3969 | -26.2786 | 41.7148 | 0 | 0
2615 | -1.9886 | 1.276 | 2.3628 | 0.33 | -0.33
2625 | -0.82394 | 1.5192 | 1.7282 | 0 | 0
2635 | -3.9949 | 17.1414 | 17.6008 | 0.329 | 0
2645 | -4.9402 | -26.3733 | 26.832 | -0.659 | 0
2655 | 13.9342 | -24.9583 | 28.5846 | 0 | -0.329
2665 | 9.9282 | 3.5841 | 10.5553 | 0.33 | 0
2675 | 3.9 | 3.6609 | 5.3491 | 0 | 0
2685 | 1.2251 | 38.1992 | 38.2188 | 0.658 | 0
2695 | -0.20737 | 9.7362 | 9.7384 | -0.329 | 0
2705 | -1.0287 | 20.0969 | 20.1232 | 0.329 | 0
2715 | -1.52 | -2.7906 | 3.1777 | -0.329 | 0
2725 | -1.8216 | 13.8179 | 13.9375 | 0.329 | 0
2735 | -2.0093 | 51.2406 | 51.28 | 0.659 | 0
2745 | -2.1258 | -0.23348 | 2.1386 | -0.659 | 0
2755 | -2.1965 | -6.8782 | 7.2204 | 0 | 0
2765 | -2.2369 | -1.6294 | 2.7674 | 0 | 0
2775 | 16.9345 | -19.2359 | 25.6281 | -0.329 | -0.329
2785 | -25.3973 | 4.5308 | 25.7983 | 0.329 | 0.658
2795 | -4.3924 | -12.2728 | 13.0352 | -0.329 | -0.329
2805 | 1.0561 | -30.7358 | 30.754 | -0.329 | 0
2815 | -1.009 | -21.9239 | 21.9471 | 0 | 0
2825 | -1.6056 | 5.4936 | 5.7234 | 0.329 | 0
2835 | -40.297 | -32.9284 | 52.0397 | -0.659 | 0.659
2845 | -32.5089 | 9.6046 | 33.8981 | 0.659 | 0
2855 | -39.6302 | -6.6745 | 40.1883 | -0.329 | 0.33
2865 | -30.1276 | -9.9654 | 31.7329 | 0 | 0
2875 | -40.1012 | -25.8801 | 47.7272 | -0.33 | 0.329
2885 | -31.4493 | -20.5017 | 37.5417 | 0 | 0
2895 | -22.5394 | 5.6746 | 23.2428 | 0.33 | 0
2905 | -37.1084 | -14.2034 | 39.7337 | -0.33 | 0.329
2915 | -30.3266 | -14.3992 | 33.5715 | 0 | 0
2925 | -22.3563 | 9.4078 | 24.2551 | 0.33 | 0
2935 | -18.2363 | 7.5301 | 19.7298 | 0 | 0
2945 | -15.6746 | -16.5913 | 22.8246 | -0.33 | 0
2955 | -13.9354 | 4.6319 | 14.685 | 0.33 | 0
2965 | -12.674 | 5.7796 | 13.9296 | 0 | 0
2975 | -30.9591 | 1.9374 | 31.0197 | 0 | 0.33
2985 | -26.2337 | 0.42277 | 26.2371 | 0 | 0
2995 | -0.25159 | -0.34109 | 0.42384 | 0 | -0.33
3005 | -0.88282 | 37.6278 | 37.6381 | 0.658 | 0
3015 | -4.9502 | -28.1234 | 28.5557 | -0.988 | 0
3025 | -25.6142 | -9.3177 | 27.2563 | 0.33 | 0.33
3035 | -2.9724 | 18.5475 | 18.7841 | 0.329 | -0.33
3045 | -1.0175 | 13.6959 | 13.7336 | 0 | 0
3055 | 34.0492 | 7.5855 | 34.8839 | 0 | -0.658
3065 | 44.2758 | -14.3289 | 46.5367 | -0.329 | -0.33
3075 | 8.4442 | 7.3131 | 11.1707 | 0.329 | 0.33
3085 | 19.8281 | 27.7441 | 34.1011 | 0.329 | -0.33
3095 | -3.2023 | 19.9256 | 20.1813 | 0 | 0.33
3105 | 13.2752 | 12.2409 | 18.0574 | 0 | -0.33
3115 | 12.0799 | -10.6019 | 16.0725 | -0.329 | 0
3125 | 6.7857 | 10.448 | 12.4582 | 0.329 | 0
3135 | 23.5436 | -27.0971 | 35.8964 | -0.658 | -0.33
3145 | 18.1274 | 15.0094 | 23.5347 | 0.658 | 0
3155 | 11.0976 | 17.4545 | 20.6837 | 0 | 0
3165 | 26.8709 | 9.8037 | 28.6035 | 0 | -0.329
3175 | 20.9159 | 6.6953 | 21.9614 | 0 | 0
3185 | 13.5486 | -14.1624 | 19.5994 | -0.329 | 0
3195 | 29.0835 | -11.2135 | 31.1704 | 0 | -0.329
3205 | 22.9511 | -5.778 | 23.6673 | 0 | 0
3215 | -3.7461 | -41.8854 | 42.0526 | -0.659 | 0.329
3225 | 15.6195 | -13.5022 | 20.6465 | 0.33 | -0.329
3235 | -3.7212 | 14.6163 | 15.0826 | 0.329 | 0.329
3245 | 14.6013 | -8.6247 | 16.9583 | -0.329 | -0.329
3255 | -23.9331 | 9.0372 | 25.5825 | 0.329 | 0.658
3265 | -20.7443 | -29.5164 | 36.0769 | -0.659 | 0
3275 | 8.4378 | 12.3835 | 14.9849 | 0.659 | -0.329
3285 | -10.4365 | -23.6282 | 25.8305 | -0.659 | 0.329
3295 | 8.8734 | -4.0616 | 9.7588 | 0.33 | -0.329
3305 | 28.7117 | 1.1619 | 28.7352 | 0 | -0.329
3315 | 1.4956 | 18.2758 | 18.3369 | 0.329 | 0.329
3325 | 16.8665 | -5.3973 | 17.709 | -0.329 | -0.329
3335 | -3.8778 | -7.7078 | 8.6283 | 0 | 0.329
3345 | -5.3436 | -42.9428 | 43.274 | -0.66 | 0
3355 | 17.389 | -14.542 | 22.6682 | 0.33 | -0.329
3365 | 33.9274 | -24.9065 | 42.088 | -0.33 | -0.329
3375 | 5.314 | -21.0952 | 21.7543 | 0 | 0.329
3385 | 0.69508 | 4.8372 | 4.8869 | 0.33 | 0
3395 | 2.5804 | 23.4418 | 23.5834 | 0.33 | 0
3405 | 2.906 | -23.1221 | 23.304 | -0.66 | 0
3415 | 22.0901 | -41.983 | 47.4399 | -0.329 | -0.329
3425 | 18.0322 | -29.2829 | 34.3897 | 0 | 0
3435 | -26.5757 | 18.9578 | 32.6445 | 0.659 | 0.658
3445 | -21.617 | -3.3599 | 21.8766 | -0.33 | 0
3455 | 8.0267 | -8.7579 | 11.8797 | 0 | -0.329
3465 | 8.5421 | -6.4237 | 10.688 | 0 | 0
3475 | 24.012 | -43.9115 | 50.0479 | -0.658 | -0.329
3485 | -0.547 | -16.2947 | 16.3039 | 0.329 | 0.329
3495 | 15.7746 | 11.4875 | 19.5141 | 0.329 | -0.329
3505 | 14.7004 | 7.3097 | 16.4175 | 0 | 0
3515 | 9.56 | -36.5756 | 37.8043 | -0.658 | 0
3525 | 26.4356 | 7.4731 | 27.4716 | 0.658 | -0.33
3535 | 1.85 | -8.5301 | 8.7284 | -0.329 | 0.33
3545 | -1.1763 | 7.4484 | 7.5407 | 0.329 | 0
3555 | 1.5248 | 6.8603 | 7.0277 | 0 | 0
3565 | 2.3004 | 2.216 | 3.1941 | 0 | 0
3575 | 21.8089 | -18.9072 | 28.8636 | -0.329 | -0.33
3585 | 17.9047 | 3.2345 | 18.1945 | 0.329 | 0
3595 | -7.4809 | 43.3246 | 43.9657 | 0.66 | 0.33
3605 | -6.3897 | -6.6944 | 9.2543 | -0.66 | 0
3615 | 17.2986 | 6.8804 | 18.6167 | 0.33 | -0.33
3625 | 15.0681 | 28.1017 | 31.8866 | 0.33 | 0
3635 | 9.8022 | -18.3775 | 20.8282 | -0.66 | 0
3645 | 7.4386 | 20.1525 | 21.4815 | 0.66 | 0
3655 | 25.3406 | 20.6331 | 32.6783 | 0 | -0.33
3665 | 20.5297 | -7.4341 | 21.8342 | -0.33 | 0
3675 | 13.8443 | -26.5495 | 29.9423 | -0.33 | 0
3685 | 10.627 | -18.6215 | 21.4405 | 0 | 0
3695 | 27.9217 | -30.2323 | 41.1535 | -0.329 | -0.329
3705 | 22.7493 | 15.6435 | 27.6089 | 0.659 | 0
3715 | 15.8156 | -22.6946 | 27.6618 | -0.659 | 0
3725 | -6.7836 | 34.6472 | 35.305 | 0.989 | 0.329
3735 | -4.8861 | -6.8037 | 8.3764 | -0.66 | 0
3745 | 19.0341 | 5.9753 | 19.95 | 0.33 | -0.329
3755 | 16.9112 | -30.3933 | 34.7813 | -0.659 | 0
3765 | -7.5188 | -7.1599 | 10.3825 | 0.329 | 0.329
3775 | 13.2301 | -19.752 | 23.7734 | -0.329 | -0.329
3785 | 13.9728 | 21.2218 | 25.4087 | 0.659 | 0
3795 | 9.7621 | -19.2341 | 21.5696 | -0.659 | 0
3805 | 7.897 | -20.721 | 22.1749 | 0 | 0
3815 | 6.8052 | 25.9592 | 26.8364 | 0.659 | 0
3825 | 25.3355 | 2.2893 | 25.4387 | -0.33 | -0.33
3835 | 20.8629 | 15.2325 | 25.8319 | 0.33 | 0
3845 | 14.369 | -6.2696 | 15.6772 | -0.33 | 0
3855 | 11.2629 | 30.5253 | 32.5368 | 0.66 | 0
3865 | 9.4314 | 6.8671 | 11.6666 | -0.33 | 0
3875 | 8.2403 | 19.2069 | 20.8999 | 0.33 | 0
3885 | 7.4052 | 16.4519 | 18.0417 | 0 | 0
3895 | 6.7829 | 10.3999 | 12.4164 | 0 | 0
3905 | 6.2951 | -30.9994 | 31.6321 | -0.66 | 0
3915 | 5.8965 | -5.5388 | 8.0899 | 0.33 | 0
3925 | 24.7512 | 1.6132 | 24.8037 | 0 | -0.329
3935 | 20.5156 | 0.34648 | 20.5185 | 0 | 0
3945 | 14.1791 | -19.0962 | 23.7847 | -0.33 | 0
3955 | 30.3621 | -15.1862 | 33.9481 | 0 | -0.329
3965 | 5.4598 | -9.1019 | 10.6139 | 0 | 0.329
3975 | 21.3691 | 12.9254 | 24.9741 | 0.33 | -0.329
3985 | 19.9233 | 48.9635 | 52.8617 | 0.659 | 0
3995 | 14.465 | -21.7766 | 26.1431 | -0.989 | 0
4005 | -7.3709 | -5.0162 | 8.9159 | 0.33 | 0.329
4015 | 14.1507 | 2.6005 | 14.3877 | 0 | -0.329
4025 | -3.9942 | 1.0795 | 4.1376 | 0 | 0.329
4035 | 15.0479 | 0.66424 | 15.0626 | 0 | -0.329
4045 | 15.3536 | 38.9017 | 41.822 | 0.659 | 0
4055 | -8.2336 | 11.6916 | 14.2999 | -0.329 | 0.329
4065 | -6.2494 | -15.8684 | 17.0546 | -0.33 | 0
4075 | -20.5102 | 7.7976 | 21.9425 | 0.33 | 0.329
4085 | -14.5476 | -9.695 | 17.4822 | -0.33 | 0
4095 | 30.9237 | 9.8103 | 32.4426 | 0.33 | -0.658
4105 | 7.1539 | 10.4014 | 12.6241 | 0 | 0.329
4115 | 0.77972 | 25.4097 | 25.4216 | 0.329 | 0
4125 | 2.4023 | 38.885 | 38.9592 | 0.329 | 0
4135 | 21.9444 | 27.8836 | 35.4831 | 0 | -0.329
4145 | 18.0965 | -19.9561 | 26.9394 | -0.658 | 0
4155 | 12.0208 | 2.3887 | 12.2559 | 0.329 | 0
4165 | 28.3991 | 26.9981 | 39.1843 | 0.329 | -0.329
4175 | 22.8442 | -17.6459 | 28.8658 | -0.658 | 0
4185 | -3.4426 | 2.4656 | 4.2344 | 0.329 | 0.329
4195 | 16.2237 | 7.3689 | 17.8187 | 0 | -0.329
4205 | 16.3 | 4.9145 | 17.0247 | 0 | 0
4215 | 11.6601 | 23.2037 | 25.9686 | 0.329 | 0
4225 | 9.5076 | 18.7551 | 21.0273 | 0 | 0
4235 | 27.524 | -26.0371 | 37.888 | -0.658 | -0.331
4245 | 3.3856 | -21.168 | 21.437 | 0 | 0.331
4255 | 19.9227 | 8.4332 | 21.6341 | 0.329 | -0.331
4265 | 37.9902 | -10.2608 | 39.3515 | -0.329 | -0.329
4275 | 9.5826 | -10.0437 | 13.8817 | 0 | 0.329
4285 | 4.9399 | -5.3876 | 7.3095 | 0 | 0
4295 | 25.922 | 15.8501 | 30.3838 | 0.329 | -0.329
4305 | 2.9979 | -6.1541 | 6.8455 | -0.329 | 0.329
4315 | 0.73889 | -7.6095 | 7.6453 | 0 | 0
4325 | 3.8135 | -23.1244 | 23.4368 | -0.33 | 0
4335 | 4.779 | 20.7803 | 21.3228 | 0.659 | 0
4345 | 24.319 | 38.9708 | 45.9362 | 0.329 | -0.329
4355 | 1.2693 | -12.2752 | 12.3406 | -0.658 | 0.329
4365 | -0.90327 | -14.1701 | 14.1989 | 0 | 0
4375 | 21.4925 | -6.7544 | 22.5288 | 0 | -0.329
4385 | 18.6426 | -3.9057 | 19.0473 | 0 | 0
4395 | 13.0281 | 16.7245 | 21.2 | 0.329 | 0
4405 | 10.4377 | 13.5834 | 17.1305 | 0 | 0
4415 | 8.9308 | 46.3673 | 47.2195 | 0.658 | 0
4425 | -11.2356 | 16.8147 | 20.2231 | -0.329 | 0.329
4435 | -7.9762 | 7.2452 | 10.7756 | 0 | 0
4445 | -2.4108 | 6.9548 | 7.3608 | 0 | 0
4455 | -0.040133 | 25.2829 | 25.283 | 0.329 | 0
4465 | 1.1813 | 1.4364 | 1.8598 | -0.329 | 0
4475 | -17.4591 | 37.1863 | 41.0809 | 0.659 | 0.331
4485 | 6.1908 | 12.9016 | 14.31 | -0.33 | -0.331
4495 | 8.5473 | -13.6407 | 16.0973 | -0.329 | 0
4505 | 5.3367 | 10.3438 | 11.6393 | 0.329 | 0
4515 | 23.3528 | -26.1508 | 35.0602 | -0.658 | -0.329
4525 | 18.8179 | -2.7393 | 19.0163 | 0.329 | 0
4535 | 12.4005 | 3.8953 | 12.9979 | 0 | 0
4545 | -9.7837 | 21.633 | 23.7425 | 0.329 | 0.329
4555 | 11.6428 | 36.657 | 38.4615 | 0.33 | -0.329
4565 | 12.7076 | -31.1078 | 33.6032 | -0.988 | 0
4575 | 8.6854 | -8.9987 | 12.5065 | 0.329 | 0
4585 | 6.95 | 0.92803 | 7.0117 | 0 | 0
4595 | 25.1495 | -18.5606 | 31.2568 | -0.329 | -0.329
4605 | 20.5695 | 24.038 | 31.6374 | 0.658 | 0
4615 | -5.1445 | 22.4307 | 23.0131 | 0 | 0.329
4625 | -4.309 | -25.2057 | 25.5714 | -0.658 | 0
4635 | -0.048608 | -21.2417 | 21.2418 | 0 | 0
4645 | -17.6324 | -11.2068 | 20.8925 | 0 | 0.329
4655 | -12.9405 | -6.9225 | 14.6758 | 0 | 0
4665 | -6.5018 | -4.6278 | 7.9806 | 0 | 0
4675 | -3.5587 | 15.9084 | 16.3016 | 0.329 | 0
4685 | -21.2461 | 12.8055 | 24.8068 | 0 | 0.331
4695 | -16.3171 | 7.2808 | 17.8678 | 0 | 0
4705 | -9.6011 | 24.0768 | 25.9205 | 0.329 | 0
4715 | -44.7994 | -0.34171 | 44.8007 | -0.329 | 0.658
4725 | -35.0832 | -3.2277 | 35.2313 | 0 | 0
4735 | -21.7853 | -0.39592 | 21.7889 | 0 | 0
4745 | -15.4758 | -18.6788 | 24.2569 | -0.329 | 0
4755 | -31.0268 | 4.8414 | 31.4023 | 0.329 | 0.329
4765 | -5.6012 | 7.1453 | 9.079 | 0 | -0.329
4775 | -21.1191 | 3.9128 | 21.4785 | 0 | 0.329
4785 | -0.19565 | 2.7133 | 2.7204 | 0 | -0.329
4795 | -17.6632 | -17.0851 | 24.5741 | -0.329 | 0.329
4805 | -16.9998 | 5.7038 | 17.9312 | 0.329 | 0
4815 | -11.9719 | 7.6227 | 14.1927 | 0 | 0
4825 | -9.5814 | -15.0154 | 17.812 | -0.329 | 0
4835 | -8.1285 | 25.9868 | 27.2284 | 0.658 | 0
4845 | -7.1488 | 4.3046 | 8.3447 | -0.329 | 0
4855 | -6.4371 | 17.6672 | 18.8033 | 0.329 | 0
4865 | -5.89 | 15.5608 | 16.6383 | 0 | 0
4875 | -5.4505 | 9.9363 | 11.3331 | 0 | 0
4885 | -24.3345 | -11.8732 | 27.0766 | -0.329 | 0.33
4895 | -0.81688 | 9.7556 | 9.7898 | 0.329 | -0.33
4905 | 1.5967 | 10.9425 | 11.0584 | 0 | 0
4915 | -1.4739 | 7.002 | 7.1555 | 0 | 0
4925 | -21.7303 | 24.5766 | 32.8057 | 0.33 | 0.33
4935 | -18.1823 | 38.9271 | 42.9641 | 0.33 | 0
4945 | -12.235 | 28.2799 | 30.8131 | 0 | 0
4955 | -9.4768 | 18.9915 | 21.2246 | 0 | 0
4965 | 11.3691 | 14.3487 | 18.3069 | 0 | -0.33
4975 | -10.8131 | 30.794 | 32.6373 | 0.329 | 0.33
4985 | -12.2451 | 5.8923 | 13.589 | -0.329 | 0
4995 | 10.8404 | 2.5442 | 11.135 | 0 | -0.33
5005 | -29.9245 | 4.9658 | 30.3337 | 0 | 0.659
5015 | 11.2551 | 5.5163 | 12.5343 | 0 | -0.659
5025 | 13.3547 | 24.7804 | 28.1499 | 0.329 | 0
5035 | 24.8041 | 1.5405 | 24.8519 | -0.329 | -0.329
5045 | -1.4003 | -20.0166 | 20.0655 | -0.33 | 0.329
5055 | -5.1025 | 6.295 | 8.1033 | 0.33 | 0
5065 | -41.11 | 9.4573 | 42.1838 | 0 | 0.659
5075 | -32.4965 | -12.6952 | 34.8883 | -0.33 | 0
5085 | -0.83124 | 47.8714 | 47.8786 | 0.989 | -0.329
5095 | 0.92928 | 41.5257 | 41.5361 | 0 | 0
5105 | -21.1446 | 6.4126 | 22.0956 | -0.33 | 0.329
5115 | -18.0172 | -15.879 | 24.0159 | -0.329 | 0
5125 | -12.2063 | -29.0228 | 31.4852 | -0.33 | 0
5135 | -28.7342 | 0.62829 | 28.7411 | 0.33 | 0.33
5145 | -23.1866 | 5.5082 | 23.8319 | 0 | 0
5155 | 3.188 | 3.5846 | 4.7972 | 0 | -0.33
5165 | -35.7666 | -16.1421 | 39.2405 | -0.33 | 0.66
5175 | -31.8619 | 6.8705 | 32.5942 | 0.33 | 0
5185 | -1.8359 | 28.0995 | 28.1594 | 0.329 | -0.33
5195 | -0.82379 | 1.5791 | 1.7811 | -0.329 | 0
5205 | -23.2921 | -1.8422 | 23.3649 | 0 | 0.33
5215 | -20.2801 | 0.79574 | 20.2957 | 0 | 0
5225 | 4.7738 | 20.8187 | 21.359 | 0.329 | -0.33
5235 | -15.6748 | 17.2269 | 23.2909 | 0 | 0.33
5245 | 3.0822 | 11.3007 | 11.7135 | 0 | -0.33
5255 | 3.5336 | 27.832 | 28.0554 | 0.33 | 0
5265 | -96.6262 | 22.3299 | 99.1728 | 0 | 1.647
5275 | -232.2263 | -42.4265 | 236.07 | -0.989 | 2.636
5285 | -343.8446 | -53.2598 | 347.945 | -0.33 | 2.964
5295 | -399.8978 | -33.0628 | 401.2623 | 0 | 2.637
5305 | -398.9168 | -77.506 | 406.3765 | -0.987 | 1.976
5315 | -418.8216 | -136.0014 | 440.3498 | -1.318 | 2.306
5325 | -442.135 | -136.6459 | 462.7693 | -0.659 | 2.306
5335 | -461.5031 | -151.434 | 485.7133 | -0.989 | 2.307
5345 | -497.7604 | -206.1661 | 538.767 | -1.647 | 2.635
5355 | -490.0736 | -363.847 | 610.3743 | -3.624 | 1.977
5365 | -617.408 | -291.3205 | 682.6861 | -0.33 | 4.282
5375 | -648.7124 | 15.8894 | 648.907 | 3.625 | 2.966
5385 | -464.147 | 158.5861 | 490.4916 | 2.305 | -0.329
5395 | -440.6352 | 170.6855 | 472.5388 | 1.319 | 1.647
5405 | -416.7202 | 139.0007 | 439.2914 | 0.658 | 0.988
5415 | -276.5376 | 44.6331 | 280.1163 | -0.658 | -0.988
5425 | -208.9956 | -2.1718 | 209.0069 | -0.33 | -0.33
5435 | -156.048 | 53.1908 | 164.8643 | 0.988 | -0.659
5445 | -114.6689 | -34.4381 | 119.7286 | -1.317 | -0.658
5455 | -27.3232 | -75.9835 | 80.7468 | -0.66 | -1.648
5465 | 60.6464 | -33.4257 | 69.2478 | 0.331 | -1.976
5475 | 83.8046 | 19.1083 | 85.9554 | 0.658 | -1.319
5485 | 39.7583 | 71.3154 | 81.6493 | 0.988 | -0.329
5495 | 48.6685 | 68.6058 | 84.1153 | 0.33 | -0.989
5505 | 48.201 | 99.8936 | 110.9147 | 0.988 | -0.658
5515 | 27.7265 | 109.9685 | 113.41 | 0.659 | -0.329
5525 | -3.7655 | 94.4789 | 94.5539 | 0.33 | 0
5535 | -23.6291 | 84.1515 | 87.406 | 0.329 | 0
5545 | -53.1383 | 41.5084 | 67.4286 | -0.329 | 0.329
5555 | -16.4814 | 47.6952 | 50.4625 | 0.329 | -0.659
5565 | 16.9586 | -36.6308 | 40.3659 | -1.318 | -0.659
5575 | 36.4237 | -30.2429 | 47.3426 | 0 | -0.659
5585 | 69.2218 | -30.4716 | 75.6319 | -0.329 | -0.988
5595 | 94.9402 | -57.4481 | 110.9681 | -0.659 | -0.988
5605 | 132.027 | -59.0691 | 144.6385 | -0.33 | -1.319
5615 | 122.6169 | -57.4853 | 135.4232 | -0.329 | -0.658
5625 | 112.6956 | -0.91932 | 112.6993 | 0.659 | -0.659
5635 | 91.4378 | -53.0306 | 105.703 | -0.988 | -0.33
5645 | 38.5341 | -7.8874 | 39.3331 | 0.658 | 0.33
5655 | 20.2272 | 78.0669 | 80.6448 | 1.318 | 0
5665 | -5.6543 | 58.0784 | 58.353 | 0 | 0.33
5675 | 31.5122 | 13.613 | 34.3269 | -0.329 | -0.66
5685 | 45.0231 | -12.9317 | 46.8434 | -0.329 | -0.329
5695 | 48.0623 | -66.7518 | 82.2544 | -0.989 | -0.33
5705 | 70.2499 | -88.131 | 112.7037 | -0.659 | -0.658
5715 | 88.1713 | -59.9341 | 106.6127 | 0 | -0.66
5725 | 80.3788 | -57.635 | 98.9067 | -0.329 | -0.329
5735 | 111.9683 | -42.9534 | 119.9245 | 0 | -0.988
5745 | 101.6657 | -30.6248 | 106.1781 | 0 | -0.33
5755 | 88.7338 | 14.5249 | 89.9147 | 0.659 | -0.329
5765 | 83.3138 | 10.812 | 84.0124 | 0 | -0.33
5775 | 80.7262 | 20.6348 | 83.3218 | 0.329 | -0.329
5785 | 79.5909 | -25.3188 | 83.5209 | -0.659 | -0.329
5795 | 79.264 | -25.1318 | 83.1528 | 0 | -0.329
5805 | 79.5187 | 2.7572 | 79.5664 | 0.33 | -0.331
5815 | 99.1014 | 2.4785 | 99.1324 | 0 | -0.658
5825 | 114.9552 | -20.8079 | 116.8232 | -0.33 | -0.659
5835 | 105.5938 | 0.9131 | 105.5978 | 0.33 | -0.329
5845 | 78.274 | 40.7729 | 88.2568 | 0.658 | 0
5855 | 97.9718 | 48.5302 | 109.3328 | 0.33 | -0.66
5865 | 40.6888 | 11.8371 | 42.3757 | -0.33 | 0.66
5875 | 67.755 | 3.5295 | 67.8469 | 0 | -0.66
5885 | 22.8995 | 22.693 | 32.2391 | 0.33 | 0.66
5895 | 17.2578 | -1.3147 | 17.3078 | -0.33 | 0
5905 | 2.9061 | 15.1197 | 15.3964 | 0.33 | 0.329
5915 | -30.9268 | -5.2884 | 31.3757 | -0.33 | 0.659
5925 | -36.5984 | -6.5934 | 37.1876 | 0 | 0.329
5935 | -37.7629 | 35.5287 | 51.849 | 0.66 | 0.329
5945 | -21.6317 | 28.9449 | 36.135 | 0 | 0
5955 | -29.0487 | -1.8773 | 29.1093 | -0.33 | 0.331
5965 | 0.083001 | -22.4313 | 22.4314 | -0.33 | -0.331
5975 | -13.8502 | 3.9066 | 14.3906 | 0.33 | 0.331
5985 | 7.9486 | 6.9996 | 10.5912 | 0 | -0.331
5995 | -9.3735 | 42.4746 | 43.4966 | 0.659 | 0.331
6005 | -27.9208 | 52.6469 | 59.5925 | 0.329 | 0.329
6015 | 0.094228 | 55.1138 | 55.1139 | 0.329 | -0.329
6025 | -34.0142 | 39.1535 | 51.8648 | 0 | 0.658
6035 | -9.089 | 46.1717 | 47.0578 | 0.33 | -0.329
6045 | -1.4477 | 55.031 | 55.05 | 0.33 | 0
6055 | 36.2915 | 60.2582 | 70.3429 | 0.329 | -0.66
6065 | 47.7803 | 64.1145 | 79.9602 | 0.33 | -0.329
6075 | 70.2816 | 67.1342 | 97.1932 | 0.329 | -0.658
6085 | 70.204 | 50.4842 | 86.4711 | 0 | -0.33
6095 | 48.3444 | 37.4724 | 61.1667 | 0 | 0
6105 | -5.112 | 68.7579 | 68.9476 | 0.659 | 0.659
6115 | -24.4423 | 75.5603 | 79.4153 | 0.33 | 0.329
6125 | -32.4386 | 17.8053 | 37.004 | -0.66 | 0.329
6135 | -39.4181 | -7.4132 | 40.1091 | -0.329 | 0.331
6145 | -25.7655 | 1.0737 | 25.7879 | 0 | 0
6155 | -34.292 | 7.8552 | 35.1802 | 0 | 0.329
6165 | -25.1045 | 10.3945 | 27.1713 | 0 | 0
6175 | -16.0687 | 30.5859 | 34.55 | 0.329 | 0
6185 | 26.9802 | 26.9401 | 38.1274 | 0 | -0.66
6195 | 40.927 | 40.0666 | 57.2744 | 0.33 | -0.329
6205 | 45.6537 | 52.3683 | 69.4745 | 0.33 | -0.329
6215 | 31.1656 | 59.6507 | 67.3015 | 0.329 | 0
6225 | 19.9472 | 64.7246 | 67.7286 | 0.329 | 0
6235 | 33.4325 | 30.1887 | 45.0454 | -0.329 | -0.329
6245 | -12.2613 | 41.1666 | 42.9538 | 0.329 | 0.658
6255 | 6.5901 | 36.7254 | 37.312 | 0 | -0.329
6265 | 29.7575 | 67.7198 | 73.9694 | 0.659 | -0.329
6275 | 3.4924 | 36.5116 | 36.6783 | -0.33 | 0.329
6285 | -0.048677 | 6.4224 | 6.4226 | -0.329 | 0
6295 | -36.0225 | 47.4135 | 59.5455 | 0.659 | 0.658
6305 | -27.5555 | 24.5296 | 36.8918 | -0.33 | 0
6315 | -34.5995 | 17.5447 | 38.7936 | 0 | 0.331
6325 | -44.3456 | 18.3445 | 47.9901 | 0 | 0.329
6335 | -31.3235 | 37.1165 | 48.5674 | 0.33 | 0
6345 | -39.9147 | 32.4852 | 51.4633 | 0 | 0.329
6355 | -11.3751 | 25.6878 | 28.0938 | 0 | -0.329
6365 | 32.4541 | 41.4775 | 52.6655 | 0.33 | -0.66
6375 | 23.2719 | 54.5161 | 59.2755 | 0.329 | 0
6385 | -8.0844 | 23.7332 | 25.0723 | -0.329 | 0.331
6395 | 29.1716 | 56.0725 | 63.2069 | 0.659 | -0.66
6405 | -13.8696 | 87.3426 | 88.437 | 0.658 | 0.66
6415 | 2.3799 | 47.549 | 47.6085 | -0.329 | -0.331
6425 | 24.8412 | 71.4355 | 75.6315 | 0.658 | -0.329
6435 | 17.5814 | 60.2302 | 62.7437 | 0 | 0
6445 | -9.0495 | 64.4494 | 65.0816 | 0.331 | 0.329
6455 | -8.6359 | 33.3825 | 34.4815 | -0.331 | 0
6465 | -4.5772 | 64.8694 | 65.0306 | 0.66 | 0
6475 | -22.3693 | 56.9548 | 61.1902 | 0 | 0.331
6485 | -36.8769 | 62.746 | 72.7802 | 0.329 | 0.329
6495 | -45.6476 | 32.7665 | 56.1903 | -0.329 | 0.329
6505 | -51.8362 | 45.5122 | 68.9808 | 0.329 | 0.329
6515 | -18.1848 | 41.8795 | 45.6572 | 0 | -0.329
6525 | -29.9035 | 54.0429 | 61.7645 | 0.33 | 0.329
6535 | -26.1057 | 84.6016 | 88.5377 | 0.659 | 0
6545 | -19.2318 | 48.6888 | 52.3494 | -0.33 | 0
6555 | -34.9409 | 54.9509 | 65.1189 | 0.33 | 0.33
6565 | -47.9734 | 48.3996 | 68.1467 | 0 | 0.329
6575 | -36.4434 | 39.7124 | 53.8999 | 0 | 0
6585 | -45.7589 | 54.028 | 70.8018 | 0.329 | 0.33
6595 | -36.6568 | 66.0634 | 75.5519 | 0.33 | 0
6605 | -65.8514 | 92.0213 | 113.1562 | 0.658 | 0.659
6615 | -53.069 | 73.4004 | 90.5756 | 0 | 0
6625 | -57.0319 | 93.8838 | 109.8489 | 0.66 | 0.329
6635 | -64.6427 | 57.3128 | 86.3912 | -0.331 | 0.329
6645 | -69.3074 | 62.5841 | 93.3824 | 0.331 | 0.331
6655 | -91.8102 | 74.3951 | 118.1683 | 0.329 | 0.658
6665 | -90.5016 | 80.3051 | 120.9936 | 0.329 | 0.329
6675 | -48.2879 | 45.7138 | 66.4941 | -0.329 | -0.329
6685 | -36.1895 | 56.3235 | 66.9478 | 0.329 | 0
6695 | -14.1416 | 32.2159 | 35.1831 | -0.329 | -0.329
6705 | -15.1604 | 9.0211 | 17.6413 | -0.329 | 0
6715 | 0.32784 | 14.4909 | 14.4946 | 0 | -0.329
6725 | -4.4646 | 58.5772 | 58.7471 | 0.658 | 0
6735 | 8.8026 | 33.4546 | 34.5933 | -0.329 | -0.331
6745 | 2.452 | 45.0407 | 45.1074 | 0.329 | 0
6755 | -43.1826 | 60.8612 | 74.6246 | 0.33 | 0.66
6765 | 0.066224 | 69.3688 | 69.3688 | 0.329 | -0.66
6775 | -16.5598 | 55.738 | 58.146 | 0 | 0.331
6785 | -58.4158 | 44.4881 | 73.4275 | 0 | 0.658
6795 | -47.2523 | -0.048393 | 47.2523 | -0.659 | 0
6805 | -14.4703 | 23.1958 | 27.3393 | 0.33 | -0.329
6815 | -11.9633 | 28.6743 | 31.0699 | 0 | 0
6825 | -14.2779 | 26.0748 | 29.728 | 0 | 0
6835 | -14.6273 | 43.9564 | 46.3263 | 0.329 | 0
6845 | 4.6992 | 19.8059 | 20.3557 | -0.329 | -0.329
6855 | 1.0595 | 16.7943 | 16.8276 | 0 | 0
6865 | -4.6574 | 38.4955 | 38.7762 | 0.329 | 0
6875 | -7.0584 | 15.8499 | 17.3505 | -0.329 | 0
6885 | -8.244 | -5.6129 | 9.9734 | -0.33 | 0
6895 | -8.8388 | -17.8576 | 19.9253 | -0.329 | 0
6905 | -28.3112 | 12.1823 | 30.821 | 0.329 | 0.329
6915 | -5.2812 | 17.2503 | 18.0407 | 0 | -0.329
6925 | -22.3404 | 15.3703 | 27.1171 | 0 | 0.329
6935 | -21.6402 | -4.3595 | 22.0749 | -0.329 | 0
6945 | -16.6865 | -0.73231 | 16.7026 | 0 | 0
6955 | -14.3955 | -14.1102 | 20.1576 | -0.329 | 0
6965 | -13.0373 | -7.6478 | 15.1149 | 0 | 0
6975 | -50.52 | -19.5818 | 54.1823 | -0.331 | 0.658
6985 | -41.9838 | 7.1589 | 42.5897 | 0.331 | 0
6995 | -48.5761 | 11.2204 | 49.8551 | 0 | 0.33
7005 | -19.4108 | 9.0171 | 21.403 | 0 | -0.33
7015 | -33.0612 | 27.6543 | 43.1022 | 0.329 | 0.33
7025 | -30.2079 | 4.3214 | 30.5155 | -0.329 | 0
7035 | -43.0053 | 21.2911 | 47.9872 | 0.329 | 0.329
7045 | -35.7683 | 20.5938 | 41.2732 | 0 | 0
7055 | -8.4091 | 15.6835 | 17.7957 | 0 | -0.329
7065 | -27.3127 | 13.4522 | 30.4458 | 0 | 0.329
7075 | -26.8061 | 31.3496 | 41.2476 | 0.329 | 0
7085 | -2.5061 | 7.3784 | 7.7923 | -0.329 | -0.329
7095 | -3.9055 | 4.6552 | 6.0765 | 0 | 0
7105 | 10.8941 | -11.6784 | 15.9708 | -0.329 | -0.33
7115 | -13.9287 | 31.5118 | 34.4529 | 0.658 | 0.33
7125 | -35.9295 | 30.0063 | 46.8114 | 0 | 0.329
7135 | -28.9092 | 1.5027 | 28.9482 | -0.329 | 0
7145 | 16.8133 | 20.5998 | 26.5901 | 0.329 | -0.659
7155 | -6.8639 | 20.48 | 21.5996 | 0 | 0.33
7165 | -51.4885 | -3.4176 | 51.6018 | -0.329 | 0.659
7175 | -22.4776 | -1.6453 | 22.5377 | 0 | -0.33
7185 | -32.9024 | 22.3306 | 39.7646 | 0.329 | 0.33
7195 | -29.1222 | 1.111 | 29.1434 | -0.329 | 0
7205 | -22.4213 | -0.089464 | 22.4215 | 0 | 0
7215 | 19.3853 | 42.1269 | 46.3732 | 0.659 | -0.659
7225 | -5.6384 | 35.6822 | 36.1249 | 0 | 0.329
7235 | 6.7159 | 4.9629 | 8.3507 | -0.33 | -0.329
7245 | 4.3005 | 22.9627 | 23.3619 | 0.33 | 0
7255 | -20.533 | 2.9104 | 20.7382 | -0.33 | 0.329
7265 | -19.0929 | -36.666 | 41.3392 | -0.658 | 0
7275 | 4.8468 | -5.952 | 7.6758 | 0.329 | -0.329
7285 | 2.9355 | -54.1382 | 54.2177 | -0.989 | 0
7295 | 17.2391 | 15.4385 | 23.1416 | 0.989 | -0.33
7305 | 11.2218 | 3.2281 | 11.6768 | -0.329 | 0
7315 | -15.1833 | -2.3387 | 15.3624 | 0 | 0.33
7325 | -14.5904 | 0.34806 | 14.5945 | 0 | 0
7335 | -29.5683 | -17.8203 | 34.5232 | -0.331 | 0.329
7345 | -4.7823 | 6.1298 | 7.7746 | 0.331 | -0.329
7355 | -1.8039 | 8.7138 | 8.8985 | 0 | 0
7365 | -4.6207 | 5.6892 | 7.3292 | 0 | 0
7375 | -24.7238 | -33.8273 | 41.8993 | -0.66 | 0.329
7385 | -1.9774 | -26.3703 | 26.4444 | 0 | -0.329
7395 | -19.2012 | 4.7953 | 19.791 | 0.329 | 0.329
7405 | -37.8701 | -12.8809 | 40.0008 | -0.329 | 0.33
7415 | 9.379 | -11.9514 | 15.1921 | 0 | -0.659
7425 | -28.6666 | -45.1506 | 53.4822 | -0.658 | 0.659
7435 | -9.639 | -34.8085 | 36.1185 | 0 | -0.33
7445 | -4.6067 | -59.6342 | 59.8119 | -0.659 | 0
7455 | -25.9894 | -26.0408 | 36.7909 | 0.329 | 0.33
7465 | -22.5674 | -33.2266 | 40.1658 | -0.329 | 0
7475 | 21.8276 | -27.408 | 35.0377 | 0 | -0.659
7485 | 16.7224 | -0.17656 | 16.7233 | 0.329 | 0
7495 | 25.4319 | 19.4191 | 31.9982 | 0.33 | -0.33
7505 | -2.276 | -7.141 | 7.4949 | -0.33 | 0.33
7515 | -6.7944 | -29.3758 | 30.1513 | -0.329 | 0
7525 | 14.408 | -22.3069 | 26.5554 | 0 | -0.33
7535 | -8.3935 | -34.158 | 35.1742 | -0.33 | 0.33
7545 | -10.4444 | -65.0498 | 65.883 | -0.659 | 0
7555 | 12.1144 | -29.6618 | 32.0403 | 0.33 | -0.33
7565 | -29.0857 | -36.4944 | 46.6671 | -0.33 | 0.659
7575 | -26.7075 | -11.2586 | 28.9836 | 0.33 | 0
7585 | 21.4301 | -45.5097 | 50.3029 | -0.659 | -0.659
7595 | -1.5424 | -39.3442 | 39.3745 | 0 | 0.33
7605 | 11.7582 | -7.9758 | 14.208 | 0.329 | -0.33
7615 | 28.8864 | -5.9853 | 29.5 | 0 | -0.329
7625 | 19.3844 | 10.7759 | 22.1782 | 0.33 | 0
7635 | 10.7663 | 25.6282 | 27.7978 | 0.329 | 0
7645 | -12.6297 | 15.7456 | 20.185 | 0 | 0.329
7655 | -11.1161 | -31.2118 | 33.1322 | -0.659 | 0
7665 | -6.5598 | -7.9924 | 10.3397 | 0.33 | 0
7675 | -24.0466 | -21.1176 | 32.0031 | -0.33 | 0.33
7685 | 19.1957 | -18.8715 | 26.9185 | 0 | -0.659
7695 | 17.8259 | -13.1142 | 22.1302 | 0 | 0
7705 | -10.5276 | -10.3648 | 14.7736 | 0 | 0.329
7715 | 27.9194 | -47.1036 | 54.7562 | -0.658 | -0.658
7725 | 4.8204 | -18.9348 | 19.5388 | 0.329 | 0.329
7735 | 17.3215 | -9.9391 | 19.9705 | 0 | -0.329
7745 | 14.6542 | -9.8658 | 17.6658 | 0 | 0
7755 | 27.8345 | -9.0469 | 29.2679 | 0 | -0.329
7765 | 1.8022 | -8.2913 | 8.4849 | 0 | 0.329
7775 | -2.0486 | -26.8363 | 26.9144 | -0.329 | 0
7785 | 19.3333 | -22.3414 | 29.5451 | 0 | -0.329
7795 | 35.1479 | 3.4046 | 35.3124 | 0.329 | -0.331
7805 | 44.3328 | -16.5359 | 47.3164 | -0.329 | -0.329
7815 | 31.3952 | -36.0495 | 47.8041 | -0.331 | 0
7825 | 20.8166 | -65.8724 | 69.0833 | -0.658 | 0
7835 | 34.5492 | -30.5269 | 46.1036 | 0.329 | -0.329
7845 | 8.1131 | -18.2033 | 19.9294 | 0 | 0.329
7855 | 3.8112 | -54.6414 | 54.7742 | -0.658 | 0
7865 | 5.5961 | -64.0343 | 64.2784 | -0.33 | 0
7875 | 5.6958 | -46.4091 | 46.7574 | 0 | 0
7885 | -13.7578 | -72.0268 | 73.329 | -0.659 | 0.329
7895 | 9.0121 | -38.0432 | 39.0961 | 0.33 | -0.329
7905 | 49.147 | -25.5844 | 55.4075 | 0 | -0.658
7915 | 37.5881 | -23.2622 | 44.204 | 0 | 0
7925 | 23.865 | -20.8733 | 31.7054 | 0 | 0
7935 | 17.3887 | -57.4627 | 60.036 | -0.66 | 0
7945 | 32.9006 | -28.7683 | 43.7043 | 0.33 | -0.33
7955 | 45.8218 | -19.2714 | 49.7094 | 0 | -0.33
7965 | 14.8987 | -18.7398 | 23.9406 | 0 | 0.33
7975 | -10.4533 | 1.7573 | 10.6 | 0.33 | 0.33
7985 | 13.604 | -39.5488 | 41.8232 | -0.66 | -0.33
7995 | 53.7359 | -55.9199 | 77.5538 | -0.329 | -0.659
8005 | 61.1587 | -60.8789 | 86.2938 | -0.329 | -0.33
8015 | 81.5772 | -46.0707 | 93.6875 | 0 | -0.658
8025 | 60.8645 | -34.3548 | 69.8909 | 0 | 0
8035 | 22.7743 | -8.9159 | 24.4573 | 0.329 | 0.329
8045 | 55.4224 | 10.2343 | 56.3594 | 0.329 | -0.658
8055 | 67.0627 | 2.8706 | 67.1241 | 0 | -0.331
8065 | 49.8543 | -23.2373 | 55.0039 | -0.329 | 0
8075 | 37.0253 | -41.3242 | 55.4848 | -0.329 | 0
8085 | 49.2438 | -32.6083 | 59.0614 | 0 | -0.329
8095 | 40.8787 | -43.5172 | 59.7061 | -0.329 | 0
8105 | 12.5602 | -35.4336 | 37.5939 | 0 | 0.329
8115 | 69.0593 | -26.833 | 74.0891 | 0 | -0.987
8125 | 79.2633 | -3.1614 | 79.3264 | 0.329 | -0.33
8135 | 95.9341 | -42.7436 | 105.0256 | -0.659 | -0.659
8145 | 73.3699 | -38.9987 | 83.0906 | 0 | 0
8155 | 72.508 | -8.9319 | 73.056 | 0.33 | -0.33
8165 | 58.0014 | -7.7758 | 58.5203 | 0 | 0
8175 | 64.5605 | -10.8045 | 65.4583 | 0 | -0.329
8185 | 72.6105 | 7.6527 | 73.0127 | 0.329 | -0.329
8195 | 38.6508 | 22.8239 | 44.8866 | 0.329 | 0.329
8205 | 11.1642 | -6.2018 | 12.7711 | -0.329 | 0.329
8215 | 33.483 | 27.5691 | 43.3725 | 0.658 | -0.329
8225 | 33.8505 | 2.5809 | 33.9488 | -0.329 | 0
8235 | 28.8499 | 14.1846 | 32.1484 | 0.329 | 0
8245 | 6.9103 | 30.3521 | 31.1288 | 0.33 | 0.329
8255 | 28.0811 | -18.2135 | 33.4706 | -0.659 | -0.329
8265 | -9.7715 | -0.1317 | 9.7724 | 0.329 | 0.659
8275 | -25.7132 | -15.5245 | 30.0362 | -0.329 | 0.33
8285 | -11.9175 | -14.6543 | 18.8885 | 0 | 0
8295 | -1.8513 | 9.3745 | 9.5556 | 0.329 | 0
8305 | -16.3615 | 26.7809 | 31.3833 | 0.33 | 0.329
8315 | 9.2373 | -1.3454 | 9.3347 | -0.33 | -0.329
8325 | 12.7096 | 32.9456 | 35.3121 | 0.66 | 0
8335 | 10.1266 | 46.4551 | 47.546 | 0.329 | 0
8345 | -9.9234 | 30.9298 | 32.4827 | 0 | 0.329
8355 | -6.4357 | 19.5258 | 20.5591 | 0 | 0
8365 | -39.1122 | 32.9898 | 51.1673 | 0.33 | 0.659
8375 | -47.8877 | 64.0095 | 79.9403 | 0.658 | 0.329
8385 | -49.6424 | 28.6698 | 57.3265 | -0.329 | 0.329
8395 | -33.3359 | 54.5973 | 63.9699 | 0.658 | 0
8405 | -1.7742 | -12.9288 | 13.05 | -0.987 | -0.329
8415 | 0.73344 | -15.3053 | 15.3228 | 0 | 0
8425 | 17.7006 | 15.0123 | 23.2095 | 0.329 | -0.329
8435 | 32.637 | 34.2904 | 47.3393 | 0.329 | -0.329
8445 | 41.9689 | 45.2964 | 61.7508 | 0.329 | -0.33
8455 | 29.3726 | 52.6762 | 60.3119 | 0.331 | 0
8465 | 38.3608 | 38.6982 | 54.4895 | 0 | -0.329
8475 | 10.1384 | 85.0882 | 85.6901 | 0.988 | 0.329
8485 | 62.734 | 48.0993 | 79.0513 | -0.33 | -0.989
8495 | 52.3175 | 68.6289 | 86.2963 | 0.659 | 0
8505 | 53.2071 | 36.8937 | 64.7467 | -0.329 | -0.329
8515 | 59.8256 | 44.2594 | 74.4178 | 0.329 | -0.329
8525 | 63.9851 | 57.5048 | 86.0285 | 0.33 | -0.329
8535 | 67.306 | 64.4043 | 93.1558 | 0.329 | -0.331
8545 | 50.751 | 49.752 | 71.0699 | 0 | 0
8555 | 56.9675 | 57.0976 | 80.6563 | 0.33 | -0.329
8565 | 65.0927 | 46.6289 | 80.0707 | 0 | -0.329
8575 | 50.5482 | 17.1176 | 53.3679 | -0.33 | 0
8585 | 38.5869 | 53.8356 | 66.2361 | 0.659 | 0
8595 | 31.9856 | 9.8892 | 33.4795 | -0.659 | 0
8605 | 8.5432 | 25.0242 | 26.4424 | 0.33 | 0.329
8615 | 9.5159 | 84.8396 | 85.3716 | 0.987 | 0
8625 | -5.8066 | 68.7464 | 68.9912 | 0 | 0.329
8635 | -0.81316 | 48.2735 | 48.2803 | 0 | 0
8645 | 5.4174 | 57.6936 | 57.9474 | 0.331 | 0
8655 | 7.9685 | 28.547 | 29.6383 | -0.331 | 0
8665 | -10.1731 | 41.8607 | 43.0791 | 0.331 | 0.331
8675 | -5.7101 | 19.1908 | 20.0223 | -0.331 | 0
8685 | 39.0489 | 35.5406 | 52.8011 | 0.331 | -0.66
8695 | 53.0753 | 53.0862 | 75.0675 | 0.329 | -0.329
8705 | -0.031563 | 43.2673 | 43.2673 | 0 | 0.658
8715 | -3.0439 | 53.2701 | 53.357 | 0.329 | 0
8725 | -34.8987 | 44.4645 | 56.5244 | 0 | 0.66
8735 | -63.1087 | 16.0907 | 65.1277 | -0.329 | 0.658
8745 | -42.0689 | 53.5159 | 68.0716 | 0.659 | 0
8755 | -23.9527 | 48.4893 | 54.0827 | 0 | 0
8765 | 4.0261 | 17.5712 | 18.0266 | -0.33 | -0.329
8775 | -33.3642 | 35.0518 | 48.3922 | 0.33 | 0.659
8785 | -28.4915 | 52.8465 | 60.0376 | 0.329 | 0
8795 | -17.1256 | 4.7214 | 17.7645 | -0.659 | 0
8805 | 65.0263 | 41.9596 | 77.3888 | 0.659 | -1.317
8815 | 110.0175 | 60.6304 | 125.618 | 0.329 | -0.989
8825 | 75.7808 | 47.022 | 89.1841 | 0 | 0
8835 | 66.9555 | 94.0521 | 115.4505 | 0.989 | -0.33
8845 | 49.349 | 57.4108 | 75.7055 | -0.329 | 0
8855 | 73.8187 | 58.7755 | 94.3597 | 0.329 | -0.658
8865 | 77.5446 | 69.3504 | 104.0319 | 0.329 | -0.33
8875 | 37.4133 | 74.8393 | 83.6701 | 0.329 | 0.33
8885 | 45.773 | 59.3383 | 74.9413 | 0 | -0.33
8895 | 1.3084 | 46.8615 | 46.8798 | 0 | 0.659
8905 | 0.73883 | 59.2378 | 59.2424 | 0.331 | 0
8915 | -11.0186 | 69.9677 | 70.83 | 0.329 | 0.329
8925 | -4.6665 | 56.7408 | 56.9324 | 0 | 0
8935 | 40.6422 | 64.6798 | 76.3889 | 0.329 | -0.658
8945 | 54.9593 | 16.1293 | 57.2773 | -0.658 | -0.33
8955 | 40.2734 | 13.8738 | 42.5961 | 0 | 0
8965 | 48.5525 | 20.3563 | 52.6472 | 0 | -0.33
8975 | 38.9847 | 22.1466 | 44.8362 | 0 | 0
8985 | 10.239 | 41.7302 | 42.968 | 0.329 | 0.33
8995 | 28.4005 | 37.5971 | 47.1183 | 0 | -0.33
9005 | 27.3656 | 50.2629 | 57.2297 | 0.329 | 0
9015 | 79.445 | 62.2327 | 100.9178 | 0.33 | -0.987
9025 | 103.2849 | 69.2305 | 124.3408 | 0.329 | -0.66
9035 | 56.0386 | 74.0397 | 92.8558 | 0.329 | 0.33
9045 | 95.822 | 58.449 | 112.2414 | 0 | -0.989
9055 | 117.1663 | 65.311 | 134.1397 | 0.33 | -0.658
9065 | 144.6473 | 54.5626 | 154.596 | 0 | -0.989
9075 | 109.3398 | 63.3655 | 126.374 | 0.33 | 0
9085 | 78.6094 | 91.973 | 120.9896 | 0.658 | 0
9095 | 100.9176 | 54.974 | 114.9196 | -0.329 | -0.658
9105 | 102.3918 | 41.2408 | 110.3851 | 0 | -0.33
9115 | 60.4169 | 38.1188 | 71.437 | 0 | 0.33
9125 | 86.5029 | 35.1528 | 93.3728 | 0 | -0.66
9135 | 75.238 | 51.9712 | 91.4426 | 0.329 | 0
9145 | 40.3148 | 7.7153 | 41.0464 | -0.658 | 0.33
9155 | 16.5232 | 7.9124 | 18.32 | 0 | 0.33
9165 | 40.2467 | 15.9113 | 43.2778 | 0 | -0.33
9175 | 60.4173 | -0.55176 | 60.4198 | -0.33 | -0.33
9185 | 70.8353 | 4.4848 | 70.9772 | 0 | -0.329
9195 | 77.312 | 10.8897 | 78.0751 | 0 | -0.33
9205 | 120.0317 | -5.6486 | 120.1645 | -0.33 | -0.987
9215 | 134.6028 | -0.40128 | 134.6034 | 0 | -0.66
9225 | 120.9217 | 44.7803 | 128.9471 | 0.66 | -0.329
9235 | 130.4905 | 1.3598 | 130.4976 | -0.66 | -0.659
9245 | 103.1175 | 17.8787 | 104.6559 | 0.33 | 0
9255 | 99.0135 | 2.12 | 99.0362 | -0.33 | -0.33
9265 | 101.3914 | 2.8457 | 101.4313 | 0 | -0.329
9275 | 102.3367 | 7.5508 | 102.6149 | 0 | -0.33
9285 | 102.9404 | -9.7162 | 103.3979 | -0.329 | -0.329
9295 | 103.4618 | -4.8311 | 103.5745 | 0 | -0.329
9305 | 103.9725 | -36.7318 | 110.2702 | -0.659 | -0.329
9315 | 85.2904 | -45.0437 | 96.4541 | -0.329 | 0
9325 | 32.1695 | -65.8117 | 73.2533 | -0.66 | 0.658
9335 | 50.5867 | -64.5305 | 81.9951 | -0.329 | -0.329
9345 | 91.4102 | -41.9607 | 100.5809 | 0 | -0.66
9355 | 59.3273 | -26.5335 | 64.9905 | 0 | 0.331
9365 | 28.8556 | -18.2564 | 34.1459 | 0 | 0.329
9375 | 30.9223 | 5.9806 | 31.4954 | 0.329 | 0
9385 | 34.6189 | 5.3332 | 35.0273 | 0 | 0
9395 | -3.1363 | -17.6632 | 17.9395 | -0.329 | 0.658
9405 | 4.3973 | -14.8558 | 15.4929 | 0 | 0
9415 | -3.4527 | 10.087 | 10.6616 | 0.329 | 0.33
9425 | -33.3092 | 28.2264 | 43.6604 | 0.331 | 0.659
9435 | -36.3754 | 0.56242 | 36.3797 | -0.331 | 0.329
9445 | -35.8062 | 16.0854 | 39.2533 | 0.331 | 0.33
9455 | -56.7579 | 14.7073 | 58.6324 | 0 | 0.658
9465 | -36.0035 | 9.4939 | 37.2342 | 0 | 0
9475 | -17.2508 | 7.1807 | 18.6856 | 0 | 0
9485 | -7.8952 | 25.1121 | 26.3239 | 0.329 | 0
9495 | -21.7891 | 58.8701 | 62.773 | 0.659 | 0.331
9505 | -14.4823 | 63.6268 | 65.2542 | 0.329 | 0
9515 | -25.4067 | 44.4374 | 51.1877 | 0 | 0.329
9525 | -17.2386 | 69.4861 | 71.5925 | 0.659 | 0
9535 | 10.571 | 35.3542 | 36.9007 | -0.33 | -0.329
9545 | 49.5351 | 42.1965 | 65.0713 | 0.33 | -0.66
9555 | 57.3894 | 16.8179 | 59.8029 | -0.33 | -0.329
9565 | 59.4387 | 50.9826 | 78.3082 | 0.66 | -0.33
9575 | 43.4417 | 63.8803 | 77.252 | 0.329 | 0
9585 | 69.7529 | 66.8461 | 96.6119 | 0.329 | -0.659
9595 | 74.7597 | 50.8201 | 90.3974 | 0 | -0.329
9605 | 74.1291 | 38.3285 | 83.4518 | 0 | -0.33
9615 | 75.2913 | 12.3809 | 76.3025 | -0.329 | -0.329
9625 | 96.0605 | 31.2726 | 101.0227 | 0.329 | -0.658
9635 | 74.6184 | 49.7675 | 89.6923 | 0.33 | 0
9645 | 16.5977 | 40.4145 | 43.69 | 0 | 0.658
9655 | 14.1767 | 50.6895 | 52.6346 | 0.329 | 0
9665 | 0.76255 | 61.334 | 61.3387 | 0.33 | 0.329
9675 | 5.9666 | 29.1103 | 29.7155 | -0.33 | 0
9685 | 31.2679 | 22.1543 | 38.321 | 0 | -0.329
9695 | 29.6757 | 22.3937 | 37.1769 | 0 | 0
9705 | 43.7499 | 21.4729 | 48.7354 | 0 | -0.329
9715 | 37.3363 | 39.726 | 54.5175 | 0.33 | 0
9725 | 10.487 | -3.6007 | 11.088 | -0.659 | 0.329
9735 | -27.9341 | -2.6392 | 28.0585 | 0 | 0.659
9745 | 2.8297 | -32.4471 | 32.5703 | -0.659 | -0.33
9755 | -26.3281 | -2.0416 | 26.4071 | 0.329 | 0.659
9765 | -18.6935 | -11.4644 | 21.9289 | -0.329 | 0
9775 | -25.5051 | -45.7673 | 52.3942 | -0.659 | 0.33
9785 | -15.8671 | -31.1585 | 34.966 | 0 | 0
9795 | 31.7804 | 3.4583 | 31.968 | 0.33 | -0.659
9805 | 28.4799 | 6.8528 | 29.2927 | 0 | 0
9815 | -0.22603 | 4.9319 | 4.937 | 0 | 0.329
9825 | -0.20615 | 23.893 | 23.8939 | 0.329 | 0
9835 | 42.2464 | 39.2274 | 57.6502 | 0.329 | -0.659
9845 | 93.4815 | 48.6067 | 105.3632 | 0.33 | -0.987
9855 | 108.7476 | 35.9412 | 114.533 | 0 | -0.66
9865 | 38.9471 | 44.8216 | 59.3789 | 0.329 | 0.66
9875 | 23.4317 | 16.482 | 28.6479 | -0.329 | 0
9885 | 4.3887 | 30.4632 | 30.7777 | 0.329 | 0.329
9895 | 6.7041 | 8.6581 | 10.9503 | -0.329 | 0
9905 | 30.4355 | -12.8566 | 33.0396 | -0.33 | -0.329
9915 | 27.9645 | 13.2747 | 30.9553 | 0.33 | 0
9925 | 60.8507 | -3.0304 | 60.9261 | -0.33 | -0.66
9935 | 31.0025 | 74.6966 | 80.8748 | 1.318 | 0.329
9945 | 59.4103 | 44.5371 | 74.2505 | -0.329 | -0.658
9955 | 50.8179 | 45.3539 | 68.1134 | 0.329 | 0
9965 | 56.6403 | 37.4046 | 67.8766 | 0 | -0.33
9975 | 103.6613 | 28.4221 | 107.4871 | 0 | -0.988
9985 | 120.1211 | 42.9272 | 127.561 | 0.33 | -0.659
9995 | 107.6775 | 93.6464 | 142.7028 | 0.988 | -0.329
10005 | 98.9171 | 16.073 | 100.2145 | -0.988 | -0.329
10015 | 57.0426 | 5.4337 | 57.3008 | 0 | 0.329
10025 | 25.1616 | 12.6897 | 28.1804 | 0 | 0.329
10035 | 6.4702 | -23.9181 | 24.7778 | -0.659 | 0.329
10045 | 13.0645 | 22.8843 | 26.3509 | 0.659 | 0
10055 | 76.6955 | 27.1002 | 81.3426 | 0 | -0.987
10065 | 124.6016 | 39.4043 | 130.6839 | 0.329 | -0.989
10075 | 114.3674 | 32.6586 | 118.939 | 0 | -0.33
10085 | 122.1526 | 5.7954 | 122.29 | -0.329 | -0.658
10095 | 114.057 | 5.9164 | 114.2104 | 0 | -0.33
10105 | 125.572 | -9.573 | 125.9364 | -0.33 | -0.659
10115 | 137.5516 | 14.8569 | 138.3517 | 0.33 | -0.658
10125 | 145.3848 | 36.6242 | 149.9269 | 0.329 | -0.66
10135 | 132.0346 | 10.2687 | 132.4333 | -0.329 | -0.329
10145 | 121.6139 | 6.839 | 121.8061 | 0 | -0.33
10155 | 116.5463 | 47.7671 | 125.9553 | 0.658 | -0.329
10165 | 113.7905 | 21.3871 | 115.7829 | -0.329 | -0.329
10175 | 227.6438 | 51.8154 | 233.4664 | 0.659 | -2.307
10185 | 376.0554 | 5.9947 | 376.1032 | -0.659 | -3.294
10195 | 438.1239 | -75.5997 | 444.5985 | -1.318 | -2.636
10205 | 531.0425 | -92.1238 | 538.9739 | -0.659 | -3.624
10215 | 414.5498 | -38.6434 | 416.347 | 0.33 | -0.329
10225 | 295.3699 | 0.67974 | 295.3706 | 0.329 | 0
10235 | 229.2421 | 79.5991 | 242.6684 | 1.318 | 0
10245 | 247.4374 | -14.9647 | 247.8895 | -1.318 | -0.988
10255 | 286.6305 | -177.2217 | 336.9934 | -2.635 | -1.318
10265 | 234.4697 | -266.5837 | 355.0253 | -2.306 | 0
10275 | 92.3082 | -165.7965 | 189.7611 | 0.329 | 1.647
10285 | 85.8727 | -25.2527 | 89.5088 | 1.318 | 0
10295 | 233.3592 | 5.6031 | 233.4265 | 0.329 | -2.306
10305 | 591.3246 | -82.7836 | 597.0912 | -1.318 | -6.589
10315 | 1082.7983 | -207.8858 | 1102.5737 | -2.306 | -10.543
10325 | 1369.4655 | -388.1192 | 1423.4017 | -3.953 | -9.554
10335 | 1201.6215 | -75.7079 | 1204.0042 | 3.624 | -3.624
10345 | 486.2359 | 152.969 | 509.7302 | 2.964 | 6.26
10355 | -47.3473 | 156.9724 | 163.9576 | 0.989 | 6.589
10365 | -16.2154 | -122.965 | 124.0295 | -3.624 | 0.659
10375 | 279.7049 | -429.086 | 512.2007 | -5.271 | -3.295
10385 | 514.8415 | -492.2414 | 712.2944 | -2.965 | -3.953
10395 | 596.0754 | -301.396 | 667.9412 | 0.659 | -2.965
10405 | 753.1828 | -122.4282 | 763.0682 | 1.318 | -4.943
10415 | 820.6514 | 79.1531 | 824.4598 | 2.965 | -3.953
10425 | 798.8838 | 47.4993 | 800.2947 | 0 | -2.964
10435 | 805.1834 | -172.6069 | 823.4765 | -2.965 | -3.295
10445 | 898.4228 | -308.9184 | 950.0495 | -2.636 | -4.613
10455 | 628.7665 | -115.4073 | 639.27 | 1.976 | 1.318
10465 | 366.7078 | -11.2907 | 366.8816 | 0.989 | 1.977
10475 | 191.0864 | -178.522 | 261.5036 | -2.636 | 2.306
10485 | 170.7679 | -237.8511 | 292.8051 | -1.317 | 0.659
10495 | 146.7314 | -254.2764 | 293.5756 | -1.318 | 0.988
10505 | 193.0059 | -173.4966 | 259.5233 | 0.329 | -0.329
10515 | 381.8751 | -71.2561 | 388.4662 | 0.989 | -2.965
10525 | 537.2288 | 13.7702 | 537.4053 | 1.317 | -3.294
10535 | 496.8959 | 31.8796 | 497.9175 | 0.66 | -0.989
10545 | 355.526 | -95.1377 | 368.0353 | -1.648 | 0.659
10555 | 163.0005 | -134.5309 | 211.3474 | -0.659 | 2.306
10565 | 10.5854 | -162.7581 | 163.102 | -0.988 | 2.635
10575 | 6.8181 | -225.0426 | 225.1459 | -1.647 | 0.989
10585 | 128.7754 | -175.4557 | 217.6415 | 0 | -0.989
10595 | 309.2774 | -90.9306 | 322.3676 | 0.658 | -2.635
10605 | 468.3588 | -151.8651 | 492.3647 | -1.317 | -3.295
10615 | 763.4744 | -172.1169 | 782.6349 | -0.66 | -6.588
10625 | 1156.6747 | -212.4035 | 1176.0151 | -1.317 | -9.555
10635 | 1915.0535 | -303.8742 | 1939.0125 | -2.307 | -17.79
10645 | 1923.6132 | 51.7925 | 1924.3103 | 4.943 | -8.236
10655 | 789.8795 | 306.119 | 847.1237 | 4.282 | 9.883
10665 | 240.1934 | 215.6059 | 322.7674 | 0.33 | 4.942
10675 | 85.587 | -119.6058 | 147.0737 | -3.954 | 3.294
10685 | -191.3725 | -354.8247 | 403.1426 | -3.953 | 6.261
10695 | -319.8694 | -396.4859 | 509.4285 | -2.306 | 4.611
10705 | 121.212 | -86.1479 | 148.7071 | 3.295 | -4.282
10715 | 538.8902 | 113.0726 | 550.6252 | 2.635 | -5.601
10725 | 650.6341 | 256.3523 | 699.3148 | 3.295 | -3.295
10735 | 620.863 | 147.0495 | 638.0395 | -0.33 | -1.976
10745 | 486.8007 | -46.1747 | 488.9857 | -1.976 | 0
10755 | 104.592 | -112.2889 | 153.4545 | -0.989 | 4.942
10765 | -388.0951 | -158.9382 | 419.3795 | -1.317 | 8.565
10775 | -477.7323 | -234.3658 | 532.1236 | -1.978 | 4.283
10785 | -404.0238 | -175.298 | 440.4141 | 0 | 2.636
10795 | -177.191 | -121.496 | 214.8439 | 0 | -0.659
10805 | 17.1131 | -152.3811 | 153.339 | -0.988 | -1.318
10815 | 111.5715 | -143.9428 | 182.1201 | -0.329 | -0.989
10825 | 145.5211 | -111.5793 | 183.3748 | 0 | -0.658
10835 | 70.1473 | -70.9544 | 99.7756 | 0.329 | 0.988
10845 | -105.3879 | -62.3085 | 122.4294 | 0 | 2.965
10855 | -192.2803 | -60.0065 | 201.4261 | 0 | 2.306
10865 | -201.0168 | -152.8393 | 252.5224 | -1.647 | 1.647
10875 | -226.6032 | -130.0711 | 261.2805 | 0 | 1.977
10885 | -214.8487 | -96.9377 | 235.7051 | 0 | 1.318
10895 | -148.0931 | -42.2488 | 154.0017 | 0.658 | 0.329
10905 | -64.1102 | -20.88 | 67.4247 | 0.331 | -0.329
10915 | -105.9617 | 27.3508 | 109.4347 | 0.988 | 1.318
10925 | 61.2057 | 47.1269 | 77.2469 | 0.658 | -2.307
10935 | 108.1404 | -19.5027 | 109.885 | -0.658 | -0.658
10945 | 77.0654 | -13.3041 | 78.2053 | 0.329 | 0
10955 | 134.5384 | 4.2674 | 134.6061 | 0.329 | -1.318
10965 | 33.6244 | 71.4663 | 78.9812 | 1.318 | 1.318
10975 | -55.7793 | 104.7677 | 118.6912 | 0.989 | 1.318
10985 | -144.0774 | 64.5948 | 157.8949 | 0 | 1.977
10995 | -265.0769 | -5.3418 | 265.1307 | -0.66 | 2.964
11005 | -372.246 | 6.2585 | 372.2986 | 0.331 | 3.295
11015 | -427.0256 | -52.1754 | 430.2013 | -0.989 | 2.965
11025 | -464.8153 | -65.561 | 469.4161 | -0.329 | 2.965
11035 | -401.0043 | -85.0555 | 409.9255 | -0.66 | 1.318
11045 | -294.7769 | -45.4838 | 298.2653 | 0.33 | 0.329
11055 | -208.3493 | -11.8673 | 208.687 | 0.33 | 0
11065 | -78.7317 | -12.824 | 79.7693 | 0 | -1.317
11075 | -62.0118 | -16.3653 | 64.1349 | 0 | 0
11085 | 12.3611 | 21.0907 | 24.4462 | 0.658 | -1.318
11095 | 135.5066 | 70.7262 | 152.8536 | 0.989 | -2.306
11105 | 88.9016 | 27.658 | 93.1046 | -0.329 | 0
11115 | 213.3497 | -11.2652 | 213.6469 | -0.331 | -2.965
11125 | 387.5235 | 45.3358 | 390.1664 | 0.989 | -3.954
11135 | 313.2719 | 74.5738 | 322.0257 | 0.659 | -0.658
11145 | 221.2456 | 183.5019 | 287.4414 | 2.306 | -0.331
11155 | 231.8465 | 154.7136 | 278.7276 | 0.33 | -1.317
11165 | 214.2974 | 136.352 | 253.9985 | 0.659 | -0.659
11175 | 197.1033 | 77.6356 | 211.8419 | -0.33 | -0.659
11185 | 35.7788 | 109.5498 | 115.2444 | 0.988 | 1.977
11195 | -108.9084 | 106.6968 | 152.4639 | 0.33 | 2.306
11205 | -198.6831 | 134.6603 | 240.0174 | 0.988 | 2.306
11215 | -239.6549 | 83.8734 | 253.9079 | -0.329 | 1.977
11225 | -210.8787 | 19.7401 | 211.8006 | -0.659 | 0.988
11235 | -55.8776 | -39.6746 | 68.5301 | -0.988 | -1.318
11245 | -20.2244 | -80.4416 | 82.9451 | -0.989 | 0
11255 | -74.7236 | -11.4827 | 75.6007 | 0.659 | 0.989
11265 | -172.7031 | -12.7414 | 173.1724 | -0.329 | 1.977
11275 | -222.3285 | -47.5997 | 227.3669 | -0.66 | 1.647
11285 | -154.243 | -90.4295 | 178.7971 | -0.987 | 0
11295 | -42.0658 | -101.6983 | 110.0549 | -0.66 | -0.989
11305 | -25.6761 | -106.6656 | 109.7124 | -0.658 | 0
11315 | -46.0282 | -112.6682 | 121.7075 | -0.659 | 0.329
11325 | -77.6961 | -99.1909 | 125.9981 | -0.329 | 0.66
11335 | -41.3464 | -70.0816 | 81.3692 | 0 | -0.329
11345 | 30.2735 | -89.1262 | 94.1274 | -0.66 | -0.989
11355 | 22.0167 | -108.6596 | 110.8677 | -0.658 | 0
11365 | 103.3992 | -100.9231 | 144.4882 | -0.33 | -1.648
11375 | 135.7985 | -113.022 | 176.6783 | -0.659 | -0.987
11385 | 129.7853 | -106.2263 | 167.7148 | -0.329 | -0.66
11395 | 69.693 | -60.6388 | 92.3806 | 0.329 | 0.33
11405 | -31.5752 | -103.9472 | 108.637 | -0.988 | 1.317
11415 | -43.6807 | -106.8834 | 115.4646 | -0.329 | 0.33
11425 | -78.956 | -99.931 | 127.3588 | -0.331 | 0.989
11435 | -72.9359 | -39.8077 | 83.0921 | 0.66 | 0.329
11445 | -159.6264 | -31.5468 | 162.7138 | 0 | 1.977
11455 | -117.9288 | 4.0557 | 117.9985 | 0.659 | 0
11465 | -90.9687 | 73.6633 | 117.0537 | 1.318 | 0.329
11475 | -64.5011 | 46.9928 | 79.8042 | 0 | 0
11485 | -83.6904 | -0.73042 | 83.6936 | -0.33 | 0.659
11495 | -103.0656 | 9.6385 | 103.5153 | 0.33 | 0.659
11505 | -133.4167 | 43.3337 | 140.2776 | 0.658 | 0.989
11515 | -117.9574 | -10.1018 | 118.3892 | -0.658 | 0.329
11525 | -64.1504 | -75.5319 | 99.0977 | -0.989 | -0.329
11535 | 69.5455 | -20.5648 | 72.5223 | 0.659 | -1.977
11545 | 187.2487 | 48.7686 | 193.4954 | 0.988 | -2.307
11555 | 244.0473 | 110.545 | 267.9166 | 1.318 | -1.977
11565 | 299.8719 | 56.7242 | 305.1898 | -0.329 | -2.305
11575 | 498.6954 | 85.5727 | 505.9839 | 0.988 | -4.943
11585 | 846.7184 | 217.9226 | 874.3125 | 2.636 | -8.235
11595 | 1753.6538 | 85.088 | 1755.7168 | -1.318 | -19.438
11605 | 2900.2748 | -229.1254 | 2909.3113 | -4.613 | -27.345
11615 | 3183.0329 | -428.8166 | 3211.788 | -4.283 | -18.449
11625 | 2307.1492 | -182.9226 | 2314.3893 | 1.977 | -1.318
11635 | 1184.5721 | -362.1498 | 1238.6943 | -4.612 | 6.919
11645 | 356.1357 | -461.8098 | 583.1817 | -2.965 | 8.895
11655 | 549.1581 | -442.0608 | 704.9769 | -1.977 | -3.295
11665 | 1042.1322 | -449.416 | 1134.9072 | -2.306 | -7.906
11675 | 2062.1145 | -965.7786 | 2277.0693 | -10.872 | -20.097
11685 | 2017.9027 | -1416.4623 | 2465.4202 | -11.531 | -6.589
11695 | 1677.9506 | -1085.1269 | 1998.2539 | -0.988 | -3.624
11705 | 1661.0562 | -448.988 | 1720.6679 | 4.942 | -6.589
11715 | 1854.6224 | -243.2762 | 1870.51 | 1.318 | -9.225
11725 | 2080.4562 | -721.3758 | 2201.9721 | -8.237 | -10.543
11735 | 2085.1268 | -772.3107 | 2223.5596 | -2.635 | -7.906
11745 | 1919.8576 | -863.3624 | 2105.0529 | -4.942 | -5.272
11755 | 1464.3789 | -575.75 | 1573.4972 | 1.647 | 0.66
11765 | 1424.6934 | -103.2242 | 1428.428 | 5.601 | -4.284
11775 | 1306.6401 | 23.4354 | 1306.8502 | 2.306 | -1.646
11785 | 1096.3792 | -26.1145 | 1096.6902 | 0.659 | 0
11795 | 987.1751 | -34.637 | 987.7826 | 0.988 | -0.66
11805 | 921.1049 | -99.5631 | 926.4702 | -0.329 | -0.658
11815 | 542.4487 | -204.1139 | 579.5801 | -1.318 | 4.942
11825 | 337.2638 | -118.1647 | 357.3651 | 1.318 | 3.294
11835 | 376.5883 | 22.8855 | 377.283 | 2.306 | 0.659
11845 | 483.1239 | -209.3442 | 526.5299 | -3.294 | -0.659
11855 | 1021.9893 | -464.9516 | 1122.7832 | -4.284 | -8.895
11865 | 1292.3929 | -333.0328 | 1334.6124 | 0.66 | -6.589
11875 | 654.1714 | 26.2747 | 654.6988 | 4.612 | 6.589
11885 | -52.9246 | 160.4135 | 168.9187 | 2.635 | 9.884
11895 | 287.395 | -10.1522 | 287.5743 | -1.317 | -3.625
11905 | 718.7669 | -46.945 | 720.2983 | 0.329 | -5.271
11915 | 787.9479 | -135.8076 | 799.5658 | -1.318 | -2.306
11925 | 506.8442 | -35.5795 | 508.0914 | 1.647 | 2.635
11935 | 310.6893 | -36.3927 | 312.8134 | 0 | 2.306
11945 | 180.5423 | -0.4065 | 180.5427 | 0.989 | 2.636
11955 | 68.4155 | 113.8805 | 132.8512 | 2.306 | 2.965
11965 | 61.9089 | -31.8028 | 69.5998 | -1.647 | 1.647
11975 | 117.3784 | -122.1116 | 169.3781 | -0.989 | 0.66
11985 | 186.8735 | -84.8998 | 205.2551 | 0.33 | 0
11995 | 303.5788 | 64.566 | 310.3689 | 2.306 | -1.318
12005 | 421.4451 | 39.3202 | 423.2754 | 0 | -1.977
12015 | 765.9028 | -174.0937 | 785.4398 | -2.965 | -6.589
12025 | 1871.8492 | -329.2145 | 1900.5792 | -2.965 | -21.085
12035 | 2242.649 | 59.2661 | 2243.432 | 5.272 | -13.178
12045 | 1950.722 | 512.5937 | 2016.9453 | 7.577 | -5.601
12055 | 881.2151 | 648.6057 | 1094.1798 | 4.941 | 9.225
12065 | 321.9592 | 675.6871 | 748.4723 | 4.284 | 5.601
12075 | 175.815 | 515.0306 | 544.2127 | 0.987 | 3.294
12085 | 25.8521 | 186.6264 | 188.4084 | -2.635 | 4.283
12095 | -218.4318 | 19.0428 | 219.2603 | -1.647 | 6.259
12105 | -619.3553 | 9.1454 | 619.4228 | -0.329 | 9.885
12115 | -594.8138 | 182.0932 | 622.0622 | 2.635 | 4.282
12125 | 92.8949 | 465.2827 | 474.4655 | 5.271 | -6.589
12135 | 1114.4634 | 392.2683 | 1181.4834 | 0.659 | -15.484
12145 | 1695.461 | 147.6032 | 1701.8739 | -1.977 | -13.508
12155 | 1863.8566 | -284.6616 | 1885.4691 | -6.588 | -10.542
12165 | 994.9817 | -306.1177 | 1041.0075 | -1.648 | 6.26
12175 | 113.358 | -135.5133 | 176.6745 | 0.659 | 9.883
12185 | -99.5342 | 107.1413 | 146.2406 | 2.965 | 4.283
12195 | -85.4659 | 58.8762 | 103.7826 | -0.659 | 2.636
12205 | -151.0039 | 65.6983 | 164.6768 | 0.659 | 3.624
12215 | -300.5389 | 226.9037 | 376.5753 | 2.965 | 4.941
12225 | -688.9673 | 156.8941 | 706.6057 | -0.33 | 9.554
12235 | -739.5 | 117.6022 | 748.7927 | 0.33 | 5.271
12245 | -566.0764 | 128.3738 | 580.4501 | 0.659 | 2.306
12255 | -246.3099 | 3.7647 | 246.3387 | -1.647 | -1.317
12265 | 237.3673 | 133.5684 | 272.3669 | 2.306 | -5.93
12275 | 726.0202 | 103.4158 | 733.3485 | -0.329 | -8.566
12285 | 650.094 | 108.0655 | 659.0147 | 0.658 | -1.647
12295 | 352.7987 | -7.8216 | 352.8854 | -1.647 | 1.647
12305 | 356.2301 | -65.9815 | 362.2892 | -0.988 | -1.647
12315 | 519.6367 | -400.1647 | 655.8613 | -6.26 | -3.624
12325 | 521.2189 | -607.8756 | 800.7384 | -5.271 | -1.648
12335 | 502.4429 | -514.3029 | 718.9967 | -1.647 | -1.647
12345 | 326.7512 | -608.0455 | 690.2794 | -4.613 | 1.318
12355 | -19.7433 | -406.9821 | 407.4607 | 0.66 | 4.942
12365 | -304.3803 | -213.7699 | 371.9475 | 0.987 | 5.601
12375 | -526.6783 | -336.2954 | 624.8877 | -2.965 | 6.259
12385 | -607.2009 | -279.5908 | 668.4788 | 0 | 4.942
12395 | -717.6781 | -399.1157 | 821.1914 | -3.294 | 5.93
12405 | -835.1531 | -205.6312 | 860.0959 | 1.977 | 6.259
12415 | -983.6116 | -182.3713 | 1000.3755 | -0.66 | 7.248
12425 | -1005.3987 | -319.9212 | 1055.0716 | -2.635 | 5.601
12435 | -690.7808 | -380.1316 | 788.4657 | -1.977 | 0
12445 | -361.7801 | -350.0678 | 503.4206 | -0.988 | -1.647
12455 | -313.5325 | -268.1939 | 412.5901 | 0 | 0.989
12465 | -561.9207 | -96.7621 | 570.191 | 1.976 | 5.271
12475 | -923.2097 | 84.9901 | 927.1135 | 2.966 | 8.236
12485 | -978.5809 | 187.9711 | 996.4706 | 2.635 | 4.942
12495 | -427.0224 | 273.0253 | 506.8441 | 2.965 | -4.613
12505 | -161.1385 | 338.8617 | 375.2237 | 2.966 | -1.976
12515 | -81.2784 | 234.752 | 248.4244 | 0.329 | -1.319
12525 | -140.8666 | 287.2857 | 319.9633 | 2.635 | 0.66
12535 | -378.7801 | 450.8503 | 588.8466 | 4.284 | 3.953
12545 | -510.8853 | 512.1785 | 723.4159 | 3.294 | 3.295
12555 | -618.0344 | 525.5116 | 811.2515 | 2.965 | 3.953
12565 | -485.5963 | 579.865 | 756.338 | 3.624 | 0.33
12575 | -6.9814 | 417.911 | 417.9693 | 0 | -5.93
12585 | 323.5396 | 268.1893 | 420.242 | -0.329 | -5.601
12595 | 500.4812 | 413.8203 | 649.4064 | 3.624 | -5.271
12605 | 545.8508 | 429.4395 | 694.5296 | 1.646 | -3.954
12615 | 483.2062 | 682.1175 | 835.9261 | 6.261 | -2.306
12625 | 331.2854 | 508.1968 | 606.6415 | -0.33 | -0.33
12635 | 309.1901 | 389.9125 | 497.6247 | 0.659 | -1.646
12645 | 319.4916 | 306.1167 | 442.4729 | 0 | -1.648
12655 | 173.6608 | 208.293 | 271.1901 | -0.659 | 0.988
12665 | -93.6858 | 102.0824 | 138.5563 | -1.318 | 3.624
12675 | -241.8284 | -107.0791 | 264.4748 | -3.624 | 2.966
12685 | -134.4108 | -264.0467 | 296.2886 | -3.624 | -0.33
12695 | -43.9224 | -250.0897 | 253.9173 | -1.647 | -0.33
12705 | 0.053112 | 17.3747 | 17.3748 | 2.636 | -0.329
12715 | 64.0005 | -17.5918 | 66.3742 | -1.318 | -0.988
12725 | 168.4856 | -167.5952 | 237.6458 | -2.636 | -1.977
12735 | 186.1757 | -113.5062 | 218.0483 | 0 | -0.988
12745 | 246.6141 | -15.8548 | 247.1232 | 0.659 | -1.977
12755 | 300.1824 | 23.401 | 301.0932 | 0.33 | -1.977
12765 | 201.5464 | -34.8917 | 204.5443 | -0.989 | 0.329
12775 | 6.6515 | -83.129 | 83.3946 | -0.988 | 2.306
12785 | -69.4835 | -149.3887 | 164.7572 | -1.648 | 1.319
12795 | -66.2392 | -352.7235 | 358.8892 | -4.282 | 0.658
12805 | -63.9974 | -373.2019 | 378.6493 | -1.977 | 0.66
12815 | -87.0146 | -383.5844 | 393.3301 | -2.307 | 0.987
12825 | -126.8869 | -347.7454 | 370.1718 | -1.317 | 1.319
12835 | -60.7738 | -225.5443 | 233.5887 | 0.329 | -0.33
12845 | 186.7801 | -178.1138 | 258.0917 | -0.329 | -3.624
12855 | 292.1424 | -102.5203 | 309.6088 | 0.659 | -2.306
12865 | 360.6169 | -24.738 | 361.4644 | 0.989 | -2.636
12875 | 434.912 | -11.7425 | 435.0705 | 0.329 | -2.964
12885 | 472.2085 | -161.6274 | 499.1035 | -2.306 | -2.637
12895 | 402.8941 | -161.6742 | 434.1224 | -0.33 | -0.987
12905 | 312.9268 | -232.8323 | 390.0437 | -1.977 | -0.33
12915 | 220.2967 | -260.5484 | 341.198 | -1.317 | 0.33
12925 | 370.9741 | -155.3478 | 402.1874 | 0.658 | -3.295
12935 | 328.9912 | -131.9529 | 354.4669 | -0.329 | -0.329
12945 | 190.8501 | 79.1951 | 206.6291 | 3.295 | 0.987
12955 | 157.2245 | 95.5996 | 184.0077 | 0.658 | 0
12965 | 90.5821 | 211.0573 | 229.6743 | 2.966 | 0.989
12975 | 35.0616 | 239.5642 | 242.1163 | 1.646 | 0.988
12985 | 153.0372 | 149.9753 | 214.2731 | 0 | -1.647
12995 | 287.5696 | 182.837 | 340.7721 | 1.648 | -2.306
13005 | 409.7097 | 130.9806 | 430.1371 | 0 | -2.965
13015 | 474.0389 | 101.1344 | 484.7072 | 0.329 | -2.636
13025 | 437.6887 | 33.3491 | 438.9574 | -0.659 | -1.317
13035 | 543.2899 | 0.71563 | 543.2903 | -0.329 | -3.624
13045 | 466.8054 | -91.8467 | 475.7553 | -1.647 | -0.66
13055 | 255.7051 | 27.3749 | 257.1662 | 1.647 | 1.648
13065 | 283.9692 | 172.7765 | 332.4007 | 2.306 | -1.318
13075 | 315.896 | 224.026 | 387.2699 | 1.647 | -0.988
13085 | 228.677 | 116.3019 | 256.5527 | -0.658 | 0.658
13095 | 215.422 | 185.7 | 284.4136 | 1.977 | -0.329
13105 | -50.0184 | -45.3446 | 67.5128 | -3.295 | 4.283
13115 | -130.8156 | -341.2936 | 365.5052 | -4.942 | 1.976
13125 | -135.932 | -514.1922 | 531.8563 | -4.612 | 1.648
13135 | 4.9175 | -412.0664 | 412.0957 | -0.989 | -0.988
13145 | 187.4428 | -382.6644 | 426.1066 | -1.977 | -2.306
13155 | 439.9098 | -121.803 | 456.461 | 2.637 | -4.613
13165 | 503.4657 | 159.417 | 528.1018 | 3.953 | -2.635
13175 | 660.016 | 914.9494 | 1128.1638 | 13.836 | -4.942
13185 | 1138.95 | 1584.5817 | 1951.437 | 15.485 | -10.872
13195 | 714.0463 | 1442.4233 | 1609.4866 | 5.601 | 2.636
13205 | 742.3721 | 805.0679 | 1095.103 | -2.636 | -4.613
13215 | 120.6523 | 568.3304 | 580.996 | 0.658 | 8.237
13225 | -422.6553 | 848.3016 | 947.7622 | 6.919 | 8.565
13235 | -668.132 | 1079.3384 | 1269.3982 | 6.919 | 7.248
13245 | -825.573 | 829.7519 | 1170.4953 | 0.329 | 7.248
13255 | -873.3207 | 99.6739 | 878.9903 | -8.566 | 5.93
13265 | -529.1292 | -39.4939 | 530.6011 | -1.977 | -0.658
13275 | 112.261 | 372.1281 | 388.6925 | 5.272 | -7.248
13285 | 399.5577 | 326.9642 | 516.2867 | -0.659 | -4.613
13295 | 581.679 | 237.9697 | 628.4744 | -0.329 | -5.271
13305 | 662.8181 | 215.4851 | 696.966 | 0 | -4.283
13315 | 564.4991 | 221.1085 | 606.2575 | 0.329 | -1.648
13325 | 493.6699 | 204.6642 | 534.4131 | 0 | -1.647
13335 | 580.6652 | 14.6848 | 580.8509 | -2.965 | -3.623
13345 | 661.0536 | 345.2701 | 745.7904 | 5.271 | -3.624
13355 | 155.8587 | 538.1077 | 560.2248 | 3.624 | 5.93
13365 | 2.5583 | 394.4191 | 394.4274 | -0.329 | 1.647
13375 | 24.926 | 177.9756 | 179.7126 | -1.977 | 0.659
13385 | -44.4543 | 77.0807 | 88.981 | -1.318 | 1.976
13395 | -91.297 | 310.5448 | 323.6869 | 3.624 | 1.648
13405 | 52.0139 | 537.1858 | 539.6981 | 4.283 | -1.318
13415 | 260.1268 | 462.4757 | 530.6126 | 0.659 | -2.965
13425 | 301.1861 | 267.9778 | 403.1441 | -1.318 | -1.318
13435 | 539.7846 | 600.5153 | 807.4566 | 6.59 | -5.271
13445 | 946.9929 | 1121.2985 | 1467.6872 | 10.542 | -8.896
13455 | 1159.8897 | 1261.8355 | 1713.9349 | 6.918 | -7.577
13465 | 1306.1938 | 820.158 | 1542.3363 | -1.647 | -7.907
13475 | 1556.8869 | 1023.6902 | 1863.287 | 7.577 | -10.212
13485 | 1755.5151 | 1595.921 | 2372.5086 | 13.178 | -10.214
13495 | 1838.4309 | 1574.3857 | 2420.4377 | 5.93 | -9.224
13505 | 1173.054 | 821.5479 | 1432.1301 | -5.6 | 3.294
13515 | -226.5141 | -94.3521 | 245.3792 | -11.86 | 18.45
13525 | -1370.785 | -720.4968 | 1548.6017 | -12.19 | 21.084
13535 | -1640.7986 | -1139.839 | 1997.8621 | -12.519 | 13.178
13545 | -1504.5958 | -1187.8777 | 1916.993 | -8.237 | 8.567
13555 | -1077.5728 | -502.4383 | 1188.9522 | 3.954 | 2.305
13565 | -146.964 | 387.0431 | 414.0057 | 10.542 | -8.895
13575 | 872.8462 | 331.6451 | 933.7285 | -0.329 | -15.155
13585 | 1144.1462 | -144.4518 | 1153.2289 | -5.93 | -8.236
13595 | 1216.7769 | -328.752 | 1260.4063 | -3.624 | -7.577
13605 | 801.2429 | -677.8286 | 1049.496 | -8.237 | 0.988
13615 | 409.1807 | -570.0581 | 701.7087 | -1.647 | 2.306
13625 | 548.612 | -558.1837 | 782.652 | -3.623 | -3.953
13635 | 740.5913 | -577.7702 | 939.305 | -3.295 | -4.612
13645 | 758.2025 | -631.194 | 986.548 | -3.953 | -2.966
13655 | 698.461 | -545.4008 | 886.177 | -1.648 | -1.976
13665 | 315.5523 | -418.1495 | 523.8533 | -0.659 | 3.953
13675 | -263.6617 | -128.3457 | 293.2407 | 2.965 | 8.895
13685 | -857.2501 | -127.5294 | 866.6842 | -0.658 | 12.19
13695 | -727.2159 | 121.1376 | 737.2363 | 4.282 | 2.965
13705 | -209.3999 | 452.8329 | 498.9048 | 6.26 | -3.295
13715 | -290.1223 | 600.3523 | 666.7787 | 4.942 | 3.955
13725 | -166.2065 | 496.2112 | 523.3069 | 1.647 | -0.66
13735 | 24.6866 | 493.9309 | 494.5474 | 2.965 | -1.647
13745 | -69.2943 | 390.1061 | 396.2127 | 0.659 | 1.976
13755 | -68.9023 | 539.2021 | 543.5866 | 4.612 | 0.331
13765 | -82.5174 | 508.564 | 515.215 | 1.647 | 0.987
13775 | -82.2931 | 477.5472 | 484.5858 | 1.977 | 0.659
13785 | -21.2963 | 146.7756 | 148.3125 | -3.624 | -0.329
13795 | 101.536 | -130.4064 | 165.2736 | -3.953 | -1.648
13805 | 361.8934 | -220.317 | 423.682 | -2.636 | -4.612
13815 | 188.1589 | -136.5649 | 232.4946 | -0.329 | 1.648
13825 | -39.075 | -420.7394 | 422.5499 | -6.26 | 2.635
13835 | 249.5601 | -477.2296 | 538.5428 | -2.965 | -4.612
13845 | 310.3841 | -419.9646 | 522.215 | -1.976 | -1.318
13855 | 13.9992 | -238.5132 | 238.9237 | 0.658 | 3.624
13865 | -324.2923 | -71.6736 | 332.1183 | 1.318 | 5.601
13875 | -218.4782 | 106.8338 | 243.1999 | 2.636 | 0
13885 | 129.4177 | 269.4972 | 298.961 | 3.294 | -3.954
13895 | 539.1297 | 34.0932 | 540.2066 | -2.636 | -6.918
13905 | 643.3309 | 142.4213 | 658.907 | 2.636 | -3.954
13915 | 356.3024 | 624.0189 | 718.5757 | 8.566 | 1.648
13925 | -147.1214 | 1263.7831 | 1272.3177 | 13.508 | 6.588
13935 | -549.7705 | 1191.7269 | 1312.4255 | 4.612 | 7.578
13945 | -652.5919 | 687.5498 | 947.9456 | -1.977 | 4.942
13955 | -454.321 | 195.3813 | 494.5517 | -4.612 | 0.658
13965 | -311.2709 | 135.6976 | 339.5636 | -0.33 | 0.66
13975 | -146.2256 | 65.1049 | 160.0643 | -1.647 | -0.989
13985 | -32.0124 | 278.8299 | 280.6616 | 3.294 | -0.988
13995 | -60.1951 | 244.504 | 251.8048 | -0.329 | 0.659
14005 | 100.8866 | 174.4482 | 201.5199 | -0.329 | -2.636
14015 | 201.4744 | 252.661 | 323.1555 | 1.647 | -1.976
14025 | 43.7582 | 492.6246 | 494.5642 | 4.612 | 1.647
14035 | -237.2103 | 763.2544 | 799.266 | 6.26 | 4.283
14045 | -82.367 | 581.4286 | 587.2338 | 0 | -1.648
14055 | 74.8665 | 489.176 | 494.8718 | 1.317 | -1.647
14065 | 138.7675 | 80.5794 | 160.4663 | -5.271 | -1.318
14075 | 80.5623 | -27.9804 | 85.283 | -1.646 | 0.33
14085 | 109.4579 | 293.9563 | 313.674 | 4.282 | -0.989
14095 | 185.0691 | 402.7316 | 443.2193 | 1.977 | -1.647
14105 | -50.0497 | 220.9606 | 226.558 | -1.648 | 3.295
14115 | -417.1061 | -36.7477 | 418.7218 | -3.624 | 6.259
14125 | -474.1796 | -151.8304 | 497.8943 | -2.635 | 2.965
14135 | -306.5937 | -119.5937 | 329.0932 | -0.989 | 0
14145 | -94.3194 | -324.7417 | 338.1617 | -4.941 | -1.647
14155 | -208.1068 | -580.2213 | 616.4132 | -6.26 | 2.635
14165 | -210.0839 | -523.5283 | 564.1074 | -2.306 | 0.66
14175 | -240.8003 | -517.3354 | 570.6318 | -3.295 | 1.647
14185 | -294.2931 | -447.7364 | 535.795 | -1.647 | 1.977
14195 | -561.7113 | -222.8606 | 604.3066 | 1.318 | 5.93
14205 | -731.6845 | -178.4388 | 753.1286 | -0.659 | 5.271
14215 | -926.7147 | -370.1325 | 997.8969 | -3.953 | 6.918
14225 | -750.6743 | -536.8073 | 922.8619 | -4.283 | 1.318
14235 | -250.0392 | -255.4411 | 357.4489 | 2.305 | -4.612
14245 | -265.2639 | 94.9155 | 281.7337 | 4.284 | 1.647
14255 | -443.8319 | 278.5634 | 524.008 | 3.624 | 3.294
14265 | -573.2109 | -15.3872 | 573.4174 | -3.295 | 3.624
14275 | -307.0817 | -140.1704 | 337.5602 | -1.318 | -2.305
14285 | -334.9812 | -83.0807 | 345.1301 | 0.33 | 1.976
14295 | -253.5257 | -55.0131 | 259.4257 | 0 | -0.658
14305 | -377.7245 | -45.4467 | 380.4487 | 0 | 2.964
14315 | -397.9567 | -134.7773 | 420.1601 | -1.647 | 1.318
14325 | -252.1659 | -110.1184 | 275.1612 | 0 | -0.989
14335 | -104.443 | -75.8792 | 129.0969 | 0 | -1.646
14345 | -163.1317 | -39.6979 | 167.8925 | 0.329 | 0.988
14355 | -434.2458 | 216.5796 | 485.2588 | 4.283 | 4.613
14365 | -457.074 | 550.5726 | 715.5745 | 6.59 | 1.646
14375 | -474.8489 | 471.5755 | 669.2272 | 1.317 | 2.307
14385 | -406.7453 | 69.5946 | 412.6562 | -3.954 | 0.659
14395 | -350.7334 | 38.2214 | 352.8099 | 0.33 | 0.658
14405 | -129.1515 | 246.7497 | 278.5059 | 3.294 | -2.635
14415 | 118.4676 | 10.7267 | 118.9522 | -3.294 | -3.953
14425 | 321.9117 | -418.5964 | 528.0626 | -6.918 | -4.613
14435 | 538.6344 | -671.643 | 860.9479 | -6.26 | -5.93
14445 | 352.6132 | -767.3275 | 844.4688 | -5.272 | 0
14455 | 36.8335 | -603.5411 | 604.664 | -1.317 | 2.636
14465 | -259.121 | -403.708 | 479.7123 | 0 | 4.283
14475 | -279.2872 | -131.4384 | 308.6704 | 2.635 | 1.318
14485 | -110.9604 | -76.8191 | 134.957 | 0.33 | -1.318
14495 | -185.0058 | -318.1787 | 368.0555 | -3.954 | 1.976
14505 | -310.5428 | -424.782 | 526.1906 | -2.635 | 2.635
14515 | -102.0612 | -488.5524 | 499.0992 | -2.965 | -2.306
14525 | 209.4005 | -557.7182 | 595.7333 | -3.295 | -4.611
14535 | 320.0257 | -609.3248 | 688.2537 | -3.294 | -2.966
14545 | 220.5103 | -608.8763 | 647.5764 | -2.636 | -0.329
14555 | 87.8521 | -647.2145 | 653.1498 | -3.295 | 0.658
14565 | -145.8533 | -531.2283 | 550.8872 | -0.658 | 3.295
14575 | -313.1927 | -533.1318 | 618.3197 | -2.306 | 3.295
14585 | -472.8458 | -616.9203 | 777.2862 | -3.295 | 4.283
14595 | -454.6765 | -658.4448 | 800.1752 | -2.965 | 1.976
14605 | -504.9497 | -509.2232 | 717.135 | 0 | 3.295
14615 | -601.0426 | -468.5103 | 762.0723 | -1.318 | 3.953
14625 | -595.5594 | -290.9197 | 662.8162 | 1.648 | 2.635
14635 | -643.3381 | -301.4444 | 710.4594 | -0.989 | 3.624
14645 | -731.526 | -375.121 | 822.0986 | -1.648 | 4.284
14655 | -798.0301 | -360.7776 | 875.7925 | -0.658 | 4.283
14665 | -653.5453 | -358.2006 | 745.2711 | -0.989 | 0.987
14675 | -539.086 | -361.1725 | 648.8908 | -0.988 | 0.989
14685 | -594.9264 | -169.6531 | 618.6434 | 2.306 | 2.966
14695 | -458.5658 | 21.5912 | 459.0739 | 2.966 | -0.331
14705 | -453.3683 | -105.5559 | 465.4942 | -1.318 | 1.648
14715 | -476.0027 | -163.6253 | 503.3406 | -0.33 | 1.647
14725 | -523.537 | -156.2935 | 546.3686 | 0 | 2.306
14735 | -540.0895 | -147.7298 | 559.9292 | 0 | 1.977
14745 | -642.8926 | -7.0473 | 642.9312 | 2.306 | 3.624
14755 | -648.9384 | 86.1091 | 654.6265 | 1.977 | 2.307
14765 | -562.7307 | -109.6028 | 573.305 | -2.306 | 0.988
14775 | -540.6952 | -210.0012 | 580.0447 | -1.318 | 1.647
14785 | -557.3235 | -59.3428 | 560.474 | 1.976 | 1.977
14795 | -397.167 | 141.3059 | 421.5554 | 3.295 | -0.988
14805 | -421.2426 | 196.6888 | 464.8998 | 1.977 | 1.646
14815 | -581.9704 | 259.2172 | 637.0895 | 2.635 | 3.624
14825 | -713.6206 | 391.7436 | 814.0746 | 3.954 | 3.954
14835 | -699.8834 | 493.8601 | 856.5831 | 3.954 | 2.306
14845 | -755.7779 | 409.9427 | 859.7984 | 1.317 | 3.624
14855 | -773.4936 | 379.9403 | 861.7697 | 1.976 | 2.965
14865 | -626.3276 | 323.4981 | 704.9378 | 0.989 | 0.329
14875 | -648.6961 | 244.1848 | 693.1326 | 0.33 | 2.636
14885 | -692.4968 | 328.0006 | 766.2482 | 2.636 | 2.636
14895 | -888.5909 | 386.6823 | 969.0805 | 2.306 | 5.6
14905 | -1080.3102 | 263.7525 | 1112.0411 | -0.33 | 6.261
14915 | -1282.3935 | 88.4036 | 1285.437 | -1.647 | 7.577
14925 | -1217.9685 | -7.6259 | 1217.9924 | -1.318 | 3.953
14935 | -959.6091 | 51.5304 | 960.9916 | 0.658 | 0.659
14945 | -860.8052 | 121.9977 | 869.4073 | 0.989 | 1.976
14955 | -823.3079 | 200.2257 | 847.3053 | 1.648 | 1.977
14965 | -873.8367 | 177.1064 | 891.6038 | 0.329 | 3.295
14975 | -859.2391 | 168.9058 | 875.6832 | 0.658 | 2.306
14985 | -779.8684 | 286.6969 | 830.897 | 2.637 | 1.318
14995 | -646.1029 | 283.9852 | 705.7596 | 0.988 | 0
15005 | -531.6578 | 226.0235 | 577.7081 | 0.329 | -0.329
15015 | -398.5817 | 343.4827 | 526.1632 | 2.965 | -1.319
15025 | -166.3192 | 446.114 | 476.109 | 2.966 | -3.624
15035 | 26.3383 | 546.016 | 546.6509 | 3.624 | -3.953
15045 | 40.9085 | 466.114 | 467.9058 | 0.988 | -1.977
15055 | -90.864 | 434.0232 | 443.4326 | 1.647 | 0.33
15065 | -255.5083 | 411.8412 | 484.6624 | 1.318 | 1.647
15075 | -453.9939 | 223.5724 | 506.0584 | -1.647 | 3.295
15085 | -645.8237 | -74.6428 | 650.1229 | -4.283 | 4.282
15095 | -677.82 | -51.8969 | 679.8038 | -0.33 | 2.636
15105 | -685.4013 | 18.6512 | 685.6551 | 0 | 2.636
15115 | -834.6283 | -46.3583 | 835.9148 | -1.648 | 4.942
15125 | -936.9237 | -13.0962 | 937.0153 | 0 | 4.612
15135 | -826.4799 | 100.0621 | 832.5151 | 1.319 | 1.647
15145 | -698.5117 | 157.7449 | 716.1019 | 0.988 | 0.988
15155 | -585.5684 | 167.7478 | 609.1221 | 0.659 | 0.33
15165 | -511.5974 | 249.4983 | 569.1936 | 1.977 | 0.33
15175 | -368.9767 | 354.3299 | 511.5599 | 2.636 | -1.318
15185 | -298.6953 | 157.0531 | 337.4679 | -1.978 | -0.659
15195 | -163.104 | 48.8374 | 170.2586 | -0.988 | -2.307
15205 | 80.2769 | 1.6391 | 80.2936 | -0.988 | -4.612
15215 | 202.2894 | 102.2239 | 226.6511 | 1.318 | -3.624
15225 | 179.4892 | -65.9513 | 191.2223 | -2.965 | -1.976
15235 | 395.1592 | -200.7613 | 443.2334 | -2.636 | -5.93
15245 | 661.2686 | -295.4832 | 724.2834 | -2.965 | -7.249
15255 | 595.6764 | -307.041 | 670.1526 | -1.977 | -2.965
15265 | 603.3248 | -254.1325 | 654.6634 | -0.988 | -4.283
15275 | 664.5372 | -28.636 | 665.1539 | 2.306 | -4.611
15285 | 696.9259 | 252.734 | 741.3367 | 4.282 | -4.284
15295 | 417.089 | 152.938 | 444.2446 | -0.658 | 0.989
15305 | 28.8205 | 120.5519 | 123.9491 | 0.658 | 3.953
15315 | -73.3546 | -82.1533 | 110.1365 | -2.964 | 1.318
15325 | 160.2362 | -205.8249 | 260.8439 | -2.306 | -3.295
15335 | 204.1191 | -117.1624 | 235.3542 | 0.329 | -0.988
15345 | 100.3067 | -61.2247 | 117.5155 | 0 | 0.659
15355 | 63.4358 | -57.9964 | 85.9516 | -0.329 | 0
15365 | 165.9158 | 93.761 | 190.5759 | 2.306 | -1.976
15375 | 400.7817 | 138.0915 | 423.9047 | 0.988 | -4.613
15385 | 550.738 | -100.3156 | 559.7996 | -3.294 | -4.283
15395 | 448.8835 | -304.6772 | 542.517 | -3.624 | -0.989
15405 | -2.9222 | -408.2346 | 408.245 | -3.295 | 5.272
15415 | -64.1998 | -340.4612 | 346.4614 | -0.989 | 0.659
15425 | 184.2266 | 3.8053 | 184.2659 | 3.955 | -3.295
15435 | 323.909 | 64.0996 | 330.1905 | 0.658 | -2.636
15445 | 452.0105 | 59.9172 | 455.9644 | 0.659 | -3.624
15455 | 507.9835 | 145.5547 | 528.4254 | 1.977 | -2.964
15465 | 502.498 | 81.9313 | 509.1335 | -0.33 | -2.306
15475 | 405.0778 | -17.3444 | 405.4489 | -0.988 | -0.66
15485 | 124.0401 | 94.8437 | 156.1451 | 1.977 | 2.966
15495 | -253.4938 | 99.905 | 272.4704 | 0.329 | 5.93
15505 | -436.9058 | 139.5432 | 458.6491 | 1.318 | 4.612
15515 | -465.9432 | 83.2947 | 473.3298 | -0.33 | 3.294
15525 | -450.0186 | -44.3851 | 452.2021 | -1.647 | 2.637
15535 | -546.0173 | -170.8373 | 572.1191 | -2.306 | 4.282
15545 | -730.6054 | -197.258 | 756.7661 | -1.317 | 5.93
15555 | -792.1835 | -72.41 | 795.486 | 0.988 | 4.613
15565 | -1037.7521 | -55.4288 | 1039.2313 | -0.33 | 8.236
15575 | -1223.3312 | -26.2107 | 1223.6119 | 0.33 | 7.906
15585 | -1075.0628 | 58.6222 | 1076.6599 | 1.318 | 3.295
15595 | -916.7697 | 82.1167 | 920.4401 | 0.658 | 2.635
15605 | -931.2187 | -25.1484 | 931.5582 | -1.318 | 4.284
15615 | -773.84 | 161.2741 | 790.4667 | 3.295 | 0.988
15625 | -318.5688 | 231.86 | 394.0116 | 1.647 | -4.612
15635 | -65.04 | 252.7822 | 261.0155 | 1.648 | -3.295
15645 | 16.8388 | 312.1671 | 312.621 | 2.306 | -2.306
15655 | 92.3056 | 187.8765 | 209.3273 | -0.659 | -2.636
15665 | 138.6994 | 219.1447 | 259.3491 | 1.647 | -2.306
15675 | 137.2881 | 270.2474 | 303.1199 | 1.648 | -1.647
15685 | 102.8056 | 87.7855 | 135.1861 | -1.977 | -0.988
15695 | 315.7047 | 74.8201 | 324.4495 | 0.329 | -4.942
15705 | 476.7161 | 269.6652 | 547.7021 | 3.294 | -4.612
15715 | 305.7534 | 260.6352 | 401.7659 | 0.66 | 0
15725 | 108.0682 | 243.4747 | 266.3807 | 0.988 | 0.988
15735 | 12.1198 | 244.3995 | 244.6999 | 0.988 | 0.658
15745 | 36.8283 | 342.8875 | 344.8596 | 2.636 | -0.658
15755 | 140.369 | 364.7083 | 390.7885 | 1.647 | -1.977
15765 | 195.1585 | 310.6729 | 366.8849 | 0.66 | -1.647
15775 | 109.7037 | 119.0467 | 161.8858 | -1.978 | 0.329
15785 | 21.5697 | 54.7561 | 58.8514 | -0.659 | 0.66
15795 | -68.8742 | 70.0014 | 98.2031 | 0 | 1.317
15805 | -54.6437 | 21.925 | 58.8782 | -0.988 | 0
15815 | -91.4386 | 169.4812 | 192.5744 | 2.306 | 0.988
15825 | -129.2228 | 177.8809 | 219.8639 | 0.33 | 0.988
15835 | 19.8471 | 117.9613 | 119.6193 | -0.33 | -1.976
15845 | 43.826 | -36.2516 | 56.8762 | -2.306 | -0.33
15855 | 113.3851 | -227.5517 | 254.236 | -3.624 | -1.647
15865 | 155.7409 | -205.4562 | 257.8129 | -0.988 | -1.317
15875 | 237.0094 | -169.9105 | 291.6214 | -0.988 | -2.307
15885 | 147.9757 | -217.865 | 263.3666 | -1.977 | 0.33
15895 | 88.1185 | -185.8019 | 205.6385 | -0.659 | 0
15905 | 139.2338 | -78.2113 | 159.6968 | 0.659 | -1.318
15915 | 338.0843 | 130.3216 | 362.3324 | 2.965 | -3.953
15925 | 371.341 | 87.4122 | 381.4906 | -0.33 | -1.977
15935 | 141.1066 | -88.6767 | 166.6572 | -2.306 | 1.977
15945 | 179.7711 | -73.3924 | 194.1754 | 0 | -1.648
15955 | 288.041 | 39.5778 | 290.7473 | 1.318 | -2.305
15965 | 182.0633 | 39.6816 | 186.3375 | 0 | 0.658
15975 | 29.4782 | -33.4529 | 44.5877 | -0.988 | 1.647
15985 | -68.3432 | -65.7572 | 94.8409 | -0.659 | 1.648
15995 | -33.4096 | -138.3675 | 142.3439 | -1.647 | 0
16005 | -115.2328 | -118.799 | 165.5047 | -0.331 | 1.976
16015 | -116.4466 | -94.1107 | 149.7219 | -0.329 | 0.659
16025 | -27.3837 | -45.4166 | 53.0334 | 0.329 | -0.659
16035 | 15.5406 | -106.0069 | 107.1399 | -1.317 | -0.329
16045 | -119.1341 | -161.6992 | 200.8471 | -1.318 | 2.306
16055 | -209.4681 | -193.912 | 285.4448 | -1.318 | 1.977
16065 | -259.0012 | -273.7403 | 376.8493 | -2.306 | 1.976
16075 | -294.859 | -317.0408 | 432.9627 | -1.976 | 1.977
16085 | -207.2259 | -285.1541 | 352.4988 | -0.988 | 0
16095 | -291.8919 | -356.8993 | 461.0618 | -2.636 | 2.635
16105 | -474.2996 | -481.4442 | 675.8318 | -3.624 | 4.284
16115 | -506.3739 | -396.7356 | 643.2835 | -0.659 | 2.635
16125 | -474.73 | -318.4301 | 571.6347 | -0.66 | 1.977
16135 | -593.9549 | -299.401 | 665.1491 | -0.987 | 4.283
16145 | -641.1604 | -254.5372 | 689.8375 | -0.33 | 3.294
16155 | -605.3291 | -219.9455 | 644.0491 | -0.329 | 2.307
16165 | -294.2454 | -218.8509 | 366.7098 | -0.66 | -2.636
16175 | -155.3592 | -278.2557 | 318.689 | -1.647 | -0.988
16185 | -113.9948 | -323.6898 | 343.1762 | -1.647 | -0.66
16195 | -121.7774 | -273.7407 | 299.6059 | -0.33 | 0
16205 | -126.7453 | -269.6262 | 297.9306 | -0.987 | 0
16215 | -162.6281 | -316.0069 | 355.3988 | -1.648 | 0.66
16225 | -246.0002 | -312.3003 | 397.552 | -0.989 | 1.646
16235 | -228.0977 | -283.932 | 364.2059 | -0.658 | 0.331
16245 | -202.0813 | -169.5926 | 263.8153 | 0.989 | 0.329
16255 | -285.3173 | -102.6113 | 303.2079 | 0.658 | 1.977
16265 | -238.3495 | -258.0858 | 351.3101 | -2.636 | 0
16275 | -148.6453 | -345.538 | 376.1541 | -1.977 | -0.659
16285 | -148.4826 | -424.6771 | 449.8864 | -2.635 | 0.329
16295 | -216.0311 | -407.4915 | 461.2145 | -1.318 | 1.317
16305 | -72.1011 | -309.7332 | 318.0145 | 0 | -1.976
16315 | -62.4344 | -261.2213 | 268.5789 | -0.329 | 0
16325 | -157.5807 | -276.6176 | 318.3536 | -0.988 | 1.318
16335 | -223.1729 | -137.8273 | 262.3023 | 1.646 | 1.318
16345 | -221.8189 | -42.1602 | 225.79 | 1.318 | 0.658
16355 | -196.4127 | 11.5641 | 196.7528 | 1.319 | 0.33
16365 | -160.8957 | 31.0356 | 163.8616 | 0.987 | 0
16375 | 16.8805 | -69.6891 | 71.7044 | -0.987 | -2.635
16385 | 38.4323 | -242.5656 | 245.5914 | -2.637 | -0.659
16395 | 11.2869 | -283.2088 | 283.4337 | -1.317 | -0.33
16405 | -57.8851 | -370.59 | 375.0835 | -2.636 | 0.659
16415 | -125.6676 | -386.6141 | 406.5253 | -1.647 | 0.988
16425 | -244.649 | -407.8751 | 475.6209 | -1.977 | 2.306
16435 | -293.3892 | -315.4812 | 430.8197 | 0 | 1.647
16445 | -221.4201 | -145.4854 | 264.9394 | 1.647 | 0
16455 | -184.8136 | 9.6393 | 185.0648 | 2.307 | 0.331
16465 | -209.3794 | 73.2012 | 221.8065 | 1.647 | 0.988
16475 | -173.5946 | 14.5778 | 174.2056 | 0 | 0
16485 | -63.6606 | -87.7506 | 108.4105 | -0.988 | -1.319
16495 | 15.8546 | -76.2094 | 77.8411 | 0.329 | -1.317
16505 | 45.5892 | -128.9501 | 136.7717 | -0.988 | -0.989
16515 | -69.9103 | -176.926 | 190.2374 | -0.988 | 1.319
16525 | -63.77 | -127.5459 | 142.5994 | 0.329 | -0.33
16535 | -37.1084 | -161.5635 | 165.7703 | -0.988 | -0.33
16545 | 72.8102 | -141.371 | 159.0191 | 0 | -1.977
16555 | 81.6473 | -174.3979 | 192.564 | -0.989 | -0.658
16565 | 112.1611 | -168.4516 | 202.376 | -0.329 | -1.318
16575 | 105.5233 | -60.6531 | 121.7126 | 1.318 | -0.659
16585 | 193.1941 | 1.8956 | 193.2034 | 0.988 | -2.306
16595 | 422.3974 | -98.8329 | 433.8058 | -1.318 | -4.942
16605 | 553.7958 | -219.2908 | 595.6327 | -1.977 | -4.282
16615 | 516.4635 | -237.1751 | 568.3191 | -0.988 | -2.306
16625 | 485.5908 | -181.2188 | 518.3036 | 0 | -2.307
16635 | 498.9631 | -64.42 | 503.1045 | 1.318 | -2.636
16645 | 363.7044 | 56.536 | 368.0723 | 1.977 | 0
16655 | 277.2122 | 41.142 | 280.2486 | 0.329 | -0.329
16665 | 292.2522 | -39.6337 | 294.9274 | -0.659 | -1.318
16675 | 406.9229 | -73.1472 | 413.445 | -0.33 | -2.965
16685 | 415.7011 | 9.3177 | 415.8055 | 1.319 | -1.647
16695 | 272.4313 | 95.8221 | 288.7918 | 1.647 | 0.659
16705 | 262.1623 | 112.5151 | 285.2871 | 0.988 | -0.989
16715 | 123.7311 | 176.6006 | 215.632 | 1.976 | 1.647
16725 | -50.6829 | 116.3373 | 126.8981 | 0 | 2.637
16735 | 63.7437 | 42.2944 | 76.4989 | -0.329 | -1.319
16745 | 189.5136 | -38.5364 | 193.3919 | -0.988 | -1.647
16755 | 85.791 | -36.2877 | 93.1498 | 0 | 1.318
16765 | 48.0591 | -5.7038 | 48.3963 | 0.33 | 0.329
16775 | 20.3635 | -63.7598 | 66.9326 | -0.989 | 0.659
16785 | -42.735 | -56.6354 | 70.9496 | 0 | 1.318
16795 | -33.0917 | -59.8825 | 68.4177 | -0.33 | 0.329
16805 | 19.0011 | -29.712 | 35.2681 | 0.33 | -0.329
16815 | 110.529 | -100.6126 | 149.4642 | -1.317 | -1.318
16825 | 212.8436 | -162.7483 | 267.9355 | -1.318 | -1.977
16835 | 204.867 | -218.4857 | 299.5104 | -1.648 | -0.658
16845 | 111.5507 | -297.3302 | 317.567 | -2.306 | 0.658
16855 | 7.402 | -355.9249 | 356.0018 | -2.306 | 1.318
16865 | -99.1813 | -261.2531 | 279.4461 | 0 | 1.977
16875 | -172.9839 | -184.6237 | 253.0007 | 0 | 1.977
16885 | -222.062 | -106.3712 | 246.2242 | 0.659 | 1.976
16895 | -258.4137 | -51.7558 | 263.5456 | 0.658 | 1.977
16905 | -229.5 | -94.3484 | 248.1368 | -0.658 | 0.989
16915 | -92.1261 | -112.2758 | 145.2346 | -0.329 | -0.989
16925 | -70.2425 | -77.4658 | 104.5703 | 0.329 | 0.329
16935 | -113.5322 | -49.286 | 123.7686 | 0.329 | 0.989
16945 | -67.2358 | -109.1347 | 128.1836 | -0.988 | -0.329
16955 | -43.4233 | -119.8436 | 127.468 | -0.33 | 0
16965 | -53.8757 | -136.124 | 146.3978 | -0.659 | 0.329
16975 | -24.2163 | -208.8825 | 210.2816 | -1.647 | -0.329
16985 | 40.3429 | -187.3203 | 191.6154 | -0.329 | -0.989
16995 | 67.1072 | -160.6378 | 174.0916 | -0.329 | -0.658
17005 | 176.9658 | -148.4775 | 231.0032 | -0.33 | -2.306
17015 | 264.9429 | -26.398 | 266.2548 | 1.648 | -2.307
17025 | 243.4964 | -7.6694 | 243.6172 | 0.329 | -0.988
17035 | 184.0247 | -126.4136 | 223.2611 | -1.647 | -0.329
17045 | 128.7491 | -137.8295 | 188.6088 | -0.33 | 0
17055 | 75.9406 | -108.0265 | 132.0481 | 0 | 0.329
17065 | 60.386 | -89.6646 | 108.1027 | 0 | 0
17075 | -42.0604 | -79.321 | 89.7825 | 0 | 1.647
17085 | -47.1997 | -53.2653 | 71.1689 | 0.33 | 0.329
17095 | 40.296 | -71.5553 | 82.1214 | -0.33 | -0.988
17105 | -51.2336 | -108.3323 | 119.8364 | -0.659 | 1.647
17115 | -272.677 | -74.7666 | 282.7416 | 0.33 | 3.953
17125 | -391.4882 | -62.688 | 396.4755 | 0 | 3.295
17135 | -459.8942 | -137.1964 | 479.9224 | -1.318 | 3.295
17145 | -627.6629 | -157.1744 | 647.0429 | -0.66 | 5.271
17155 | -799.6277 | -84.0006 | 804.0277 | 0.66 | 5.93
17165 | -920.2297 | -85.6535 | 924.2073 | -0.329 | 5.93
17175 | -930.3495 | -137.8767 | 940.5106 | -0.989 | 4.613
17185 | -841.7362 | -78.449 | 845.384 | 0.658 | 2.965
17195 | -689.6659 | -4.7045 | 689.6819 | 0.989 | 1.318
17205 | -610.3712 | -54.6375 | 612.8118 | -0.658 | 1.647
17215 | -533.743 | -43.4869 | 535.5116 | 0.329 | 0.988
17225 | -403.4836 | -22.0239 | 404.0842 | 0.329 | -0.329
17235 | -252.4896 | 28.7572 | 254.122 | 0.989 | -1.319
17245 | -52.7544 | 48.7801 | 71.8507 | 0.659 | -2.964
17255 | 129.8245 | 97.0569 | 162.094 | 1.318 | -3.624
17265 | 82.4422 | 155.9091 | 176.3643 | 1.646 | -0.659
17275 | -5.1358 | 197.5924 | 197.6591 | 1.647 | 0
17285 | -31.3757 | 149.9745 | 153.2214 | 0.331 | -0.33
17295 | -152.5279 | 149.7875 | 213.778 | 0.987 | 1.647
17305 | -148.9902 | 181.3871 | 234.7325 | 1.319 | 0
17315 | -164.2943 | 147.5833 | 220.8471 | 0.329 | 0.66
17325 | -203.0619 | 156.774 | 256.5389 | 0.988 | 0.988
17335 | -191.0579 | 153.6906 | 245.2018 | 0.659 | 0.329
17345 | -215.5475 | 148.6879 | 261.8565 | 0.659 | 0.989
17355 | -296.9558 | 147.5512 | 331.5933 | 0.659 | 1.977
17365 | -376.1627 | 90.3089 | 386.8515 | -0.33 | 2.306
17375 | -409.6325 | 103.4869 | 422.5025 | 0.66 | 1.976
17385 | -411.0743 | 104.2049 | 424.0764 | 0.329 | 1.648
17395 | -394.3325 | 118.3799 | 411.7183 | 0.658 | 1.318
17405 | -404.1602 | 131.2961 | 424.9519 | 0.66 | 1.647
17415 | -378.5 | 119.8396 | 397.0186 | 0.329 | 0.988
17425 | -338.3284 | 110.1904 | 355.8202 | 0.33 | 0.659
17435 | -312.8744 | 124.579 | 336.7645 | 0.658 | 0.659
17445 | -202.0531 | 98.7153 | 224.8781 | 0 | -0.989
17455 | -135.5637 | 94.9711 | 165.5204 | 0.329 | -0.658
17465 | -40.7894 | 39.7406 | 56.9481 | -0.658 | -1.648
17475 | 51.6455 | 52.2368 | 73.4571 | 0.329 | -1.976
17485 | 115.7514 | 70.7825 | 135.6781 | 0.329 | -1.977
17495 | 161.4411 | 60.1344 | 172.277 | 0 | -1.977
17505 | 196.8891 | 49.7573 | 203.0791 | 0 | -1.976
17515 | 302.9267 | 24.4744 | 303.9138 | -0.329 | -3.295
17525 | 388.9007 | 4.9488 | 388.9322 | -0.329 | -3.295
17535 | 389.789 | 30.8886 | 391.011 | 0.329 | -2.306
17545 | 408.3365 | 13.9557 | 408.5749 | -0.329 | -2.635
17555 | 394.8388 | -5.2747 | 394.874 | -0.329 | -1.977
17565 | 347.8261 | -16.7099 | 348.2272 | -0.33 | -1.318
17575 | 357.4876 | -44.0381 | 360.1899 | -0.659 | -1.976
17585 | 414.139 | -65.5929 | 419.3012 | -0.659 | -2.637
17595 | 438.8905 | -60.6996 | 443.0681 | -0.329 | -2.306
17605 | 319.3317 | -56.2425 | 324.2467 | -0.329 | 0
17615 | 227.0999 | -75.1089 | 239.198 | -0.66 | 0
17625 | 118.8584 | -110.5803 | 162.3432 | -0.988 | 0.989
17635 | 41.1683 | -98.1953 | 106.476 | -0.329 | 0.988
17645 | 49.5735 | -46.7517 | 68.1414 | 0.329 | 0
17655 | 79.7254 | 84.9864 | 116.5283 | 1.977 | -0.329
17665 | 57.8057 | 85.6102 | 103.2987 | 0.329 | 0.329
17675 | 73.1502 | 49.283 | 88.203 | 0 | -0.329
17685 | 127.3949 | 48.714 | 136.391 | 0.329 | -0.988
17695 | 146.1514 | 54.0976 | 155.8422 | 0.33 | -0.66
17705 | 210.8563 | -19.1935 | 211.728 | -0.988 | -1.647
17715 | 185.6556 | -58.0894 | 194.5312 | -0.659 | -0.329
17725 | 291.2782 | -38.4898 | 293.8102 | 0 | -2.635
17735 | 288.4039 | -41.2488 | 291.3387 | -0.33 | -0.989
17745 | 268.4643 | 8.7794 | 268.6078 | 0.66 | -0.988
17755 | 339.3929 | -27.4241 | 340.499 | -0.66 | -2.307
17765 | 303.0314 | 11.9795 | 303.2681 | 0.66 | -0.659
17775 | 283.2858 | 13.7335 | 283.6185 | 0 | -0.987
17785 | 222.3693 | -32.6034 | 224.7468 | -0.66 | 0
17795 | 233.0878 | -27.7908 | 234.7387 | 0 | -0.989
17805 | 213.1365 | -55.571 | 220.2619 | -0.658 | -0.329
17815 | 249.7272 | -81.4577 | 262.6766 | -0.659 | -1.319
17825 | 302.572 | -58.8322 | 308.2386 | 0 | -1.647
17835 | 317.9656 | 37.2694 | 320.1423 | 1.317 | -1.317
17845 | 267.6067 | 50.4056 | 272.3124 | 0.33 | -0.33
17855 | 190.6377 | 8.5727 | 190.8304 | -0.33 | 0.33
17865 | 62.3461 | -39.4212 | 73.7635 | -0.658 | 1.646
17875 | 27.2448 | -70.4167 | 75.5036 | -0.659 | 0.66
17885 | 91.3736 | -31.991 | 96.812 | 0.329 | -0.66
17895 | 176.4734 | -57.2188 | 185.5178 | -0.659 | -1.317
17905 | 77.0282 | -123.92 | 145.9093 | -1.317 | 1.317
17915 | -12.7493 | -55.5675 | 57.0113 | 0.658 | 1.318
17925 | -45.2254 | -12.9227 | 47.0354 | 0.329 | 0.989
17935 | -103.767 | -52.1119 | 116.1173 | -0.658 | 1.648
17945 | -151.4844 | -66.1003 | 165.2779 | -0.329 | 1.646
17955 | -88.468 | -30.9955 | 93.7406 | 0.329 | 0
17965 | -57.0046 | -22.8899 | 61.4286 | 0 | 0.33
17975 | 10.2196 | -60.9317 | 61.7828 | -0.659 | -0.659
17985 | 3.1607 | -128.613 | 128.6518 | -1.318 | 0.329
17995 | -13.2701 | -99.4031 | 100.285 | 0 | 0.33
18005 | 17.0834 | 8.4746 | 19.0699 | 1.318 | -0.33
18015 | 61.4489 | -49.8343 | 79.1166 | -0.989 | -0.659
18025 | 71.6903 | -72.5552 | 101.9988 | -0.329 | -0.329
18035 | 74.9071 | -36.4755 | 83.3158 | 0.329 | -0.329
18045 | 155.598 | -66.5979 | 169.2513 | -0.658 | -1.647
18055 | 200.9292 | -58.2099 | 209.1911 | 0 | -1.319
18065 | 225.3207 | -6.2617 | 225.4077 | 0.658 | -1.318
18075 | 225.0174 | -7.2409 | 225.1339 | 0 | -0.988
18085 | 244.1505 | -91.9535 | 260.8925 | -1.318 | -1.318
18095 | 186.0251 | -155.5487 | 242.4886 | -1.317 | 0
18105 | 157.8214 | -135.5671 | 208.053 | -0.33 | -0.329
18115 | 262.8435 | -115.531 | 287.1135 | -0.329 | -2.306
18125 | 328.3867 | -126.4252 | 351.8823 | -0.659 | -1.976
18135 | 344.5938 | -176.1725 | 387.0163 | -1.318 | -1.648
18145 | 201.8383 | -194.7739 | 280.4916 | -0.988 | 0.988
18155 | 148.7261 | -184.2803 | 236.8094 | -0.659 | 0
18165 | 131.6718 | -158.1224 | 205.7672 | -0.33 | 0
18175 | 79.2676 | -140.9874 | 161.743 | -0.329 | 0.66
18185 | 57.4717 | -151.1379 | 161.6962 | -0.658 | 0.329
18195 | 161.5554 | -161.2025 | 228.2244 | -0.66 | -1.648
18205 | 146.863 | -109.5059 | 183.1946 | 0.329 | 0
18215 | 193.7334 | -29.5385 | 195.9723 | 0.989 | -1.318
18225 | 297.361 | -32.6017 | 299.1429 | 0 | -2.306
18235 | 274.1198 | -63.045 | 281.2763 | -0.329 | -0.658
18245 | 282.5294 | -4.377 | 282.5633 | 0.988 | -1.318
18255 | 338.9308 | -10.4682 | 339.0924 | 0 | -1.977
18265 | 285.5106 | 13.2241 | 285.8167 | 0.659 | -0.329
18275 | 352.5121 | 38.1578 | 354.5713 | 0.659 | -2.306
18285 | 303.9467 | -41.9222 | 306.8242 | -0.988 | -0.33
18295 | 252.3321 | -10.2202 | 252.539 | 0.659 | -0.33
18305 | 321.7201 | 29.7725 | 323.0947 | 0.658 | -1.976
18315 | 343.2923 | -63.4545 | 349.1076 | -1.317 | -1.318
18325 | 251.6529 | -120.9918 | 279.2279 | -0.989 | 0.33
18335 | 200.4357 | -168.9219 | 262.1241 | -1.318 | 0
18345 | 252.3047 | -127.6339 | 282.7509 | 0 | -1.318
18355 | 391.9243 | -148.5372 | 419.1276 | -0.988 | -2.966
18365 | 395.9025 | -79.8891 | 403.8825 | 0.659 | -1.317
18375 | 400.2368 | 18.2504 | 400.6526 | 1.318 | -1.647
18385 | 374.469 | 24.8777 | 375.2945 | 0.329 | -0.989
18395 | 277.2268 | -114.7038 | 300.0194 | -1.977 | 0.329
18405 | 206.5061 | -66.3827 | 216.9135 | 0.659 | 0.331
18415 | 184.0816 | -82.4163 | 201.6891 | -0.659 | 0
18425 | 228.9424 | -15.4136 | 229.4607 | 0.988 | -0.989
18435 | 263.3751 | -31.9376 | 265.3044 | -0.329 | -0.988
18445 | 223.7479 | -96.3196 | 243.5992 | -0.988 | 0
18455 | 208.3164 | -139.6098 | 250.772 | -0.989 | -0.33
18465 | 261.2302 | -50.3272 | 266.0339 | 0.989 | -1.318
18475 | 360.1438 | -53.5204 | 364.0989 | -0.329 | -2.306
18485 | 506.5071 | -53.7167 | 509.3476 | 0 | -3.624
18495 | 553.3731 | -66.6714 | 557.375 | -0.33 | -2.636
18505 | 517.4323 | -116.5596 | 530.3983 | -0.988 | -1.647
18515 | 512.5038 | -191.996 | 547.2866 | -1.648 | -1.977
18525 | 461.8145 | -149.0463 | 485.2705 | 0 | -0.988
18535 | 461.5526 | -87.6753 | 469.8061 | 0.33 | -1.647
18545 | 452.652 | -128.2097 | 470.4589 | -0.988 | -1.318
18555 | 405.3552 | -129.0965 | 425.416 | -0.33 | -0.659
18565 | 313.2669 | -178.217 | 360.4129 | -1.317 | 0.33
18575 | 343.6149 | -182.2273 | 388.9447 | -0.66 | -1.318
18585 | 302.4158 | -119.8824 | 325.3108 | 0.33 | 0
18595 | 220.3856 | -151.0153 | 267.1618 | -0.989 | 0.658
18605 | 163.6059 | -166.6622 | 233.5448 | -0.658 | 0.66
18615 | 107.5966 | -74.7642 | 131.0218 | 0.988 | 0.988
18625 | 27.0461 | -117.7203 | 120.7873 | -0.988 | 1.647
18635 | -14.4926 | -90.0488 | 91.2075 | 0.329 | 1.318
18645 | -118.1123 | -74.3435 | 139.5617 | 0 | 2.635
18655 | -260.0544 | -165.9188 | 308.4759 | -1.647 | 3.624
18665 | -228.1784 | -161.1056 | 279.3213 | -0.329 | 1.318
18675 | -230.6546 | -180.8375 | 293.0934 | -0.989 | 1.977
18685 | -270.6556 | -184.3899 | 327.4967 | -0.659 | 2.306
18695 | -227.2648 | -183.378 | 292.0219 | -0.658 | 0.989
18705 | -96.2282 | -107.9091 | 144.583 | 0.658 | -0.66
18715 | -120.8993 | -68.0211 | 138.721 | 0.329 | 1.318
18725 | -103.3518 | -67.8807 | 123.6502 | 0 | 0.33
18735 | -117.8595 | -126.4219 | 172.8391 | -0.987 | 0.988
18745 | -155.5977 | -36.0646 | 159.7226 | 1.317 | 1.319
18755 | -259.1262 | -50.5778 | 264.0161 | -0.33 | 2.635
18765 | -107.4964 | -137.1316 | 174.2428 | -1.318 | -1.318
18775 | 5.9861 | -61.6909 | 61.9806 | 0.989 | -0.988
18785 | 25.4287 | -9.1671 | 27.0306 | 0.659 | -0.329
18795 | 33.3351 | -22.5633 | 40.2533 | 0 | -0.331
18805 | 80.6194 | -16.0021 | 82.1921 | 0.329 | -0.988
18815 | 99.6307 | -24.747 | 102.6581 | 0 | -0.658
18825 | 167.0451 | 5.7526 | 167.1441 | 0.66 | -1.648
18835 | 145.2956 | -43.9956 | 151.8105 | -0.66 | -0.33
18845 | 158.3411 | -107.3333 | 191.2913 | -0.988 | -0.988
18855 | 197.7857 | 6.8127 | 197.903 | 1.648 | -1.318
18865 | 149.8884 | -11.4174 | 150.3227 | -0.33 | 0
18875 | -25.6489 | 29.6372 | 39.1948 | 0.988 | 2.306
18885 | -57.6638 | 111.9243 | 125.9054 | 1.647 | 0.66
18895 | -173.5964 | 149.7334 | 229.2505 | 1.319 | 2.635
18905 | -157.1557 | 56.2331 | 166.9133 | -0.66 | 0.66
18915 | -185.8467 | 1.9945 | 185.8574 | -0.329 | 1.646
18925 | 8.4378 | 111.8283 | 112.1461 | 1.976 | -2.306
18935 | 51.519 | 48.8732 | 71.0127 | -0.658 | -0.329
18945 | 185.1252 | 56.7198 | 193.6194 | 0.658 | -2.636
18955 | 201.3078 | 215.661 | 295.0161 | 2.966 | -0.988
18965 | 310.0634 | 105.1499 | 327.4078 | -0.989 | -2.965
18975 | 482.4056 | 72.2777 | 487.7901 | 0.33 | -4.283
18985 | 566.3537 | 171.1559 | 591.6509 | 1.977 | -3.624
18995 | 444.7852 | 131.8284 | 463.9101 | 0 | -0.659
19005 | 388.8557 | 124.2581 | 408.2264 | 0.658 | -1.318
19015 | 334.6981 | 150.98 | 367.1754 | 0.988 | -0.659
19025 | 392.5687 | 113.1087 | 408.5385 | 0 | -2.306
19035 | 486.2405 | 118.6976 | 500.5187 | 0.66 | -2.965
19045 | 396.1553 | 246.6698 | 466.6744 | 2.635 | -0.329
19055 | 239.4747 | 268.4946 | 359.7743 | 1.318 | 0.988
19065 | 98.3135 | 306.0391 | 321.4428 | 1.977 | 1.647
19075 | 5.5121 | 227.0082 | 227.0751 | 0 | 1.647
19085 | -151.5424 | 141.4958 | 207.331 | -0.329 | 3.295
19095 | -175.9192 | 110.2184 | 207.5949 | 0 | 1.647
19105 | -6.6131 | 132.8355 | 133 | 0.658 | -1.318
19115 | -36.7186 | 247.5494 | 250.2578 | 2.306 | 1.318
19125 | -187.8272 | 102.7759 | 214.1073 | -1.646 | 2.965
19135 | -199.3558 | 201.8909 | 283.7299 | 2.306 | 1.318
19145 | -306.6456 | 195.6683 | 363.7549 | 0.329 | 3.295
19155 | -363.5801 | 164.7401 | 399.1614 | 0.329 | 2.635
19165 | -433.6791 | 92.7864 | 443.4939 | -0.658 | 3.295
19175 | -281.0653 | 230.7285 | 363.639 | 2.635 | -0.33
19185 | -213.927 | 331.2555 | 394.3285 | 2.306 | 0.659
19195 | -193.7376 | 269.6469 | 332.0297 | 0.33 | 0.66
19205 | -199.756 | 157.9623 | 254.6656 | -0.66 | 0.987
19215 | -15.0128 | 104.6804 | 105.7514 | -0.329 | -2.306
19225 | 56.1754 | 172.801 | 181.7027 | 1.318 | -0.988
19235 | 44.6642 | 209.8273 | 214.5283 | 0.988 | -0.33
19245 | 95.4726 | 263.9027 | 280.6415 | 1.647 | -1.318
19255 | 199.8583 | 305.5613 | 365.1178 | 1.648 | -2.306
19265 | 334.0652 | 370.5497 | 498.9054 | 2.306 | -3.294
19275 | 142.3338 | 170.5074 | 222.1073 | -1.977 | 1.647
19285 | 247.7112 | 178.4388 | 305.2888 | 0.989 | -2.965
19295 | 123.2609 | 48.7326 | 132.5448 | -1.977 | 1.318
19305 | 73.8984 | 65.6155 | 98.825 | 0.33 | 0
19315 | 8.4148 | 197.7325 | 197.9115 | 1.976 | 0.988
19325 | -64.5323 | 135.0888 | 149.7111 | -0.658 | 1.318
19335 | -170.9284 | 123.7044 | 210.9959 | 0.329 | 2.306
19345 | -249.553 | 112.5591 | 273.7631 | 0 | 2.306
19355 | -282.2233 | 176.5833 | 332.9139 | 1.317 | 1.977
19365 | -305.3386 | 133.2669 | 333.1542 | -0.329 | 1.977
19375 | -288.061 | 106.6085 | 307.1555 | 0 | 1.318
19385 | -180.1571 | 96.5224 | 204.3849 | 0 | -0.33
19395 | -44.5691 | 88.8082 | 99.3645 | 0 | -1.318
19405 | 63.9522 | 82.8359 | 104.6503 | 0 | -1.647
19415 | 269.0562 | 58.7892 | 275.4041 | -0.329 | -3.953
19425 | 442.7082 | 77.8187 | 449.4956 | 0.329 | -4.283
19435 | 422.6993 | 18.7449 | 423.1147 | -0.988 | -1.977
19445 | 512.3831 | -52.7808 | 515.0944 | -1.318 | -3.953
19455 | 563.9372 | -61.2729 | 567.2561 | -0.659 | -3.295
19465 | 690.7548 | 33.7005 | 691.5764 | 0.988 | -4.942
19475 | 700.3693 | 47.054 | 701.9482 | 0 | -3.295
19485 | 619.7612 | 2.6066 | 619.7667 | -0.658 | -1.976
19495 | 569.2636 | -48.9728 | 571.3663 | -0.989 | -1.977
19505 | 604.8736 | -6.7559 | 604.9114 | 0.33 | -2.964
19515 | 622.079 | -103.1462 | 630.5722 | -1.978 | -2.637
19525 | 458.3282 | -132.5071 | 477.0984 | -0.987 | 0.331
19535 | 331.5654 | -234.9677 | 406.3809 | -2.636 | 0.329
19545 | 298.1323 | -243.6587 | 385.0356 | -1.318 | -0.329
19555 | 320.1938 | -141.3345 | 349.9993 | 0.33 | -0.989
19565 | 278.281 | 8.1828 | 278.4013 | 1.647 | 0
19575 | 315.6615 | 12.6452 | 315.9147 | 0 | -1.318
19585 | 121.5076 | 74.5566 | 142.558 | 1.318 | 2.636
19595 | -61.8886 | 16.5753 | 64.0699 | -0.66 | 2.965
19605 | -60.0483 | -19.7787 | 63.2218 | -0.329 | 0.988
19615 | -26.9093 | 4.7459 | 27.3246 | 0.329 | 0.659
19625 | -168.5625 | -204.5064 | 265.021 | -3.624 | 3.295
19635 | -193.4498 | -279.5686 | 339.9727 | -1.976 | 1.647
19645 | -136.1925 | -228.4393 | 265.9566 | -0.659 | 0.659
19655 | -100.9493 | -76.9772 | 126.9498 | 1.318 | 0.659
19665 | -47.8021 | 68.4163 | 83.4616 | 1.977 | 0
19675 | -88.1691 | 141.8564 | 167.0241 | 1.647 | 1.317
19685 | -129.4488 | 128.6921 | 182.5339 | 0.659 | 1.318
19695 | -19.8386 | 193.2773 | 194.2928 | 1.977 | -0.988
19705 | -27.2641 | 137.7333 | 140.4058 | 0 | 0.659
19715 | -53.9677 | 65.8385 | 85.1306 | -0.33 | 0.659
19725 | -182.8608 | 5.4957 | 182.9434 | -0.659 | 2.636
19735 | -264.3857 | -14.6606 | 264.7918 | -0.33 | 2.306
19745 | -291.966 | -62.5706 | 298.5954 | -0.987 | 1.976
19755 | -196.4877 | -101.293 | 221.0603 | -0.989 | 0
19765 | -161.9609 | -183.8647 | 245.0256 | -1.977 | 0.659
19775 | -154.1909 | -132.4935 | 203.2962 | 0 | 0.659
19785 | -53.2761 | -101.7703 | 114.8718 | -0.329 | -0.988
19795 | -70.6295 | -73.5549 | 101.9747 | 0 | 0.658
19805 | 34.2053 | 42.585 | 54.6213 | 1.647 | -1.647
19815 | 107.6941 | 91.983 | 141.6294 | 0.988 | -1.317
19825 | 224.9761 | 191.636 | 295.5311 | 2.307 | -2.636
19835 | 392.5951 | 156.0276 | 422.4636 | 0.329 | -3.954
19845 | 590.1423 | 39.2335 | 591.445 | -0.989 | -5.271
19855 | 789.7323 | 134.1101 | 801.0384 | 1.977 | -6.259
19865 | 875.2799 | 34.2767 | 875.9508 | -1.317 | -5.272
19875 | 1027.1612 | -7.9652 | 1027.1921 | -0.33 | -6.918
19885 | 1039.8405 | -17.7494 | 1039.992 | -0.33 | -4.942
19895 | 732.6754 | -161.3986 | 750.2418 | -2.635 | 0.33
19905 | 718.1359 | -179.5307 | 740.2367 | -0.989 | -3.295
19915 | 608.9267 | -192.5429 | 638.6427 | -1.317 | -0.659
19925 | 356.598 | -154.0076 | 388.4334 | -0.33 | 1.977
19935 | 371.1981 | -65.7571 | 376.9774 | 0.66 | -1.318
19945 | 280.2619 | -63.1584 | 287.2903 | -0.33 | 0.989
19955 | 93.5032 | -150.5673 | 177.2381 | -1.647 | 2.635
19965 | 152.7004 | -100.4785 | 182.7932 | 0.329 | -0.659
19975 | 161.0201 | -163.2759 | 229.3174 | -1.647 | 0.33
19985 | 66.7092 | -73.3344 | 99.1365 | 0.989 | 1.647
19995 | 50.0869 | -104.0039 | 115.4362 | -0.989 | 0.658
20005 | 143.4849 | -225.1897 | 267.0174 | -2.306 | -0.987
20015 | 153.5923 | -214.0667 | 263.4676 | -0.66 | 0
20025 | 201.6591 | -55.7276 | 209.2175 | 1.648 | -0.989
20035 | 203.6621 | -74.7542 | 216.948 | -0.659 | -0.329
20045 | 100.0982 | -56.3708 | 114.8796 | 0.329 | 1.318
20055 | 39.7815 | -86.7015 | 95.3924 | -0.658 | 0.987
20065 | -108.4088 | -193.0888 | 221.4402 | -1.977 | 2.966
20075 | -90.0326 | 56.5087 | 106.2973 | 3.624 | 0.658
20085 | -19.1835 | 153.6668 | 154.8596 | 1.648 | 0
20095 | -36.5391 | 242.6879 | 245.4232 | 2.635 | 0.989
20105 | -100.5136 | 48.0415 | 111.4046 | -1.977 | 1.648
20115 | 25.5553 | 0.83068 | 25.5688 | 0 | -1.318
20125 | 74.1056 | 22.3084 | 77.3906 | 0.329 | -0.33
20135 | 29.4905 | 92.6248 | 97.2062 | 1.319 | 0.659
20145 | 71.176 | 106.7063 | 128.2664 | 0.658 | -0.659
20155 | 35.5333 | -7.0158 | 36.2193 | -1.318 | 0.659
20165 | -21.5782 | 1.8977 | 21.6615 | 0.33 | 0.989
20175 | -115.773 | 27.8894 | 119.0849 | 0.33 | 1.976
20185 | -166.104 | -36.9221 | 170.1581 | -0.989 | 1.648
20195 | -80.291 | -32.9905 | 86.8045 | 0 | -0.331
20205 | 45.2696 | -76.4647 | 88.8605 | -0.988 | -1.317
20215 | 49.828 | -58.841 | 77.1044 | 0 | 0
20225 | -38.7224 | -76.1398 | 85.4207 | -0.66 | 1.317
20235 | 12.3777 | -58.2591 | 59.5594 | 0 | -0.658
20245 | 85.5789 | -40.4306 | 94.6487 | 0 | -0.988
20255 | -23.446 | 64.7314 | 68.8467 | 1.648 | 1.646
20265 | -136.5493 | 184.8807 | 229.8403 | 2.306 | 1.978
20275 | 6.1894 | 322.4209 | 322.4803 | 3.294 | -1.647
20285 | 148.281 | 401.8342 | 428.32 | 2.966 | -1.977
20295 | 116.361 | 548.9333 | 561.1307 | 4.612 | 0
20305 | 59.447 | 627.2753 | 630.086 | 3.953 | 0.329
20315 | 123.6883 | 618.3125 | 630.5626 | 2.966 | -1.318
20325 | 181.9346 | 422.2829 | 459.8076 | -0.33 | -1.318
20335 | 254.6418 | 259.0775 | 363.2679 | -0.659 | -1.977
20345 | 232.1025 | 145.5919 | 273.9865 | -0.988 | -0.658
20355 | 34.5535 | 90.5767 | 96.9437 | -0.659 | 2.306
20365 | -131.4135 | 17.9637 | 132.6356 | -1.318 | 2.636
20375 | 16.8855 | 37.7848 | 41.3861 | 0 | -1.647
20385 | 109.2981 | 251.8003 | 274.4985 | 3.295 | -0.989
20395 | 14.1005 | 315.2816 | 315.5967 | 1.647 | 1.318
20405 | 68.0357 | 332.3884 | 339.28 | 1.647 | -0.989
20415 | 71.5203 | 215.3096 | 226.8775 | -0.659 | 0
20425 | 289.7198 | 27.0686 | 290.9816 | -2.306 | -3.953
20435 | 313.6253 | -24.2147 | 314.5587 | -0.989 | -1.317
20445 | 48.609 | -273.5709 | 277.8558 | -4.941 | 2.964
20455 | -91.1037 | -457.17 | 466.1591 | -4.613 | 1.977
20465 | -255.5017 | -434.6254 | 504.163 | -2.305 | 3.624
20475 | -400.101 | -506.4517 | 645.4256 | -3.954 | 3.953
20485 | -459.6723 | -429.7037 | 629.2407 | -1.318 | 3.295
20495 | -576.2877 | -419.9053 | 713.0413 | -2.306 | 4.612
20505 | -750.5873 | -301.7899 | 808.986 | 0 | 5.931
20515 | -957.2441 | -343.2301 | 1016.9185 | -2.306 | 7.247
20525 | -897.8251 | -341.635 | 960.6271 | -1.318 | 3.624
20535 | -895.0827 | -328.4189 | 953.4317 | -1.318 | 4.613
20545 | -981.6085 | -247.6369 | 1012.3632 | 0 | 5.6
20555 | -938.9698 | -71.0102 | 941.651 | 1.977 | 3.624
20565 | -881.8108 | -40.4797 | 882.7395 | 0.329 | 3.295
20575 | -759.6767 | -96.5394 | 765.7862 | -0.659 | 1.647
20585 | -866.5309 | -76.1425 | 869.8698 | 0.33 | 4.942
20595 | -914.8449 | -87.4538 | 919.0154 | -0.33 | 3.953
20605 | -740.3396 | -24.4694 | 740.7438 | 0.989 | 0.66
20615 | -548.1994 | 68.8685 | 552.5084 | 1.648 | -0.331
20625 | -350.9784 | 152.0692 | 382.506 | 1.976 | -1.646
20635 | -137.6381 | 190.309 | 234.8654 | 1.647 | -2.966
20645 | 12.4113 | 196.2065 | 196.5987 | 1.318 | -2.965
20655 | 132.6528 | 222.0218 | 258.6319 | 1.647 | -3.294
20665 | 184.72 | 93.3023 | 206.9463 | -0.988 | -2.636
20675 | 280.5221 | 48.2405 | 284.6398 | 0 | -3.624
20685 | 440.4184 | 152.3869 | 466.0366 | 1.977 | -4.941
20695 | 640.1044 | 234.8509 | 681.8274 | 1.977 | -6.26
20705 | 615.3543 | 168.1639 | 637.9185 | 0 | -3.295
20715 | 544.8681 | 148.7351 | 564.8038 | 0.658 | -2.635
20725 | 457.0311 | 149.9037 | 480.987 | 0.659 | -1.648
20735 | 558.0321 | 208.3415 | 595.656 | 1.647 | -4.282
20745 | 656.0656 | 236.3636 | 697.3449 | 1.318 | -4.283
20755 | 699.6483 | 269.7539 | 749.8499 | 1.648 | -3.954
20765 | 751.3478 | 201.055 | 777.7831 | 0 | -4.283
20775 | 854.4484 | 67.3758 | 857.1007 | -1.318 | -5.271
20785 | 879.5322 | 71.9902 | 882.4735 | 0.329 | -4.283
20795 | 758.832 | 150.3448 | 773.5823 | 1.318 | -1.976
20805 | 672.5332 | 184.4988 | 697.3813 | 0.989 | -1.977
20815 | 610.8956 | 142.5767 | 627.313 | 0 | -1.647
20825 | 495.8078 | 70.0226 | 500.728 | -0.66 | -0.33
20835 | 470.6225 | 40.2646 | 472.3418 | -0.329 | -1.318
20845 | 524.3255 | 44.579 | 526.2172 | 0 | -2.306
20855 | 660.3019 | 9.5336 | 660.3707 | -0.659 | -3.953
20865 | 528.8204 | -21.2571 | 529.2475 | -0.659 | 0
20875 | 368.817 | -60.164 | 373.692 | -0.988 | 0.658
20885 | 368.1627 | 25.3224 | 369.0325 | 0.988 | -0.987
20895 | 345.151 | -76.7295 | 353.5769 | -1.977 | -0.33
20905 | 356.2485 | -40.5227 | 358.5458 | 0.329 | -0.988
20915 | 291.5311 | 85.9667 | 303.9418 | 1.648 | 0.329
20925 | 196.3958 | 94.685 | 218.0288 | 0.329 | 0.989
20935 | 92.3688 | 123.5323 | 154.2473 | 0.989 | 1.647
20945 | -96.9926 | -58.7532 | 113.3997 | -2.635 | 3.624
20955 | -335.2497 | -54.0695 | 339.5819 | 0 | 5.27
20965 | -370.5814 | -191.9261 | 417.3323 | -2.966 | 2.966
20975 | -282.8461 | -219.1162 | 357.7902 | -1.318 | 1.318
20985 | -325.361 | -160.554 | 362.8186 | -0.329 | 2.965
20995 | -285.0111 | -45.6439 | 288.6428 | 0.989 | 1.318
21005 | -363.0058 | -4.8755 | 363.0385 | 0.329 | 3.294
21015 | -479.1618 | -27.4184 | 479.9456 | -0.329 | 3.954
21025 | -483.6275 | -83.8763 | 490.847 | -0.989 | 2.635
21035 | -422.3147 | -65.6696 | 427.3899 | 0 | 1.647
21045 | -423.3758 | -120.5687 | 440.2089 | -1.318 | 2.306
21055 | -400.1367 | -55.3844 | 403.9515 | 0.659 | 1.648
21065 | -382.2492 | 25.3111 | 383.0863 | 0.988 | 1.647
21075 | -356.8269 | 74.4679 | 364.5146 | 0.989 | 1.318
21085 | -340.5327 | 67.2929 | 347.1179 | 0.329 | 1.317
21095 | -313.9957 | 39.7126 | 316.4971 | 0 | 0.989
21105 | -334.1412 | 42.1484 | 336.789 | 0.329 | 1.647
21115 | -354.9842 | 87.4535 | 365.598 | 0.989 | 1.648
21125 | -290.9584 | 237.7106 | 375.7168 | 2.965 | 0.329
21135 | -220.4412 | 216.7107 | 309.1243 | 0.659 | 0
21145 | -234.2695 | 238.4774 | 334.2957 | 1.648 | 0.988
21155 | -290.976 | 213.1187 | 360.6752 | 0.658 | 1.647
21165 | -368.4481 | 150.9276 | 398.1623 | 0 | 2.307
21175 | -499.2794 | 129.5526 | 515.8137 | 0.33 | 3.624
21185 | -498.9615 | 160.3395 | 524.0909 | 0.988 | 1.977
21195 | -407.6651 | 185.5224 | 447.8944 | 0.988 | 0.658
21205 | -326.9276 | 200.4709 | 383.4974 | 0.989 | 0.33
21215 | -317.1546 | 172.5694 | 361.0641 | 0.329 | 0.988
21225 | -222.3348 | 150.3003 | 268.3709 | 0.33 | -0.659
21235 | -67.9185 | 234.8402 | 244.4644 | 1.976 | -1.977
21245 | -55.9119 | 265.9229 | 271.7373 | 1.318 | -0.329
21255 | -24.3094 | 200.0959 | 201.5671 | 0 | -0.988
21265 | 87.5161 | 245.9194 | 261.0276 | 1.648 | -2.307
21275 | 58.5806 | 218.0639 | 225.7953 | 0.329 | -0.329
21285 | 4.8506 | 224.0593 | 224.1118 | 0.988 | 0
21295 | -176.4763 | 103.5703 | 204.6233 | -1.317 | 2.636
21305 | -350.2871 | 4.9906 | 350.3226 | -1.318 | 3.294
21315 | -480.0971 | -14.6581 | 480.3208 | -0.659 | 3.624
21325 | -491.1575 | -81.4792 | 497.87 | -1.647 | 2.306
21335 | -472.8096 | -61.5633 | 476.8008 | -0.33 | 1.978
21345 | -314.2013 | -19.2478 | 314.7903 | 0 | -0.66
21355 | -195.3218 | 4.0646 | 195.3641 | 0 | -0.659
21365 | -108.9165 | -61.1572 | 124.912 | -1.318 | -0.988
21375 | -107.4593 | -0.6458 | 107.4613 | 0.659 | 0
21385 | -189.9356 | 57.6625 | 198.4956 | 0.659 | 1.318
21395 | -325.5876 | 31.2688 | 327.0857 | -0.33 | 2.635
21405 | -534.5306 | -13.7945 | 534.7086 | -0.658 | 4.613
21415 | -606.9261 | -23.6229 | 607.3857 | -0.33 | 3.295
21425 | -641.1202 | -26.4974 | 641.6676 | -0.329 | 3.293
21435 | -557.9356 | -30.2961 | 558.7576 | -0.33 | 1.318
21445 | -455.7219 | 23.7604 | 456.3409 | 0.659 | 0.659
21455 | -413.6938 | 104.6676 | 426.7293 | 1.318 | 0.989
21465 | -393.8834 | 178.8351 | 432.5808 | 1.647 | 0.989
21475 | -419.1255 | 209.553 | 468.5922 | 1.318 | 1.646
21485 | -364.1304 | 208.8823 | 419.7889 | 0.989 | 0.33
21495 | -353.9069 | 209.5685 | 411.3017 | 0.988 | 0.988
21505 | -241.0729 | 194.7208 | 309.8908 | 0.659 | -0.988
21515 | -187.3263 | 261.6635 | 321.8058 | 1.977 | -0.33
21525 | -277.0981 | 280.5747 | 394.3419 | 1.317 | 1.647
21535 | -347.7719 | 401.1032 | 530.8758 | 3.295 | 1.648
21545 | -520.2992 | 288.8866 | 595.1191 | -0.33 | 3.953
21555 | -593.6954 | 202.8744 | 627.4012 | 0 | 2.966
21565 | -609.6641 | 162.8697 | 631.0443 | 0 | 2.635
21575 | -547.3085 | 118.4187 | 559.9729 | -0.329 | 1.318
21585 | -482.4702 | 105.3475 | 493.8377 | 0 | 0.989
21595 | -444.8706 | 137.6836 | 465.6894 | 0.659 | 0.987
21605 | -308.2285 | 181.0091 | 357.448 | 0.988 | -0.987
21615 | -203.1495 | 228.2002 | 305.5242 | 1.318 | -0.989
21625 | -81.4305 | 279.7148 | 291.3267 | 1.647 | -1.977
21635 | -183.1501 | 296.7169 | 348.6902 | 1.318 | 1.318
21645 | -351.5044 | 248.1425 | 430.2674 | 0.329 | 2.635
21655 | -400.8096 | 211.4245 | 453.1541 | 0.33 | 1.648
21665 | -284.432 | 115.1909 | 306.8722 | -0.988 | -0.659
21675 | -212.4454 | 99.906 | 234.7643 | 0 | -0.33
21685 | -156.6655 | 139.5152 | 209.7822 | 0.658 | -0.659
21695 | -115.9125 | 128.0429 | 172.7157 | 0 | -0.658
21705 | -87.5836 | 15.5552 | 88.9542 | -1.647 | -0.66
21715 | -123.7865 | 6.3687 | 123.9502 | -0.329 | 0.331
21725 | -190.5171 | -4.7306 | 190.5758 | -0.659 | 0.987
21735 | -176.2187 | 56.061 | 184.9212 | 0.659 | 0
21745 | -59.0894 | 85.5117 | 103.9413 | 0.329 | -1.647
21755 | -9.5431 | 96.5306 | 97.0012 | 0.329 | -0.988
21765 | -101.2064 | 161.5454 | 190.6296 | 1.318 | 0.988
21775 | -268.7671 | 135.3446 | 300.9218 | 0 | 2.636
21785 | -287.1665 | 124.4071 | 312.9565 | 0.33 | 0.988
21795 | -338.189 | 86.0683 | 348.9693 | -0.33 | 1.977
21805 | -405.4086 | -2.2612 | 405.4149 | -1.318 | 2.306
21815 | -452.1081 | 29.7476 | 453.0857 | 0.33 | 2.307
21825 | -542.1306 | 65.9198 | 546.1236 | 0.33 | 3.293
21835 | -574.4295 | 121.5284 | 587.1443 | 0.988 | 2.637
21845 | -360.9074 | 104.3091 | 375.6788 | 0 | -1.319
21855 | -310.8638 | 83.0951 | 321.778 | 0 | 0.659
21865 | -405.006 | 130.1734 | 425.4116 | 0.988 | 2.307
21875 | -513.1833 | 227.1142 | 561.1933 | 1.977 | 2.964
21885 | -564.7697 | 219.0758 | 605.7714 | 0.659 | 2.637
21895 | -518.3008 | 297.4205 | 597.574 | 2.306 | 1.317
21905 | -481.3053 | 406.4694 | 629.9779 | 2.965 | 1.318
21915 | -329.7305 | 385.1309 | 506.999 | 1.318 | -0.988
21925 | -252.3322 | 436.0717 | 503.8155 | 2.635 | -0.33
21935 | -233.0635 | 546.8456 | 594.4398 | 3.624 | 0
21945 | -392.4033 | 493.3409 | 630.3694 | 1.318 | 2.965
21955 | -497.5595 | 344.9679 | 605.4488 | -0.329 | 2.635
21965 | -572.8061 | 245.7424 | 623.2946 | -0.33 | 2.966
21975 | -491.9557 | 188.683 | 526.8982 | -0.329 | 0.658
21985 | -326.6176 | 170.5855 | 368.4813 | 0 | -0.987
21995 | -272.3183 | 178.7109 | 325.722 | 0.329 | 0
22005 | -116.0572 | 241.1026 | 267.5812 | 1.318 | -2.306
22015 | -67.2127 | 190.9178 | 202.4035 | -0.329 | -0.989
22025 | -106.5038 | 159.8804 | 192.1062 | 0 | 0
22035 | -54.8326 | 204.077 | 211.315 | 0.988 | -1.318
22045 | 132.1267 | 143.3575 | 194.9585 | -0.659 | -3.624
22055 | 254.3382 | 105.5518 | 275.3709 | -0.329 | -3.294
22065 | 349.0888 | 87.2597 | 359.8295 | -0.33 | -3.624
22075 | 421.797 | 53.9118 | 425.2284 | -0.659 | -3.624
22085 | 611.7238 | -10.9905 | 611.8225 | -1.317 | -5.93
22095 | 648.6797 | -2.4025 | 648.6841 | -0.329 | -3.954
22105 | 583.2488 | 29.7722 | 584.0082 | 0 | -2.636
22115 | 584.4347 | 66.9948 | 588.262 | 0.329 | -3.294
22125 | 527.6183 | -5.4345 | 527.6463 | -1.318 | -1.977
22135 | 466.3347 | -203.0694 | 508.6307 | -3.624 | -1.647
22145 | 433.3143 | -155.5451 | 460.3863 | -0.33 | -1.648
22155 | 455.5529 | -55.33 | 458.9007 | 0.33 | -2.306
22165 | 612.8615 | 155.3843 | 632.2527 | 2.965 | -4.611
22175 | 1331.0295 | 174.6319 | 1342.4365 | 0.659 | -14.826
22185 | 2015.896 | 333.7626 | 2043.3389 | 3.624 | -17.131
22195 | 3424.4722 | 874.7278 | 3534.4248 | 10.543 | -33.604
22205 | 4668.0709 | 858.1768 | 4746.2989 | 3.293 | -36.57
22215 | 4343.6326 | 219.3463 | 4349.1673 | -6.259 | -16.802
22225 | 5631.2943 | -666.1322 | 5670.5562 | -13.507 | -44.476
22235 | 5397.8716 | -1037.9562 | 5496.76 | -9.554 | -20.096
22245 | 3204.4837 | -2598.7685 | 4125.8107 | -32.946 | 11.201
22255 | 1718.8364 | -4072.7149 | 4420.5662 | -36.899 | 9.884
22265 | 1235.194 | -4690.9183 | 4850.8163 | -30.968 | 3.953
22275 | 1175.7717 | -4377.7137 | 4532.8597 | -18.778 | 0.329
22285 | 1199.1872 | -3027.556 | 3256.4006 | 0.658 | -0.988
22295 | -140.5297 | -2645.47 | 2649.1999 | -8.895 | 21.744
22305 | -460.981 | -3035.938 | 3070.7366 | -16.802 | 8.566
22315 | -216.4513 | -2753.4515 | 2761.9461 | -6.589 | 3.295
22325 | 721.1592 | -3087.3006 | 3170.4094 | -17.131 | -10.543
22335 | 2143.7782 | -2722.6822 | 3465.3692 | -4.942 | -23.392
22345 | 1984.7509 | -2138.5806 | 2917.664 | -0.989 | -3.953
22355 | 995.6555 | -1712.8793 | 1981.2333 | 0 | 7.907
22365 | 249.4115 | -1252.0122 | 1276.6129 | 3.295 | 9.224
22375 | 239.9339 | -1344.1783 | 1365.4243 | -3.954 | 1.648
22385 | 637.5344 | -1652.599 | 1771.3084 | -7.248 | -4.283
22395 | 1251.1728 | -1596.1584 | 2028.0915 | -2.964 | -10.213
22405 | 1457.0295 | -793.6173 | 1659.1453 | 9.224 | -6.589
22415 | 542.2283 | -542.5362 | 767.0444 | 2.965 | 10.543
22425 | -141.1029 | -707.0149 | 720.9577 | -1.318 | 9.883
22435 | -568.6692 | -489.1185 | 750.081 | 4.284 | 10.543
22445 | -501.0827 | -749.9488 | 901.9462 | -3.954 | 4.282
22455 | 186.6252 | -450.6278 | 487.7441 | 5.271 | -6.259
22465 | 410.028 | -9.8405 | 410.1461 | 7.577 | -1.647
22475 | 739.9715 | -198.2917 | 766.0792 | -0.659 | -6.26
22485 | 790.0004 | -190.4228 | 812.6263 | 2.636 | -2.636
22495 | 706.6375 | 112.3125 | 715.5073 | 6.589 | -1.318
22505 | 407.3127 | -401.94 | 572.2406 | -6.259 | 2.966
22515 | -83.0623 | -535.2619 | 541.6684 | -0.989 | 7.577
22525 | -351.6287 | -359.2999 | 502.7317 | 1.977 | 6.259
22535 | -528.9925 | -152.9427 | 550.6583 | 3.295 | 6.59
22545 | -991.6459 | -53.425 | 993.084 | 2.635 | 12.189
22555 | -1068.4072 | -338.5784 | 1120.7717 | -3.294 | 7.248
22565 | -736.2534 | -83.183 | 740.9376 | 4.941 | 1.318
22575 | -218.3916 | 79.2468 | 232.3251 | 3.295 | -3.624
22585 | 124.3274 | 134.7483 | 183.3424 | 2.965 | -3.624
22595 | 325.1255 | 179.3853 | 371.3296 | 2.965 | -3.624
22605 | 592.0726 | -49.6872 | 594.1538 | -1.648 | -5.93
22615 | 235.5623 | -535.0803 | 584.6371 | -6.917 | 3.624
22625 | -226.0967 | -606.4999 | 647.2726 | -2.307 | 6.259
22635 | -245.1473 | -561.0771 | 612.2946 | -1.648 | 1.648
22645 | 250.0539 | -505.9922 | 564.4068 | -0.987 | -6.259
22655 | 811.1288 | -415.7937 | 911.4902 | 0 | -9.554
22665 | 1139.9111 | -604.3063 | 1290.1873 | -4.283 | -8.896
22675 | 250.5711 | -613.2317 | 662.4493 | -1.647 | 9.883
22685 | 723.6631 | -144.5688 | 737.9624 | 5.93 | -10.542
22695 | 1015.8709 | 521.6323 | 1141.9693 | 11.201 | -6.26
22705 | 1830.146 | 17.9034 | 1830.2335 | -5.272 | -18.449
22715 | 845.8893 | -279.0949 | 890.7428 | -2.305 | 9.554
22725 | 628.3169 | -773.2084 | 996.3099 | -8.896 | -1.977
22735 | 2194.1737 | -267.4712 | 2210.4161 | 6.259 | -28.003
22745 | 2694.9477 | -29.1121 | 2695.1049 | 2.307 | -15.813
22755 | 2355.666 | -492.1645 | 2406.5303 | -6.918 | -7.248
22765 | 3065.6136 | -763.7705 | 3159.3246 | -5.272 | -23.392
22775 | 3874.0918 | -1186.4903 | 4051.7091 | -10.212 | -26.026
22785 | 2543.7756 | -1550.0256 | 2978.8208 | -10.873 | 5.93
22795 | 842.8363 | -1233.2161 | 1493.7185 | -1.318 | 16.143
22805 | 462.1037 | -155.0418 | 487.4195 | 12.52 | 4.283
22815 | 77.007 | 715.4179 | 719.5505 | 14.166 | 8.895
22825 | 538.484 | 696.7836 | 880.6091 | 4.613 | -4.941
22835 | 398.2487 | 635.6418 | 750.095 | 4.942 | 4.282
22845 | 379.6723 | 689.8264 | 787.4081 | 5.6 | 0.659
22855 | 425.6743 | 426.4409 | 602.5367 | 0 | 0.33
22865 | -81.7704 | 261.8063 | 274.279 | 0.659 | 9.224
22875 | -690.8995 | 34.3052 | 691.7506 | -1.977 | 12.519
22885 | -507.2374 | -149.6762 | 528.8599 | -2.306 | 2.306
22895 | -1024.0808 | -90.5569 | 1028.0768 | 0.659 | 14.496
22905 | -1322.591 | -105.4023 | 1326.7843 | -0.659 | 11.202
22915 | -1192.135 | -99.4173 | 1196.2732 | 0 | 6.26
22925 | -985.1654 | 372.2551 | 1053.1499 | 7.907 | 4.282
22935 | -1105.172 | 761.6824 | 1342.224 | 8.236 | 8.236
22945 | -819.537 | 729.8552 | 1097.4195 | 3.624 | 0.989
22955 | -846.4426 | 391.419 | 932.5631 | -1.317 | 5.601
22965 | -607.4593 | 79.9804 | 612.702 | -2.636 | 0
22975 | -401.4584 | -244.5629 | 470.0849 | -4.943 | 0
22985 | -614.3547 | -65.7956 | 617.8679 | 1.978 | 5.6
22995 | -724.987 | -101.9126 | 732.115 | -1.647 | 4.283
23005 | -713.509 | 125.8867 | 724.5292 | 3.624 | 3.295
23015 | -916.3384 | 131.0678 | 925.6645 | 0.329 | 6.919
23025 | -972.166 | -4.4513 | 972.1762 | -1.318 | 4.941
23035 | -989.1304 | -38.6675 | 989.8859 | -0.329 | 4.942
23045 | -898.687 | 126.1705 | 907.5006 | 2.635 | 2.964
23055 | -736.4675 | 370.0018 | 824.1879 | 4.613 | 1.318
23065 | -610.6538 | 632.6706 | 879.301 | 6.259 | 0.989
23075 | -496.4805 | 507.7998 | 710.1786 | 0.989 | 0.33
23085 | -380.0374 | 443.4666 | 584.0301 | 1.976 | -0.33
23095 | -433.5966 | 664.1877 | 793.1906 | 5.93 | 1.977
23105 | -563.2719 | 787.5306 | 968.2353 | 4.942 | 3.294
23115 | -668.3267 | 662.0863 | 940.7544 | 1.647 | 3.624
23125 | -696.1289 | 659.5686 | 958.9714 | 3.295 | 2.965
23135 | -978.6821 | 496.847 | 1097.5771 | 0 | 7.578
23145 | -1071.9296 | 249.4882 | 1100.5805 | -1.977 | 5.271
23155 | -1087.1825 | 237.7687 | 1112.8791 | 0.659 | 4.942
23165 | -1281.8892 | 276.4713 | 1311.3643 | 0.988 | 7.907
23175 | -1386.1132 | 313.0031 | 1421.014 | 1.318 | 6.917
23185 | -1466.3837 | 469.8448 | 1539.8166 | 3.624 | 7.249
23195 | -1400.2691 | 358.3432 | 1445.3939 | -0.33 | 4.942
23205 | -1252.6543 | 304.8757 | 1289.2215 | 0.66 | 3.294
23215 | -1101.9096 | 386.8272 | 1167.8357 | 2.306 | 2.306
23225 | -776.942 | 298.1824 | 832.1968 | -0.33 | -1.647
23235 | -692.2527 | 136.8408 | 705.6481 | -1.647 | 0.989
23245 | -687.919 | 124.1343 | 699.0292 | 0 | 1.317
23255 | -771.8447 | 227.8834 | 804.7826 | 1.647 | 2.965
23265 | -737.3565 | 128.2578 | 748.4281 | -1.318 | 1.318
23275 | -827.4418 | -7.1073 | 827.4723 | -1.976 | 3.624
23285 | -907.7928 | 1.6931 | 907.7944 | -0.33 | 3.624
23295 | -1029.9229 | -18.2114 | 1030.0839 | -0.988 | 4.942
23305 | -1005.7407 | -26.3906 | 1006.0869 | -0.659 | 2.965
23315 | -991.9181 | -12.0916 | 991.9918 | -0.329 | 3.294
23325 | -898.6866 | -42.8488 | 899.7075 | -0.989 | 1.647
23335 | -538.413 | -33.8247 | 539.4745 | -0.329 | -3.293
23345 | -172.3209 | -4.075 | 172.3691 | 0 | -4.943
23355 | -123.7446 | -5.4522 | 123.8646 | -0.33 | -1.647
23365 | -0.37925 | 45.6644 | 45.666 | 0.659 | -3.624
23375 | -112.4398 | -9.3117 | 112.8248 | -0.988 | 0.329
23385 | -249.4933 | 129.8093 | 281.2425 | 2.306 | 0.989
23395 | -207.5358 | 155.6918 | 259.4437 | 0.659 | -0.989
23405 | -116.2466 | 207.4773 | 237.8236 | 1.647 | -1.647
23415 | -91.0096 | 120.6053 | 151.0907 | -0.659 | -0.988
23425 | -77.4969 | 63.7188 | 100.3288 | -0.329 | -0.989
23435 | -42.3043 | 56.5362 | 70.6116 | 0 | -1.317
23445 | -68.7363 | 34.7742 | 77.032 | -0.329 | -0.33
23455 | -186.1071 | 15.8547 | 186.7812 | -0.33 | 1.318
23465 | -268.9461 | 60.9512 | 275.7663 | 0.659 | 1.318
23475 | -296.0059 | 97.335 | 311.5984 | 0.659 | 0.988
23485 | -329.3115 | 155.7657 | 364.2925 | 1.318 | 1.318
23495 | -393.7916 | 256.8004 | 470.1258 | 2.306 | 1.977
23505 | -306.8539 | 368.4184 | 479.4699 | 2.965 | -0.33
23515 | -269.1022 | 330.7428 | 426.388 | 0.988 | 0.33
23525 | -122.9591 | 310.9706 | 334.3974 | 1.318 | -1.977
23535 | -102.7991 | 329.8798 | 345.5262 | 1.647 | -0.329
23545 | -242.04 | 366.801 | 439.4615 | 1.977 | 1.976
23555 | -401.7575 | 318.2521 | 512.5363 | 0.659 | 2.966
23565 | -408.7145 | 334.896 | 528.3965 | 1.647 | 1.317
23575 | -512.5653 | 283.0578 | 585.5296 | 0.329 | 3.295
23585 | -527.0059 | 218.212 | 570.3961 | 0 | 1.976
23595 | -485.1103 | 197.1545 | 523.6429 | 0.33 | 1.318
23605 | -440.3776 | 129.6163 | 459.0565 | -0.659 | 0.988
23615 | -394.5728 | 56.3442 | 398.5754 | -0.989 | 0.66
23625 | -345.4717 | 45.5417 | 348.4605 | -0.329 | 0.329
23635 | -389.0769 | 23.2977 | 389.7738 | -0.659 | 1.647
23645 | -332.871 | 78.0846 | 341.9069 | 0.659 | 0
23655 | -201.3779 | 65.0752 | 211.6314 | -0.329 | -1.318
23665 | -147.1454 | 61.7596 | 159.5808 | 0 | -0.658
23675 | -100.0179 | 121.2358 | 157.1677 | 0.988 | -0.989
23685 | -118.9904 | 204.7889 | 236.8485 | 1.648 | 0
23695 | -117.0472 | 261.1825 | 286.2103 | 1.646 | -0.329
23705 | -144.8315 | 239.1735 | 279.6071 | 0.66 | 0.329
23715 | -243.0022 | 333.8305 | 412.9078 | 2.635 | 1.647
23725 | -313.9015 | 263.3164 | 409.719 | 0 | 1.648
23735 | -297.6697 | 173.2685 | 344.426 | -0.329 | 0.658
23745 | -183.5178 | 121.2891 | 219.9769 | -0.33 | -0.988
23755 | -99.6731 | 70.2154 | 121.9218 | -0.659 | -0.988
23765 | -107.5459 | 71.6598 | 129.2333 | 0 | 0
23775 | -80.6939 | -18.9509 | 82.8893 | -1.646 | -0.659
23785 | -71.3515 | 38.7134 | 81.1774 | 0.658 | -0.329
23795 | -47.7886 | 135.9683 | 144.122 | 1.318 | -0.66
23805 | -103.3459 | 311.3082 | 328.014 | 3.294 | 0.66
23815 | -52.7755 | 400.5672 | 404.0288 | 2.636 | -0.989
23825 | -39.0043 | 411.0851 | 412.9314 | 1.977 | -0.329
23835 | 38.4852 | 360.7136 | 362.7608 | 0.988 | -1.648
23845 | 45.7081 | 345.8283 | 348.8359 | 1.318 | -0.658
23855 | 98.8756 | 364.8193 | 377.9808 | 1.647 | -1.648
23865 | 70.5543 | 362.448 | 369.2512 | 1.318 | -0.329
23875 | 3.4485 | 301.4644 | 301.4841 | 0.329 | 0.329
23885 | -19.8185 | 198.6791 | 199.6651 | -0.658 | 0
23895 | 29.4258 | 185.0711 | 187.3958 | 0.329 | -0.988
23905 | 50.4686 | 148.5291 | 156.8693 | -0.329 | -0.659
23915 | 20.9234 | 172.5445 | 173.8085 | 0.658 | 0
23925 | 17.5993 | 177.0913 | 177.9636 | 0.33 | -0.329
23935 | 2.3198 | 172.929 | 172.9446 | 0.329 | 0
23945 | -10.2434 | 208.4108 | 208.6624 | 0.989 | 0
23955 | -16.9062 | 197.8211 | 198.5422 | 0.329 | 0
23965 | 17.6629 | 125.6164 | 126.8521 | -0.658 | -0.66
23975 | 26.5486 | 129.6456 | 132.336 | 0.329 | -0.329
23985 | 85.7706 | 219.5882 | 235.7447 | 1.647 | -1.317
23995 | 134.3468 | 285.2527 | 315.3064 | 1.648 | -1.318
24005 | 164.7226 | 381.2688 | 415.3305 | 2.635 | -1.318
24015 | 186.6656 | 395.3825 | 437.2314 | 1.647 | -1.318
24025 | 126.9415 | 396.281 | 416.1163 | 1.648 | 0
24035 | 118.4865 | 479.7082 | 494.1245 | 2.964 | -0.659
24045 | 86.0673 | 529.2083 | 536.1614 | 2.636 | 0
24055 | 97.5453 | 731.2724 | 737.7495 | 5.601 | -0.659
24065 | 93.6944 | 777.1187 | 782.7465 | 3.624 | -0.329
24075 | 144.7828 | 807.2313 | 820.1125 | 3.953 | -1.318
24085 | 226.0647 | 842.312 | 872.1208 | 3.954 | -1.977
24095 | 282.6482 | 756.6658 | 807.7333 | 1.976 | -1.976
24105 | 300.4376 | 710.5012 | 771.4109 | 2.306 | -1.648
24115 | 331.5804 | 655.9473 | 734.9915 | 1.648 | -1.976
24125 | 301.6251 | 540.9155 | 619.3281 | 0.329 | -0.989
24135 | 372.6519 | 478.0469 | 606.1339 | 0.659 | -2.635
24145 | 380.9852 | 424.7785 | 570.6019 | 0.33 | -1.648
24155 | 357.5028 | 423.5834 | 554.2844 | 0.987 | -1.318
24165 | 460.6446 | 446.3095 | 641.3935 | 1.319 | -3.294
24175 | 452.3368 | 459.7406 | 644.9574 | 1.318 | -1.647
24185 | 450.1468 | 388.9464 | 594.9046 | 0 | -1.977
24195 | 498.0436 | 388.5269 | 631.6649 | 0.987 | -2.636
24205 | 441.3509 | 380.1209 | 582.4796 | 0.66 | -0.988
24215 | 430.4922 | 444.6326 | 618.8874 | 1.977 | -1.647
24225 | 378.7898 | 439.2566 | 580.0242 | 0.988 | -0.66
24235 | 394.7578 | 346.2588 | 525.0989 | -0.33 | -1.646
24245 | 436.4749 | 258.1977 | 507.1256 | -0.658 | -1.977
24255 | 445.2003 | 239.6991 | 505.6273 | 0 | -1.647
24265 | 371.3606 | 231.9408 | 437.8416 | 0 | -0.33
24275 | 314.8254 | 183.3512 | 364.325 | -0.66 | -0.33
24285 | 417.2901 | 46.9924 | 419.9277 | -2.306 | -2.635
24295 | 330.2605 | -56.7522 | 335.1012 | -2.306 | 0.33
24305 | 184.691 | -46.992 | 190.5755 | -0.989 | 1.318
24315 | 186.1251 | -35.2558 | 189.4348 | -0.987 | -0.33
24325 | 221.7455 | 0.70459 | 221.7466 | -0.33 | -0.659
24335 | 240.2679 | 43.3988 | 244.1559 | 0 | -0.659
24345 | 325.6583 | 48.9241 | 329.3127 | -0.33 | -1.976
24355 | 314.2259 | 46.1712 | 317.5999 | -0.329 | -0.66
24365 | 368.9391 | -14.1362 | 369.2098 | -1.317 | -1.977
24375 | 381.4496 | -63.2175 | 386.6526 | -1.318 | -1.317
24385 | 401.0581 | -75.2329 | 408.0535 | -0.989 | -1.647
24395 | 419.8662 | -198.3263 | 464.35 | -2.965 | -1.647
24405 | 452.2985 | -183.9728 | 488.2826 | -0.989 | -1.977
24415 | 343.4532 | -175.9266 | 385.8889 | -1.318 | 0.329
24425 | 235.1813 | -144.9249 | 276.249 | -0.658 | 0.659
24435 | 207.9772 | -103.4897 | 232.3029 | -0.329 | 0
24445 | 215.3042 | -97.8878 | 236.512 | -0.659 | -0.33
24455 | 333.8348 | -138.4627 | 361.4106 | -1.318 | -2.305
24465 | 328.1633 | -189.9818 | 379.1889 | -1.647 | -0.659
24475 | 285.1609 | -206.695 | 352.1925 | -1.319 | -0.33
24485 | 201.7149 | -81.44 | 217.5348 | 0.989 | 0.659
24495 | 255.999 | 54.1736 | 261.6682 | 1.648 | -1.318
24505 | 271.2733 | -14.0292 | 271.6358 | -0.989 | -0.658
24515 | 211.4194 | -81.6444 | 226.6362 | -0.988 | 0.329
24525 | 69.093 | -78.1408 | 104.3064 | -0.33 | 1.977
24535 | 61.0316 | -50.4066 | 79.1561 | 0 | 0.329
24545 | 52.7392 | -89.8593 | 104.1927 | -0.988 | 0.659
24555 | 36.5146 | -86.9868 | 94.3399 | -0.329 | 0.659
24565 | 23.1877 | -39.0403 | 45.4072 | 0.329 | 0.658
24575 | 11.3759 | -4.8494 | 12.3664 | 0.329 | 0.66
24585 | -95.2202 | 53.5679 | 109.2538 | 0.989 | 2.306
24595 | -142.6592 | 1.2846 | 142.665 | -0.66 | 1.647
24605 | -224.4929 | -27.8032 | 226.208 | -0.329 | 2.636
24615 | -253.6101 | -115.0848 | 278.5006 | -1.647 | 1.976
24625 | -404.1666 | -106.5188 | 417.9676 | -0.33 | 4.283
24635 | -490.3513 | -48.7891 | 492.7725 | 0.33 | 3.624
24645 | -483.4436 | -68.622 | 488.2896 | -0.659 | 2.636
24655 | -576.1349 | 3.1737 | 576.1436 | 0.988 | 4.283
24665 | -622.5429 | 431.1765 | 757.2799 | 7.248 | 3.624
24675 | -803.9849 | 815.6453 | 1145.2811 | 8.237 | 6.259
24685 | -915.125 | 734.1608 | 1173.2203 | 2.635 | 5.601
24695 | -1002.7861 | 584.6784 | 1160.788 | 1.648 | 5.93
24705 | -1055.463 | 393.2527 | 1126.3435 | -0.33 | 5.601
24715 | -1059.0459 | 323.3601 | 1107.312 | 0.659 | 4.941
24725 | -1068.0341 | 334.9176 | 1119.3153 | 1.318 | 4.942
24735 | -1143.7872 | 231.1989 | 1166.9199 | -0.659 | 5.93
24745 | -1153.0247 | 260.534 | 1182.093 | 1.317 | 4.943
24755 | -1022.0723 | 243.6365 | 1050.7096 | 0.33 | 2.635
24765 | -967.1084 | 218.2804 | 991.4359 | 0.33 | 3.294
24775 | -796.4197 | 184.4438 | 817.4985 | 0 | 0.659
24785 | -646.5761 | 139.9803 | 661.555 | -0.33 | 0.329
24795 | -631.9792 | 185.1833 | 658.5519 | 0.989 | 1.648
24805 | -575.6665 | 129.01 | 589.9454 | -0.659 | 0.659
24815 | -485.7877 | 92.8906 | 494.5891 | -0.33 | 0
24825 | -363.8028 | -1.3644 | 363.8053 | -1.647 | -0.989
24835 | -294.0762 | -56.8844 | 299.5274 | -1.318 | -0.658
24845 | -211.2047 | -127.699 | 246.8086 | -1.976 | -1.318
24855 | -145.245 | -68.5176 | 160.5951 | 0 | -1.318
24865 | -117.0941 | -73.8337 | 138.4284 | -0.989 | -0.988
24875 | 58.7636 | -75.808 | 95.9167 | -0.659 | -3.624
24885 | 125.8883 | -113.2109 | 169.3062 | -1.318 | -2.306
24895 | 158.6043 | -146.2356 | 215.7317 | -1.318 | -2.307
24905 | 114.8788 | -91.5024 | 146.8667 | 0 | -0.988
24915 | 122.597 | -85.9477 | 149.7232 | -0.658 | -1.647
24925 | 163.3537 | 155.829 | 225.759 | 3.624 | -1.977
24935 | 139.1797 | 118.5423 | 182.8203 | -0.33 | -0.989
24945 | 157.8723 | 165.5484 | 228.7574 | 1.648 | -1.647
24955 | 125.5705 | 129.8943 | 180.6668 | 0 | -0.659
24965 | 194.9804 | 129.1075 | 233.8506 | 0.658 | -2.306
24975 | 279.5623 | 179.1143 | 332.0196 | 1.318 | -2.636
24985 | 317.2756 | 63.2912 | 323.5268 | -1.318 | -2.306
24995 | 400.1447 | -15.3734 | 400.4399 | -0.988 | -3.294
25005 | 641.7028 | 309.3664 | 712.3834 | 5.271 | -6.26
25015 | 654.0491 | 571.5103 | 868.5645 | 5.271 | -3.294
25025 | 560.1471 | 437.069 | 710.4886 | 0.329 | -1.977
25035 | 505.6847 | 294.3369 | 585.1079 | 0 | -1.977
25045 | 444.0265 | 200.9534 | 487.3826 | -0.329 | -1.317
25055 | 307.968 | -68.2649 | 315.4431 | -3.953 | 0.329
25065 | 268.5313 | -118.5814 | 293.5484 | -1.318 | -0.659
25075 | 237.8587 | 70.0842 | 247.9689 | 1.976 | -0.329
25085 | 173.7204 | 54.2291 | 181.9878 | -0.658 | 0.329
25095 | 164.5808 | 181.0702 | 244.6901 | 2.306 | -0.329
25105 | 241.5138 | 313.2695 | 395.5588 | 2.636 | -1.648
25115 | 260.6278 | 240.7484 | 354.8051 | 0 | -0.988
25125 | 301.3665 | 95.8437 | 316.24 | -1.318 | -1.647
25135 | 277.891 | 173.9526 | 327.8459 | 1.647 | -0.659
25145 | 157.7439 | 81.5403 | 177.5724 | -1.318 | 0.988
25155 | 108.1242 | -50.4203 | 119.3024 | -1.976 | 0.33
25165 | -9.9667 | -230.7914 | 231.0065 | -3.625 | 1.976
25175 | 164.9917 | -304.3347 | 346.1818 | -2.635 | -2.635
25185 | 280.4411 | -478.8789 | 554.9524 | -4.942 | -1.977
25195 | 181.2962 | -467.583 | 501.4999 | -2.306 | 0.659
25205 | 250.3622 | -55.8828 | 256.5231 | 4.283 | -1.977
25215 | 211.0419 | -56.0043 | 218.3465 | -0.988 | 0
25225 | 201.2155 | -26.9965 | 203.0185 | 0.659 | -0.658
25235 | 71.8873 | 193.5 | 206.422 | 3.624 | 1.647
25245 | 44.1454 | 110.0569 | 118.5805 | -0.659 | 0.329
25255 | 119.3351 | -4.6237 | 119.4247 | -0.989 | -0.988
25265 | 250.4463 | 164.4159 | 299.593 | 2.966 | -2.306
25275 | 341.0757 | 80.3332 | 350.4084 | -0.989 | -2.306
25285 | 300.5404 | 59.745 | 306.4213 | 0.329 | -0.659
25295 | 147.6436 | 223.678 | 268.0121 | 2.966 | 1.317
25305 | -18.3802 | 254.2413 | 254.9048 | 1.318 | 2.306
25315 | -51.1907 | 4.6322 | 51.3999 | -2.966 | 0.989
25325 | 35.2402 | 83.1371 | 90.2975 | 1.648 | -0.659
25335 | 58.9609 | -140.1848 | 152.0795 | -3.954 | 0
25345 | 79.8871 | -268.6301 | 280.2572 | -2.636 | -0.33
25355 | 134.6204 | -155.4277 | 205.622 | 0.33 | -0.988
25365 | 231.8745 | -160.8692 | 282.2139 | -1.318 | -1.976
25375 | 90.3243 | -76.359 | 118.2759 | 0.659 | 1.647
25385 | 4.8939 | -118.9536 | 119.0542 | -1.317 | 0.988
25395 | 196.478 | -189.3697 | 272.8818 | -1.648 | -2.965
25405 | 159.5678 | -175.901 | 237.4932 | -0.659 | 0.33
25415 | -76.7772 | -216.9961 | 230.1783 | -1.648 | 3.294
25425 | -207.3623 | -122.377 | 240.7805 | 0.66 | 2.636
25435 | -259.8917 | -156.5172 | 303.3831 | -1.318 | 2.306
25445 | -355.0826 | -49.3948 | 358.5017 | 1.318 | 3.294
25455 | -278.9143 | 27.6316 | 280.2797 | 0.988 | 0.659
25465 | -288.1624 | -8.8052 | 288.2969 | -0.329 | 1.977
25475 | -318.3676 | -79.7865 | 328.2131 | -0.988 | 1.976
25485 | -281.5876 | 66.4256 | 289.3164 | 2.306 | 0.989
25495 | -291.4958 | 57.4441 | 297.1021 | 0 | 1.647
25505 | -252.0538 | -14.4208 | 252.466 | -0.66 | 0.659
25515 | -296.0956 | -77.8184 | 306.1508 | -0.988 | 1.977
25525 | -436.7166 | -156.7301 | 463.9889 | -1.647 | 3.624
25535 | -348.2727 | -78.4333 | 356.9954 | 0.658 | 0.329
25545 | -357.8353 | -46.4038 | 360.8315 | 0 | 1.977
25555 | -294.6138 | -58.3096 | 300.3286 | -0.329 | 0.33
25565 | -372.755 | -125.3432 | 393.2648 | -1.317 | 2.635
25575 | -26.2739 | 131.3196 | 133.9222 | 3.953 | -4.612
25585 | -23.6871 | 152.6295 | 154.4566 | 0.659 | 0.329
25595 | -24.9288 | 240.5213 | 241.8097 | 2.635 | -0.659
25605 | 18.4876 | 287.8886 | 288.4816 | 1.977 | -0.988
25615 | -6.1873 | 216.5928 | 216.6812 | 0.33 | 0
25625 | -85.8847 | 66.772 | 108.7873 | -1.318 | 0.988
25635 | -140.4842 | -93.3136 | 168.6513 | -2.306 | 0.989
25645 | -190.8139 | -64.9409 | 201.5621 | 0 | 1.318
25655 | -91.7633 | -6.8254 | 92.0168 | 0.329 | -0.989
25665 | -66.0139 | 5.0596 | 66.2075 | 0 | 0
25675 | 69.7955 | 45.2324 | 83.1708 | 0.659 | -2.306
25685 | 122.9139 | 0.23366 | 122.9142 | -0.659 | -1.318
25695 | 202.7579 | 150.3612 | 252.4268 | 2.635 | -2.306
25705 | 288.3742 | 10.4307 | 288.5628 | -1.976 | -2.635
25715 | 368.1777 | -69.672 | 374.7119 | -0.988 | -2.966
25725 | 427.232 | -157.7133 | 455.4127 | -1.977 | -2.965
25735 | 490.1627 | -91.7483 | 498.6754 | 0.33 | -3.294
25745 | 329.2554 | -68.1334 | 336.231 | -0.33 | 0.329
25755 | 200.1744 | -105.7417 | 226.3871 | -0.988 | 0.33
25765 | 304.5213 | 133.3057 | 332.4209 | 3.624 | -2.636
25775 | 380.3653 | 155.3544 | 410.8683 | 0.658 | -2.306
25785 | 246.5181 | 132.9029 | 280.0613 | 0.66 | 0.659
25795 | 156.7535 | 32.944 | 160.1779 | -0.989 | 0.329
25805 | 92.4094 | -23.0628 | 95.2438 | -0.659 | 0.659
25815 | 181.734 | -12.2889 | 182.149 | 0 | -1.647
25825 | 219.8831 | -20.113 | 220.801 | -0.329 | -0.988
25835 | 58.5563 | -69.4572 | 90.8468 | -0.989 | 1.976
25845 | -69.5955 | -68.6707 | 97.7711 | -0.329 | 1.977
25855 | -125.807 | -100.3746 | 160.9424 | -0.989 | 1.647
25865 | -104.6282 | -148.88 | 181.9679 | -1.317 | 0.659
25875 | -11.329 | -163.885 | 164.2761 | -0.989 | -0.659
25885 | 14.7147 | -152.6097 | 153.3175 | -0.658 | 0
25895 | -37.9959 | -203.5237 | 207.04 | -1.648 | 0.988
25905 | -79.8963 | -248.042 | 260.5921 | -1.647 | 0.989
25915 | 29.4821 | -26.6062 | 39.7125 | 2.636 | -1.318
25925 | 176.1458 | -22.1891 | 177.5378 | -0.33 | -2.306
25935 | 233.9125 | 38.9839 | 237.1388 | 1.318 | -1.647
25945 | 110.5928 | 24.828 | 113.3455 | 0 | 0.988
25955 | -5.8588 | -131.9191 | 132.0492 | -2.306 | 1.318
25965 | -112.7251 | -209.2234 | 237.6581 | -1.647 | 1.976
25975 | -244.4101 | -170.2262 | 297.8477 | -0.33 | 2.966
25985 | -281.4251 | -233.5139 | 365.6896 | -1.976 | 1.976
25995 | -164.5437 | -83.5906 | 184.559 | 1.647 | -0.329
26005 | 114.7281 | 142.4327 | 182.8923 | 3.294 | -3.624
26015 | 5.741 | 23.2549 | 23.9531 | -1.317 | 1.647
26025 | -22.7619 | -38.2156 | 44.4807 | -0.331 | 0
26035 | -10.9182 | -149.6108 | 150.0087 | -1.976 | 0
26045 | -25.3238 | -44.2593 | 50.992 | 1.318 | 0.33
26055 | 39.3104 | -136.6059 | 142.1495 | -1.977 | -0.989
26065 | -41.2589 | -118.9891 | 125.9393 | 0 | 1.318
26075 | 56.6581 | -44.4829 | 72.0338 | 0.659 | -1.647
26085 | -1.9685 | -73.4825 | 73.5089 | -0.659 | 0.988
26095 | -165.9769 | -9.7179 | 166.2612 | 0.989 | 2.636
26105 | -106.0148 | 68.6798 | 126.3173 | 1.317 | -0.33
26115 | -19.3319 | 41.9002 | 46.1448 | 0 | -0.658
26125 | -47.5057 | 33.2647 | 57.9943 | 0.329 | 0.658
26135 | -21.6848 | 93.953 | 96.423 | 1.318 | -0.329
26145 | -88.9405 | 27.3558 | 93.0524 | -0.658 | 1.317
26155 | -149.0188 | -91.3972 | 174.8143 | -1.647 | 1.318
26165 | -241.664 | 22.0038 | 242.6636 | 1.647 | 2.306
26175 | -215.4917 | 49.2272 | 221.0429 | 0.329 | 0.66
26185 | -203.9153 | -11.4662 | 204.2374 | -0.658 | 0.988
26195 | -283.7359 | 2.2041 | 283.7444 | 0.329 | 2.306
26205 | -194.806 | 3.8221 | 194.8435 | 0 | -0.33
26215 | -286.6838 | 114.9006 | 308.8523 | 1.977 | 2.636
26225 | -323.1378 | 89.3027 | 335.2507 | 0 | 1.648
26235 | -294.1482 | 32.4758 | 295.9356 | -0.33 | 0.988
26245 | -197.9739 | 95.9629 | 220.0058 | 1.317 | -0.33
26255 | -167.6059 | 115.0674 | 203.3033 | 0.66 | 0.33
26265 | -119.95 | 118.1247 | 168.3492 | 0.659 | -0.33
26275 | -177.6745 | 7.6914 | 177.8409 | -1.319 | 1.318
26285 | -152.9245 | -78.9653 | 172.1088 | -1.317 | 0
26295 | -82.0846 | -129.4345 | 153.2683 | -1.318 | -0.659
26305 | -72.1584 | -67.4601 | 98.7811 | 0.329 | 0
26315 | -110.9056 | -92.9083 | 144.6789 | -0.987 | 0.659
26325 | -119.1813 | -108.4467 | 161.1362 | -0.66 | 0.33
26335 | -80.2301 | 20.6226 | 82.8382 | 1.647 | -0.33
26345 | -49.8217 | -70.4242 | 86.2657 | -1.647 | -0.329
26355 | 7.0357 | -29.6219 | 30.446 | 0.66 | -0.989
26365 | 12.0436 | 63.6625 | 64.7916 | 1.317 | -0.329
26375 | 9.7198 | 66.1348 | 66.8453 | 0.33 | -0.329
26385 | 69.831 | 38.8043 | 79.8883 | 0 | -1.318
26395 | 42.4088 | 118.6705 | 126.0206 | 1.646 | 0
26405 | -102.4137 | -158.888 | 189.0343 | -4.282 | 1.976
26415 | 22.9998 | -27.2433 | 35.6537 | 1.976 | -1.976
26425 | 67.0581 | 11.5614 | 68.0475 | 0 | -0.659
26435 | 16.1419 | -75.2059 | 76.9187 | -1.318 | 0.329
26445 | -20.8902 | -119.3094 | 121.1244 | -0.987 | 0.33
26455 | 113.2829 | -26.3963 | 116.3175 | 0.987 | -2.306
26465 | 146.5418 | -9.184 | 146.8293 | 0 | -0.989
26475 | 73.9874 | 6.3549 | 74.2598 | 0.331 | 0.329
26485 | 21.5691 | -35.9528 | 41.9265 | -0.66 | 0.33
26495 | 12.833 | -91.0489 | 91.9488 | -0.988 | 0
26505 | -66.0828 | -30.5489 | 72.8023 | 0.659 | 1.318
26515 | -71.9217 | 99.8363 | 123.0447 | 1.976 | 0.329
26525 | 50.5164 | 94.4086 | 107.0742 | 0.33 | -1.647
26535 | -11.1064 | 54.9502 | 56.0614 | 0 | 0.988
26545 | -60.1988 | 90.9737 | 109.0876 | 0.989 | 0.659
26555 | -43.3686 | 29.5475 | 52.4775 | -0.659 | 0
26565 | 10.6546 | 128.0852 | 128.5276 | 1.977 | -0.659
26575 | 10.1326 | 104.2715 | 104.7626 | 0 | 0
26585 | 59.8098 | 142.8971 | 154.909 | 1.317 | -0.988
26595 | 45.0583 | 185.8306 | 191.2152 | 1.318 | 0
26605 | 44.7351 | 250.4853 | 254.4487 | 1.977 | -0.33
26615 | 31.833 | 107.7162 | 112.3215 | -1.319 | 0
26625 | 20.8074 | 65.1492 | 68.3913 | 0 | 0
26635 | 53.4758 | 78.8878 | 95.3045 | 0.331 | -0.658
26645 | 119.0726 | -8.8893 | 119.404 | -1.318 | -1.318
26655 | 108.2108 | -43.2775 | 116.5441 | -0.66 | -0.33
26665 | 130.5482 | 20.2873 | 132.1151 | 0.66 | -0.988
26675 | 155.0107 | 49.7877 | 162.8101 | 0.329 | -0.988
26685 | 113.2757 | -35.2769 | 118.6416 | -1.318 | 0
26695 | -16.5413 | 30.4601 | 34.6617 | 0.989 | 1.647
26705 | -129.8482 | 38.9752 | 135.5715 | 0 | 1.977
26715 | 67.2172 | 86.8127 | 109.7934 | 0.987 | -2.636
26725 | 78.9008 | 51.7892 | 94.3793 | -0.329 | 0
26735 | -27.2119 | -22.4851 | 35.2997 | -0.988 | 1.318
26745 | 34.4157 | -33.7475 | 48.201 | -0.33 | -0.988
26755 | 59.7319 | -72.2783 | 93.7659 | -0.988 | -0.33
26765 | 25.4267 | -29.0435 | 38.6011 | 0.33 | 0.33
26775 | -58.3113 | 87.0212 | 104.7516 | 1.647 | 1.317
26785 | -157.3132 | 72.5246 | 173.226 | 0 | 1.977
26795 | -167.517 | 103.3229 | 196.8186 | 0.989 | 0.988
26805 | -89.5465 | 137.4107 | 164.013 | 0.988 | -0.329
26815 | -149.0663 | 216.1695 | 262.5833 | 1.976 | 1.647
26825 | -191.3874 | 65.9382 | 202.4277 | -1.647 | 1.318
26835 | -250.9041 | 14.4235 | 251.3183 | -0.329 | 1.977
26845 | -317.1724 | -54.1468 | 321.7611 | -1.319 | 2.306
26855 | -364.2702 | -72.1645 | 371.3495 | -0.658 | 2.306
26865 | -282.4087 | -116.1747 | 305.3706 | -1.318 | 0.329
26875 | -236.2726 | -116.0571 | 263.2375 | -0.659 | 0.66
26885 | -256.5359 | -207.4399 | 329.9121 | -2.306 | 1.317
26895 | -257.3735 | -35.2603 | 259.7776 | 1.977 | 0.989
26905 | -254.3904 | 18.027 | 255.0283 | 0.329 | 0.988
26915 | -273.7716 | -32.4177 | 275.6842 | -0.658 | 1.318
26925 | -155.8704 | -88.4501 | 179.2177 | -0.989 | -0.989
26935 | -175.5444 | -27.7836 | 177.7294 | 0.658 | 0.989
26945 | -269.2586 | -31.3823 | 271.0813 | -0.329 | 1.976
26955 | -159.8439 | 106.5355 | 192.0935 | 2.306 | -0.987
26965 | 54.3777 | 182.411 | 190.3437 | 1.647 | -2.966
26975 | 182.4229 | 278.0421 | 332.544 | 2.637 | -2.635
26985 | 221.0047 | -12.0921 | 221.3352 | -3.624 | -1.978
26995 | 208.2271 | -21.0145 | 209.2848 | 0.329 | -1.317
27005 | 202.963 | 45.1357 | 207.9212 | 0.658 | -1.318
27015 | 322.7227 | 214.3 | 387.3944 | 2.966 | -3.295
27025 | 249.0103 | 187.2815 | 311.5774 | 0.329 | -0.329
27035 | 194.7483 | 161.771 | 253.1734 | 0.659 | -0.659
27045 | 251.7737 | 273.2791 | 371.5797 | 2.636 | -1.976
27055 | 91.1734 | 191.2694 | 211.8882 | -0.329 | 1.647
27065 | -102.7011 | -82.2486 | 131.5763 | -3.624 | 2.635
27075 | -33.8691 | -162.0894 | 165.5901 | -1.648 | -0.658
27085 | -133.0859 | -207.808 | 246.7711 | -1.976 | 2.306
27095 | -273.3022 | -249.8809 | 370.3169 | -1.977 | 2.964
27105 | -442.3528 | -301.2608 | 535.1954 | -2.306 | 4.284
27115 | -661.6039 | -342.7388 | 745.1105 | -2.307 | 5.93
27125 | -744.205 | -354.8137 | 824.4597 | -1.977 | 4.612
27135 | -657.1985 | -307.4156 | 725.5441 | -0.987 | 2.307
27145 | -711.1392 | -255.2043 | 755.5449 | -0.66 | 4.282
27155 | -798.5377 | -129.1959 | 808.9215 | 0.989 | 4.612
27165 | -764.7689 | -229.1802 | 798.3702 | -2.306 | 2.965
27175 | -735.5805 | -231.0138 | 771.0032 | -0.66 | 2.966
27185 | -709.3047 | -113.2601 | 718.2903 | 0.989 | 2.635
27195 | -599.6748 | -47.1873 | 601.5285 | 0.659 | 0.989
27205 | -327.8162 | 122.417 | 349.9277 | 2.965 | -2.307
27215 | -303.846 | 177.4864 | 351.8861 | 1.648 | 0.66
27225 | -148.6342 | 103.3331 | 181.0245 | 0 | -2.307
27235 | -49.7046 | 107.4109 | 118.3539 | 0.987 | -1.647
27245 | -109.1105 | 147.0326 | 183.0948 | 1.319 | 0.33
27255 | -79.7744 | 137.4908 | 158.9581 | 0.658 | -0.989
27265 | -115.0823 | 108.1103 | 157.898 | 0.329 | 0.329
27275 | -109.6996 | 52.2631 | 121.5131 | -0.329 | -0.329
27285 | -74.5174 | -25.0466 | 78.6141 | -0.988 | -0.659
27295 | -163.2189 | -174.2444 | 238.7499 | -2.636 | 1.318
27305 | -197.6129 | -187.5912 | 272.4726 | -0.988 | 0.659
27315 | -322.4843 | -180.361 | 369.4945 | -0.989 | 2.635
27325 | -286.967 | -241.4613 | 375.0381 | -1.976 | 0.329
27335 | -298.039 | -216.3896 | 368.3092 | -0.659 | 1.318
27345 | -321.7548 | -112.607 | 340.8907 | 0.659 | 1.319
27355 | -316.9488 | -21.3549 | 317.6674 | 0.989 | 0.987
27365 | -331.5866 | -79.9842 | 341.0969 | -0.989 | 1.318
27375 | -403.8124 | -154.3593 | 432.3092 | -1.318 | 2.306
27385 | -344.264 | 50.9612 | 348.0154 | 2.965 | 0.331
27395 | -287.8294 | 125.3733 | 313.9494 | 1.318 | 0.329
27405 | -296.7074 | 33.2562 | 298.5654 | -0.659 | 0.988
27415 | -212.7851 | 59.9092 | 221.058 | 0.989 | -0.659
27425 | -142.379 | 138.2213 | 198.4361 | 1.647 | -0.658
27435 | -138.6169 | 134.4513 | 193.1108 | 0.658 | 0
27445 | -178.2168 | 143.0784 | 228.5446 | 0.989 | 0.658
27455 | -185.8264 | 137.5854 | 231.2167 | 0.659 | 0.329
27465 | -145.744 | 75.3044 | 164.049 | -0.329 | -0.329
27475 | -75.3917 | -47.4884 | 89.1014 | -1.648 | -0.989
27485 | -44.2054 | -38.311 | 58.4966 | 0 | -0.658
27495 | -65.06 | 23.0758 | 69.0311 | 0.659 | 0
27505 | -291.9496 | 139.1177 | 323.4012 | 1.976 | 3.624
27515 | -427.0473 | 126.589 | 445.4146 | 0.331 | 2.965
27525 | -479.982 | -109.6867 | 492.3555 | -3.295 | 2.636
27535 | -362.7927 | -210.4519 | 419.4145 | -1.977 | 0
27545 | -347.6044 | -101.027 | 361.988 | 0.659 | 1.318
27555 | -417.83 | -14.5627 | 418.0837 | 0.658 | 2.306
27565 | -374.2971 | 49.8105 | 377.5969 | 0.989 | 0.658
27575 | -388.6155 | -22.4286 | 389.2622 | -0.989 | 1.647
27585 | -354.9403 | 10.1114 | 355.0843 | 0.66 | 0.659
27595 | -169.9242 | -25.5049 | 171.8277 | -0.66 | -1.977
27605 | 103.3948 | 90.105 | 137.1473 | 1.978 | -4.282
27615 | 370.9983 | 171.5757 | 408.7517 | 1.646 | -5.601
27625 | 420.0133 | 273.1725 | 501.0333 | 2.637 | -3.295
27635 | 515.1182 | 139.0718 | 533.5614 | -0.989 | -4.611
27645 | 567.7822 | 138.1019 | 584.3362 | 0.989 | -3.954
27655 | 585.4551 | 71.2344 | 589.7729 | -0.66 | -3.624
27665 | 587.5904 | 48.9321 | 589.6243 | 0 | -3.295
27675 | 654.8717 | 6.247 | 654.9015 | -0.658 | -4.282
27685 | 716.8148 | -106.0665 | 724.6196 | -1.977 | -4.284
27695 | 820.1143 | -170.3367 | 837.6169 | -1.648 | -5.27
27705 | 807.7657 | -34.7795 | 808.5141 | 1.319 | -3.624
27715 | 542.3341 | -60.6578 | 545.7157 | -0.989 | 0.658
27725 | 270.0657 | -69.4291 | 278.8474 | -0.33 | 1.977
27735 | 61.0428 | -122.2756 | 136.6658 | -1.318 | 2.636
27745 | 134.8699 | -128.8376 | 186.5182 | -0.658 | -0.989
27755 | 113.984 | -49.5923 | 124.305 | 0.658 | 0.659
27765 | -44.7495 | 47.9269 | 65.5706 | 1.318 | 2.636
27775 | 104.2244 | 208.1749 | 232.8079 | 2.966 | -1.976
27785 | 279.6281 | 190.4124 | 338.3028 | 0.659 | -2.637
27795 | 613.1277 | 119.5405 | 624.6723 | 0 | -6.588
27805 | 879.5629 | 232.1579 | 909.6858 | 2.636 | -6.919
27815 | 1164.6379 | 294.2151 | 1201.2261 | 1.976 | -8.895
27825 | 1202.3945 | 266.6868 | 1231.6146 | 0.988 | -5.93
27835 | 1710.5509 | 111.1136 | 1714.1559 | -1.318 | -14.497
27845 | 3251.1757 | 54.8913 | 3251.6391 | -0.329 | -33.604
27855 | 5331.0318 | -118.923 | 5332.3581 | -2.965 | -49.417
27865 | 7334.4092 | 472.8941 | 7349.6386 | 9.554 | -58.642
27875 | 7521.6362 | 1063.3427 | 7596.4274 | 11.202 | -37.888
27885 | 5672.9421 | 831.8535 | 5733.6072 | 0.988 | -5.93
27895 | 3000.5262 | 1100.6897 | 3196.0406 | 9.554 | 17.461
27905 | 659.0507 | 814.8084 | 1047.9793 | -0.33 | 27.345
27915 | 1431.5236 | -1307.5925 | 1938.8291 | -31.956 | -11.86
27925 | 3452.821 | -898.7912 | 3567.8843 | 2.636 | -32.287
27935 | 3726.7614 | -2090.1123 | 4272.8586 | -28.663 | -14.166
27945 | 4790.575 | -1730.6674 | 5093.6056 | -2.635 | -33.275
27955 | 4266.9727 | -1653.1662 | 4576.0261 | -9.885 | -8.566
27965 | 2316.8302 | -882.9156 | 2479.3633 | 5.272 | 15.156
27975 | 2966.7852 | -207.8349 | 2974.0561 | 6.26 | -19.439
27985 | 3450.068 | -180.5617 | 3454.7897 | 0 | -14.165
27995 | 3041.1081 | -45.2817 | 3041.4452 | 2.964 | -4.284
28005 | 2490.3352 | 614.0205 | 2564.9153 | 11.861 | -0.658
28015 | 1654.8634 | 1081.8797 | 1977.1284 | 11.202 | 7.577
28025 | 1204.4962 | 1216.0267 | 1711.5876 | 8.565 | 4.942
28035 | 345.3214 | 1035.3549 | 1091.4241 | 3.953 | 15.155
28045 | -293.5936 | 393.6968 | 491.1155 | -4.941 | 14.496
28055 | -1018.1483 | 205.6234 | 1038.7045 | -0.33 | 19.766
28065 | -1424.2614 | 273.341 | 1450.2537 | 1.647 | 17.132
28075 | -1644.7455 | 72.6507 | 1646.3492 | -2.635 | 16.143
28085 | -1340.9213 | -659.6973 | 1494.4131 | -12.19 | 7.577
28095 | -781.2156 | -1072.6149 | 1326.9516 | -9.884 | 1.648
28105 | 198.5491 | -1150.5792 | 1167.5847 | -7.248 | -9.225
28115 | 994.8923 | -1242.129 | 1591.4444 | -7.906 | -11.201
28125 | 1602.9938 | -1491.1922 | 2189.3476 | -10.543 | -13.178
28135 | 1727.9429 | -1944.2121 | 2601.105 | -14.825 | -8.237
28145 | 2013.1122 | -1806.9944 | 2705.1524 | -6.589 | -12.189
28155 | 2250.391 | -1544.4175 | 2729.3745 | -4.613 | -11.86
28165 | 2146.122 | -2383.2447 | 3207.1319 | -21.414 | -7.248
28175 | 1371.5991 | -1940.9882 | 2376.7034 | -1.647 | 4.612
28185 | 821.407 | -1536.4475 | 1742.2343 | -2.965 | 4.282
28195 | 432.8516 | -1280.9548 | 1352.1115 | -1.647 | 5.601
28205 | 837.212 | -595.7493 | 1027.5413 | 7.248 | -5.93
28215 | 1474.0676 | -311.9585 | 1506.7161 | 3.294 | -10.872
28225 | 1807.6911 | 205.3417 | 1819.3165 | 9.884 | -9.554
28235 | 1458.8463 | 371.697 | 1505.4539 | 5.601 | -0.33
28245 | 725.2614 | 177.2133 | 746.5981 | 0.988 | 7.249
28255 | 181.9013 | 295.9844 | 347.4116 | 5.271 | 7.906
28265 | -79.5362 | 576.9839 | 582.4401 | 7.577 | 6.59
28275 | -0.75409 | 187.3569 | 187.3585 | -2.635 | 2.306
28285 | 41.8317 | -181.6762 | 186.4299 | -3.295 | 2.635
28295 | 33.7624 | -155.3011 | 158.9287 | 0.659 | 2.636
28305 | -237.196 | -366.1768 | 436.2882 | -3.953 | 6.919
28315 | -615.8288 | -553.6937 | 828.1437 | -3.954 | 9.554
28325 | -981.6408 | -838.5205 | 1291.021 | -6.918 | 11.201
28335 | -897.2004 | -1226.0093 | 1519.2325 | -9.884 | 5.271
28345 | -368.4168 | -1445.6876 | 1491.8926 | -8.895 | -2.306
28355 | -96.4574 | -1527.5275 | 1530.5699 | -7.907 | -0.659
28365 | -66.3017 | -1092.7014 | 1094.711 | 0.659 | 0.988
28375 | -215.2842 | -855.0341 | 881.7203 | -0.988 | 3.624
28385 | -175.952 | -39.6402 | 180.362 | 11.201 | 0.989
28395 | 69.95 | 381.4602 | 387.8207 | 7.578 | -2.306
28405 | 554.6906 | 252.5447 | 609.4756 | 1.647 | -7.578
28415 | 903.3677 | 260.7756 | 940.2537 | 3.624 | -7.577
28425 | 505.4853 | 223.3727 | 552.6398 | 1.977 | 2.965
28435 | 477.5894 | 579.8918 | 751.2431 | 8.565 | -2.306
28445 | 736.6293 | 882.9601 | 1149.8875 | 8.566 | -5.601
28455 | 732.4706 | 843.6374 | 1117.2454 | 4.612 | -2.306
28465 | 523.9925 | 1012.0889 | 1139.6894 | 8.237 | 0.659
28475 | -466.5604 | 450.6094 | 648.6351 | -4.284 | 15.154
28485 | -796.7973 | 217.9876 | 826.0778 | -0.329 | 7.907
28495 | -1167.0552 | -354.6581 | 1219.7541 | -8.895 | 12.19
28505 | -962.9695 | -864.2838 | 1293.9462 | -9.884 | 3.295
28515 | -231.5363 | -764.7688 | 799.0497 | -2.635 | -5.931
28525 | 351.3949 | -862.3872 | 931.2304 | -6.26 | -7.247
28535 | 684.4937 | -725.4586 | 997.4075 | -1.647 | -6.919
28545 | 1262.7214 | -161.7339 | 1273.037 | 5.93 | -13.178
28555 | 1801.8746 | -62.738 | 1802.9664 | 0.659 | -14.825
28565 | 2284.509 | 66.7457 | 2285.4838 | 2.965 | -16.802
28575 | 2406.3307 | -3.965 | 2406.3339 | -0.33 | -12.849
28585 | 2402.9861 | -57.3901 | 2403.6713 | 0 | -11.531
28595 | 2281.1013 | -55.385 | 2281.7735 | 0.33 | -8.895
28605 | 2310.5852 | 86.3833 | 2312.1994 | 2.636 | -10.543
28615 | 2644.6394 | 487.3129 | 2689.1619 | 7.577 | -15.155
28625 | 1820.7474 | 517.0055 | 1892.7271 | 2.965 | 3.624
28635 | 461.3947 | 164.2356 | 489.7534 | -2.636 | 15.155
28645 | -12.0111 | -627.1118 | 627.2268 | -11.86 | 7.577
28655 | -171.2567 | -1330.3732 | 1341.3507 | -14.167 | 6.59
28665 | 322.4746 | -1228 | 1269.6353 | -4.611 | -4.283
28675 | 836.3049 | -938.8473 | 1257.3147 | -1.977 | -6.589
28685 | 1522.7973 | -605.6893 | 1638.8322 | 0.988 | -13.178
28695 | 2547.7378 | 33.2243 | 2547.9545 | 8.237 | -22.403
28705 | 3260.9951 | 705.2655 | 3336.3885 | 11.86 | -22.073
28715 | 1988.7458 | 175.8412 | 1996.5044 | -4.942 | 7.577
28725 | 352.7483 | -746.8415 | 825.9562 | -12.519 | 17.791
28735 | -1512.2675 | -1040.3927 | 1835.5843 | -7.248 | 31.956
28745 | -2526.7485 | -2046.831 | 3251.7649 | -22.403 | 27.015
28755 | -1721.5524 | -2394.7674 | 2949.348 | -14.496 | 2.636
28765 | -2010.0127 | -2269.0252 | 3031.2747 | -9.883 | 18.779
28775 | -1692.0152 | -2068.1546 | 2672.1113 | -7.578 | 5.601
28785 | -2048.7488 | -1407.6128 | 2485.7082 | 1.977 | 17.131
28795 | -2637.8885 | -1236.6272 | 2913.3662 | -3.295 | 20.426
28805 | -2778.7834 | -881.9856 | 2915.3964 | 2.306 | 15.813
28815 | -2489.2688 | -419.6044 | 2524.3865 | 5.272 | 9.555
28825 | -1663.9361 | -47.0977 | 1664.6025 | 6.26 | -1.318
28835 | -1047.7889 | 127.7598 | 1055.5492 | 4.941 | -1.976
28845 | -517.3274 | -198.161 | 553.9814 | -2.635 | -4.943
28855 | 97.8491 | -143.5333 | 173.7131 | 2.635 | -9.224
28865 | 401.5588 | 49.5583 | 404.6054 | 3.953 | -6.918
28875 | 1182.2513 | 182.0986 | 1196.1932 | 3.954 | -17.132
28885 | 2171.1919 | 253.8005 | 2185.9755 | 3.624 | -23.391
28895 | 2753.8526 | 251.0699 | 2765.274 | 2.636 | -21.415
28905 | 2696.7073 | 196.188 | 2703.8343 | 1.647 | -13.836
28915 | 2247.9868 | -102.9746 | 2250.344 | -2.965 | -6.919
28925 | 1757.4365 | -113.0896 | 1761.0713 | 0.658 | -3.294
28935 | 1196.5766 | -33.234 | 1197.038 | 1.318 | 1.317
28945 | 364.6466 | -138.2435 | 389.9723 | -1.318 | 9.225
28955 | -164.0686 | -95.5607 | 189.8693 | 0.989 | 8.237
28965 | -406.3464 | -635.6759 | 754.4542 | -9.224 | 6.917
28975 | -745.9901 | -1078.1009 | 1311.0312 | -9.225 | 9.885
28985 | -499.9711 | -1360.5545 | 1449.5102 | -9.554 | 0.988
28995 | -147.0438 | -1634.6571 | 1641.2573 | -10.872 | -1.319
29005 | -251.3504 | -1514.7314 | 1535.444 | -5.272 | 3.955
29015 | -191.0321 | -1637.5044 | 1648.6096 | -9.224 | 0.658
29025 | -692.7625 | -1401.1981 | 1563.0982 | -2.636 | 10.543
29035 | -1327.3716 | -679.4237 | 1491.1512 | 6.26 | 14.166
29045 | -1233.6958 | -88.7678 | 1236.8852 | 7.577 | 5.271
29055 | -566.983 | 489.8238 | 749.2644 | 11.201 | -3.953
29065 | 320.0054 | 1402.3932 | 1438.4402 | 19.768 | -11.201
29075 | 840.6748 | 1713.7968 | 1908.8828 | 13.507 | -9.884
29085 | 651.1251 | 1775.4495 | 1891.0803 | 11.861 | -1.318
29095 | 130.883 | 1857.316 | 1861.9219 | 11.86 | 4.612
29105 | -328.6598 | 1627.2347 | 1660.0934 | 6.259 | 6.59
29115 | -789.3258 | 1194.7032 | 1431.9047 | 1.648 | 9.554
29125 | -1244.4458 | 609.0664 | 1385.4989 | -3.624 | 11.86
29135 | -1659.4803 | 175.4469 | 1668.729 | -4.283 | 13.507
29145 | -2013.5962 | -169.4765 | 2020.7157 | -5.601 | 14.496
29155 | -2022.6861 | -293.3411 | 2043.8464 | -3.624 | 10.214
29165 | -2152.9748 | -347.1476 | 2180.7824 | -3.294 | 12.518
29175 | -2162.9901 | -130.6892 | 2166.9347 | 1.318 | 10.214
29185 | -1747.0772 | -62.39 | 1748.1908 | -0.33 | 2.964
29195 | -1252.6024 | 118.6091 | 1258.2054 | 2.636 | -0.329
29205 | -555.9093 | 260.3405 | 613.8504 | 2.636 | -6.918
29215 | -82.4115 | 400.9967 | 409.3775 | 3.623 | -6.589
29225 | 133.8705 | 252.8409 | 286.0941 | -0.659 | -5.272
29235 | 837.7017 | 641.5322 | 1055.134 | 8.237 | -14.825
29245 | 1150.975 | 735.335 | 1365.8188 | 3.953 | -10.542
29255 | 1068.4922 | 664.9355 | 1258.497 | 2.636 | -6.26
29265 | 866.9656 | 800.7656 | 1180.1927 | 5.6 | -3.624
29275 | 506.0989 | 293.1139 | 584.852 | -5.271 | 0.659
29285 | 54.1171 | -147.8332 | 157.4272 | -5.601 | 4.283
29295 | -264.319 | -269.5788 | 377.541 | -3.295 | 4.612
29305 | -499.001 | -428.7568 | 657.9015 | -4.941 | 5.271
29315 | -584.054 | -218.1596 | 623.4682 | 0.988 | 3.953
29325 | -578.6535 | -116.5325 | 590.2708 | -0.329 | 2.966
29335 | -831.3344 | -183.9218 | 851.4365 | -1.977 | 7.248
29345 | -1025.2896 | -282.4487 | 1063.483 | -2.635 | 6.919
29355 | -1012.3495 | -81.5802 | 1015.6313 | 1.977 | 4.612
29365 | -1016.545 | -221.9718 | 1040.4976 | -3.295 | 4.942
29375 | -983.6194 | -181.4224 | 1000.2106 | 0 | 3.953
29385 | -675.8725 | -0.19402 | 675.8725 | 1.977 | -0.989
29395 | -522.4958 | 27.1458 | 523.2005 | 0.329 | 0.329
29405 | -778.9268 | -206.208 | 805.7597 | -3.624 | 5.931
29415 | -1008.3234 | -231.5675 | 1034.5721 | -0.988 | 6.26
29425 | -740.629 | 92.5925 | 746.3945 | 4.283 | -0.659
29435 | -338.393 | 203.3312 | 394.7827 | 1.976 | -3.624
29445 | 77.7157 | 28.9624 | 82.937 | -1.647 | -6.26
29455 | 401.2813 | 240.587 | 467.8769 | 4.283 | -6.918
29465 | 427.1549 | 365.1743 | 561.973 | 2.965 | -3.624
29475 | 237.7745 | 306.8013 | 388.1543 | 0.989 | -0.329
29485 | 228.6189 | 663.7539 | 702.0226 | 7.906 | -2.307
29495 | 89.1042 | 869.4155 | 873.9696 | 6.26 | 0.659
29505 | 53.9138 | 785.5551 | 787.4031 | 2.965 | -0.659
29515 | 55.5898 | 564.6885 | 567.4181 | 0.329 | -0.659
29525 | -270.1524 | 151.2249 | 309.5986 | -4.282 | 4.942
29535 | -181.1086 | 50.8506 | 188.112 | -0.989 | -0.988
29545 | -116.0122 | 199.4918 | 230.7722 | 1.977 | 0
29555 | -465.6512 | 76.4995 | 471.8932 | -1.977 | 6.259
29565 | -552.9347 | -69.381 | 557.2706 | -2.306 | 2.965
29575 | -317.4623 | -24.99 | 318.4444 | 0 | -1.318
29585 | -316.1594 | 97.1655 | 330.7536 | 1.318 | 1.648
29595 | -357.5858 | 3.296 | 357.601 | -1.647 | 1.647
29605 | -263.1675 | -108.7792 | 284.7632 | -1.977 | -0.329
29615 | -224.1298 | -139.6097 | 264.055 | -1.318 | 0.329
29625 | -229.5914 | -2.1391 | 229.6013 | 1.318 | 0.658
29635 | -253.026 | -31.3095 | 254.9558 | -0.989 | 0.989
29645 | -134.4113 | 92.8962 | 163.3894 | 1.977 | -1.318
29655 | -209.3329 | 299.3832 | 365.3089 | 3.624 | 1.648
29665 | -461.0826 | 401.076 | 611.113 | 2.965 | 4.612
29675 | -544.2378 | 324.9689 | 633.8766 | 0.659 | 2.965
29685 | -500.4193 | 340.1577 | 605.0841 | 1.977 | 1.647
29695 | -277.7393 | 315.2709 | 420.1605 | 0.988 | -1.647
29705 | 77.9673 | 444.9628 | 451.7419 | 3.624 | -4.941
29715 | 249.0382 | 518.3968 | 575.1132 | 2.965 | -3.624
29725 | 363.0465 | 326.1391 | 488.0261 | -0.988 | -3.955
29735 | 394.4838 | 193.2948 | 439.2953 | -0.659 | -2.964
29745 | 359.2033 | 105.0223 | 374.2415 | -0.988 | -1.977
29755 | 302.8095 | 121.1667 | 326.1517 | 0.329 | -1.318
29765 | 176.2957 | -31.9535 | 179.1681 | -2.635 | 0.329
29775 | 107.8902 | -47.9146 | 118.0512 | -0.66 | 0
29785 | 55.3827 | -56.4148 | 79.0561 | -0.988 | 0.33
29795 | -307.616 | -55.1632 | 312.5229 | -0.659 | 5.931
29805 | -820.512 | -74.4621 | 823.8838 | -0.988 | 9.883
29815 | -1002.3736 | -36.5961 | 1003.0414 | 0 | 6.919
29825 | -1171.8998 | 147.7703 | 1181.1796 | 2.635 | 8.236
29835 | -1279.2914 | 303.9164 | 1314.8961 | 2.966 | 7.577
29845 | -1223.932 | 362.0836 | 1276.3675 | 2.306 | 5.271
29855 | -1418.5383 | 415.4201 | 1478.1152 | 2.635 | 9.225
29865 | -1408.2502 | 575.1099 | 1521.1575 | 4.613 | 5.93
29875 | -1012.4375 | 527.171 | 1141.4635 | 1.647 | -0.329
29885 | -917.0853 | 395.0138 | 998.5396 | 0.329 | 2.964
29895 | -1140.2525 | 312.6254 | 1182.3326 | 0.33 | 6.919
29905 | -947.9617 | 363.3154 | 1015.1992 | 1.976 | 0.66
29915 | -626.9875 | 411.5605 | 749.9969 | 1.977 | -1.648
29925 | -630.7221 | 457.9711 | 779.4536 | 2.306 | 1.977
29935 | -477.9381 | 472.9148 | 672.3639 | 1.978 | -1.318
29945 | -240.8257 | 327.4624 | 406.4833 | -0.66 | -2.966
29955 | -172.6333 | 272.0572 | 322.2071 | 0.329 | -1.317
29965 | -293.5843 | 22.5401 | 294.4483 | -3.624 | 1.317
29975 | -515.4288 | -252.9329 | 574.1445 | -4.941 | 3.624
29985 | -491.128 | -359.1049 | 608.4103 | -3.624 | 0.66
29995 | -383.0211 | -420.8296 | 569.0367 | -3.624 | -0.329
30005 | -446.8544 | -244.7186 | 509.4763 | 0.329 | 1.976
30015 | -548.5874 | -261.8663 | 607.8833 | -2.306 | 2.635
30025 | -535.7207 | -26.168 | 536.3594 | 2.636 | 1.319
30035 | -494.7249 | 16.4328 | 494.9978 | 0 | 0.987
30045 | -297.0826 | -204.9752 | 360.9334 | -3.624 | -1.976
30055 | -126.0373 | -26.1379 | 128.719 | 2.307 | -2.306
30065 | -114.5327 | 168.9988 | 204.1527 | 2.635 | -0.659
30075 | 113.6551 | 338.7744 | 357.3312 | 3.624 | -4.613
30085 | 440.9763 | 438.0557 | 621.573 | 3.294 | -6.918
30095 | 670.3718 | 559.9607 | 873.4726 | 4.283 | -6.918
30105 | 593.8188 | 751.6082 | 957.8808 | 5.93 | -2.966
30115 | 603.0122 | 857.1651 | 1048.0247 | 5.271 | -4.282
30125 | 512.1194 | 598.6911 | 787.8435 | -0.329 | -1.977
30135 | -56.5552 | 242.604 | 249.1088 | -2.965 | 6.589
30145 | -597.8647 | 282.147 | 661.0969 | 1.647 | 8.566
30155 | -1016.7377 | 164.119 | 1029.8984 | -1.647 | 9.883
30165 | -1071.4347 | 198.3242 | 1089.6352 | 0.989 | 5.93
30175 | -1279.2275 | 55.8026 | 1280.444 | -2.307 | 9.225
30185 | -1280.2399 | 60.1223 | 1281.6509 | 0 | 5.93
30195 | -1109.6215 | 203.0577 | 1128.048 | 1.977 | 3.294
30205 | -944.9764 | 245.0166 | 976.2241 | 0.988 | 2.306
30215 | -908.4408 | 448.119 | 1012.9538 | 4.283 | 3.295
30225 | -538.9018 | 572.1052 | 785.9514 | 3.624 | -2.964
30235 | 136.6655 | 698.5453 | 711.7886 | 4.613 | -9.554
30245 | 671.6626 | 622.8842 | 916.0324 | 1.647 | -10.543
30255 | 941.0101 | 649.458 | 1143.3703 | 3.294 | -9.225
30265 | 1294.1971 | 868.5657 | 1558.638 | 6.26 | -12.19
30275 | 1231.7366 | 864.2036 | 1504.6671 | 3.295 | -6.259
30285 | 1026.1419 | 891.9476 | 1359.6094 | 4.282 | -3.954
30295 | 780.5646 | 607.2952 | 988.9836 | -1.318 | -1.647
30305 | 609.2756 | 380.0903 | 718.1124 | -1.318 | -1.318
30315 | 283.2 | 270.935 | 391.9286 | -0.988 | 2.636
30325 | -147.1041 | 355.7823 | 384.9944 | 1.648 | 5.93
30335 | -231.7518 | 234.9426 | 330.0105 | -1.648 | 2.306
30345 | -387.5498 | -75.5035 | 394.8362 | -4.942 | 4.613
30355 | -336.1608 | -204.0524 | 393.2448 | -3.295 | 1.317
30365 | -11.3261 | -251.5794 | 251.8342 | -2.964 | -3.294
30375 | 66.2312 | -294.1308 | 301.4955 | -2.966 | -0.659
30385 | -807.6154 | -487.4239 | 943.3052 | -5.6 | 14.496
30395 | -2130.3776 | -453.0894 | 2178.0264 | -2.306 | 25.368
30405 | -2833.7941 | -348.527 | 2855.1462 | -1.318 | 21.743
30415 | -2696.8358 | -41.7536 | 2697.159 | 2.965 | 12.19
30425 | -1906.9073 | 124.8246 | 1910.9884 | 1.977 | 0.659
30435 | -926.0479 | 344.276 | 987.973 | 4.282 | -6.919
30445 | -18.3486 | 337.7885 | 338.2865 | 1.318 | -11.531
30455 | 965.313 | 96.7976 | 970.154 | -2.305 | -18.119
30465 | 1025.9368 | 596.9083 | 1186.9481 | 9.224 | -7.248
30475 | 735.2706 | 917.9234 | 1176.0979 | 7.248 | -2.965
30485 | 556.51 | 679.4155 | 878.2419 | 0.33 | -2.635
30495 | 191.5761 | 327.3756 | 379.3101 | -2.306 | 2.305
30505 | -375.1921 | 318.9061 | 492.4127 | 1.317 | 7.578
30515 | -361.5654 | 203.1075 | 414.7073 | -1.317 | 0.658
30525 | -165.1856 | 210.4388 | 267.5271 | 0.658 | -1.317
30535 | 261.0228 | 351.7479 | 438.0177 | 2.635 | -6.589
30545 | 398.55 | 414.2158 | 574.819 | 1.977 | -3.624
30555 | -67.8565 | 788.6805 | 791.5942 | 7.908 | 5.271
30565 | -986.9385 | 489.3857 | 1101.6107 | -2.307 | 14.826
30575 | -1345.7609 | -378.3128 | 1397.9245 | -12.189 | 9.883
30585 | -768.3789 | -703.8162 | 1041.9997 | -7.249 | -2.965
30595 | -1028.9438 | 341.7256 | 1084.2056 | 13.179 | 9.225
30605 | -1277.8757 | 760.5491 | 1487.0781 | 6.259 | 7.907
30615 | -1157.3454 | 42.5433 | 1158.1271 | -8.565 | 3.624
30625 | -730.257 | -334.1463 | 803.0747 | -5.272 | -1.977
30635 | -7.3779 | -157.1178 | 157.2909 | 0.659 | -9.225
30645 | 328.3656 | 206.568 | 387.9359 | 4.283 | -6.26
30655 | 814.1295 | 447.3831 | 928.9556 | 4.283 | -11.531
30665 | 1139.7954 | 51.8938 | 1140.9761 | -4.942 | -10.541
30675 | 909.1114 | -163.9798 | 923.7818 | -2.965 | -2.966
30685 | 838.7457 | 394.4427 | 926.8653 | 8.236 | -4.942
30695 | 1373.3118 | 940.3694 | 1664.4158 | 9.883 | -13.837
30705 | 1289.3727 | 892.2114 | 1567.9679 | 3.295 | -4.942
30715 | 652.6931 | 1135.3431 | 1309.5847 | 8.896 | 3.624
30725 | 171.3676 | 1680.4428 | 1689.158 | 14.165 | 4.283
30735 | -91.271 | 484.0437 | 492.5736 | -13.178 | 3.954
30745 | -161.3756 | -193.9145 | 252.2794 | -7.577 | 2.306
30755 | 65.8957 | 613.6968 | 617.2245 | 11.532 | -2.306
30765 | 160.0077 | 434.306 | 462.8436 | -2.966 | -0.989
30775 | -21.8705 | -251.8643 | 252.8121 | -9.554 | 2.636
30785 | 656.3091 | 147.8091 | 672.7475 | 5.272 | -11.531
30795 | 437.0293 | -414.3413 | 602.2237 | -11.202 | 1.977
30805 | 605.906 | -545.3991 | 815.2192 | -3.953 | -5.93
30815 | 37.0065 | 617.1522 | 618.2607 | 15.813 | 7.577
30825 | -1247.9623 | 27.9599 | 1248.2755 | -9.554 | 21.086
30835 | -621.7909 | -225.1819 | 661.3099 | -2.636 | -5.272
30845 | 818.8758 | -10.383 | 818.9417 | 1.647 | -18.778
30855 | 1679.7832 | 896.3203 | 1903.9595 | 14.497 | -17.133
30865 | 1760.147 | 1537.1666 | 2336.878 | 13.837 | -9.883
30875 | 1585.9031 | 1821.0944 | 2414.8445 | 12.189 | -6.589
30885 | 1247.9991 | 1762.1587 | 2159.3298 | 7.907 | -2.307
30895 | 606.5112 | 1143.5891 | 1294.4698 | -1.977 | 4.943
30905 | 330.7359 | 773.3582 | 841.1119 | -0.658 | 1.976
30915 | -548.0022 | -142.8599 | 566.3174 | -13.178 | 14.826
30925 | -1394.148 | -651.1143 | 1538.7003 | -9.884 | 17.46
30935 | -1428.4153 | -1044.9839 | 1769.8479 | -11.86 | 8.566
30945 | -1184.9391 | -1098.0095 | 1615.4582 | -7.578 | 4.943
30955 | -920.7975 | -63.2015 | 922.9639 | 10.543 | 2.635
30965 | -1115.0416 | -65.9637 | 1116.9911 | -2.965 | 8.566
30975 | -643.2973 | 271.0431 | 698.0658 | 5.929 | -2.966
30985 | -217.4723 | 675.3243 | 709.4766 | 7.249 | -3.294
30995 | -323.8809 | 660.9982 | 736.0825 | 2.636 | 2.636
31005 | -772.0886 | 405.4274 | 872.062 | -0.989 | 8.236
31015 | -1224.6599 | 425.3088 | 1296.4102 | 2.306 | 10.543
31025 | -1600.3872 | 407.4534 | 1651.4411 | 0.989 | 11.86
31035 | -1975.0419 | 206.3016 | 1985.7872 | -1.977 | 13.837
31045 | -2230.7637 | -174.834 | 2237.6044 | -5.93 | 13.507
31055 | -2316.2999 | -697.3994 | 2419.0103 | -10.213 | 11.86
31065 | -1674.3946 | -490.8183 | 1744.8496 | -0.33 | -0.329
31075 | -1089.4118 | -120.6178 | 1096.0687 | 2.306 | -1.977
31085 | -1054.7787 | 99.8746 | 1059.4966 | 2.306 | 3.295
31095 | -1374.7277 | 245.4845 | 1396.4737 | 2.636 | 8.236
31105 | -1451.975 | 361.5317 | 1496.3077 | 2.965 | 5.601
31115 | -1368.3136 | 462.0777 | 1444.2291 | 3.295 | 3.953
31125 | -1253.4152 | 342.9086 | 1299.4753 | 0 | 2.966
31135 | -1257.2436 | 185.9181 | 1270.9159 | -0.988 | 4.282
31145 | -1315.1301 | -198.0458 | 1329.9584 | -5.93 | 4.942
31155 | -1067.8711 | -291.9341 | 1107.0565 | -2.636 | 0
31165 | -846.0837 | -219.0067 | 873.9689 | -0.988 | -0.33
31175 | -655.5983 | -20.7685 | 655.9271 | 1.646 | -1.317
31185 | -502.0221 | 98.269 | 511.5496 | 1.318 | -1.648
31195 | -125.8262 | -184.4312 | 223.2646 | -4.612 | -6.259
31205 | -45.2753 | -13.9004 | 47.3611 | 2.306 | -2.636
31215 | -542.2549 | -251.8295 | 597.8783 | -4.942 | 6.259
31225 | -377.4748 | -391.9237 | 544.1428 | -3.294 | -2.964
31235 | 111.5223 | 8.2726 | 111.8287 | 4.612 | -7.578
31245 | 44.6556 | 268.1033 | 271.7968 | 3.624 | -0.659
31255 | -139.475 | 191.7165 | 237.0832 | 0 | 0.659
31265 | -277.6252 | 135.8466 | 309.0793 | 0.33 | 1.319
31275 | -627.969 | -93.1716 | 634.8433 | -3.295 | 5.93
31285 | -1157.1482 | -250.074 | 1183.8619 | -2.965 | 10.541
31295 | -1701.3164 | -512.3088 | 1776.7774 | -5.93 | 13.509
31305 | -1768.1858 | -635.328 | 1878.8621 | -4.612 | 8.236
31315 | -1507.6342 | -626.9938 | 1632.8142 | -3.295 | 3.624
31325 | -1085.9247 | -662.6542 | 1272.1411 | -3.954 | -0.659
31335 | -518.3402 | -398.0169 | 653.5243 | 1.319 | -5.601
31345 | -147.1382 | -438.828 | 462.8387 | -2.966 | -5.271
31355 | 311.3947 | -156.2428 | 348.3942 | 3.295 | -9.225
31365 | 790.232 | 165.8662 | 807.4517 | 4.613 | -11.53
31375 | 1475.1389 | 658.2631 | 1615.3467 | 9.554 | -17.462
31385 | 1815.2861 | 1059.4878 | 2101.8511 | 10.212 | -14.495
31395 | 1757.9358 | 1478.581 | 2297.072 | 12.849 | -9.884
31405 | 1188.749 | 1598.1492 | 1991.7844 | 9.554 | -0.659
31415 | 347.7863 | 1185.1785 | 1235.1532 | 1.318 | 6.919
31425 | -346.4656 | 613.5837 | 704.6442 | -3.295 | 9.224
31435 | -1095.3553 | -22.2 | 1095.5802 | -7.906 | 14.496
31445 | -1705.6212 | -568.1584 | 1797.7619 | -9.884 | 15.814
31455 | -2120.8433 | -1085.9304 | 2382.692 | -12.519 | 15.813
31465 | -2283.6914 | -1321.0076 | 2638.2395 | -10.214 | 13.507
31475 | -2060.9782 | -1279.1998 | 2425.6924 | -6.917 | 7.579
31485 | -1716.9488 | -931.886 | 1953.5416 | -1.318 | 4.282
31495 | -1359.0154 | -406.0103 | 1418.3679 | 3.624 | 1.648
31505 | -826.5569 | 39.5875 | 827.5044 | 5.271 | -3.624
31515 | -241.9585 | 418.2585 | 483.2019 | 6.918 | -7.248
31525 | 365.5483 | 716.0494 | 803.9604 | 7.578 | -10.873
31535 | 771.8493 | 884.086 | 1173.6095 | 6.918 | -10.542
31545 | 928.0805 | 964.0972 | 1338.214 | 6.26 | -8.566
31555 | 867.7898 | 1050.0509 | 1362.2283 | 6.589 | -5.6
31565 | 434.3671 | 878.6906 | 980.1897 | 2.306 | 1.318
31575 | -64.1918 | 650.7855 | 653.9436 | 0.659 | 4.612
31585 | -476.1547 | 206.2098 | 518.889 | -4.613 | 6.259
31595 | -839.385 | -114.5713 | 847.168 | -4.612 | 7.908
31605 | -1013.0084 | -289.344 | 1053.5207 | -4.283 | 6.588
31615 | -1103.2351 | -464.8473 | 1197.1678 | -5.271 | 6.259
31625 | -1024.5314 | -580.7347 | 1177.6746 | -4.942 | 3.624
31635 | -602.8201 | -509.9782 | 789.6011 | -2.306 | -2.635
31645 | -65.7016 | -129.444 | 145.1635 | 3.295 | -6.589
31655 | 312.0352 | 164.92 | 352.9371 | 3.623 | -6.918
31665 | 648.8971 | 356.5133 | 740.3845 | 3.954 | -8.566
31675 | 1028.0372 | 733.7692 | 1263.043 | 8.236 | -10.872
31685 | 789.025 | 848.1372 | 1158.4028 | 5.272 | -1.977
31695 | 324.7061 | 1127.3315 | 1173.1626 | 9.224 | 2.307
31705 | -160.1412 | 518.4663 | 542.6347 | -5.271 | 5.601
31715 | -94.2423 | 178.9446 | 202.2444 | -2.306 | -0.989
31725 | -294.0184 | 168.1392 | 338.6999 | 0 | 4.282
31735 | -318.5966 | 39.8448 | 321.0785 | -2.307 | 1.318
31745 | -359.3277 | 117.4973 | 378.0503 | 0.989 | 2.306
31755 | -407.7677 | 81.0089 | 415.7367 | -0.989 | 2.306
31765 | -404.3508 | 84.877 | 413.163 | 0 | 1.648
31775 | -363.3664 | 97.4229 | 376.1999 | 0 | 0.989
31785 | -184.0362 | 138.9003 | 230.5702 | 0.66 | -1.648
31795 | 122.077 | 418.8437 | 436.2715 | 4.941 | -4.612
31805 | 10.9981 | 576.2323 | 576.3373 | 3.954 | 0.988
31815 | -74.7071 | 314.2315 | 322.99 | -1.976 | 0.329
31825 | 164.9399 | 371.0136 | 406.025 | 2.635 | -4.282
31835 | 381.1188 | 141.4686 | 406.5278 | -2.966 | -4.613
31845 | 438.0306 | 69.5905 | 443.5241 | -0.658 | -3.294
31855 | 296.5246 | 210.2601 | 363.5053 | 1.976 | -0.329
31865 | 288.6887 | 219.0542 | 362.3891 | 0.33 | -1.978
31875 | 101.8732 | 296.678 | 313.6813 | 1.976 | 1.648
31885 | -145.5805 | 172.596 | 225.7943 | -1.317 | 3.294
31895 | -385.4687 | 60.573 | 390.199 | -1.318 | 4.613
31905 | -588.0994 | -60.6656 | 591.2201 | -2.306 | 5.271
31915 | -805.1319 | 4.478 | 805.1444 | 0.329 | 6.589
31925 | -1119.2034 | -105.3416 | 1124.1499 | -2.636 | 9.225
31935 | -1046.918 | -232.3279 | 1072.3868 | -2.964 | 3.953
31945 | -809.9745 | -44.8544 | 811.2156 | 1.647 | 1.318
31955 | -433.3088 | 73.3359 | 439.4709 | 0.988 | -2.636
31965 | -116.5206 | 108.1858 | 159.0007 | 0.659 | -3.624
31975 | 198.668 | 166.7011 | 259.342 | 1.318 | -5.601
31985 | 882.5551 | 981.1259 | 1319.6634 | 14.496 | -13.507
31995 | 860.1933 | 910.5711 | 1252.6261 | 2.306 | -4.283
32005 | 917.2701 | 1118.8988 | 1446.8306 | 8.895 | -6.918
32015 | 1003.8061 | 876.955 | 1332.9204 | 0.659 | -6.589
32025 | 801.7191 | 610.9463 | 1007.9726 | 0 | -1.976
32035 | 264.793 | 543.6023 | 604.6642 | 1.318 | 4.611
32045 | -421.0348 | 231.4603 | 480.4625 | -3.624 | 9.884
32055 | -1099.0464 | -73.3324 | 1101.4902 | -4.612 | 13.508
32065 | -1601.0516 | -365.2081 | 1642.1764 | -6.26 | 14.166
32075 | -2019.36 | -592.5226 | 2104.4946 | -6.589 | 15.484
32085 | -2156.2053 | -827.9053 | 2309.6858 | -7.907 | 12.519
32095 | -1884.9808 | -872.1038 | 2076.9491 | -5.6 | 6.259
32105 | -1448.1801 | -741.8789 | 1627.1478 | -2.966 | 1.978
32115 | -846.8975 | -563.0012 | 1016.959 | -1.318 | -3.624
32125 | -438.1218 | -627.9252 | 765.6637 | -4.282 | -3.624
32135 | 249.833 | 116.9757 | 275.862 | 9.883 | -11.201
32145 | 728.7336 | 530.0388 | 901.107 | 6.589 | -10.543
32155 | 1491.1211 | 809.3292 | 1696.6013 | 7.907 | -18.45
32165 | 2367.0386 | 1366.2698 | 2733.0505 | 13.837 | -23.39
32175 | 2355.0447 | 1715.5459 | 2913.6461 | 12.519 | -12.52
32185 | 1649.8187 | 1744.9865 | 2401.4328 | 9.225 | -1.647
32195 | 368.1906 | 1401.469 | 1449.0271 | 2.965 | 12.19
32205 | -823.9724 | 950.9068 | 1258.2345 | -0.659 | 17.461
32215 | -1825.4364 | 358.4122 | 1860.2896 | -5.93 | 21.414
32225 | -2414.9504 | -338.9896 | 2438.6265 | -10.872 | 19.767
32235 | -2445.0937 | -840.5471 | 2585.5372 | -11.202 | 13.508
32245 | -2444.3548 | -1150.2166 | 2701.4567 | -10.871 | 13.178
32255 | -2332.1647 | -967.8618 | 2525.0245 | -3.954 | 10.213
32265 | -2044.2677 | -1089.5076 | 2316.4752 | -8.565 | 6.259
32275 | -998.1249 | -618.1011 | 1174.0112 | 2.306 | -8.566
32285 | -188.364 | -94.13 | 210.5741 | 4.613 | -9.224
32295 | 199.2453 | 126.7033 | 236.1195 | 2.964 | -7.578
32305 | 561.0083 | 419.166 | 700.3074 | 5.93 | -9.554
32315 | 955.8098 | 894.5587 | 1309.1248 | 10.213 | -11.53
32325 | 1077.6064 | 1145.9476 | 1573.0325 | 8.566 | -8.566
32335 | 1231.7712 | 1510.018 | 1948.6956 | 12.19 | -9.884
32345 | 1706.8059 | 1589.7844 | 2332.5096 | 8.565 | -15.484
32355 | 2067.5513 | 1355.3565 | 2472.1974 | 3.954 | -15.155
32365 | 1773.8563 | 1543.3395 | 2351.2683 | 9.884 | -5.929
32375 | 788.3677 | 1113.6892 | 1364.4879 | -0.989 | 6.917
32385 | 94.5272 | 723.0472 | 729.2 | -1.317 | 6.919
32395 | -843.9459 | 237.1246 | 876.6258 | -5.931 | 16.144
32405 | -1765.7085 | -478.4154 | 1829.3736 | -12.19 | 20.096
32415 | -2470.5615 | -952.2675 | 2647.7326 | -11.53 | 21.414
32425 | -2713.2324 | -1369.5594 | 3039.2965 | -13.507 | 17.132
32435 | -2549.882 | -1550.4596 | 2984.2626 | -11.202 | 11.53
32445 | -2129.9967 | -1194.1722 | 2441.9118 | -2.965 | 5.931
32455 | -1387.3188 | -835.5098 | 1619.4846 | -1.318 | -2.307
32465 | -573.4084 | -560.812 | 802.0644 | 0 | -7.577
32475 | 136.0957 | -180.4175 | 225.9923 | 3.624 | -10.542
32485 | 783.525 | 87.798 | 788.4288 | 3.624 | -13.508
32495 | 1584.7423 | 157.2335 | 1592.5233 | 1.976 | -19.437
32505 | 2271.7525 | 406.6246 | 2307.8568 | 5.601 | -21.085
32515 | 3002.9791 | 939.8415 | 3146.615 | 11.201 | -25.368
32525 | 2997.7041 | 1372.7129 | 3297.0548 | 11.861 | -15.813
32535 | 2551.0171 | 1735.9142 | 3085.6258 | 13.178 | -8.896
32545 | 1992.3541 | 1637.8132 | 2579.1291 | 6.918 | -3.953
32555 | 1226.2475 | 1352.6791 | 1825.7666 | 3.624 | 3.294
32565 | 14.4176 | 625.5928 | 625.7589 | -5.93 | 15.155
32575 | -864.0577 | 43.4959 | 865.1517 | -6.919 | 15.484
32585 | -1665.9329 | -387.1858 | 1710.3349 | -8.236 | 19.767
32595 | -2501.0423 | -893.5203 | 2655.8598 | -11.859 | 24.05
32605 | -3110.5224 | -1190.0111 | 3330.3867 | -10.543 | 24.05
32615 | -2834.2748 | -1058.264 | 3025.3985 | -4.942 | 11.861
32625 | -2185.452 | -859.9011 | 2348.5379 | -3.294 | 4.612
32635 | -1404.1872 | -412.1066 | 1463.4116 | 2.635 | -1.977
32645 | -609.8148 | -132.7093 | 624.088 | 1.977 | -6.919
32655 | 374.8916 | 210.4133 | 429.9041 | 5.271 | -14.825
32665 | 1281.4036 | 327.9137 | 1322.6952 | 2.965 | -18.45
32675 | 2071.0295 | 555.3293 | 2144.1907 | 5.931 | -21.413
32685 | 2555.9202 | 859.0871 | 2696.4344 | 7.906 | -20.097
32695 | 2493.3775 | 1134.4424 | 2739.3231 | 8.896 | -13.178
32705 | 1910.5528 | 1022.5399 | 2166.9795 | 3.624 | -3.954
32715 | 1059.4839 | 535.5135 | 1187.1314 | -2.966 | 3.954
32725 | 269.6128 | 290.909 | 396.6347 | -1.318 | 7.906
32735 | -566.3575 | -76.0812 | 571.4448 | -5.601 | 13.509
32745 | -1091.6287 | 145.1786 | 1101.2402 | 2.966 | 12.518
32755 | -1640.0575 | -95.1486 | 1642.8152 | -4.942 | 16.144
32765 | -2059.0168 | -386.9216 | 2095.0557 | -5.601 | 16.143
32775 | -2299.3379 | -394.4964 | 2332.9342 | -2.635 | 15.155
32785 | -2485.4673 | -553.6646 | 2546.388 | -5.601 | 15.154
32795 | -2321.6931 | -701.4967 | 2425.357 | -5.601 | 9.554
32805 | -1821.0736 | -493.5122 | 1886.76 | -0.329 | 2.966
32815 | -1141.5341 | -325.6933 | 1187.0873 | -0.33 | -2.966
32825 | -497.9083 | -164.5166 | 524.3838 | 0.989 | -6.259
32835 | 97.3023 | 137.526 | 168.467 | 4.282 | -9.225
32845 | 621.9379 | 414.9056 | 747.6319 | 5.272 | -11.201
32855 | 777.8432 | 578.637 | 969.4642 | 4.942 | -7.577
32865 | 926.4489 | 591.5162 | 1099.181 | 3.294 | -8.566
32875 | 954.2867 | 733.0038 | 1203.3111 | 5.6 | -6.589
32885 | 480.4831 | 649.453 | 807.8696 | 1.978 | 1.977
32895 | -235.8599 | 530.9967 | 581.0228 | 1.317 | 8.236
32905 | -675.9359 | 198.9363 | 704.6027 | -3.295 | 7.577
32915 | -859.0107 | -46.7488 | 860.2818 | -3.293 | 6.259
32925 | -997.5969 | -480.796 | 1107.4133 | -8.237 | 6.59
32935 | -1032.9145 | -808.6129 | 1311.7801 | -8.236 | 5.271
32945 | -714.1593 | -749.6784 | 1035.3943 | -3.624 | -0.659
32955 | -475.3145 | -476.8397 | 673.2755 | 0 | -0.659
32965 | -269.4881 | 123.9428 | 296.6238 | 7.248 | -1.977
32975 | -70.2944 | 572.5911 | 576.8898 | 7.577 | -2.965
32985 | 105.1508 | 787.8114 | 794.7978 | 6.589 | -3.624
32995 | 593.3004 | 869.7039 | 1052.8011 | 5.6 | -9.883
33005 | 489.9743 | 664.0475 | 825.2478 | 0.989 | -1.648
33015 | 61.2765 | 30.1824 | 68.3066 | -7.248 | 3.295
33025 | 47.6493 | 16.0667 | 50.2851 | 0.329 | -1.318
33035 | 255.2113 | -18.6052 | 255.8886 | -1.647 | -3.953
33045 | -135.5176 | 13.182 | 136.1572 | 0 | 5.271
33055 | -606.8333 | -414.9285 | 735.1274 | -7.907 | 7.577
33065 | -790.5319 | -595.4397 | 989.6914 | -4.942 | 5.601
33075 | -853.321 | -826.5811 | 1188.0206 | -7.577 | 4.942
33085 | -579.4628 | -902.4018 | 1072.43 | -5.601 | -0.659
33095 | -369.7375 | -673.4805 | 768.298 | -0.988 | -0.659
33105 | -85.3139 | -467.672 | 475.3899 | -0.329 | -3.624
33115 | 332.3534 | 69.5087 | 339.5442 | 6.918 | -7.248
33125 | 686.7957 | 279.4154 | 741.4589 | 3.624 | -8.236
33135 | 866.723 | 543.3377 | 1022.949 | 6.589 | -7.248
33145 | 891.5483 | 488.5011 | 1016.608 | 1.977 | -5.601
33155 | 838.1913 | 284.8056 | 885.2564 | -0.329 | -4.282
33165 | 738.3567 | 408.0103 | 843.5894 | 3.953 | -2.966
33175 | 700.3351 | 751.0842 | 1026.9356 | 7.577 | -3.295
33185 | 308.7902 | 1190.8917 | 1230.2741 | 10.873 | 3.295
33195 | -167.014 | 1271.6995 | 1282.6197 | 6.917 | 6.259
33205 | -749.3093 | 1027.488 | 1271.6902 | 2.307 | 10.873
33215 | -1297.5187 | 590.0543 | 1425.3838 | -2.307 | 13.178
33225 | -1713.6265 | -50.4836 | 1714.3699 | -8.236 | 13.837
33235 | -1871.9755 | -593.1942 | 1963.7137 | -9.883 | 11.531
33245 | -1867.8314 | -852.1404 | 2053.0313 | -8.237 | 9.554
33255 | -1866.6086 | -921.4103 | 2081.6399 | -6.588 | 9.224
33265 | -1762.262 | -1017.6119 | 2034.9696 | -7.248 | 6.919
33275 | -1545.734 | -1151.0434 | 1927.2246 | -7.907 | 4.283
33285 | -1081.1641 | -1088.5687 | 1534.2417 | -4.942 | -1.318
33295 | -598.9309 | -904.9719 | 1085.2154 | -2.635 | -3.954
33305 | -72.7882 | -521.8459 | 526.8977 | 1.976 | -7.577
33315 | 661.4071 | -2.8158 | 661.4131 | 6.26 | -13.836
33325 | 983.3755 | 371.9586 | 1051.3708 | 6.589 | -10.214
33335 | 764.053 | 668.0305 | 1014.9098 | 7.578 | -3.295
33345 | 563.9981 | 706.9443 | 904.3583 | 4.611 | -2.635
33355 | 898.1041 | 837.3314 | 1227.8904 | 6.59 | -9.883
33365 | 486.6016 | 1099.1762 | 1202.0689 | 8.894 | 2.306
33375 | -41.9341 | 493.1839 | 494.9635 | -4.941 | 4.942
33385 | 195.0961 | -64.578 | 205.5063 | -5.93 | -4.613
33395 | 230.0788 | -539.3218 | 586.3483 | -8.566 | -0.988
33405 | -535.8204 | -1154.4671 | 1272.752 | -13.507 | 11.531
33415 | -1129.3668 | -1235.3573 | 1673.7912 | -7.248 | 11.53
33425 | -926.8536 | -723.0645 | 1175.5339 | 1.647 | 1.977
33435 | -633.1986 | -337.2101 | 717.3918 | 1.977 | 0.329
33445 | -435.9563 | -184.3346 | 473.3256 | 0.988 | -0.329
33455 | -204.6946 | -4.6439 | 204.7473 | 2.636 | -2.306
33465 | 129.2014 | 380.6265 | 401.9571 | 6.918 | -5.271
33475 | 501.5851 | 783.182 | 930.0332 | 8.895 | -7.578
33485 | 857.1644 | 1039.4279 | 1347.2717 | 8.566 | -9.224
33495 | 992.4559 | 1135.4236 | 1508.0303 | 7.248 | -7.248
33505 | 903.5729 | 937.8164 | 1302.284 | 2.635 | -4.283
33515 | 730.7686 | 717.6673 | 1024.2407 | 1.319 | -2.306
33525 | 608.8657 | 592.689 | 849.7045 | 1.318 | -1.978
33535 | 372.0416 | 890.4555 | 965.0522 | 7.577 | 0.989
33545 | -509.4489 | 737.7198 | 896.5315 | 0.659 | 13.178
33555 | -1366.39 | 394.773 | 1422.2754 | -2.306 | 16.473
33565 | -2040.0479 | -97.6774 | 2042.385 | -6.919 | 18.45
33575 | -2910.5038 | -1272.0726 | 3176.3503 | -21.085 | 25.367
33585 | -3064.6747 | -2359.7009 | 3867.8701 | -24.709 | 16.802
33595 | -2157.6206 | -2655.949 | 3421.8988 | -17.461 | 0.329
33605 | -1174.1127 | -2162.277 | 2460.4842 | -6.259 | -5.27
33615 | -396.9084 | -1758.4487 | 1802.6863 | -5.272 | -8.237
33625 | 181.0296 | -1311.0595 | 1323.4987 | -0.989 | -9.554
33635 | 837.1375 | -763.8834 | 1133.2771 | 3.295 | -14.166
33645 | 1742.8603 | -165.413 | 1750.6923 | 7.248 | -21.415
33655 | 2505.4142 | 570.6339 | 2569.5765 | 12.849 | -23.061
33665 | 3187.3044 | 1229.5272 | 3416.2328 | 15.155 | -25.698
33675 | 3408.0698 | 1682.318 | 3800.6755 | 15.154 | -20.755
33685 | 3251.0043 | 1712.4934 | 3674.4609 | 10.214 | -15.484
33695 | 2886.3506 | 1957.9888 | 3487.7987 | 14.166 | -10.543
33705 | 1884.3047 | 1720.5899 | 2551.6727 | 5.93 | 2.966
33715 | 843.7174 | 1135.3134 | 1414.4948 | -0.659 | 8.565
33725 | -92.4378 | 595.6541 | 602.784 | -3.295 | 13.178
33735 | -899.2245 | 27.7947 | 899.654 | -7.248 | 16.143
33745 | -1592.4732 | -575.1609 | 1693.1571 | -10.871 | 18.45
33755 | -1993.5292 | -1033.6692 | 2245.5803 | -11.531 | 16.802
33765 | -1932.0162 | -1076.1562 | 2211.515 | -6.918 | 10.872
33775 | -1586.5442 | -1107.6289 | 1934.9327 | -7.248 | 5.601
33785 | -974.1331 | -1055.1544 | 1436.0662 | -5.272 | -1.319
33795 | -488.983 | -834.9829 | 967.6263 | -1.976 | -2.636
33805 | -123.4494 | -553.6915 | 567.2865 | 0.329 | -3.953
33815 | 308.9213 | -66.3626 | 315.9689 | 5.601 | -7.248
33825 | 965.1501 | 531.5743 | 1101.8557 | 9.883 | -13.178
33835 | 1348.0777 | 924.3971 | 1634.5713 | 9.555 | -11.531
33845 | 1508.9547 | 1041.8946 | 1833.709 | 7.247 | -10.212
33855 | 1536.7888 | 869.5749 | 1765.752 | 2.965 | -8.567
33865 | 1380.7913 | 788.8358 | 1590.2348 | 3.624 | -5.271
33875 | 1224.0614 | 926.3291 | 1535.0609 | 6.26 | -4.282
33885 | 912.6908 | 1106.9258 | 1434.6739 | 7.248 | -0.33
33895 | 271.0457 | 966.6399 | 1003.9215 | 2.636 | 6.919
33905 | -727.0682 | 364.8931 | 813.4956 | -5.601 | 16.143
33915 | -1262.8101 | -167.8179 | 1273.9122 | -7.248 | 13.178
33925 | -1462.0396 | -501.2188 | 1545.5679 | -7.248 | 11.201
33935 | -1900.7695 | -1008.8654 | 2151.9141 | -12.19 | 16.143
33945 | -2382.9407 | -1665.6065 | 2907.3444 | -16.802 | 18.121
33955 | -2118.8758 | -1812.8102 | 2788.5328 | -11.201 | 7.577
33965 | -1428.2104 | -1262.1412 | 1905.9867 | -0.659 | -0.33
33975 | -1033.8871 | -1094.0158 | 1505.2551 | -4.613 | 0.659
33985 | -503.605 | -746.513 | 900.4997 | 0.989 | -4.942
33995 | 56.4618 | -93.3159 | 109.0679 | 7.577 | -7.907
34005 | 453.2682 | 193.3427 | 492.7814 | 4.613 | -8.235
34015 | 737.611 | 397.4853 | 837.8929 | 5.601 | -8.567
34025 | 1213.1966 | 616.179 | 1360.7066 | 6.588 | -13.178
34035 | 1718.3202 | 857.2017 | 1920.2654 | 7.907 | -15.484
34045 | 1599.4726 | 846.8668 | 1809.8331 | 4.613 | -7.248
34055 | 1438.8805 | 903.6741 | 1699.1186 | 5.93 | -6.589
34065 | 1248.1136 | 1305.0134 | 1805.7817 | 11.53 | -4.283
34075 | 766.5893 | 1317.9192 | 1524.6541 | 6.26 | 1.977
34085 | 250.6889 | 783.4077 | 822.5403 | -2.306 | 4.942
34095 | -314.9814 | 434.7284 | 536.8446 | -1.648 | 8.894
34105 | -767.7043 | -134.0249 | 779.3154 | -8.236 | 9.885
34115 | -995.0448 | -385.3751 | 1067.0652 | -5.271 | 8.565
34125 | -1283.8372 | -590.5634 | 1413.1536 | -6.588 | 10.872
34135 | -1307.4388 | -757.2982 | 1510.9258 | -6.59 | 7.248
34145 | -1330.4402 | -821.9793 | 1563.8801 | -5.601 | 7.577
34155 | -1305.1517 | -776.9907 | 1518.9258 | -3.953 | 6.26
34165 | -932.9251 | -349.9322 | 996.3944 | 2.966 | 0
34175 | -755.2879 | 5.1259 | 755.3053 | 3.623 | 1.647
34185 | -913.167 | -458.3883 | 1021.7601 | -7.907 | 5.601
34195 | -453.9896 | -704.8376 | 838.3929 | -5.271 | -4.612
34205 | 669.1013 | 150.9766 | 685.9231 | 11.201 | -17.131
34215 | 1111.3383 | 699.806 | 1313.3169 | 8.895 | -10.873
34225 | 900.3762 | 720.3542 | 1153.0774 | 4.283 | -3.624
34235 | 879.6493 | 807.0044 | 1193.75 | 5.931 | -5.93
34245 | 1452.6876 | 1503.6785 | 2090.7774 | 16.142 | -14.825
34255 | 934.7163 | 1574.4841 | 1831.0365 | 7.908 | 1.977
34265 | -86.0955 | 869.799 | 874.0497 | -3.624 | 11.201
34275 | -686.4847 | 591.1228 | 905.918 | 0.329 | 9.883
34285 | -843.0097 | 262.3274 | 882.8822 | -3.624 | 6.59
34295 | -1030.3262 | 48.1244 | 1031.4495 | -2.965 | 8.236
34305 | -1350.5315 | -194.3953 | 1364.4504 | -4.941 | 10.872
34315 | -1636.3384 | -359.1268 | 1675.2837 | -4.613 | 11.53
34325 | -2168.6763 | -776.6703 | 2303.5567 | -9.883 | 17.132
34335 | -2506.8512 | -1260.0097 | 2805.6956 | -12.52 | 15.814
34345 | -2209.2602 | -1290.6272 | 2558.6225 | -7.248 | 6.918
34355 | -1515.2139 | -895.9142 | 1760.2657 | -0.659 | -0.988
34365 | -955.5205 | -526.5306 | 1090.9876 | 0.988 | -2.636
34375 | -674.5737 | -290.3383 | 734.4018 | 1.318 | -1.648
34385 | -372.2265 | -377.568 | 530.1982 | -2.635 | -3.953
34395 | 65.9319 | -257.0541 | 265.3749 | 0.988 | -7.577
34405 | 483.504 | -58.3523 | 487.0125 | 2.306 | -9.225
34415 | 698.1933 | -99.0161 | 705.1794 | -0.659 | -7.907
34425 | 939.477 | 41.0707 | 940.3743 | 2.637 | -9.554
34435 | 1368.8936 | 306.8133 | 1402.8557 | 4.941 | -13.507
34445 | 1510.0289 | 552.5267 | 1607.9406 | 5.93 | -10.213
34455 | 1282.7184 | 528.786 | 1387.4369 | 2.636 | -4.942
34465 | 1128.0953 | 743.4291 | 1351.0314 | 6.918 | -4.942
34475 | 836.6165 | 863.1652 | 1202.0737 | 5.6 | -0.988
34485 | 343.4168 | 680.6411 | 762.3696 | 1.318 | 3.954
34495 | -74.6193 | 330.6086 | 338.9249 | -2.306 | 5.27
34505 | -610.9219 | -115.6832 | 621.7782 | -5.929 | 9.884
34515 | -1059.2048 | -747.9644 | 1296.6748 | -11.531 | 10.873
34525 | -1341.994 | -1122.9367 | 1749.8385 | -10.214 | 10.541
34535 | -1196.0955 | -1103.705 | 1627.5163 | -5.93 | 4.613
34545 | -847.4242 | -791.7173 | 1159.7173 | -0.988 | 0.659
34555 | -531.3289 | -428.4242 | 682.5377 | 1.647 | -0.988
34565 | -280.986 | -142.7927 | 315.187 | 2.636 | -1.978
34575 | -101.3757 | -40.232 | 109.0672 | 1.317 | -2.306
34585 | 54.9489 | 32.9884 | 64.0907 | 1.648 | -2.964
34595 | 204.973 | 111.3944 | 233.2867 | 1.976 | -3.624
34605 | 563.695 | 189.8199 | 594.7972 | 2.307 | -7.908
34615 | 916.8586 | 229.5506 | 945.1577 | 1.977 | -9.223
34625 | 1081.0488 | 373.3252 | 1143.695 | 3.953 | -7.908
34635 | 1131.79 | 490.7645 | 1233.6119 | 3.953 | -6.918
34645 | 1199.1087 | 568.8218 | 1327.185 | 3.954 | -7.248
34655 | 921.9746 | 493.1867 | 1045.5957 | 1.647 | -1.318
34665 | 381.7545 | 107.203 | 396.5211 | -3.953 | 4.283
34675 | 51.1661 | -195.6913 | 202.2697 | -4.284 | 3.624
34685 | -119.0392 | -299.7884 | 322.5577 | -2.964 | 3.294
34695 | -426.0611 | -589.8597 | 727.6417 | -6.919 | 6.59
34705 | -760.7343 | -1054.3841 | 1300.1701 | -10.872 | 8.236
34715 | -1034.3587 | -1408.8776 | 1747.8083 | -11.201 | 8.895
34725 | -1017.9349 | -1704.1859 | 1985.0544 | -12.19 | 5.272
34735 | -725.4053 | -1713.285 | 1860.5264 | -8.566 | 0.658
34745 | -199.2646 | -1249.7074 | 1265.494 | -0.658 | -4.942
34755 | 297.2938 | -416.6652 | 511.853 | 7.906 | -7.248
34765 | 581.2349 | 407.4759 | 709.8385 | 12.19 | -6.589
34775 | 779.534 | 913.9885 | 1201.2694 | 11.531 | -6.918
34785 | 734.9018 | 1066.5077 | 1295.1908 | 8.565 | -3.624
34795 | 444.4022 | 803.2551 | 917.9935 | 2.307 | 0.659
34805 | 90.4938 | 578.4322 | 585.4681 | 1.648 | 3.294
34815 | 33.4622 | 179.6109 | 182.7014 | -3.295 | 0.329
34825 | -45.8821 | -46.5505 | 65.3614 | -2.306 | 1.648
34835 | 34.0997 | -281.4869 | 283.5448 | -4.284 | -0.988
34845 | -8.0293 | -300.9293 | 301.0364 | -1.647 | 0.988
34855 | -273.8785 | -503.5854 | 573.2432 | -5.27 | 4.612
34865 | -416.6223 | -565.2679 | 702.2121 | -3.295 | 3.624
34875 | -706.4017 | -625.7224 | 943.6799 | -3.954 | 7.249
34885 | -704.3978 | -761.4762 | 1037.3149 | -5.271 | 3.293
34895 | -632.4322 | -849.0801 | 1058.7292 | -4.942 | 2.636
34905 | -410.5963 | -678.1236 | 792.7426 | -0.988 | -0.659
34915 | -135.7732 | -429.1476 | 450.1134 | 0.988 | -2.635
34925 | 25.6137 | -154.4161 | 156.526 | 2.965 | -2.306
34935 | 83.6423 | 89.527 | 122.5198 | 3.954 | -1.648
34945 | 332.4856 | 387.9529 | 510.9346 | 6.259 | -5.271
34955 | 436.8392 | 644.4184 | 778.5265 | 6.919 | -3.624
34965 | 219.6509 | 629.6011 | 666.8163 | 3.624 | 0.989
34975 | 130.4311 | 470.7017 | 488.4387 | 1.318 | -0.329
34985 | 123.6291 | 314.7955 | 338.2017 | 0.329 | -0.66
34995 | -69.8945 | 146.6444 | 162.4494 | -0.989 | 2.636
35005 | -300.1587 | -137.2246 | 330.0391 | -3.953 | 3.954
35015 | -413.9451 | -360.194 | 548.7169 | -4.283 | 3.293
35025 | -386.6662 | -463.6519 | 603.725 | -3.624 | 1.648
35035 | -325.5586 | -473.4228 | 574.5586 | -2.636 | 0.988
35045 | -196.2063 | -386.3876 | 433.35 | -0.988 | -0.658
35055 | -9.339 | -116.2766 | 116.6511 | 2.636 | -2.307
35065 | 22.8803 | -36.8029 | 43.3355 | 0.659 | -0.659
35075 | 45.4629 | 62.7521 | 77.49 | 1.977 | -0.988
35085 | 128.2803 | 203.1489 | 240.2609 | 2.964 | -1.977
35095 | 154.7638 | 111.0931 | 190.5086 | -0.329 | -1.317
35105 | 52.1147 | 25.9059 | 58.1985 | -0.329 | 0.658
35115 | -121.5863 | -303.7001 | 327.1345 | -5.272 | 2.306
35125 | 471.102 | -114.4314 | 484.8006 | 2.306 | -9.883
35135 | 579.4464 | 45.8758 | 581.2596 | 1.648 | -3.295
35145 | 602.2193 | 101.4854 | 610.7105 | 1.318 | -3.953
35155 | 533.363 | 327.7123 | 625.9964 | 4.612 | -1.977
35165 | 443.323 | 487.2024 | 658.712 | 4.283 | -1.318
35175 | 296.9372 | 488.1384 | 571.3587 | 2.635 | 0.33
35185 | 157.1166 | 406.6549 | 435.9517 | 1.318 | 0.988
35195 | 29.1359 | 375.3646 | 376.4937 | 1.648 | 1.648
35205 | -115.9447 | 253.2721 | 278.5497 | -0.329 | 2.635
35215 | -104.6601 | 64.9413 | 123.171 | -1.977 | 0.659
35225 | -121.586 | 32.4605 | 125.8445 | -0.33 | 1.318
35235 | -245.3417 | -105.2908 | 266.9807 | -2.636 | 2.965
35245 | -400.6338 | -317.6151 | 511.26 | -4.282 | 3.953
35255 | -318.1974 | -448.3087 | 549.7547 | -3.953 | 0.659
35265 | -279.2334 | -397.6822 | 485.9243 | -1.648 | 1.318
35275 | -121.6138 | -412.603 | 430.1525 | -2.636 | -1.318
35285 | 172.5336 | -311.1235 | 355.7607 | -0.329 | -4.283
35295 | 321.8038 | -38.0201 | 324.042 | 2.965 | -3.294
35305 | 423.6661 | 213.8583 | 474.5822 | 3.953 | -3.624
35315 | 463.2018 | 433.5066 | 634.4162 | 4.942 | -2.965
35325 | 587.0607 | 470.7424 | 752.4883 | 2.965 | -4.613
35335 | 653.0747 | 503.4519 | 824.6032 | 3.295 | -3.953
35345 | 425.3597 | 312.2577 | 527.6701 | -0.66 | 0.659
35355 | 345.0399 | 86.4708 | 355.7102 | -1.976 | -0.988
35365 | 383.6536 | 22.515 | 384.3137 | -0.659 | -1.977
35375 | 511.6104 | -60.2321 | 515.1438 | -1.647 | -3.624
35385 | 549.1038 | 25.5814 | 549.6993 | 0.988 | -2.635
35395 | 409.3817 | 314.0065 | 515.9394 | 4.612 | 0
35405 | 245.5018 | 598.9312 | 647.2942 | 5.93 | 0.988
35415 | -70.129 | 747.6095 | 750.8915 | 5.272 | 4.612
35425 | -398.9823 | 745.2932 | 845.3691 | 3.624 | 6.26
35435 | -928.6506 | 569.1759 | 1089.1984 | 0.658 | 11.53
35445 | -1495.6072 | 118.5838 | 1500.301 | -4.941 | 14.496
35455 | -1622.3784 | -397.7635 | 1670.4274 | -8.237 | 9.884
35465 | -1297.7074 | -571.7885 | 1418.0926 | -5.27 | 3.294
35475 | -1110.8283 | -755.3949 | 1343.3394 | -6.919 | 3.954
35485 | -979.4322 | -1026.9272 | 1419.1078 | -8.895 | 2.965
35495 | -687.6953 | -982.7607 | 1199.4763 | -4.612 | -0.659
35505 | -478.4702 | -872.5887 | 995.1606 | -3.624 | -0.659
35515 | -163.8006 | -917.9373 | 932.4374 | -5.272 | -3.953
35525 | 204.1803 | -709.2256 | 738.0315 | -0.659 | -6.259
35535 | 652.1944 | -367.7587 | 748.7349 | 2.307 | -9.555
35545 | 1091.0332 | -83.3176 | 1094.2099 | 3.293 | -11.531
35555 | 1439.2311 | 234.0728 | 1458.1414 | 5.601 | -12.189
35565 | 1515.5007 | 499.9553 | 1595.8376 | 6.26 | -9.225
35575 | 1527.0066 | 739.4005 | 1696.6032 | 7.248 | -8.566
35585 | 1449.4021 | 953.59 | 1734.964 | 7.907 | -6.589
35595 | 1216.7171 | 1054.5174 | 1610.0955 | 6.919 | -3.294
35605 | 794.0922 | 1051.2694 | 1317.4785 | 5.601 | 1.318
35615 | 62.0051 | 674.8772 | 677.7196 | -0.989 | 8.894
35625 | -573.9845 | 222.317 | 615.5348 | -3.954 | 10.872
35635 | -1007.4815 | -278.8955 | 1045.3715 | -7.577 | 11.202
35645 | -938.5507 | -759.3611 | 1207.2724 | -9.883 | 4.942
35655 | -712.2809 | -666.5091 | 975.4889 | -2.636 | 2.306
35665 | -740.0669 | -401.3455 | 841.8891 | 0 | 4.942
35675 | -653.6669 | -225.9408 | 691.6138 | 0.329 | 2.306
35685 | -389.0443 | -33.7508 | 390.5055 | 1.977 | -0.989
35695 | -129.2453 | 213.9221 | 249.934 | 3.954 | -2.306
35705 | -329.3356 | 309.8243 | 452.1648 | 2.635 | 3.953
35715 | -496.7314 | 148.0356 | 518.321 | -0.989 | 3.624
35725 | -411.3679 | -73.402 | 417.8653 | -2.635 | 0.66
35735 | -429.4644 | -503.7749 | 661.9885 | -7.577 | 2.306
35745 | -448.2021 | -742.5327 | 867.3177 | -6.26 | 1.976
35755 | -341.3765 | -705.7274 | 783.9573 | -3.294 | 0
35765 | 48.5884 | -402.7895 | 405.7096 | 1.318 | -5.271
35775 | 588.864 | 138.3249 | 604.8922 | 6.918 | -9.554
35785 | 944.8027 | 631.5462 | 1136.443 | 8.895 | -9.225
35795 | 845.2832 | 1031.3044 | 1333.4513 | 10.214 | -3.624
35805 | 310.4145 | 981.1901 | 1029.1215 | 4.611 | 3.954
35815 | -200.8875 | 724.8863 | 752.2073 | 1.319 | 6.26
35825 | -501.2234 | 393.1743 | 637.0329 | -1.648 | 5.93
35835 | -669.0217 | -15.2642 | 669.1958 | -4.942 | 5.601
35845 | -651.931 | -351.568 | 740.6849 | -5.93 | 3.293
35855 | -463.4701 | -340.9714 | 575.3834 | -1.977 | 0.331
35865 | -373.8205 | -134.2929 | 397.2107 | 0.988 | 0.987
35875 | -377.0809 | 79.4066 | 385.3511 | 2.307 | 1.648
35885 | -733.581 | 58.9947 | 735.9494 | -0.329 | 7.577
35895 | -996.5323 | -270.8648 | 1032.688 | -5.272 | 7.248
35905 | -845.9482 | -499.5637 | 982.4419 | -4.942 | 1.977
35915 | -560.7183 | -594.879 | 817.4877 | -4.282 | -0.659
35925 | -321.4804 | -562.9515 | 648.2778 | -2.636 | -1.647
35935 | -94.5782 | -578.8441 | 586.5198 | -3.294 | -2.966
35945 | 157.4965 | -512.9294 | 536.5647 | -1.648 | -4.611
35955 | 375.3078 | -347.0702 | 511.1885 | 0.33 | -5.272
35965 | 353.764 | -310.0464 | 470.4017 | -0.989 | -2.306
35975 | 401.6998 | -286.6501 | 493.4887 | -0.659 | -3.624
35985 | 579.7282 | -54.4001 | 582.275 | 2.966 | -5.601
35995 | 604.1178 | 164.9473 | 626.2315 | 3.624 | -3.624
36005 | 550.6328 | 285.884 | 620.4242 | 3.294 | -2.636
36015 | 504.5953 | 442.2269 | 670.9553 | 4.612 | -2.306
36025 | 522.8172 | 564.4093 | 769.3475 | 4.612 | -2.964
36035 | 433.1607 | 592.58 | 734.0158 | 3.624 | -0.989
36045 | 285.2846 | 421.2583 | 508.7689 | 0.33 | 0.329
36055 | 91.6912 | 257.2764 | 273.1272 | -0.33 | 1.977
36065 | -61.5615 | 200.9283 | 210.1475 | 0.33 | 2.307
36075 | -237.627 | 137.1684 | 274.3752 | -0.33 | 3.623
36085 | -251.4755 | 108.1651 | 273.7511 | 0 | 1.647
36095 | -362.5726 | -2.9794 | 362.5848 | -1.647 | 3.624
36105 | -407.0053 | 4.8737 | 407.0345 | 0 | 2.637
36115 | -429.9633 | -69.8812 | 435.6051 | -1.647 | 2.635
36125 | -416.6547 | -139.4286 | 439.3649 | -1.647 | 1.976
36135 | -352.3358 | -87.1511 | 362.9544 | 0 | 0.989
36145 | -252.6137 | -119.5734 | 279.4843 | -1.318 | 0
36155 | -71.6344 | -102.0122 | 124.6514 | -0.329 | -1.976
36165 | 57.469 | 14.5652 | 59.286 | 1.317 | -1.977
36175 | 213.3018 | 137.9662 | 254.0322 | 1.977 | -3.295
36185 | 155.9717 | 256.7515 | 300.4139 | 2.636 | -0.329
36195 | 76.6879 | 223.8001 | 236.5746 | 0.658 | 0
36205 | 113.2503 | 226.2546 | 253.0153 | 1.318 | -1.318
36215 | 57.1229 | 377.6934 | 381.9886 | 3.624 | 0.329
36225 | -263.644 | 170.7724 | 314.12 | -1.976 | 4.942
36235 | -351.234 | -90.3309 | 362.6638 | -3.295 | 2.306
36245 | -278.7387 | -272.0171 | 389.4722 | -3.624 | 0.659
36255 | -422.3252 | -486.025 | 643.878 | -5.271 | 3.953
36265 | -515.6374 | -567.175 | 766.5307 | -3.954 | 3.295
36275 | -547.7077 | -632.545 | 836.7179 | -4.282 | 2.965
36285 | -304.4219 | -884.2017 | 935.1392 | -7.578 | -1.647
36295 | 211.412 | -758.6469 | 787.5533 | -1.976 | -7.248
36305 | 500.1135 | -363.4009 | 618.202 | 2.635 | -5.93
36315 | 375.905 | -324.7264 | 496.7412 | -1.318 | -0.989
36325 | 344.6432 | -524.7692 | 627.8229 | -4.283 | -2.306
36335 | 438.3979 | -553.8696 | 706.374 | -2.306 | -3.624
36345 | 458.4407 | -605.6136 | 759.5628 | -3.294 | -2.635
36355 | 600.9431 | -694.5494 | 918.4397 | -3.954 | -4.942
36365 | 1183.8603 | -125.6125 | 1190.5056 | 6.919 | -12.849
36375 | 1496.2733 | 620.8603 | 1619.9696 | 11.86 | -10.542
36385 | 1209.715 | 1040.3767 | 1595.5545 | 10.543 | -2.636
36395 | 828.7367 | 895.0231 | 1219.7831 | 3.624 | 0
36405 | 523.3177 | 517.8283 | 736.2116 | -0.66 | 1.318
36415 | 120.6776 | 471.0453 | 486.258 | 2.636 | 4.942
36425 | -339.5017 | 476.3285 | 584.9361 | 2.306 | 7.907
36435 | -601.8475 | 52.4665 | 604.13 | -4.942 | 6.918
36445 | -249.7371 | -125.2799 | 279.3988 | -2.306 | -1.977
36455 | 321.6715 | 282.6253 | 428.1935 | 5.93 | -6.918
36465 | 233.6169 | 471.3604 | 526.0775 | 3.624 | 0.988
36475 | -120.4122 | 317.8537 | 339.8971 | -0.329 | 4.613
36485 | -164.4109 | 155.2338 | 226.116 | -0.989 | 1.317
36495 | -0.90855 | 348.6625 | 348.6637 | 3.955 | -1.317
36505 | -309.1006 | 365.9917 | 479.0544 | 1.317 | 5.93
36515 | -870.8979 | 53.992 | 872.5699 | -3.624 | 10.872
36525 | -1108.8117 | -354.0764 | 1163.9731 | -6.589 | 8.236
36535 | -1084.4432 | -860.535 | 1384.3907 | -10.543 | 5.6
36545 | -1090.8459 | -1393.592 | 1769.758 | -13.507 | 5.93
36555 | -970.6318 | -1922.3068 | 2153.4599 | -16.144 | 3.295
36565 | -731.7031 | -2186.8951 | 2306.0572 | -14.165 | 0.659
36575 | -35.3532 | -1941.8195 | 1942.1413 | -6.919 | -8.566
36585 | 1056.8933 | -1183.615 | 1586.8106 | 2.965 | -18.449
36595 | 1999.9511 | -3.8515 | 1999.9548 | 14.166 | -21.415
36605 | 1571.4312 | 448.2999 | 1634.1263 | 7.907 | -3.294
36615 | 1436.2905 | 720.3621 | 1606.8142 | 8.895 | -7.907
36625 | 1744.1715 | 943.3377 | 1982.9322 | 8.896 | -12.519
36635 | 1711.3959 | 1189.7858 | 2084.3383 | 10.212 | -7.577
36645 | 1176.3834 | 1175.9179 | 1663.3282 | 6.59 | 0.659
36655 | 524.476 | 1043.3152 | 1167.725 | 4.612 | 5.271
36665 | 425.933 | 513.185 | 666.9167 | -3.294 | -0.329
36675 | 673.4586 | 107.7685 | 682.0268 | -3.624 | -4.613
36685 | 809.4212 | 27.1626 | 809.8769 | -0.989 | -3.954
36695 | 758.6527 | 651.5338 | 1000.0251 | 10.213 | -1.976
36705 | 326.0482 | 1022.9731 | 1073.6766 | 8.236 | 4.613
36715 | -117.942 | 677.9158 | 688.099 | -0.987 | 6.588
36725 | -348.936 | 389.9031 | 523.2407 | -0.989 | 5.601
36735 | -532.751 | 162.8972 | 557.0989 | -2.306 | 6.259
36745 | -541.5044 | 220.6521 | 584.7344 | 1.317 | 3.954
36755 | -1043.2645 | -190.7135 | 1060.5529 | -6.918 | 12.519
36765 | -1080.16 | -426.4104 | 1161.2801 | -4.942 | 5.93
36775 | -870.717 | -508.7512 | 1008.4522 | -4.283 | 2.965
36785 | -401.6877 | -380.0985 | 553.017 | -0.988 | -2.965
36795 | -284.5906 | -437.8177 | 522.184 | -3.624 | 0.659
36805 | -225.4426 | -882.7664 | 911.0988 | -9.884 | 0
36815 | 403.7474 | -1053.0358 | 1127.7838 | -6.919 | -9.884
36825 | 877.1021 | -651.4262 | 1092.5494 | 1.319 | -9.554
36835 | 834.7128 | -209.5009 | 860.6021 | 3.624 | -3.953
36845 | 910.0685 | 80.7211 | 913.6413 | 3.953 | -6.259
36855 | 1205.1196 | 358.2694 | 1257.2471 | 5.601 | -9.554
36865 | 1204.6549 | 595.6284 | 1343.8626 | 6.259 | -5.601
36875 | 1120.1568 | 838.55 | 1399.256 | 7.578 | -4.613
36885 | 1122.5044 | 1076.9565 | 1555.5872 | 8.565 | -5.271
36895 | 1069.932 | 1156.6787 | 1575.6459 | 6.919 | -3.954
36905 | 860.6442 | 1113.8514 | 1407.6127 | 5.272 | -0.987
36915 | 750.3527 | 1056.63 | 1295.9537 | 4.611 | -1.648
36925 | 371.181 | 631.5216 | 732.5264 | -2.306 | 3.953
36935 | 19.8839 | 350.2173 | 350.7813 | -1.647 | 4.943
36945 | -204.4458 | 121.7433 | 237.9485 | -2.965 | 4.941
36955 | -413.8723 | -97.7315 | 425.2549 | -3.954 | 5.931
36965 | -725.686 | -251.5756 | 768.0563 | -3.953 | 8.565
36975 | -963.7412 | -166.0425 | 977.9403 | -0.659 | 8.566
36985 | -1090.7272 | -228.4922 | 1114.4032 | -2.965 | 7.907
36995 | -1034.187 | -327.2136 | 1084.7172 | -3.295 | 5.271
37005 | -1055.972 | -723.0034 | 1279.7698 | -8.894 | 6.259
37015 | -682.106 | -1015.0185 | 1222.9191 | -8.566 | -0.988
37025 | 50.6593 | -755.7999 | 757.4957 | -0.988 | -8.566
37035 | 637.5276 | -424.7621 | 766.0706 | 0.988 | -9.883
37045 | 836.5699 | -248.6294 | 872.7347 | 0.658 | -6.919
37055 | 777.5628 | 41.1361 | 778.6501 | 3.954 | -3.953
37065 | 762.0676 | 449.2699 | 884.6414 | 7.248 | -4.283
37075 | 667.0051 | 660.3506 | 938.594 | 5.93 | -2.307
37085 | 487.131 | 709.6963 | 860.7935 | 4.612 | -0.329
37095 | 42.7354 | 440.7808 | 442.8476 | -0.658 | 5.272
37105 | -185.3213 | 240.2118 | 303.3903 | -0.66 | 3.624
37115 | -170.1067 | 77.5892 | 186.9662 | -1.646 | 1.318
37125 | -151.8924 | -358.5028 | 389.3528 | -7.248 | 1.317
37135 | -155.6654 | -956.3638 | 968.9497 | -11.861 | 1.318
37145 | -126.9588 | -1124.6326 | 1131.776 | -7.577 | 0.658
37155 | 160.996 | -776.7141 | 793.2241 | -0.33 | -3.953
37165 | 400.3955 | -483.1619 | 627.5046 | 0.33 | -4.282
37175 | 372.5637 | -93.8122 | 384.1932 | 4.283 | -1.319
37185 | 140.4039 | 431.857 | 454.1076 | 8.565 | 1.977
37195 | 187.9793 | 780.4425 | 802.7619 | 8.237 | -1.647
37205 | 377.6845 | 1039.9493 | 1106.4086 | 8.895 | -3.623
37215 | 297.2106 | 866.3453 | 915.9084 | 2.636 | 0
37225 | 517.9621 | 777.148 | 933.9399 | 3.624 | -5.272
37235 | 891.9023 | 705.432 | 1137.1561 | 2.635 | -8.237
37245 | 784.9356 | 469.3348 | 914.5485 | -0.658 | -1.976
37255 | 662.7067 | 472.1051 | 813.6728 | 2.305 | -1.977
37265 | 534.2861 | 378.0883 | 654.5322 | 0 | -0.658
37275 | 371.4829 | 156.7979 | 403.2185 | -2.305 | 0.658
37285 | 242.4787 | 95.8096 | 260.7209 | -0.66 | 0.989
37295 | -13.1216 | -59.8238 | 61.2459 | -2.965 | 3.953
37305 | -167.4902 | -208.3216 | 267.3029 | -3.294 | 3.295
37315 | -279.0983 | -441.9053 | 522.6626 | -5.601 | 3.624
37325 | -191.745 | -523.4042 | 557.421 | -3.953 | 0.659
37335 | 92.0489 | -393.2059 | 403.8364 | -0.989 | -2.966
37345 | 270.6447 | -280.2429 | 389.5955 | -0.659 | -2.635
37355 | 427.103 | -106.9144 | 440.2813 | 1.318 | -3.624
37365 | 596.6694 | -23.1388 | 597.1179 | 0.659 | -4.613
37375 | 678.9262 | 76.02 | 683.1689 | 1.647 | -3.953
37385 | 731.2435 | 266.6742 | 778.3522 | 3.624 | -3.954
37395 | 794.6351 | 368.8147 | 876.0532 | 2.965 | -4.282
37405 | 905.0078 | 467.2134 | 1018.4927 | 3.624 | -5.272
37415 | 973.1759 | 621.9522 | 1154.9441 | 4.942 | -4.942
37425 | 962.7977 | 662.8053 | 1168.8842 | 3.624 | -3.953
37435 | 899.9549 | 606.4878 | 1085.2402 | 2.306 | -2.965
37445 | 746.7841 | 610.1965 | 964.3787 | 2.966 | -0.988
37455 | 409.5532 | 514.6509 | 657.7229 | 0.987 | 2.965
37465 | 147.1181 | 363.6847 | 392.314 | -0.329 | 3.295
37475 | 41.3044 | 206.5321 | 210.6218 | -1.318 | 2.306
37485 | 13.7609 | 120.7528 | 121.5344 | -0.988 | 1.647
37495 | 65.7547 | 126.6589 | 142.7101 | 0 | 0.329
37505 | 22.166 | 134.2248 | 136.0428 | 0 | 1.648
37515 | -124.7158 | 113.1401 | 168.3885 | -0.329 | 3.295
37525 | -198.1237 | 16.5003 | 198.8096 | -1.648 | 2.635
37535 | -184.5216 | 17.9769 | 185.3952 | -0.329 | 1.647
37545 | -99.9856 | -46.1303 | 110.1141 | -1.647 | 0.329
37555 | -121.3471 | -125.1517 | 174.3218 | -1.977 | 1.648
37565 | -59.6783 | -141.0584 | 153.1632 | -1.318 | 0
37575 | 185.8838 | -14.5439 | 186.4519 | 0.989 | -3.295
37585 | 269.6578 | 22.8927 | 270.6278 | 0 | -1.647
37595 | 435.3464 | 86.8428 | 443.9236 | 0.988 | -3.954
37605 | 646.5915 | 176.5585 | 670.2638 | 1.647 | -5.271
37615 | 678.7689 | 218.9275 | 713.2015 | 1.318 | -3.294
37625 | 686.8995 | 320.1425 | 757.8404 | 2.635 | -3.295
37635 | 648.8489 | 362.0947 | 743.046 | 1.977 | -2.305
37645 | 528.3031 | 306.9545 | 611.0034 | 0.66 | -0.66
37655 | 406.7859 | 246.6937 | 475.7442 | 0.329 | 0
37665 | 311.6642 | 173.7974 | 356.8474 | -0.329 | 0.329
37675 | 422.9518 | 239.1431 | 485.8782 | 1.646 | -2.635
37685 | 385.3464 | 300.4144 | 488.611 | 1.647 | -0.329
37695 | 140.0248 | 219.5567 | 260.4075 | -0.329 | 2.964
37705 | 35.4751 | 189.6056 | 192.8957 | 0.329 | 1.648
37715 | -71.7418 | 297.7064 | 306.2286 | 2.307 | 2.636
37725 | -350.4512 | 17.887 | 350.9073 | -3.954 | 5.93
37735 | -429.2483 | -10.4123 | 429.3746 | -0.329 | 3.624
37745 | -441.9351 | -59.0231 | 445.8591 | -1.648 | 3.295
37755 | -695.3961 | -152.9393 | 712.0156 | -2.306 | 7.247
37765 | -963.4987 | -355.2237 | 1026.8952 | -4.611 | 8.237
37775 | -666.3428 | -278.4894 | 722.1974 | -0.66 | 0
37785 | -472.8442 | -233.9924 | 527.5738 | -1.317 | 0.987
37795 | -410.6326 | -286.2958 | 500.5841 | -2.307 | 1.318
37805 | -378.296 | -313.4106 | 491.2576 | -1.977 | 1.319
37815 | -224.1769 | -271.8933 | 352.3936 | -0.988 | -0.989
37825 | 163.1786 | -107.1551 | 195.2165 | 1.318 | -5.601
37835 | 313.0578 | -25.6874 | 314.1099 | 0.659 | -3.295
37845 | 36.6785 | -63.187 | 73.061 | -0.659 | 2.637
37855 | 14.3697 | 0.059054 | 14.3698 | 0.988 | -0.659
37865 | 109.3659 | 137.3097 | 175.5416 | 2.306 | -1.647
37875 | 135.5377 | 138.638 | 193.8839 | 0.66 | -0.989
37885 | -123.2348 | 47.4865 | 132.0674 | -0.66 | 3.624
37895 | -248.737 | 4.5699 | 248.779 | -0.329 | 2.306
37905 | -113.426 | 43.5003 | 121.4814 | 0.659 | -0.988
37915 | -61.525 | 134.6341 | 148.0259 | 1.647 | 0
37925 | -125.5614 | 199.5771 | 235.7895 | 1.647 | 1.317
37935 | -138.5948 | 182.6733 | 229.2991 | 0.66 | 0.66
37945 | -61.0857 | 165.9057 | 176.7941 | 0.658 | -0.66
37955 | -136.832 | 122.3995 | 183.5882 | 0 | 1.647
37965 | -305.9316 | -24.2396 | 306.8903 | -1.976 | 3.295
37975 | -327.7874 | -94.713 | 341.1967 | -1.318 | 1.648
37985 | -248.7121 | -14.8142 | 249.1529 | 0.658 | 0.329
37995 | -329.3515 | -104.168 | 345.4321 | -1.976 | 2.636
38005 | -427.6496 | -173.3622 | 461.4527 | -1.647 | 2.964
38015 | -337.1384 | -114.5077 | 356.0538 | 0 | 0.33
38025 | -181.8006 | -27.4486 | 183.8611 | 0.659 | -0.988
38035 | -195.9481 | -30.4593 | 198.3014 | -0.329 | 0.988
38045 | -169.2045 | -82.4378 | 188.2183 | -0.989 | 0
38055 | -41.2445 | -80.6087 | 90.5476 | -0.33 | -1.648
38065 | 150.246 | 23.9779 | 152.1473 | 1.319 | -3.293
38075 | 151.3929 | 26.2556 | 153.6528 | 0 | -0.989
38085 | 74.8103 | -26.5499 | 79.3819 | -0.66 | 0
38095 | 28.847 | -61.8461 | 68.2429 | -0.659 | 0
38105 | 160.3147 | -24.414 | 162.163 | 0.33 | -2.635
38115 | 270.648 | 7.8582 | 270.762 | 0.329 | -2.637
38125 | 126.0801 | -51.2899 | 136.1134 | -0.988 | 0.989
38135 | 24.8847 | -100.8696 | 103.8938 | -0.989 | 0.659
38145 | 14.3746 | -90.9061 | 92.0355 | -0.329 | 0
38155 | 33.0766 | -60.4758 | 68.9303 | 0 | -0.33
38165 | -12.0709 | -79.616 | 80.5258 | -0.659 | 0.659
38175 | -12.7219 | -195.5214 | 195.9349 | -2.305 | 0
38185 | 263.7681 | -33.7761 | 265.9219 | 1.976 | -4.612
38195 | 403.2268 | 91.2709 | 413.4274 | 1.647 | -3.295
38205 | 260.3389 | 99.2716 | 278.6237 | 0.659 | 0.33
38215 | 88.0881 | 59.5289 | 106.3165 | 0 | 1.318
38225 | 41.3887 | 33.9661 | 53.5417 | 0 | 0.329
38235 | 139.701 | 117.8322 | 182.7589 | 1.648 | -1.647
38245 | 101.239 | 148.9868 | 180.1288 | 0.987 | 0.33
38255 | -100.4185 | 122.1319 | 158.1141 | 0.33 | 2.964
38265 | -152.3004 | 45.3186 | 158.8999 | -0.659 | 1.319
38275 | 6.8702 | 183.3185 | 183.4472 | 2.635 | -1.648
38285 | 127.0963 | 227.7083 | 260.7768 | 1.318 | -1.647
38295 | -132.6904 | 179.9624 | 223.5916 | 0.33 | 3.953
38305 | -502.5063 | 31.0904 | 503.4672 | -1.648 | 6.59
38315 | -250.0772 | -115.1269 | 275.3049 | -2.306 | -1.977
38325 | -11.7462 | -267.2563 | 267.5143 | -3.294 | -1.977
38335 | -60.5388 | -490.2524 | 493.9761 | -5.271 | 0.988
38345 | -255.0248 | -615.8959 | 666.6074 | -4.613 | 3.295
38355 | -237.6438 | -483.0167 | 538.3119 | -0.988 | 0.658
38365 | 128.3588 | -89.6819 | 156.5848 | 3.954 | -4.941
38375 | 345.8227 | 150.0018 | 376.9535 | 3.295 | -3.954
38385 | 405.5681 | 129.4391 | 425.7229 | 0.658 | -2.964
38395 | 463.4845 | 60.8554 | 467.4626 | 0 | -3.295
38405 | 304.0741 | -52.2713 | 308.5342 | -1.318 | 0.329
38415 | 100.7351 | -72.4452 | 124.0801 | -0.329 | 1.647
38425 | 31.1671 | 62.6313 | 69.9576 | 1.976 | 0.66
38435 | 288.5067 | 128.653 | 315.8919 | 1.318 | -4.284
38445 | 512.3103 | 198.4712 | 549.4112 | 1.977 | -4.611
38455 | 627.5972 | 195.733 | 657.4113 | 0.988 | -4.284
38465 | 645.2713 | 322.1973 | 721.2394 | 3.295 | -3.294
38475 | 465.2957 | 507.2649 | 688.3442 | 4.613 | 0
38485 | 101.3205 | 444.5804 | 455.9798 | 1.317 | 3.953
38495 | 19.5089 | 359.5699 | 360.0988 | 0.989 | 0.988
38505 | -93.6481 | 375.2999 | 386.8074 | 1.976 | 2.637
38515 | -39.9168 | 73.5385 | 83.6736 | -3.624 | 0
38525 | 91.8831 | -169.2761 | 192.6056 | -3.624 | -1.319
38535 | 2.7523 | -253.8737 | 253.8886 | -2.635 | 1.648
38545 | -586.8122 | -439.2428 | 732.9958 | -4.942 | 10.212
38555 | -632.3212 | -551.3443 | 838.9342 | -4.283 | 3.295
38565 | -240.7836 | -275.6419 | 365.9989 | 1.648 | -2.635
38575 | 109.6475 | -154.5339 | 189.4817 | 0 | -3.953
38585 | -139.0871 | -286.9259 | 318.86 | -2.966 | 3.953
38595 | -237.4046 | -415.9575 | 478.938 | -3.295 | 1.647
38605 | -27.2218 | -495.4997 | 496.2469 | -3.294 | -2.307
38615 | 328.2298 | -511.277 | 607.5681 | -2.636 | -5.6
38625 | 459.1919 | -310.2905 | 554.1998 | 0.989 | -3.624
38635 | 214.5415 | -195.5969 | 290.3208 | 0.329 | 1.647
38645 | 351.4279 | -102.0542 | 365.9462 | 0.988 | -3.953
38655 | 624.7532 | 119.29 | 636.0398 | 3.624 | -5.93
38665 | 635.7244 | 401.1991 | 751.7355 | 5.601 | -2.966
38675 | 272.3566 | 521.5362 | 588.369 | 4.283 | 2.966
38685 | 22.5082 | 668.2815 | 668.6605 | 5.6 | 2.635
38695 | -153.6833 | 578.3431 | 598.414 | 1.978 | 3.295
38705 | 319.9969 | 229.1941 | 393.6089 | -2.636 | -6.918
38715 | 401.861 | 330.2259 | 520.1359 | 3.294 | -1.647
38725 | -62.5948 | -131.0696 | 145.2493 | -6.918 | 5.929
38735 | -873.2902 | -704.223 | 1121.8582 | -9.884 | 13.837
38745 | -752.6614 | -615.2058 | 972.0995 | -1.976 | 1.977
38755 | -524.4529 | -472.9472 | 706.2081 | -1.648 | 1.318
38765 | -478.1394 | -548.8728 | 727.9276 | -3.953 | 2.306
38775 | -396.2374 | -899.8892 | 983.2623 | -8.566 | 0.989
38785 | -105.8298 | -1149.0117 | 1153.8751 | -8.236 | -2.966
38795 | 300.4185 | -786.163 | 841.6077 | 0.659 | -6.259
38805 | 619.072 | -470.9968 | 777.8741 | 0.988 | -6.919
38815 | 789.6339 | -108.3124 | 797.0278 | 4.283 | -6.259
38825 | 981.9254 | 360.1951 | 1045.9054 | 7.907 | -7.577
38835 | 1231.4625 | 612.9223 | 1375.563 | 6.589 | -9.225
38845 | 1593.5557 | 728.3108 | 1752.1006 | 5.93 | -12.19
38855 | 1290.6438 | 548.4967 | 1402.3587 | 1.318 | -2.306
38865 | 811.7175 | 335.755 | 878.4171 | 0 | 1.318
38875 | 400.8218 | 329.0041 | 518.5574 | 1.977 | 3.294
38885 | 310.8243 | 123.1074 | 334.316 | -1.977 | 0.33
38895 | 454.906 | 492.8465 | 670.699 | 7.248 | -2.636
38905 | 520.523 | 496.2734 | 719.1881 | 1.647 | -1.977
38915 | 370.7862 | 601.9171 | 706.9558 | 4.612 | 0.989
38925 | 152.3019 | 639.0375 | 656.9359 | 3.295 | 2.635
38935 | -284.663 | 459.6307 | 540.6417 | 0 | 7.577
38945 | -244.3918 | -116.0786 | 270.5579 | -7.577 | 1.318
38955 | -218.9764 | -78.2933 | 232.5522 | 0.329 | 2.306
38965 | -759.0182 | -64.0163 | 761.713 | -1.318 | 11.202
38975 | -732.4214 | -424.0204 | 846.3063 | -6.919 | 3.294
38985 | -21.573 | -266.514 | 267.3857 | 0.66 | -7.248
38995 | 569.4463 | 41.921 | 570.9873 | 2.964 | -8.566
39005 | 734.0174 | -74.6017 | 737.7987 | -2.306 | -5.27
39015 | 756.765 | -128.8767 | 767.6603 | -0.987 | -4.284
39025 | 536.4139 | 129.9566 | 551.9317 | 3.623 | 0
39035 | 86.1034 | -70.7059 | 111.4142 | -3.294 | 4.942
39045 | -149.7978 | -291.6477 | 327.8685 | -3.624 | 3.624
39055 | 50.2324 | -380.3682 | 383.6708 | -2.966 | -1.976
39065 | 256.691 | -471.9289 | 537.2217 | -3.624 | -2.636
39075 | 450.9608 | -410.4319 | 609.7704 | -1.317 | -3.954
39085 | 526.3611 | -10.7812 | 526.4715 | 4.612 | -2.964
39095 | 393.6951 | 247.6195 | 465.0927 | 3.953 | 0
39105 | 252.4983 | 295.7202 | 388.8519 | 2.306 | 0.658
39115 | 206.6184 | 261.8405 | 333.544 | 1.318 | 0
39125 | 301.0778 | 263.6816 | 400.2197 | 1.648 | -1.976
39135 | 299.3553 | 316.2005 | 435.4266 | 2.306 | -0.659
39145 | 472.8863 | 475.7453 | 670.7868 | 4.282 | -3.953
39155 | 444.3172 | 579.9047 | 730.5527 | 3.955 | -0.989
39165 | 413.1864 | 529.7923 | 671.8652 | 1.976 | -1.318
39175 | 387.6082 | 565.7916 | 685.8281 | 3.294 | -0.988
39185 | 235.8814 | 767.157 | 802.6019 | 5.931 | 1.317
39195 | 197.009 | 692.5145 | 719.9923 | 1.977 | 0
39205 | 208.0802 | 514.3749 | 554.8684 | 0.329 | -0.329
39215 | 270.1236 | 633.7145 | 688.8838 | 4.282 | -1.317
39225 | 238.4748 | 504.7315 | 558.233 | 0 | 0
39235 | 164.422 | 242.7084 | 293.1586 | -2.305 | 0.658
39245 | 344.2706 | 9.1209 | 344.3914 | -3.295 | -3.294
39255 | 34.0656 | -68.0636 | 76.1125 | -1.977 | 4.612
39265 | 23.6231 | -570.868 | 571.3566 | -9.883 | 0
39275 | 18.1597 | -476.3019 | 476.648 | -1.318 | 0.988
39285 | 490.2208 | -409.8099 | 638.9527 | -2.635 | -7.577
39295 | 1059.2772 | -203.3623 | 1078.6215 | 0.987 | -10.872
39305 | 1107.3519 | 452.3109 | 1196.1661 | 9.554 | -5.271
39315 | 572.8776 | 358.1055 | 675.5948 | -0.329 | 3.623
39325 | -87.3489 | -288.3064 | 301.2481 | -8.565 | 8.237
39335 | -135.5194 | -1031.4371 | 1040.3019 | -13.508 | 1.648
39345 | -23.7912 | -1434.3718 | 1434.5691 | -11.86 | 0.329
39355 | 280.6661 | -1277.1273 | 1307.6037 | -4.942 | -3.953
39365 | 692.3848 | -529.4118 | 871.5925 | 5.6 | -7.248
39375 | 1106.5185 | 2.2102 | 1106.5207 | 5.601 | -9.554
39385 | 1005.3821 | 517.0578 | 1130.5494 | 9.225 | -2.966
39395 | 774.0441 | 768.6662 | 1090.8676 | 7.248 | -0.988
39405 | 427.7142 | 1034.7942 | 1119.7046 | 9.224 | 2.636
39415 | 379.8169 | 1172.0272 | 1232.0343 | 7.907 | -0.659
39425 | 484.3964 | 1362.3515 | 1445.905 | 9.554 | -2.306
39435 | 381.5189 | 1601.7401 | 1646.5503 | 10.872 | 0.659
39445 | 262.9259 | 1593.1017 | 1614.6527 | 7.577 | 0.987
39455 | -79.618 | 1347.1627 | 1349.5134 | 3.624 | 5.601
39465 | -534.9535 | 819.0245 | 978.2517 | -2.635 | 8.896
39475 | -1102.4823 | 200.6502 | 1120.5926 | -6.918 | 13.178
39485 | -1568.7602 | -117.0885 | 1573.1238 | -5.272 | 14.166
39495 | -1351.3705 | -686.9889 | 1515.967 | -11.86 | 4.942
39505 | -1003.9809 | -996.7968 | 1414.7726 | -9.554 | 2.306
39515 | -655.4407 | -1546.5154 | 1679.6763 | -15.814 | -0.33
39525 | -280.099 | -1853.0535 | 1874.1032 | -13.507 | -2.964
39535 | -125.7095 | -1834.4155 | 1838.7177 | -9.884 | -1.318
39545 | 222.5257 | -1638.5119 | 1653.5535 | -6.589 | -5.93
39555 | 804.9702 | -1487.1342 | 1691.0189 | -5.93 | -11.202
39565 | 1570.4208 | -1091.1135 | 1912.2632 | -0.329 | -17.131
39575 | 2099.3355 | -537.3569 | 2167.0168 | 4.282 | -16.802
39585 | 2180.3765 | 508.8149 | 2238.9583 | 15.814 | -12.19
39595 | 2421.6153 | 677.1235 | 2514.5014 | 5.601 | -15.484
39605 | 2521.0908 | 990.6103 | 2708.728 | 10.872 | -13.178
39615 | 2476.5211 | 1367.6384 | 2829.062 | 12.189 | -11.202
39625 | 2660.5906 | 2060.154 | 3364.9631 | 19.438 | -14.496
39635 | 2418.8434 | 1518.6709 | 2856.075 | 0.989 | -7.248
39645 | 1717.1371 | 466.891 | 1779.4794 | -8.567 | 1.318
39655 | 730.0917 | -273.9828 | 779.808 | -9.554 | 9.884
39665 | -44.675 | -1914.3201 | 1914.8413 | -29.98 | 11.531
39675 | -83.0996 | -3119.0952 | 3120.2019 | -29.32 | 3.623
39685 | 267.3969 | -3198.4959 | 3209.6537 | -17.791 | -1.976
39695 | 511.2882 | -2571.6513 | 2621.9851 | -6.919 | -2.306
39705 | 654.0575 | -1646.1571 | 1771.3341 | 1.977 | -2.636
39715 | 333.7999 | -721.1863 | 794.6899 | 7.577 | 4.283
39725 | -33.47 | -583.1122 | 584.072 | -0.329 | 5.93
39735 | -271.0822 | -365.4872 | 455.0456 | 3.295 | 5.93
39745 | -180.2772 | -45.5437 | 185.9411 | 5.271 | 1.647
39755 | 514.5659 | -8.8642 | 514.6422 | 1.977 | -8.894
39765 | 912.7475 | 514.6368 | 1047.8354 | 10.872 | -6.919
39775 | 926.9621 | 1011.5932 | 1372.0713 | 11.86 | -3.624
39785 | 841.662 | 1221.0504 | 1483.0236 | 9.883 | -2.306
39795 | 679.8255 | 1399.1366 | 1555.5533 | 10.543 | -0.33
39805 | 762.3805 | 996.5335 | 1254.7123 | 0.989 | -3.623
39815 | 738.1141 | 699.6925 | 1017.0457 | 1.317 | -1.648
39825 | 602.5132 | 403.893 | 725.3631 | -1.317 | 0
39835 | 334.3477 | -106.1104 | 350.7817 | -6.59 | 2.965
39845 | -128.7573 | -701.9852 | 713.6958 | -10.543 | 7.577
39855 | 228.036 | -1169.7616 | 1191.7813 | -11.53 | -4.282
39865 | 793.6805 | -1292.4458 | 1516.6888 | -8.236 | -8.236
39875 | 902.1606 | -1440.4228 | 1699.621 | -9.554 | -3.954
39885 | 692.6037 | -1197.4309 | 1383.3079 | -2.966 | 0
39895 | 599.4527 | -927.3988 | 1104.2699 | -1.647 | -0.988
39905 | 276.9713 | -585.4171 | 647.6313 | 1.647 | 3.953
39915 | 256.0673 | -427.6916 | 498.4882 | 0.329 | 0
39925 | 690.0365 | -405.964 | 800.598 | -0.658 | -6.919
39935 | 1110.0682 | -125.3207 | 1117.1198 | 3.953 | -8.565
39945 | 1394.4495 | 218.3239 | 1411.4372 | 5.93 | -8.895
39955 | 1506.5678 | 374.6263 | 1552.4469 | 4.613 | -7.578
39965 | 2118.8664 | 872.8158 | 2291.5939 | 11.531 | -16.802
39975 | 2690.9643 | 1387.416 | 3027.5753 | 13.507 | -18.12
39985 | 3395.2431 | 1468.4475 | 3699.1909 | 8.895 | -23.72
39995 | 3712.1431 | 1481.2754 | 3996.7716 | 8.566 | -20.097
40005 | 3409.2147 | 1488.4857 | 3719.9912 | 7.907 | -11.53
40015 | 3095.5055 | 1033.4563 | 3263.4623 | -0.33 | -9.885
40025 | 2689.1544 | 960.0982 | 2855.4054 | 4.284 | -5.6
40035 | 2189.7496 | 641.9055 | 2281.8953 | -1.648 | -1.648
40045 | 1608.2398 | 34.1116 | 1608.6015 | -7.577 | 2.637
40055 | 1459.3165 | -28.5001 | 1459.5948 | -1.318 | -1.648
40065 | 1903.7738 | -121.0846 | 1907.6206 | -3.295 | -10.212
40075 | 2452.3437 | -341.9845 | 2476.0741 | -5.27 | -13.838
40085 | 2749.402 | -509.9145 | 2796.2876 | -5.272 | -12.849
40095 | 3099.6518 | -279.6245 | 3112.2389 | 0.659 | -15.813
40105 | 3291.0748 | 444.6301 | 3320.9741 | 9.883 | -14.496
40115 | 2896.1172 | 1042.1932 | 3077.9314 | 11.201 | -5.601
40125 | 3165.5654 | 1337.7621 | 3436.628 | 9.885 | -15.484
40135 | 3638.9136 | 892.369 | 3746.7339 | -0.989 | -18.449
40145 | 3958.4086 | 93.5749 | 3959.5145 | -8.565 | -18.449
40155 | 3462.7968 | -365.3123 | 3482.013 | -7.248 | -6.26
40165 | 3176.4908 | -224.0919 | 3184.3855 | -0.331 | -8.237
40175 | 2215.336 | -49.6809 | 2215.893 | 0.331 | 6.261
40185 | 840.5938 | -22.457 | 840.8937 | -0.66 | 17.131
40195 | 295.0589 | -140.2829 | 326.7095 | -2.635 | 10.213
40205 | 198.1783 | -658.228 | 687.4146 | -9.883 | 6.918
40215 | 161.9057 | -1112.2465 | 1123.9688 | -10.873 | 5.93
40225 | 574.7732 | -1462.2856 | 1571.1917 | -11.86 | -2.306
40235 | 873.3798 | -808.8448 | 1190.3874 | 3.624 | -2.306
40245 | 1210.5789 | -120.7101 | 1216.5822 | 6.26 | -5.6
40255 | 1480.1084 | 326.0079 | 1515.5864 | 6.918 | -6.26
40265 | 1280.8926 | 475.0458 | 1366.1458 | 4.612 | 0
40275 | 616.8349 | 944.8809 | 1128.3994 | 11.202 | 8.236
40285 | -172.902 | 1423.2878 | 1433.7515 | 12.849 | 13.508
40295 | 381.4789 | 1402.3606 | 1453.3208 | 6.917 | -5.272
40305 | 1317.5651 | 1568.6018 | 2048.5335 | 10.543 | -12.519
40315 | 1778.6185 | 1710.198 | 2467.4401 | 9.883 | -10.213
40325 | 1722.4391 | 1022.4432 | 2003.0443 | -3.624 | -4.942
40335 | 1906.9298 | 446.2329 | 1958.4445 | -4.282 | -9.225
40345 | 2341.7728 | 117.7231 | 2344.7299 | -4.283 | -13.507
40355 | 2527.3967 | 23.2356 | 2527.5035 | -2.306 | -11.201
40365 | 2439.1897 | 814.1207 | 2571.4663 | 12.189 | -7.907
40375 | 2128.9783 | 471.3737 | 2180.5371 | -4.282 | -3.624
40385 | 1091.9149 | -396.1891 | 1161.5696 | -12.19 | 10.543
40395 | 879.1905 | -1096.0104 | 1405.0675 | -14.166 | 0.988
40405 | 800.2547 | -1838.8193 | 2005.4087 | -19.108 | 1.976
40415 | 892.2517 | -2187.0416 | 2362.0466 | -15.814 | -1.318
40425 | 79.2689 | -2540.4616 | 2541.698 | -18.121 | 13.838
40435 | -869.0714 | -2511.4196 | 2657.539 | -12.518 | 18.449
40445 | -1788.7721 | -1711.9633 | 2475.9895 | 0.659 | 23.391
40455 | -1253.154 | -1672.7163 | 2090.0657 | -8.567 | 2.965
40465 | -418.6567 | -2152.5 | 2192.836 | -14.825 | -2.965
40475 | -407.5417 | -2717.2543 | 2747.6464 | -18.448 | 5.271
40485 | -899.288 | -2763.9368 | 2906.5556 | -12.52 | 11.86
40495 | -1071.6306 | -2506.3737 | 2725.8579 | -8.237 | 8.566
40505 | -707.4682 | -1750.4568 | 1888.0175 | 1.978 | 0.989
40515 | -414.997 | -1477.8355 | 1534.9985 | -2.636 | 0.659
40525 | -241.0499 | -1417.1472 | 1437.5018 | -3.295 | 0.329
40535 | -174.1625 | -1793.0804 | 1801.5188 | -10.542 | 0.989
40545 | -331.6677 | -1841.1313 | 1870.7667 | -6.26 | 4.282
40555 | 20.3222 | -1873.0687 | 1873.179 | -7.247 | -3.953
40565 | 595.4035 | -1764.299 | 1862.057 | -4.613 | -8.566
40575 | 754.5592 | -1022.3509 | 1270.6538 | 6.589 | -4.612
40585 | 971.8192 | -554.1184 | 1118.6955 | 4.942 | -7.248
40595 | 871.1539 | 53.7445 | 872.8102 | 10.872 | -2.306
40605 | 523.1395 | 381.5224 | 647.4831 | 8.566 | 1.977
40615 | 461.1217 | 735.8318 | 868.3788 | 11.201 | -0.989
40625 | 542.6847 | 1003.3065 | 1140.6712 | 10.871 | -2.306
40635 | 754.4569 | 660.4036 | 1002.6655 | 1.648 | -4.942
40645 | 622.658 | 930.328 | 1119.4701 | 10.872 | 0
40655 | 702.7772 | 1216.838 | 1405.2012 | 10.543 | -3.624
40665 | 707.0679 | 1243.9218 | 1430.8342 | 7.906 | -1.977
40675 | 497.9323 | 1108.2677 | 1214.9872 | 5.272 | 1.318
40685 | 111.092 | 932.9388 | 939.5298 | 3.624 | 5.272
40695 | -527.9617 | 506.1323 | 731.3777 | -1.977 | 11.53
40705 | -873.8146 | 27.8359 | 874.2579 | -4.942 | 9.554
40715 | -1193.1315 | -1265.6002 | 1739.3409 | -21.744 | 11.531
40725 | -1463.0051 | -1741.8034 | 2274.7006 | -13.178 | 11.861
40735 | -2238.0286 | -1893.0281 | 2931.2672 | -12.19 | 21.743
40745 | -2063.3382 | -2268.115 | 3066.2208 | -16.143 | 8.237
40755 | -1956.66 | -1969.8429 | 2776.4725 | -5.601 | 10.213
40765 | -1628.6343 | -2209.9638 | 2745.2485 | -14.166 | 4.282
40775 | -967.0377 | -3360.9778 | 3497.3324 | -28.992 | -2.964
40785 | -664.5765 | -2794.4643 | 2872.4019 | -4.282 | -0.33
40795 | -902.4732 | -1804.333 | 2017.4428 | 2.635 | 6.26
40805 | -622.3511 | -1818.9229 | 1922.4467 | -7.907 | -1.977
40815 | -2.1218 | -1707.5506 | 1707.5519 | -3.624 | -7.907
40825 | 316.4134 | -1247.0979 | 1286.612 | 1.977 | -5.93
40835 | 786.4986 | -738.7791 | 1079.0619 | 4.942 | -10.872
40845 | 1020.768 | -204.4806 | 1041.0473 | 8.236 | -8.566
40855 | 835.6514 | 249.3794 | 872.0684 | 9.554 | -2.964
40865 | 737.6803 | 507.5745 | 895.4352 | 8.566 | -3.624
40875 | 871.6376 | 746.3679 | 1147.5266 | 9.554 | -6.261
40885 | 419.1607 | 614.504 | 743.8487 | 3.953 | 3.624
40895 | 931.1793 | 8.3546 | 931.2168 | -4.612 | -11.53
40905 | 985.1454 | 44.2701 | 986.1395 | 3.294 | -3.954
40915 | 846.3365 | 212.1889 | 872.5306 | 3.954 | -2.636
40925 | 467.8606 | -187.2768 | 503.9506 | -4.612 | 2.636
40935 | 1076.9137 | -650.3092 | 1258.0323 | -6.919 | -12.519
40945 | 1100.8375 | -615.6787 | 1261.3102 | -1.317 | -3.624
40955 | 1235.8057 | -445.8083 | 1313.7582 | 0.329 | -7.577
40965 | 1313.1036 | -306.1613 | 1348.3233 | 0.988 | -6.26
40975 | 1681.4609 | -143.1857 | 1687.5465 | 2.307 | -11.861
40985 | 2290.9187 | -239.8964 | 2303.445 | -1.318 | -17.131
40995 | 2000.7818 | -506.6259 | 2063.9277 | -4.283 | -4.612
41005 | 1982.406 | -825.605 | 2147.4537 | -6.589 | -9.224
41015 | 1740.0096 | -1619.8991 | 2377.3318 | -16.473 | -3.624
41025 | 1445.849 | -1488.0687 | 2074.8079 | -3.954 | -1.977
41035 | 1305.8945 | -1438.2809 | 1942.6818 | -6.588 | -2.636
41045 | 1596.2983 | -1328.2474 | 2076.6342 | -3.954 | -8.895
41055 | 2009.5656 | -534.3767 | 2079.4019 | 8.237 | -11.861
41065 | 2460.2904 | 873.1883 | 2610.6487 | 22.073 | -14.825
41075 | 2143.6621 | 1408.0564 | 2564.7436 | 14.166 | -3.953
41085 | 2738.5352 | 784.7574 | 2848.7575 | -0.988 | -19.108
41095 | 3972.5035 | -344.3713 | 3987.4021 | -12.19 | -30.639
41105 | 4176.0495 | -865.8522 | 4264.8669 | -8.236 | -19.109
41115 | 3823.6375 | -1069.9111 | 3970.5055 | -7.248 | -12.518
41125 | 3266.1277 | -1347.5727 | 3533.2057 | -9.554 | -6.59
41135 | 3199.1277 | -2682.3658 | 4174.8658 | -28.663 | -11.531
41145 | 2891.1317 | -3742.372 | 4729.0581 | -28.991 | -5.6
41155 | 2813.1563 | -4372.0186 | 5198.884 | -28.333 | -8.566
41165 | 2713.7501 | -4512.8047 | 5265.9136 | -23.062 | -6.918
41175 | 2131.3022 | -4697.8649 | 5158.7192 | -24.38 | 1.647
41185 | 1609.2431 | -4633.4719 | 4904.9694 | -19.766 | 2.965
41195 | 1240.4407 | -4064.5762 | 4249.6438 | -10.543 | 3.624
41205 | 833.0391 | -3098.8398 | 3208.8568 | -0.659 | 6.26
41215 | 258.9122 | -1967.1853 | 1984.1506 | 7.578 | 10.871
41225 | -496.802 | -994.0994 | 1111.3262 | 11.201 | 16.473
41235 | -878.5099 | 574.8624 | 1049.8793 | 27.015 | 13.507
41245 | -892.3808 | 994.2478 | 1335.9911 | 14.167 | 9.555
41255 | -803.4426 | 1698.8021 | 1879.2149 | 23.39 | 7.577
41265 | -781.8296 | 1980.8702 | 2129.5785 | 17.462 | 7.578
41275 | -1000.3011 | 2266.6925 | 2477.5991 | 19.437 | 10.871
41285 | -1313.4532 | 2486.3671 | 2811.9709 | 18.449 | 12.849
41295 | -1415.322 | 2460.9839 | 2838.9396 | 14.826 | 10.542
41305 | -1233.5392 | 2295.5024 | 2605.9452 | 11.86 | 6.26
41315 | -1132.9736 | 2200.5494 | 2475.0852 | 11.531 | 6.589
41325 | -703.7165 | 2029.4662 | 2148.0107 | 8.895 | -0.329
41335 | -480.8948 | 1658.9031 | 1727.1998 | 4.283 | 1.317
41345 | -284.4517 | 1814.2114 | 1836.3757 | 11.202 | -0.329
41355 | -393.0991 | 1849.3141 | 1890.632 | 8.565 | 3.953
41365 | -426.89 | 2209.0764 | 2249.9452 | 14.825 | 2.636
41375 | -464.0088 | 2649.8942 | 2690.2125 | 17.132 | 3.295
41385 | -459.9824 | 2590.4177 | 2630.9405 | 10.872 | 2.635
41395 | -184.4894 | 2399.311 | 2406.3935 | 8.895 | -1.977
41405 | 123.9507 | 2435.1328 | 2438.2853 | 11.202 | -3.624
41415 | 285.6862 | 909.4137 | 953.2313 | -16.144 | -2.965
41425 | 211.194 | 23.6773 | 212.5171 | -10.542 | 0
41435 | 282.1329 | -178.8932 | 334.0685 | -6.26 | -2.306
41445 | 56.4233 | 306.7911 | 311.9365 | 4.283 | 2.966
41455 | -288.1339 | 897.6812 | 942.7898 | 8.236 | 5.6
41465 | -516.7193 | 1818.6508 | 1890.632 | 17.79 | 5.601
41475 | -25.6493 | 2246.481 | 2246.6274 | 13.838 | -5.272
41485 | 876.7397 | 2607.8458 | 2751.2783 | 16.142 | -13.837
41495 | 1326.6526 | 2221.5407 | 2587.5181 | 4.613 | -10.871
41505 | 1327.3144 | 1414.6562 | 1939.8494 | -3.624 | -6.59
41515 | 1320.0697 | 1260.3639 | 1825.1304 | 2.966 | -6.588
41525 | 1351.855 | 2036.7344 | 2444.5448 | 16.472 | -6.59
41535 | 1143.3789 | 2865.3916 | 3085.0907 | 20.426 | -2.306
41545 | 853.7348 | 3035.3106 | 3153.0895 | 14.166 | 0
41555 | 689.3655 | 2655.803 | 2743.8138 | 6.589 | -0.329
41565 | 636.6193 | 2101.1289 | 2195.4559 | 1.647 | -0.989
41575 | 415.4107 | 1340.2347 | 1403.1376 | -5.27 | 2.306
41585 | 47.8302 | 178.0758 | 184.3874 | -16.144 | 5.601
41595 | -175.1752 | -557.5437 | 584.4154 | -14.496 | 4.942
41605 | -486.2157 | -1032.2703 | 1141.0467 | -14.825 | 7.907
41615 | -400.8484 | -1499.8066 | 1552.4494 | -16.802 | 2.306
41625 | -729.014 | -1633.6946 | 1788.9717 | -12.849 | 9.555
41635 | -1130.5345 | -1689.7612 | 2033.0768 | -12.189 | 11.201
41645 | -1766.9074 | -1430.3125 | 2273.2698 | -6.26 | 17.46
41655 | -2286.019 | -1023.3516 | 2504.622 | -2.306 | 18.121
41665 | -2619.3269 | -754.7248 | 2725.8912 | -1.977 | 17.79
41675 | -2634.7449 | -283.3613 | 2649.9385 | 3.624 | 13.837
41685 | -2458.9077 | -172.955 | 2464.9829 | -0.329 | 10.542
41695 | -2249.6332 | -441.106 | 2292.4712 | -5.272 | 8.566
41705 | -2233.0479 | -778.5313 | 2364.8707 | -7.577 | 10.213
41715 | -2206.4862 | -694.748 | 2313.2783 | -2.306 | 9.224
41725 | -1866.5373 | -460.4836 | 1922.5001 | 0 | 3.624
41735 | -1615.0812 | -158.8208 | 1622.8713 | 2.635 | 3.624
41745 | -1419.4909 | -11.3066 | 1419.536 | 1.648 | 2.636
41755 | -1499.6966 | 30.225 | 1500.0011 | 0.989 | 6.26
41765 | -1756.9609 | 154.5781 | 1763.7477 | 2.635 | 9.225
41775 | -1668.5479 | 333.8322 | 1701.6157 | 3.953 | 4.611
41785 | -1642.9033 | 174.6931 | 1652.165 | -0.988 | 5.93
41795 | -1481.9452 | 263.7261 | 1505.2286 | 2.965 | 2.966
41805 | -1315.0718 | 663.2507 | 1472.8595 | 7.906 | 2.306
41815 | -788.3233 | 997.6074 | 1271.485 | 8.567 | -4.941
41825 | -366.7127 | 1156.3558 | 1213.1105 | 7.577 | -5.272
41835 | -160.5511 | 1128.1157 | 1139.4831 | 5.271 | -4.283
41845 | -521.4014 | 1071.9001 | 1191.9855 | 4.612 | 4.283
41855 | -1036.6206 | 1091.1936 | 1505.0866 | 5.272 | 8.236
41865 | -1500.1883 | 874.543 | 1736.488 | 0.988 | 10.543
41875 | -1862.1491 | 283.4653 | 1883.6007 | -6.26 | 11.531
41885 | -1971.2181 | 30.0805 | 1971.4476 | -3.294 | 9.224
41895 | -2130.4041 | -147.7502 | 2135.5214 | -4.283 | 10.872
41905 | -2213.7751 | -288.34 | 2232.474 | -4.283 | 9.884
41915 | -1907.4821 | -255.6206 | 1924.5337 | -1.976 | 3.624
41925 | -1482.5779 | -151.4255 | 1490.2909 | -0.659 | 0.329
41935 | -1208.4591 | 312.2995 | 1248.1604 | 6.259 | 0.329
41945 | -1236.0958 | 505.4478 | 1335.4439 | 3.624 | 3.624
41955 | -1201.2154 | 625.8611 | 1354.4816 | 4.283 | 2.307
41965 | -786.6653 | 913.2042 | 1205.315 | 7.577 | -3.954
41975 | -500.9765 | 961.4111 | 1084.1073 | 4.613 | -3.294
41985 | -292.3355 | 1276.3011 | 1309.3527 | 9.883 | -3.953
41995 | -252.4413 | 1256.9017 | 1282.0018 | 4.942 | -1.978
42005 | -382.4638 | 1202.113 | 1261.4889 | 4.942 | 0.66
42015 | -390.5221 | 1097.7337 | 1165.1295 | 3.294 | -0.66
42025 | -383.3538 | 913.4288 | 990.612 | 1.318 | -0.329
42035 | -394.6248 | 636.1839 | 748.6379 | -1.318 | 0
42045 | -473.2718 | 482.3638 | 675.767 | -0.658 | 1.318
42055 | -527.9056 | 798.4261 | 957.1669 | 6.259 | 1.318
42065 | -631.4834 | 979.1836 | 1165.1489 | 4.942 | 2.635
42075 | -668.148 | 679.1546 | 952.7186 | -1.647 | 1.977
42085 | -950.4919 | 299.5289 | 996.5703 | -3.954 | 6.589
42095 | -963.2138 | 54.5014 | 964.7545 | -3.953 | 2.965
42105 | -1123.3011 | -293.5853 | 1161.0331 | -7.248 | 6.26
42115 | -1039.101 | -595.9042 | 1197.845 | -7.908 | 2.306
42125 | -1083.1834 | -611.0885 | 1243.6702 | -4.611 | 4.612
42135 | -1397.4184 | -609.4989 | 1524.5547 | -4.612 | 8.895
42145 | -1386.7004 | -579.0984 | 1502.7618 | -3.624 | 4.613
42155 | -1203.5745 | -548.7977 | 1322.7889 | -3.295 | 2.306
42165 | -1104.5173 | -504.0152 | 1214.0798 | -2.636 | 2.635
42175 | -845.0549 | -461.9282 | 963.0657 | -2.306 | -0.987
42185 | -839.7823 | -557.5462 | 1008.0139 | -4.283 | 2.306
42195 | -1179.9653 | -605.6093 | 1326.3034 | -3.624 | 7.577
42205 | -1240.6724 | -247.8141 | 1265.1798 | 2.966 | 4.282
42215 | -967.683 | 50.689 | 969.0097 | 3.293 | -0.329
42225 | -725.2955 | 167.6439 | 744.4179 | 2.307 | -0.988
42235 | -558.5948 | 159.253 | 580.8526 | 0.988 | -1.318
42245 | -504.5862 | 171.4288 | 532.9119 | 1.318 | -0.329
42255 | -356.3004 | 596.2978 | 694.6374 | 8.236 | -2.307
42265 | -385.9439 | 397.3677 | 553.9438 | -0.988 | 0.33
42275 | -462.2124 | 294.3355 | 547.9724 | 0.988 | 0.988
42285 | -290.304 | 335.5269 | 443.6831 | 1.977 | -2.635
42295 | -273.8591 | 275.8093 | 388.6767 | 0.329 | -0.329
42305 | -747.7052 | 377.0234 | 837.3827 | 2.966 | 7.577
42315 | -456.1296 | 875.3833 | 987.0918 | 9.883 | -3.624
42325 | 198.3101 | 657.4257 | 686.6843 | -0.329 | -9.554
42335 | -259.7996 | 148.606 | 299.2985 | -4.943 | 5.93
42345 | -928.9012 | 220.0716 | 954.6146 | 1.978 | 9.883
42355 | -960.2908 | 476.1903 | 1071.8748 | 4.283 | 3.295
42365 | -893.3536 | 467.3852 | 1008.2309 | 1.318 | 2.964
42375 | -1700.3975 | 371.1464 | 1740.4314 | 0.329 | 17.133
42385 | -1835.5797 | 3.6307 | 1835.5833 | -4.942 | 8.236
42395 | -1341.5064 | 33.1878 | 1341.9169 | 0.329 | 0
42405 | -955.0179 | 89.9201 | 959.2418 | 0 | -0.659
42415 | -910.5066 | 142.8579 | 921.6456 | 0.66 | 2.306
42425 | -817.2787 | 274.3963 | 862.1124 | 2.306 | 0.659
42435 | -444.0189 | 369.6372 | 577.7408 | 2.306 | -4.283
42445 | 12.5628 | 407.6048 | 407.7984 | 1.976 | -7.248
42455 | 57.9504 | 239.4075 | 246.3213 | -1.318 | -2.635
42465 | -100.7429 | 606.3352 | 614.6474 | 7.248 | 0
42475 | -43.1971 | 966.539 | 967.5038 | 7.908 | -2.636
42485 | -115.8011 | 801.4489 | 809.7717 | 1.317 | 0
42495 | -451.3448 | 548.6659 | 710.4551 | -0.329 | 4.612
42505 | -635.9563 | 303.3727 | 704.6102 | -1.977 | 3.624
42515 | -481.471 | -89.447 | 489.7091 | -5.93 | -0.659
42525 | -906.7918 | -105.0037 | 912.8511 | -1.318 | 8.895
42535 | -1298.0097 | 235.4103 | 1319.1843 | 3.953 | 9.225
42545 | -1572.0496 | 324.9322 | 1605.2791 | 1.318 | 9.883
42555 | -1360.9017 | 551.0141 | 1468.22 | 4.943 | 2.966
42565 | -853.1409 | 388.797 | 937.5567 | -0.989 | -2.636
42575 | -337.1244 | 457.884 | 568.6042 | 2.965 | -5.601
42585 | -210.699 | 959.4286 | 982.2918 | 9.883 | -1.977
42595 | -297.1574 | 1451.3351 | 1481.4439 | 11.86 | 0.33
42605 | 52.3249 | 775.3123 | 777.076 | -5.271 | -6.589
42615 | -86.4143 | 354.1691 | 364.5589 | -2.635 | 0.989
42625 | -536.6858 | 143.5688 | 555.557 | -2.966 | 5.93
42635 | -763.0955 | 307.2974 | 822.646 | 2.307 | 4.612
42645 | -764.6727 | 220.6582 | 795.8733 | -1.647 | 2.636
42655 | -1101.3392 | -63.7647 | 1103.1836 | -4.613 | 8.565
42665 | -1516.4068 | -479.6017 | 1590.4425 | -8.236 | 10.872
42675 | -1509.1726 | -470.8674 | 1580.9232 | -2.965 | 5.93
42685 | -1353.711 | -268.9826 | 1380.1757 | -0.33 | 3.953
42695 | -1111.7171 | 66.6745 | 1113.7146 | 3.295 | 1.318
42705 | -643.4178 | 219.0772 | 679.6921 | 1.977 | -3.953
42715 | -154.7449 | 292.4315 | 330.8507 | 1.976 | -6.589
42725 | 190.9675 | 402.7608 | 445.7408 | 2.966 | -6.918
42735 | 440.4396 | 583.0688 | 730.7231 | 4.612 | -7.248
42745 | 506.5055 | 562.5249 | 756.9558 | 1.976 | -5.272
42755 | 725.665 | 279.0471 | 777.4683 | -2.306 | -8.236
42765 | 996.2295 | 380.4502 | 1066.4031 | 2.966 | -9.555
42775 | 945.3861 | 544.7673 | 1091.1124 | 3.623 | -5.27
42785 | 739.9224 | 720.5554 | 1032.8046 | 4.942 | -2.636
42795 | 309.2079 | 557.4664 | 637.4781 | 0 | 2.636
42805 | -87.5555 | 238.9003 | 254.4393 | -2.964 | 4.283
42815 | -394.6428 | 83.4534 | 403.3701 | -1.978 | 5.271
42825 | -541.4467 | -95.8978 | 549.8736 | -3.623 | 4.283
42835 | -787.8179 | 16.2705 | 787.9859 | 0.658 | 6.918
42845 | -965.1003 | -146.9677 | 976.2265 | -3.953 | 6.589
42855 | -1179.6002 | -406.9573 | 1247.8265 | -5.601 | 8.237
42865 | -1424.9363 | -353.4426 | 1468.1162 | -1.647 | 9.554
42875 | -1549.3591 | -116.1047 | 1553.7033 | 1.318 | 8.565
42885 | -1347.6583 | 99.9148 | 1351.3571 | 2.306 | 3.624
42895 | -1042.6201 | 60.6187 | 1044.3808 | -0.659 | 0.989
42905 | -1312.8353 | -12.9204 | 1312.8989 | -0.988 | 8.895
42915 | -1148.8536 | -245.9236 | 1174.88 | -4.283 | 1.647
42925 | -908.071 | -442.6611 | 1010.2187 | -4.613 | 0.659
42935 | -941.5222 | -259.549 | 976.642 | 0.66 | 3.624
42945 | -975.5134 | 71.0994 | 978.101 | 3.623 | 3.295
42955 | -832.9368 | 231.9653 | 864.6338 | 2.636 | 0.659
42965 | -738.2739 | 164.2658 | 756.3277 | 0 | 0.987
42975 | -610.3135 | 143.1203 | 626.87 | 0.659 | -0.329
42985 | -417.6213 | -140.777 | 440.7105 | -4.283 | -1.977
42995 | -259.3028 | -153.6981 | 301.4316 | -0.658 | -2.305
43005 | -325.2488 | 438.7786 | 546.1808 | 8.894 | 0.658
43015 | -251.3647 | 680.0924 | 725.0585 | 5.271 | -1.647
43025 | -186.7474 | 550.3233 | 581.1457 | 1.318 | -1.317
43035 | -146.462 | 451.204 | 474.3797 | 1.319 | -1.319
43045 | -228.2299 | 658.7846 | 697.1987 | 5.6 | 0.659
43055 | -367.9481 | 760.3436 | 844.6941 | 4.283 | 1.977
43065 | -362.6469 | 847.7792 | 922.0858 | 4.942 | 0.33
43075 | -338.5343 | 940.2942 | 999.3791 | 5.27 | 0.329
43085 | -576.2116 | 760.9494 | 954.4966 | 0.989 | 4.612
43095 | -1092.8854 | 424.6748 | 1172.4961 | -2.306 | 10.214
43105 | -1330.2103 | 217.0488 | 1347.8018 | -1.976 | 7.906
43115 | -1610.1936 | 0.31921 | 1610.1936 | -3.624 | 10.543
43125 | -1891.7969 | -312.7646 | 1917.4768 | -6.261 | 11.531
43135 | -1786.2144 | -560.8299 | 1872.1891 | -6.588 | 6.259
43145 | -1401.9157 | -440.5548 | 1469.5088 | -1.648 | 1.318
43155 | -1182.5167 | -449.756 | 1265.1585 | -3.624 | 1.977
43165 | -1321.5675 | -192.8885 | 1335.5697 | 1.648 | 6.259
43175 | -1296.9184 | -295.2264 | 1330.0963 | -3.624 | 3.624
43185 | -1056.144 | -215.6855 | 1077.9427 | 0 | 0.329
43195 | -804.6232 | -181.154 | 824.7638 | -0.989 | -0.988
43205 | -352.2254 | -102.7402 | 366.9036 | 0.33 | -5.93
43215 | 2.2903 | -98.4289 | 98.4556 | -0.659 | -6.26
43225 | -76.0409 | -31.5396 | 82.3224 | 0.659 | -0.988
43235 | 112.2025 | -12.9939 | 112.9524 | 0 | -5.6
43245 | 439.5778 | 105.7259 | 452.1135 | 1.977 | -7.907
43255 | 617.3608 | 278.9766 | 677.4675 | 3.294 | -6.919
43265 | 484.7435 | 418.5484 | 640.4366 | 3.624 | -2.636
43275 | 96.212 | 301.0219 | 316.0237 | 0 | 2.307
43285 | -244.9526 | 295.809 | 384.0635 | 1.647 | 3.624
43295 | -395.3649 | 322.5441 | 510.2432 | 1.647 | 2.635
43305 | -306.034 | 263.061 | 403.5565 | 0.33 | -0.329
43315 | -402.3837 | 446.8048 | 601.2879 | 4.283 | 2.635
43325 | -444.7712 | 240.5307 | 505.6446 | -1.977 | 1.648
43335 | -631.8748 | 123.0207 | 643.739 | -0.659 | 4.612
43345 | -899.0716 | -95.653 | 904.1455 | -3.624 | 6.589
43355 | -989.7768 | -381.2672 | 1060.6709 | -5.601 | 4.942
43365 | -1036.8221 | -425.6762 | 1120.8034 | -2.964 | 4.941
43375 | -966.909 | -453.8606 | 1068.1303 | -3.295 | 2.966
43385 | -819.3133 | -473.1817 | 946.137 | -2.965 | 1.318
43395 | -627.3035 | -434.5283 | 763.1019 | -1.977 | -0.33
43405 | -440.8686 | -391.1209 | 589.3561 | -1.647 | -1.318
43415 | -240.1405 | -331.3895 | 409.2511 | -0.988 | -2.636
43425 | 93.6639 | -120.2775 | 152.4454 | 1.976 | -5.93
43435 | 340.9734 | 209.7076 | 400.3 | 4.942 | -5.93
43445 | 349.0516 | 401.9933 | 532.3868 | 4.283 | -3.294
43455 | 326.9037 | 555.792 | 644.8029 | 4.941 | -2.965
43465 | 197.6906 | 595.0867 | 627.0644 | 3.624 | -0.659
43475 | 146.7406 | 273.2547 | 310.1628 | -2.306 | -1.318
43485 | 134.7356 | 67.4902 | 150.6938 | -1.647 | -1.318
43495 | 112.1177 | -248.3596 | 272.4938 | -5.271 | -0.989
43505 | 175.582 | -311.5901 | 357.6555 | -2.306 | -2.305
43515 | 270.879 | -284.4092 | 392.7646 | -1.648 | -2.965
43525 | 88.6433 | -219.2911 | 236.5295 | -0.658 | 1.317
43535 | 109.8123 | -409.0595 | 423.5427 | -4.613 | -1.647
43545 | -47.1454 | -400.6205 | 403.385 | -1.646 | 1.976
43555 | -223.9694 | -460.5342 | 512.1075 | -3.295 | 2.637
43565 | -488.2789 | -546.2449 | 732.6662 | -3.624 | 5.271
43575 | -663.3216 | -625.796 | 911.9299 | -3.954 | 4.941
43585 | -619.764 | -531.7076 | 816.5908 | -1.318 | 2.307
43595 | -445.0061 | -531.3166 | 693.0568 | -2.635 | 0
43605 | -540.498 | -440.3838 | 697.1915 | -0.659 | 3.623
43615 | -492.4538 | -365.8091 | 613.4551 | -0.659 | 0.989
43625 | -337.0766 | -363.9137 | 496.0381 | -1.318 | -0.659
43635 | -97.9819 | -369.4826 | 382.2537 | -1.317 | -2.965
43645 | 70.5085 | -352.2374 | 359.2251 | -0.989 | -2.966
43655 | -16.3741 | -261.5455 | 262.0576 | 0.329 | 0.331
43665 | 20.7553 | -269.6026 | 270.4004 | -0.988 | -1.648
43675 | 154.025 | -212.296 | 262.2848 | 0.33 | -2.965
43685 | 78.65 | -101.6825 | 128.5502 | 1.318 | 0
43695 | -90.0977 | -81.1758 | 121.2729 | 0.329 | 1.647
43705 | -219.6627 | -153.3978 | 267.9227 | -0.989 | 1.977
43715 | -260.8617 | -89.9375 | 275.9304 | 0.989 | 1.318
43725 | -243.6048 | -83.275 | 257.4452 | 0 | 0.659
43735 | -212.2112 | -109.8561 | 238.9601 | -0.329 | 0.329
43745 | -232.1056 | -106.1292 | 255.2184 | 0 | 0.989
43755 | -253.1528 | -2.0775 | 253.1613 | 1.646 | 0.988
43765 | -246.8544 | 176.0002 | 303.1718 | 3.295 | 0.659
43775 | -279.3985 | 187.6864 | 336.5854 | 1.318 | 1.317
43785 | -346.7102 | 312.7062 | 466.8973 | 3.624 | 1.978
43795 | -549.1053 | 290.027 | 620.9929 | 1.318 | 4.612
43805 | -568.3387 | 6.376 | 568.3745 | -2.965 | 2.306
43815 | -346.7884 | -182.3297 | 391.7988 | -2.635 | -1.318
43825 | -184.1678 | -152.6836 | 239.2281 | -0.331 | -1.318
43835 | 22.8725 | -1.1168 | 22.8997 | 1.648 | -3.294
43845 | 174.5416 | 122.7373 | 213.3758 | 1.976 | -3.295
43855 | 272.3252 | 352.2759 | 445.2632 | 4.613 | -3.294
43865 | 189.4467 | 428.0082 | 468.0609 | 2.965 | -0.659
43875 | 218.3883 | 441.9168 | 492.9339 | 2.636 | -2.306
43885 | 112.5037 | 498.3804 | 510.9208 | 3.295 | 0.329
43895 | -130.5344 | 203.3735 | 241.6609 | -2.637 | 2.965
43905 | -165.0237 | -475.0143 | 502.8632 | -10.212 | 0.659
43915 | 282.0987 | -690.6458 | 746.0371 | -5.601 | -6.919
43925 | 570.2739 | -372.255 | 681.0184 | 1.317 | -5.93
43935 | 383.1787 | 155.348 | 413.4718 | 6.26 | 0
43945 | 87.2669 | 411.6328 | 420.7815 | 4.612 | 2.306
43955 | -194.4588 | 489.9915 | 527.1678 | 3.624 | 3.954
43965 | -188.2348 | 313.0175 | 365.2565 | -0.329 | 0.659
43975 | -269.7776 | 139.353 | 303.6432 | -0.989 | 2.635
43985 | -315.7396 | -17.7996 | 316.2409 | -1.976 | 1.977
43995 | -552.0895 | -296.0271 | 626.4462 | -4.942 | 5.601
44005 | -685.6357 | -173.6568 | 707.2857 | 0.659 | 4.612
44015 | -646.0632 | -140.0283 | 661.064 | -0.988 | 2.636
44025 | -557.8493 | 77.0076 | 563.1394 | 2.965 | 1.647
44035 | -449.6838 | 231.9038 | 505.9593 | 2.636 | 0.659
44045 | -380.9546 | 299.2708 | 484.4475 | 2.306 | 0.659
44055 | -419.7814 | 209.3439 | 469.0856 | 0 | 1.977
44065 | -361.4811 | 99.217 | 374.8501 | -0.66 | 0.329
44075 | -95.4259 | -82.268 | 125.9925 | -2.635 | -3.295
44085 | 45.2807 | -116.9899 | 125.4471 | -0.989 | -2.306
44095 | -14.3472 | -44.7798 | 47.022 | 0.33 | 0
44105 | -6.9634 | -186.9063 | 187.0359 | -2.965 | -0.988
44115 | 134.1052 | -198.6518 | 239.6805 | -0.988 | -2.965
44125 | 13.954 | -260.4927 | 260.8661 | -2.307 | 0.988
44135 | -98.4035 | -378.0987 | 390.6941 | -3.293 | 0.989
44145 | 74.3245 | -482.9826 | 488.6679 | -3.625 | -2.966
44155 | 222.0981 | -363.9333 | 426.3508 | -0.33 | -2.964
44165 | 308.7875 | -264.2319 | 406.409 | -0.329 | -2.966
44175 | 445.6709 | -348.806 | 565.9401 | -2.635 | -4.282
44185 | 417.7425 | -388.2037 | 570.2727 | -1.977 | -1.977
44195 | 326.6955 | -403.7715 | 519.3856 | -1.977 | -0.989
44205 | -53.5234 | -398.9713 | 402.5454 | -1.647 | 4.613
44215 | -262.1756 | -242.793 | 357.3297 | 0.988 | 3.295
44225 | -235.9975 | -84.6394 | 250.7163 | 1.647 | 0.988
44235 | -227.1276 | 72.763 | 238.4982 | 2.636 | 1.318
44245 | -103.1929 | 183.0686 | 210.1496 | 2.636 | -0.989
44255 | -200.3068 | 429.6152 | 474.017 | 5.6 | 2.307
44265 | -261.9218 | 525.398 | 587.0656 | 3.954 | 1.646
44275 | -97.412 | 305.4801 | 320.6356 | -0.659 | -1.646
44285 | -24.4526 | 196.3809 | 197.8974 | 0.329 | -0.66
44295 | 22.7026 | 78.5588 | 81.7734 | -0.988 | -0.988
44305 | -344.4476 | 69.5633 | 351.4018 | 0.33 | 5.93
44315 | -755.3764 | 309.4643 | 816.3098 | 4.282 | 7.907
44325 | -751.9831 | 340.8545 | 825.6272 | 1.648 | 3.295
44335 | -712.8128 | 252.4467 | 756.1954 | 0.329 | 3.295
44345 | -635.0324 | 233.4158 | 676.5716 | 0.989 | 1.976
44355 | -469.0689 | 157.5115 | 494.8086 | -0.33 | 0
44365 | -336.1313 | 78.3208 | 345.1353 | -0.659 | -0.33
44375 | -313.9457 | 66.8314 | 320.9803 | 0 | 0.659
44385 | -251.5673 | 142.1604 | 288.9562 | 1.318 | -0.329
44395 | -294.4802 | 64.3308 | 301.425 | -0.989 | 1.317
44405 | -279.3616 | -48.5558 | 283.55 | -1.647 | 0.331
44415 | -158.9263 | -121.6164 | 200.1203 | -1.647 | -1.319
44425 | -29.9617 | -34.2933 | 45.5383 | 0.659 | -1.976
44435 | -1.1353 | 0.022566 | 1.1355 | 0 | -0.989
44445 | 126.325 | -69.5866 | 144.2231 | -1.318 | -2.965
44455 | 252.6518 | -145.0131 | 291.3104 | -1.647 | -3.294
44465 | 318.7937 | -98.1413 | 333.5583 | 0 | -2.966
44475 | 345.6899 | 21.833 | 346.3787 | 1.318 | -2.635
44485 | 350.1807 | 123.0427 | 371.1685 | 1.647 | -2.306
44495 | 70.9944 | 302.3113 | 310.5356 | 3.624 | 2.635
44505 | -105.7363 | 397.6317 | 411.4501 | 2.965 | 1.977
44515 | -5.5517 | 491.1718 | 491.2032 | 3.624 | -1.318
44525 | -11.3013 | 680.6535 | 680.7473 | 5.6 | 0.33
44535 | -98.2402 | 730.0514 | 736.6317 | 3.954 | 1.317
44545 | -102.4303 | 578.505 | 587.5032 | 0.988 | 0.33
44555 | -229.5075 | 315.4703 | 390.122 | -1.647 | 2.636
44565 | -259.0536 | 138.543 | 293.7736 | -1.647 | 1.318
44575 | -436.537 | -23.7186 | 437.1808 | -2.635 | 4.282
44585 | -699.3573 | -235.6638 | 737.996 | -4.284 | 6.26
44595 | -749.4796 | -562.897 | 937.3221 | -7.247 | 3.953
44605 | -476.982 | -765.6083 | 902.0355 | -6.59 | -0.988
44615 | -255.6956 | -741.3848 | 784.2396 | -3.953 | -1.318
44625 | -53.6795 | -258.8827 | 264.3893 | 3.953 | -2.635
44635 | 124.3153 | -93.2186 | 155.3834 | 0.659 | -3.295
44645 | 322.3033 | 90.739 | 334.8328 | 2.965 | -4.613
44655 | 793.4415 | 83.9173 | 797.8669 | 0.33 | -10.212
44665 | 1287.037 | 113.0374 | 1291.9914 | 1.318 | -12.52
44675 | 1414.1197 | 75.3665 | 1416.1266 | 0 | -8.894
44685 | 1172.7248 | 3.1504 | 1172.729 | -0.66 | -3.624
44695 | 544.6997 | -42.6242 | 546.3649 | -0.658 | 4.282
44705 | 47.7685 | 84.7358 | 97.2727 | 1.976 | 5.272
44715 | -367.1352 | 93.6431 | 378.8896 | 0.33 | 7.248
44725 | -691.8164 | 232.3292 | 729.7854 | 2.965 | 7.906
44735 | -819.5606 | 331.3138 | 883.9957 | 2.635 | 6.26
44745 | -1096.6889 | 158.3152 | 1108.057 | -1.317 | 9.554
44755 | -1309.2243 | -59.0277 | 1310.5542 | -2.636 | 9.224
44765 | -1109.7618 | -273.4463 | 1142.9542 | -3.953 | 3.295
44775 | -951.7832 | -74.3247 | 954.6808 | 1.976 | 3.295
44785 | -845.6575 | 103.9873 | 852.027 | 1.977 | 2.635
44795 | -553.7318 | 198.7238 | 588.3112 | 1.977 | -1.318
44805 | -301.4542 | 431.8013 | 526.6184 | 4.942 | -1.977
44815 | -107.2451 | 418.9489 | 432.4577 | 1.647 | -2.635
44825 | 159.435 | 245.8027 | 292.982 | -0.659 | -4.942
44835 | 645.184 | -139.3669 | 660.0648 | -5.271 | -9.883
44845 | 832.9997 | -52.0197 | 834.6224 | 0.988 | -6.919
44855 | 719.7306 | -353.6988 | 801.9445 | -6.259 | -3.294
44865 | 546.4747 | -517.2438 | 752.4465 | -4.283 | -1.647
44875 | -32.0886 | -228.9739 | 231.2114 | 1.977 | 6.588
44885 | -383.6285 | 16.4937 | 383.9829 | 2.306 | 5.272
44895 | -517.4419 | 268.885 | 583.134 | 4.282 | 4.282
44905 | -644.0365 | 542.7319 | 842.2238 | 5.93 | 4.942
44915 | -265.8383 | 522.2861 | 586.0484 | 2.307 | -3.294
44925 | -133.8071 | 617.1442 | 631.4834 | 4.612 | -0.33
44935 | -295.6229 | 776.1728 | 830.5643 | 5.601 | 2.966
44945 | -364.9997 | 622.5251 | 721.6386 | 0.989 | 1.977
44955 | -891.8312 | 644.401 | 1100.2797 | 3.623 | 10.541
44965 | -1176.7601 | 683.164 | 1360.69 | 3.294 | 8.237
44975 | -980.9792 | 647.6601 | 1175.493 | 2.306 | 2.306
44985 | -785.4285 | 353.3768 | 861.2625 | -2.306 | 1.648
44995 | -722.6574 | 150.3804 | 738.1382 | -1.976 | 2.305
45005 | -775.8169 | -137.1929 | 787.8539 | -4.941 | 3.624
45015 | -439.6183 | -429.7547 | 614.7791 | -6.261 | -2.965
45025 | -184.2914 | -419.2043 | 457.9253 | -2.635 | -2.635
45035 | -212.704 | -370.636 | 427.3336 | -2.306 | 0.329
45045 | -328.276 | -301.8239 | 445.9403 | -1.318 | 1.647
45055 | -226.4528 | -203.2709 | 304.3024 | -0.329 | -1.318
45065 | -88.4203 | -179.6994 | 200.2749 | -0.989 | -1.976
45075 | 40.1718 | 53.2685 | 66.7181 | 2.966 | -2.636
45085 | 169.7395 | 217.777 | 276.1129 | 2.635 | -3.294
45095 | 244.7794 | 387.9787 | 458.7422 | 3.953 | -2.965
45105 | 354.5952 | 417.7006 | 547.9156 | 2.306 | -3.954
45115 | 347.8988 | 426.1448 | 550.1209 | 2.307 | -2.306
45125 | 240.2638 | 558.7265 | 608.1956 | 4.282 | -0.659
45135 | 35.3128 | 572.4653 | 573.5534 | 2.636 | 1.648
45145 | -182.5248 | 414.9597 | 453.3286 | 0 | 2.964
45155 | -364.2989 | 359.321 | 511.6886 | 0.988 | 3.624
45165 | -389.7514 | 209.4399 | 442.4605 | -1.318 | 1.977
45175 | -530.4632 | 342.0961 | 631.206 | 2.966 | 4.284
45185 | -594.7954 | 354.8298 | 692.5935 | 0.988 | 3.293
45195 | -667.8312 | 430.3708 | 794.492 | 2.636 | 3.955
45205 | -711.6574 | 441.442 | 837.4529 | 1.647 | 3.623
45215 | -647.5568 | 303.5899 | 715.1899 | -0.659 | 1.977
45225 | -715.9416 | 372.777 | 807.1772 | 2.307 | 3.954
45235 | -442.2137 | 392.9113 | 591.5507 | 1.317 | -1.977
45245 | -137.663 | 428.5554 | 450.1232 | 1.976 | -3.295
45255 | 33.1433 | 345.3314 | 346.9183 | 0 | -2.965
45265 | 62.9177 | 274.5798 | 281.6962 | 0 | -1.648
45275 | -16.7295 | 331.2505 | 331.6727 | 1.648 | 0
45285 | -243.1516 | 208.8297 | 320.5192 | -1.318 | 2.966
45295 | -442.2902 | 310.4269 | 540.3568 | 2.307 | 3.624
45305 | -412.575 | 87.1354 | 421.6761 | -3.295 | 0.988
45315 | -255.8649 | -39.0256 | 258.824 | -1.977 | -0.988
45325 | -148.6592 | -0.78278 | 148.6612 | -0.329 | -0.989
45335 | -202.1168 | 145.557 | 249.0744 | 1.647 | 0.989
45345 | -175.6211 | 16.4419 | 176.3891 | -2.307 | -0.329
45355 | -101.1789 | 63.5775 | 119.4959 | 0.66 | -0.989
45365 | -29.8546 | 108.7039 | 112.7291 | 0.329 | -1.318
45375 | -38.3567 | 163.756 | 168.1882 | 0.988 | -0.33
45385 | -30.9206 | 281.0956 | 282.7911 | 2.307 | -0.658
45395 | 59.7728 | 289.6153 | 295.7192 | 0.988 | -1.977
45405 | 112.8037 | 224.138 | 250.9234 | 0 | -1.647
45415 | -28.8367 | 63.9461 | 70.1474 | -1.977 | 1.318
45425 | -6.3272 | 5.5275 | 8.4016 | -0.988 | -0.989
45435 | -76.2503 | -19.3267 | 78.6615 | -0.989 | 0.989
45445 | -277.3696 | -60.1904 | 283.8253 | -1.318 | 3.294
45455 | -441.0476 | 118.1202 | 456.591 | 2.307 | 3.624
45465 | -564.5932 | 165.6811 | 588.401 | 0.659 | 3.954
45475 | -670.7227 | 247.678 | 714.9918 | 1.977 | 4.283
45485 | -710.399 | 86.1253 | 715.6006 | -1.977 | 3.624
45495 | -584.299 | -72.725 | 588.8075 | -2.306 | 0.987
45505 | -586.7039 | 63.6948 | 590.1512 | 1.647 | 2.637
45515 | -596.8187 | 281.0661 | 659.6898 | 3.294 | 2.306
45525 | -600.6027 | 345.7791 | 693.0272 | 1.977 | 2.306
45535 | -472.6659 | 295.577 | 557.4754 | 0.659 | 0
45545 | -238.8581 | 240.0239 | 338.6218 | 0.33 | -2.306
45555 | -75.678 | 208.8082 | 222.0991 | 0.329 | -2.306
45565 | -70.647 | 191.7498 | 204.3501 | 0.329 | -0.66
45575 | 115.9255 | 219.9254 | 248.608 | 0.989 | -3.953
45585 | 199.1365 | -82.9413 | 215.7188 | -4.613 | -2.635
45595 | 163.5868 | -213.3569 | 268.8528 | -2.635 | -1.319
45605 | 160.1155 | -460.4693 | 487.513 | -5.93 | -1.647
45615 | 114.6514 | -525.1423 | 537.5122 | -3.624 | -0.658
45625 | 101.5696 | -413.6295 | 425.9175 | -1.318 | -0.989
45635 | 45.5306 | -319.3098 | 322.5396 | -0.988 | 0
45645 | 22.6689 | -175.1079 | 176.5691 | 0.658 | -0.33
45655 | 73.2171 | -151.1409 | 167.9414 | -0.658 | -1.318
45665 | 18.7515 | -134.3703 | 135.6724 | -0.33 | 0.331
45675 | 25.8578 | -136.6749 | 139.0994 | -0.659 | -0.66
45685 | -13.0522 | 50.7049 | 52.3579 | 2.635 | 0.329
45695 | -163.651 | -67.7878 | 177.1351 | -1.976 | 2.307
45705 | -275.0557 | -76.0227 | 285.3683 | 0 | 2.306
45715 | -285.3621 | 7.1899 | 285.4526 | 0.988 | 1.318
45725 | -75.5084 | 142.2278 | 161.0288 | 2.306 | -2.307
45735 | -165.5491 | 104.2188 | 195.6223 | 0 | 1.977
45745 | -137.7806 | -56.4071 | 148.88 | -1.976 | -0.329
45755 | -204.245 | -148.7643 | 252.6793 | -1.648 | 1.647
45765 | -308.5941 | -314.3237 | 440.488 | -3.624 | 2.306
45775 | -320.0519 | -287.1496 | 429.9862 | -0.987 | 1.318
45785 | -434.6586 | -284.611 | 519.5493 | -1.648 | 3.295
45795 | -531.7279 | -223.7066 | 576.8701 | -0.329 | 3.295
45805 | -689.5373 | -79.6907 | 694.127 | 1.317 | 4.941
45815 | -580.5773 | -93.7509 | 588.098 | -0.659 | 0.989
45825 | -517.4291 | -28.5436 | 518.2158 | 0.989 | 1.647
45835 | -422.61 | 322.3187 | 531.4965 | 5.93 | 0.329
45845 | -237.6547 | 243.3472 | 340.1435 | 0 | -1.647
45855 | 9.1324 | 152.1158 | 152.3897 | 0.329 | -3.624
45865 | 335.27 | 233.7062 | 408.6864 | 2.306 | -6.259
45875 | 472.6501 | 288.9923 | 553.9988 | 1.977 | -4.613
45885 | 434.856 | 512.1292 | 671.8452 | 5.271 | -2.635
45895 | 391.6052 | 459.0207 | 603.3694 | 1.319 | -2.306
45905 | 417.2332 | 61.4468 | 421.7336 | -4.284 | -2.966
45915 | 334.7658 | -341.7272 | 478.3781 | -6.259 | -0.989
45925 | 135.6103 | -505.8459 | 523.7081 | -4.612 | 1.318
45935 | -290.4142 | -502.2595 | 580.1767 | -2.966 | 6.261
45945 | -638.0662 | -251.6771 | 685.908 | 1.319 | 6.917
45955 | -571.0843 | -88.3325 | 577.8754 | 0.987 | 1.977
45965 | -321.1849 | -157.8871 | 357.894 | -1.647 | -0.988
45975 | -371.2582 | -149.7413 | 400.3188 | -0.329 | 2.636
45985 | -412.4405 | 8.7114 | 412.5325 | 1.976 | 1.976
45995 | -562.2708 | -103.0947 | 571.6441 | -1.976 | 4.284
46005 | -491.5333 | -138.1398 | 510.5757 | -0.659 | 0.988
46015 | -474.0225 | -99.5939 | 484.372 | 0 | 1.976
46025 | -292.8965 | 119.8158 | 316.4557 | 3.295 | -1.318
46035 | 62.3107 | 152.9051 | 165.1139 | 0.988 | -4.941
46045 | 63.6913 | 12.905 | 64.9856 | -1.318 | -0.66
46055 | -36.0006 | -106.7222 | 112.6307 | -1.647 | 0.331
46065 | 140.0385 | -350.6513 | 377.5806 | -4.613 | -3.624
46075 | 296.6729 | -341.0124 | 452.0003 | -1.318 | -3.624
46085 | 392.3705 | -110.4879 | 407.6299 | 1.977 | -3.624
46095 | 268.71 | -101.3015 | 287.1708 | -0.659 | -0.33
46105 | 130.6884 | -187.9634 | 228.9316 | -1.647 | 0.33
46115 | 321.0421 | -188.0574 | 372.0667 | -0.659 | -4.284
46125 | 201.3174 | -407.3792 | 454.4078 | -4.612 | 0.66
46135 | -388.8535 | -510.1852 | 641.4795 | -3.294 | 8.565
46145 | 61.43 | -673.7075 | 676.5024 | -5.272 | -6.589
46155 | 136.4251 | -805.6462 | 817.1154 | -5.271 | -0.329
46165 | -143.8674 | -356.0278 | 383.9969 | 3.953 | 3.624
46175 | -324.4791 | 81.5326 | 334.5657 | 5.272 | 3.294
46185 | -292.6089 | -19.4916 | 293.2574 | -0.989 | 0.989
46195 | -276.3886 | -100.8372 | 294.2088 | -0.329 | 1.318
46205 | -69.479 | -257.9941 | 267.1859 | -2.636 | -2.307
46215 | 53.0809 | -260.3061 | 265.663 | -0.659 | -1.647
46225 | 230.9569 | -64.7699 | 239.8671 | 2.307 | -3.624
46235 | -94.6548 | 215.5294 | 235.3985 | 4.612 | 4.283
46245 | -354.1657 | 313.0446 | 472.6841 | 2.965 | 3.953
46255 | -380.0409 | 303.1528 | 486.1406 | 1.977 | 1.977
46265 | -190.7379 | 51.2497 | 197.5031 | -2.306 | -1.318
46275 | -397.6744 | 54.9462 | 401.4524 | 0.988 | 4.613
46285 | -730.1742 | 159.4101 | 747.3726 | 1.976 | 6.918
46295 | -779.9399 | 55.4381 | 781.9077 | -0.987 | 3.954
46305 | -652.7479 | 134.0117 | 666.3625 | 1.976 | 1.647
46315 | -569.0395 | 239.1379 | 617.2462 | 2.306 | 1.646
46325 | -222.8777 | 476.9276 | 526.4356 | 5.272 | -3.624
46335 | 79.3616 | 427.2812 | 434.5889 | 1.317 | -4.282
46345 | 170.4717 | 301.7426 | 346.5678 | 0.33 | -2.635
46355 | 142.4735 | 114.314 | 182.6647 | -1.647 | -1.318
46365 | 50.2139 | 99.3143 | 111.2869 | 0.329 | 0
46375 | 126.2584 | 35.9091 | 131.2655 | -0.989 | -2.306
46385 | 12.788 | -119.0579 | 119.7427 | -2.635 | 0.987
46395 | 5.3937 | -174.7535 | 174.8367 | -1.648 | -0.658
46405 | 141.827 | -124.3922 | 188.6486 | -0.329 | -2.635
46415 | 206.4388 | -126.4808 | 242.104 | -0.989 | -1.977
46425 | -125.5655 | -160.742 | 203.9723 | -1.317 | 4.283
46435 | -426.7695 | -91.2097 | 436.4074 | 0.329 | 4.941
46445 | -628.2462 | -33.7875 | 629.1541 | 0.33 | 5.271
46455 | -456.4492 | -156.7789 | 482.6235 | -2.306 | 0
46465 | -520.2053 | -125.245 | 535.0699 | 0 | 3.624
46475 | -654.0287 | 190.1593 | 681.1124 | 4.612 | 4.284
46485 | -608.7745 | 368.6628 | 711.7012 | 3.624 | 1.976
46495 | -564.0031 | 349.2443 | 663.3785 | 1.647 | 1.977
46505 | -605.4391 | 481.8939 | 773.8076 | 4.283 | 2.965
46515 | -530.6769 | 526.4413 | 747.5015 | 2.965 | 0.988
46525 | -332.1604 | 640.5382 | 721.5398 | 4.612 | -1.318
46535 | -173.0291 | 566.4763 | 592.3128 | 1.647 | -1.647
46545 | -93.1017 | 400.9647 | 411.6316 | 0 | -1.318
46555 | 15.6106 | 333.3417 | 333.707 | 0.66 | -2.306
46565 | 196.7129 | 207.9518 | 286.2515 | -0.989 | -3.953
46575 | 274.1095 | 131.3518 | 303.9561 | -0.658 | -2.965
46585 | 357.5606 | 68.5098 | 364.0648 | -0.989 | -3.624
46595 | 159.9316 | -55.2713 | 169.213 | -2.306 | 0.988
46605 | -38.1414 | -111.1107 | 117.4749 | -1.648 | 1.647
46615 | -133.5643 | -65.8008 | 148.8932 | -0.329 | 1.318
46625 | -245.7977 | -128.5361 | 277.3771 | -1.977 | 2.306
46635 | -214.0939 | -172.6122 | 275.0112 | -1.647 | 0.33
46645 | -138.9505 | -313.5623 | 342.9702 | -3.624 | -0.33
46655 | -131.8744 | -426.8796 | 446.7852 | -3.624 | 0.33
46665 | -40.6238 | -346.8743 | 349.245 | -0.988 | -1.319
46675 | -119.9651 | -221.9662 | 252.3106 | 0 | 1.319
46685 | -139.7368 | -108.1661 | 176.7095 | 0.659 | 0.329
46695 | -136.2752 | -112.629 | 176.7943 | -0.659 | 0.329
46705 | -98.1001 | -263.9929 | 281.6307 | -2.965 | -0.329
46715 | -68.3518 | -435.4601 | 440.7918 | -3.954 | -0.329
46725 | -204.5423 | -568.8337 | 604.491 | -4.282 | 2.306
46735 | -295.403 | -505.8397 | 585.7788 | -1.648 | 1.976
46745 | -171.6767 | -294.9023 | 341.2334 | 0.988 | -0.988
46755 | -184.4347 | -188.2844 | 263.5662 | 0.33 | 0.988
46765 | -162.1348 | -404.9011 | 436.1566 | -4.283 | 0
46775 | -327.1156 | -256.1332 | 415.4622 | 1.318 | 3.295
46785 | -387.8459 | -22.8351 | 388.5175 | 2.635 | 1.977
46795 | -274.0994 | 258.2546 | 376.5978 | 4.942 | -0.33
46805 | -14.4819 | 265.5915 | 265.9861 | 1.648 | -3.294
46815 | 169.7607 | 242.67 | 296.1543 | 1.647 | -3.294
46825 | 166.7517 | 264.711 | 312.8546 | 1.977 | -1.318
46835 | 153.2215 | 232.1769 | 278.1779 | 0.988 | -1.318
46845 | 118.3781 | 188.5676 | 222.6457 | 0.659 | -0.659
46855 | 76.9383 | 164.9714 | 182.0304 | 0.659 | -0.329
46865 | 149.2957 | 115.6563 | 188.8534 | 0 | -1.977
46875 | 98.5609 | 61.1105 | 115.9687 | -0.329 | 0
46885 | -49.195 | 6.6258 | 49.6392 | -0.66 | 1.646
46895 | -113.1604 | -49.5573 | 123.5363 | -0.988 | 0.989
46905 | -143.8598 | -11.9223 | 144.353 | 0.329 | 0.988
46915 | -244.1241 | 22.9172 | 245.1974 | 0.33 | 2.307
46925 | -342.2418 | -36.576 | 344.1907 | -0.988 | 2.635
46935 | -370.0377 | 124.1345 | 390.3041 | 2.635 | 1.977
46945 | -251.5285 | 108.5658 | 273.9583 | 0 | -0.329
46955 | -104.3586 | 124.5286 | 162.4749 | 0.989 | -1.318
46965 | 47.0983 | 170.9733 | 177.3418 | 1.317 | -2.306
46975 | 35.0398 | 184.288 | 187.5896 | 0.989 | -0.33
46985 | 10.3204 | 75.7483 | 76.4481 | -0.989 | -0.329
46995 | -15.7086 | 68.642 | 70.4165 | 0.33 | 0
47005 | -51.2968 | 62.6346 | 80.9597 | 0 | 0.329
47015 | 59.9613 | -24.4725 | 64.7631 | -1.318 | -1.976
47025 | 230.4165 | -111.1177 | 255.8103 | -1.647 | -3.295
47035 | 443.3142 | -206.0462 | 488.8583 | -2.306 | -4.942
47045 | 479.9851 | -101.8466 | 490.6714 | 0.658 | -2.965
47055 | 374.1576 | -68.8283 | 380.4356 | -0.329 | -0.988
47065 | 206.6644 | -163.4302 | 263.476 | -1.977 | 0.659
47075 | 269.8058 | -276.5622 | 386.37 | -2.636 | -2.307
47085 | 382.3249 | -217.9325 | 440.076 | -0.329 | -2.964
47095 | 473.7135 | -180.8978 | 507.0784 | -0.659 | -3.295
47105 | 382.6143 | -227.2755 | 445.0257 | -1.647 | -0.659
47115 | 247.192 | -325.1941 | 408.479 | -2.635 | 0.33
47125 | 66.557 | -281.0526 | 288.8259 | -0.66 | 1.976
47135 | -194.3417 | -350.9863 | 401.1983 | -2.635 | 4.283
47145 | -380.2683 | -306.4164 | 488.3595 | -0.658 | 4.283
47155 | -442.4127 | -239.6999 | 503.175 | -0.331 | 3.294
47165 | -348.8574 | -182.4009 | 393.6643 | 0 | 0.989
47175 | -377.7601 | -145.1974 | 404.7035 | 0 | 2.635
47185 | -425.5514 | -102.8026 | 437.7926 | 0.331 | 2.636
47195 | -439.4447 | -14.1688 | 439.6731 | 1.317 | 2.306
47205 | -432.0248 | 90.6757 | 441.438 | 1.976 | 1.977
47215 | -527.0692 | 183.2204 | 558.0068 | 2.307 | 3.624
47225 | -378.1431 | 190.2012 | 423.2832 | 1.317 | -0.329
47235 | -344.6564 | 382.7757 | 515.078 | 4.613 | 1.317
47245 | -274.7885 | 524.5947 | 592.2063 | 4.283 | 0
47255 | -4.8392 | 649.8217 | 649.8397 | 4.942 | -3.624
47265 | 216.4551 | 707.2798 | 739.6604 | 4.282 | -3.953
47275 | 355.3858 | 593.8066 | 692.0299 | 1.648 | -3.954
47285 | 393.3173 | 452.3822 | 599.4565 | 0.658 | -2.964
47295 | 284.7287 | 387.4674 | 480.8341 | 0.989 | -0.66
47305 | 149.6508 | 221.5516 | 267.3583 | -1.318 | 0.329
47315 | 48.4018 | -0.60219 | 48.4055 | -2.965 | 0.66
47325 | -51.5367 | 58.4074 | 77.8939 | 0.659 | 1.318
47335 | -43.3179 | 51.4909 | 67.2885 | -0.659 | 0
47345 | -256.9582 | 21.0589 | 257.8197 | -0.659 | 3.953
47355 | -511.6489 | -76.1749 | 517.2883 | -1.977 | 5.271
47365 | -642.6318 | 58.1995 | 645.2618 | 1.648 | 4.613
47375 | -513.7302 | 137.6998 | 531.8646 | 0.988 | 0.988
47385 | -238.2347 | 190.4035 | 304.9742 | 1.318 | -1.977
47395 | -72.5887 | 439.7819 | 445.7322 | 4.942 | -1.647
47405 | -114.7245 | 556.0575 | 567.769 | 3.624 | 0.659
47415 | -236.3718 | 537.4847 | 587.1639 | 2.306 | 1.977
47425 | 48.0956 | 197.6623 | 203.4295 | -3.295 | -4.283
47435 | 117.7726 | -59.3187 | 131.8677 | -3.295 | -1.318
47445 | 257.0685 | 3.771 | 257.0962 | 0.331 | -3.624
47455 | 225.299 | 341.4865 | 409.1121 | 4.941 | -0.989
47465 | 490.2975 | 315.0423 | 582.7892 | 0.329 | -6.259
47475 | 739.6466 | 90.6972 | 745.1866 | -2.306 | -6.589
47485 | 609.5712 | 52.8493 | 611.8579 | -0.329 | -1.647
47495 | 243.0885 | -138.5593 | 279.8048 | -3.624 | 2.635
47505 | -140.7395 | -221.3043 | 262.2655 | -2.306 | 4.942
47515 | -199.64 | -202.0127 | 284.0163 | -1.318 | 1.648
47525 | -494.4677 | -229.1952 | 545.0035 | -1.977 | 6.588
47535 | -744.34 | -204.0181 | 771.7937 | -0.988 | 6.59
47545 | -672.7321 | 9.1544 | 672.7944 | 2.306 | 2.635
47555 | -643.7602 | 91.5062 | 650.2311 | 0.988 | 3.295
47565 | -597.0278 | 65.3384 | 600.5925 | 0 | 2.306
47575 | -394.3493 | -70.6058 | 400.6202 | -1.977 | -0.659
47585 | -36.3699 | -74.3816 | 82.7973 | -0.329 | -4.283
47595 | 425.8528 | 58.1613 | 429.8062 | 1.647 | -7.907
47605 | 767.3677 | 328.089 | 834.5631 | 4.612 | -8.236
47615 | 1010.3087 | 483.9774 | 1120.249 | 3.955 | -8.566
47625 | 1089.5828 | 401.5282 | 1161.213 | 0.987 | -6.918
47635 | 1203.6479 | 177.9768 | 1216.735 | -1.647 | -7.908
47645 | 1406.4663 | -127.4974 | 1412.2334 | -4.282 | -9.554
47655 | 1299.0672 | -298.8101 | 1332.9903 | -3.625 | -4.941
47665 | 973.5372 | -207.2262 | 995.3478 | -0.329 | -0.988
47675 | 719.7484 | -167.0896 | 738.8888 | -0.989 | -0.33
47685 | 590.8411 | -182.3055 | 618.3272 | -1.317 | -0.659
47695 | 553.9824 | -256.1746 | 610.3457 | -2.307 | -1.317
47705 | 418.4493 | -295.5456 | 512.2958 | -1.976 | 0.658
47715 | 174.8707 | -319.1624 | 363.9291 | -1.977 | 2.966
47725 | -211.8528 | -301.0809 | 368.1458 | -1.318 | 6.588
47735 | -454.3059 | -518.7381 | 689.5528 | -5.27 | 5.93
47745 | -452.8236 | -622.4741 | 769.7553 | -3.954 | 3.295
47755 | -234.6999 | -519.2906 | 569.8656 | -1.318 | -0.329
47765 | -66.0848 | -402.1878 | 407.5809 | -0.659 | -0.659
47775 | -71.2936 | -200.5552 | 212.8501 | 1.647 | 0.988
47785 | -210.5286 | -17.7274 | 211.2736 | 2.307 | 2.965
47795 | -296.2213 | 215.2495 | 366.1685 | 4.282 | 2.636
47805 | -461.8573 | 192.6446 | 500.424 | 0.988 | 4.612
47815 | -457.5589 | -21.1684 | 458.0483 | -1.976 | 2.306
47825 | -129.7344 | -437.1755 | 456.0192 | -6.589 | -2.965
47835 | -20.9297 | -483.099 | 483.5522 | -2.306 | -0.659
47845 | -123.3898 | -216.0527 | 248.8047 | 1.977 | 1.648
47855 | -222.0837 | 167.3447 | 278.0745 | 5.27 | 1.976
47865 | 26.5456 | 484.8884 | 485.6145 | 6.261 | -3.294
47875 | 252.0431 | 730.7766 | 773.0201 | 6.918 | -3.624
47885 | 252.1436 | 902.5657 | 937.1239 | 6.918 | -1.319
47895 | 273.5344 | 815.0678 | 859.7422 | 3.295 | -1.976
47905 | 517.0173 | 436.216 | 676.4549 | -1.977 | -5.601
47915 | 671.4274 | 151.0911 | 688.2175 | -2.306 | -4.941
47925 | 705.2196 | 140.0474 | 718.9909 | 0.33 | -3.953
47935 | 576.0068 | 22.2899 | 576.4379 | -1.977 | -1.318
47945 | 213.986 | 146.2031 | 259.1628 | 1.977 | 3.294
47955 | -140.7678 | 108.2899 | 177.6014 | -0.659 | 4.941
47965 | -562.1562 | 47.7794 | 564.1831 | -0.66 | 8.237
47975 | -748.5867 | -159.1256 | 765.3124 | -3.624 | 6.26
47985 | -875.2511 | -281.3085 | 919.3471 | -2.964 | 6.589
47995 | -770.5683 | -331.6473 | 838.9073 | -2.636 | 2.965
48005 | -630.9425 | -254.1889 | 680.2209 | -0.659 | 1.976
48015 | -268.4273 | -22.7133 | 269.3866 | 2.306 | -2.964
48025 | -23.5721 | 198.7441 | 200.1371 | 3.295 | -2.636
48035 | 230.7568 | 570.8498 | 615.7257 | 7.248 | -4.612
48045 | 454.4803 | 749.4749 | 876.5073 | 5.601 | -5.272
48055 | 473.1372 | 714.2119 | 856.7131 | 3.294 | -2.965
48065 | 359.331 | 438.5528 | 566.9633 | -0.988 | -0.988
48075 | 363.5242 | 30.9475 | 364.8392 | -4.612 | -2.306
48085 | 545.8543 | -264.0416 | 606.362 | -4.942 | -4.942
48095 | 477.8366 | -294.6008 | 561.3532 | -2.306 | -1.318
48105 | 229.0353 | -260.1736 | 346.623 | -1.648 | 1.647
48115 | 135.7159 | -211.344 | 251.1674 | -0.989 | 0.329
48125 | 78.9074 | -50.3227 | 93.5882 | 1.318 | 0.66
48135 | -22.3957 | -30.2489 | 37.6372 | -0.329 | 1.647
48145 | -175.1483 | -21.2682 | 176.4349 | 0 | 2.965
48155 | -401.4265 | -220.289 | 457.8979 | -3.624 | 4.942
48165 | -508.7259 | -284.656 | 582.9503 | -1.976 | 3.953
48175 | -572.3475 | -112.3154 | 583.2636 | 1.317 | 3.954
48185 | -530.0371 | 134.4245 | 546.8174 | 3.294 | 2.306
48195 | -479.8588 | 318.0964 | 575.7168 | 3.624 | 1.976
48205 | -400.4069 | 358.6506 | 537.5462 | 2.306 | 0.989
48215 | -348.1993 | 339.9102 | 486.6022 | 1.648 | 0.988
48225 | -359.7909 | 332.9863 | 490.234 | 1.647 | 1.647
48235 | -298.5483 | 336.8794 | 450.132 | 1.647 | 0.329
48245 | -266.7785 | 344.481 | 435.704 | 1.648 | 0.66
48255 | -80.6306 | 314.8852 | 325.0445 | 0.988 | -2.306
48265 | -30.3196 | 197.4548 | 199.769 | -0.659 | -0.659
48275 | 39.6354 | 111.9306 | 118.741 | -0.658 | -1.648
48285 | 139.5725 | -14.8191 | 140.357 | -1.977 | -2.306
48295 | 231.1123 | -51.4693 | 236.7741 | -0.989 | -2.635
48305 | 277.3778 | -181.4709 | 331.4667 | -2.964 | -2.307
48315 | 271.2231 | -289.3781 | 396.6128 | -2.966 | -1.646
48325 | 288.3787 | -339.9163 | 445.7638 | -2.635 | -1.977
48335 | 290.9528 | -337.7172 | 445.765 | -1.977 | -1.647
48345 | 198.0941 | -300.331 | 359.7777 | -1.318 | 0
48355 | 13.9713 | -374.9868 | 375.247 | -2.965 | 1.976
48365 | -95.505 | -406.0516 | 417.132 | -2.306 | 1.648
48375 | -196.4533 | -344.0087 | 396.1514 | -0.989 | 2.306
48385 | -251.8484 | -183.7478 | 311.7545 | 0.989 | 1.976
48395 | -249.4949 | -90.2026 | 265.3002 | 0.658 | 1.318
48405 | -229.2987 | 56.6816 | 236.2006 | 2.307 | 0.988
48415 | -297.1153 | 206.1994 | 361.6569 | 2.965 | 2.306
48425 | -434.089 | 38.6571 | 435.8069 | -1.648 | 3.624
48435 | -438.1084 | -9.5085 | 438.2116 | 0 | 1.977
48445 | -408.6224 | -67.0347 | 414.0844 | -0.987 | 1.647
48455 | -435.2524 | 0.33809 | 435.2525 | 0.987 | 2.306
48465 | -502.6632 | 5.687 | 502.6953 | 0 | 2.966
48475 | -477.3336 | -62.0944 | 481.3555 | -0.987 | 1.647
48485 | -490.5266 | -149.8846 | 512.915 | -1.648 | 2.306
48495 | -550.9076 | -132.451 | 566.606 | -0.329 | 2.965
48505 | -463.2258 | -70.9331 | 468.6253 | 0.329 | 0.659
48515 | -292.5954 | 7.5011 | 292.6915 | 0.988 | -0.988
48525 | -215.7081 | 137.9271 | 256.0349 | 2.307 | -0.33
48535 | -99.8833 | 174.7462 | 201.2782 | 1.317 | -1.647
48545 | -48.2617 | 189.2432 | 195.3002 | 1.318 | -0.988
48555 | -39.3114 | 186.0091 | 190.1178 | 0.989 | -0.659
48565 | 66.1309 | 262.0988 | 270.313 | 2.306 | -2.307
48575 | 115.5079 | 230.8594 | 258.1437 | 0.658 | -1.646
48585 | 46.1889 | 254.296 | 258.4567 | 1.648 | 0
48595 | -63.3965 | 93.4442 | 112.92 | -1.648 | 0.988
48605 | -95.2709 | -19.1746 | 97.1813 | -1.318 | 0.329
48615 | -105.2847 | -40.8305 | 112.9248 | -0.658 | 0.329
48625 | -382.3156 | -128.2105 | 403.2408 | -1.977 | 4.942
48635 | -563.231 | -47.091 | 565.1962 | 0.659 | 4.283
48645 | -396.1516 | 66.4659 | 401.6887 | 1.318 | -0.329
48655 | -102.7394 | 20.5077 | 104.7662 | -0.659 | -2.965
48665 | -5.2009 | 163.2941 | 163.3769 | 2.635 | -1.318
48675 | 35.2262 | 539.6831 | 540.8315 | 6.919 | -1.318
48685 | 376.7007 | 524.7229 | 645.9393 | 1.977 | -6.589
48695 | 359.8543 | 428.3666 | 559.4579 | 1.318 | -1.647
48705 | 338.4367 | 324.5434 | 468.9007 | 0.329 | -2.306
48715 | 294.8749 | 123.914 | 319.8529 | -1.976 | -1.318
48725 | 149.9438 | -19.4492 | 151.1999 | -1.977 | 0.659
48735 | 28.4594 | -29.2587 | 40.8168 | -0.66 | 0.988
48745 | -140.581 | -65.922 | 155.2699 | -1.317 | 2.636
48755 | -128.4541 | -276.5491 | 304.926 | -4.283 | 0.329
48765 | -272.2741 | -537.134 | 602.2011 | -5.93 | 3.295
48775 | -439.2149 | -621.5635 | 761.0854 | -4.283 | 3.953
48785 | -588.3474 | -551.3868 | 806.3375 | -2.306 | 4.613
48795 | -483.5649 | -447.3008 | 658.7208 | -1.318 | 0.988
48805 | -430.0376 | -271.9613 | 508.8175 | 0.659 | 1.647
48815 | -610.9823 | -189.7005 | 639.7544 | 0 | 4.942
48825 | -395.1858 | -188.8467 | 437.9896 | -0.659 | -1.318
48835 | -63.5739 | -57.6659 | 85.8312 | 1.648 | -3.624
48845 | 73.2878 | 414.9726 | 421.3946 | 7.906 | -2.306
48855 | 452.3358 | 559.052 | 719.1292 | 4.283 | -7.577
48865 | 637.1461 | 380.6354 | 742.185 | 0.33 | -5.601
48875 | 524.9193 | 444.5337 | 687.8594 | 3.623 | -1.977
48885 | 420.8333 | 497.5474 | 651.6549 | 2.965 | -1.647
48895 | 316.2171 | 294.7724 | 432.3008 | -0.987 | -0.66
48905 | 173.1518 | 195.3656 | 261.0542 | 0 | 0.66
48915 | 57.6539 | 58.706 | 82.2822 | -1.648 | 0.988
48925 | 23.7544 | -6.6002 | 24.6543 | -0.989 | 0.33
48935 | 7.4501 | -2.1388 | 7.751 | -0.329 | 0.329
48945 | -64.8234 | -56.1592 | 85.7667 | -1.318 | 1.317
48955 | -180.2482 | -200.8549 | 269.8743 | -2.964 | 2.307
48965 | -320.9235 | -290.1037 | 432.6107 | -2.637 | 3.294
48975 | -421.5334 | -383.1797 | 569.664 | -3.294 | 3.295
48985 | -489.6128 | -398.1098 | 631.0404 | -2.306 | 3.295
48995 | -425.5158 | -270.0729 | 503.9872 | 0 | 1.318
49005 | -201.9354 | -234.6135 | 309.5504 | -0.988 | -1.648
49015 | -5.4163 | -77.6618 | 77.8505 | 1.647 | -2.306
49025 | 1.0711 | 8.0547 | 8.1256 | 0.988 | -0.33
49035 | 26.4451 | 12.4727 | 29.2388 | 0.329 | -0.988
49045 | 173.0029 | 109.5096 | 204.7495 | 1.977 | -2.965
49055 | 306.1833 | 210.4874 | 371.555 | 2.307 | -3.295
49065 | 394.1189 | 181.4252 | 433.8719 | 0.658 | -3.294
49075 | 302.5225 | 132.7384 | 330.3625 | 0.33 | -0.659
49085 | 170.578 | 49.7263 | 177.6783 | -0.659 | 0.33
49095 | -44.1155 | -85.0825 | 95.8395 | -1.976 | 2.635
49105 | -158.1678 | -160.6441 | 225.4409 | -1.648 | 1.977
49115 | -278.4875 | -165.8585 | 324.1363 | -0.989 | 2.965
49125 | -331.9779 | -128.9962 | 356.1592 | -0.329 | 2.306
49135 | -268.1813 | -85.7036 | 281.5428 | 0 | 0.659
49145 | -182.4958 | -193.8969 | 266.2719 | -2.306 | 0
49155 | -150.4722 | -247.5763 | 289.717 | -1.647 | 0.329
49165 | -99.1088 | -291.3491 | 307.7448 | -1.977 | -0.329
49175 | 35.6387 | -269.3051 | 271.653 | -0.989 | -1.977
49185 | 192.8422 | -268.5937 | 330.6519 | -1.317 | -2.964
49195 | 319.5785 | -180.9565 | 367.2543 | 0.329 | -3.295
49205 | 425.0833 | -227.2868 | 482.0323 | -1.647 | -3.624
49215 | 386.4169 | -222.3072 | 445.8009 | -0.658 | -1.647
49225 | 351.4515 | -148.6812 | 381.6075 | 0.329 | -1.648
49235 | 206.9078 | -134.3496 | 246.6995 | -0.329 | 0.659
49245 | 195.3519 | -133.9599 | 236.8705 | -0.331 | -0.988
49255 | 172.4954 | -208.2264 | 270.394 | -1.646 | -0.329
49265 | 129.4314 | -343.8282 | 367.383 | -2.966 | 0
49275 | 62.0839 | -324.2743 | 330.164 | -0.988 | 0.658
49285 | -82.5631 | -216.4047 | 231.6196 | 0.33 | 2.306
49295 | -74.3613 | -86.2335 | 113.8676 | 1.317 | 0.329
49305 | -146.7192 | -56.6898 | 157.2904 | 0.33 | 1.978
49315 | -139.7617 | -86.3952 | 164.3091 | -0.33 | 0.659
49325 | -46.832 | -144.5495 | 151.9467 | -0.988 | -0.659
49335 | 94.4491 | -68.404 | 116.6179 | 0.988 | -1.978
49345 | 114.2244 | -57.0317 | 127.6708 | 0 | -0.658
49355 | 150.9536 | -120.295 | 193.023 | -0.988 | -1.318
49365 | 166.7232 | -146.7459 | 222.1058 | -0.659 | -0.988
49375 | 194.2605 | -176.5977 | 262.5336 | -0.988 | -1.318
49385 | 295.0332 | -238.2302 | 379.2074 | -1.648 | -2.635
49395 | 123.4398 | -187.6921 | 224.6458 | 0 | 1.647
49405 | -63.1165 | -121.3818 | 136.8109 | 0.33 | 2.306
49415 | -118.3475 | -196.872 | 229.7057 | -1.648 | 1.318
49425 | -87.1509 | -263.9382 | 277.9544 | -1.647 | 0.329
49435 | -103.5883 | -263.6617 | 283.2808 | -0.988 | 0.988
49445 | -107.398 | -355.033 | 370.9215 | -2.635 | 0.66
49455 | -146.6471 | -413.0286 | 438.2899 | -2.307 | 1.317
49465 | -181.0217 | -465.2374 | 499.214 | -2.635 | 1.318
49475 | -300.1436 | -314.1513 | 434.485 | 0.658 | 2.965
49485 | -298.0941 | -287.6434 | 414.2449 | -0.988 | 1.318
49495 | -320.5802 | -277.0713 | 423.7218 | -0.659 | 1.976
49505 | -311.2677 | -244.779 | 395.9853 | -0.329 | 1.318
49515 | -244.7199 | -221.6769 | 330.1946 | -0.33 | 0.33
49525 | -102.4376 | -149.6304 | 181.3359 | 0.659 | -1.318
49535 | 75.4608 | -132.2643 | 152.2766 | 0 | -2.636
49545 | 235.7175 | -89.4208 | 252.1088 | 0.659 | -3.295
49555 | 171.4373 | 5.3964 | 171.5222 | 1.648 | -0.329
49565 | 185.3456 | 133.5338 | 228.4387 | 2.635 | -1.647
49575 | 104.4038 | 33.3345 | 109.5963 | -0.659 | 0.33
49585 | -40.256 | -96.0544 | 104.1489 | -1.318 | 1.646
49595 | -98.8111 | -248.9051 | 267.801 | -2.635 | 0.989
49605 | -165.4738 | -278.373 | 323.8411 | -1.318 | 1.648
49615 | -121.7185 | -226.4228 | 257.0656 | -0.329 | 0
49625 | -61.3207 | -133.4206 | 146.8376 | 0.658 | -0.33
49635 | -64.9282 | -108.6125 | 126.5399 | 0 | 0.33
49645 | -113.6085 | -120.7892 | 165.822 | -0.329 | 0.988
49655 | -206.8931 | -109.7722 | 234.2107 | 0 | 1.976
49665 | -178.4939 | -232.3231 | 292.9746 | -2.306 | 0.33
49675 | -29.8951 | -331.5498 | 332.8949 | -2.307 | -1.647
49685 | -38.7681 | -178.6354 | 182.7938 | 1.318 | 0.329
49695 | -105.9448 | -185.2786 | 213.4302 | -0.987 | 0.988
49705 | -110.4906 | -163.4997 | 197.333 | 0 | 0.33
49715 | -86.0574 | -481.336 | 488.9685 | -5.931 | 0
49725 | -127.271 | -528.5369 | 543.6443 | -2.306 | 0.988
49735 | -87.0255 | -245.7608 | 260.7141 | 2.306 | -0.329
49745 | 183.0929 | -95.7114 | 206.6003 | 1.318 | -4.283
49755 | 407.2444 | 34.3098 | 408.6871 | 2.306 | -4.612
49765 | 335.5125 | -42.2366 | 338.1605 | -0.659 | -0.988
49775 | 206.1094 | -249.517 | 323.6353 | -2.965 | 0
49785 | 246.9573 | -275.7286 | 370.1542 | -0.988 | -1.977
49795 | 144.6475 | -210.4663 | 255.38 | 0 | 0.659
49805 | -100.2932 | -320.396 | 335.7265 | -2.636 | 3.294
49815 | -349.8776 | -572.3609 | 670.8288 | -5.271 | 4.612
49825 | -344.1894 | -714.2682 | 792.8716 | -4.613 | 1.648
49835 | -48.5072 | -701.5024 | 703.1774 | -2.964 | -2.966
49845 | 31.8939 | -515.7024 | 516.6877 | 0 | -0.658
49855 | -279.3893 | -190.8462 | 338.3499 | 3.294 | 4.942
49865 | -657.0863 | 34.2919 | 657.9805 | 3.294 | 7.248
49875 | -503.3311 | 75.5559 | 508.9705 | 1.648 | 0.329
49885 | -229.9712 | -59.6753 | 237.5877 | -0.989 | -1.647
49895 | -160.113 | -253.0465 | 299.4473 | -2.635 | 0
49905 | -370.1879 | -321.379 | 490.2281 | -1.648 | 3.953
49915 | -574.0068 | -293.0836 | 644.5012 | -0.658 | 4.613
49925 | -432.2786 | -155.2648 | 459.3168 | 1.317 | 0
49935 | -168.9674 | -111.6056 | 202.4989 | 0.33 | -2.307
49945 | -54.2724 | 56.3778 | 78.2557 | 2.965 | -1.317
49955 | -92.2752 | 153.6321 | 179.2136 | 2.305 | 0.329
49965 | -317.4591 | 265.7096 | 413.9829 | 3.295 | 3.624
49975 | -367.7721 | 258.1207 | 449.3135 | 1.648 | 1.648
49985 | -162.2862 | 128.4537 | 206.9714 | -0.33 | -1.977
49995 | -44.1693 | -18.5197 | 47.8947 | -1.318 | -1.318
50005 | 53.7875 | 99.6839 | 113.2695 | 2.306 | -1.977
50015 | 184.0428 | 250.0162 | 310.4511 | 2.966 | -2.965
50025 | 241.1695 | 132.4857 | 275.164 | -0.659 | -2.306
50035 | 333.4495 | -146.7722 | 364.3222 | -3.624 | -3.295
50045 | 775.3505 | -358.9485 | 854.4076 | -3.953 | -9.554
50055 | 677.9506 | -49.2633 | 679.7381 | 3.624 | -1.977
50065 | 217.517 | 442.4776 | 493.0518 | 7.577 | 3.624
50075 | 58.0215 | 501.116 | 504.4638 | 2.965 | 0.988
50085 | 95.946 | 242.4636 | 260.757 | -1.317 | -0.658
50095 | 11.69 | -400.9252 | 401.0956 | -9.225 | 1.318
50105 | 67.0023 | -1230.9769 | 1232.799 | -15.485 | -0.989
50115 | -220.8203 | -1630.2082 | 1645.0959 | -12.519 | 4.942
50125 | -1080.9052 | -1286.5412 | 1680.3405 | -2.636 | 15.484
50135 | -1293.5229 | -860.7677 | 1553.7447 | 0 | 8.237
50145 | -1065.5417 | -518.5063 | 1185.0012 | 1.648 | 3.294
50155 | -686.2641 | -266.0502 | 736.0306 | 2.305 | -0.659
50165 | -672.3257 | -123.2072 | 683.5217 | 1.977 | 3.295
50175 | -1026.8041 | 218.6584 | 1049.8276 | 6.26 | 8.565
50185 | -738.5312 | 484.9893 | 883.54 | 6.26 | -0.988
50195 | -212.0064 | 598.8824 | 635.3006 | 5.271 | -5.271
50205 | 344.9116 | 620.5602 | 709.9711 | 4.283 | -8.896
50215 | 897.6934 | 414.3838 | 988.7201 | 0.329 | -11.86
50225 | 1301.9973 | 303.2503 | 1336.8462 | 0.989 | -12.19
50235 | 1310.6293 | 450.498 | 1385.8924 | 4.282 | -7.577
50245 | 1130.3008 | 559.3642 | 1261.1376 | 3.954 | -4.612
50255 | 989.853 | 891.8787 | 1332.3876 | 8.566 | -3.953
50265 | 981.2056 | 1057.8922 | 1442.8792 | 6.919 | -4.942
50275 | 885.4791 | 899.6252 | 1262.299 | 2.635 | -2.965
50285 | 506.9797 | 528.7495 | 732.5329 | -1.648 | 2.306
50295 | 229.976 | -11.5594 | 230.2663 | -6.588 | 2.306
50305 | 29.4254 | -558.812 | 559.5862 | -9.555 | 2.965
50315 | -70.8079 | -813.5687 | 816.6442 | -7.577 | 2.306
50325 | -59.4882 | -756.1766 | 758.5129 | -3.954 | 0.988
50335 | 5.5804 | -617.3468 | 617.372 | -2.306 | 0
50345 | -148.2049 | -561.9631 | 581.1775 | -2.635 | 3.295
50355 | -381.0006 | -413.3515 | 562.1574 | -0.33 | 4.942
50365 | -446.5516 | -325.0658 | 552.3369 | -0.659 | 3.295
50375 | -209.1381 | -340.0121 | 399.1829 | -1.647 | -1.318
50385 | -49.5054 | -494.4943 | 496.9662 | -3.953 | -0.989
50395 | -65.0501 | -574.5136 | 578.1845 | -3.295 | 0.659
50405 | -167.9317 | -617.2654 | 639.7012 | -3.294 | 1.977
50415 | -125.8721 | -574.8472 | 588.4667 | -1.977 | 0
50425 | -78.9668 | -330.9354 | 340.2264 | 1.647 | 0
50435 | -170.9898 | -74.0037 | 186.3171 | 2.965 | 1.977
50445 | -383.3222 | 187.8665 | 426.8838 | 4.612 | 4.282
50455 | -517.3847 | 409.3409 | 659.7325 | 5.272 | 3.954
50465 | -483.6218 | 523.4441 | 712.6596 | 4.612 | 1.976
50475 | -433.4687 | 486.1099 | 651.3048 | 2.636 | 1.648
50485 | -449.4519 | 440.6489 | 629.4271 | 2.306 | 2.306
50495 | -376.1083 | 406.4316 | 553.7546 | 1.976 | 0.659
50505 | -182.4636 | 391.7569 | 432.1648 | 1.978 | -1.647
50515 | -44.6391 | 351.2641 | 354.0891 | 1.317 | -1.648
50525 | -77.369 | 324.5749 | 333.6688 | 1.318 | 0.33
50535 | -131.8215 | 351.434 | 375.3436 | 1.977 | 0.658
50545 | -160.834 | 396.5901 | 427.9618 | 2.306 | 0.66
50555 | -60.8577 | 410.1665 | 414.6567 | 1.976 | -1.318
50565 | 175.3472 | 264.5698 | 317.4017 | -0.658 | -3.954
50575 | 192.836 | 94.2647 | 214.6429 | -1.648 | -1.318
50585 | 101.4123 | 23.1139 | 104.013 | -0.987 | 0
50595 | -13.7763 | 3.4262 | 14.196 | -0.66 | 0.989
50605 | 161.8013 | 84.3213 | 182.4547 | 0.989 | -3.295
50615 | 432.1518 | 164.9686 | 462.5687 | 1.317 | -5.271
50625 | 403.1438 | 20.7456 | 403.6772 | -1.977 | -1.647
50635 | 295.6085 | -140.7696 | 327.4148 | -2.635 | -0.659
50645 | 292.5717 | -262.0274 | 392.7551 | -2.965 | -1.647
50655 | 231.1281 | -267.7904 | 353.7399 | -1.648 | -0.33
50665 | 296.2285 | -130.6625 | 323.7654 | 0.66 | -2.306
50675 | 399.3489 | 44.6284 | 401.8348 | 1.976 | -2.965
50685 | 391.7418 | 43.4633 | 394.1455 | 0 | -1.647
50695 | 203.9457 | -16.8589 | 204.6413 | -0.658 | 1.318
50705 | -12.2384 | 60.4988 | 61.7242 | 1.317 | 2.635
50715 | -18.963 | 149.7464 | 150.9424 | 1.647 | 0.33
50725 | 74.9562 | 148.1214 | 166.0072 | 0.659 | -0.989
50735 | 40.4084 | 120.2116 | 126.8214 | 0.33 | 0.659
50745 | -22.2213 | -68.4121 | 71.9305 | -2.636 | 0.989
50755 | -158.9031 | -174.5146 | 236.0202 | -1.977 | 2.635
50765 | -166.3493 | -95.4736 | 191.8002 | 0.33 | 0.989
50775 | -194.6214 | 66.6314 | 205.7115 | 1.976 | 1.647
50785 | -131.356 | 310.473 | 337.1171 | 4.284 | 0
50795 | -79.1228 | 290.5368 | 301.118 | 0.988 | 0
50805 | -14.5015 | 265.9506 | 266.3457 | 1.318 | -0.659
50815 | 50.322 | 151.863 | 159.9834 | -0.659 | -0.988
50825 | 131.7035 | 84.3883 | 156.4199 | -0.33 | -1.648
50835 | 170.9779 | -6.5393 | 171.1029 | -1.317 | -1.318
50845 | 270.9606 | 59.9094 | 277.5046 | 0.988 | -2.635
50855 | 504.739 | 219.7004 | 550.4813 | 2.636 | -5.271
50865 | 621.6066 | 252.5459 | 670.9502 | 1.317 | -4.283
50875 | 553.6049 | 143.2598 | 571.8407 | -0.659 | -1.977
50885 | 385.97 | 23.3385 | 386.6749 | -1.318 | 0
50895 | 313.8321 | 62.9149 | 320.0764 | 0.66 | -0.659
50905 | 225.6783 | 49.1205 | 230.9622 | -0.33 | 0.329
50915 | 140.8038 | 63.3008 | 154.3784 | 0.33 | 0.66
50925 | 162.1198 | 60.105 | 172.903 | 0 | -0.66
50935 | 263.1574 | -273.9439 | 379.8646 | -5.601 | -1.977
50945 | 238.0491 | -230.5283 | 331.3769 | -0.33 | -0.329
50955 | 184.2163 | 546.1869 | 576.4163 | 11.531 | 0
50965 | 247.5037 | 1169.6802 | 1195.5793 | 12.19 | -1.647
50975 | 322.9713 | 1490.8674 | 1525.4494 | 11.201 | -1.977
50985 | 543.1588 | 1511.0797 | 1605.7345 | 7.907 | -4.941
50995 | 711.4297 | 927.2086 | 1168.695 | -2.306 | -4.942
51005 | 816.557 | 475.8101 | 945.0718 | -2.635 | -4.942
51015 | 834.1461 | 819.3363 | 1169.2355 | 7.577 | -3.954
51025 | 865.6153 | 1210.3233 | 1488.0095 | 8.895 | -4.282
51035 | 1150.6531 | 1119.8877 | 1605.6622 | 3.294 | -8.566
51045 | 1398.7256 | 1015.2594 | 1728.3474 | 3.295 | -8.895
51055 | 1503.0036 | 646.1101 | 1635.9945 | -2.306 | -7.907
51065 | 1459.2173 | 328.9303 | 1495.831 | -2.966 | -5.93
51075 | 1144.1738 | 0.14334 | 1144.1738 | -5.271 | -0.988
51085 | 783.2417 | -523.6843 | 942.1851 | -10.213 | 1.317
51095 | 552.1307 | -679.4954 | 875.5354 | -6.259 | 1.318
51105 | 487.0143 | -673.7322 | 831.323 | -4.942 | 0
51115 | 374.1354 | -402.1646 | 549.2847 | 0 | 1.318
51125 | 393.999 | -342.6517 | 522.1546 | -2.306 | -0.659
51135 | 457.9008 | -428.1563 | 626.8899 | -3.624 | -1.317
51145 | 204.6443 | -612.6288 | 645.905 | -5.601 | 3.624
51155 | -142.9755 | -732.5477 | 746.37 | -5.271 | 5.929
51165 | -264.8239 | -714.4071 | 761.9116 | -3.624 | 3.954
51175 | -310.9838 | -565.5313 | 645.3964 | -1.318 | 3.624
51185 | -491.454 | -560.7238 | 745.6126 | -2.965 | 5.93
51195 | -719.8572 | -355.402 | 802.8107 | 0.988 | 7.248
51205 | -867.336 | -112.6096 | 874.6158 | 2.307 | 6.919
51215 | -990.8504 | 196.7492 | 1010.1954 | 4.941 | 7.248
51225 | -1033.8587 | 456.0685 | 1129.9834 | 5.601 | 6.259
51235 | -1050.7806 | 533.3474 | 1178.3885 | 3.953 | 5.93
51245 | -924.604 | 444.2348 | 1025.7861 | 1.648 | 3.295
51255 | -1009.2852 | 365.0022 | 1073.2582 | 1.318 | 6.259
51265 | -878.0396 | 347.3546 | 944.2503 | 1.647 | 2.306
51275 | -742.2106 | 520.0316 | 906.2613 | 4.612 | 1.976
51285 | -727.677 | 737.9788 | 1036.4008 | 5.93 | 2.966
51295 | -560.1577 | 791.7068 | 969.8331 | 4.284 | 0
51305 | -464.9123 | 586.2774 | 748.241 | 0.329 | 0.658
51315 | -417.923 | 184.2605 | 456.7401 | -3.953 | 0.66
51325 | -461.7717 | -113.4537 | 475.5049 | -4.284 | 1.977
51335 | -326.1173 | -161.8588 | 364.0753 | -1.977 | -0.989
51345 | -15.5801 | -390.0921 | 390.4031 | -5.6 | -4.283
51355 | 226.9023 | -488.6567 | 538.7672 | -3.954 | -4.612
51365 | 171.5372 | -328.0379 | 370.1809 | -0.329 | -0.988
51375 | 132.7134 | -131.78 | 187.0263 | 0.989 | -1.318
51385 | 342.2969 | 179.2094 | 386.3718 | 4.282 | -4.942
51395 | 766.5271 | 189.1147 | 789.5113 | 0.659 | -9.224
51405 | 826.287 | 445.4118 | 938.6916 | 5.601 | -4.942
51415 | 771.4225 | 821.7192 | 1127.0826 | 8.237 | -3.954
51425 | 831.4077 | 793.5559 | 1149.3345 | 3.293 | -5.271
51435 | 1052.863 | 852.1312 | 1354.4918 | 5.272 | -7.907
51445 | 1150.4458 | 779.7851 | 1389.8166 | 2.636 | -6.589
51455 | 1188.5475 | 525.3463 | 1299.4745 | -0.66 | -6.26
51465 | 1227.814 | 387.2211 | 1287.4267 | 0 | -6.259
51475 | 1133.7851 | 298.4273 | 1172.4025 | -0.329 | -3.953
51485 | 777.8133 | 6.3352 | 777.8391 | -4.282 | 0.988
51495 | 214.3302 | -199.0683 | 292.5161 | -3.954 | 6.259
51505 | -158.0011 | -266.2759 | 309.6243 | -2.965 | 5.931
51515 | -232.2644 | -176.444 | 291.6834 | -0.659 | 3.294
51525 | -2.3652 | -92.7021 | 92.7322 | -0.329 | -1.317
51535 | -48.4662 | -12.3925 | 50.0255 | 0.329 | 2.306
51545 | -364.4338 | 57.8758 | 369.0008 | 0.659 | 6.259
51555 | -159.0686 | 178.5586 | 239.136 | 1.976 | -1.317
51565 | -74.0488 | 170.3082 | 185.7097 | 0.33 | 0.658
51575 | -314.6751 | 71.6129 | 322.721 | -0.988 | 4.942
51585 | -296.5735 | -93.3509 | 310.9184 | -2.636 | 1.317
51595 | -189.6119 | -94.4668 | 211.8411 | -0.659 | 0.33
51605 | 64.282 | 58.669 | 87.0301 | 1.647 | -2.965
51615 | 363.9392 | 130.2443 | 386.5428 | 0.989 | -4.942
51625 | 430.5525 | 143.1816 | 453.7361 | 0.659 | -2.635
51635 | 683.7098 | 73.9998 | 687.7027 | -0.659 | -6.59
51645 | 645.6016 | 1.3211 | 645.603 | -0.989 | -2.306
51655 | 487.603 | -44.0756 | 489.591 | -0.988 | -0.658
51665 | 219.5292 | -15.6069 | 220.0833 | 0 | 2.306
51675 | 397.52 | 182.1976 | 437.2849 | 2.965 | -3.953
51685 | 345.2996 | 254.0906 | 428.7118 | 1.647 | 0
51695 | 203.2513 | 377.7738 | 428.9803 | 3.295 | 0.987
51705 | 94.2414 | 497.5258 | 506.3727 | 3.624 | 1.318
51715 | 42.7458 | 405.5489 | 407.7955 | 0.659 | 0.989
51725 | -66.5127 | 364.3512 | 370.3724 | 1.318 | 2.306
51735 | 57.8108 | 414.7621 | 418.7717 | 2.306 | -1.318
51745 | 129.3251 | -22.3033 | 131.2342 | -5.93 | -0.658
51755 | 21.8207 | -414.3245 | 414.8987 | -6.59 | 1.647
51765 | -163.8586 | -460.6898 | 488.9629 | -3.294 | 3.294
51775 | -197.0849 | -487.8517 | 526.1575 | -3.623 | 1.647
51785 | -222.9116 | -491.5214 | 539.7063 | -2.966 | 1.977
51795 | -194.9095 | -288.0221 | 347.7735 | 0.659 | 0.989
51805 | -288.642 | -271.1769 | 396.0444 | -1.648 | 2.964
51815 | -527.5246 | -411.3189 | 668.9286 | -3.624 | 5.601
51825 | -569.7363 | -285.4723 | 637.2549 | 0.331 | 3.294
51835 | -481.1056 | -206.4682 | 523.5377 | -0.331 | 1.648
51845 | -194.058 | -251.553 | 317.7065 | -1.646 | -2.306
51855 | 51.6682 | -61.5607 | 80.3699 | 2.306 | -2.966
51865 | 260.2418 | 367.4518 | 450.2739 | 6.919 | -3.953
51875 | 173.8345 | 386.6728 | 423.9508 | 1.976 | 0
51885 | 203.8217 | 215.5881 | 296.6842 | -0.33 | -1.977
51895 | 123.5163 | 88.6965 | 152.0637 | -0.659 | 0.33
51905 | -235.8395 | -20.3609 | 236.7168 | -1.318 | 5.271
51915 | -347.5823 | 368.6961 | 506.7053 | 6.59 | 2.635
51925 | -269.7731 | 478.3138 | 549.1463 | 2.964 | 0.66
51935 | -80.3842 | 345.5369 | 354.7638 | 0.331 | -1.647
51945 | -64.9097 | 444.7391 | 449.4509 | 3.624 | 0.329
51955 | 226.9025 | 397.5113 | 457.7117 | 0.987 | -4.942
51965 | 101.4602 | 475.4396 | 486.145 | 3.295 | 1.318
51975 | -274.2979 | 614.484 | 672.9264 | 4.283 | 5.271
51985 | -11.7227 | 384.7455 | 384.9241 | -1.318 | -3.624
51995 | -100.4196 | 171.5768 | 198.8032 | -1.647 | 2.306
52005 | -80.8502 | -142.1046 | 163.4946 | -4.942 | -0.329
52015 | 6.9404 | -218.4881 | 218.5983 | -2.306 | -0.988
52025 | 235.5376 | -165.5019 | 287.8695 | -0.989 | -3.954
52035 | 214.9246 | -366.0799 | 424.508 | -4.941 | -0.659
52045 | -81.2058 | -464.8854 | 471.9246 | -3.624 | 3.624
52055 | -161.5281 | -437.994 | 466.8298 | -2.307 | 1.318
52065 | 11.9269 | -498.3593 | 498.502 | -3.624 | -1.976
52075 | 201.7896 | -234.5949 | 309.4411 | 1.977 | -2.966
52085 | 168.1709 | -212.333 | 270.863 | -1.317 | -0.329
52095 | -69.4113 | -168.8532 | 182.5632 | 0 | 2.965
52105 | -279.0677 | -314.6027 | 420.5397 | -3.295 | 3.623
52115 | -256.7658 | -536.4158 | 594.7021 | -4.942 | 0.989
52125 | -336.8715 | -821.2784 | 887.6828 | -7.248 | 2.966
52135 | -168.5538 | -794.9092 | 812.583 | -3.294 | -1.318
52145 | -157.7849 | -612.6809 | 632.6721 | -0.989 | 0.987
52155 | -108.6376 | -265.7869 | 287.1321 | 2.966 | -0.329
52165 | -195.6052 | 266.3677 | 330.4742 | 7.906 | 1.977
52175 | -121.2878 | 468.3391 | 483.7894 | 4.943 | -0.659
52185 | -25.8663 | 490.8106 | 491.4917 | 3.624 | -0.989
52195 | -237.8735 | 92.8846 | 255.3651 | -3.624 | 3.624
52205 | -761.06 | -189.1614 | 784.2157 | -3.295 | 9.554
52215 | -811.9301 | -456.2613 | 931.3457 | -5.272 | 3.955
52225 | -537.6148 | -492.5071 | 729.1042 | -2.635 | -0.331
52235 | -196.5736 | -263.9985 | 329.1449 | 1.317 | -2.964
52245 | -224.4944 | -385.8268 | 446.3856 | -3.624 | 1.318
52255 | -365.0946 | -581.1404 | 686.3077 | -4.612 | 2.635
52265 | -492.0292 | -648.6399 | 814.1415 | -3.624 | 3.295
52275 | -555.6516 | -589.5485 | 810.1334 | -1.976 | 2.965
52285 | -536.893 | -508.6741 | 739.5968 | -1.318 | 1.976
52295 | -348.6853 | -365.8198 | 505.3767 | 0.329 | -0.988
52305 | -131.7524 | -53.9627 | 142.3751 | 3.954 | -2.306
52315 | -105.2549 | -115.0672 | 155.9457 | -0.989 | -0.33
52325 | -10.4525 | -299.6396 | 299.8218 | -2.635 | -1.977
52335 | 94.1157 | -261.2094 | 277.6475 | 0 | -2.305
52345 | 185.0276 | -129.3837 | 225.7772 | 1.317 | -2.636
52355 | 251.7356 | -39.6124 | 254.8331 | 1.318 | -2.636
52365 | 358.6978 | 15.813 | 359.0462 | 1.318 | -3.624
52375 | 386.2433 | -21.9756 | 386.868 | 0 | -2.635
52385 | 285.7659 | -264.6396 | 389.4821 | -3.624 | -0.659
52395 | 176.0803 | -329.9442 | 373.9885 | -1.647 | 0
52405 | 53.6434 | -210.1727 | 216.9106 | 0.659 | 0.988
52415 | 28.909 | 14.0853 | 32.1579 | 2.965 | 0
52425 | 139.8178 | 170.4083 | 220.4269 | 2.965 | -1.976
52435 | 90.5148 | 16.9773 | 92.0932 | -1.318 | 0.329
52445 | -5.1302 | -363.5681 | 363.6043 | -5.6 | 0.989
52455 | -27.3126 | -630.0051 | 630.5969 | -5.601 | 0.329
52465 | -207.1793 | -829.6707 | 855.1472 | -6.26 | 3.295
52475 | -140.756 | -664.1134 | 678.8659 | -0.988 | -0.33
52485 | -23.5672 | -367.7942 | 368.5485 | 1.647 | -0.988
52495 | 236.9883 | 33.7442 | 239.3786 | 5.272 | -4.283
52505 | 276.3764 | 159.1688 | 318.9336 | 2.635 | -1.647
52515 | 100.0687 | 154.052 | 183.7002 | 1.647 | 1.318
52525 | 49.6019 | 158.0425 | 165.6435 | 1.648 | 0
52535 | 136.4234 | -57.9133 | 148.207 | -2.307 | -1.648
52545 | 223.3628 | -89.6378 | 240.6779 | 0 | -1.976
52555 | 374.4309 | -18.2284 | 374.8744 | 0.989 | -3.624
52565 | 391.393 | 242.7192 | 460.5443 | 4.612 | -1.977
52575 | 272.9073 | 209.7142 | 344.1779 | 0.659 | 0
52585 | 112.27 | 90.8052 | 144.3958 | -0.329 | 1.317
52595 | -51.2371 | -362.9363 | 366.5351 | -6.919 | 2.307
52605 | -218.8221 | -609.9211 | 647.9867 | -5.271 | 3.294
52615 | -297.5144 | -394.3743 | 494.01 | 0.658 | 2.636
52625 | -96.0438 | -293.5421 | 308.8549 | -0.658 | -1.647
52635 | -33.9848 | -149.2957 | 153.1149 | 1.318 | 0
52645 | 13.8299 | -40.2811 | 42.5892 | 1.318 | -0.66
52655 | 14.3396 | 120.8915 | 121.739 | 2.964 | 0
52665 | 199.9067 | 203.1047 | 284.9811 | 2.306 | -3.294
52675 | 331.4985 | 78.114 | 340.5775 | -0.658 | -2.965
52685 | 311.3035 | -58.7715 | 316.8027 | -1.318 | -1.318
52695 | 308.7255 | -159.1235 | 347.3208 | -1.648 | -1.647
52705 | 185.4439 | -261.5244 | 320.6001 | -2.306 | 0.659
52715 | 243.4291 | -468.3418 | 527.8274 | -4.612 | -1.977
52725 | 158.3662 | -431.3109 | 459.4659 | -1.318 | 0.659
52735 | -40.1691 | -263.1868 | 266.2346 | 0.659 | 2.636
52745 | -120.4532 | -210.1656 | 242.2366 | -0.329 | 1.646
52755 | -64.1546 | -97.7117 | 116.8905 | 1.318 | 0
52765 | 56.3249 | -47.4553 | 73.6512 | 0.658 | -1.317
52775 | -36.1511 | -138.6837 | 143.3181 | -1.317 | 1.648
52785 | 180.5835 | -152.8333 | 236.5764 | -0.33 | -3.624
52795 | 180.9744 | -223.0376 | 287.2238 | -1.648 | -0.33
52805 | -33.2466 | -473.8224 | 474.9874 | -4.941 | 2.636
52815 | -71.332 | -335.0592 | 342.5682 | 0.659 | 0.658
52825 | -127.8612 | -211.0896 | 246.7941 | 0.329 | 1.647
52835 | -65.0522 | -344.8864 | 350.9678 | -2.964 | -0.329
52845 | 106.901 | -115.3042 | 157.2351 | 2.964 | -2.306
52855 | 246.5143 | 284.571 | 376.4969 | 6.26 | -2.636
52865 | 410.9594 | 345.0545 | 536.6099 | 2.636 | -3.953
52875 | 492.4662 | 253.3636 | 553.8195 | 0.988 | -3.295
52885 | 503.4896 | 7.2444 | 503.5417 | -2.306 | -2.635
52895 | 264.3406 | -493.4141 | 559.7619 | -7.907 | 1.647
52905 | 293.3542 | -641.3933 | 705.2958 | -4.283 | -1.976
52915 | 281.9938 | -368.3762 | 463.9198 | 1.318 | -0.659
52925 | 159.1454 | -278.6163 | 320.8649 | -0.659 | 0.988
52935 | 30.8582 | -299.8155 | 301.3993 | -1.317 | 1.647
52945 | -207.3112 | -413.7964 | 462.8233 | -2.966 | 4.283
52955 | -269.4378 | -519.8745 | 585.5478 | -3.294 | 2.306
52965 | -387.5279 | -627.5435 | 737.5559 | -3.954 | 3.954
52975 | -375.794 | -340.9252 | 507.3964 | 2.306 | 1.977
52985 | -240.4227 | -9.7703 | 240.6211 | 3.953 | 0
52995 | -53.0308 | 390.656 | 394.2389 | 7.249 | -1.648
53005 | -159.3855 | 656.5958 | 675.664 | 6.918 | 2.306
53015 | -268.2609 | 500.4521 | 567.8171 | 1.318 | 2.306
53025 | -328.4212 | 175.1825 | 372.2223 | -1.976 | 2.306
53035 | -234.5137 | 23.5846 | 235.6966 | -0.989 | 0
53045 | -138.7911 | -87.4456 | 164.0418 | -1.647 | -0.329
53055 | -64.3635 | -108.7433 | 126.3636 | -0.659 | -0.659
53065 | -92.5059 | -18.6661 | 94.3704 | 0.988 | 0.659
53075 | 70.0922 | 48.1734 | 85.0505 | 0.989 | -2.635
53085 | 93.1153 | 46.6584 | 104.1512 | 0.329 | -0.659
53095 | -49.8647 | 213.2228 | 218.9759 | 3.295 | 1.646
53105 | -211.5921 | 215.0758 | 301.7098 | 0.988 | 2.637
53115 | -200.87 | 268.3219 | 335.1797 | 2.306 | 0.658
53125 | -194.7823 | 708.4124 | 734.7029 | 8.895 | 0.989
53135 | 86.2366 | 589.7566 | 596.0282 | 0.989 | -3.953
53145 | 174.0935 | 320.1024 | 364.3818 | -0.989 | -1.648
53155 | 179.3839 | 140.3756 | 227.7804 | -1.317 | -1.318
53165 | 170.7325 | 225.4387 | 282.7935 | 1.976 | -0.989
53175 | 245.4124 | 329.0179 | 410.4632 | 2.306 | -2.306
53185 | 310.0452 | 254.1092 | 400.8735 | 0 | -2.305
53195 | 544.5664 | 127.6376 | 559.3245 | -0.988 | -5.601
53205 | 536.9418 | 102.631 | 546.6622 | 0 | -2.306
53215 | 405.8112 | 59.0794 | 410.0892 | -0.659 | -0.66
53225 | 381.0696 | 136.0867 | 404.6401 | 1.318 | -1.646
53235 | 365.2934 | 125.3143 | 386.1903 | 0 | -1.318
53245 | 180.2232 | -91.9235 | 202.3125 | -3.295 | 1.647
53255 | 76.4363 | -123.4231 | 145.175 | -0.987 | 0.988
53265 | -34.5731 | 17.0553 | 38.551 | 1.317 | 1.977
53275 | -195.6964 | 40.5788 | 199.8592 | 0 | 3.294
53285 | -178.6747 | -157.374 | 238.0992 | -3.295 | 0.989
53295 | -323.3968 | -119.1861 | 344.6605 | 0 | 3.954
53305 | -378.3064 | -78.3848 | 386.3417 | -0.329 | 2.635
53315 | -420.9713 | -105.1721 | 433.9101 | -0.988 | 2.965
53325 | -500.5847 | 23.4278 | 501.1327 | 1.647 | 3.624
53335 | -545.3589 | 110.0511 | 556.352 | 1.317 | 3.294
53345 | -673.3773 | 21.2909 | 673.7138 | -0.988 | 4.942
53355 | -817.3215 | -53.8313 | 819.0924 | -0.988 | 5.601
53365 | -670.277 | -56.298 | 672.6372 | -0.33 | 1.318
53375 | -526.9536 | -52.2692 | 529.5396 | -0.329 | 0.988
53385 | -336.2269 | -91.3474 | 348.4148 | -0.989 | -0.988
53395 | -374.9348 | -162.0174 | 408.4431 | -1.646 | 1.977
53405 | -315.9753 | -193.8663 | 370.7081 | -1.318 | 0
53415 | -175.1472 | -192.8457 | 260.511 | -0.989 | -1.318
53425 | -95.871 | -173.8992 | 198.5754 | -0.659 | -0.988
53435 | -29.6765 | -47.3529 | 55.8837 | 1.318 | -1.318
53445 | 39.9554 | -67.0181 | 78.0248 | -0.659 | -1.648
53455 | 264.714 | -121.795 | 291.3889 | -0.988 | -4.612
53465 | 497.5981 | -39.0801 | 499.1303 | 0.988 | -5.6
53475 | 521.5504 | 128.6645 | 537.1865 | 2.636 | -3.295
53485 | 294.2166 | 284.4849 | 409.2616 | 3.294 | 0.658
53495 | 169.3851 | 254.1389 | 305.4143 | 0.989 | 0
53505 | -40.4761 | 25.8019 | 48.0006 | -2.306 | 2.637
53515 | -81.6064 | -157.4843 | 177.3722 | -2.636 | 0.658
53525 | -46.8283 | -113.4762 | 122.7589 | 0 | 0
53535 | -26.8997 | -44.0026 | 51.5735 | 0.33 | 0
53545 | -114.9816 | 108.3105 | 157.9618 | 2.306 | 1.648
53555 | -283.726 | 201.3428 | 347.9071 | 1.976 | 3.294
53565 | -538.8122 | 235.0423 | 587.8464 | 1.648 | 5.601
53575 | -607.4519 | 257.9321 | 659.9446 | 1.647 | 3.623
53585 | -405.391 | 47.3088 | 408.1421 | -2.307 | -0.329
53595 | -313.0425 | -118.6991 | 334.7912 | -2.306 | 0.659
53605 | -395.1457 | -79.3339 | 403.0311 | 0 | 2.636
53615 | -427.5466 | -16.6713 | 427.8715 | 0.33 | 1.976
53625 | -458.5449 | -40.8489 | 460.3608 | -0.659 | 2.306
53635 | -447.4292 | 66.2187 | 452.3027 | 1.647 | 1.648
53645 | -321.8202 | 118.4537 | 342.9279 | 0.988 | -0.33
53655 | -94.0464 | 275.1612 | 290.7893 | 3.295 | -2.635
53665 | -29.7919 | 495.5344 | 496.4292 | 4.942 | -0.989
53675 | 50.8924 | 649.6985 | 651.6887 | 4.941 | -1.976
53685 | 216.6812 | 636.2515 | 672.1359 | 2.966 | -3.624
53695 | 149.1972 | 658.3455 | 675.0397 | 3.624 | -0.33
53705 | 271.7471 | 731.7317 | 780.5625 | 4.282 | -3.624
53715 | 471.7189 | 753.3059 | 888.8129 | 3.624 | -4.942
53725 | 725.6618 | 709.9764 | 1015.2101 | 2.637 | -6.918
53735 | 796.0244 | 567.3359 | 977.5095 | 0.658 | -4.942
53745 | 753.956 | 467.3 | 887.0282 | 0.659 | -3.624
53755 | 580.1758 | 161.9772 | 602.3625 | -3.624 | -0.988
53765 | 307.1443 | -128.9329 | 333.1086 | -4.612 | 1.647
53775 | 180.6591 | -336.6487 | 382.0603 | -4.942 | 0.659
53785 | -75.2095 | -421.5272 | 428.1841 | -3.954 | 3.954
53795 | -273.5204 | -440.7275 | 518.7043 | -3.294 | 3.953
53805 | -341.0774 | -444.1702 | 560.0187 | -2.965 | 2.965
53815 | -307.8839 | -419.1229 | 520.0543 | -2.306 | 1.647
53825 | -307.1222 | -273.9145 | 411.5254 | 0 | 1.977
53835 | -168.1222 | -131.7896 | 213.6202 | 0.659 | -0.659
53845 | -176.8633 | -65.0551 | 188.4484 | 0.329 | 1.318
53855 | -152.9535 | -86.1682 | 175.5555 | -0.659 | 0.329
53865 | -87.7355 | -222.206 | 238.8996 | -2.636 | -0.329
53875 | -139.8282 | -227.5126 | 267.0466 | -0.988 | 1.318
53885 | -363.1594 | -250.8343 | 441.3644 | -1.647 | 4.283
53895 | -548.4089 | -336.1231 | 643.2193 | -2.636 | 4.611
53905 | -474.0048 | -151.3417 | 497.579 | 1.647 | 1.319
53915 | -441.5675 | -53.3152 | 444.7745 | 0.66 | 1.976
53925 | -269.5873 | 45.6486 | 273.4247 | 1.647 | -0.988
53935 | -175.2259 | 44.1912 | 180.7124 | 0.329 | -0.33
53945 | -206.9002 | 128.44 | 243.5252 | 1.977 | 0.989
53955 | -82.8766 | 203.8979 | 220.0975 | 1.977 | -1.647
53965 | -51.7736 | 79.0172 | 94.4681 | -0.989 | -0.33
53975 | -48.0653 | -23.071 | 53.3155 | -0.988 | -0.329
53985 | 56.4872 | -212.4272 | 219.8093 | -3.295 | -1.977
53995 | -31.6499 | -411.4715 | 412.687 | -4.282 | 0.988
54005 | 38.3726 | -199.4529 | 203.1106 | 1.647 | -1.647
54015 | 117.0142 | -53.0043 | 128.4593 | 0.988 | -1.648
54025 | 374.7959 | -4.2318 | 374.8197 | 0.66 | -5.27
54035 | 364.2342 | -52.5166 | 368.0007 | -0.66 | -1.647
54045 | 495.6865 | -150.0204 | 517.8911 | -1.647 | -4.613
54055 | 527.216 | -523.9379 | 743.2817 | -6.918 | -2.965
54065 | 226.6227 | -578.15 | 620.9792 | -2.966 | 2.306
54075 | -58.5643 | -493.1169 | 496.5824 | -1.647 | 3.295
54085 | -117.221 | -253.3815 | 279.1827 | 1.647 | 1.317
54095 | 112.969 | 14.4253 | 113.8863 | 3.295 | -2.964
54105 | 249.6534 | 343.5161 | 424.6529 | 5.93 | -2.306
54115 | 221.6283 | 480.9036 | 529.5162 | 4.283 | -0.66
54125 | 115.084 | 422.2595 | 437.6613 | 1.976 | 0.66
54135 | 42.4872 | 342.1061 | 344.7343 | 1.318 | 0.658
54145 | 77.46 | -63.173 | 99.9544 | -4.942 | -0.658
54155 | -254.2388 | -331.0578 | 417.4166 | -4.282 | 5.6
54165 | -373.7179 | -326.856 | 496.4875 | -1.648 | 2.965
54175 | -530.8966 | -308.1271 | 613.8351 | -1.647 | 4.942
54185 | -509.7048 | 92.3629 | 518.0056 | 5.271 | 2.306
54195 | -401.179 | 77.5641 | 408.6084 | -0.329 | 0.989
54205 | -316.5415 | 0.38481 | 316.5417 | -0.329 | 0.658
54215 | -154.2597 | 256.242 | 299.092 | 4.612 | -1.318
54225 | -17.6639 | 429.2365 | 429.5998 | 3.953 | -1.647
54235 | 10.1432 | 295.1671 | 295.3413 | 0 | -0.659
54245 | 328.5087 | 163.3881 | 366.8973 | -0.329 | -5.93
54255 | 528.6337 | 92.7661 | 536.7114 | -0.33 | -4.942
54265 | 738.0923 | 32.4918 | 738.8071 | -0.658 | -6.588
54275 | 419.8544 | -258.9404 | 493.2827 | -4.942 | 1.646
54285 | 171.1645 | -523.1077 | 550.3989 | -5.601 | 1.318
54295 | 121.9923 | -500.2899 | 514.9487 | -2.306 | 0
54305 | 200.7117 | -175.7427 | 266.7783 | 2.635 | -1.647
54315 | 88.0151 | 96.0384 | 130.2691 | 3.295 | 1.318
54325 | -54.2884 | 296.7695 | 301.6941 | 3.953 | 1.977
54335 | 28.0408 | 508.5614 | 509.3338 | 5.272 | -0.988
54345 | 144.8208 | 296.6223 | 330.0877 | -0.989 | -1.648
54355 | 407.3626 | 438.6619 | 598.6389 | 4.613 | -4.942
54365 | 276.1532 | 622.8569 | 681.3305 | 4.941 | 0.659
54375 | 60.984 | 564.002 | 567.2894 | 1.978 | 1.976
54385 | 45.0193 | 83.7673 | 95.0984 | -5.272 | 0
54395 | -20.0618 | -253.8438 | 254.6353 | -4.942 | 1.318
54405 | -157.6695 | -313.0135 | 350.4813 | -2.635 | 2.637
54415 | 50.0618 | -280.4977 | 284.9301 | -1.648 | -2.637
54425 | 229.2923 | 116.9217 | 257.3823 | 4.942 | -2.635
54435 | 117.062 | 92.1948 | 149.008 | -0.659 | 0.988
54445 | 321.3821 | 276.4078 | 423.8959 | 3.953 | -4.282
54455 | 530.3482 | 585.8699 | 790.2612 | 6.261 | -4.613
54465 | 734.5285 | 586.5035 | 939.9566 | 2.635 | -5.93
54475 | 479.0384 | 229.8067 | 531.3087 | -2.966 | 0.989
54485 | 145.1752 | 143.0363 | 203.8019 | 0 | 2.964
54495 | 418.8645 | 152.2425 | 445.6739 | 0.331 | -5.27
54505 | 731.7725 | 114.5908 | 740.6902 | -0.331 | -6.261
54515 | 574.3557 | 139.1458 | 590.9704 | 0.66 | -0.329
54525 | 153.8717 | -28.6084 | 156.5086 | -2.636 | 4.283
54535 | -96.6834 | 3.6342 | 96.7517 | 0.329 | 3.624
54545 | -85.6435 | -116.5188 | 144.6079 | -2.635 | 0.989
54555 | -102.0538 | -230.5742 | 252.1496 | -2.636 | 1.647
54565 | -95.6237 | -319.7822 | 333.7732 | -2.965 | 0.988
54575 | -168.3906 | -462.1229 | 491.8465 | -4.283 | 2.306
54585 | -291.7732 | -436.7769 | 525.2672 | -1.976 | 3.294
54595 | -285.9073 | -385.8166 | 480.2056 | -1.648 | 1.648
54605 | -348.2807 | -344.7948 | 490.0846 | -1.318 | 2.965
54615 | -430.1448 | -245.8683 | 495.4551 | 0 | 3.294
54625 | -258.4252 | -2.5959 | 258.4382 | 2.966 | -0.659
54635 | -234.4182 | 136.0939 | 271.0599 | 2.306 | 1.319
54645 | -366.7462 | 194.2111 | 414.9949 | 1.976 | 3.294
54655 | -313.3336 | 216.2287 | 380.7004 | 1.648 | 0.659
54665 | -426.4264 | 42.6791 | 428.5569 | -1.648 | 3.624
54675 | -516.301 | 24.2917 | 516.8722 | 0.33 | 3.295
54685 | -702.4585 | -150.5658 | 718.4135 | -2.965 | 5.6
54695 | -694.915 | -161.7074 | 713.4817 | -0.659 | 2.965
54705 | -668.8553 | -199.818 | 698.065 | -1.648 | 2.965
54715 | -475.0926 | -11.1924 | 475.2244 | 2.307 | -0.329
54725 | -521.0314 | 66.966 | 525.3172 | 0.988 | 2.965
54735 | -495.6985 | 36.9066 | 497.0705 | 0 | 1.318
54745 | -535.3423 | 52.1574 | 537.8771 | 0.659 | 2.635
54755 | -443.5112 | 72.8369 | 449.4524 | 0.659 | 0.33
54765 | -401.3214 | 143.9446 | 426.3553 | 1.647 | 0.988
54775 | -463.96 | 46.2964 | 466.2641 | -0.988 | 2.306
54785 | -399.1374 | 56.1511 | 403.0678 | 0.659 | 0.329
54795 | -144.7411 | 46.9198 | 152.156 | 0 | -2.964
54805 | -53.3718 | 51.0357 | 73.8457 | 0.329 | -1.318
54815 | 42.6128 | 116.1249 | 123.6966 | 1.318 | -2.306
54825 | 84.4381 | 31.7934 | 90.2253 | -0.988 | -1.648
54835 | 71.7474 | 70.9627 | 100.9128 | 0.988 | -0.988
54845 | 85.7154 | 120.1167 | 147.564 | 0.988 | -1.318
54855 | -9.755 | 147.1965 | 147.5194 | 0.988 | 0.659
54865 | -122.7029 | -180.4358 | 218.2042 | -4.941 | 1.318
54875 | -115.8901 | -326.4368 | 346.3979 | -2.965 | 0
54885 | -39.5571 | -216.4028 | 219.9885 | 0 | -0.989
54895 | -24.053 | -149.4005 | 151.3243 | -0.33 | -0.329
54905 | 54.8017 | -84.549 | 100.7559 | 0.33 | -1.647
54915 | 81.9106 | -1.1716 | 81.919 | 0.988 | -0.988
54925 | 15.9776 | 17.3891 | 23.6149 | 0.33 | 0.329
54935 | -206.2312 | -169.6385 | 267.0365 | -2.966 | 3.295
54945 | -292.4712 | -200.3003 | 354.485 | -0.988 | 1.976
54955 | -271.8781 | -136.8162 | 304.3622 | 0 | 0.988
54965 | -276.2724 | -56.2489 | 281.9404 | 0.659 | 1.318
54975 | -327.353 | -138.1236 | 355.3 | -1.647 | 1.977
54985 | -272.3506 | -155.5866 | 313.6591 | -0.659 | 0.329
54995 | -358.333 | -286.9485 | 459.0664 | -2.965 | 2.636
55005 | -363.7352 | -337.5838 | 496.2521 | -1.977 | 1.318
55015 | -217.8267 | -108.5171 | 243.3607 | 2.307 | -0.988
55025 | -109.6358 | 89.2533 | 141.3724 | 2.635 | -0.989
55035 | -124.1429 | 110.3887 | 166.1238 | 0.988 | 0.329
55045 | -201.3753 | 91.9098 | 221.3582 | 0.659 | 1.318
55055 | -196.2709 | 105.5489 | 222.8516 | 0.988 | 0.33
55065 | -122.8377 | 122.5544 | 173.5186 | 0.989 | -0.659
55075 | -11.7295 | 20.5659 | 23.6756 | -0.989 | -1.647
55085 | 66.49 | 74.9527 | 100.194 | 1.318 | -1.648
55095 | 97.3666 | 175.3414 | 200.5613 | 1.977 | -1.317
55105 | 195.3002 | -105.0139 | 221.7433 | -3.953 | -2.636
55115 | 140.9044 | -375.8078 | 401.3547 | -4.612 | -0.329
55125 | 202.8173 | -213.8749 | 294.7496 | 0.988 | -2.306
55135 | 443.6747 | 282.4628 | 525.9586 | 6.918 | -5.272
55145 | 489.6351 | 249.4199 | 549.5023 | 0.33 | -2.965
55155 | 228.6512 | 59.9062 | 236.3686 | -1.318 | 1.647
55165 | -61.7186 | -34.2413 | 70.5808 | -0.988 | 3.295
55175 | -149.4419 | -121.5193 | 192.6131 | -1.648 | 1.647
55185 | -187.9562 | -145.8518 | 237.9081 | -0.988 | 1.648
55195 | -222.0094 | -137.2339 | 261.0006 | -0.659 | 1.647
55205 | -230.5586 | -171.9685 | 287.629 | -1.318 | 1.317
55215 | -276.8238 | -69.1891 | 285.3394 | 0.989 | 1.977
55225 | -240.9018 | 54.8728 | 247.0723 | 1.647 | 0.659
55235 | -55.067 | 152.6585 | 162.2868 | 1.977 | -1.976
55245 | 61.6843 | 6.3746 | 62.0128 | -1.648 | -1.648
55255 | -65.9898 | 17.4937 | 68.2692 | 0.659 | 1.648
55265 | -39.4124 | 325.7354 | 328.1111 | 5.271 | -0.66
55275 | 66.281 | 444.5527 | 449.4667 | 3.295 | -1.647
55285 | 195.7553 | 456.5647 | 496.761 | 2.635 | -2.635
55295 | 363.5248 | 489.9004 | 610.0432 | 2.966 | -3.954
55305 | 368.9544 | 466.5446 | 594.8035 | 1.976 | -1.976
55315 | 338.8682 | 641.4639 | 725.4706 | 5.272 | -1.648
55325 | 463.2993 | 618.5698 | 772.8356 | 2.306 | -3.953
55335 | 474.6044 | 364.6909 | 598.5389 | -1.318 | -2.306
55345 | 275.186 | 30.1583 | 276.8336 | -3.954 | 0.988
55355 | 128.0602 | -329.5653 | 353.5713 | -6.259 | 0.989
55365 | 7.2206 | -538.948 | 538.9963 | -5.601 | 1.647
55375 | -172.6039 | -652.4628 | 674.9072 | -5.271 | 3.294
55385 | -189.2722 | -680.7439 | 706.5665 | -4.283 | 1.318
55395 | -126.4399 | -514.2557 | 529.5715 | -0.988 | 0.329
55405 | -185.0705 | -433.1907 | 471.0682 | -1.648 | 1.977
55415 | -206.7473 | -309.3866 | 372.1082 | 0 | 1.318
55425 | -214.7565 | -104.3716 | 238.7756 | 1.977 | 1.318
55435 | -283.0552 | 211.1517 | 353.1364 | 4.942 | 2.306
55445 | -320.3857 | 224.645 | 391.2958 | 1.318 | 1.977
55455 | -419.8131 | 180.4039 | 456.9339 | 0.988 | 3.294
55465 | -327.7546 | 300.9559 | 444.9692 | 3.295 | 0.33
55475 | -205.9432 | 445.1455 | 490.4764 | 3.953 | -0.33
55485 | -287.6206 | 466.8614 | 548.3476 | 2.635 | 2.306
55495 | -309.6359 | 590.1314 | 666.4304 | 4.613 | 1.318
55505 | -194.1261 | 525.3018 | 560.024 | 1.647 | -0.659
55515 | 85.5255 | 403.335 | 412.3029 | 0.659 | -3.953
55525 | 230.6258 | 311.9088 | 387.9115 | 0.329 | -2.965
55535 | 252.13 | 27.0872 | 253.5809 | -3.624 | -1.977
55545 | 362.6265 | -476.6784 | 598.9326 | -8.565 | -3.624
55555 | 612.4958 | -625.4003 | 875.3723 | -4.942 | -6.26
55565 | 588.7139 | -686.2646 | 904.1809 | -4.942 | -2.635
55575 | 659.988 | -672.6427 | 942.3547 | -3.623 | -4.613
55585 | 781.4768 | -667.9994 | 1028.0706 | -3.624 | -5.27
55595 | 755.4268 | -854.2699 | 1140.3713 | -6.59 | -3.295
55605 | 575.7689 | -760.8921 | 954.1837 | -2.306 | -0.66
55615 | 240.1141 | -608.3819 | 654.0514 | -1.318 | 2.966
55625 | -32.9808 | -406.8454 | 408.18 | 0.659 | 3.624
55635 | -474.0214 | -326.6392 | 575.6644 | -0.329 | 8.236
55645 | -783.5581 | -290.4979 | 835.6748 | -0.33 | 7.907
55655 | -557.9508 | -128.8598 | 572.6377 | 1.977 | 0.659
55665 | -636.5902 | 209.2525 | 670.0998 | 5.601 | 5.271
55675 | -724.2084 | 475.5772 | 866.4015 | 5.93 | 4.612
55685 | -737.1958 | 456.0286 | 866.8446 | 2.636 | 3.954
55695 | -790.2695 | 387.5374 | 880.1767 | 1.976 | 4.612
55705 | -900.2061 | 225.0576 | 927.9127 | -0.329 | 5.601
55715 | -891.6888 | 16.3718 | 891.8391 | -1.977 | 3.953
55725 | -687.0193 | -331.982 | 763.0253 | -5.6 | 0.659
55735 | -559.494 | -486.7218 | 741.5738 | -3.955 | 0.989
55745 | -322.3477 | -375.1068 | 494.5838 | -0.658 | -1.977
55755 | 85.3633 | -76.1719 | 114.4074 | 2.965 | -5.93
55765 | 396.2254 | -214.8315 | 450.7185 | -2.965 | -6.26
55775 | 443.0042 | -349.1018 | 564.0256 | -2.635 | -3.624
55785 | 616.3946 | -379.2979 | 723.7466 | -1.977 | -6.259
55795 | 869.5474 | -261.0318 | 907.8823 | 0.329 | -7.907
55805 | 1036.2999 | -266.6592 | 1070.0582 | -1.318 | -7.577
55815 | 1037.5484 | -312.7689 | 1083.6656 | -1.647 | -5.601
55825 | 924.6953 | -246.4396 | 956.9712 | 0 | -3.624
55835 | 664.9702 | -400.9738 | 776.5085 | -3.624 | -0.329
55845 | 468.4683 | -345.4195 | 582.0456 | -0.329 | 0
55855 | 297.6882 | -62.2016 | 304.1173 | 3.294 | 0.988
55865 | 239.6299 | 122.044 | 268.9186 | 2.965 | 0
55875 | 326.6219 | 344.3548 | 474.6179 | 4.942 | -1.977
55885 | 182.3636 | 587.9268 | 615.5602 | 6.259 | 1.647
55895 | -7.6755 | 799.1273 | 799.1641 | 6.919 | 2.635
55905 | -266.4103 | 796.1354 | 839.5272 | 4.283 | 4.943
55915 | -397.396 | 457.793 | 606.2161 | -1.318 | 3.953
55925 | -341.2077 | 135.6325 | 367.1769 | -2.636 | 1.647
55935 | -509.8814 | 55.8744 | 512.9337 | -0.658 | 5.272
55945 | -705.1202 | -88.7854 | 710.6879 | -2.636 | 5.93
55955 | -683.4405 | -342.6713 | 764.5355 | -4.942 | 3.294
55965 | -617.4925 | -334.7746 | 702.4037 | -1.647 | 2.636
55975 | -626.2432 | -129.7915 | 639.5517 | 1.318 | 3.294
55985 | -533.6872 | -46.876 | 535.7419 | 0.329 | 1.318
55995 | -327.7494 | 22.7776 | 328.5399 | 0.988 | -0.988
56005 | 64.739 | 151.3667 | 164.6299 | 2.307 | -5.272
56015 | 366.4339 | -4.8005 | 366.4653 | -1.977 | -5.6
56025 | 480.134 | -105.2742 | 491.5397 | -1.318 | -4.283
56035 | 570.7436 | -228.1664 | 614.661 | -2.635 | -4.613
56045 | 552.7773 | -263.4828 | 612.361 | -1.647 | -2.964
56055 | 577.8272 | -124.0884 | 591.001 | 0.988 | -3.624
56065 | 538.6314 | -56.7022 | 541.6077 | 0.329 | -2.306
56075 | 586.8046 | 47.9839 | 588.7632 | 1.647 | -3.624
56085 | 544.4723 | 70.6169 | 549.0326 | 0.66 | -1.977
56095 | 448.6656 | 55.7437 | 452.1152 | 0.329 | -0.989
56105 | 292.0836 | -28.4166 | 293.4626 | -0.989 | 0.66
56115 | 48.9223 | -71.4857 | 86.6232 | -0.658 | 2.964
56125 | -46.0422 | 4.0054 | 46.2161 | 0.988 | 1.648
56135 | -35.1563 | -68.8409 | 77.2984 | -1.318 | 0.658
56145 | -9.6948 | -140.649 | 140.9828 | -1.318 | 0.33
56155 | 0.83949 | -162.178 | 162.1802 | -0.989 | 0.33
56165 | -74.5224 | -135.9315 | 155.0192 | -0.329 | 1.647
56175 | -233.7189 | -116.4834 | 261.1377 | -0.329 | 3.294
56185 | -235.0844 | -30.8169 | 237.0956 | 0.989 | 1.318
56195 | -84.6776 | -3.8061 | 84.7631 | 0.329 | -0.988
56205 | 21.5984 | -14.6157 | 26.079 | 0 | -0.989
56215 | 137.8035 | -79.2875 | 158.9853 | -0.989 | -1.976
56225 | 67.1152 | -146.4984 | 161.1404 | -1.317 | 0.658
56235 | -59.5887 | -209.0725 | 217.3985 | -1.647 | 1.648
56245 | -6.3403 | -233.3648 | 233.4509 | -1.318 | -0.659
56255 | 127.7258 | -363.0512 | 384.8637 | -3.295 | -1.977
56265 | 180.0876 | -448.5204 | 483.324 | -2.965 | -1.318
56275 | 89.733 | -461.3683 | 470.0136 | -2.307 | 0.659
56285 | 37.6114 | -470.0658 | 471.5681 | -2.305 | 0.33
56295 | -5.0929 | -445.0132 | 445.0423 | -1.648 | 0.659
56305 | 2.4379 | -409.1295 | 409.1368 | -1.317 | 0
56315 | -83.2946 | -273.7595 | 286.1507 | 0.659 | 1.647
56325 | -40.6649 | -250.0152 | 253.3007 | -0.659 | -0.329
56335 | -51.1429 | -329.1011 | 333.0512 | -1.977 | 0.658
56345 | -131.1712 | -483.6104 | 501.0837 | -3.624 | 1.648
56355 | -113.5394 | -728.4267 | 737.2223 | -5.931 | 0.329
56365 | -205.2462 | -635.3234 | 667.654 | -1.317 | 2.306
56375 | -306.5751 | -554.5115 | 633.6177 | -1.647 | 2.636
56385 | -257.3323 | -351.3836 | 435.5346 | 1.318 | 0.659
56395 | -96.1709 | -179.6645 | 203.7846 | 1.646 | -1.319
56405 | -61.3932 | -55.122 | 82.508 | 1.977 | 0
56415 | -19.1039 | 68.5873 | 71.1982 | 2.636 | -0.658
56425 | -39.664 | 216.7058 | 220.3057 | 3.624 | 0.329
56435 | -157.6515 | 268.7488 | 311.5765 | 2.635 | 1.977
56445 | -282.7008 | 165.3656 | 327.5142 | 0.33 | 2.636
56455 | -307.3521 | 71.1671 | 315.4838 | 0 | 1.647
56465 | -219.5953 | 1.7993 | 219.6027 | -0.33 | 0
56475 | -40.0601 | 17.1464 | 43.5754 | 0.66 | -1.977
56485 | 66.2722 | -115.6542 | 133.2963 | -1.977 | -1.647
56495 | 50.0445 | -245.2796 | 250.3328 | -2.307 | -0.33
56505 | -102.5614 | -421.344 | 433.6469 | -3.953 | 1.977
56515 | -175.3627 | -473.9239 | 505.3276 | -2.635 | 1.318
56525 | -93.6694 | -382.2554 | 393.5647 | -0.66 | -0.659
56535 | 127.1396 | -181.4192 | 221.5342 | 1.648 | -3.294
56545 | 285.9958 | -61.7419 | 292.5844 | 1.318 | -3.295
56555 | 210.3031 | -129.6565 | 247.059 | -0.989 | -0.329
56565 | 198.8277 | -94.4366 | 220.1153 | 0.66 | -1.319
56575 | 136.8694 | -67.8511 | 152.7645 | 0.329 | 0
56585 | 87.3031 | 1.9075 | 87.3239 | 1.318 | 0
56595 | -54.2247 | 0.37556 | 54.226 | 0.329 | 1.977
56605 | -315.4183 | -9.1449 | 315.5508 | 0.33 | 4.613
56615 | -502.813 | -106.1298 | 513.8914 | -1.319 | 4.612
56625 | -602.3726 | -238.099 | 647.7221 | -2.305 | 4.283
56635 | -787.6092 | -384.4063 | 876.4111 | -3.295 | 6.26
56645 | -724.2896 | -390.1935 | 822.7067 | -1.648 | 2.635
56655 | -312.5732 | -438.7464 | 538.7025 | -2.635 | -3.294
56665 | -73.1518 | -276.7129 | 286.2188 | 0.989 | -2.307
56675 | -63.2326 | -162.4421 | 174.3152 | 0.659 | -0.329
56685 | -88.368 | 30.6784 | 93.5418 | 2.965 | 0
56695 | -211.9617 | 118.5625 | 242.868 | 1.977 | 1.977
56705 | -245.9014 | 183.5649 | 306.8608 | 2.306 | 0.988
56715 | -348.5487 | 198.2205 | 400.9707 | 1.647 | 2.636
56725 | -316.7758 | 150.218 | 350.5886 | 0.659 | 0.659
56735 | -277.037 | 214.6166 | 350.4423 | 2.305 | 0.659
56745 | -335.7734 | 258.9119 | 424.0037 | 1.977 | 1.976
56755 | -271.6594 | 399.896 | 483.4415 | 3.953 | 0
56765 | -364.7534 | 340.4326 | 498.9383 | 0.989 | 2.636
56775 | -434.6416 | 46.4339 | 437.1149 | -2.965 | 2.306
56785 | -337.0369 | -87.2716 | 348.1526 | -1.647 | 0
56795 | -238.0831 | -15.0957 | 238.5612 | 0.659 | -0.329
56805 | -122.0559 | -146.6689 | 190.8125 | -2.636 | -1.318
56815 | 152.4876 | -269.8552 | 309.9586 | -2.635 | -4.613
56825 | 242.6605 | -325.0156 | 405.6097 | -2.306 | -2.635
56835 | 242.4319 | -419.9396 | 484.8943 | -3.295 | -1.977
56845 | 211.6572 | -304.5039 | 370.8388 | 0 | -1.318
56855 | 196.5052 | -243.8198 | 313.1491 | -0.659 | -1.318
56865 | 195.1014 | -262.6475 | 327.1823 | -1.318 | -1.317
56875 | 391.4808 | -224.194 | 451.1321 | -0.329 | -4.613
56885 | 454.6704 | -36.85 | 456.1612 | 2.306 | -2.964
56895 | 55.1721 | -184.977 | 193.0297 | -2.635 | 4.282
56905 | -254.446 | -291.1522 | 386.6683 | -1.977 | 4.283
56915 | -239.6336 | -32.5232 | 241.8305 | 3.294 | 0.989
56925 | -262.5738 | 504.4432 | 568.6896 | 8.895 | 1.976
56935 | -378.8752 | 616.6186 | 723.716 | 4.283 | 3.295
56945 | -353.991 | 622.1986 | 715.8497 | 3.954 | 1.317
56955 | -188.7312 | 667.2997 | 693.4756 | 4.283 | -0.988
56965 | -207.4552 | 368.0034 | 422.4502 | -1.648 | 1.318
56975 | -268.1765 | 229.8369 | 353.1907 | 0 | 1.647
56985 | -420.6966 | 273.4173 | 501.7397 | 1.648 | 3.624
56995 | -478.9432 | 274.976 | 552.2666 | 0.987 | 2.636
57005 | -275.6415 | 246.397 | 369.7158 | 0.66 | -1.318
57015 | -79.3249 | 169.5158 | 187.1578 | -0.329 | -1.977
57025 | 58.4675 | -2.4667 | 58.5196 | -2.307 | -2.306
57035 | 110.8918 | -166.6853 | 200.2023 | -2.965 | -1.647
57045 | 123.6532 | -218.0064 | 250.6331 | -1.976 | -1.318
57055 | 117.4765 | -188.5617 | 222.1626 | -0.989 | -0.988
57065 | 309.3669 | -170.3871 | 353.185 | -0.988 | -4.283
57075 | 544.2486 | -263.532 | 604.6947 | -2.636 | -5.601
57085 | 608.1627 | -246.374 | 656.1723 | -0.988 | -3.953
57095 | 467.2949 | -182.5423 | 501.6834 | -0.33 | -0.988
57105 | 231.2965 | 28.859 | 233.0899 | 2.636 | 1.317
57115 | 17.8967 | 32.3148 | 36.9397 | 0 | 2.307
57125 | -156.915 | 138.4738 | 209.2781 | 2.306 | 2.964
57135 | -351.4564 | 255.2726 | 434.3797 | 2.636 | 4.284
57145 | -453.7015 | 292.612 | 539.8767 | 1.977 | 3.623
57155 | -384.281 | 256.8643 | 462.2241 | 0.988 | 1.318
57165 | -369.3042 | 213.2039 | 426.4288 | 0.658 | 1.977
57175 | -379.9954 | 93.529 | 391.3364 | -0.988 | 1.976
57185 | -487.6981 | -32.4276 | 488.775 | -1.647 | 3.624
57195 | -576.3036 | -56.6469 | 579.0809 | -0.659 | 3.624
57205 | -365.441 | -82.7733 | 374.6979 | -0.988 | -0.988
57215 | -80.3186 | -12.0828 | 81.2224 | 0.659 | -2.965
57225 | 65.708 | 122.3584 | 138.8853 | 1.977 | -2.306
57235 | 111.0305 | 79.657 | 136.6492 | -0.331 | -1.647
57245 | 103.1846 | 67.4405 | 123.2692 | 0.331 | -0.989
57255 | 139.2863 | -23.4514 | 141.2468 | -1.318 | -1.647
57265 | 175.8891 | -97.071 | 200.8974 | -1.318 | -1.647
57275 | 87.4593 | -83.2382 | 120.7383 | -0.33 | 0.329
57285 | 36.9603 | -125.3092 | 130.6463 | -1.318 | 0
57295 | -3.4124 | -243.0342 | 243.0581 | -2.635 | 0.33
57305 | 7.02 | -292.0511 | 292.1354 | -1.977 | -0.33
57315 | -17.9704 | -221.8162 | 222.5429 | -0.329 | 0.33
57325 | -99.232 | -91.671 | 135.0947 | 0.988 | 1.318
57335 | -254.7405 | -62.228 | 262.2309 | 0 | 2.964
57345 | -348.6315 | -56.768 | 353.2231 | 0 | 2.636
57355 | -443.5395 | -127.0098 | 461.3662 | -1.318 | 3.294
57365 | -420.4702 | -28.9289 | 421.4642 | 1.318 | 1.648
57375 | -299.933 | 41.5842 | 302.802 | 0.989 | 0
57385 | -237.4561 | 39.0971 | 240.6533 | 0.329 | 0.33
57395 | -400.3545 | 206.9591 | 450.6837 | 3.295 | 3.623
57405 | -515.4705 | 344.9908 | 620.2649 | 3.293 | 3.295
57415 | -426.2972 | 276.2854 | 507.9989 | 0.66 | 0.659
57425 | -177.7815 | 156.9836 | 237.1711 | -0.329 | -2.307
57435 | -60.8241 | 161.1044 | 172.204 | 0.988 | -1.317
57445 | -156.2243 | 200.5387 | 254.2082 | 1.318 | 1.317
57455 | -100.5241 | 188.2417 | 213.4011 | 0.658 | -0.988
57465 | 4.3352 | 213.4148 | 213.4588 | 1.318 | -1.647
57475 | 74.2305 | 46.597 | 87.6439 | -1.976 | -1.647
57485 | 81.9917 | -51.3017 | 96.7187 | -1.318 | -0.988
57495 | 162.5804 | -119.386 | 201.7063 | -1.648 | -2.307
57505 | 289.9859 | -54.7566 | 295.1104 | 0.329 | -3.294
57515 | 382.2268 | -75.8512 | 389.6803 | -0.987 | -3.295
57525 | 368.1243 | -13.4681 | 368.3706 | 0.658 | -1.976
57535 | 220.4306 | 22.8537 | 221.6122 | 0.329 | 0.329
57545 | 134.9657 | 18.7978 | 136.2684 | 0 | 0
57555 | 54.9868 | -101.4019 | 115.3511 | -1.976 | 0.659
57565 | 17.7008 | -118.1191 | 119.438 | -0.659 | 0.329
57575 | -21.6523 | -190.0612 | 191.2905 | -1.976 | 0.659
57585 | -33.0594 | -388.0941 | 389.4996 | -4.283 | 0.33
57595 | 57.4793 | -554.9983 | 557.9668 | -4.613 | -1.318
57605 | 89.0415 | -433.9307 | 442.9721 | -0.658 | -0.659
57615 | -132.0497 | -386.2466 | 408.1955 | -1.648 | 3.295
57625 | -210.6851 | -362.8744 | 419.6023 | -1.318 | 1.647
57635 | -410.6093 | -347.5576 | 537.9556 | -1.317 | 4.612
57645 | -400.2615 | -322.3092 | 513.8994 | -0.989 | 1.647
57655 | -212.9624 | -209.3331 | 298.619 | 0.659 | -0.988
57665 | -256.7968 | -163.0449 | 304.1846 | 0 | 1.976
57675 | -360.9538 | -181.8848 | 404.1902 | -0.659 | 2.636
57685 | -409.0942 | -43.1289 | 411.3614 | 1.977 | 2.306
57695 | -399.659 | 110.9572 | 414.7757 | 2.635 | 1.648
57705 | -469.713 | 57.7869 | 473.2543 | 0 | 2.965
57715 | -436.2493 | -16.0419 | 436.5442 | -0.329 | 1.317
57725 | -247.5357 | -35.4372 | 250.0594 | 0 | -1.317
57735 | -14.856 | 74.3602 | 75.8297 | 1.976 | -2.965
57745 | 83.5865 | 124.5473 | 149.9958 | 1.319 | -1.977
57755 | 2.5544 | 205.3882 | 205.4041 | 2.305 | 0.329
57765 | -176.5163 | 155.7117 | 235.3808 | 0.33 | 2.306
57775 | -124.7549 | 223.619 | 256.0649 | 2.307 | -0.658
57785 | -19.8835 | 235.9765 | 236.8128 | 1.317 | -1.318
57795 | 7.3021 | 234.0835 | 234.1973 | 1.318 | -0.659
57805 | -20.2855 | 162.1413 | 163.4053 | 0 | 0
57815 | -78.0463 | 88.6657 | 118.1221 | -0.329 | 0.659
57825 | -174.5494 | 24.843 | 176.3085 | -0.659 | 1.647
57835 | -223.365 | -36.9647 | 226.403 | -0.989 | 1.318
57845 | -173.1973 | -137.3918 | 221.0743 | -1.976 | 0
57855 | -93.8196 | -173.6113 | 197.3398 | -1.319 | -0.659
57865 | -23.0309 | -249.43 | 250.491 | -2.305 | -0.988
57875 | 4.2594 | -293.4875 | 293.5184 | -1.977 | -0.659
57885 | -134.1409 | -148.1027 | 199.8204 | 0.989 | 1.977
57895 | -281.5358 | -187.9968 | 338.5339 | -1.648 | 2.635
57905 | -201.5845 | -170.827 | 264.2313 | -0.33 | -0.329
57915 | -124.3371 | 10.5414 | 124.7832 | 2.307 | -0.329
57925 | -200.254 | 107.5509 | 227.3078 | 1.647 | 1.647
57935 | -382.9431 | 138.7218 | 407.2949 | 1.317 | 3.624
57945 | -493.9664 | -127.4786 | 510.1505 | -3.624 | 3.294
57955 | -425.6496 | -125.6092 | 443.7964 | 0 | 0.988
57965 | -271.6582 | 36.6356 | 274.1174 | 1.977 | -0.659
57975 | -284.7762 | 109.2818 | 305.0246 | 1.318 | 1.318
57985 | -413.4697 | -9.3647 | 413.5757 | -1.318 | 2.966
57995 | -486.8172 | -105.0047 | 498.013 | -1.317 | 2.635
58005 | -259.2 | 130.3026 | 290.1093 | 3.624 | -1.977
58015 | -114.8986 | 363.2014 | 380.9422 | 4.283 | -1.318
58025 | -3.0217 | 333.8275 | 333.8412 | 1.318 | -1.977
58035 | 97.4948 | 215.0504 | 236.1184 | 0 | -2.306
58045 | 206.7771 | 122.2689 | 240.2217 | -0.331 | -2.964
58055 | 249.9206 | -8.8791 | 250.0783 | -1.646 | -2.307
58065 | 392.7694 | 31.8695 | 394.0602 | 0.659 | -4.283
58075 | 569.0057 | 138.0334 | 585.5089 | 1.647 | -5.271
58085 | 483.0956 | 264.8685 | 550.9416 | 2.635 | -1.647
58095 | 268.9396 | 160.181 | 313.0279 | -0.658 | 0.659
58105 | 187.4709 | 25.2882 | 189.1688 | -1.318 | -0.33
58115 | -94.5722 | 20.5172 | 96.7722 | 0 | 3.954
58125 | -7.3826 | 88.5567 | 88.8639 | 0.988 | -1.318
58135 | 160.8164 | 155.0829 | 223.4113 | 1.317 | -2.306
58145 | 164.5355 | 216.4798 | 271.9108 | 1.648 | -0.659
58155 | 167.7271 | 162.6241 | 233.6214 | 0 | -0.988
58165 | 24.8327 | 210.8222 | 212.2797 | 1.647 | 1.647
58175 | -165.9991 | -102.5931 | 195.1436 | -4.612 | 2.965
58185 | -293.6252 | -227.3685 | 371.3653 | -2.307 | 2.965
58195 | -375.4815 | -369.0363 | 526.4733 | -3.953 | 2.965
58205 | -242.1096 | -408.7738 | 475.0927 | -2.635 | -0.33
58215 | 95.7516 | -253.8571 | 271.315 | 0.329 | -4.282
58225 | 160.9703 | -216.5042 | 269.7879 | -0.988 | -1.318
58235 | 12.845 | -198.4585 | 198.8737 | -0.659 | 1.318
58245 | -343.5975 | -222.0544 | 409.1056 | -1.317 | 5.6
58255 | -408.1089 | -341.4683 | 532.1217 | -2.966 | 2.306
58265 | -200.7471 | -451.9178 | 494.4988 | -3.295 | -1.318
58275 | -69.7529 | -389.9186 | 396.1085 | -0.987 | -0.988
58285 | -79.771 | -180.1033 | 196.9787 | 1.647 | 0.33
58295 | 113.7891 | -301.8192 | 322.5566 | -2.965 | -3.295
58305 | 82.888 | -352.4588 | 362.074 | -1.648 | 0
58315 | -48.9982 | -342.9165 | 346.3994 | -1.318 | 1.318
58325 | -229.5412 | -184.8852 | 294.74 | 1.318 | 2.966
58335 | -200.8667 | -159.5544 | 256.5249 | -0.329 | 0.329
58345 | -41.5221 | -88.2154 | 97.4989 | 0.988 | -1.648
58355 | 106.6927 | 90.01 | 139.5892 | 2.965 | -2.305
58365 | 143.9243 | 67.4891 | 158.9622 | 0.329 | -1.319
58375 | 121.3145 | -163.1683 | 203.3251 | -2.964 | -0.658
58385 | 11.7048 | -194.4401 | 194.7921 | -0.66 | 0.988
58395 | 9.1657 | 200.6753 | 200.8845 | 5.93 | -0.33
58405 | -32.5864 | 390.7519 | 392.1083 | 3.955 | 0.659
58415 | 44.0252 | 461.41 | 463.5055 | 3.623 | -1.317
58425 | 228.0325 | 439.7265 | 495.3365 | 2.307 | -3.295
58435 | 128.3782 | 617.5384 | 630.7413 | 5.6 | 0.659
58445 | -69.0892 | 734.9239 | 738.1642 | 4.941 | 2.306
58455 | -139.6549 | 594.1313 | 610.3241 | 1.319 | 1.318
58465 | -56.3828 | 425.8106 | 429.5273 | 0.329 | -0.659
58475 | 182.1436 | 327.13 | 374.4199 | 0.329 | -3.624
58485 | 46.5085 | 309.5348 | 313.0093 | 0.989 | 1.647
58495 | -93.7358 | 131.9766 | 161.8772 | -1.977 | 1.648
58505 | -149.0346 | -164.2283 | 221.7707 | -4.613 | 1.317
58515 | -66.4047 | -237.9257 | 247.0187 | -2.305 | -0.659
58525 | 0.37028 | -187.4095 | 187.4099 | -0.988 | -0.658
58535 | -40.7698 | -254.2215 | 257.4699 | -2.637 | 0.658
58545 | -40.8894 | -303.8962 | 306.6347 | -2.305 | 0
58555 | -69.9516 | -239.2839 | 249.299 | -0.659 | 0.659
58565 | -96.2235 | -305.5551 | 320.3481 | -2.636 | 0.66
58575 | -73.6045 | -259.8177 | 270.0423 | -0.659 | 0
58585 | -34.9758 | -327.9025 | 329.7626 | -2.636 | -0.33
58595 | -298.1571 | -378.6712 | 481.9642 | -2.306 | 4.612
58605 | -646.7268 | -445.75 | 785.4608 | -2.964 | 6.919
58615 | -823.4905 | -442.2061 | 934.71 | -1.977 | 5.93
58625 | -661.4861 | -261.8419 | 711.4247 | 0.988 | 1.318
58635 | -627.8717 | -184.9378 | 654.5417 | 0 | 2.964
58645 | -605.5391 | -0.69779 | 605.5395 | 2.636 | 2.306
58655 | -435.239 | 297.3722 | 527.1273 | 5.27 | -0.329
58665 | -232.2328 | 643.5389 | 684.1596 | 7.578 | -1.647
58675 | -156.975 | 790.987 | 806.4128 | 5.931 | -0.659
58685 | -61.7306 | 666.6788 | 669.5306 | 2.306 | -1.647
58695 | 130.1301 | 497.8793 | 514.6044 | 0.987 | -3.624
58705 | 312.1536 | 420.2553 | 523.502 | 1.319 | -4.283
58715 | 552.1497 | 385.2218 | 673.2497 | 1.318 | -6.259
58725 | 674.0477 | 308.332 | 741.2213 | 0.329 | -5.271
58735 | 693.5498 | 290.7956 | 752.0462 | 0.988 | -4.284
58745 | 790.7667 | 269.678 | 835.4868 | 0.659 | -5.601
58755 | 804.1269 | 98.0955 | 810.0882 | -1.976 | -4.282
58765 | 733.5154 | 61.2209 | 736.0658 | -0.33 | -2.965
58775 | 614.4702 | -58.3083 | 617.2305 | -2.307 | -1.647
58785 | 481.6447 | -159.9213 | 507.5001 | -2.305 | -0.66
58795 | 262.4948 | -359.5509 | 445.1745 | -4.612 | 1.648
58805 | 279.5268 | -437.2026 | 518.9233 | -3.295 | -1.318
58815 | 321.4654 | -266.3519 | 417.4726 | 0.329 | -1.318
58825 | 299.8684 | -233.3119 | 379.9414 | -1.318 | -0.659
58835 | 105.3084 | -377.7213 | 392.1265 | -3.624 | 2.307
58845 | -102.4106 | -317.9563 | 334.0421 | -0.658 | 3.294
58855 | -258.7048 | -289.9645 | 388.597 | -1.319 | 3.624
58865 | -365.3852 | -443.3297 | 574.4977 | -3.953 | 3.624
58875 | -326.7305 | -298.0625 | 442.2602 | 0.66 | 1.647
58885 | -371.5305 | -257.3595 | 451.9611 | -0.989 | 2.965
58895 | -464.7261 | -241.6106 | 523.7805 | -0.659 | 3.625
58905 | -650.2358 | -226.3291 | 688.4995 | -0.659 | 5.6
58915 | -773.7658 | -63.9512 | 776.404 | 1.976 | 5.272
58925 | -797.034 | 178.8461 | 816.8532 | 3.955 | 4.282
58935 | -642.4724 | 193.2945 | 670.9199 | 1.317 | 1.318
58945 | -550.1266 | 102.4378 | 559.5827 | 0 | 1.647
58955 | -355.9993 | 142.1581 | 383.3333 | 1.647 | -0.988
58965 | -269.5461 | 229.5927 | 354.0733 | 2.306 | 0
58975 | -95.6676 | 233.519 | 252.3558 | 1.318 | -2.306
58985 | 117.5745 | 268.023 | 292.6775 | 1.977 | -3.624
58995 | 226.3731 | 206.8962 | 306.677 | 0.329 | -2.966
59005 | 332.4869 | 98.2395 | 346.6966 | -0.658 | -3.624
59015 | 321.1893 | 103.908 | 337.5787 | 0.658 | -1.976
59025 | 250.0163 | -11.4411 | 250.278 | -1.647 | -0.988
59035 | 304.8315 | -70.9158 | 312.9717 | -0.988 | -2.636
59045 | 344.7214 | -118.0901 | 364.3873 | -1.318 | -2.306
59055 | 195.7327 | -174.6611 | 262.3314 | -1.648 | 0.658
59065 | 79.6733 | -120.4013 | 144.3756 | 0 | 0.66
59075 | -2.907 | -131.419 | 131.4511 | -0.987 | 0.988
59085 | -38.987 | -135.4142 | 140.9148 | -0.66 | 0.659
59095 | -79.4423 | -211.6999 | 226.1149 | -1.977 | 0.988
59105 | -169.4618 | -217.1702 | 275.4636 | -0.987 | 1.977
59115 | -218.8286 | -191.9747 | 291.1017 | -0.66 | 1.647
59125 | -171.7378 | -158.8915 | 233.9666 | -0.329 | 0.329
59135 | -154.1578 | -214.9625 | 264.525 | -1.648 | 0.66
59145 | -248.8064 | -187.9894 | 311.8407 | -0.329 | 2.306
59155 | -344.9905 | -118.6964 | 364.8387 | 0.329 | 2.635
59165 | -446.6272 | -53.7704 | 449.8523 | 0.66 | 3.295
59175 | -482.529 | -69.0526 | 487.4449 | -0.329 | 2.635
59185 | -446.242 | -125.9912 | 463.6871 | -0.989 | 1.647
59195 | -326.1205 | -164.5068 | 365.263 | -0.988 | 0
59205 | -242.3603 | -110.3077 | 266.2823 | 0.329 | 0
59215 | -176.5374 | -6.9846 | 176.6755 | 1.317 | -0.329
59225 | -170.1809 | 45.0241 | 176.0361 | 0.989 | 0.329
59235 | -94.6832 | -2.9006 | 94.7276 | -0.329 | -0.987
59245 | -11.8194 | 15.6177 | 19.586 | 0.659 | -1.319
59255 | 100.7364 | -34.9368 | 106.6227 | -0.659 | -2.305
59265 | 126.5521 | -137.5415 | 186.904 | -1.647 | -1.319
59275 | 117.2609 | -92.9092 | 149.607 | 0.329 | -0.987
59285 | 212.3845 | -160.2828 | 266.0785 | -1.648 | -2.637
59295 | 274.4582 | -169.6398 | 322.653 | -0.658 | -2.306
59305 | 350.4507 | -67.5267 | 356.8971 | 0.988 | -2.965
59315 | 392.1321 | 123.8465 | 411.2244 | 2.965 | -2.635
59325 | 324.6521 | 144.1011 | 355.1959 | 0.988 | -0.989
59335 | 293.1949 | 137.1006 | 323.6662 | 0.989 | -1.317
59345 | 247.1214 | 84.2715 | 261.0951 | 0 | -0.66
59355 | 252.8839 | -50.2427 | 257.8267 | -1.647 | -1.317
59365 | 189.3567 | -146.2479 | 239.258 | -1.648 | 0
59375 | 79.1866 | -165.067 | 183.0782 | -0.988 | 0.988
59385 | 61.377 | -231.1547 | 239.1644 | -1.976 | 0
59395 | 60.4215 | -268.1775 | 274.8999 | -1.648 | 0
59405 | 93.8327 | -309.3108 | 323.2301 | -1.976 | -0.659
59415 | 99.9764 | -381.8484 | 394.7195 | -2.637 | -0.329
59425 | -74.523 | -399.0751 | 405.9737 | -1.976 | 2.635
59435 | -135.6371 | -349.5683 | 374.9605 | -0.988 | 1.319
59445 | -61.3999 | -430.8304 | 435.1836 | -2.966 | -0.33
59455 | -83.0251 | -487.6378 | 494.6552 | -2.635 | 0.988
59465 | -97.1386 | -385.3321 | 397.3874 | -0.329 | 0.659
59475 | -159.9607 | -304.2779 | 343.7622 | -0.33 | 1.647
59485 | -173.4373 | -261.5391 | 313.8204 | -0.33 | 0.989
59495 | -176.3544 | -312.2198 | 358.5834 | -1.647 | 0.988
59505 | -182.8172 | -259.9285 | 317.7813 | 0 | 0.988
59515 | -132.2308 | -323.5481 | 349.5259 | -1.977 | 0
59525 | -93.4393 | -405.1796 | 415.8141 | -2.306 | 0
59535 | -53.4606 | -340.7696 | 344.9376 | -0.329 | -0.329
59545 | -83.0859 | -205.8586 | 221.9933 | 0.988 | 0.659
59555 | -188.1261 | -56.7087 | 196.4874 | 1.977 | 1.976
59565 | -130.0047 | 25.4871 | 132.4795 | 1.647 | -0.329
59575 | -12.3005 | 114.6558 | 115.3137 | 2.307 | -1.318
59585 | -31.3112 | 241.4631 | 243.4848 | 3.294 | 0.329
59595 | -60.651 | 221.0655 | 229.2346 | 1.318 | 0.331
59605 | 2.98 | 99.2224 | 99.2671 | -0.329 | -0.989
59615 | -1.1953 | 114.6004 | 114.6067 | 1.318 | 0
59625 | 4.0858 | -5.655 | 6.9766 | -1.318 | -0.33
59635 | 110.0183 | -11.5373 | 110.6216 | 0.329 | -1.976
59645 | 327.6336 | -108.4723 | 345.1232 | -1.648 | -4.283
59655 | 466.569 | -96.22 | 476.3874 | 0 | -3.954
59665 | 340.6061 | -89.3321 | 352.1261 | -0.329 | -0.329
59675 | 236.384 | -35.8321 | 239.0844 | 0.659 | -0.33
59685 | 166.5344 | 6.7915 | 166.6728 | 0.659 | 0
59695 | 84.1864 | 89.2723 | 122.7065 | 1.648 | 0.659
59705 | -69.0114 | -21.0889 | 72.1617 | -1.318 | 2.307
59715 | -142.6932 | -291.4853 | 324.5382 | -4.283 | 1.647
59725 | -202.2353 | -367.2253 | 419.2297 | -2.307 | 1.977
59735 | -268.9143 | -373.93 | 460.585 | -1.977 | 2.306
59745 | -357.6843 | -270.7095 | 448.5774 | 0 | 2.964
59755 | -406.2391 | -194.0114 | 450.1896 | 0 | 2.636
59765 | -343.0193 | -134.3904 | 368.406 | 0.33 | 0.988
59775 | -160.8265 | -36.9391 | 165.0141 | 1.318 | -1.317
59785 | -167.5167 | 130.2335 | 212.1853 | 2.965 | 0.988
59795 | -296.431 | 251.7854 | 388.9309 | 2.965 | 2.636
59805 | -388.0512 | 330.0577 | 509.4329 | 2.965 | 2.635
59815 | -232.4251 | 406.1614 | 467.9621 | 3.295 | -0.988
59825 | 11.4648 | 369.635 | 369.8127 | 1.647 | -2.965
59835 | 154.6103 | 377.2467 | 407.7001 | 2.306 | -2.636
59845 | 163.1871 | 380.0549 | 413.6082 | 1.977 | -1.317
59855 | 201.9437 | 152.5095 | 253.0621 | -1.977 | -1.977
59865 | 242.532 | 111.4456 | 266.9118 | 0.33 | -1.976
59875 | 157.5879 | 2.0066 | 157.6006 | -1.648 | 0
59885 | 110.1664 | -73.1469 | 132.2388 | -1.318 | -0.331
59895 | 53.0567 | -135.5613 | 145.5743 | -1.647 | 0.331
59905 | 69.6796 | -202.2653 | 213.9311 | -1.977 | -0.66
59915 | 206.487 | -40.3842 | 210.399 | 1.647 | -2.635
59925 | 98.2168 | 130.1298 | 163.0347 | 2.307 | 0.988
59935 | -6.7644 | 252.5463 | 252.6368 | 2.636 | 0.988
59945 | -120.9683 | 390.7145 | 409.0124 | 3.624 | 1.977
59955 | -106.964 | 299.3614 | 317.8971 | 0.329 | 0.329
59965 | 12.4199 | 272.9414 | 273.2238 | 1.318 | -1.318
59975 | 57.7886 | 336.3022 | 341.2311 | 2.306 | -0.658
59985 | -59.0688 | 310.3066 | 315.8787 | 0.989 | 1.647
59995 | -248.4208 | 397.6197 | 468.8436 | 2.964 | 3.295
60005 | -647.6795 | 285.4214 | 707.7811 | -0.329 | 7.906
60015 | -674.937 | -201.7237 | 704.4376 | -6.919 | 3.295
60025 | -437.4952 | -562.362 | 712.4977 | -6.918 | -0.329
60035 | -372.2941 | -857.9613 | 935.2543 | -8.237 | 1.317
60045 | -266.9524 | -879.0766 | 918.7161 | -4.942 | -0.329
60055 | -203.5149 | -896.8964 | 919.6964 | -5.27 | 0
60065 | -247.3173 | -706.8996 | 748.9145 | -1.318 | 1.318
60075 | -189.5375 | -391.6687 | 435.1193 | 1.647 | -0.329
60085 | -344.9522 | -202.682 | 400.09 | 1.318 | 3.293
60095 | -461.3082 | 38.7058 | 462.9291 | 3.623 | 2.966
60105 | -563.4268 | 217.0863 | 603.8015 | 3.624 | 3.624
60115 | -542.8871 | 351.5557 | 646.7749 | 3.955 | 1.977
60125 | -326.8814 | 430.5864 | 540.6071 | 3.623 | -1.319
60135 | -130.343 | 565.3585 | 580.1892 | 4.942 | -1.976
60145 | -105.0778 | 790.7962 | 797.7468 | 6.919 | -0.33
60155 | 50.7491 | 788.1412 | 789.7734 | 3.953 | -2.965
60165 | 86.7564 | 845.0181 | 849.4599 | 5.271 | -1.317
60175 | 56.1067 | 971.6558 | 973.2743 | 6.26 | -0.66
60185 | 40.7961 | 1013.1119 | 1013.933 | 5.271 | -0.658
60195 | -38.5405 | 828.9046 | 829.8001 | 1.647 | 0.658
60205 | -39.6246 | 673.6681 | 674.8324 | 1.318 | -0.329
60215 | -26.0712 | 704.4662 | 704.9484 | 3.294 | -0.329
60225 | 19.7269 | 747.1664 | 747.4267 | 3.295 | -0.988
60235 | -59.3955 | 694.9926 | 697.526 | 1.977 | 0.988
60245 | -127.8653 | 518.0004 | 533.5484 | -0.33 | 0.989
60255 | -357.9179 | 390.2041 | 529.4945 | -0.329 | 4.282
60265 | -535.2851 | 160.7829 | 558.9108 | -2.965 | 4.283
60275 | -548.5168 | 45.2606 | 550.3809 | -1.977 | 2.636
60285 | -568.5319 | -0.15628 | 568.5319 | -1.647 | 2.964
60295 | -423.8457 | 1.5162 | 423.8484 | -0.988 | 0
60305 | -234.2822 | -116.4253 | 261.6162 | -2.966 | -1.318
60315 | -93.6429 | -218.6635 | 237.8712 | -2.964 | -1.646
60325 | -42.5844 | -94.4973 | 103.6493 | 0.329 | -0.989
60335 | -147.7494 | -12.7545 | 148.2989 | 0 | 1.318
60345 | -267.7591 | 40.9024 | 270.8652 | 0.329 | 1.977
60355 | -264.5819 | 36.7915 | 267.1276 | -0.329 | 0.658
60365 | 0.97135 | 6.7638 | 6.8332 | -0.66 | -3.624
60375 | 185.6385 | 23.8346 | 187.1623 | 0 | -3.294
60385 | 253.6111 | 1.9274 | 253.6184 | -0.658 | -2.636
60395 | 182.6843 | 55.7316 | 190.9962 | 0.658 | -0.658
60405 | 33.474 | 102.2541 | 107.5937 | 0.66 | 0.988
60415 | -141.9882 | 166.2983 | 218.6681 | 1.317 | 2.306
60425 | -335.6848 | 251.772 | 419.6111 | 1.977 | 3.624
60435 | -488.4435 | 177.643 | 519.7442 | -0.329 | 3.954
60445 | -417.7189 | 148.7885 | 443.4266 | 0.329 | 0.988
60455 | -179.5797 | 67.2343 | 191.7533 | -0.988 | -1.977
60465 | -14.8745 | -35.977 | 38.9307 | -1.647 | -1.976
60475 | -34.6259 | 67.3004 | 75.6855 | 1.318 | 0
60485 | -120.2301 | 197.514 | 231.2294 | 1.976 | 0.987
60495 | -252.1425 | 373.4732 | 450.6196 | 3.624 | 2.307
60505 | -478.347 | 326.782 | 579.312 | 0.659 | 4.612
60515 | -257.2447 | 154.8869 | 300.2745 | -1.318 | -1.977
60525 | 2.0409 | 135.0977 | 135.1131 | 0.33 | -2.964
60535 | 22.4812 | -67.4732 | 71.1199 | -3.295 | -0.66
60545 | -82.6315 | -407.5617 | 415.8539 | -6.26 | 0.989
60555 | 37.9372 | -608.2097 | 609.3917 | -5.601 | -2.307
60565 | 209.7295 | -789.322 | 816.7103 | -6.588 | -3.293
60575 | 284.9706 | -678.8579 | 736.2447 | -2.306 | -2.637
60585 | 175.8411 | -447.9319 | 481.21 | 0 | 0
60595 | 263.8097 | -302.9783 | 401.7355 | 0 | -2.964
60605 | 378.2839 | -12.1196 | 378.478 | 3.624 | -3.295
60615 | 259.8044 | 262.2738 | 369.1691 | 4.612 | 0
60625 | -52.3527 | 460.347 | 463.3143 | 4.942 | 3.624
60635 | -387.0523 | 518.8876 | 647.3437 | 3.624 | 5.601
60645 | -321.9601 | 420.9647 | 529.9713 | 1.317 | 0.658
60655 | -65.2052 | 526.1948 | 530.2194 | 4.284 | -2.305
60665 | -87.2529 | 616.3196 | 622.4652 | 3.953 | 0.988
60675 | 11.1215 | 537.3189 | 537.4339 | 1.647 | -1.647
60685 | 105.4346 | 398.2069 | 411.9286 | 0.33 | -1.647
60695 | 122.292 | 368.0527 | 387.8378 | 1.318 | -0.989
60705 | -24.1538 | 364.9996 | 365.7979 | 1.317 | 1.647
60715 | -98.1749 | 227.8066 | 248.0608 | -0.988 | 0.989
60725 | 60.5299 | 62.5086 | 87.0126 | -1.977 | -2.307
60735 | 208.2312 | -85.3528 | 225.0452 | -2.636 | -2.635
60745 | 47.5332 | 5.6291 | 47.8653 | 0.66 | 1.647
60755 | -130.2525 | -103.1173 | 166.1291 | -2.636 | 2.306
60765 | -313.7089 | -350.4502 | 470.3494 | -4.942 | 3.624
60775 | -327.1397 | -334.2523 | 467.7018 | -1.647 | 1.648
60785 | -281.4834 | -218.8806 | 356.5692 | -0.329 | 0.987
60795 | -219.3636 | -130.6618 | 255.329 | 0 | 0.331
60805 | -353.3587 | 92.0704 | 365.1566 | 2.964 | 3.293
60815 | -374.3607 | 142.5488 | 400.5822 | 0.989 | 1.648
60825 | -253.5478 | 266.295 | 367.6949 | 2.965 | -0.33
60835 | -301.032 | 371.6816 | 478.2964 | 2.965 | 1.977
60845 | -283.0517 | 170.5042 | 330.439 | -1.647 | 0.659
60855 | -178.8574 | -12.857 | 179.3189 | -1.977 | -0.659
60865 | -124.0975 | 151.2313 | 195.63 | 2.635 | -0.329
60875 | -76.3009 | 106.0865 | 130.6758 | -0.658 | -0.659
60885 | -2.1115 | 208.0201 | 208.0308 | 2.306 | -1.318
60895 | -62.4504 | 307.9138 | 314.183 | 2.306 | 0.659
60905 | 74.7686 | 231.7054 | 243.4702 | 0 | -2.635
60915 | 276.6245 | 107.4465 | 296.759 | -0.988 | -3.954
60925 | 201.4198 | 142.9452 | 246.9884 | 0.988 | -0.329
60935 | 257.7682 | 205.6896 | 329.7766 | 1.318 | -2.636
60945 | 272.2932 | 166.415 | 319.1199 | 0 | -1.648
60955 | 234.2043 | 186.4567 | 299.3622 | 0.988 | -0.987
60965 | 384.1759 | 116.0875 | 401.3321 | -0.659 | -3.954
60975 | 474.1861 | 150.6026 | 497.5275 | 0.989 | -3.294
60985 | 408.1982 | 75.9423 | 415.2023 | -0.989 | -1.319
60995 | 259.9716 | -51.5931 | 265.0417 | -1.977 | 0.33
61005 | 142.0237 | -99.795 | 173.5793 | -1.317 | 0.659
61015 | 109.0399 | -201.8532 | 229.4219 | -2.636 | 0
61025 | 190.3495 | -265.6377 | 326.797 | -2.306 | -1.647
61035 | 272.9048 | -228.7759 | 356.1115 | -0.989 | -1.977
61045 | 150.7962 | -200.0583 | 250.5251 | -0.988 | 0.988
61055 | -88.2587 | -267.2088 | 281.4074 | -2.306 | 3.295
61065 | -176.9739 | -172.215 | 246.9368 | 0.33 | 1.976
61075 | -257.6029 | -222.5902 | 340.4492 | -1.977 | 2.637
61085 | -151.2735 | -361.5636 | 391.9335 | -3.295 | -0.331
61095 | -139.0602 | -362.9072 | 388.6379 | -1.647 | 0.989
61105 | -117.1923 | -368.534 | 386.7187 | -1.977 | 0.329
61115 | -116.6523 | -37.9799 | 122.6794 | 3.954 | 0.659
61125 | -238.1314 | 204.0173 | 313.5755 | 3.624 | 2.636
61135 | -507.4881 | 475.9188 | 695.732 | 5.93 | 5.601
61145 | -396.9748 | 677.0575 | 784.854 | 5.93 | 0.329
61155 | 29.4229 | 503.5618 | 504.4206 | 0.659 | -4.942
61165 | 272.0515 | 474.0423 | 546.5603 | 2.635 | -3.953
61175 | 270.1034 | 113.2579 | 292.8877 | -3.953 | -1.648
61185 | 64.87 | -20.2513 | 67.9575 | -1.318 | 1.648
61195 | -62.5058 | 50.7679 | 80.5255 | 0.659 | 1.318
61205 | -32.0876 | 584.7219 | 585.6017 | 8.895 | -0.329
61215 | 116.8681 | 1049.3242 | 1055.8122 | 9.884 | -2.306
61225 | 301.3841 | 1454.3853 | 1485.2842 | 11.86 | -3.624
61235 | 369.6448 | 1723.5975 | 1762.7892 | 11.531 | -2.637
61245 | 21.1525 | 1429.7084 | 1429.8649 | 3.294 | 3.954
61255 | -329.0765 | 1270.7939 | 1312.7103 | 4.613 | 5.271
61265 | -546.4399 | 1202.9889 | 1321.2793 | 4.283 | 5.272
61275 | -591.2504 | 474.988 | 758.4132 | -7.577 | 3.624
61285 | -289.4629 | -377.6225 | 475.802 | -12.52 | -1.977
61295 | 187.8513 | -921.3128 | 940.2687 | -12.189 | -6.26
61305 | 857.0482 | -983.055 | 1304.1966 | -7.248 | -12.19
61315 | 1638.223 | -1431.5007 | 2175.5387 | -14.496 | -17.46
61325 | 1744.259 | -1404.4995 | 2239.4326 | -7.248 | -9.884
61335 | 1566.9805 | -1162.7254 | 1951.2453 | -4.283 | -6.589
61345 | 1360.0773 | -585.9336 | 1480.9215 | 3.294 | -4.613
61355 | 246.1779 | -274.4632 | 368.6918 | 1.647 | 12.52
61365 | -617.5131 | -213.9625 | 653.5307 | 0 | 12.848
61375 | -881.5266 | 314.7192 | 936.0221 | 8.566 | 8.566
61385 | -780.9803 | 1200.8885 | 1432.5025 | 16.473 | 4.283
61395 | -1102.9368 | 1789.9781 | 2102.4964 | 15.813 | 10.872
61405 | -1366.7286 | 1625.8815 | 2124.0146 | 6.59 | 10.213
61415 | -1632.9354 | 858.6737 | 1844.9386 | -3.953 | 11.86
61425 | -1594.0992 | 520.9552 | 1677.0648 | -0.66 | 7.577
61435 | -1784.1545 | 512.8425 | 1856.3983 | 1.647 | 11.532
61445 | -1399.989 | 388.4417 | 1452.8785 | -0.658 | 1.646
61455 | -579.0128 | 529.079 | 784.3343 | 3.624 | -6.918
61465 | 98.1935 | 621.6214 | 629.3292 | 2.964 | -8.895
61475 | 641.33 | 644.262 | 909.0532 | 2.637 | -10.872
61485 | 881.4292 | 716.4718 | 1135.8913 | 3.624 | -8.565
61495 | 1034.7916 | 622.0129 | 1207.3499 | 0.987 | -8.567
61505 | 1051.746 | 424.3672 | 1134.1328 | -0.987 | -6.588
61515 | 880.2935 | 347.2637 | 946.3132 | 0 | -3.295
61525 | 615.8591 | -15.1509 | 616.0454 | -5.601 | -0.659
61535 | 583.4917 | -379.9045 | 696.2686 | -6.919 | -2.965
61545 | 677.1887 | -484.5419 | 832.6857 | -4.612 | -4.282
61555 | 979.6438 | -713.9016 | 1212.1705 | -7.578 | -8.237
61565 | 749.6652 | -544.4605 | 926.5178 | -1.317 | -0.33
61575 | 108.2401 | -178.7457 | 208.9639 | 2.306 | 6.919
61585 | -493.0051 | 115.7006 | 506.3997 | 3.294 | 9.554
61595 | -480.7244 | 239.3684 | 537.0225 | 2.306 | 2.635
61605 | -129.8738 | 673.9494 | 686.349 | 8.567 | -2.306
61615 | 296.1139 | 1035.9104 | 1077.4014 | 8.894 | -5.6
61625 | -1.7091 | 958.6572 | 958.6588 | 3.624 | 4.282
61635 | -20.6171 | 570.0018 | 570.3745 | -1.647 | -0.329
61645 | 15.5222 | 592.0641 | 592.2675 | 3.294 | 0
61655 | -130.0028 | 1095.872 | 1103.5561 | 10.543 | 2.635
61665 | -440.7033 | 860.1062 | 966.4378 | 0 | 5.931
61675 | -588.6153 | 854.0282 | 1037.2233 | 4.283 | 4.612
61685 | -247.681 | 808.63 | 845.7117 | 2.306 | -2.635
61695 | -170.4404 | 316.8503 | 359.7834 | -5.271 | 0.658
61705 | 73.9087 | -460.831 | 466.7202 | -12.19 | -3.624
61715 | 82.5404 | -1004.0563 | 1007.4433 | -12.19 | -0.329
61725 | 166.1996 | -1137.9117 | 1149.985 | -8.565 | -2.306
61735 | -96.1154 | -813.9984 | 819.6533 | -1.648 | 3.624
61745 | -105.8144 | -929.0408 | 935.0473 | -7.577 | 0
61755 | -101.9682 | -922.7727 | 928.3895 | -4.613 | 0.659
61765 | 249.6673 | -1259.1406 | 1283.6544 | -10.871 | -5.601
61775 | 396.0084 | -1167.2914 | 1232.6361 | -4.283 | -3.295
61785 | 225.5403 | -858.0409 | 887.188 | -0.988 | 0.66
61795 | 151.2131 | -700.877 | 717.0035 | -1.648 | -0.33
61805 | 186.3282 | -509.5937 | 542.59 | 0.33 | -1.317
61815 | 275.7961 | 32.0159 | 277.6482 | 7.248 | -2.307
61825 | 263.8106 | 417.5621 | 493.9172 | 6.918 | -0.988
61835 | 225.0898 | 383.111 | 444.3416 | 2.306 | -0.659
61845 | 30.6656 | 278.1439 | 279.8293 | 1.318 | 2.306
61855 | -232.6586 | 153.4334 | 278.6967 | 0 | 4.283
61865 | -431.7074 | -423.0636 | 604.4453 | -8.566 | 4.613
61875 | -427.9739 | -493.9554 | 653.5699 | -2.306 | 2.306
61885 | -605.6829 | -233.5694 | 649.1583 | 1.648 | 5.6
61895 | -803.3098 | -112.4635 | 811.1441 | 0.658 | 6.259
61905 | -880.5768 | 363.1907 | 952.5351 | 7.907 | 5.272
61915 | -950.8305 | 293.0805 | 994.9748 | 0.329 | 5.601
61925 | -1014.5603 | 15.775 | 1014.6829 | -2.306 | 5.6
61935 | -1279.0901 | 34.8254 | 1279.5641 | 0.989 | 9.225
61945 | -1435.7091 | 396.1568 | 1489.3626 | 6.259 | 8.236
61955 | -1513.1399 | 514.1658 | 1598.111 | 3.624 | 7.907
61965 | -1290.2031 | 326.8251 | 1330.9541 | -0.329 | 2.965
61975 | -832.5574 | 13.6325 | 832.669 | -3.295 | -1.977
61985 | -308.6518 | -138.5003 | 338.302 | -2.306 | -5.6
61995 | 139.4408 | -180.2974 | 227.9274 | -1.647 | -7.248
62005 | -40.9751 | -380.9604 | 383.1576 | -4.612 | 0.988
62015 | -26.1077 | -255.634 | 256.9637 | 0.329 | -2.307
62025 | 472.0179 | 99.5471 | 482.4007 | 4.283 | -9.554
62035 | 725.4608 | 113.4527 | 734.2785 | 0.329 | -7.248
62045 | 709.0847 | 460.8082 | 845.6626 | 6.919 | -4.611
62055 | 449.8835 | 967.3111 | 1066.8111 | 10.543 | -0.33
62065 | 290.718 | 1219.8574 | 1254.0212 | 8.894 | -0.659
62075 | 234.7419 | 1218.9495 | 1241.3467 | 6.261 | -0.988
62085 | -99.7587 | 1123.3155 | 1127.7365 | 4.611 | 4.282
62095 | -301.7605 | 1189.7531 | 1227.4249 | 6.59 | 3.295
62105 | -449.2651 | 1193.1641 | 1274.943 | 5.27 | 3.954
62115 | -461.9233 | 903.3904 | 1014.6366 | 0.331 | 2.305
62125 | -405.2567 | 610.979 | 733.1633 | -0.989 | 1.319
62135 | -392.0816 | 335.0409 | 515.7329 | -2.635 | 1.647
62145 | -414.9736 | 50.9172 | 418.0857 | -4.284 | 1.977
62155 | -455.4789 | 6.0919 | 455.5196 | -1.646 | 2.306
62165 | -506.4197 | -63.2322 | 510.352 | -2.637 | 2.636
62175 | -487.2576 | -134.742 | 505.5446 | -2.635 | 1.647
62185 | -296.5605 | -93.1704 | 310.8518 | -0.989 | -1.318
62195 | -115.7431 | -61.6162 | 131.1222 | -0.987 | -1.977
62205 | 16.6627 | -419.1908 | 419.5218 | -7.248 | -2.306
62215 | -105.8185 | -787.8517 | 794.9263 | -8.567 | 1.318
62225 | -211.7009 | -644.7749 | 678.6398 | -1.976 | 1.318
62235 | -131.1302 | -159.61 | 206.5683 | 3.953 | -0.989
62245 | 39.0134 | 191.9168 | 195.842 | 4.284 | -2.635
62255 | 292.3707 | 340.6134 | 448.8854 | 3.293 | -4.943
62265 | 570.3098 | 429.71 | 714.0756 | 3.295 | -6.588
62275 | 649.5957 | 228.9819 | 688.7723 | -1.318 | -4.613
62285 | 517.5636 | 107.034 | 528.5152 | -0.659 | -1.647
62295 | 425.1979 | -120.6572 | 441.9858 | -3.624 | -1.647
62305 | 423.2621 | -427.5956 | 601.655 | -5.93 | -2.307
62315 | 377.312 | -448.7552 | 586.2982 | -2.636 | -1.317
62325 | 265.1581 | -300.705 | 400.9143 | -0.329 | 0
62335 | 225.8824 | -299.845 | 375.4063 | -1.977 | -0.659
62345 | 134.7353 | -289.1089 | 318.9633 | -1.317 | 0.659
62355 | 43.8352 | -392.2519 | 394.6936 | -3.295 | 0.988
62365 | 80.6507 | -538.5903 | 544.5953 | -4.283 | -0.658
62375 | 2.0279 | -429.1179 | 429.1227 | -0.659 | 1.318
62385 | -284.0263 | -291.7382 | 407.1635 | 0 | 4.941
62395 | -747.4234 | -154.9067 | 763.3071 | 0.989 | 9.225
62405 | -791.0485 | 33.1684 | 791.7436 | 2.635 | 4.282
62415 | -680.6735 | 51.6154 | 682.6277 | 0.659 | 2.636
62425 | -488.8283 | -69.5231 | 493.7475 | -1.317 | 0.33
62435 | -381.9407 | -173.9536 | 419.6886 | -1.648 | 0.658
62445 | -329.5632 | 110.4909 | 347.5919 | 4.283 | 0.66
62455 | -336.4191 | 20.207 | 337.0254 | -1.318 | 1.317
62465 | -481.8321 | -62.3085 | 485.8441 | -0.659 | 3.624
62475 | -652.1197 | 99.6331 | 659.6869 | 2.636 | 4.613
62485 | -612.8437 | -74.3014 | 617.3314 | -2.636 | 1.976
62495 | -490.2289 | -104.9361 | 501.3342 | -0.329 | 0.659
62505 | -182.102 | 25.3023 | 183.8515 | 1.647 | -3.295
62515 | 350.8528 | -110.1782 | 367.7457 | -2.305 | -8.565
62525 | 270.0915 | -352.9054 | 444.4004 | -4.284 | -0.659
62535 | 9.9259 | -362.7075 | 362.8433 | -1.647 | 1.647
62545 | -241.1089 | -286.2894 | 374.2928 | -0.659 | 3.295
62555 | -287.4239 | -394.6659 | 488.2352 | -3.295 | 1.318
62565 | -275.7549 | -475.6199 | 549.7772 | -2.964 | 0.987
62575 | -254.4463 | -944.9162 | 978.5753 | -10.214 | 0.66
62585 | -69.098 | -1258.6566 | 1260.5519 | -9.224 | -2.306
62595 | -176.4327 | -1328.3287 | 1339.9946 | -7.249 | 1.977
62605 | -424.6545 | -567.1391 | 708.5042 | 6.59 | 4.282
62615 | -688.6988 | -113.9346 | 698.0595 | 4.283 | 5.93
62625 | -523.1006 | -252.0514 | 580.6583 | -1.977 | 0
62635 | -405.8383 | -232.3505 | 467.6446 | 0.658 | 0.659
62645 | -320.3987 | -324.9558 | 456.3459 | -1.976 | 0
62655 | -185.2943 | -504.1931 | 537.1636 | -3.624 | -1.317
62665 | -434.5894 | -528.5157 | 684.2491 | -1.977 | 4.612
62675 | -322.0263 | -314.2721 | 449.9643 | 1.648 | -0.988
62685 | -223.1691 | 617.1983 | 656.3065 | 14.825 | -0.331
62695 | -372.5457 | 861.3178 | 938.4341 | 6.919 | 2.966
62705 | -495.9205 | 868.3875 | 1000.017 | 5.93 | 2.965
62715 | -489.6663 | 866.809 | 995.5556 | 5.271 | 1.648
62725 | -399.353 | 770.299 | 867.6655 | 3.295 | 0.329
62735 | -452.0673 | 633.6623 | 778.3911 | 1.976 | 2.306
62745 | -547.6494 | 841.2413 | 1003.7962 | 6.918 | 2.966
62755 | -592.1054 | 954.2254 | 1123.0026 | 5.601 | 2.635
62765 | -503.1731 | 857.5633 | 994.2827 | 2.965 | 0.658
62775 | -375.5926 | 766.5666 | 853.6359 | 2.636 | -0.329
62785 | -292.8394 | 356.9334 | 461.6887 | -3.623 | -0.329
62795 | -300.1464 | 142.1191 | 332.093 | -1.978 | 0.658
62805 | -330.8685 | -22.4861 | 331.6317 | -2.965 | 0.989
62815 | -502.188 | -11.726 | 502.3249 | -0.658 | 3.624
62825 | -709.9007 | -87.0634 | 715.2196 | -2.307 | 4.941
62835 | -638.0023 | -356.4545 | 730.8261 | -5.601 | 1.318
62845 | -580.3008 | -504.5131 | 768.949 | -4.612 | 1.648
62855 | -637.7953 | -457.1891 | 784.7323 | -2.305 | 2.965
62865 | -1035.4416 | -305.5356 | 1079.5792 | -0.331 | 8.895
62875 | -1265.9839 | -34.91 | 1266.4652 | 2.636 | 7.577
62885 | -1279.1554 | -39.5583 | 1279.7669 | -0.659 | 5.601
62895 | -728.2737 | -484.5541 | 874.743 | -7.577 | -3.954
62905 | -39.6106 | -706.9732 | 708.082 | -5.601 | -8.565
62915 | 721.029 | -702.7127 | 1006.8207 | -3.624 | -13.837
62925 | 1617.2659 | -947.0456 | 1874.1517 | -7.907 | -20.096
62935 | 2334.5512 | -1235.8577 | 2641.4908 | -9.224 | -21.415
62945 | 2270.0716 | -1319.7371 | 2625.8201 | -7.249 | -11.86
62955 | 1880.2323 | -1541.1302 | 2431.1223 | -10.212 | -6.59
62965 | 1519.2607 | -1520.9191 | 2149.7321 | -6.59 | -4.282
62975 | 1084.849 | -1160.0892 | 1588.3023 | -0.987 | -0.329
62985 | 335.9774 | -405.4738 | 526.5832 | 7.577 | 7.577
62995 | -100.5793 | 456.315 | 467.2682 | 13.178 | 5.93
63005 | -427.7655 | 1193.4675 | 1267.8123 | 15.813 | 7.248
63015 | -188.2893 | 1175.6195 | 1190.6024 | 6.919 | -0.989
63025 | 117.033 | 457.4973 | 472.2292 | -4.283 | -2.635
63035 | 578.1989 | 126.7888 | 591.9369 | -1.318 | -7.577
63045 | 790.2302 | -182.2132 | 810.9658 | -4.282 | -5.601
63055 | 476.1886 | -600.3606 | 766.2822 | -7.578 | 1.647
63065 | 262.8782 | -778.9881 | 822.148 | -5.6 | 0.988
63075 | -284.4586 | -301.1114 | 414.228 | 4.282 | 8.566
63085 | -876.8345 | 535.9663 | 1027.6666 | 12.19 | 11.531
63095 | -1157.7365 | 1398.5606 | 1815.5786 | 17.132 | 9.554
63105 | -1235.4016 | 1291.1069 | 1786.9455 | 5.271 | 7.907
63115 | -1031.7713 | 571.4398 | 1179.4471 | -4.283 | 3.294
63125 | -908.7759 | 410.1513 | 997.0445 | 1.318 | 3.624
63135 | -1056.028 | 416.8823 | 1135.3352 | 1.647 | 6.919
63145 | -999.796 | -508.3828 | 1121.6261 | -14.167 | 3.624
63155 | -821.4223 | -1436.3452 | 1654.6365 | -17.46 | 1.648
63165 | -457.5587 | -1838.5198 | 1894.6015 | -14.167 | -2.637
63175 | 205.5188 | -1603.568 | 1616.6843 | -5.93 | -9.554
63185 | 220.3208 | -1059.1608 | 1081.8331 | 0.329 | -1.647
63195 | -1.6117 | -764.9964 | 764.9981 | -0.658 | 0.989
63205 | -324.7638 | -1080.8847 | 1128.62 | -8.567 | 4.282
63215 | -658.6226 | -896.2478 | 1112.2248 | -0.658 | 6.26
63225 | -860.5665 | -403.8202 | 950.6026 | 4.282 | 5.931
63235 | -1295.1149 | -203.1026 | 1310.9436 | 1.977 | 11.201
63245 | -1689.9863 | -318.1878 | 1719.6794 | -1.646 | 12.189
63255 | -1858.8916 | -564.6885 | 1942.7689 | -4.284 | 10.543
63265 | -1683.2941 | -594.782 | 1785.2855 | -1.977 | 5.601
63275 | -1343.7276 | -469.2966 | 1423.3212 | 0 | 1.976
63285 | -876.8036 | -263.3462 | 915.4976 | 1.977 | -2.306
63295 | -406.406 | -139.061 | 429.5391 | 1.647 | -4.942
63305 | 41.4206 | -83.7849 | 93.4643 | 1.319 | -7.248
63315 | 485.8519 | 185.8564 | 520.1871 | 5.271 | -9.554
63325 | 591.1684 | 574.8386 | 824.5723 | 8.236 | -5.93
63335 | 451.5481 | 792.5273 | 912.1377 | 7.248 | -2.636
63345 | 231.6416 | 910.9616 | 939.9515 | 6.919 | -0.329
63355 | 79.3615 | 851.2195 | 854.911 | 4.282 | 0
63365 | 54.7757 | 694.5713 | 696.7278 | 2.306 | -0.988
63375 | 74.1591 | 599.9456 | 604.5117 | 2.306 | -1.318
63385 | 90.3513 | 498.6251 | 506.7448 | 1.318 | -1.318
63395 | 218.1841 | 317.0028 | 384.8312 | -0.658 | -3.295
63405 | 340.4297 | 247.1021 | 420.6564 | 0.329 | -3.624
63415 | 440.8954 | 236.2999 | 500.2263 | 0.659 | -3.953
63425 | 533.5568 | 305.4432 | 614.7995 | 1.976 | -4.283
63435 | 642.1828 | 474.3686 | 798.3886 | 3.955 | -4.942
63445 | 707.1892 | 615.8588 | 937.7626 | 4.282 | -4.612
63455 | 735.4222 | 688.0132 | 1007.079 | 3.953 | -4.283
63465 | 704.3888 | 832.451 | 1090.4762 | 5.601 | -3.294
63475 | 552.2823 | 909.7566 | 1064.271 | 4.942 | -0.989
63485 | 387.6969 | 785.2686 | 875.7601 | 1.977 | 0
63495 | 169.4177 | 594.1336 | 617.8164 | 0.329 | 1.977
63505 | 16.0558 | 395.3194 | 395.6453 | -0.989 | 1.976
63515 | -41.4965 | 225.4154 | 229.2031 | -1.647 | 1.318
63525 | -58.9704 | 131.9087 | 144.4902 | -1.317 | 0.989
63535 | 1.1808 | 71.6826 | 71.6923 | -1.318 | -0.329
63545 | 63.8274 | 64.0833 | 90.4467 | -0.659 | -0.66
63555 | 80.0441 | 154.2509 | 173.7826 | 0.988 | -0.329
63565 | 122.987 | 238.2446 | 268.1162 | 1.318 | -0.989
63575 | 137.2156 | 267.6149 | 300.7422 | 0.988 | -0.658
63585 | 103.4947 | 242.7898 | 263.9281 | 0.33 | 0
63595 | 115.8329 | 183.4985 | 216.9999 | -0.33 | -0.659
63605 | 93.1857 | 218.3961 | 237.4457 | 0.989 | 0
63615 | 52.011 | 234.1238 | 239.8314 | 0.658 | 0.329
63625 | 43.2608 | 256.2823 | 259.9079 | 0.989 | 0
63635 | -36.1959 | 177.5926 | 181.2437 | -0.659 | 1.318
63645 | -100.9227 | 130.9333 | 165.3146 | -0.33 | 1.318
63655 | -102.7193 | 145.9857 | 178.5023 | 0.33 | 0.659
63665 | -120.1988 | 120.5847 | 170.2599 | -0.33 | 0.988
63675 | -120.1963 | 56.3916 | 132.7673 | -0.988 | 0.659
63685 | -23.4697 | -29.2536 | 37.5047 | -1.647 | -0.988
63695 | 11.4399 | -109.973 | 110.5664 | -1.977 | -0.33
63705 | 60.99 | -147.3627 | 159.4853 | -1.647 | -0.988
63715 | 138.9878 | -230.0273 | 268.7567 | -2.635 | -1.648
63725 | 175.2829 | -221.2439 | 282.264 | -1.318 | -1.317
63735 | 215.4528 | -207.2725 | 298.9679 | -1.318 | -1.647
63745 | 267.2644 | -207.1773 | 338.1608 | -1.318 | -1.977
63755 | 325.2266 | -154.2373 | 359.9465 | -0.33 | -2.306
63765 | 310.5999 | -115.1301 | 331.2511 | -0.329 | -1.318
63775 | 295.8417 | -56.7682 | 301.239 | 0.329 | -1.318
63785 | 273.6307 | -34.1387 | 275.7521 | 0 | -0.988
63795 | 221.2912 | 14.0798 | 221.7387 | 0.66 | -0.33
63805 | 184.8203 | -24.825 | 186.4801 | -0.66 | -0.329
63815 | 145.0148 | -4.3659 | 145.0805 | 0.33 | 0
63825 | 97.4925 | 2.3768 | 97.5215 | 0 | 0.329
63835 | 64.1516 | 21.0564 | 67.5189 | 0.33 | 0.33
63845 | 23.0285 | -20.6045 | 30.9007 | -0.66 | 0.659
63855 | 30.2594 | -75.4711 | 81.3112 | -0.988 | 0
63865 | 39.2652 | -53.3229 | 66.22 | 0 | 0
63875 | 22.0105 | -30.2756 | 37.4309 | 0 | 0.329
63885 | 63.9232 | -19.1052 | 66.7172 | 0 | -0.659
63895 | 99.0538 | 25.8536 | 102.3722 | 0.659 | -0.659
63905 | 60.5892 | 2.908 | 60.659 | -0.329 | 0.33
63915 | 46.2944 | -2.514 | 46.3626 | 0 | 0
63925 | 4.1337 | -76.8745 | 76.9856 | -1.318 | 0.659
63935 | -30.0157 | -117.558 | 121.3294 | -0.988 | 0.658
63945 | -70.7859 | -80.57 | 107.2481 | 0 | 0.989
63955 | -82.3895 | -108.2729 | 136.0553 | -0.989 | 0.659
63965 | -49.9792 | -138.9824 | 147.6958 | -0.988 | 0
63975 | -45.8247 | -138.403 | 145.7919 | -0.659 | 0.329
63985 | -30.4963 | -175.014 | 177.6512 | -1.317 | 0
63995 | -18.1798 | -207.0701 | 207.8666 | -1.319 | 0
64005 | 7.3373 | -247.084 | 247.1929 | -1.647 | -0.329
64015 | -12.2055 | -277.9507 | 278.2186 | -1.647 | 0.329
64025 | -31.4961 | -299.8009 | 301.4508 | -1.648 | 0.33
64035 | -42.2149 | -278.4536 | 281.6354 | -0.988 | 0.329
64045 | -30.2794 | -185.255 | 187.7133 | 0.33 | 0
64055 | -20.4817 | -214.2718 | 215.2485 | -1.318 | 0
64065 | 3.4834 | -194.4718 | 194.503 | -0.33 | -0.329
64075 | 21.452 | -169.2465 | 170.6006 | -0.329 | -0.33
64085 | 51.4139 | -117.3596 | 128.1276 | 0.329 | -0.659
64095 | 54.7551 | -39.9177 | 67.7609 | 0.988 | -0.329
64105 | 111.7166 | -4.4123 | 111.8037 | 0.66 | -1.318
64115 | 178.1347 | -3.6629 | 178.1724 | 0.329 | -1.647
64125 | 242.0291 | -21.8077 | 243.0096 | 0 | -1.977
64135 | 249.1107 | -90.5503 | 265.0575 | -0.989 | -1.317
64145 | 269.8026 | -102.1714 | 288.5003 | -0.329 | -1.648
64155 | 272.1665 | -100.6164 | 290.1694 | -0.329 | -1.318
64165 | 254.2512 | -63.1544 | 261.9774 | 0.329 | -0.989
64175 | 301.2946 | -52.9644 | 305.9145 | 0 | -1.976
64185 | 266.7933 | -12.4461 | 267.0834 | 0.659 | -0.659
64195 | 252.1715 | -75.2347 | 263.1553 | -0.988 | -0.989
64205 | 251.0349 | -92.2863 | 267.4608 | -0.33 | -0.987
64215 | 212.765 | -54.111 | 219.538 | 0.33 | -0.33
64225 | 260.2486 | -25.5011 | 261.495 | 0.329 | -1.647
64235 | 266.3199 | -47.3094 | 270.4893 | -0.329 | -0.989
64245 | 261.787 | -28.1407 | 263.2951 | 0.329 | -0.988
64255 | 242.4215 | 30.9087 | 244.384 | 0.989 | -0.659
64265 | 247.536 | 54.4036 | 253.444 | 0.658 | -0.988
64275 | 274.6271 | 66.2348 | 282.5015 | 0.66 | -1.318
64285 | 237.0491 | 18.8726 | 237.7992 | -0.33 | -0.329
64295 | 184.9476 | -18.1931 | 185.8402 | -0.33 | 0
64305 | 151.7256 | -95.76 | 179.4175 | -1.318 | 0
64315 | 188.6779 | -134.742 | 231.8507 | -0.988 | -0.988
64325 | 181.7517 | -193.8426 | 265.7229 | -1.647 | -0.331
64335 | 206.3591 | -259.7028 | 331.7072 | -1.977 | -0.987
64345 | 210.1102 | -325.276 | 387.2348 | -2.306 | -0.66
64355 | 188.738 | -315.3617 | 367.5255 | -1.318 | -0.329
64365 | 211.5807 | -322.9335 | 386.0731 | -1.647 | -0.988
64375 | 175.4615 | -337.4351 | 380.3277 | -1.647 | 0
64385 | 199.6706 | -368.832 | 419.4107 | -1.977 | -0.989
64395 | 226.3021 | -356.5653 | 422.3168 | -1.317 | -0.988
64405 | 240.9481 | -364.5124 | 436.95 | -1.648 | -0.989
64415 | 212.166 | -377.106 | 432.6931 | -1.647 | -0.329
64425 | 207.8547 | -444.6765 | 490.8571 | -2.636 | -0.658
64435 | 171.8708 | -422.3115 | 455.9458 | -1.317 | 0
64445 | 161.6044 | -377.6184 | 410.7452 | -0.989 | -0.331
64455 | 120.6103 | -294.6457 | 318.3755 | 0 | 0.331
64465 | 125.5072 | -274.0439 | 301.4168 | -0.659 | -0.331
64475 | 115.6765 | -250.3361 | 275.7702 | -0.329 | 0
64485 | 64.9992 | -210.737 | 220.5334 | 0 | 0.66
64495 | 45.4876 | -162.9708 | 169.1999 | 0.329 | 0.329
64505 | 16.7685 | -90.4715 | 92.0124 | 0.988 | 0.659
64515 | 30.9977 | -17.7436 | 35.7169 | 1.318 | 0
64525 | 63.7361 | 33.0274 | 71.7851 | 1.318 | -0.33
64535 | 26.2521 | 49.3453 | 55.8939 | 0.988 | 0.66
64545 | 10.538 | 61.4474 | 62.3445 | 0.989 | 0.329
64555 | -52.8772 | -2.3378 | 52.9289 | -0.329 | 1.317
64565 | -66.2777 | 6.6259 | 66.6081 | 0.658 | 0.66
64575 | -30.3068 | 27.3267 | 40.8075 | 0.659 | 0
64585 | -5.6011 | -36.8 | 37.2238 | -0.659 | 0
64595 | -32.0266 | -68.7353 | 75.8304 | -0.329 | 0.659
64605 | 1.6367 | -101.1019 | 101.1152 | -0.66 | -0.33
64615 | 90.368 | -125.3056 | 154.4923 | -0.658 | -1.318
64625 | 152.8562 | -159.8788 | 221.1928 | -0.988 | -1.317
64635 | 171.7716 | -186.0408 | 253.2127 | -0.989 | -0.989
64645 | 163.625 | -222.593 | 276.2621 | -1.318 | -0.658
64655 | 197.345 | -308.3109 | 366.061 | -2.306 | -1.318
64665 | 189.4794 | -296.4988 | 351.8721 | -0.988 | -0.659
64675 | 140.5172 | -258.4891 | 294.2137 | -0.659 | 0
64685 | 164.3931 | -199.2146 | 258.2858 | 0 | -0.989
64695 | 191.1943 | -158.5274 | 248.3671 | 0 | -0.988
64705 | 129.6562 | -115.6799 | 173.7601 | 0.329 | 0.33
64715 | 98.564 | -104.0755 | 143.3408 | 0 | 0
64725 | 123.9017 | -79.8973 | 147.4287 | 0.33 | -0.66
64735 | 144.7601 | -59.1131 | 156.3645 | 0.33 | -0.658
64745 | 155.9954 | -6.6321 | 156.1364 | 0.987 | -0.659
64755 | 201.7163 | 34.7343 | 204.6849 | 0.989 | -1.318
64765 | 199.0264 | 42.6345 | 203.5416 | 0.659 | -0.659
64775 | 210.1251 | 28.2966 | 212.0219 | 0.329 | -0.989
64785 | 184.6524 | 58.4251 | 193.675 | 0.989 | -0.329
64795 | 162.9588 | 10.018 | 163.2664 | -0.329 | -0.329
64805 | 132.3582 | -32.355 | 136.2554 | -0.331 | 0
64815 | 90.9353 | 22.2887 | 93.627 | 0.989 | 0.329
64825 | 100.2825 | 31.3 | 105.0537 | 0.33 | -0.329
64835 | 92.7818 | 124.458 | 155.2361 | 1.976 | 0
64845 | 82.2514 | 124.8479 | 149.5068 | 0.66 | 0
64855 | 75.3092 | 130.7176 | 150.8594 | 0.988 | 0
64865 | 69.9838 | 124.2026 | 142.5624 | 0.658 | 0
64875 | 46.4385 | 138.3465 | 145.9325 | 0.989 | 0.329
64885 | 65.8643 | 114.8372 | 132.3847 | 0.329 | -0.329
64895 | 64.7484 | 75.8334 | 99.7149 | 0 | 0
64905 | 97.0382 | 51.0712 | 109.6571 | 0 | -0.66
64915 | 123.6497 | 17.6303 | 124.9003 | -0.329 | -0.658
64925 | 158.1743 | -25.9837 | 160.2943 | -0.659 | -0.988
64935 | 164.5304 | -56.656 | 174.0119 | -0.659 | -0.66
64945 | 146.5969 | -115.0687 | 186.3638 | -1.317 | -0.329
64955 | 172.7068 | -160.176 | 235.5504 | -1.318 | -0.989
64965 | 139.4464 | -247.4702 | 284.0542 | -2.306 | 0
64975 | 108.4984 | -296.0463 | 315.302 | -1.977 | 0
64985 | 130.0031 | -325.7485 | 350.732 | -1.977 | -0.658
64995 | 111.2248 | -330.9961 | 349.1838 | -1.647 | 0
65005 | 110.5839 | -317.0859 | 335.8159 | -1.318 | -0.329
65015 | 133.7434 | -329.6349 | 355.7337 | -1.647 | -0.659
65025 | 112.0556 | -306.6316 | 326.465 | -0.988 | 0
65035 | 129.8867 | -269.109 | 298.8147 | -0.66 | -0.66
65045 | 129.5387 | -207.7139 | 244.7965 | 0 | -0.329
65055 | 124.794 | -164.8873 | 206.7882 | 0 | -0.329
65065 | 141.9185 | -120.2308 | 186.0008 | 0.329 | -0.659
65075 | 117.5559 | -145.546 | 187.091 | -0.658 | 0
65085 | 95.4435 | -150.7554 | 178.4284 | -0.329 | 0
65095 | 25.3364 | -128.24 | 130.7189 | 0 | 0.988
65105 | 9.6607 | -130.1661 | 130.5241 | -0.33 | 0.329
65115 | 25.785 | -76.9115 | 81.1187 | 0.659 | 0
65125 | 54.6646 | -70.8958 | 89.5234 | 0 | -0.329
65135 | 111.9362 | -35.8491 | 117.5367 | 0.658 | -0.988
65145 | 75.901 | 14.8847 | 77.3467 | 0.989 | 0.33
65155 | 39.5967 | 12.126 | 41.4118 | 0.33 | 0.329
65165 | 19.9176 | 25.058 | 32.0096 | 0.658 | 0.329
65175 | -12.285 | 78.8787 | 79.8296 | 1.318 | 0.659
65185 | -17.8032 | 82.3186 | 84.2217 | 0.659 | 0.33
65195 | -19.0496 | 41.065 | 45.2684 | 0 | 0.329
65205 | -3.1161 | 32.318 | 32.4679 | 0.33 | 0
65215 | 8.5053 | 14.1024 | 16.4686 | 0 | 0
65225 | -5.1987 | 19.0434 | 19.7403 | 0.329 | 0.33
65235 | -36.7348 | -11.7751 | 38.5759 | -0.329 | 0.658
65245 | -40.4505 | -76.1916 | 86.2635 | -0.989 | 0.329
65255 | -59.3643 | -102.2739 | 118.2542 | -0.658 | 0.66
65265 | -18.8379 | -134.401 | 135.7147 | -0.989 | -0.329
65275 | -22.9888 | -179.4248 | 180.8915 | -1.317 | 0.329
65285 | -54.0807 | -193.2293 | 200.6547 | -0.989 | 0.658
65295 | -18.2888 | -200.6601 | 201.4919 | -0.989 | -0.329
65305 | -43.9981 | -208.7144 | 213.3015 | -0.988 | 0.659
65315 | 4.5082 | -235.5154 | 235.5585 | -1.318 | -0.659
65325 | 10.8038 | -219.2649 | 219.5309 | -0.658 | 0
65335 | 24.8123 | -223.5774 | 224.95 | -0.989 | -0.329
65345 | 77.1108 | -194.3997 | 209.1347 | -0.33 | -0.989
65355 | 97.0415 | -132.0916 | 163.9062 | 0.33 | -0.658
65365 | 125.6108 | -88.8762 | 153.8735 | 0.33 | -0.989
65375 | 130.072 | -43.6257 | 137.193 | 0.659 | -0.659
65385 | 207.9497 | -49.0265 | 213.6509 | 0 | -1.976
65395 | 195.5496 | -18.9315 | 196.4638 | 0.658 | -0.659
65405 | 194.3332 | -28.6067 | 196.4274 | 0 | -0.989
65415 | 240.7914 | -1.9421 | 240.7992 | 0.66 | -1.647
65425 | 258.7745 | 4.9691 | 258.8222 | 0.329 | -1.317
65435 | 248.8758 | 44.8853 | 252.891 | 0.988 | -0.989
65445 | 223.7716 | 40.3327 | 227.3774 | 0.329 | -0.659
65455 | 150.2952 | 31.9038 | 153.644 | 0.33 | 0.33
65465 | 135.3675 | 30.0756 | 138.6683 | 0.33 | -0.33
65475 | 115.3064 | -27.1948 | 118.4699 | -0.66 | 0
65485 | 116.6183 | -52.2481 | 127.7877 | -0.329 | -0.33
65495 | 101.0831 | -62.4899 | 118.8393 | -0.329 | 0
65505 | 105.8138 | -70.3303 | 127.0548 | -0.33 | -0.329
65515 | 111.9182 | -56.9366 | 125.5686 | 0 | -0.33
65525 | 56.7324 | -65.3586 | 86.5466 | -0.329 | 0.659
65535 | 50.5225 | -94.3425 | 107.0188 | -0.66 | 0
65545 | 54.0747 | -76.9381 | 94.0401 | 0 | 0
65555 | 72.6886 | -59.6615 | 94.0379 | 0 | -0.329
65565 | 67.1339 | -31.5401 | 74.1737 | 0.331 | 0
65575 | 97.5598 | -30.1124 | 102.1013 | 0 | -0.659
65585 | 65.6895 | 25.0313 | 70.2971 | 0.988 | 0.329
65595 | 53.9348 | 13.0187 | 55.4838 | 0 | 0
65605 | 89.9911 | 14.4065 | 91.137 | 0.329 | -0.658
65615 | 156.2203 | 21.9846 | 157.7596 | 0.329 | -1.318
65625 | 183.4034 | 46.526 | 189.2128 | 0.66 | -0.988
65635 | 177.9262 | 27.6446 | 180.061 | 0 | -0.66
65645 | 154.7033 | 48.3579 | 162.0852 | 0.658 | -0.329
65655 | 139.4375 | 50.9904 | 148.4684 | 0.329 | -0.329
65665 | 189.2859 | 29.9235 | 191.6365 | 0 | -1.318
65675 | 172.9472 | 34.5626 | 176.367 | 0.331 | -0.33
65685 | 171.0581 | 41.9532 | 176.1277 | 0.329 | -0.658
65695 | 137.7567 | 46.3361 | 145.3408 | 0.329 | 0
65705 | 129.7886 | 30.4464 | 133.3119 | 0 | -0.33
65715 | 110.1857 | 56.3763 | 123.7706 | 0.659 | 0
65725 | 93.6718 | 41.7061 | 102.5369 | 0 | 0
65735 | 83.3713 | 44.503 | 94.5055 | 0.329 | 0
65745 | 37.6057 | 12.9819 | 39.7834 | -0.329 | 0.659
65755 | 20.7211 | 63.4235 | 66.7226 | 0.989 | 0.329
65765 | 13.0917 | 12.987 | 18.4406 | -0.66 | 0.33
65775 | -32.7672 | -17.724 | 37.2536 | -0.329 | 0.989
65785 | -69.7391 | -49.5257 | 85.5356 | -0.659 | 0.987
65795 | -74.7437 | -54.8664 | 92.7197 | -0.329 | 0.66
65805 | -58.2416 | -75.0909 | 95.0301 | -0.66 | 0.329
65815 | -48.2297 | -54.7007 | 72.9265 | 0 | 0.33
65825 | -83.1157 | -55.547 | 99.9684 | -0.329 | 0.987
65835 | -132.1868 | -80.9657 | 155.0122 | -0.658 | 1.318
65845 | -166.5781 | -81.0678 | 185.2572 | -0.33 | 1.319
65855 | -189.9513 | -97.4191 | 213.4759 | -0.659 | 1.318
65865 | -226.923 | -131.855 | 262.4496 | -0.988 | 1.646
65875 | -199.1766 | -195.6256 | 279.1786 | -1.647 | 0.66
65885 | -194.1462 | -243.081 | 311.0967 | -1.648 | 0.987
65895 | -218.5454 | -254.9219 | 335.7786 | -1.318 | 1.319
65905 | -257.7522 | -262.6202 | 367.975 | -1.317 | 1.647
65915 | -267.8324 | -233.3966 | 355.2579 | -0.66 | 1.318
65925 | -234.5836 | -250.175 | 342.9533 | -1.317 | 0.659
65935 | -249.3644 | -251.5507 | 354.2038 | -0.988 | 1.318
65945 | -230.0853 | -230.5759 | 325.7369 | -0.659 | 0.658
65955 | -192.7627 | -293.5892 | 351.2152 | -1.977 | 0.329
65965 | -168.9489 | -309.5791 | 352.6797 | -1.318 | 0.33
65975 | -174.489 | -273.9048 | 324.7619 | -0.658 | 0.659
65985 | -104.1619 | -268.2798 | 287.7911 | -0.989 | -0.659
65995 | -46.3804 | -290.4259 | 294.106 | -1.318 | -0.659
66005 | -50.3427 | -250.3687 | 255.3799 | -0.33 | 0
66015 | -76.2786 | -216.1408 | 229.2057 | -0.329 | 0.329
66025 | -53.7466 | -255.2027 | 260.8009 | -1.318 | -0.329
66035 | -31.1847 | -231.5759 | 233.6662 | -0.329 | -0.329
66045 | -55.7198 | -224.5245 | 231.3351 | -0.659 | 0.329
66055 | -95.4065 | -225.6716 | 245.0103 | -0.659 | 0.659
66065 | -140.3768 | -187.36 | 234.1141 | 0 | 0.989
66075 | -132.5959 | -214.5475 | 252.2148 | -0.988 | 0.329
66085 | -121.6534 | -184.5159 | 221.0106 | 0 | 0.329
66095 | -78.9349 | -172.919 | 190.0834 | -0.329 | -0.329
66105 | -46.4116 | -151.3013 | 158.2597 | 0 | -0.329
66115 | -65.499 | -133.1879 | 148.4222 | 0 | 0.329
66125 | -25.1662 | -83.1065 | 86.8333 | 0.658 | -0.659
66135 | -26.3699 | -63.217 | 68.4964 | 0.329 | 0
66145 | -34.45 | -34.0716 | 48.4529 | 0.66 | 0
66155 | 39.954 | -67.3002 | 78.2664 | -0.33 | -1.318
66165 | 23.5468 | -76.6754 | 80.2096 | 0 | 0
66175 | -0.5747 | -56.1973 | 56.2002 | 0.33 | 0
66185 | 8.122 | -39.7814 | 40.602 | 0.329 | -0.329
66195 | -1.2385 | -29.0424 | 29.0688 | 0.33 | 0
66205 | -29.4258 | 36.7508 | 47.0797 | 1.318 | 0.329
66215 | -49.022 | 31.5293 | 58.286 | 0.329 | 0.329
66225 | -41.3615 | -38.7186 | 56.656 | -0.66 | 0
66235 | -14.6199 | -30.0149 | 33.3862 | 0.331 | -0.329
66245 | -14.9294 | -11.8371 | 19.0527 | 0.329 | 0
66255 | -18.8322 | -21.3423 | 28.4631 | 0 | 0
66265 | 18.2445 | -29.8581 | 34.991 | 0 | -0.658
66275 | 48.3939 | -72.2695 | 86.9761 | -0.66 | -0.66
66285 | 85.8816 | -104.7182 | 135.431 | -0.658 | -0.988
66295 | 114.1018 | -66.4 | 132.0158 | 0.329 | -0.989
66305 | 94.7263 | -14.486 | 95.8275 | 0.66 | -0.329
66315 | 97.8081 | -77.5056 | 124.7939 | -0.989 | -0.658
66325 | 67.973 | -75.3883 | 101.5073 | 0 | 0
66335 | 101.3977 | -79.9256 | 129.1108 | -0.329 | -0.989
66345 | 76.5273 | -49.9644 | 91.394 | 0.329 | 0
66355 | 88.6769 | -62.8866 | 108.7121 | -0.329 | -0.659
66365 | 86.3195 | -21.04 | 88.8467 | 0.658 | -0.329
66375 | 61.8175 | -41.1547 | 74.2638 | -0.329 | 0
66385 | 44.6034 | -26.3215 | 51.7908 | 0.329 | 0
66395 | 54.0237 | -65.4812 | 84.8902 | -0.658 | -0.33
66405 | 43.6852 | -42.8215 | 61.1725 | 0.329 | 0
66415 | 13.8838 | -74.5622 | 75.8438 | -0.659 | 0.33
66425 | -26.6728 | -48.4206 | 55.2811 | 0.33 | 0.659
66435 | -55.1555 | -59.1041 | 80.842 | -0.33 | 0.658
66445 | -35.2931 | -74.2605 | 82.2206 | -0.329 | 0
66455 | -56.8123 | -44.0002 | 71.8586 | 0.329 | 0.66
66465 | -2.6216 | 0.42258 | 2.6554 | 0.659 | -0.66
66475 | 24.9689 | -27.407 | 37.0755 | -0.329 | -0.329
66485 | 93.5707 | -34.9707 | 99.8921 | 0 | -1.318
66495 | 108.9856 | 4.8205 | 109.0922 | 0.658 | -0.659
66505 | 54.2946 | -21.6812 | 58.4635 | -0.329 | 0.329
66515 | 13.8788 | -10.167 | 17.2043 | 0.329 | 0.33
66525 | 30.2299 | -13.036 | 32.9208 | 0 | -0.33
66535 | 27.425 | -18.8903 | 33.3012 | 0 | 0
66545 | -37.0214 | 36.236 | 51.8038 | 0.989 | 0.989
66555 | -67.3319 | 42.2781 | 79.5048 | 0.329 | 0.659
66565 | -82.1033 | 77.0489 | 112.5943 | 0.988 | 0.659
66575 | -93.9519 | 50.4969 | 106.6625 | 0 | 0.659
66585 | -65.0556 | 43.9659 | 78.519 | 0.33 | 0
66595 | -61.6768 | 8.058 | 62.201 | -0.33 | 0.329
66605 | -27.0406 | -59.0813 | 64.9753 | -0.988 | -0.329
66615 | -18.1579 | -67.715 | 70.1073 | -0.329 | 0
66625 | 1.9744 | -85.823 | 85.8457 | -0.66 | -0.329
66635 | -38.7581 | -103.3594 | 110.3873 | -0.658 | 0.658
66645 | 2.7818 | -153.8691 | 153.8943 | -1.318 | -0.658
66655 | -13.839 | -136.0772 | 136.7791 | -0.33 | 0.329
66665 | -55.5811 | -154.5494 | 164.24 | -0.987 | 0.658
66675 | -102.0108 | -176.8011 | 204.1197 | -0.989 | 0.989
66685 | -76.4924 | -210.483 | 223.9513 | -1.318 | 0
66695 | -70.9889 | -217.5445 | 228.834 | -0.988 | 0.33
66705 | -35.6837 | -239.7482 | 242.3892 | -1.318 | -0.33
66715 | -64.9213 | -221.5939 | 230.9083 | -0.659 | 0.659
66725 | -94.2277 | -147.9441 | 175.4033 | 0.329 | 0.658
66735 | -33.9602 | -133.8558 | 138.0966 | -0.329 | -0.658
66745 | -3.3605 | -153.2006 | 153.2374 | -0.659 | -0.329
66755 | 28.9585 | -147.5185 | 150.3339 | -0.33 | -0.659
66765 | 15.5378 | -101.3621 | 102.5461 | 0.33 | 0
66775 | 20.7972 | -86.0106 | 88.4892 | 0 | -0.33
66785 | -27.7245 | -99.6773 | 103.4612 | -0.33 | 0.659
66795 | -29.0666 | -109.653 | 113.44 | -0.329 | 0
66805 | -21.371 | -114.4003 | 116.3794 | -0.329 | 0
66815 | -18.2992 | -97.8797 | 99.5755 | 0 | 0
66825 | -16.639 | -26.6452 | 31.4137 | 0.988 | 0
66835 | -34.8587 | -30.4172 | 46.2637 | 0 | 0.33
66845 | 8.2484 | -23.8182 | 25.206 | 0.33 | -0.659
66855 | 26.2283 | -31.8841 | 41.2858 | 0 | -0.33
66865 | 32.5584 | -39.2708 | 51.0123 | 0 | -0.33
66875 | -0.38485 | -3.7084 | 3.7283 | 0.658 | 0.33
66885 | 31.2821 | -12.5926 | 33.7216 | 0 | -0.659
66895 | 43.3214 | -5.5997 | 43.6818 | 0.33 | -0.329
66905 | 26.9071 | 23.6999 | 35.8563 | 0.659 | 0
66915 | 14.9289 | -31.2344 | 34.6188 | -0.659 | 0
66925 | 27.9491 | -1.0153 | 27.9676 | 0.659 | -0.329
66935 | 78.02 | -23.5503 | 81.4969 | -0.33 | -0.989
66945 | 38.5365 | -49.5022 | 62.7338 | -0.329 | 0.329
66955 | 58.2114 | -5.7889 | 58.4986 | 0.659 | -0.658
66965 | -12.2744 | 11.887 | 17.0869 | 0.33 | 0.988
66975 | -35.5411 | 17.8844 | 39.7872 | 0.329 | 0.33
66985 | -2.222 | 42.4144 | 42.4725 | 0.658 | -0.33
66995 | 41.7101 | 81.4321 | 91.4927 | 0.989 | -0.659
67005 | 31.8525 | 109.7139 | 114.2441 | 0.988 | 0
67015 | 57.405 | 90.2223 | 106.9364 | 0.329 | -0.659
67025 | 101.1513 | 93.2723 | 137.5911 | 0.66 | -0.989
67035 | 73.6076 | 101.6458 | 125.4988 | 0.658 | 0
67045 | 66.7074 | 107.822 | 126.7891 | 0.66 | -0.329
67055 | 49.7345 | 55.3604 | 74.4197 | -0.33 | 0
67065 | 55.1047 | 52.6993 | 76.2479 | 0.33 | -0.329
67075 | 43.3722 | 40.7757 | 59.5299 | 0 | 0
67085 | 32.27 | 28.668 | 43.1649 | 0 | 0
67095 | -12.3769 | 40.7175 | 42.557 | 0.329 | 0.658
67105 | -47.1107 | 70.3975 | 84.7067 | 0.659 | 0.66
67115 | -29.9752 | 33.7593 | 45.1465 | -0.329 | 0
67125 | -52.8821 | 39.3195 | 65.8979 | 0.329 | 0.659
67135 | 0.39245 | 13.0842 | 13.0901 | -0.329 | -0.659
67145 | 8.2645 | 27.1758 | 28.4047 | 0.329 | 0
67155 | 3.6033 | 24.1678 | 24.435 | 0 | 0
67165 | -16.9572 | 55.7845 | 58.3048 | 0.658 | 0.329
67175 | -32.891 | 63.4598 | 71.4771 | 0.331 | 0.33
67185 | -23.2256 | 83.1672 | 86.3494 | 0.658 | 0
67195 | -14.621 | 23.3326 | 27.5351 | -0.658 | 0
67205 | 8.7423 | 69.2353 | 69.785 | 0.987 | -0.33
67215 | 7.0916 | 40.1138 | 40.7358 | -0.329 | 0
67225 | 60.0654 | 44.2015 | 74.5763 | 0.329 | -0.989
67235 | 103.8624 | -20.7603 | 105.9169 | -0.987 | -0.987
67245 | 92.0039 | -18.1062 | 93.7686 | 0 | -0.33
67255 | 99.317 | 14.1147 | 100.3149 | 0.329 | -0.659
67265 | 52.7379 | -4.1942 | 52.9045 | -0.329 | 0.329
67275 | 91.545 | 34.164 | 97.7122 | 0.658 | -0.988
67285 | 112.0905 | 49.6475 | 122.5935 | 0.329 | -0.658
67295 | 119.8007 | 92.7242 | 151.4926 | 0.989 | -0.66
67305 | 107.2085 | 108.2315 | 152.3408 | 0.659 | -0.329
67315 | 136.0022 | 76.2827 | 155.9348 | 0 | -0.989
67325 | 85.3046 | 71.3778 | 111.228 | 0.329 | 0.33
67335 | 98.1649 | 73.9549 | 122.9052 | 0.329 | -0.659
67345 | 138.3198 | 36.9799 | 143.1778 | -0.329 | -0.988
67355 | 164.9681 | 65.4019 | 177.4595 | 0.66 | -0.989
67365 | 143.3801 | 74.7554 | 161.698 | 0.329 | -0.329
67375 | 144.2722 | 56.1283 | 154.8058 | 0 | -0.659
67385 | 112.302 | 42.293 | 120.0019 | 0 | 0
67395 | 86.0544 | 53.7152 | 101.443 | 0.329 | 0
67405 | 71.2233 | 44.6937 | 84.085 | 0 | 0
67415 | 61.5336 | 54.1985 | 81.9991 | 0.329 | 0
67425 | 73.878 | 6.3659 | 74.1518 | -0.658 | -0.329
67435 | 45.6057 | 42.8316 | 62.5654 | 0.658 | 0.329
67445 | 0.98659 | 22.388 | 22.4097 | -0.329 | 0.659
67455 | 8.8809 | -3.1695 | 9.4295 | -0.329 | 0
67465 | 38.6784 | 40.0803 | 55.6996 | 0.658 | -0.329
67475 | 38.4888 | 56.9737 | 68.756 | 0.33 | 0
67485 | 52.9841 | 42.8044 | 68.1141 | 0 | -0.33
67495 | 84.8975 | 31.8139 | 90.6626 | 0 | -0.659
67505 | 88.2474 | 25.9825 | 91.9929 | 0 | -0.33
67515 | 125.3266 | 3.0381 | 125.3634 | -0.33 | -0.987
67525 | 118.197 | 4.4136 | 118.2794 | 0 | -0.331
67535 | 126.2611 | -10.62 | 126.7069 | -0.329 | -0.658
67545 | 137.1134 | -24.6254 | 139.3072 | -0.329 | -0.659
67555 | 144.3134 | -33.5157 | 148.1542 | -0.329 | -0.659
67565 | 130.6856 | -1.6715 | 130.6963 | 0.329 | -0.33
67575 | 119.9774 | -14.7399 | 120.8795 | -0.329 | -0.329
67585 | 76.3444 | 7.1654 | 76.6799 | 0.329 | 0.329
67595 | 81.3301 | 9.1805 | 81.8466 | 0 | -0.329
67605 | 111.0088 | 25.0343 | 113.7966 | 0.329 | -0.658
67615 | 54.074 | 19.8015 | 57.5856 | 0 | 0.658
67625 | 24.0059 | 32.1957 | 40.1602 | 0.329 | 0.329
67635 | 29.7782 | 44.2418 | 53.3299 | 0.33 | 0
67645 | 15.3388 | 89.9674 | 91.2656 | 0.989 | 0.33
67655 | 20.2499 | 183.2299 | 184.3454 | 1.976 | 0
67665 | 64.4394 | 136.0156 | 150.5081 | 0 | -0.659
67675 | 77.625 | 126.3842 | 148.3193 | 0.659 | -0.329
67685 | 61.95 | 114.1674 | 129.8922 | 0.329 | 0
67695 | 69.2598 | 45.9043 | 83.0911 | -0.658 | -0.329
67705 | 58.839 | 71.7514 | 92.7917 | 0.658 | 0
67715 | 67.7902 | 44.9409 | 81.3338 | -0.329 | -0.33
67725 | 77.2685 | 15.295 | 78.7678 | -0.329 | -0.33
67735 | 101.7429 | -1.8566 | 101.7599 | -0.33 | -0.659
67745 | 82.0748 | -13.5237 | 83.1815 | -0.329 | 0
67755 | 44.0268 | 16.2038 | 46.914 | 0.329 | 0.33
67765 | 18.8244 | -17.7644 | 25.883 | -0.659 | 0.329
67775 | 41.7307 | -31.6604 | 52.3816 | -0.33 | -0.329
67785 | 23.0509 | -55.1065 | 59.7333 | -0.658 | 0.329
67795 | -35.7346 | -74.9346 | 83.0191 | -0.659 | 0.989
67805 | -78.3057 | -69.0584 | 104.4071 | -0.33 | 0.988
67815 | -105.1785 | -63.8711 | 123.053 | -0.329 | 0.988
67825 | -86.1676 | -82.1232 | 119.0339 | -0.659 | 0.33
67835 | -51.4832 | -117.2285 | 128.0354 | -0.989 | 0
67845 | -49.4023 | -142.8709 | 151.1711 | -0.987 | 0.329
67855 | -72.528 | -160.1005 | 175.7626 | -0.989 | 0.66
67865 | -70.919 | -115.4506 | 135.493 | 0 | 0.329
67875 | -66.9062 | -41.7266 | 78.8514 | 0.659 | 0.329
67885 | -85.382 | -50.2726 | 99.0828 | -0.33 | 0.659
67895 | -101.0814 | -104.7738 | 145.585 | -0.988 | 0.659
67905 | -149.6279 | -65.7366 | 163.4314 | 0.329 | 1.317
67915 | -149.4604 | -46.5521 | 156.5424 | 0 | 0.66
67925 | -201.1657 | -21.5813 | 202.32 | 0.33 | 1.647
67935 | -208.2932 | -1.8373 | 208.3014 | 0.329 | 0.988
67945 | -206.9704 | 10.7328 | 207.2485 | 0.33 | 0.989
67955 | -114.056 | 19.7548 | 115.7541 | 0.33 | -0.66
67965 | -42.2203 | 45.8129 | 62.3007 | 0.658 | -0.658
67975 | 56.5574 | -10.156 | 57.462 | -0.658 | -1.648
67985 | 52.6034 | 0.26627 | 52.604 | 0.329 | -0.329
67995 | 19.2817 | -37.8663 | 42.4929 | -0.659 | 0
68005 | 58.9814 | -34.8685 | 68.5173 | 0 | -0.989
68015 | 96.2728 | -82.6247 | 126.8672 | -0.989 | -0.987
68025 | 138.8305 | -124.0129 | 186.1534 | -0.987 | -1.319
68035 | 151.8214 | -129.9942 | 199.8705 | -0.66 | -0.987
68045 | 120.8488 | -151.6264 | 193.8943 | -0.988 | -0.331
68055 | 117.9108 | -113.5532 | 163.6988 | 0 | -0.658
68065 | 65.3109 | -62.189 | 90.1831 | 0.33 | 0.329
68075 | 119.5643 | -107.046 | 160.482 | -0.989 | -1.317
68085 | 153.0361 | -71.7906 | 169.0383 | 0.33 | -0.989
68095 | 168.1956 | -53.4829 | 176.4942 | 0 | -0.988
68105 | 160.901 | -67.2731 | 174.3984 | -0.33 | -0.659
68115 | 136.0949 | -58.8393 | 148.2696 | 0 | -0.33
68125 | 100.5953 | -87.7574 | 133.4945 | -0.659 | 0
68135 | 96.0958 | -74.3732 | 121.5145 | 0 | -0.329
68145 | 39.7278 | -116.131 | 122.7384 | -0.989 | 0.659
68155 | 32.3131 | -115.1118 | 119.5612 | -0.329 | 0
68165 | 35.1831 | -106.7692 | 112.4167 | -0.329 | 0
68175 | 53.5678 | -84.6828 | 100.2032 | 0 | -0.33
68185 | 67.1722 | -106.8047 | 126.1719 | -0.659 | -0.329
68195 | 74.5418 | -70.314 | 102.4721 | 0.329 | -0.329
68205 | 21.6196 | -75.0736 | 78.1246 | -0.329 | 0.658
68215 | -20.9714 | -9.5952 | 23.0623 | 0.988 | 0.659
68225 | -65.3916 | -11.6732 | 66.4253 | 0 | 0.989
68235 | -59.5123 | -4.9485 | 59.7177 | 0.329 | 0.329
68245 | -31.9008 | 6.1248 | 32.4835 | 0.331 | 0
68255 | 23.3896 | 32.8476 | 40.3241 | 0.658 | -0.658
68265 | 24.0484 | 54.0912 | 59.1961 | 0.659 | 0
68275 | 35.9347 | 49.0944 | 60.8405 | 0.33 | -0.33
68285 | -28.3937 | 25.3387 | 38.0559 | 0 | 0.988
68295 | -81.7597 | -28.9259 | 86.7258 | -0.66 | 0.989
68305 | -93.7008 | 28.4597 | 97.9275 | 0.989 | 0.658
68315 | -42.2095 | 43.2544 | 60.4367 | 0.33 | -0.329
68325 | -22.4472 | 81.2184 | 84.2633 | 0.987 | 0
68335 | -16.5063 | 113.8705 | 115.0607 | 0.989 | 0
68345 | -12.2726 | 115.4326 | 116.0831 | 0.659 | 0
68355 | 28.9941 | 115.3714 | 118.9589 | 0.659 | -0.659
68365 | 42.277 | 137.3899 | 143.7475 | 0.988 | -0.33
68375 | -68.6253 | 137.0984 | 153.3147 | 0.66 | 1.648
68385 | -155.6182 | 153.937 | 218.8918 | 0.987 | 1.647
68395 | -149.0426 | 112.5539 | 186.7675 | 0 | 0.659
68405 | -157.4179 | 135.7648 | 207.8761 | 0.989 | 0.989
68415 | -171.0511 | 143.8135 | 223.4744 | 0.659 | 0.987
68425 | -200.8644 | 163.7037 | 259.1243 | 0.988 | 1.318
68435 | -186.7094 | 104.2896 | 213.8615 | -0.33 | 0.659
68445 | -154.0835 | 93.4222 | 180.1928 | 0.33 | 0.33
68455 | -114.7511 | 115.4936 | 162.8085 | 0.659 | 0
68465 | -108.0921 | 111.7948 | 155.5055 | 0.33 | 0.33
68475 | -69.5225 | 28.6861 | 75.2082 | -0.989 | -0.33
68485 | -76.486 | -54.4335 | 93.8782 | -1.317 | 0.33
68495 | -49.4361 | -88.8138 | 101.6455 | -0.989 | -0.33
68505 | -43.1978 | -128.3734 | 135.4466 | -1.317 | 0
68515 | -62.233 | -199.2024 | 208.6973 | -1.978 | 0.33
68525 | -75.6978 | -156.9951 | 174.2918 | -0.329 | 0.329
68535 | -102.0822 | -155.9424 | 186.3835 | -0.988 | 0.658
68545 | -141.1321 | -111.1718 | 179.6592 | 0 | 0.989
68555 | -149.469 | -113.2548 | 187.5303 | -0.66 | 0.659
68565 | -113.6227 | -66.6757 | 131.7413 | 0.331 | 0
68575 | -48.4959 | -8.2996 | 49.201 | 0.658 | -0.659
68585 | -22.6505 | 48.5481 | 53.572 | 0.988 | -0.329
68595 | -10.3578 | 126.1862 | 126.6106 | 1.647 | -0.329
68605 | -0.28255 | 106.036 | 106.0364 | 0.331 | -0.331
68615 | -30.8625 | 101.6448 | 106.227 | 0.658 | 0.331
68625 | -93.21 | 107.9744 | 142.6414 | 0.659 | 0.987
68635 | -98.1434 | 113.5383 | 150.0769 | 0.659 | 0.33
68645 | -151.6057 | 118.7907 | 192.602 | 0.659 | 1.318
68655 | -177.9922 | 142.914 | 228.2666 | 0.988 | 0.988
68665 | -171.836 | 143.5882 | 223.9312 | 0.659 | 0.659
68675 | -186.8627 | 103.3932 | 213.5599 | 0 | 0.988
68685 | -202.2593 | 112.5729 | 231.4768 | 0.659 | 0.989
68695 | -193.716 | 127.0068 | 231.639 | 0.659 | 0.658
68705 | -225.495 | 116.0211 | 253.5919 | 0.33 | 1.319
68715 | -234.7616 | 68.1702 | 244.4589 | -0.33 | 0.987
68725 | -256.9981 | 71.6174 | 266.7904 | 0.33 | 1.318
68735 | -295.9906 | 42.9247 | 299.0868 | -0.33 | 1.648
68745 | -344.1865 | 16.6228 | 344.5877 | -0.33 | 1.976
68755 | -321.8797 | 19.9526 | 322.4975 | 0 | 0.989
68765 | -339.1984 | 4.8825 | 339.2335 | -0.329 | 1.647
68775 | -323.0017 | -48.0743 | 326.5597 | -0.988 | 0.989
68785 | -345.9229 | -30.5187 | 347.2666 | 0 | 1.647
68795 | -293.1586 | -48.7923 | 297.1912 | -0.66 | 0.329
68805 | -267.0488 | 6.539 | 267.1288 | 0.66 | 0.659
68815 | -276.971 | -23.0721 | 277.9303 | -0.66 | 0.989
68825 | -266.6151 | -38.5017 | 269.3807 | -0.329 | 0.658
68835 | -275.5978 | -42.6745 | 278.8822 | -0.329 | 0.989
68845 | -208.4336 | 10.7684 | 208.7116 | 0.658 | -0.329
68855 | -191.462 | 72.1831 | 204.6169 | 0.989 | 0.329
68865 | -150.9884 | 111.726 | 187.8303 | 0.988 | -0.329
68875 | -174.1251 | 137.1939 | 221.6793 | 0.989 | 0.658
68885 | -121.0363 | 136.1332 | 182.1594 | 0.658 | -0.658
68895 | -13.707 | 96.4123 | 97.3818 | 0 | -1.648
68905 | 43.0084 | 87.2662 | 97.2888 | 0.33 | -1.318
68915 | -0.17941 | 125.7629 | 125.763 | 0.989 | 0
68925 | -53.9174 | 194.5022 | 201.8371 | 1.647 | 0.329
68935 | -7.5387 | 205.0965 | 205.235 | 0.988 | -0.987
68945 | -20.6466 | 244.577 | 245.447 | 1.647 | 0
68955 | -1.0849 | 337.5197 | 337.5214 | 2.636 | -0.66
68965 | 2.0235 | 310.9365 | 310.9431 | 0.988 | -0.329
68975 | -18.0611 | 299.5367 | 300.0808 | 1.318 | 0
68985 | -31.5045 | 245.3527 | 247.3671 | 0.33 | 0
68995 | -57.2033 | 184.7482 | 193.4014 | 0 | 0.329
69005 | -56.6526 | 166.1943 | 175.5849 | 0.329 | 0
69015 | -129.1794 | 139.1769 | 189.8882 | 0 | 1.318
69025 | -169.0591 | 79.0666 | 186.6347 | -0.659 | 0.989
69035 | -169.9262 | 53.7483 | 178.224 | -0.329 | 0.659
69045 | -169.893 | -17.1246 | 170.7538 | -1.318 | 0.658
69055 | -191.9215 | -74.3086 | 205.8048 | -1.318 | 0.989
69065 | -229.7609 | -92.098 | 247.532 | -0.988 | 1.318
69075 | -219.1466 | -84.9584 | 235.0386 | -0.66 | 0.659
69085 | -130.5487 | -158.8803 | 205.6354 | -1.976 | -0.659
69095 | -123.0325 | -203.0663 | 237.4298 | -1.648 | 0.329
69105 | -73.2474 | -190.1308 | 203.7521 | -0.987 | -0.659
69115 | -87.2196 | -180.8878 | 200.8175 | -0.989 | 0.33
69125 | -10.0409 | -161.3386 | 161.6507 | -0.659 | -1.318
69135 | 57.8182 | -91.3795 | 108.1349 | 0.329 | -1.318
69145 | 137.5249 | -59.9962 | 150.0421 | 0 | -1.977
69155 | 178.0495 | -84.7229 | 197.1791 | -0.658 | -1.647
69165 | 145.9265 | -124.9284 | 192.098 | -0.989 | -0.659
69175 | 179.6061 | -132.5919 | 223.2464 | -0.658 | -1.647
69185 | 216.6306 | -115.288 | 245.3979 | -0.33 | -1.648
69195 | 164.4797 | -160.9922 | 230.1566 | -1.318 | -0.329
69205 | 141.912 | -124.1943 | 188.5822 | 0 | -0.658
69215 | 194.3526 | -106.8502 | 221.788 | -0.329 | -1.648
69225 | 180.219 | -64.6385 | 191.4602 | 0.329 | -0.659
69235 | 103.9592 | 6.9821 | 104.1934 | 0.989 | 0.33
69245 | 108.3879 | 172.639 | 203.8435 | 2.964 | -0.66
69255 | 65.8202 | 180.9618 | 192.5603 | 0.989 | 0.33
69265 | 46.6353 | 167.2728 | 173.6521 | 0.988 | 0
69275 | 0.88683 | 148.9551 | 148.9578 | 0.66 | 0.659
69285 | -93.5084 | 196.1204 | 217.2718 | 1.647 | 1.648
69295 | -143.2414 | 142.8107 | 202.2696 | 0 | 1.317
69305 | -172.189 | 94.1604 | 196.2529 | 0 | 1.318
69315 | -175.8132 | 126.7714 | 216.7517 | 0.988 | 0.988
69325 | -140.6683 | 157.5847 | 211.2357 | 0.989 | 0.33
69335 | -78.0476 | 175.367 | 191.9506 | 0.988 | -0.33
69345 | -55.4291 | 168.6069 | 177.4843 | 0.658 | 0
69355 | -46.6109 | 182.3128 | 188.1768 | 0.989 | 0
69365 | -97.8355 | 157.9854 | 185.8256 | 0.329 | 0.989
69375 | -119.8255 | 156.4715 | 197.0824 | 0.66 | 0.658
69385 | -109.646 | 141.8981 | 179.3246 | 0.329 | 0.33
69395 | -102.0054 | 206.4704 | 230.2935 | 1.647 | 0.33
69405 | -79.8559 | 241.6804 | 254.5317 | 1.317 | 0
69415 | -121.0956 | 220.7738 | 251.8039 | 0.66 | 0.987
69425 | -119.1889 | 223.3029 | 253.1209 | 0.988 | 0.33
69435 | -71.6902 | 231.522 | 242.3673 | 0.989 | -0.33
69445 | -18.6054 | 160.5708 | 161.6451 | -0.33 | -0.658
69455 | -41.1985 | 85.3836 | 94.8033 | -0.659 | 0.329
69465 | -45.3519 | 18.8083 | 49.0973 | -0.988 | 0
69475 | -118.489 | -84.6595 | 145.6259 | -1.977 | 1.318
69485 | -138.8802 | -84.5686 | 162.6024 | -0.659 | 0.659
69495 | -200.9235 | -35.6306 | 204.0583 | 0 | 1.647
69505 | -214.0726 | 109.4922 | 240.4488 | 1.976 | 0.989
69515 | -254.6995 | 119.4421 | 281.3152 | 0.33 | 1.646
69525 | -271.639 | 144.2979 | 307.5868 | 0.989 | 1.319
69535 | -223.0128 | 113.8115 | 250.3752 | 0 | 0.329
69545 | -244.3019 | 124.0042 | 273.9716 | 0.658 | 1.318
69555 | -232.8934 | 120.8348 | 262.3745 | 0.33 | 0.658
69565 | -257.3675 | 95.7752 | 274.6105 | 0 | 1.319
69575 | -300.983 | 97.3186 | 316.3253 | 0.33 | 1.647
69585 | -331.6962 | -51.5232 | 335.674 | -2.307 | 1.647
69595 | -371.7081 | -94.4873 | 383.5293 | -0.988 | 1.977
69605 | -441.1986 | -124.6759 | 458.4761 | -1.318 | 2.635
69615 | -455.411 | -115.0002 | 469.7065 | -0.659 | 1.977
69625 | -460.6414 | -67.5656 | 465.5702 | 0 | 1.976
69635 | -431.3169 | -16.8993 | 431.6478 | 0.33 | 1.319
69645 | -314.2442 | 72.3693 | 322.4697 | 1.318 | -0.33
69655 | -229.0064 | 40.7527 | 232.6042 | -0.33 | -0.329
69665 | -102.5431 | 42.6989 | 111.0778 | 0.33 | -1.647
69675 | -8.4263 | 74.3113 | 74.7875 | 0.658 | -1.648
69685 | 128.8551 | 116.1072 | 173.4489 | 0.989 | -2.965
69695 | 214.3177 | 88.1153 | 231.7248 | 0 | -2.635
69705 | 231.1409 | 42.6629 | 235.0452 | -0.33 | -1.977
69715 | 225.2935 | 14.3392 | 225.7494 | -0.33 | -1.647
69725 | 170.2267 | 74.3651 | 185.7614 | 0.989 | -0.659
69735 | 94.93 | 124.0292 | 156.1888 | 0.988 | 0
69745 | 47.8912 | 133.2895 | 141.6321 | 0.66 | 0
69755 | -16.4486 | 156.3103 | 157.1734 | 0.987 | 0.659
69765 | -24.2167 | 157.3636 | 159.2161 | 0.66 | 0
69775 | -98.8917 | 232.8776 | 253.005 | 1.977 | 1.318
69785 | -199.3785 | 218.5688 | 295.8447 | 0.658 | 1.976
69795 | -248.8288 | 119.8266 | 276.1779 | -0.658 | 1.648
69805 | -259.4657 | 127.1655 | 288.9525 | 0.658 | 1.317
69815 | -268.1457 | 167.3101 | 316.0614 | 0.989 | 1.318
69825 | -278.5186 | 192.6034 | 338.6277 | 0.988 | 1.318
69835 | -230.9081 | 227.4029 | 324.0843 | 1.318 | 0.329
69845 | -252.1969 | 272.925 | 371.6064 | 1.647 | 1.318
69855 | -221.5844 | 190.5836 | 292.27 | -0.33 | 0.33
69865 | -192.1929 | 83.1769 | 209.4195 | -0.988 | 0.329
69875 | -196.0215 | 34.1057 | 198.9664 | -0.658 | 0.658
69885 | -182.8737 | -89.4699 | 203.587 | -2.307 | 0.331
69895 | -228.3345 | -186.4949 | 294.8169 | -2.306 | 1.317
69905 | -286.3913 | -267.6435 | 391.986 | -2.635 | 1.647
69915 | -305.4648 | -308.7743 | 434.339 | -2.307 | 1.318
69925 | -257.7895 | -280.1325 | 380.6963 | -1.317 | 0.33
69935 | -259.8078 | -260.4384 | 367.8699 | -1.318 | 0.988
69945 | -251.907 | -236.7546 | 345.702 | -0.988 | 0.659
69955 | -243.2336 | -223.005 | 329.9907 | -0.989 | 0.659
69965 | -200.6153 | -256.4761 | 325.6171 | -1.647 | 0
69975 | -167.8669 | -209.3143 | 268.3128 | -0.33 | 0
69985 | -129.1188 | -148.682 | 196.9213 | 0 | -0.33
69995 | -42.8856 | -111.9596 | 119.8921 | 0 | -1.318
70005 | -16.5966 | -32.3502 | 36.3591 | 0.988 | -0.658
70015 | -5.5328 | 47.2096 | 47.5327 | 1.318 | -0.659
70025 | -12.8478 | 61.8757 | 63.1955 | 0.66 | -0.329
70035 | -55.6426 | 124.8503 | 136.6883 | 1.646 | 0.329
70045 | -85.532 | 198.2772 | 215.9389 | 1.977 | 0.329
70055 | -120.6587 | 249.4655 | 277.1129 | 1.977 | 0.659
70065 | -183.9312 | 266.4105 | 323.7364 | 1.647 | 1.318
70075 | -287.4162 | 260.0292 | 387.5864 | 1.318 | 2.306
70085 | -342.9171 | 181.7896 | 388.1232 | 0 | 1.977
70095 | -394.9001 | 201.7352 | 443.4446 | 1.318 | 2.305
70105 | -416.7645 | 155.3019 | 444.7598 | 0 | 1.978
70115 | -412.2298 | 131.3634 | 432.6543 | 0.329 | 1.647
70125 | -392.3975 | 103.95 | 405.9328 | 0 | 1.318
70135 | -400.667 | 25.3662 | 401.4691 | -0.989 | 1.647
70145 | -393.541 | -33.1966 | 394.9387 | -0.987 | 1.318
70155 | -426.0717 | -108.021 | 439.5516 | -1.648 | 1.977
70165 | -397.9822 | -125.7241 | 417.3684 | -0.988 | 0.988
70175 | -352.4583 | -209.8923 | 410.2214 | -2.307 | 0.659
70185 | -286.1864 | -242.5 | 375.1119 | -1.647 | 0
70195 | -220.4059 | -220.077 | 311.4685 | -0.988 | -0.33
70205 | -118.9963 | -321.3396 | 342.6649 | -2.965 | -1.317
70215 | -5.8701 | -352.111 | 352.16 | -1.977 | -1.977
70225 | 15.573 | -343.1859 | 343.539 | -1.647 | -0.989
70235 | -34.1084 | -361.0032 | 362.6109 | -1.977 | 0
70245 | -47.7956 | -342.3834 | 345.7033 | -1.317 | -0.329
70255 | -85.2741 | -289.4069 | 301.7085 | -0.66 | 0.329
70265 | -55.6329 | -235.2355 | 241.7245 | -0.329 | -0.658
70275 | -120.5812 | -182.2349 | 218.5163 | 0 | 0.988
70285 | -177.968 | -31.6552 | 180.7614 | 1.977 | 0.988
70295 | -209.9697 | 120.5575 | 242.1185 | 2.636 | 0.988
70305 | -230.8833 | 240.6886 | 333.5238 | 2.965 | 0.989
70315 | -245.6247 | 343.1362 | 421.9881 | 3.294 | 0.988
70325 | -256.7755 | 398.8694 | 474.3738 | 2.965 | 0.989
70335 | -284.7998 | 458.3044 | 539.5867 | 3.294 | 1.318
70345 | -326.5068 | 412.6528 | 526.2024 | 1.648 | 1.647
70355 | -376.3492 | 376.1312 | 532.084 | 1.647 | 1.977
70365 | -412.5281 | 344.6244 | 537.5365 | 1.318 | 1.976
70375 | -456.9394 | 288.2928 | 540.2835 | 0.659 | 2.306
70385 | -549.3418 | 231.3939 | 596.0869 | 0.329 | 3.295
70395 | -562.5965 | 195.8083 | 595.6977 | 0.329 | 2.306
70405 | -583.5246 | 117.1028 | 595.1588 | -0.658 | 2.635
70415 | -549.6724 | 38.4484 | 551.0154 | -0.988 | 1.648
70425 | -542.2127 | 24.7292 | 542.7763 | -0.33 | 1.976
70435 | -488.9617 | -18.1247 | 489.2975 | -0.988 | 0.989
70445 | -505.6961 | -36.8973 | 507.0404 | -0.66 | 1.977
70455 | -490.9755 | -47.265 | 493.2453 | -0.658 | 1.318
70465 | -436.01 | -57.6675 | 439.8071 | -0.659 | 0.658
70475 | -436.1016 | -86.3779 | 444.5737 | -0.989 | 1.319
70485 | -463.3108 | -33.2591 | 464.5031 | 0.33 | 1.647
70495 | -481.9171 | 30.1404 | 482.8587 | 0.659 | 1.646
70505 | -531.7761 | 49.4985 | 534.0748 | 0.33 | 2.307
70515 | -512.7448 | 57.6662 | 515.9773 | 0.329 | 1.317
70525 | -491.7016 | 6.72 | 491.7475 | -0.659 | 1.318
70535 | -482.4028 | -53.1715 | 485.3243 | -0.989 | 1.319
70545 | -477.5408 | -72.6415 | 483.0342 | -0.658 | 1.317
70555 | -551.9466 | -178.5433 | 580.1059 | -2.306 | 2.636
70565 | -534.9822 | -206.2608 | 573.3668 | -1.318 | 1.318
70575 | -587.0495 | -175.6997 | 612.7785 | -0.659 | 2.635
70585 | -521.7666 | -41.1521 | 523.387 | 1.317 | 0.659
70595 | -461.0293 | -57.476 | 464.5982 | -0.658 | 0.659
70605 | -409.1093 | -130.0197 | 429.2733 | -1.318 | 0.33
70615 | -353.7805 | -138.7951 | 380.0326 | -0.659 | 0
70625 | -353.2594 | -233.2777 | 423.3329 | -2.306 | 0.658
70635 | -338.2947 | -330.9215 | 473.2361 | -2.636 | 0.329
70645 | -379.5149 | -414.1311 | 561.726 | -2.964 | 1.318
70655 | -413.5498 | -435.318 | 600.4374 | -2.307 | 1.319
70665 | -335.4498 | -390.0193 | 514.4333 | -1.317 | -0.33
70675 | -251.0645 | -359.6261 | 438.5936 | -1.318 | -0.659
70685 | -159.0721 | -289.7007 | 330.5003 | -0.33 | -1.317
70695 | -112.0044 | -258.4102 | 281.6395 | -0.659 | -0.989
70705 | -140.1538 | -264.4646 | 299.3069 | -0.988 | 0
70715 | -219.1497 | -232.461 | 319.4757 | -0.329 | 0.989
70725 | -291.0339 | -166.9416 | 335.5148 | 0.329 | 1.317
70735 | -335.1952 | -197.5404 | 389.0733 | -0.989 | 1.318
70745 | -304.6042 | -56.7658 | 309.8485 | 1.977 | 0.329
70755 | -315.5858 | 83.4789 | 326.4401 | 2.307 | 0.989
70765 | -350.9779 | 171.0413 | 390.4364 | 2.306 | 1.317
70775 | -317.8746 | 326.6492 | 455.7894 | 3.953 | 0.33
70785 | -249.1072 | 409.0468 | 478.9297 | 3.295 | -0.33
70795 | -221.3205 | 382.833 | 442.2034 | 1.976 | 0
70805 | -207.5283 | 364.8067 | 419.7046 | 1.977 | 0
70815 | -196.25 | 268.6725 | 332.7146 | 0.329 | 0
70825 | -167.8833 | 25.8818 | 169.8666 | -2.635 | -0.329
70835 | -260.1754 | -148.2218 | 299.4344 | -2.636 | 1.647
70845 | -278.25 | -406.2664 | 492.418 | -5.272 | 0.659
70855 | -332.8162 | -618.6505 | 702.4921 | -5.6 | 1.647
70865 | -302.4181 | -778.8606 | 835.5122 | -5.93 | 0.33
70875 | -250.6943 | -722.3385 | 764.6048 | -2.965 | 0
70885 | -218.8555 | -595.6437 | 634.5779 | -1.647 | 0
70895 | -141.7694 | -580.1049 | 597.1769 | -2.636 | -0.988
70905 | -140.1606 | -648.5168 | 663.4901 | -3.624 | 0
70915 | -148.3377 | -723.4185 | 738.4703 | -3.954 | 0
70925 | -187.0362 | -623.0698 | 650.5371 | -1.317 | 0.658
70935 | -177.1331 | -425.053 | 460.4847 | 0.659 | 0
70945 | -104.4305 | -196.0062 | 222.0904 | 2.306 | -0.988
70955 | -88.285 | -2.4843 | 88.32 | 2.965 | -0.329
70965 | -123.2331 | 49.8018 | 132.9158 | 1.648 | 0.329
70975 | -109.3099 | 38.4763 | 115.8839 | 0.987 | -0.329
70985 | -206.2353 | 37.1422 | 209.5532 | 0.989 | 1.647
70995 | -286.3145 | 83.808 | 298.3283 | 1.648 | 1.647
71005 | -409.5244 | 29.1932 | 410.5636 | 0 | 2.965
71015 | -444.1487 | 2.0274 | 444.1533 | 0.329 | 1.977
71025 | -380.9279 | -62.0121 | 385.9425 | -0.66 | 0.658
71035 | -335.6885 | -71.4272 | 343.2034 | 0 | 0.66
71045 | -275.1217 | -87.1147 | 288.5843 | -0.329 | 0
71055 | -155.3022 | -62.9263 | 167.5664 | 0.329 | -1.318
71065 | 8.355 | -136.6953 | 136.9504 | -1.317 | -2.635
71075 | 162.0309 | -219.2222 | 272.6029 | -1.647 | -3.295
71085 | 209.9026 | -309.6647 | 374.1006 | -2.306 | -2.306
71095 | 121.9166 | -489.6429 | 504.5927 | -4.284 | -0.33
71105 | -18.5519 | -605.0616 | 605.346 | -3.953 | 0.989
71115 | -166.6503 | -580.7112 | 604.1505 | -2.306 | 1.976
71125 | -168.1773 | -443.5381 | 474.3518 | -0.329 | 0.329
71135 | -210.5339 | -330.4272 | 391.7992 | 0 | 1.319
71145 | -252.8196 | -187.6795 | 314.8671 | 1.318 | 1.318
71155 | -299.1186 | -163.2373 | 340.7615 | 0 | 1.647
71165 | -391.824 | -314.4338 | 502.3889 | -2.636 | 2.635
71175 | -462.2613 | -332.3757 | 569.3497 | -0.988 | 2.635
71185 | -297.5761 | -282.8456 | 410.5523 | -0.33 | -0.987
71195 | -164.3648 | -57.8627 | 174.2524 | 2.965 | -0.989
71205 | -14.2518 | 132.5098 | 133.274 | 3.295 | -2.306
71215 | 36.3741 | 117.0661 | 122.5869 | 0.988 | -1.318
71225 | 22.0421 | -4.1872 | 22.4362 | -0.659 | -0.659
71235 | 91.3317 | -83.4683 | 123.7273 | -0.658 | -1.976
71245 | 154.0107 | -106.2285 | 187.093 | -0.331 | -1.977
71255 | 118.4666 | -154.549 | 194.7299 | -0.988 | -0.659
71265 | 50.2604 | -288.2933 | 292.6416 | -2.636 | 0
71275 | 46.846 | -387.7506 | 390.5702 | -2.635 | -0.659
71285 | 74.1995 | -449.6813 | 455.7619 | -2.635 | -0.988
71295 | 94.6341 | -512.905 | 521.5622 | -2.966 | -0.989
71305 | 50.7159 | -638.5539 | 640.5647 | -4.282 | 0
71315 | -80.4736 | -812.7685 | 816.7427 | -5.601 | 1.648
71325 | -136.8191 | -862.8684 | 873.6483 | -4.283 | 0.988
71335 | -221.0353 | -715.747 | 749.0997 | -1.318 | 1.977
71345 | -287.7386 | -492.6611 | 570.5335 | 0.659 | 1.977
71355 | -331.5641 | -308.3596 | 452.7917 | 1.318 | 1.976
71365 | -325.5115 | -230.0853 | 398.6189 | 0.659 | 1.317
71375 | -455.106 | -242.6653 | 515.7596 | -0.33 | 3.624
71385 | -680.1252 | -329.9045 | 755.9149 | -1.647 | 5.601
71395 | -533.8787 | -198.409 | 569.5547 | 1.647 | 0.33
71405 | -395.7457 | -155.7197 | 425.2802 | 0.33 | 0.33
71415 | -404.4795 | -88.3322 | 414.0124 | 1.318 | 1.647
71425 | -233.6814 | -125.9479 | 265.4616 | -0.33 | -1.647
71435 | -15.7451 | -278.0969 | 278.5423 | -2.306 | -2.966
71445 | -6.2496 | -404.7588 | 404.807 | -2.636 | -0.658
71455 | 76.1573 | -578.7255 | 583.7149 | -4.282 | -2.306
71465 | 251.6282 | -552.4645 | 607.0699 | -1.648 | -3.955
71475 | 131.0196 | -493.8136 | 510.8993 | -1.318 | 0.331
71485 | -0.48083 | -311.6349 | 311.6352 | 1.318 | 0.658
71495 | -320.3529 | -195.4481 | 375.2678 | 0.988 | 4.942
71505 | -463.3704 | -149.9957 | 487.043 | 0.66 | 3.294
71515 | -513.1356 | -158.7814 | 537.1403 | 0 | 2.966
71525 | -572.0249 | -338.2144 | 664.531 | -2.966 | 3.294
71535 | -448.8705 | -589.5036 | 740.9448 | -4.941 | 0.33
71545 | -465.5078 | -586.9818 | 749.1629 | -1.977 | 2.306
71555 | -602.6879 | -480.7285 | 770.9296 | -0.659 | 3.953
71565 | -550.4294 | -298.7867 | 626.2954 | 1.318 | 1.318
71575 | -416.5482 | -172.0089 | 450.6656 | 1.318 | 0
71585 | -426.1164 | 96.444 | 436.8943 | 4.612 | 1.647
71595 | -529.6001 | 282.1602 | 600.0755 | 4.283 | 2.965
71605 | -700.3941 | 320.5002 | 770.2416 | 2.965 | 4.613
71615 | -688.3029 | 306.1783 | 753.33 | 2.306 | 2.306
71625 | -621.89 | 305.9047 | 693.0547 | 2.306 | 1.647
71635 | -431.0318 | 182.728 | 468.1644 | 0 | -0.989
71645 | -406.5344 | -81.9188 | 414.7058 | -2.965 | 0.989
71655 | -511.802 | -305.6156 | 596.1059 | -3.624 | 2.635
71665 | -491.6443 | -543.0924 | 732.5732 | -5.271 | 0.989
71675 | -420.6937 | -559.2845 | 699.8445 | -2.635 | 0.329
71685 | -393.2483 | -358.8222 | 532.351 | 0.658 | 0.659
71695 | -457.2969 | -217.1015 | 506.2149 | 0.659 | 1.978
71705 | -392.9393 | -44.6104 | 395.4635 | 2.307 | 0
71715 | -272.5048 | 2.4255 | 272.5156 | 0.988 | -0.989
71725 | -248.5976 | -95.7461 | 266.3983 | -0.988 | 0
71735 | -300.3552 | -341.6205 | 454.8822 | -3.954 | 0.989
71745 | -413.4336 | -555.9025 | 692.7878 | -4.612 | 2.305
71755 | -377.4224 | -596.8442 | 706.1662 | -2.966 | 0.33
71765 | -160.1471 | -439.6409 | 467.9008 | 0 | -2.635
71775 | -76.6067 | -228.2922 | 240.8027 | 1.648 | -1.319
71785 | 171.031 | -148.683 | 226.6235 | 0.659 | -4.942
71795 | 331.8039 | -149.6517 | 363.991 | 0 | -4.282
71805 | 428.2638 | -208.5233 | 476.3317 | -0.989 | -4.283
71815 | 406.3819 | -326.8256 | 521.499 | -2.306 | -2.636
71825 | 428.2777 | -429.2561 | 606.3683 | -2.636 | -3.295
71835 | 520.7832 | -418.0921 | 667.8444 | -1.317 | -4.282
71845 | 404.4365 | -362.8136 | 543.3255 | -0.66 | -0.988
71855 | 172.303 | -270.4539 | 320.6769 | 0.331 | 1.317
71865 | 95.1465 | -360.2247 | 372.5784 | -2.307 | 0
71875 | 162.3736 | -405.5952 | 436.8897 | -1.648 | -1.648
71885 | 100.8055 | -460.7316 | 471.6305 | -2.305 | 0.331
71895 | 96.5183 | -620.2287 | 627.6938 | -4.283 | -0.66
71905 | 30.2955 | -452.9268 | 453.9388 | 0.659 | 0.66
71915 | -314.7229 | -435.5772 | 537.3807 | -1.648 | 5.6
71925 | -443.3397 | -422.3654 | 612.3256 | -0.988 | 3.294
71935 | -440.2218 | -442.4557 | 624.1493 | -1.647 | 2.307
71945 | -328.425 | -270.9717 | 425.78 | 1.647 | 0.329
71955 | -250.9389 | 80.804 | 263.6278 | 5.272 | 0.33
71965 | -250.7049 | 100.9463 | 270.2649 | 1.317 | 0.987
71975 | -336.467 | -78.125 | 345.4179 | -1.317 | 2.307
71985 | -345.3679 | -274.5973 | 441.2286 | -2.636 | 1.318
71995 | -456.379 | -130.1938 | 474.5864 | 1.976 | 3.294
72005 | -358.4804 | -68.8127 | 365.0252 | 0.66 | 0
72015 | -188.6484 | 62.5346 | 198.743 | 2.635 | -1.318
72025 | -194.9042 | 207.8428 | 284.9321 | 3.295 | 0.66
72035 | -470.1919 | 94.9813 | 479.6894 | -0.33 | 4.941
72045 | -544.1366 | 168.0163 | 569.4858 | 2.636 | 2.636
72055 | -388.8916 | 352.3218 | 524.7546 | 4.282 | -0.329
72065 | -177.4768 | 310.0028 | 357.2111 | 1.318 | -1.977
72075 | 57.2422 | 143.2563 | 154.2694 | -0.658 | -3.624
72085 | 276.4344 | -5.4046 | 276.4872 | -1.318 | -4.613
72095 | 465.5036 | -212.7106 | 511.8002 | -3.295 | -5.271
72105 | 695.602 | -380.7436 | 792.9867 | -3.624 | -6.918
72115 | 618.6335 | -471.0882 | 777.5805 | -3.294 | -2.636
72125 | 464.554 | -532.2021 | 706.4344 | -3.295 | -1.317
72135 | 532.0857 | -369.2778 | 647.6738 | 0.33 | -3.955
72145 | 553.9261 | -317.922 | 638.6772 | -0.989 | -2.964
72155 | 597.6197 | -599.8245 | 846.7224 | -5.93 | -3.624
72165 | 332.7243 | -728.241 | 800.65 | -4.283 | 1.647
72175 | 159.2193 | -979.9853 | 992.8353 | -7.577 | 0.988
72185 | 147.0755 | -721.528 | 736.3653 | 0.329 | -0.329
72195 | 33.1007 | -219.4603 | 221.9425 | 4.942 | 1.647
72205 | -160.431 | -211.7583 | 265.6684 | -0.659 | 3.295
72215 | -67.5778 | -153.6979 | 167.8982 | 1.318 | -0.66
72225 | 83.0728 | -194.7771 | 211.7527 | -0.659 | -1.646
72235 | 172.9272 | 70.0354 | 186.5712 | 4.612 | -1.647
72245 | 263.9408 | 430.5003 | 504.9706 | 6.919 | -2.307
72255 | 290.6661 | 578.9808 | 647.8469 | 5.271 | -1.647
72265 | 322.4331 | 722.1966 | 790.9052 | 6.26 | -1.976
72275 | 485.6445 | 438.2643 | 654.1607 | -0.659 | -4.284
72285 | 1151.8579 | 534.5898 | 1269.8673 | 4.941 | -13.507
72295 | 1353.386 | 444.5125 | 1424.5158 | 0.989 | -8.236
72305 | 1041.2754 | 115.243 | 1047.6332 | -2.965 | -1.647
72315 | 795.8506 | -115.7505 | 804.2241 | -2.965 | -1.319
72325 | 918.6585 | -425.3655 | 1012.3583 | -5.93 | -5.6
72335 | 967.8037 | -424.2364 | 1056.7027 | -1.977 | -4.283
72345 | 1077.5796 | -467.3995 | 1174.5808 | -3.294 | -5.93
72355 | 1036.965 | -412.1884 | 1115.8834 | -1.318 | -3.624
72365 | 667.0556 | -384.9777 | 770.176 | -1.648 | 1.977
72375 | 604.1147 | -401.6726 | 725.4623 | -1.976 | -1.648
72385 | 535.4241 | -304.5228 | 615.9652 | 0 | -0.329
72395 | 391.5857 | -285.4078 | 484.5586 | -0.988 | 0.988
72405 | 152.2203 | -481.7352 | 505.2127 | -4.284 | 3.295
72415 | 53.6491 | -828.0286 | 829.7647 | -7.577 | 1.976
72425 | -115.0905 | -708.9746 | 718.2554 | -1.317 | 3.954
72435 | -215.5477 | -557.5188 | 597.7358 | -0.989 | 3.295
72445 | -88.2213 | -309.5265 | 321.8535 | 1.977 | 0
72455 | 86.4303 | 176.4503 | 196.4813 | 7.248 | -1.319
72465 | 249.8739 | 585.3429 | 636.4458 | 8.235 | -2.306
72475 | 547.2755 | 581.9311 | 798.8456 | 3.625 | -5.6
72485 | 668.6253 | 378.6639 | 768.4049 | 0.659 | -3.954
72495 | 804.9896 | 39.5755 | 805.9618 | -2.965 | -5.271
72505 | 724.0505 | 2.0919 | 724.0536 | 0.329 | -1.977
72515 | 476.2019 | 39.9973 | 477.8786 | 0.659 | 0.988
72525 | 306.9857 | 135.3432 | 335.4966 | 1.977 | 0.989
72535 | 228.597 | 148.6315 | 272.6681 | 0.988 | 0.659
72545 | 314.0799 | 88.6732 | 326.3573 | 0 | -1.648
72555 | 307.2398 | 430.6778 | 529.0366 | 6.589 | -0.329
72565 | 70.3973 | 732.5642 | 735.9389 | 6.918 | 3.295
72575 | -35.7355 | 783.1221 | 783.937 | 4.613 | 1.976
72585 | 220.6267 | 785.1665 | 815.575 | 4.283 | -3.294
72595 | 345.4159 | 264.522 | 435.0678 | -4.942 | -1.977
72605 | 434.4325 | -388.6497 | 582.9067 | -9.224 | -2.635
72615 | 97.1851 | -799.534 | 805.4188 | -8.896 | 4.282
72625 | 108.8277 | -1076.777 | 1082.2625 | -9.224 | -0.658
72635 | 388.7914 | -988.9964 | 1062.6724 | -4.283 | -4.284
72645 | 469.8939 | -546.0334 | 720.3838 | 1.977 | -2.306
72655 | 244.3173 | -239.3751 | 342.04 | 1.976 | 1.977
72665 | 338.6065 | -147.0413 | 369.1552 | 0.659 | -2.635
72675 | 837.2767 | -178.1644 | 856.0227 | -0.659 | -9.225
72685 | 1300.8684 | -87.7304 | 1303.8233 | 1.317 | -10.872
72695 | 1448.2302 | 532.798 | 1543.1281 | 10.543 | -8.236
72705 | 1337.8663 | 780.641 | 1548.963 | 6.59 | -4.942
72715 | 1590.772 | 852.2259 | 1804.6729 | 5.93 | -10.543
72725 | 1655.5686 | 745.3563 | 1815.6165 | 2.964 | -7.577
72735 | 1422.7694 | 440.0206 | 1489.2585 | -0.988 | -3.294
72745 | 1219.8885 | 153.8644 | 1229.5536 | -2.306 | -2.636
72755 | 1260.9181 | 72.1044 | 1262.9781 | -0.659 | -5.272
72765 | 1510.7467 | -154.4388 | 1518.6201 | -3.953 | -8.565
72775 | 1774.0254 | -414.288 | 1821.7576 | -5.272 | -9.883
72785 | 1395.2672 | -226.0349 | 1413.4576 | 0.989 | -0.33
72795 | 1113.3194 | 136.1999 | 1121.6196 | 4.283 | -0.988
72805 | 836.5258 | -68.6154 | 839.3351 | -3.295 | 1.318
72815 | 504.1485 | -354.8028 | 616.4825 | -4.612 | 3.623
72825 | 616.3734 | -203.99 | 649.252 | 0.988 | -2.306
72835 | 621.165 | 461.4479 | 773.8088 | 9.884 | -0.329
72845 | 273.6642 | 506.2845 | 575.5138 | 2.306 | 4.942
72855 | 423.3377 | 390.97 | 576.2572 | 1.318 | -2.307
72865 | 491.9541 | 644.8721 | 811.0973 | 6.589 | -0.659
72875 | -44.1919 | 598.0627 | 599.6932 | 1.976 | 8.567
72885 | -338.564 | -15.7035 | 338.928 | -7.248 | 6.259
72895 | -435.7614 | -48.9745 | 438.5048 | 0 | 5.271
72905 | -357.5024 | 268.4635 | 447.0801 | 4.284 | 2.635
72915 | -325.0141 | 44.6634 | 328.0686 | -3.295 | 2.966
72925 | -22.5271 | 222.9161 | 224.0515 | 3.624 | -2.306
72935 | 418.2394 | 339.9673 | 538.9823 | 2.306 | -5.931
72945 | 694.2576 | 328.8018 | 768.1824 | 1.318 | -5.601
72955 | 572.4942 | 183.342 | 601.1355 | -0.989 | -0.658
72965 | 190.9857 | -116.4518 | 223.6885 | -4.282 | 3.953
72975 | 118.6088 | 34.0684 | 123.4046 | 1.976 | 0.66
72985 | 153.6444 | 325.7118 | 360.1316 | 4.283 | 0
72995 | 400.6752 | 436.3983 | 592.4391 | 2.965 | -3.955
73005 | 818.4236 | 585.9472 | 1006.5542 | 4.612 | -7.906
73015 | 957.5475 | 743.4581 | 1212.2818 | 5.272 | -5.272
73025 | 769.8939 | 815.4742 | 1121.4878 | 4.613 | -0.987
73035 | 610.1291 | 498.1773 | 787.6789 | -1.648 | -0.659
73045 | 390.6328 | 173.8342 | 427.5656 | -2.965 | 1.646
73055 | 195.7368 | -158.8875 | 252.1074 | -5.272 | 2.307
73065 | 203.8348 | -486.9107 | 527.8548 | -6.918 | 0
73075 | 475.7902 | -542.151 | 721.321 | -3.954 | -4.283
73085 | 772.2995 | -253.6805 | 812.8962 | 1.318 | -5.93
73095 | 752.6152 | -409.8252 | 856.9634 | -4.941 | -2.306
73105 | 496.2314 | -436.2204 | 660.7071 | -2.307 | 1.318
73115 | 373.0472 | -287.0763 | 470.7197 | 0 | 0.329
73125 | 430.4838 | -261.0797 | 503.4669 | -1.317 | -1.647
73135 | 384.8496 | 212.7198 | 439.726 | 6.918 | 0
73145 | 583.0768 | 763.3795 | 960.5867 | 9.884 | -4.283
73155 | 961.8432 | 1221.7612 | 1554.9415 | 11.531 | -7.907
73165 | 1226.9796 | 1189.5117 | 1708.9227 | 5.6 | -7.907
73175 | 1201.8731 | 922.2031 | 1514.9117 | 1.977 | -4.612
73185 | 1380.0299 | 602.1311 | 1505.6707 | -0.659 | -8.237
73195 | 1413.5911 | 609.9381 | 1539.5662 | 2.965 | -5.93
73205 | 1072.5866 | 564.3338 | 1211.9879 | 1.318 | 0
73215 | 991.7729 | 436.3669 | 1083.5265 | 0 | -2.964
73225 | 835.2022 | 328.2054 | 897.3748 | -0.329 | -0.33
73235 | 571.7429 | 105.2813 | 581.3554 | -2.966 | 1.976
73245 | 425.6309 | -101.0593 | 437.4639 | -3.624 | 1.318
73255 | 357.9956 | -161.1322 | 392.5868 | -2.306 | 0.989
73265 | 557.7645 | -137.1678 | 574.3834 | -1.318 | -3.295
73275 | 867.9613 | -164.6853 | 883.4467 | -1.976 | -5.93
73285 | 1093.2614 | -84.2052 | 1096.4994 | 0 | -6.26
73295 | 946.3556 | -1.2449 | 946.3564 | 0.329 | -1.317
73305 | 986.8921 | -31.9434 | 987.4089 | -0.988 | -4.284
73315 | 1039.0882 | -297.7075 | 1080.8951 | -4.942 | -3.953
73325 | 1028.7136 | -425.0282 | 1113.0591 | -3.624 | -3.295
73335 | 713.3586 | -201.4123 | 741.2472 | 1.318 | 1.978
73345 | 431.4743 | -159.7586 | 460.101 | -0.989 | 2.635
73355 | 373.2898 | -268.4828 | 459.8134 | -2.635 | 0.659
73365 | 772.2215 | -292.5604 | 825.7831 | -1.647 | -6.589
73375 | 963.5792 | -355.1543 | 1026.9467 | -2.636 | -4.613
73385 | 719.8667 | -371.8269 | 810.2242 | -1.976 | 0.989
73395 | 559.6829 | -244.3612 | 610.7024 | 0.329 | 0.33
73405 | 441.4884 | -90.7142 | 450.7117 | 1.317 | 0.988
73415 | 414.2861 | -164.9683 | 445.9232 | -1.646 | 0
73425 | 498.0822 | -299.0801 | 580.9774 | -2.636 | -1.647
73435 | 500.6393 | -135.6676 | 518.6958 | 1.647 | -0.66
73445 | 331.1751 | 181.6974 | 377.7444 | 4.612 | 1.977
73455 | 448.5339 | 361.5535 | 576.1107 | 3.954 | -2.306
73465 | 411.1988 | 447.8949 | 608.0249 | 3.624 | 0.329
73475 | 714.5714 | 510.391 | 878.1294 | 3.623 | -5.93
73485 | 622.6413 | 600.1971 | 864.8229 | 4.284 | 0
73495 | 553.8359 | 577.5316 | 800.1731 | 2.635 | -0.987
73505 | 670.0379 | 518.0424 | 846.9467 | 1.977 | -3.295
73515 | 648.7785 | 448.4712 | 788.6951 | 1.318 | -1.318
73525 | 689.1902 | 348.6939 | 772.3798 | 0.329 | -2.635
73535 | 656.2417 | 397.0678 | 767.0176 | 2.306 | -1.318
73545 | 679.4903 | 200.2443 | 708.3818 | -1.977 | -2.306
73555 | 611.6288 | 70.6015 | 615.6901 | -1.317 | -0.66
73565 | 378.9944 | 118.6399 | 397.1299 | 0.659 | 2.307
73575 | 149.98 | 123.9443 | 194.5666 | 0 | 3.294
73585 | 287.0775 | 247.1866 | 378.8333 | 2.306 | -1.647
73595 | 548.9501 | 441.9481 | 704.7442 | 3.953 | -3.954
73605 | 506.4805 | 575.6177 | 766.7192 | 3.953 | -0.329
73615 | 438.8344 | 621.9156 | 761.1535 | 3.295 | -0.33
73625 | 732.0031 | 498.2943 | 885.5088 | 0.66 | -5.929
73635 | 855.1026 | 558.1015 | 1021.1159 | 3.293 | -3.954
73645 | 673.84 | 266.918 | 724.7797 | -2.964 | 0
73655 | 436.4558 | 213.7615 | 485.9914 | 0.329 | 1.648
73665 | 341.8613 | 244.0935 | 420.0605 | 0.659 | 0.658
73675 | -33.0434 | 25.2507 | 41.5868 | -3.295 | 6.259
73685 | -618.7916 | -96.8245 | 626.3211 | -2.306 | 11.202
73695 | 638.1397 | -833.2612 | 1049.5458 | -13.837 | -17.461
73705 | 2464.0828 | -610.3989 | 2538.5608 | 0 | -30.638
73715 | 1541.3975 | -215.1253 | 1556.3371 | 1.977 | 5.929
73725 | 1670.9045 | -437.2773 | 1727.1749 | -5.601 | -12.19
73735 | 1308.6427 | 298.2738 | 1342.2046 | 10.873 | 0.33
73745 | 885.5277 | 546.5608 | 1040.619 | 4.282 | 1.318
73755 | 953.629 | 204.9715 | 975.4084 | -2.635 | -3.954
73765 | 1049.7121 | 65.2895 | 1051.7405 | -0.66 | -3.953
73775 | 980.4896 | 116.2844 | 987.3611 | 0.989 | -1.977
73785 | -196.8042 | 526.21 | 561.8085 | 7.248 | 17.132
73795 | -1020.4078 | 667.3369 | 1219.25 | 4.283 | 15.484
73805 | -671.9611 | 816.3263 | 1057.3175 | 5.93 | 1.318
73815 | 759.0143 | 424.4722 | 869.6432 | -2.965 | -17.791
73825 | 1472.31 | -244.1316 | 1492.4131 | -8.895 | -12.519
73835 | -325.924 | -581.622 | 666.7163 | -6.919 | 24.38
73845 | -3143.7677 | 132.9459 | 3146.5776 | 8.566 | 47.77
73855 | -2238.2079 | 344.1972 | 2264.519 | 2.306 | -0.659
73865 | -1152.3084 | 471.8257 | 1245.1643 | 3.953 | -1.647
73875 | -31.9658 | 642.8375 | 643.6318 | 4.943 | -11.86
73885 | -49.7014 | 899.4454 | 900.8176 | 7.248 | 1.647
73895 | -360.8223 | 937.0447 | 1004.1142 | 4.612 | 4.283
73905 | -442.8715 | 1058.8516 | 1147.7377 | 6.589 | 2.635
73915 | -1004.9431 | 808.7004 | 1289.9252 | 0.329 | 11.861
73925 | -1337.5422 | 677.2033 | 1499.2076 | 1.648 | 9.883
73935 | -693.442 | 705.7418 | 989.4106 | 2.964 | -4.282
73945 | -559.9292 | 775.2126 | 956.282 | 3.624 | 2.306
73955 | -446.3611 | 881.6954 | 988.2434 | 4.613 | 0
73965 | 25.1333 | 882.979 | 883.3366 | 3.294 | -6.26
73975 | -638.6464 | 816.6905 | 1036.751 | 2.307 | 11.202
73985 | -979.3851 | 812.3604 | 1272.4483 | 2.964 | 6.918
73995 | -402.7897 | 745.4509 | 847.3114 | 1.648 | -5.271
74005 | 366.1441 | 884.2476 | 957.0556 | 4.942 | -10.543
74015 | -14.1519 | 834.6366 | 834.7566 | 1.976 | 4.612
74025 | -129.1329 | 751.6539 | 762.6657 | 1.648 | 0
74035 | -649.7435 | 763.3556 | 1002.4362 | 2.635 | 9.225
74045 | -1358.7193 | 186.7784 | 1371.4971 | -7.577 | 14.167
74055 | -1281.2738 | 185.1889 | 1294.5878 | 0.329 | 4.612
74065 | -976.3742 | -71.2498 | 978.9704 | -5.601 | 1.647
74075 | -529.3536 | -317.7468 | 617.3964 | -5.6 | -2.965
74085 | -549.8963 | -262.4598 | 609.3202 | -1.977 | 2.636
74095 | -838.5352 | -151.0981 | 852.0399 | -0.988 | 6.259
74105 | -1078.2051 | -113.525 | 1084.1652 | -1.318 | 6.919
74115 | -1094.7921 | -239.9463 | 1120.7783 | -3.624 | 4.613
74125 | -821.1163 | -251.5662 | 858.7884 | -1.977 | 0
74135 | -485.0497 | -302.8304 | 571.8212 | -2.965 | -2.307
74145 | -227.6781 | -471.0144 | 523.1557 | -4.941 | -2.965
74155 | -253.0387 | -601.5716 | 652.6232 | -4.942 | 0.329
74165 | 457.0403 | -304.5964 | 549.2402 | 1.647 | -12.519
74175 | 794.6702 | -277.2022 | 841.6304 | -1.977 | -8.236
74185 | 994.4856 | -142.9744 | 1004.7105 | 0.988 | -8.895
74195 | 661.3113 | -25.0593 | 661.7859 | 0.989 | -0.33
74205 | 260.8684 | -187.8306 | 321.4539 | -2.966 | 1.977
74215 | 177.9549 | -114.7258 | 211.7308 | 0.66 | -0.659
74225 | -182.7279 | -428.6808 | 466.0008 | -6.26 | 5.271
74235 | -433.6128 | -739.6359 | 857.3688 | -6.918 | 4.613
74245 | -289.2672 | -662.9287 | 723.2911 | -2.307 | -0.33
74255 | 221.9987 | -772.2813 | 803.5557 | -5.601 | -6.918
74265 | 626.7249 | -721.5204 | 955.7069 | -2.635 | -7.578
74275 | 376.3718 | -645.5138 | 747.224 | -2.306 | 0.988
74285 | -120.9501 | -532.7637 | 546.3205 | -0.989 | 5.601
74295 | -352.3035 | -590.4696 | 687.5842 | -3.294 | 3.954
74305 | -241.4632 | -750.7707 | 788.6451 | -4.942 | 0
74315 | -203.4988 | -768.9605 | 795.432 | -3.294 | 0.988
74325 | -263.1694 | -996.8437 | 1030.9973 | -7.248 | 1.977
74335 | -331.6675 | -1246.1348 | 1289.5174 | -8.236 | 2.306
74345 | -263.9528 | -1106.0615 | 1137.1205 | -2.966 | 0.33
74355 | 24.7017 | -959.1952 | 959.5132 | -2.635 | -3.624
74365 | 179.2352 | -867.6935 | 886.012 | -2.307 | -2.636
74375 | 241.2051 | -814.4017 | 849.3703 | -2.306 | -2.306
74385 | 362.6078 | -592.0658 | 694.2812 | 0.989 | -3.624
74395 | 172.1135 | -306.1852 | 351.2441 | 2.965 | 1.318
74405 | -162.5118 | 22.553 | 164.0692 | 5.271 | 4.282
74415 | -193.7493 | 216.6079 | 290.6162 | 4.613 | 0.989
74425 | -4.453 | 129.4565 | 129.533 | 0.988 | -1.977
74435 | 149.7672 | 96.1664 | 177.9837 | 1.647 | -2.306
74445 | -27.6328 | 122.613 | 125.6882 | 1.977 | 2.306
74455 | -393.1124 | 247.063 | 464.3033 | 3.624 | 5.93
74465 | -742.8071 | 175.4015 | 763.2353 | 0.658 | 7.578
74475 | -457.7376 | 107.067 | 470.0926 | 0.66 | -1.318
74485 | -298.6812 | 193.235 | 355.739 | 2.635 | 0.329
74495 | -340.0507 | 117.8346 | 359.8881 | 0 | 1.977
74505 | -266.8027 | 256.9227 | 370.3956 | 3.624 | 0
74515 | -276.257 | 465.8076 | 541.5668 | 4.942 | 1.318
74525 | -88.4349 | 664.9147 | 670.7699 | 5.93 | -2.306
74535 | 47.7985 | 440.2966 | 442.8835 | -0.329 | -1.977
74545 | -86.6676 | 344.9006 | 355.623 | 1.317 | 1.648
74555 | -27.2941 | 342.4478 | 343.5338 | 1.647 | -1.319
74565 | 107.7006 | 268.1234 | 288.9456 | 0.331 | -2.306
74575 | 179.0621 | 267.7677 | 322.1223 | 1.317 | -1.976
74585 | 126.7321 | 223.5683 | 256.9899 | 0.329 | -0.33
74595 | -165.3561 | 377.2183 | 411.8692 | 3.624 | 3.954
74605 | -324.3218 | 450.4605 | 555.0669 | 2.636 | 2.964
74615 | -368.0111 | 501.6628 | 622.1718 | 2.965 | 2.306
74625 | -89.5415 | 370.8787 | 381.5347 | 0 | -2.964
74635 | -102.4668 | 207.4397 | 231.367 | -0.988 | 0.988
74645 | -334.7351 | 181.6022 | 380.824 | 0.329 | 3.953
74655 | -480.761 | 294.8593 | 563.9798 | 2.306 | 3.624
74665 | -526.7717 | 552.8638 | 763.6405 | 5.271 | 2.965
74675 | -421.9905 | 758.3608 | 867.8635 | 5.601 | 0.659
74685 | -35.4195 | 620.27 | 621.2804 | 0.989 | -4.612
74695 | 171.7583 | 516.9685 | 544.7544 | 1.317 | -3.295
74705 | 338.1397 | 434.7937 | 550.803 | 0.66 | -4.282
74715 | 656.0343 | 245.3993 | 700.4298 | -1.648 | -7.578
74725 | 359.2209 | 183.0851 | 403.187 | -0.329 | 1.648
74735 | 130.2457 | 178.1187 | 220.6586 | 0 | 0.988
74745 | -130.4982 | 305.354 | 332.0705 | 2.306 | 3.624
74755 | -375.78 | 498.7381 | 624.46 | 3.953 | 4.613
74765 | -384.1747 | 514.7758 | 642.3273 | 1.977 | 1.976
74775 | -159.4122 | 428.424 | 457.1208 | 0.658 | -1.647
74785 | -324.7923 | 312.8153 | 450.9362 | -0.329 | 3.953
74795 | -206.6302 | 236.3473 | 313.9364 | -0.329 | -0.989
74805 | -172.2756 | 209.2802 | 271.0666 | 0 | 0.66
74815 | -390.6033 | 212.1553 | 444.5007 | 0.329 | 4.282
74825 | -310.5035 | 251.8612 | 399.808 | 0.989 | 0
74835 | -233.545 | 145.361 | 275.0874 | -1.318 | 0.33
74845 | -181.9287 | -81.1755 | 199.2172 | -3.624 | 0
74855 | -70.3687 | -147.1521 | 163.1119 | -1.977 | -1.318
74865 | 166.0215 | -20.0817 | 167.2316 | 0.659 | -3.954
74875 | 243.5397 | 227.365 | 333.1763 | 3.295 | -2.306
74885 | 200.0666 | 339.418 | 393.994 | 2.305 | -0.987
74895 | 114.3068 | 164.4833 | 200.3018 | -1.647 | 0
74905 | 3.1496 | 176.4748 | 176.5029 | 0.989 | 0.987
74915 | 179.4304 | 200.6441 | 269.1715 | 0.658 | -3.294
74925 | 123.085 | 207.0949 | 240.9112 | 0.66 | 0.329
74935 | 45.6336 | 269.3254 | 273.1641 | 1.647 | 0.33
74945 | -184.883 | 241.6137 | 304.235 | 0.33 | 3.624
74955 | -418.1923 | 191.4201 | 459.9201 | 0 | 4.612
74965 | -378.7001 | 45.3532 | 381.4062 | -1.977 | 1.318
74975 | -308.8556 | 165.8223 | 350.555 | 1.977 | 0.988
74985 | -200.3155 | 473.4695 | 514.1008 | 5.271 | -0.329
74995 | -125.4002 | 457.9355 | 474.7948 | 1.317 | -0.33
75005 | -159.7645 | 330.1197 | 366.7475 | 0 | 0.988
75015 | -193.583 | 328.5577 | 381.3457 | 1.318 | 0.989
75025 | -172.9323 | 404.13 | 439.5755 | 2.306 | 0.329
75035 | -19.5883 | 305.8038 | 306.4305 | -0.329 | -1.976
75045 | 39.4027 | 199.0383 | 202.901 | -0.659 | -0.988
75055 | 25.4521 | 135.3525 | 137.7248 | -0.659 | -0.33
75065 | -118.3654 | -39.9005 | 124.9097 | -2.965 | 1.976
75075 | -322.2799 | -175.6012 | 367.0152 | -2.965 | 3.624
75085 | -288.1434 | -146.4033 | 323.2036 | -0.988 | 0.66
75095 | -296.098 | -78.677 | 306.3725 | -0.33 | 1.647
75105 | -225.6826 | -60.7267 | 233.71 | -0.659 | 0
75115 | -32.6344 | -39.6964 | 51.3888 | -0.329 | -2.307
75125 | 28.8126 | -6.3836 | 29.5113 | 0 | -0.988
75135 | 243.8304 | 14.9924 | 244.2908 | 0 | -4.282
75145 | 225.8587 | 7.3096 | 225.9769 | -0.329 | -0.989
75155 | 625.0134 | 152.4397 | 643.3348 | 2.306 | -8.566
75165 | 617.6796 | 230.8955 | 659.4246 | 1.647 | -2.635
75175 | 839.9412 | 212.0221 | 866.2878 | 0.658 | -7.578
75185 | 1091.4471 | 137.9065 | 1100.1249 | -0.329 | -8.236
75195 | 991.0096 | 125.6691 | 998.9458 | 0.329 | -3.624
75205 | 764.5372 | 89.4119 | 769.7478 | -0.329 | -1.318
75215 | 567.499 | -17.9446 | 567.7826 | -1.647 | -0.329
75225 | 697.706 | -59.0251 | 700.1982 | -0.988 | -4.613
75235 | 517.746 | -39.6497 | 519.262 | -0.33 | 0.66
75245 | 366.0776 | -45.2184 | 368.8597 | -0.659 | 0.329
75255 | 420.5652 | -56.3097 | 424.3181 | -0.658 | -1.977
75265 | 416.6256 | -141.8448 | 440.11 | -1.977 | -0.988
75275 | 378.1369 | -229.6988 | 442.4354 | -2.307 | -0.659
75285 | 44.3161 | -192.2785 | 197.3194 | -0.658 | 4.612
75295 | 109.9196 | -214.5737 | 241.0897 | -1.648 | -0.988
75305 | -250.5622 | -34.5332 | 252.9307 | 1.977 | 6.919
75315 | -110.9919 | 16.0593 | 112.1477 | 0.329 | -0.989
75325 | 174.8112 | -72.2453 | 189.1516 | -1.317 | -2.966
75335 | 232.2331 | 72.919 | 243.4119 | 2.306 | -0.987
75345 | 11.8092 | 299.575 | 299.8077 | 3.953 | 2.964
75355 | -197.3274 | 144.4654 | 244.5574 | -1.318 | 3.624
75365 | -97.2787 | -155.5727 | 183.483 | -3.953 | -0.329
75375 | -97.2128 | -334.6236 | 348.4585 | -3.624 | 1.318
75385 | -89.2795 | -401.8737 | 411.6714 | -2.965 | 0.659
75395 | 55.8506 | -465.1495 | 468.4905 | -3.294 | -1.648
75405 | 68.8181 | -422.423 | 427.9919 | -1.648 | 0
75415 | -59.7861 | -329.854 | 335.2284 | -0.658 | 1.977
75425 | -40.0506 | -349.4072 | 351.6951 | -1.977 | 0
75435 | -178.2858 | -265.2141 | 319.569 | 0 | 2.965
75445 | -107.9756 | -231.5573 | 255.4946 | -0.66 | -0.329
75455 | -87.1142 | -260.5857 | 274.7613 | -1.317 | 0.659
75465 | -305.2123 | -168.7089 | 348.7366 | 0.659 | 4.283
75475 | -150.651 | -186.8949 | 240.0529 | -0.989 | -1.318
75485 | 311.3658 | -275.5569 | 415.7887 | -1.977 | -6.589
75495 | 368.2962 | -182.7817 | 411.1585 | 0.66 | -1.977
75505 | 256.9098 | -136.1586 | 290.7608 | 0 | -0.329
75515 | 113.2568 | -176.9121 | 210.0595 | -0.989 | 0.988
75525 | 97.4427 | -248.0689 | 266.5206 | -1.647 | -0.33
75535 | 604.3973 | -507.6183 | 789.286 | -5.271 | -8.894
75545 | 2021.4071 | -916.7091 | 2219.559 | -8.895 | -26.356
75555 | 1647.9397 | -649.3524 | 1771.2606 | 0.658 | -1.978
75565 | 1209.9793 | -336.2553 | 1255.8334 | 1.648 | -2.635
75575 | 546.2694 | -7.1092 | 546.3156 | 4.282 | 5.601
75585 | -220.7214 | 259.6846 | 340.8137 | 4.942 | 10.542
75595 | -502.7861 | 415.8596 | 652.4823 | 4.612 | 6.589
75605 | 101.15 | 118.2969 | 155.6454 | -2.306 | -6.259
75615 | 475.9137 | -254.7504 | 539.807 | -4.611 | -4.613
75625 | 308.849 | -296.0535 | 427.8264 | -1.319 | 1.318
75635 | -521.6196 | 309.396 | 606.4758 | 8.896 | 12.849
75645 | -351.3628 | 334.1626 | 484.8922 | 1.317 | -0.659
75655 | -331.0825 | 220.3883 | 397.7268 | 0.66 | 3.294
75665 | -227.5027 | 187.4158 | 294.7578 | 0.987 | 0.33
75675 | -136.9754 | 44.5053 | 144.0242 | -1.317 | 0.329
75685 | -131.2526 | 146.9882 | 197.0603 | 2.306 | 0.988
75695 | -195.2115 | 98.4585 | 218.6358 | -0.329 | 1.977
75705 | -207.1458 | 93.4618 | 227.2543 | 0.658 | 1.318
75715 | -16.8413 | 87.483 | 89.0893 | 0.33 | -1.977
75725 | -216.2098 | -151.1823 | 263.8233 | -3.624 | 3.954
75735 | -79.7034 | -280.4765 | 291.5814 | -2.635 | -1.648
75745 | 589.8691 | -442.7606 | 737.5518 | -4.283 | -10.542
75755 | 1141.4356 | -607.5352 | 1293.0484 | -4.942 | -11.531
75765 | 1257.5694 | -377.0301 | 1312.8718 | 0.988 | -7.578
75775 | 1120.1006 | -261.2085 | 1150.1544 | -0.33 | -4.282
75785 | 920.3879 | -143.9394 | 931.5752 | 0.989 | -2.306
75795 | 610.2469 | -18.3391 | 610.5224 | 1.648 | 0.988
75805 | 418.1863 | 200.1543 | 463.6179 | 3.953 | 0.659
75815 | 694.8197 | 150.7819 | 710.992 | 0.329 | -5.93
75825 | 871.1604 | -9.0163 | 871.2071 | -1.318 | -4.942
75835 | 631.9633 | -110.6223 | 641.5723 | -1.317 | 0.659
75845 | 589.1858 | -244.9197 | 638.0639 | -2.636 | -1.977
75855 | 334.6386 | -342.967 | 479.1757 | -2.635 | 2.636
75865 | -67.0646 | -136.5945 | 152.17 | 1.976 | 5.93
75875 | -230.3056 | 109.0893 | 254.8355 | 3.295 | 3.954
75885 | -240.7171 | 264.0274 | 357.2887 | 3.294 | 2.635
75895 | -176.8982 | 458.3322 | 491.2854 | 4.942 | 1.318
75905 | 531.8261 | 392.9148 | 661.2269 | 1.318 | -10.213
75915 | 1210.4723 | -22.0051 | 1210.6723 | -4.613 | -12.519
75925 | 946.0198 | -495.9919 | 1068.158 | -7.577 | -0.66
75935 | 678.7036 | -578.3335 | 891.6883 | -3.624 | -0.658
75945 | 361.9787 | -614.903 | 713.5365 | -3.954 | 2.636
75955 | 216.3833 | -163.8661 | 271.4292 | 4.613 | 1.317
75965 | 623.3287 | 171.231 | 646.4199 | 4.283 | -6.918
75975 | 969.0188 | -200.3267 | 989.5091 | -5.272 | -7.248
75985 | 672.0437 | -692.2813 | 964.8296 | -8.235 | 1.317
75995 | 276.1495 | -680.0902 | 734.0171 | -2.637 | 3.624
76005 | 376.1232 | -735.4361 | 826.0357 | -4.612 | -2.306
76015 | 517.7516 | -582.8629 | 779.6126 | -0.659 | -2.635
76025 | 265.5795 | -493.9114 | 560.786 | -1.317 | 2.965
76035 | -237.2796 | -132.7943 | 271.9116 | 4.282 | 7.906
76045 | -265.2805 | -64.5807 | 273.0282 | 0.659 | 2.307
76055 | -95.2583 | -84.0722 | 127.0523 | 0.33 | 0
76065 | 122.3469 | -142.5629 | 187.8642 | -0.659 | -1.976
76075 | 512.9137 | -316.5283 | 602.7194 | -2.965 | -6.261
76085 | 254.3375 | -231.3568 | 343.8219 | 0.659 | 2.966
76095 | 575.3042 | -388.2808 | 694.0727 | -3.624 | -6.919
76105 | 492.6185 | -825.2726 | 961.118 | -8.566 | 0
76115 | 185.3246 | -910.5452 | 929.2135 | -4.612 | 2.966
76125 | -228.0581 | -309.9344 | 384.7984 | 5.93 | 6.588
76135 | -151.8742 | 71.0717 | 167.6811 | 4.613 | 0.329
76145 | 108.1438 | 137.5271 | 174.9537 | 2.305 | -2.306
76155 | 272.8715 | -62.0148 | 279.8298 | -1.647 | -2.306
76165 | 135.5551 | -208.334 | 248.5523 | -1.647 | 1.648
76175 | -6.4549 | -207.7525 | 207.8528 | -0.33 | 1.976
76185 | 44.9761 | -173.9166 | 179.6381 | 0 | -0.329
76195 | 116.802 | -152.8259 | 192.3499 | 0 | -0.659
76205 | 252.9313 | -178.4993 | 309.5743 | -0.658 | -2.306
76215 | 179.3901 | -200.0788 | 268.7235 | -0.66 | 0.659
76225 | 121.8485 | -134.4605 | 181.4571 | 0.66 | 0.33
76235 | 0.5907 | -41.9457 | 41.9498 | 1.317 | 1.976
76245 | -131.012 | 136.0304 | 188.8609 | 3.295 | 2.635
76255 | -8.3194 | 210.6891 | 210.8533 | 2.306 | -0.987
76265 | -246.0378 | 268.9588 | 364.5181 | 2.636 | 4.941
76275 | -618.3336 | 356.8436 | 713.9144 | 3.294 | 7.577
76285 | -698.1731 | 348.8047 | 780.4552 | 1.976 | 4.613
76295 | -380.1716 | 337.9545 | 508.6685 | 1.978 | -1.318
76305 | -9.7428 | 168.4109 | 168.6925 | -0.989 | -3.624
76315 | 89.5844 | 58.5805 | 107.0375 | -0.658 | -1.318
76325 | -162.0984 | 20.636 | 163.4066 | -0.331 | 3.624
76335 | -568.3948 | -39.9039 | 569.7938 | -0.988 | 7.248
76345 | -692.6112 | 66.5423 | 695.8004 | 1.648 | 4.613
76355 | -859.9852 | 42.3449 | 861.0271 | -0.329 | 6.588
76365 | -1021.4415 | -94.5857 | 1025.8115 | -1.977 | 6.919
76375 | -1039.8457 | -115.556 | 1046.2468 | -0.66 | 5.271
76385 | -761.6733 | -18.1338 | 761.8891 | 0.989 | 0.33
76395 | -595.2968 | 72.2347 | 599.6634 | 1.317 | 0.988
76405 | -169.8195 | 69.7485 | 183.5851 | 0.331 | -4.942
76415 | -153.0272 | -190.7764 | 244.5668 | -3.954 | 0.33
76425 | 88.3885 | -257.3662 | 272.1211 | -1.647 | -4.612
76435 | 230.8257 | -289.2947 | 370.0972 | -1.977 | -3.295
76445 | 269.3298 | -226.6801 | 352.0261 | -0.33 | -2.636
76455 | 225.0017 | -214.8668 | 311.1165 | -0.988 | -1.317
76465 | 140.0236 | -278.8102 | 311.9964 | -1.977 | -0.33
76475 | 146.5858 | -406.3807 | 432.0101 | -3.294 | -1.318
76485 | -4.9506 | -519.1511 | 519.1747 | -3.624 | 1.648
76495 | -568.9463 | -633.7096 | 851.6383 | -4.283 | 9.224
76505 | -508.8581 | -430.1107 | 666.2821 | 0.659 | 0.988
76515 | -325.9958 | -376.8782 | 498.3076 | -1.318 | 0
76525 | -191.6285 | -416.711 | 458.6606 | -1.977 | -0.658
76535 | -89.8538 | -349.6413 | 361.0024 | -0.329 | -0.989
76545 | 167.6287 | -253.0727 | 303.5542 | 0.329 | -4.283
76555 | 190.2053 | -459.4419 | 497.2574 | -4.283 | -1.318
76565 | -478.0634 | -691.8902 | 840.9855 | -5.271 | 9.884
76575 | -800.0924 | -474.0745 | 929.997 | 0.989 | 6.589
76585 | -392.5147 | -204.2572 | 442.4803 | 2.306 | -2.965
76595 | 127.7854 | -136.2209 | 186.7759 | 0.658 | -6.26
76605 | 553.4339 | -398.6019 | 682.0356 | -4.282 | -7.906
76615 | 738.4112 | -679.3766 | 1003.396 | -5.601 | -6.26
76625 | 562.6794 | -780.1715 | 961.9125 | -4.283 | -1.318
76635 | 504.2735 | -872.4432 | 1007.6948 | -4.942 | -2.636
76645 | 716.991 | -737.7323 | 1028.7493 | -1.317 | -6.259
76655 | 1122.9584 | -646.0352 | 1295.5297 | -1.647 | -10.213
76665 | 1437.8199 | -836.9589 | 1663.6785 | -5.601 | -10.543
76675 | 1493.1322 | -844.0927 | 1715.2073 | -2.965 | -7.906
76685 | 966.9255 | -819.2781 | 1267.3443 | -2.966 | 1.647
76695 | 533.642 | -815.0347 | 974.1947 | -2.964 | 2.306
76705 | 440.6185 | -740.7725 | 861.9099 | -1.648 | -0.329
76715 | 753.6566 | -493.0462 | 900.6069 | 1.648 | -6.26
76725 | 899.4528 | -656.5254 | 1113.5712 | -4.283 | -4.612
76735 | 769.5469 | -1263.5954 | 1479.485 | -11.861 | -1.318
76745 | 280.506 | -1185.5591 | 1218.2914 | -2.964 | 5.271
76755 | 305.5742 | -985.9875 | 1032.2533 | -1.977 | -1.318
76765 | 510.1104 | -882.5951 | 1019.4051 | -1.977 | -3.294
76775 | 444.083 | -712.0116 | 839.1485 | 0 | 0
76785 | 478.565 | -799.1367 | 931.4741 | -3.624 | -1.977
76795 | 160.433 | -737.8239 | 755.0648 | -0.989 | 4.283
76805 | 183.6618 | -953.0456 | 970.581 | -5.929 | -0.659
76815 | 254.4813 | -891.1024 | 926.7276 | -1.648 | -0.659
76825 | 416.7214 | -591.3385 | 723.421 | 1.977 | -2.965
76835 | 286.7525 | -283.9131 | 403.5265 | 3.624 | 1.318
76845 | 81.7945 | -61.3921 | 102.2709 | 3.953 | 2.636
76855 | 64.2142 | 164.1445 | 176.258 | 5.272 | 0.658
76865 | 166.6722 | 216.2448 | 273.0228 | 3.294 | -0.988
76875 | -70.925 | -25.5571 | 75.3891 | -1.318 | 4.283
76885 | 9.5515 | -182.7238 | 182.9733 | -0.989 | -0.659
76895 | -20.9675 | 222.0659 | 223.0536 | 7.248 | 1.647
76905 | 113.7388 | 616.9315 | 627.3285 | 8.237 | -1.647
76915 | 230.4185 | 730.0813 | 765.5792 | 5.93 | -1.648
76925 | 121.8857 | 273.9275 | 299.8206 | -2.965 | 1.318
76935 | -146.9745 | -112.8878 | 185.3244 | -3.624 | 4.283
76945 | 545.9853 | -332.8795 | 639.4597 | -3.624 | -10.871
76955 | 1398.8397 | -240.1979 | 1419.3124 | 0.33 | -15.485
76965 | 1566.3766 | -113.3219 | 1570.4705 | 0.988 | -8.895
76975 | 1503.9758 | -176.7 | 1514.3203 | -1.318 | -6.918
76985 | 1296.3288 | -69.316 | 1298.1807 | 1.647 | -3.624
76995 | 797.4338 | -295.4871 | 850.4194 | -3.953 | 2.635
77005 | 599.411 | -362.8876 | 700.7003 | -1.648 | 0
77015 | 536.2706 | -65.3862 | 540.2421 | 3.624 | -0.329
77025 | 316.7542 | 221.2574 | 386.3782 | 4.613 | 2.636
77035 | 123.979 | 303.586 | 327.9257 | 2.965 | 2.964
77045 | 170.8942 | 536.6349 | 563.189 | 6.26 | 0
77055 | 334.3609 | 536.5267 | 632.1852 | 2.965 | -1.976
77065 | 209.7325 | 375.6341 | 430.2194 | 0.659 | 1.976
77075 | 256.9716 | 194.4504 | 322.2504 | -0.659 | -0.988
77085 | 358.2397 | 138.2804 | 384.0015 | 0.329 | -1.647
77095 | 207.0864 | 59.9353 | 215.5853 | -0.659 | 1.977
77105 | 74.1856 | 17.7142 | 76.2712 | -0.329 | 1.976
77115 | -23.2664 | -5.3748 | 23.8792 | -0.329 | 2.306
77125 | -112.281 | 92.3529 | 145.3825 | 1.647 | 2.636
77135 | -178.2 | 247.4074 | 304.9027 | 2.965 | 2.636
77145 | -304.1483 | 410.6305 | 511.0025 | 3.953 | 3.953
77155 | -443.295 | 407.6634 | 602.2457 | 1.976 | 4.613
77165 | -294.1999 | 179.8437 | 344.8149 | -1.646 | 0.329
77175 | -15.1833 | 166.3974 | 167.0887 | 0.988 | -2.307
77185 | 33.3778 | -37.0821 | 49.8915 | -2.966 | 0
77195 | -138.9915 | -93.7864 | 167.6739 | -0.987 | 2.966
77205 | -365.4902 | 48.142 | 368.6472 | 1.647 | 4.613
77215 | -614.3624 | 211.1529 | 649.6358 | 2.635 | 6.259
77225 | -674.1636 | 238.0003 | 714.9411 | 1.318 | 4.282
77235 | -662.195 | 318.6935 | 734.8931 | 2.636 | 3.624
77245 | -626.9577 | 465.4612 | 780.8522 | 3.953 | 2.966
77255 | -457.1764 | 456.91 | 646.3567 | 1.977 | 0.329
77265 | -334.827 | 455.2057 | 565.0852 | 2.306 | 0.329
77275 | -306.3858 | 391.1919 | 496.8937 | 0.988 | 0.989
77285 | -257.0471 | 150.8006 | 298.0168 | -2.306 | 0.33
77295 | -755.4792 | -64.4379 | 758.2223 | -2.965 | 9.554
77305 | -812.3598 | -488.5567 | 947.9537 | -7.907 | 3.624
77315 | -758.3218 | -615.577 | 976.7226 | -4.612 | 3.294
77325 | -610.0847 | -493.425 | 784.6474 | -1.647 | 0.988
77335 | -601.1313 | -622.7404 | 865.5429 | -5.271 | 2.636
77345 | -428.9724 | -816.1004 | 921.9746 | -6.26 | -0.659
77355 | -153.4935 | -719.9501 | 736.1307 | -2.307 | -2.965
77365 | -99.1958 | -362.8139 | 376.13 | 2.307 | -0.659
77375 | -259.9145 | -113.541 | 283.632 | 2.306 | 2.306
77385 | -261.9039 | -104.8042 | 282.0949 | 0 | 0.33
77395 | -156.602 | -117.6639 | 195.88 | 0 | -0.989
77405 | -80.467 | -172.9229 | 190.7282 | -0.989 | -0.988
77415 | 197.4844 | -78.6394 | 212.5659 | 1.319 | -4.942
77425 | 279.9964 | 256.4195 | 379.6695 | 5.6 | -2.635
77435 | 136.5233 | 524.7884 | 542.2559 | 5.93 | 0.329
77445 | 186.7772 | 598.7618 | 627.2172 | 4.284 | -2.307
77455 | 27.0127 | 526.2621 | 526.9549 | 2.306 | 1.648
77465 | -361.7203 | 498.7268 | 616.0925 | 2.635 | 5.931
77475 | -617.4994 | 231.168 | 659.3513 | -1.977 | 5.6
77485 | -617.0712 | 25.802 | 617.6104 | -1.976 | 2.965
77495 | -641.7657 | -206.4642 | 674.1592 | -3.954 | 3.624
77505 | -584.8392 | -528.4324 | 788.2117 | -6.589 | 1.976
77515 | -656.7185 | -567.8049 | 868.1484 | -3.294 | 3.954
77525 | -539.1905 | -510.3873 | 742.443 | -2.307 | 0.659
77535 | -339.4234 | -523.9161 | 624.2566 | -2.964 | -0.988
77545 | 2.414 | -590.2243 | 590.2292 | -3.624 | -4.612
77555 | 229.9669 | -395.2442 | 457.2776 | 0.658 | -4.284
77565 | 349.9147 | -64.5505 | 355.8189 | 3.624 | -3.953
77575 | 377.2777 | -71.9932 | 384.0853 | -0.329 | -2.965
77585 | 322.4969 | -22.4203 | 323.2753 | 1.318 | -1.647
77595 | 174.5858 | -57.7824 | 183.8994 | -0.329 | 0.329
77605 | 113.1248 | -36.9983 | 119.0214 | 0.658 | -0.329
77615 | -140.5112 | 88.4277 | 166.0206 | 2.306 | 3.624
77625 | -433.6638 | -46.9223 | 436.1949 | -1.647 | 5.27
77635 | -666.6159 | -323.6387 | 741.0255 | -4.283 | 5.931
77645 | -574.4224 | -608.3856 | 836.7163 | -5.93 | 1.648
77655 | -313.5336 | -474.175 | 568.4586 | -0.329 | -1.318
77665 | -198.7481 | -207.2466 | 287.1445 | 1.977 | -0.33
77675 | -108.3284 | 19.8906 | 110.1394 | 2.964 | -0.989
77685 | 92.427 | 30.9692 | 97.4774 | 0.66 | -3.294
77695 | 396.611 | 171.8805 | 432.2536 | 3.293 | -5.93
77705 | 307.0852 | 277.9495 | 414.1947 | 2.966 | -0.659
77715 | 186.0672 | 400.5307 | 441.64 | 3.953 | -0.329
77725 | 13.3006 | 515.2785 | 515.4501 | 4.283 | 1.647
77735 | -145.9576 | 540.5148 | 559.8749 | 3.295 | 2.306
77745 | -305.0398 | 441.451 | 536.5895 | 1.318 | 3.295
77755 | -300.8918 | 430.0568 | 524.8664 | 2.306 | 1.317
77765 | -321.7494 | 520.8778 | 612.2388 | 3.624 | 1.977
77775 | -620.7152 | 977.9716 | 1158.3246 | 10.212 | 6.589
77785 | -1106.9588 | 1254.9589 | 1673.4036 | 8.896 | 10.872
77795 | -1279.8795 | 1068.8614 | 1667.5 | 2.965 | 7.907
77805 | -1444.5865 | 935.4084 | 1720.9936 | 3.295 | 9.225
77815 | -1319.3452 | 614.3342 | 1455.3619 | -1.318 | 4.612
77825 | -1195.8157 | 415.2486 | 1265.862 | -0.659 | 4.283
77835 | -1295.758 | 346.4177 | 1341.2658 | 0 | 6.918
77845 | -858.2992 | -233.8345 | 889.582 | -9.225 | -2.306
77855 | -709.713 | -329.8412 | 782.6159 | -2.965 | 1.318
77865 | -635.6479 | -476.9727 | 794.7019 | -5.601 | 0.659
77875 | -514.7145 | -567.4094 | 766.0838 | -4.612 | -0.33
77885 | -348.9007 | -626.43 | 717.0399 | -4.612 | -1.647
77895 | -113.34 | -489.5036 | 502.4537 | -1.319 | -3.624
77905 | 192.9822 | -443.9861 | 484.1134 | -2.305 | -5.93
77915 | 318.3063 | -385.1542 | 499.6626 | -1.319 | -4.283
77925 | 7.1581 | -862.4575 | 862.4872 | -10.212 | 2.306
77935 | -58.7187 | -1524.3891 | 1525.5196 | -14.825 | -0.658
77945 | 68.5489 | -1496.7012 | 1498.2701 | -6.589 | -2.636
77955 | -45.2394 | -1374.7606 | 1375.5047 | -5.931 | 0.988
77965 | -266.6413 | -1392.7113 | 1418.0064 | -6.918 | 2.965
77975 | -317.1899 | -1415.6334 | 1450.7334 | -6.589 | 1.318
77985 | -117.8729 | -1112.9628 | 1119.1873 | -0.988 | -2.306
77995 | 55.0864 | -863.2702 | 865.026 | -0.66 | -2.636
78005 | 63.1823 | -683.9794 | 686.8914 | 0 | -0.988
78015 | 75.6847 | -450.7426 | 457.0526 | 1.977 | -1.318
78025 | 77.1546 | -186.0919 | 201.4523 | 3.624 | -0.988
78035 | -112.552 | -96.3393 | 148.1527 | 1.977 | 2.306
78045 | -220.0898 | -259.1873 | 340.0258 | -1.648 | 1.647
78055 | -138.7951 | -495.594 | 514.6625 | -3.624 | -0.659
78065 | -30.712 | -570.147 | 570.9735 | -2.306 | -1.317
78075 | 17.7923 | -540.7419 | 541.0345 | -1.317 | -0.989
78085 | 121.7065 | -498.6955 | 513.332 | -0.989 | -2.306
78095 | 357.2992 | -300.4311 | 466.8207 | 1.977 | -4.942
78105 | 359.7847 | -225.3413 | 424.5277 | 0.659 | -1.977
78115 | 373.6433 | -347.9976 | 510.5993 | -1.977 | -2.635
78125 | 519.4441 | -423.2142 | 670.0242 | -1.647 | -4.613
78135 | 694.4227 | -515.9184 | 865.098 | -2.636 | -5.601
78145 | 856.7424 | -814.5587 | 1182.1647 | -6.588 | -6.259
78155 | 1051.0852 | -1078.8948 | 1506.2516 | -7.248 | -7.577
78165 | 1140.5784 | -1538.0677 | 1914.8293 | -12.19 | -6.59
78175 | 1142.4995 | -1616.189 | 1979.2352 | -7.578 | -5.6
78185 | 1191.0291 | -1706.3333 | 2080.8949 | -8.895 | -6.26
78195 | 898.6975 | -1633.6796 | 1864.5552 | -5.93 | -0.329
78205 | 1091.9594 | -1230.378 | 1645.0548 | 0 | -7.577
78215 | 1668.5911 | -768.4085 | 1837.0215 | 2.965 | -13.838
78225 | 1698.6235 | -1121.9041 | 2035.6794 | -8.236 | -7.248
78235 | 1271.8788 | -1550.1559 | 2005.1581 | -9.884 | -0.658
78245 | 858.5527 | -1424.4029 | 1663.1405 | -3.295 | 1.318
78255 | 701.1675 | -1900.6623 | 2025.871 | -13.836 | -0.329
78265 | -146.9473 | -1461.3649 | 1468.7345 | 0.988 | 12.847
78275 | -414.3368 | -899.5024 | 990.3431 | 3.294 | 5.931
78285 | -25.7321 | -680.009 | 680.4957 | 1.319 | -2.307
78295 | 180.695 | 301.8861 | 351.8322 | 16.142 | -0.988
78305 | 300.0949 | 117.9753 | 322.4517 | -0.329 | -1.647
78315 | 299.9687 | -297.0333 | 422.1493 | -2.635 | -0.329
78325 | 188.1404 | -461.1466 | 498.0492 | -1.648 | 1.318
78335 | 411.6576 | -381.1406 | 561.0082 | 0.989 | -3.954
78345 | 469.6374 | -207.2428 | 513.3312 | 2.635 | -1.647
78355 | 626.147 | 30.7322 | 626.9007 | 4.612 | -4.283
78365 | 661.2008 | 240.8262 | 703.6929 | 5.272 | -2.636
78375 | 705.1848 | 520.567 | 876.5134 | 7.577 | -3.294
78385 | 1075.1856 | 501.4961 | 1186.3904 | 3.624 | -8.896
78395 | 751.276 | 733.9744 | 1050.3019 | 8.237 | 1.648
78405 | 328.7968 | 989.1601 | 1042.3747 | 8.894 | 3.624
78415 | 227.3223 | 1126.0515 | 1148.7677 | 8.237 | 0.988
78425 | 363.3837 | 1340.3965 | 1388.7802 | 10.213 | -1.976
78435 | 1059.3264 | 1383.4205 | 1742.4192 | 7.907 | -12.19
78445 | 1352.918 | 1388.0401 | 1938.3091 | 7.578 | -8.236
78455 | 1504.1332 | 1664.5971 | 2243.5018 | 11.86 | -8.566
78465 | 1301.1501 | 1669.4349 | 2116.6021 | 7.906 | -2.965
78475 | 1272.9768 | 1530.5229 | 1990.721 | 5.93 | -5.271
78485 | 1072.921 | 1472.0652 | 1821.5749 | 6.26 | -1.318
78495 | 1009.3806 | 1573.9875 | 1869.8358 | 8.236 | -2.966
78505 | 613.4369 | 1898.6782 | 1995.3155 | 12.19 | 3.624
78515 | 682.839 | 1994.312 | 2107.9728 | 9.554 | -2.964
78525 | 760.6141 | 1901.9913 | 2048.4396 | 7.248 | -2.306
78535 | 590.8666 | 2537.6645 | 2605.5449 | 19.108 | 0.988
78545 | 642.4102 | 2534.8603 | 2614.9966 | 9.884 | -2.306
78555 | 498.7151 | 3190.2839 | 3229.029 | 22.732 | 1.318
78565 | 1227.7006 | 3271.0348 | 3493.8399 | 14.167 | -13.509
78575 | 1274.9377 | 2589.8386 | 2886.6468 | 2.964 | -3.953
78585 | 706.2148 | 951.4118 | 1184.8728 | -16.802 | 4.283
78595 | 262.6934 | 254.315 | 365.6282 | -8.565 | 4.942
78605 | 113.4555 | 327.4212 | 346.5209 | -1.648 | 2.965
78615 | 568.1468 | -689.5281 | 893.4427 | -20.096 | -6.26
78625 | 97.3078 | -557.9116 | 566.334 | -2.965 | 7.908
78635 | -938.6835 | -503.1492 | 1065.0285 | -6.26 | 17.79
78645 | -1528.931 | -1190.679 | 1937.8716 | -16.802 | 15.484
78655 | -1209.1405 | -1998.8891 | 2336.1461 | -21.085 | 3.953
78665 | -2363.737 | -3212.8853 | 3988.7196 | -32.286 | 28.334
78675 | -3076.8414 | -3948.6002 | 5005.8363 | -29.321 | 23.061
78685 | -3848.8328 | -4288.8969 | 5762.6514 | -27.015 | 29.651
78695 | -5059.3058 | -3678.7787 | 6255.3966 | -11.861 | 39.863
78705 | -5374.8996 | -3190.6509 | 6250.5839 | -11.201 | 29.651
78715 | -4416.9364 | -3408.3412 | 5579.0785 | -18.779 | 10.543
78725 | -3579.3139 | -3577.9651 | 5060.9606 | -17.46 | 7.906
78735 | -1934.2684 | -5740.2199 | 6057.3525 | -52.713 | -12.519
78745 | 187.2019 | -5647.6354 | 5650.7371 | -21.414 | -28.333
78755 | 313.531 | -4004.7701 | 4017.0244 | 0.329 | -5.601
78765 | 805.1154 | -2072.2546 | 2223.1621 | 14.496 | -16.143
78775 | 1095.1335 | -170.4278 | 1108.3154 | 25.368 | -12.189
78785 | 832.1451 | 1363.4112 | 1597.2964 | 29.651 | -4.613
78795 | 37.9687 | 1479.7241 | 1480.2111 | 13.837 | 5.931
78805 | -333.6196 | 1801.3834 | 1832.0164 | 19.437 | 2.964
78815 | -55.5523 | 2173.6675 | 2174.3773 | 19.438 | -4.612
78825 | 976.5218 | 2524.6505 | 2706.9272 | 20.426 | -18.12
78835 | 1627.163 | 2376.828 | 2880.4463 | 12.849 | -16.143
78845 | 1855.9328 | 1674.227 | 2499.5045 | 2.635 | -13.508
78855 | 1689.7177 | 971.5697 | 1949.1264 | -1.318 | -7.906
78865 | 1156.153 | 565.1742 | 1286.9001 | -0.988 | -0.659
78875 | 950.5915 | 274.5813 | 989.4539 | -1.977 | -3.295
78885 | 1380.7918 | 98.5769 | 1384.3061 | -1.647 | -11.86
78895 | 2505.1835 | 715.4876 | 2605.3535 | 10.872 | -25.038
78905 | 2967.782 | 906.6201 | 3103.1742 | 5.601 | -18.779
78915 | 2259.8816 | 681.307 | 2360.3482 | 0.988 | -2.635
78925 | 237.1003 | -232.5811 | 332.1303 | -11.86 | 22.732
78935 | -1385.9762 | -1661.9245 | 2164.0063 | -24.709 | 25.697
78945 | -814.6492 | -2165.808 | 2313.9528 | -16.143 | -1.318
78955 | -315.072 | -1389.6994 | 1424.9683 | 1.318 | 0
78965 | -1330.1145 | -589.9423 | 1455.0727 | 4.941 | 20.755
78975 | -2076.3482 | -392.8937 | 2113.1937 | 0.329 | 18.779
78985 | -2989.9135 | -194.8548 | 2996.2561 | 2.636 | 27.015
78995 | -3921.0768 | -993.9467 | 4045.0925 | -13.837 | 30.969
79005 | -3738.8618 | -1671.2383 | 4095.3785 | -14.166 | 16.472
79015 | -3813.7104 | -1935.2052 | 4276.6115 | -11.86 | 21.085
79025 | -4383.8292 | -1369.2926 | 4592.7029 | 0.659 | 27.674
79035 | -4675.5831 | -869.2053 | 4755.6908 | 1.647 | 24.709
79045 | -4560.5097 | -1666.364 | 4855.4112 | -16.802 | 19.438
79055 | -5362.1576 | -2946.249 | 6118.261 | -27.016 | 34.263
79065 | -6683.4475 | -3684.2003 | 7631.6317 | -24.708 | 44.805
79075 | -6271.7716 | -2427.3479 | 6725.1124 | 4.612 | 21.414
79085 | -4739.5246 | -1507.0228 | 4973.3501 | 2.965 | 2.636
79095 | -3135.1315 | -1558.0582 | 3500.942 | -5.93 | -7.248
79105 | -1353.4929 | -559.8638 | 1464.7152 | 13.178 | -20.096
79115 | 226.9441 | 1163.6399 | 1185.5637 | 28.333 | -26.027
79125 | -353.3321 | 815.84 | 889.0661 | 1.647 | 2.306
79135 | -543.5842 | -587.1121 | 800.1152 | -14.496 | -4.283
79145 | 1775.9439 | -422.9321 | 1825.609 | 4.284 | -42.829
79155 | 2869.0791 | 490.4511 | 2910.697 | 14.165 | -29.651
79165 | 2623.8754 | 660.3924 | 2705.7052 | 6.261 | -16.142
79175 | 2630.8129 | 645.6945 | 2708.8924 | 5.6 | -19.108
79185 | 2585.3188 | 614.5997 | 2657.3683 | 4.612 | -15.814
79195 | 2662.0118 | 802.8797 | 2780.4537 | 7.907 | -17.132
79205 | 2860.2925 | 416.2418 | 2890.4205 | -1.648 | -18.449
79215 | 2272.9416 | -580.9394 | 2346.0081 | -13.178 | -5.271
79225 | 722.0792 | -1518.412 | 1681.3606 | -17.131 | 13.507
79235 | -1258.7914 | -2552.1509 | 2845.7038 | -24.379 | 28.663
79245 | -2956.0839 | -3350.7515 | 4468.3294 | -25.368 | 34.592
79255 | -4012.9165 | -3510.486 | 5331.6987 | -18.779 | 33.275
79265 | -4362.8568 | -3220.2862 | 5422.6158 | -12.189 | 27.015
79275 | -4290.3146 | -2585.2141 | 5009.005 | -4.283 | 21.414
79285 | -3004.5826 | -2033.6569 | 3628.123 | -1.977 | -0.658
79295 | -2663.2268 | -1647.9898 | 3131.876 | -0.988 | 9.554
79305 | -2268.4692 | -1964.6098 | 3000.9406 | -10.543 | 3.294
79315 | -762.5774 | -2522.5371 | 2635.2833 | -15.155 | -17.132
79325 | -0.70994 | -2377.5264 | 2377.5265 | -6.259 | -10.871
79335 | -298.2324 | -2471.2157 | 2489.1464 | -10.872 | 0.988
79345 | -1220.3468 | -2243.0504 | 2553.5311 | -4.612 | 12.519
79355 | -2120.8807 | -2234.7678 | 3080.9613 | -7.908 | 17.132
79365 | -2735.5663 | -2263.4697 | 3550.58 | -7.577 | 17.789
79375 | -3307.2918 | -2046.2393 | 3889.1226 | -3.624 | 20.757
79385 | -3359.9219 | -1454.3859 | 3661.1902 | 3.624 | 14.495
79395 | -3173.46 | -1003.6853 | 3328.3979 | 3.953 | 11.201
79405 | -2768.1292 | -551.4584 | 2822.5246 | 6.919 | 5.931
79415 | -2613.5158 | -605.245 | 2682.6827 | 0.329 | 7.907
79425 | -2254.8729 | -1279.016 | 2592.3607 | -9.883 | 2.635
79435 | -2000.9761 | -1821.2866 | 2705.7329 | -10.872 | 2.966
79445 | -1586.6774 | -1737.5762 | 2353.0228 | -3.953 | -1.648
79455 | -756.5322 | -1565.853 | 1739.0332 | -2.965 | -10.543
79465 | -107.778 | -1665.8614 | 1669.3443 | -6.26 | -11.201
79475 | 216.4238 | -1882.9447 | 1895.3417 | -8.236 | -9.554
79485 | 785.8976 | -1534.7536 | 1724.269 | 0.329 | -15.484
79495 | 1918.6356 | -985.1339 | 2156.7688 | 4.612 | -27.016
79505 | 2697.2877 | -657.027 | 2776.1566 | 3.954 | -25.696
79515 | 2707.9375 | -649.332 | 2784.7006 | 0.659 | -17.132
79525 | 2531.5393 | -829.9514 | 2664.1153 | -2.306 | -14.166
79535 | 2630.037 | -1062.5838 | 2836.5787 | -4.284 | -16.802
79545 | 2583.8936 | -1094.452 | 2806.124 | -2.305 | -13.508
79555 | 2214.4897 | -702.743 | 2323.3193 | 4.282 | -7.577
79565 | 1911.2268 | -31.0228 | 1911.4786 | 10.543 | -6.589
79575 | 1596.7841 | 732.3189 | 1756.7045 | 15.484 | -3.954
79585 | 930.547 | 785.4291 | 1217.7095 | 7.248 | 3.954
79595 | 63.9875 | 128.3727 | 143.4362 | -3.624 | 10.542
79605 | -32.5217 | -970.3353 | 970.8801 | -14.495 | 1.977
79615 | 1020.8695 | 1506.2854 | 1819.6347 | 40.851 | -15.814
79625 | 466.7465 | 3443.4138 | 3474.903 | 37.888 | 7.248
79635 | -819.9737 | 4209.8817 | 4288.993 | 32.286 | 18.779
79645 | -1230.7008 | 3175.0639 | 3405.2394 | 5.93 | 10.872
79655 | -814.008 | 1700.1342 | 1884.9577 | -5.601 | 0.658
79665 | -1122.6921 | 2494.1803 | 2735.2098 | 23.721 | 11.202
79675 | -1719.435 | 826.1823 | 1907.6252 | -19.108 | 15.485
79685 | -733.9318 | -779.2476 | 1070.4591 | -20.756 | -8.567
79695 | -267.3402 | -1043.9247 | 1077.6129 | -9.224 | -2.306
79705 | -621.0105 | 944.5144 | 1130.3811 | 26.356 | 6.589
79715 | -741.8551 | 1196.3554 | 1407.6986 | 4.612 | 3.624
79725 | 1037.9705 | -230.6632 | 1063.2912 | -17.461 | -27.344
79735 | 2714.2052 | -1241.8188 | 2984.7988 | -16.802 | -31.957
79745 | 3689.1131 | -596.7096 | 3737.0601 | 4.283 | -30.639
79755 | 3336.3228 | 536.6241 | 3379.2033 | 13.837 | -13.508
79765 | 3971.1868 | 615.092 | 4018.5399 | 2.635 | -29.65
79775 | 4783.7572 | 324.3733 | 4794.742 | -0.989 | -32.286
79785 | 4212.4596 | 528.6354 | 4245.5001 | 5.601 | -12.849
79795 | 3245.1378 | 1102.0978 | 3427.1765 | 11.861 | -4.613
79805 | 2154.6198 | 1072.666 | 2406.865 | 4.283 | 3.954
79815 | 1028.3762 | 116.8329 | 1034.9915 | -10.543 | 10.871
79825 | -460.4543 | -306.1392 | 552.937 | -5.601 | 23.392
79835 | -1874.9951 | -281.0405 | 1895.9405 | -1.976 | 29.322
79845 | -3596.1016 | -121.4939 | 3598.1533 | 0.33 | 42.169
79855 | -4499.4204 | -946.2194 | 4597.8381 | -15.485 | 35.91
79865 | -5001.1207 | -1094.7568 | 5119.5411 | -6.259 | 34.593
79875 | -5848.4041 | -7.5166 | 5848.409 | 12.189 | 41.84
79885 | -6309.1155 | -304.0202 | 6316.4363 | -6.918 | 37.557
79895 | -5798.914 | -1009.6679 | 5886.1561 | -11.861 | 23.062
79905 | -4235.7135 | -1382.9592 | 4455.7654 | -10.542 | 2.306
79915 | -2721.8732 | -1355.6409 | 3040.7821 | -6.26 | -5.271
79925 | -1282.1901 | -2188.021 | 2536.0299 | -21.085 | -13.837
79935 | -1039.519 | -2022.0599 | 2273.6152 | -6.259 | -1.318
79945 | -2491.3232 | -370.8801 | 2518.7781 | 17.79 | 24.38
79955 | -2451.1372 | 1280.1424 | 2765.2917 | 25.368 | 4.942
79965 | -1249.268 | 2377.8695 | 2686.0629 | 26.027 | -10.872
79975 | -235.3657 | 2790.0067 | 2799.9169 | 20.755 | -13.508
79985 | 113.7325 | 2465.6142 | 2468.2359 | 10.543 | -8.566
79995 | -13.3955 | 1473.5082 | 1473.5691 | -2.636 | -2.964
80005 | -574.5947 | 1816.1226 | 1904.8518 | 14.825 | 5.27
80015 | -1459.4289 | 3060.9509 | 3391.0697 | 28.662 | 13.838
80025 | -1370.7774 | 2880.5987 | 3190.1222 | 10.214 | 1.976
80035 | -474.8701 | 2036.8212 | 2091.4451 | 0.658 | -10.213
80045 | 574.4366 | 1263.0513 | 1387.5431 | -3.294 | -17.131
80055 | 896.3488 | 1549.1601 | 1789.7872 | 9.884 | -10.542
80065 | 858.1297 | 2516.3225 | 2658.621 | 21.085 | -7.248
80075 | -8.2572 | 2701.0479 | 2701.0606 | 12.519 | 7.577
80085 | -634.2692 | 1553.182 | 1677.6983 | -7.577 | 7.248
80095 | -516.383 | 1085.3393 | 1201.9204 | -0.66 | -0.659
80105 | -293.8907 | 1428.4029 | 1458.3232 | 8.237 | -1.977
80115 | -127.68 | 1378.2764 | 1384.1777 | 2.635 | -2.635
80125 | -673.95 | 73.4293 | 677.9384 | -17.79 | 8.565
80135 | -1371.5258 | -628.0657 | 1508.4924 | -12.519 | 12.849
80145 | -1617.5487 | -629.6674 | 1735.7836 | -6.259 | 9.224
80155 | -1167.463 | -639.144 | 1330.9677 | -6.59 | -0.658
80165 | -1127.6974 | -9.0735 | 1127.7339 | 5.272 | 4.612
80175 | -1247.2659 | -1354.5778 | 1841.3455 | -26.027 | 5.6
80185 | -155.4593 | 300.2397 | 338.0998 | 22.732 | -14.495
80195 | -1546.2218 | 1486.4154 | 2144.8152 | 16.473 | 24.38
80205 | -1484.7061 | 1135.8465 | 1869.358 | 0.658 | 1.317
80215 | -1240.0078 | 854.1255 | 1505.7057 | 1.648 | 2.965
80225 | -1183.2788 | 323.7293 | 1226.7638 | -5.601 | 3.295
80235 | -1004.0388 | -761.067 | 1259.8877 | -17.461 | 0.658
80245 | -1521.9929 | -641.7083 | 1651.7421 | -1.976 | 11.86
80255 | -3095.268 | -1836.9061 | 3599.2927 | -26.356 | 31.299
80265 | -3351.5232 | -1500.8702 | 3672.2363 | -2.637 | 15.814
80275 | -3892.5926 | 758.3637 | 3965.7776 | 28.333 | 25.038
80285 | -4189.8061 | 219.6952 | 4195.562 | -8.894 | 21.414
80295 | -3142.2913 | -214.433 | 3149.5993 | -3.295 | 0.33
80305 | -2240.1388 | -48.3818 | 2240.6612 | 1.647 | -1.318
80315 | -1269.0747 | -18.1717 | 1269.2048 | -0.329 | -9.225
80325 | -548.4158 | -204.0571 | 585.1489 | -3.295 | -9.883
80335 | -352.5865 | -499.3197 | 611.2589 | -5.93 | -5.272
80345 | 202.3356 | -783.325 | 809.035 | -7.248 | -12.848
80355 | 575.9487 | -708.3343 | 912.9372 | -2.636 | -11.202
80365 | 453.0719 | -147.4956 | 476.4757 | 5.601 | -4.942
80375 | 513.9267 | -276.6344 | 583.65 | -3.624 | -7.577
80385 | 1299.5785 | -659.0644 | 1457.1445 | -6.918 | -19.108
80395 | 1890.2994 | -410.678 | 1934.3961 | 1.647 | -18.45
80405 | 2285.8656 | 1040.863 | 2511.6882 | 22.403 | -18.778
80415 | 2258.7531 | 2687.7985 | 3510.8725 | 31.957 | -13.178
80425 | 1776.8215 | 2963.4905 | 3455.3394 | 17.79 | -5.272
80435 | 1570.4327 | 2436.7001 | 2898.925 | 7.577 | -7.248
80445 | 1757.6785 | 1908.5779 | 2594.6297 | 4.283 | -11.53
80455 | 1912.5597 | 2382.4298 | 3055.1361 | 17.461 | -11.202
80465 | 1496.187 | 2147.4315 | 2617.2576 | 5.601 | -2.306
80475 | 1861.3054 | 2070.819 | 2784.3759 | 8.895 | -14.167
80485 | 2449.9286 | 2618.1246 | 3585.6278 | 17.79 | -17.789
80495 | 2537.1999 | 2730.1198 | 3727.0548 | 12.19 | -12.52
80505 | 2673.2284 | 2670.8027 | 3778.801 | 10.872 | -14.496
80515 | 2683.7301 | 2561.1884 | 3709.7295 | 9.224 | -12.189
80525 | 2692.1854 | 1944.2754 | 3320.8536 | -0.329 | -12.19
80535 | 2592.9886 | 1388.0485 | 2941.1339 | -1.977 | -9.884
80545 | 2549.5827 | 1450.7851 | 2933.4535 | 4.942 | -10.212
80555 | 2452.1974 | 1109.5537 | 2691.5389 | -2.636 | -8.566
80565 | 2100.5431 | 488.3644 | 2156.567 | -7.907 | -3.624
80575 | 1308.3187 | 357.9519 | 1356.4023 | -2.635 | 5.6
80585 | 351.694 | 528.779 | 635.0558 | 0.988 | 12.19
80595 | -1187.7333 | 212.7794 | 1206.6422 | -6.259 | 27.344
80605 | -1740.2159 | -1658.3274 | 2403.8305 | -33.275 | 17.462
80615 | 176.835 | -2656.1107 | 2661.9907 | -25.697 | -20.097
80625 | 1850.5745 | -2159.3239 | 2843.8188 | -7.907 | -23.391
80635 | 2285.5259 | -1567.6248 | 2771.4755 | -4.612 | -14.166
80645 | 1904.1469 | -1646.7595 | 2517.4575 | -11.201 | -4.284
80655 | 1839.128 | -2014.6694 | 2727.8718 | -14.826 | -7.906
80665 | 2325.9204 | -1849.0666 | 2971.3554 | -7.248 | -15.484
80675 | 3176.3044 | -1075.9341 | 3353.5867 | 3.295 | -23.392
80685 | 3425.3663 | -452.6735 | 3455.148 | 4.612 | -17.131
80695 | 3095.8074 | -810.834 | 3200.2305 | -7.907 | -9.554
80705 | 2810.7191 | -1402.5956 | 3141.2444 | -12.19 | -8.566
80715 | 3399.3726 | -1053.4672 | 3558.866 | 0.33 | -21.085
80725 | 4333.5381 | -462.8 | 4358.1804 | 4.612 | -28.333
80735 | 4389.5457 | -278.8077 | 4398.3912 | 1.318 | -18.12
80745 | 4001.8953 | -624.5403 | 4050.3353 | -5.93 | -12.189
80755 | 3149.8992 | -1067.3567 | 3325.8255 | -8.895 | -1.648
80765 | 2594.376 | -719.8868 | 2692.4011 | 1.977 | -2.305
80775 | 2706.1601 | -819.5525 | 2827.5376 | -5.272 | -9.554
80785 | 2684.0384 | -1230.8799 | 2952.8169 | -9.554 | -6.919
80795 | 2524.4003 | -1576.6985 | 2976.3358 | -10.543 | -5.272
80805 | 1870.8755 | -1246.0794 | 2247.8632 | -0.987 | 3.954
80815 | 908.9466 | -557.379 | 1066.2342 | 5.929 | 11.86
80825 | 502.6595 | 43.7365 | 504.5587 | 8.236 | 7.248
80835 | 412.4518 | 239.2529 | 476.8211 | 4.942 | 4.942
80845 | 962.3947 | 246.7431 | 993.5219 | 3.295 | -5.93
80855 | 1485.8038 | 53.7678 | 1486.7764 | -0.329 | -7.907
80865 | 1634.2807 | -136.8965 | 1640.0043 | -1.318 | -5.271
80875 | 1519.1885 | -169.1143 | 1528.5723 | 0 | -2.306
80885 | 1522.6133 | -53.7562 | 1523.5619 | 1.977 | -3.954
80895 | 1202.3175 | -39.7967 | 1202.976 | 0.658 | 1.976
80905 | 1207.9082 | 13.0421 | 1207.9787 | 1.647 | -2.635
80915 | 1242.8674 | 293.759 | 1277.1115 | 5.601 | -2.306
80925 | 628.5326 | 684.4044 | 929.2269 | 8.566 | 8.236
80935 | -250.4309 | 440.2391 | 506.4841 | -0.329 | 14.825
80945 | -13.1128 | -1.2733 | 13.1745 | -3.954 | 0.33
80955 | 644.2975 | -166.2753 | 665.4072 | -1.977 | -6.26
80965 | 368.067 | 143.9359 | 395.2099 | 4.613 | 5.601
80975 | 186.1524 | 143.7501 | 235.1952 | 0.329 | 3.295
80985 | 226.2373 | -8.7239 | 226.4054 | -1.318 | 1.317
80995 | 42.1439 | -70.0693 | 81.7668 | -0.658 | 4.942
81005 | -87.4631 | -97.6885 | 131.1215 | -0.659 | 4.283
81015 | 465.7238 | -291.014 | 549.1701 | -3.624 | -6.589
81025 | 1440.2573 | -20.7311 | 1440.4065 | 3.624 | -15.814
81035 | 1689.7908 | 393.7928 | 1735.0693 | 6.588 | -8.565
81045 | 1712.8571 | 512.5764 | 1787.9077 | 3.954 | -7.578
81055 | 1968.4163 | 351.2061 | 1999.502 | 0.329 | -11.201
81065 | 1842.4988 | 443.8774 | 1895.2121 | 3.954 | -5.271
81075 | 1565.1645 | 380.7639 | 1610.8138 | 0.988 | -2.636
81085 | 1394.6831 | 388.3837 | 1447.751 | 2.306 | -2.636
81095 | 1167.3836 | 513.4694 | 1275.3177 | 3.953 | -0.329
81105 | 1061.7307 | 340.6262 | 1115.0329 | -0.658 | -1.318
81115 | 1064.1954 | 362.2182 | 1124.1502 | 2.306 | -2.306
81125 | 1374.963 | 763.6757 | 1572.8076 | 8.237 | -7.577
81135 | 1902.2344 | 742.3741 | 2041.9635 | 2.635 | -12.52
81145 | 1828.9473 | 688.9922 | 1954.4203 | 2.965 | -4.941
81155 | 1230.1835 | 353.8563 | 1280.0648 | -2.636 | 3.294
81165 | 1072.8487 | 57.9726 | 1074.4139 | -3.294 | -1.317
81175 | 1134.3866 | 108.8891 | 1139.6007 | 0.659 | -2.966
81185 | 1306.9547 | 174.0894 | 1318.4982 | 0.659 | -5.271
81195 | 1100.9404 | 449.1526 | 1189.0365 | 4.942 | 0.329
81205 | 872.3887 | 467.0455 | 989.5421 | 1.647 | 0.989
81215 | 655.208 | 247.0633 | 700.2412 | -1.647 | 2.306
81225 | 519.8974 | 261.3012 | 581.869 | 1.318 | 1.976
81235 | 736.9026 | 499.0563 | 889.9902 | 4.612 | -3.293
81245 | 699.1178 | 576.6836 | 906.2724 | 2.965 | 0.329
81255 | 524.1139 | 412.5888 | 667.027 | -0.33 | 1.977
81265 | 303.9145 | 555.6737 | 633.354 | 4.283 | 3.624
81275 | 280.2696 | 412.2062 | 498.4627 | -0.659 | 1.317
81285 | 567.9539 | 325.2258 | 654.4795 | 0.33 | -3.624
81295 | 894.8216 | 388.1575 | 975.3829 | 1.977 | -5.601
81305 | 1064.0668 | 171.696 | 1077.8301 | -2.636 | -4.941
81315 | 739.3015 | -224.7183 | 772.6998 | -6.26 | 2.306
81325 | 473.749 | 16.7007 | 474.0433 | 2.636 | 2.306
81335 | 132.5033 | 213.7876 | 251.5199 | 1.976 | 5.6
81345 | 72.829 | 476.9233 | 482.4519 | 4.942 | 2.307
81355 | 388.0722 | 420.4924 | 572.2009 | 0.659 | -3.294
81365 | 734.3038 | 457.4816 | 865.154 | 2.636 | -5.272
81375 | 893.3627 | 206.8026 | 916.9865 | -2.636 | -4.282
81385 | 1154.1447 | -116.7664 | 1160.0363 | -4.612 | -7.248
81395 | 1221.4511 | 55.9824 | 1222.7333 | 1.977 | -4.943
81405 | 861.4626 | 417.569 | 957.3306 | 5.271 | 1.648
81415 | 568.7387 | 579.2433 | 811.7798 | 3.953 | 1.976
81425 | 707.6964 | 797.0939 | 1065.9235 | 6.26 | -3.294
81435 | 804.2817 | 1101.2088 | 1363.6458 | 8.566 | -2.636
81445 | 823.5755 | 1397.7068 | 1622.3011 | 9.883 | -2.305
81455 | 929.199 | 1568.7511 | 1823.2912 | 9.225 | -3.954
81465 | 1032.5896 | 1802.0175 | 2076.8987 | 11.201 | -4.283
81475 | 926.8891 | 1913.7764 | 2126.4204 | 9.883 | -1.317
81485 | 720.3755 | 1720.8952 | 1865.5887 | 5.272 | 0.658
81495 | 350.3021 | 1522.6391 | 1562.4153 | 4.282 | 4.612
81505 | 120.6726 | 1396.3686 | 1401.5731 | 3.955 | 3.953
81515 | 59.2066 | 1095.0857 | 1096.685 | 0 | 2.636
81525 | 17.9664 | 757.4662 | 757.6793 | -1.977 | 2.636
81535 | 474.2992 | 552.7428 | 728.3435 | -1.647 | -5.93
81545 | 1407.6043 | 442.9653 | 1475.6585 | -1.318 | -15.813
81555 | 1856.3473 | 460.592 | 1912.6344 | 0.329 | -12.191
81565 | 1673.853 | 800.9234 | 1855.6029 | 5.93 | -4.942
81575 | 889.6347 | 843.7083 | 1226.0887 | 2.307 | 5.931
81585 | 215.6438 | 589.9211 | 628.0996 | -1.648 | 7.907
81595 | -640.4419 | 362.8987 | 736.1123 | -2.307 | 15.484
81605 | -1184.2 | 86.2241 | 1187.3349 | -4.611 | 14.167
81615 | -1661.9586 | -77.7005 | 1663.774 | -3.954 | 16.472
81625 | -1643.1879 | -355.139 | 1681.1276 | -6.919 | 9.884
81635 | -1357.7333 | -574.8821 | 1474.425 | -6.918 | 5.6
81645 | -1191.2041 | -1051.6891 | 1589.0303 | -12.519 | 5.601
81655 | -1412.7897 | -1118.7896 | 1802.1279 | -7.248 | 10.542
81665 | -1503.2226 | -1354.9862 | 2023.7751 | -11.201 | 8.566
81675 | -1471.1374 | -1522.4211 | 2117.0761 | -10.214 | 7.248
81685 | -1615.0914 | -1559.8915 | 2245.3912 | -8.894 | 9.883
81695 | -1482.5374 | -1580.4326 | 2166.9528 | -8.566 | 5.272
81705 | -1001.036 | -1598.7615 | 1886.2957 | -8.236 | -0.988
81715 | -681.0511 | -1533.6386 | 1678.0578 | -6.59 | -0.66
81725 | -482.018 | -1323.6043 | 1408.6411 | -3.624 | -0.988
81735 | -233.177 | -1182.243 | 1205.0187 | -3.624 | -2.965
81745 | -145.3285 | -1455.958 | 1463.1931 | -9.554 | -1.318
81755 | -271.4456 | -1575.5298 | 1598.7423 | -7.577 | 1.647
81765 | -517.5021 | -1569.429 | 1652.5483 | -6.59 | 4.284
81775 | -721.2698 | -1418.2862 | 1591.1524 | -3.953 | 4.941
81785 | -963.9709 | -1042.9942 | 1420.2383 | 0.66 | 6.919
81795 | -1081.0976 | -853.3401 | 1377.3023 | -0.66 | 5.93
81805 | -804.4522 | -834.0154 | 1158.7601 | -1.977 | 0
81815 | -10.3387 | -1076.3243 | 1076.3739 | -6.259 | -9.884
81825 | 661.2599 | -953.9206 | 1160.7021 | -0.989 | -11.53
81835 | 914.2551 | -681.7512 | 1140.4591 | 1.318 | -8.566
81845 | 1084.9568 | -154.2383 | 1095.8653 | 7.249 | -8.896
81855 | 1097.5696 | 444.9255 | 1184.3216 | 10.872 | -6.588
81865 | 631.4575 | 857.5614 | 1064.9649 | 10.872 | 1.647
81875 | -287.7646 | 1076.1769 | 1113.9862 | 9.883 | 11.531
81885 | -987.431 | 966.8635 | 1381.9714 | 5.271 | 12.518
81895 | -1383.6627 | 715.7263 | 1557.8147 | 2.306 | 11.861
81905 | -1167.5738 | 431.7106 | 1244.8304 | 0 | 3.624
81915 | -754.512 | 197.1479 | 779.8433 | -0.989 | -0.329
81925 | -634.0841 | -42.9168 | 635.5348 | -2.635 | 1.977
81935 | -1350.6479 | 62.4651 | 1352.0916 | 1.977 | 14.825
81945 | -1808.6693 | -269.2514 | 1828.6008 | -5.601 | 12.848
81955 | -1370.6965 | -1005.9732 | 1700.2326 | -13.178 | 0.989
81965 | -643.6849 | -1205.4438 | 1366.5376 | -7.577 | -5.272
81975 | -285.7232 | -1201.2438 | 1234.7569 | -6.259 | -3.295
81985 | -75.0312 | -741.6587 | 745.4444 | 1.976 | -3.624
81995 | -250.252 | -263.2939 | 363.2488 | 4.283 | 1.978
82005 | -630.0136 | -83.4108 | 635.5112 | 2.306 | 5.93
82015 | -1018.4148 | -87.562 | 1022.1721 | 0.659 | 8.236
82025 | -1121.3906 | -149.8423 | 1131.3575 | -0.33 | 5.6
82035 | -934.1072 | -204.9978 | 956.337 | -0.658 | 1.648
82045 | -604.1945 | -81.2949 | 609.6391 | 1.976 | -1.648
82055 | -343.6357 | 25.5676 | 344.5855 | 1.977 | -2.305
82065 | -295.8629 | 167.4992 | 339.9866 | 3.295 | -0.33
82075 | -490.7679 | 467.0729 | 677.5029 | 6.588 | 3.294
82085 | -597.0099 | 500.2572 | 778.8954 | 3.295 | 2.636
82095 | -626.0676 | 417.5744 | 752.5484 | 1.977 | 2.306
82105 | -585.104 | 411.615 | 715.3835 | 2.636 | 1.318
82115 | -533.2601 | 292.8633 | 608.3875 | 0.329 | 0.988
82125 | -443.1444 | 48.2646 | 445.765 | -2.306 | 0
82135 | -377.3811 | -160.0955 | 409.9354 | -2.965 | 0
82145 | -316.8356 | -234.8217 | 394.3679 | -1.977 | -0.329
82155 | -137.5791 | -276.4146 | 308.7605 | -1.977 | -2.635
82165 | 39.5959 | -273.6055 | 276.4558 | -1.318 | -3.295
82175 | 235.9902 | -426.1635 | 487.1413 | -3.953 | -4.612
82185 | 226.8517 | -535.4203 | 581.4951 | -3.624 | -1.978
82195 | 224.6134 | -640.4455 | 678.6911 | -4.283 | -2.306
82205 | 282.4316 | -625.8173 | 686.5967 | -2.636 | -2.964
82215 | 296.0824 | -416.6744 | 511.1579 | 0.66 | -2.307
82225 | 171.2188 | -515.3572 | 543.0552 | -3.624 | 0
82235 | 118.5351 | -495.4147 | 509.398 | -1.319 | -0.659
82245 | -70.7716 | -338.9158 | 346.2261 | 0.66 | 2.306
82255 | -217.0261 | -171.6515 | 276.703 | 1.646 | 2.307
82265 | -380.1773 | -100.0937 | 393.1329 | 0.989 | 3.623
82275 | -480.3239 | -79.4747 | 486.8544 | 0.659 | 3.295
82285 | -505.7492 | -5.4203 | 505.7782 | 1.647 | 2.636
82295 | -543.4718 | 75.7406 | 548.7242 | 1.977 | 2.965
82305 | -425.8606 | 56.1456 | 429.5458 | 0.659 | 0.329
82315 | -352.0365 | 132.3887 | 376.107 | 2.306 | 0.66
82325 | -414.6544 | 166.0394 | 446.6625 | 1.648 | 2.306
82335 | -470.5583 | 28.8996 | 471.445 | -0.989 | 2.305
82345 | -465.1214 | -114.3419 | 478.9697 | -1.648 | 1.648
82355 | -534.7916 | -144.338 | 553.9274 | -0.658 | 2.965
82365 | -653.3248 | -133.7767 | 666.8804 | -0.329 | 3.954
82375 | -680.3434 | -109.3052 | 689.068 | 0 | 2.964
82385 | -729.4049 | 2.6751 | 729.4098 | 1.647 | 3.624
82395 | -717.1096 | 87.4651 | 722.4239 | 1.647 | 2.636
82405 | -781.3914 | 292.3822 | 834.302 | 4.283 | 3.954
82415 | -918.738 | 488.5432 | 1040.5547 | 4.941 | 5.271
82425 | -981.9435 | 619.4744 | 1161.0175 | 4.942 | 4.612
82435 | -923.5232 | 672.2443 | 1142.2817 | 4.283 | 2.965
82445 | -861.393 | 557.6516 | 1026.1449 | 1.647 | 2.636
82455 | -848.714 | 531.3786 | 1001.3385 | 2.636 | 2.965
82465 | -733.6418 | 538.8692 | 910.2803 | 2.636 | 0.988
82475 | -644.4414 | 624.2453 | 897.2106 | 3.953 | 0.989
82485 | -516.4984 | 618.6256 | 805.8959 | 2.636 | -0.33
82495 | -422.0374 | 489.969 | 646.6724 | 0.659 | -0.33
82505 | -438.7991 | 494.6224 | 661.208 | 2.306 | 0.989
82515 | -495.2886 | 501.7132 | 705.0014 | 1.976 | 1.647
82525 | -510.5133 | 616.6576 | 800.5563 | 3.954 | 1.319
82535 | -531.9096 | 652.8238 | 842.0847 | 2.965 | 1.646
82545 | -701.837 | 761.5731 | 1035.649 | 4.612 | 4.283
82555 | -929.1137 | 756.7865 | 1198.323 | 2.965 | 5.93
82565 | -1084.6 | 683.0825 | 1281.7796 | 1.977 | 5.93
82575 | -1070.3196 | 579.3004 | 1217.0345 | 0.989 | 3.954
82585 | -1052.2379 | 510.8963 | 1169.7092 | 0.988 | 3.953
82595 | -977.779 | 490.6852 | 1093.9944 | 1.318 | 2.636
82605 | -906.3693 | 461.3499 | 1017.0295 | 0.988 | 2.306
82615 | -731.2337 | 303.3394 | 791.6549 | -1.318 | 0
82625 | -467.3071 | 142.7642 | 488.6282 | -1.976 | -2.306
82635 | -359.612 | 286.8126 | 459.9807 | 2.306 | -0.989
82645 | -265.0041 | 413.8613 | 491.435 | 2.306 | -1.647
82655 | -245.0739 | 383.9353 | 455.486 | 0.658 | -0.659
82665 | -253.1474 | 348.8073 | 430.9874 | 0.66 | -0.329
82675 | -385.1907 | 407.8203 | 560.9718 | 1.976 | 1.977
82685 | -425.0382 | 419.1724 | 596.9615 | 1.319 | 0.988
82695 | -393.5414 | 532.4925 | 662.1353 | 3.293 | 0.33
82705 | -444.9096 | 682.855 | 815.0064 | 4.284 | 1.646
82715 | -317.3367 | 746.8562 | 811.4781 | 3.624 | -1.317
82725 | -262.516 | 668.5023 | 718.1992 | 1.646 | -0.329
82735 | -222.2664 | 743.0095 | 775.542 | 3.955 | -0.66
82745 | -72.5752 | 821.3665 | 824.5666 | 3.953 | -2.635
82755 | 140.6734 | 735.7048 | 749.0331 | 1.647 | -4.282
82765 | 369.7886 | 684.2207 | 777.7542 | 1.977 | -5.601
82775 | 340.7571 | 798.7363 | 868.3865 | 4.283 | -2.307
82785 | 147.7071 | 759.9163 | 774.1384 | 1.976 | 0.329
82795 | 40.1021 | 499.9016 | 501.5076 | -1.647 | 0
82805 | 65.9169 | 367.0551 | 372.927 | -0.659 | -1.317
82815 | 97.2459 | 453.3999 | 463.7113 | 1.977 | -1.318
82825 | 58.4271 | 679.5077 | 682.015 | 4.612 | -0.329
82835 | 65.7498 | 779.5136 | 782.2816 | 3.624 | -0.989
82845 | 158.2304 | 847.2653 | 861.9137 | 3.953 | -2.306
82855 | 229.9137 | 919.0845 | 947.4052 | 4.284 | -2.306
82865 | 160.2794 | 972.6067 | 985.7247 | 4.282 | -0.329
82875 | 44.8251 | 954.3842 | 955.4363 | 3.295 | 0.658
82885 | -105.944 | 882.4115 | 888.7486 | 2.306 | 1.977
82895 | -171.7145 | 662.5562 | 684.4462 | -0.659 | 1.318
82905 | -186.8689 | 347.7214 | 394.7532 | -3.294 | 0.988
82915 | -140.9713 | 33.6765 | 144.9379 | -4.942 | 0
82925 | -107.2055 | -123.5931 | 163.6101 | -3.954 | 0
82935 | -71.2737 | 46.3742 | 85.0324 | 0.659 | -0.329
82945 | 68.9686 | 25.9879 | 73.7024 | -1.977 | -2.306
82955 | 137.4799 | 177.3526 | 224.3985 | 1.647 | -1.648
82965 | 76.5008 | 324.1267 | 333.0323 | 1.977 | 0
82975 | 8.8297 | 253.8287 | 253.9822 | -0.658 | 0.33
82985 | 8.6432 | 202.0159 | 202.2008 | -0.33 | -0.33
82995 | 74.527 | 197.3083 | 210.9143 | 0 | -1.318
83005 | 85.9098 | 233.4601 | 248.7652 | 0.659 | -0.658
83015 | 278.136 | 163.1907 | 322.4761 | -0.988 | -3.954
83025 | 165.1971 | 195.9407 | 256.2866 | 0.659 | 0.659
83035 | -29.5286 | 252.7867 | 254.5055 | 0.987 | 1.977
83045 | -74.0186 | 266.9987 | 277.0687 | 0.66 | 0.659
83055 | -201.9275 | 367.1693 | 419.0323 | 2.306 | 2.635
83065 | -403.3499 | 312.2411 | 510.084 | 0 | 4.283
83075 | -469.5369 | 61.1961 | 473.508 | -3.295 | 2.965
83085 | -521.7779 | -103.1549 | 531.8769 | -2.964 | 3.295
83095 | -588.8865 | -103.4822 | 597.9096 | -1.318 | 3.624
83105 | -738.5036 | 19.1541 | 738.752 | 0.658 | 5.271
83115 | -875.541 | 103.8823 | 881.6822 | 0.66 | 5.6
83125 | -875.3146 | 13.559 | 875.4196 | -1.648 | 3.955
83135 | -774.0171 | -47.7297 | 775.4874 | -1.318 | 2.306
83145 | -593.6755 | -60.599 | 596.7603 | -0.988 | 0.329
83155 | -491.7372 | -31.1423 | 492.7223 | -0.33 | 0.658
83165 | -668.7248 | -68.4519 | 672.2191 | -1.317 | 4.613
83175 | -720.9421 | -278.947 | 773.0258 | -4.284 | 2.965
83185 | -615.6992 | -440.627 | 757.1246 | -4.282 | 0.989
83195 | -595.5907 | -426.5544 | 732.5824 | -2.306 | 1.976
83205 | -715.0345 | -350.3191 | 796.2397 | -1.318 | 3.953
83215 | -885.3959 | -210.3144 | 910.0319 | 0.329 | 5.272
83225 | -830.6999 | -114.9433 | 838.6145 | 0.33 | 2.306
83235 | -924.6882 | -22.6691 | 924.9661 | 0.988 | 4.942
83245 | -983.2862 | -111.6175 | 989.6011 | -1.647 | 4.283
83255 | -975.9326 | -249.7093 | 1007.3724 | -2.635 | 3.624
83265 | -934.5697 | -358.7009 | 1001.0429 | -2.966 | 2.965
83275 | -986.8313 | -295.8806 | 1030.2336 | -0.658 | 4.283
83285 | -1057.6864 | -142.5247 | 1067.2459 | 0.987 | 4.611
83295 | -1011.0983 | 56.6609 | 1012.6847 | 2.637 | 2.966
83305 | -1028.1654 | 39.5732 | 1028.9267 | 0 | 3.953
83315 | -960.6728 | -35.0308 | 961.3113 | -0.66 | 2.306
83325 | -827.4827 | -231.8465 | 859.3488 | -3.294 | 0.989
83335 | -640.949 | -377.2823 | 743.7457 | -3.294 | -0.66
83345 | -549.0048 | -273.0533 | 613.1594 | 0 | 0
83355 | -478.0807 | -143.0587 | 499.026 | 0.658 | -0.329
83365 | -365.2886 | 29.4076 | 366.4705 | 2.306 | -1.317
83375 | -278.8289 | -2.3316 | 278.8387 | -0.329 | -1.318
83385 | -238.3447 | 9.5589 | 238.5363 | 0.659 | -0.989
83395 | -265.5465 | 35.842 | 267.9545 | 0.659 | 0
83405 | -417.953 | 91.5626 | 427.865 | 1.318 | 2.307
83415 | -565.7416 | 193.0217 | 597.7632 | 2.306 | 2.965
83425 | -791.6629 | 248.8381 | 829.8497 | 1.977 | 5.271
83435 | -898.0463 | 148.577 | 910.254 | -0.33 | 4.283
83445 | -936.7778 | -65.0913 | 939.0365 | -2.636 | 3.953
83455 | -871.9881 | -232.316 | 902.4046 | -2.964 | 2.307
83465 | -862.4017 | -394.5329 | 948.3633 | -3.954 | 2.964
83475 | -699.0457 | -510.7373 | 865.7467 | -3.953 | 0
83485 | -627.8328 | -513.2436 | 810.9211 | -2.636 | 0.989
83495 | -657.1389 | -454.3346 | 798.9064 | -1.648 | 1.977
83505 | -777.2643 | -477.251 | 912.0901 | -2.635 | 3.624
83515 | -826.3146 | -433.0775 | 932.9265 | -1.318 | 2.964
83525 | -886.6168 | -434.0591 | 987.1659 | -1.977 | 3.624
83535 | -838.9997 | -428.4555 | 942.0694 | -1.647 | 1.977
83545 | -776.3059 | -385.0213 | 866.5404 | -0.988 | 1.647
83555 | -778.5776 | -277.8347 | 826.6651 | 0.329 | 2.306
83565 | -807.4846 | -220.0729 | 836.9369 | 0 | 2.636
83575 | -731.6494 | -93.3049 | 737.5749 | 1.648 | 0.988
83585 | -668.1948 | 101.0068 | 675.786 | 3.295 | 0.989
83595 | -651.0148 | 200.9466 | 681.3221 | 2.635 | 1.318
83605 | -622.6853 | 337.6857 | 708.3563 | 3.953 | 0.988
83615 | -541.2675 | 446.6672 | 701.7707 | 3.953 | 0
83625 | -479.0491 | 580.3284 | 752.5085 | 4.943 | 0
83635 | -400.5408 | 608.0284 | 728.1013 | 3.624 | -0.658
83645 | -340.5316 | 584.1916 | 676.1964 | 2.964 | -0.66
83655 | -318.2931 | 577.3584 | 659.2823 | 2.966 | -0.329
83665 | -320.8778 | 526.4067 | 616.4954 | 1.976 | 0
83675 | -376.9557 | 434.9384 | 575.558 | 0.989 | 0.989
83685 | -300.8074 | 394.8918 | 496.4117 | 1.317 | -0.989
83695 | -151.6673 | 397.5432 | 425.4922 | 1.647 | -2.306
83705 | -84.4078 | 384.1799 | 393.3431 | 1.319 | -1.648
83715 | 11.9796 | 507.6643 | 507.8056 | 3.624 | -2.635
83725 | 90.9474 | 551.9141 | 559.3573 | 2.635 | -2.636
83735 | 127.5952 | 587.6614 | 601.3539 | 2.965 | -2.306
83745 | 156.3663 | 581.5673 | 602.2217 | 2.306 | -2.306
83755 | 222.4155 | 518.1545 | 563.8729 | 1.318 | -2.965
83765 | 316.942 | 589.9169 | 669.6672 | 3.294 | -3.624
83775 | 370.2496 | 601.6015 | 706.4058 | 2.307 | -3.294
83785 | 369.7542 | 578.9895 | 686.984 | 1.977 | -2.636
83795 | 315.5214 | 586.3201 | 665.8265 | 2.306 | -1.648
83805 | 243.3226 | 674.733 | 717.2661 | 3.624 | -0.988
83815 | 276.9905 | 591.0653 | 652.7495 | 0.987 | -2.305
83825 | 335.7657 | 437.0007 | 551.0973 | -0.329 | -2.637
83835 | 376.5362 | 316.5995 | 491.9499 | -0.658 | -2.635
83845 | 329.0455 | 220.7986 | 396.2613 | -0.989 | -1.318
83855 | 368.5796 | 231.4474 | 435.2227 | 0.33 | -2.635
83865 | 336.5559 | 284.6673 | 440.8008 | 0.988 | -1.318
83875 | 247.3357 | 259.2029 | 358.2752 | 0 | -0.33
83885 | 207.0913 | 306.1866 | 369.6445 | 1.318 | -0.659
83895 | 188.7185 | 425.3348 | 465.3218 | 2.635 | -0.659
83905 | 80.4773 | 528.345 | 534.439 | 2.966 | 0.989
83915 | -42.205 | 613.7464 | 615.1958 | 3.294 | 1.647
83925 | -143.0631 | 558.2152 | 576.2562 | 1.318 | 1.976
83935 | -58.4955 | 239.6499 | 246.6856 | -3.294 | -0.658
83945 | 130.5138 | -54.6242 | 141.4838 | -4.284 | -2.636
83955 | 239.4707 | -87.3684 | 254.9106 | -1.647 | -2.307
83965 | 281.4954 | -31.5379 | 283.2566 | -0.659 | -1.976
83975 | 366.9267 | -22.4255 | 367.6114 | -0.989 | -2.965
83985 | 339.7367 | 46.8789 | 342.9558 | 0.331 | -1.318
83995 | 329.3413 | -17.1393 | 329.787 | -1.648 | -1.647
84005 | 257.4362 | 13.3705 | 257.7832 | 0 | -0.329
84015 | 125.6469 | 260.7692 | 289.4611 | 3.624 | 0.988
84025 | -80.6677 | 329.6584 | 339.3847 | 1.648 | 2.965
84035 | -323.7644 | -37.1471 | 325.8884 | -4.942 | 4.613
84045 | -454.7649 | -630.704 | 777.5594 | -10.214 | 3.953
84055 | -94.6571 | -619.1886 | 626.3821 | -2.964 | -3.624
84065 | 576.2228 | -63.717 | 579.7349 | 5.271 | -10.214
84075 | 1020.7868 | -205.2766 | 1041.2224 | -3.953 | -9.883
84085 | 1022.7812 | -964.4976 | 1405.8225 | -13.509 | -5.271
84095 | 789.2075 | -1496.6192 | 1691.9567 | -13.178 | -1.648
84105 | 791.8926 | -1705.2126 | 1880.1181 | -11.201 | -4.282
84115 | 1166.9726 | -1633.0923 | 2007.191 | -7.577 | -9.883
84125 | 1728.8935 | -1433.9932 | 2246.1989 | -4.941 | -14.497
84135 | 2011.7803 | -1221.1597 | 2353.3999 | -3.295 | -12.519
84145 | 1683.4192 | -825.7898 | 1875.0544 | 1.318 | -3.953
84155 | 1426.9593 | -507.5332 | 1514.5306 | 1.977 | -3.954
84165 | 1574.8119 | -292.6654 | 1601.7757 | 2.305 | -8.565
84175 | 1800.6608 | -225.9593 | 1814.7829 | 0.988 | -9.884
84185 | 2031.3318 | -71.1184 | 2032.5764 | 2.966 | -11.201
84195 | 2237.5388 | 155.2217 | 2242.9163 | 4.612 | -11.86
84205 | 2561.083 | 435.7758 | 2597.8927 | 6.589 | -14.826
84215 | 2869.6173 | 717.9475 | 2958.0656 | 7.907 | -15.814
84225 | 3148.4289 | 978.4855 | 3296.9741 | 8.895 | -16.802
84235 | 3224.3968 | 1092.8111 | 3404.5515 | 7.578 | -14.495
84245 | 3086.2463 | 1192.3707 | 3308.5744 | 7.906 | -11.201
84255 | 2790.7009 | 1322.8042 | 3088.3365 | 8.566 | -7.578
84265 | 2504.6417 | 1451.665 | 2894.9199 | 8.896 | -5.931
84275 | 1869.9628 | 1632.2283 | 2482.1221 | 10.212 | 1.978
84285 | 1154.3015 | 1778.6553 | 2120.3836 | 10.213 | 6.259
84295 | 423.9207 | 1620.4903 | 1675.0216 | 5.601 | 10.543
84305 | -202.7161 | 1037.4348 | 1057.0548 | -2.306 | 12.518
84315 | -505.2387 | 199.5031 | 543.2013 | -9.554 | 10.214
84325 | -345.7587 | 86.2154 | 356.3456 | -1.648 | 3.953
84335 | -656.643 | 690.1458 | 952.6181 | 8.566 | 11.202
84345 | -856.0998 | 248.5755 | 891.4575 | -6.589 | 9.224
84355 | -402.6841 | -396.941 | 565.4349 | -9.883 | -0.659
84365 | -96.5464 | -538.8751 | 547.4555 | -5.272 | 0
84375 | -300.1118 | -592.8264 | 664.4623 | -5.271 | 5.931
84385 | -340.8878 | -755.2773 | 828.6424 | -6.918 | 3.293
84395 | -452.8903 | -702.0171 | 835.4266 | -3.624 | 5.272
84405 | -674.4184 | -402.597 | 785.4454 | 0.659 | 7.248
84415 | -918.3384 | -23.4742 | 918.6384 | 3.624 | 8.566
84425 | -941.9436 | 71.5855 | 944.6598 | 0.988 | 5.93
84435 | -774.7595 | -284.0435 | 825.1866 | -5.6 | 2.965
84445 | -723.4929 | -810.4589 | 1086.4095 | -9.885 | 3.954
84455 | -433.1169 | -1111.5156 | 1192.9196 | -8.894 | -0.989
84465 | -133.7609 | -1198.2952 | 1205.7377 | -7.248 | -2.306
84475 | 14.2972 | -625.085 | 625.2485 | 3.624 | -1.647
84485 | -110.3408 | -203.4433 | 231.4396 | 3.294 | 1.976
84495 | 822.1274 | -762.1869 | 1121.0809 | -10.213 | -15.814
84505 | 1630.8117 | -586.6215 | 1733.1104 | 0.988 | -16.472
84515 | 1450.5162 | -397.9095 | 1504.1041 | 0 | -4.942
84525 | 1313.8111 | -508.8597 | 1408.9137 | -3.294 | -5.93
84535 | 1294.0467 | -667.0397 | 1455.8499 | -4.283 | -5.93
84545 | 1167.3378 | -788.251 | 1408.5514 | -4.612 | -3.624
84555 | 1023.14 | -677.1206 | 1226.9098 | -1.318 | -2.636
84565 | 1034.8018 | -543.22 | 1168.7184 | -0.659 | -4.282
84575 | 1239.5752 | -638.137 | 1394.19 | -3.624 | -7.249
84585 | 1340.2918 | -806.5336 | 1564.2502 | -4.942 | -6.259
84595 | 1452.8291 | -593.6011 | 1569.4186 | 0.66 | -7.248
84605 | 1372.4295 | -292.3554 | 1403.2228 | 2.635 | -4.282
84615 | 1149.1737 | -290.8461 | 1185.4078 | -0.659 | -1.648
84625 | 999.3427 | -207.1121 | 1020.5789 | 1.317 | -1.647
84635 | 876.8386 | -429.7578 | 976.4925 | -3.953 | -0.989
84645 | 504.8157 | -830.2163 | 971.6471 | -7.577 | 3.953
84655 | -47.7372 | -931.0393 | 932.2623 | -4.612 | 8.566
84665 | -476.2853 | -887.5955 | 1007.31 | -3.295 | 9.225
84675 | -548.9659 | -807.0192 | 976.0346 | -2.306 | 5.601
84685 | -507.4235 | -855.128 | 994.3453 | -3.953 | 4.282
84695 | -848.7182 | -1197.52 | 1467.7795 | -8.896 | 10.214
84705 | -1240.9826 | -1211.814 | 1734.5117 | -4.612 | 11.86
84715 | -1474.3575 | -736.2478 | 1647.9657 | 2.965 | 11.201
84725 | -1618.9714 | -173.0949 | 1628.1985 | 6.589 | 10.872
84735 | -1622.9968 | 62.1796 | 1624.1874 | 4.283 | 8.896
84745 | -1540.639 | 36.4669 | 1541.0705 | 1.647 | 7.248
84755 | -1330.3063 | -98.3582 | 1333.9374 | -0.33 | 4.282
84765 | -1232.4142 | -161.6651 | 1242.9724 | 0 | 4.942
84775 | -1120.829 | -260.9373 | 1150.8023 | -1.317 | 3.624
84785 | -930.3962 | -427.389 | 1023.8645 | -2.965 | 1.647
84795 | -857.9326 | -638.865 | 1069.6714 | -4.612 | 2.636
84805 | -828.3343 | -785.4136 | 1141.4956 | -4.613 | 2.635
84815 | -961.4472 | -629.5245 | 1149.2092 | -0.329 | 5.272
84825 | -974.1899 | -363.9724 | 1039.9625 | 1.976 | 3.624
84835 | -886.143 | -439.3914 | 989.0976 | -2.306 | 2.306
84845 | -767.9365 | -513.1152 | 923.5874 | -1.976 | 1.318
84855 | -670.5386 | -621.7355 | 914.4272 | -3.295 | 0.988
84865 | -608.4129 | -895.3211 | 1082.4815 | -6.589 | 0.989
84875 | -529.4628 | -1118.1654 | 1237.1842 | -6.918 | 0.329
84885 | -451.0665 | -1261.6826 | 1339.8895 | -6.919 | 0
84895 | -184.6504 | -1055.4937 | 1071.5236 | -1.648 | -3.624
84905 | 2.7608 | -696.6568 | 696.6623 | 1.648 | -3.295
84915 | -112.6856 | -344.896 | 362.8378 | 3.624 | 0.66
84925 | -57.1996 | -420.0442 | 423.9209 | -1.647 | -1.977
84935 | 40.6932 | -360.8305 | 363.1179 | 0.988 | -2.307
84945 | 30.5785 | 202.0564 | 204.3571 | 9.225 | -0.988
84955 | 441.4427 | 732.8858 | 855.5661 | 10.871 | -8.237
84965 | 991.5374 | 828.8568 | 1292.3428 | 6.59 | -11.86
84975 | 1484.625 | 580.0202 | 1593.9056 | 1.647 | -13.836
84985 | 1712.7917 | 257.761 | 1732.0786 | -0.989 | -11.861
84995 | 1960.046 | -75.1669 | 1961.4868 | -3.294 | -13.507
85005 | 2015.7385 | -81.4697 | 2017.3842 | 0.33 | -10.873
85015 | 2055.4342 | 10.9787 | 2055.4635 | 1.317 | -10.872
85025 | 2193.6327 | -163.1806 | 2199.6937 | -2.635 | -12.189
85035 | 2320.4561 | -352.6052 | 2347.0933 | -3.295 | -12.19
85045 | 2345.7101 | -413.6174 | 2381.8974 | -2.306 | -10.871
85055 | 2392.9288 | -446.1484 | 2434.1645 | -2.306 | -11.201
85065 | 2394.2015 | -456.428 | 2437.3198 | -1.977 | -10.214
85075 | 2232.8207 | -312.4501 | 2254.5761 | 0.659 | -7.248
85085 | 1969.784 | -164.1499 | 1976.6118 | 1.318 | -4.612
85095 | 1703.4229 | 81.2277 | 1705.3585 | 3.953 | -2.965
85105 | 1571.5818 | 145.917 | 1578.3412 | 1.977 | -3.624
85115 | 1556.9958 | 187.5094 | 1568.246 | 2.306 | -4.612
85125 | 1630.1407 | 344.7353 | 1666.1936 | 4.283 | -5.93
85135 | 1568.892 | 374.0959 | 1612.8762 | 2.636 | -3.954
85145 | 1412.3003 | 285.3811 | 1440.845 | 0.988 | -2.307
85155 | 1110.4643 | 380.266 | 1173.7688 | 3.624 | 0.989
85165 | 794.6465 | 571.9041 | 979.0492 | 5.271 | 2.636
85175 | 657.1853 | 728.2266 | 980.9212 | 5.601 | 1.318
85185 | 747.3216 | 546.797 | 926.0003 | 0.659 | -1.648
85195 | 584.0766 | 453.7205 | 739.5998 | 1.647 | 2.306
85205 | 328.7401 | 481.849 | 583.3083 | 2.636 | 3.953
85215 | 111.1109 | 415.439 | 430.0409 | 0.988 | 4.613
85225 | -177.0299 | 224.2851 | 285.733 | -1.318 | 6.919
85235 | -223.4542 | -8.387 | 223.6115 | -2.965 | 3.953
85245 | -297.4911 | -70.5347 | 305.7386 | -1.318 | 4.942
85255 | -457.2799 | -134.2874 | 476.59 | -1.977 | 6.26
85265 | -414.1234 | -307.0322 | 515.5259 | -3.953 | 3.294
85275 | -335.5615 | -633.0257 | 716.4657 | -7.248 | 2.636
85285 | -264.1133 | -816.7463 | 858.3882 | -6.259 | 1.976
85295 | -265.42 | -852.3159 | 892.6871 | -4.942 | 2.636
85305 | -167.723 | -746.3341 | 764.9481 | -2.636 | 0.659
85315 | -304.5897 | -791.7807 | 848.3464 | -4.613 | 4.283
85325 | -358.3549 | -933.1679 | 999.6102 | -5.929 | 2.965
85335 | -301.1276 | -694.3465 | 756.8321 | 0 | 1.647
85345 | -32.2695 | -283.1546 | 284.9875 | 3.624 | -2.306
85355 | -334.3375 | 29.2425 | 335.6139 | 4.283 | 6.26
85365 | -809.1745 | 245.3692 | 845.5587 | 4.612 | 9.554
85375 | -1124.974 | 373.7828 | 1185.4451 | 4.283 | 9.554
85385 | -1290.8611 | 214.7653 | 1308.6048 | 0 | 8.895
85395 | -1159.6583 | 357.8765 | 1213.6239 | 4.612 | 4.612
85405 | -944.7366 | 339.2017 | 1003.7853 | 1.648 | 2.635
85415 | -529.9364 | 470.9595 | 708.9679 | 4.612 | -2.306
85425 | -448.1615 | 539.1713 | 701.1094 | 3.624 | 1.319
85435 | -366.606 | 363.7961 | 516.4761 | 0 | 0
85445 | 112.0878 | 268.4754 | 290.9342 | 0.658 | -6.919
85455 | 808.1795 | -136.0764 | 819.5553 | -5.6 | -12.52
85465 | 930.186 | -180.9136 | 947.6158 | -0.988 | -6.259
85475 | 956.7525 | -309.8505 | 1005.6752 | -3.624 | -6.259
85485 | 744.3324 | -299.5592 | 802.3506 | -1.318 | -1.648
85495 | 320.4412 | -485.5281 | 581.7388 | -4.942 | 2.965
85505 | 188.1459 | -553.8028 | 584.8901 | -3.294 | 0.33
85515 | 260.0152 | -524.3005 | 585.2341 | -2.306 | -1.647
85525 | 489.5302 | -490.1527 | 692.7405 | -1.977 | -4.613
85535 | 368.2111 | -668.2089 | 762.9434 | -5.271 | 0.329
85545 | 260.4414 | -1068.6369 | 1099.9157 | -9.554 | 0
85555 | 325.3921 | -977.8663 | 1030.5836 | -2.966 | -1.976
85565 | 424.094 | -554.1746 | 697.8289 | 2.306 | -2.636
85575 | 469.5361 | -457.0552 | 655.2584 | -0.988 | -2.306
85585 | 496.0944 | -444.1958 | 665.8976 | -0.988 | -2.305
85595 | 267.911 | -197.0659 | 332.5828 | 2.965 | 1.976
85605 | -239.303 | 133.4344 | 273.9902 | 5.271 | 7.578
85615 | -506.4909 | 129.3712 | 522.7523 | 1.318 | 5.929
85625 | -386.6087 | 17.3866 | 386.9994 | 0 | 1.319
85635 | -247.6303 | -26.5143 | 249.0457 | 0.329 | 0.658
85645 | -139.3505 | -270.8347 | 304.5817 | -3.623 | 0
85655 | -381.8235 | -478.5437 | 612.2036 | -3.955 | 5.272
85665 | -628.1909 | -431.5025 | 762.1143 | -0.987 | 5.93
85675 | -514.5082 | -262.9941 | 577.8275 | 0.987 | 1.318
85685 | -522.6441 | 118.9114 | 536.0007 | 5.601 | 3.293
85695 | -566.6645 | 224.6894 | 609.5851 | 2.636 | 3.295
85705 | -463.1136 | 450.9609 | 646.4054 | 5.93 | 0.989
85715 | -363.0349 | 545.4972 | 655.2568 | 4.283 | 0.659
85725 | 20.1827 | 518.0761 | 518.469 | 2.965 | -4.943
85735 | 235.7745 | 428.375 | 488.9732 | 1.648 | -3.624
85745 | 159.3173 | 316.1692 | 354.0409 | 0.658 | -0.329
85755 | 188.5796 | 131.6855 | 230.0072 | -1.318 | -1.977
85765 | 200.8602 | 291.2349 | 353.7832 | 3.624 | -1.318
85775 | 90.2619 | 443.5301 | 452.6214 | 3.624 | 0.66
85785 | 104.7585 | 625.9014 | 634.6077 | 5.272 | -0.989
85795 | 310.1003 | 607.455 | 682.0292 | 2.636 | -3.953
85805 | 389.316 | 517.8802 | 647.8942 | 1.646 | -2.635
85815 | 270.945 | 428.0681 | 506.6098 | 0.989 | 0
85825 | 219.4167 | 334.9039 | 400.3802 | 0.329 | -0.66
85835 | 50.3652 | 235.7347 | 241.055 | -0.329 | 1.977
85845 | -157.2815 | 207.0899 | 260.0456 | 0.329 | 3.294
85855 | -392.3093 | 99.0007 | 404.6081 | -1.318 | 4.943
85865 | -577.6114 | -161.647 | 599.8039 | -4.282 | 5.271
85875 | -703.437 | -239.0311 | 742.9397 | -2.306 | 5.271
85885 | -832.9526 | -327.4033 | 894.9877 | -3.295 | 5.93
85895 | -838.5503 | -463.9069 | 958.3195 | -4.283 | 4.283
85905 | -839.0171 | -547.8849 | 1002.0617 | -3.953 | 4.282
85915 | -663.7331 | -394.6432 | 772.1948 | -0.329 | 0.989
85925 | -398.0633 | -140.7619 | 422.2183 | 1.976 | -1.318
85935 | -87.7258 | 44.7725 | 98.4906 | 2.306 | -3.624
85945 | 124.5475 | 215.901 | 249.2495 | 3.295 | -3.624
85955 | 144.4029 | 355.4396 | 383.6529 | 3.624 | -1.647
85965 | 187.2651 | 413.0592 | 453.5263 | 2.965 | -2.306
85975 | 274.2067 | 393.6958 | 479.7768 | 1.976 | -2.965
85985 | 458.5465 | 382.8128 | 597.3361 | 1.977 | -4.942
85995 | 581.8807 | 424.2896 | 720.1436 | 2.636 | -4.613
86005 | 662.7832 | 404.9964 | 776.7262 | 1.648 | -4.612
86015 | 784.4289 | 444.7795 | 901.7524 | 2.635 | -5.6
86025 | 729.6381 | 543.7077 | 909.9395 | 3.624 | -2.966
86035 | 834.4058 | 675.4288 | 1073.5163 | 4.612 | -5.6
86045 | 923.432 | 694.3603 | 1155.3626 | 3.294 | -5.271
86055 | 827.6052 | 641.4623 | 1047.0933 | 2.306 | -2.636
86065 | 734.4497 | 648.0086 | 979.4547 | 2.966 | -2.306
86075 | 783.5629 | 628.3874 | 1004.411 | 2.306 | -3.953
86085 | 856.105 | 670.7374 | 1087.5681 | 3.294 | -4.284
86095 | 982.9547 | 654.5891 | 1180.9686 | 2.306 | -5.6
86105 | 1080.6885 | 732.9318 | 1305.7858 | 3.954 | -5.601
86115 | 1205.004 | 746.2218 | 1417.3502 | 2.965 | -6.589
86125 | 1359.9741 | 688.2966 | 1524.2315 | 1.977 | -7.577
86135 | 1379.8896 | 668.3191 | 1533.2142 | 2.306 | -5.93
86145 | 1291.2229 | 568.5097 | 1410.8366 | 0.659 | -4.284
86155 | 1216.4407 | 356.8586 | 1267.705 | -1.647 | -3.953
86165 | 1275.6227 | 205.3372 | 1292.0436 | -1.647 | -5.601
86175 | 1182.0385 | 34.6185 | 1182.5453 | -2.966 | -2.964
86185 | 1042.4084 | -130.6736 | 1050.5669 | -3.624 | -1.977
86195 | 993.5696 | -170.6968 | 1008.126 | -2.306 | -2.636
86205 | 895.876 | -77.8344 | 899.2508 | -0.329 | -1.317
86215 | 896.7357 | 100.7271 | 902.3751 | 1.647 | -2.636
86225 | 910.8852 | 161.9374 | 925.1679 | 0.659 | -2.635
86235 | 934.3955 | 221.8414 | 960.369 | 1.318 | -2.966
86245 | 912.8253 | 210.1516 | 936.7036 | 0.329 | -2.306
86255 | 853.7906 | 250.7677 | 889.8555 | 1.318 | -1.647
86265 | 850.326 | 365.7698 | 925.6575 | 2.635 | -2.306
86275 | 970.5358 | 545.9322 | 1113.5447 | 4.283 | -4.283
86285 | 1101.1927 | 636.5735 | 1271.9478 | 3.624 | -4.942
86295 | 1090.3657 | 708.7231 | 1300.456 | 3.953 | -3.295
86305 | 1146.9624 | 689.6843 | 1338.3524 | 2.637 | -4.611
86315 | 1203.4542 | 710.9385 | 1397.7609 | 3.294 | -4.613
86325 | 1125.4082 | 779.0222 | 1368.729 | 3.954 | -2.635
86335 | 947.0066 | 755.8599 | 1211.6707 | 2.635 | -0.66
86345 | 861.9816 | 714.0305 | 1119.3087 | 2.306 | -1.317
86355 | 780.6259 | 616.0358 | 994.423 | 0.989 | -0.66
86365 | 622.5651 | 450.2276 | 768.3048 | -0.659 | 0.989
86375 | 504.3433 | 411.2583 | 650.7653 | 0.659 | 0.988
86385 | 484.861 | 439.6028 | 654.4775 | 1.318 | 0
86395 | 570.0002 | 438.3153 | 719.0414 | 0.988 | -1.646
86405 | 629.3869 | 238.1393 | 672.9325 | -2.306 | -1.648
86415 | 619.349 | 21.9017 | 619.7362 | -3.295 | -0.989
86425 | 584.6316 | -82.097 | 590.3677 | -2.635 | -0.658
86435 | 540.0405 | -51.18 | 542.4602 | -0.989 | -0.329
86445 | 488.1157 | -123.6963 | 503.5451 | -2.635 | 0
86455 | 449.9558 | -101.759 | 461.3189 | -0.989 | 0
86465 | 403.6483 | -191.9186 | 446.9505 | -2.965 | 0.329
86475 | 386.24 | -105.1317 | 400.2924 | 0 | 0
86485 | 336.1118 | -5.5423 | 336.1575 | 0.33 | 0.658
86495 | 254.4216 | -66.8434 | 263.0559 | -1.648 | 1.318
86505 | 231.6964 | -12.532 | 232.0351 | 0.329 | 0.659
86515 | 219.4189 | 23.5963 | 220.684 | 0 | 0.66
86525 | 262.1328 | 94.8389 | 278.7615 | 0.989 | -0.331
86535 | 216.077 | 33.5801 | 218.6708 | -0.989 | 0.989
86545 | 91.3332 | 12.8877 | 92.238 | -0.329 | 2.306
86555 | 152.8363 | 29.6028 | 155.6768 | 0 | -0.329
86565 | 195.0649 | 79.3185 | 210.5748 | 0.659 | 0
86575 | 265.4042 | 95.8661 | 282.1874 | 0.329 | -0.989
86585 | 527.861 | 159.2627 | 551.3636 | 1.318 | -4.612
86595 | 782.2053 | 171.5478 | 800.7957 | 0.66 | -5.601
86605 | 1081.5955 | 172.1742 | 1095.2135 | 0.658 | -7.906
86615 | 1375.4741 | 214.2759 | 1392.0643 | 1.318 | -9.225
86625 | 1389.6516 | 210.3145 | 1405.4764 | 0.659 | -5.93
86635 | 1458.902 | 297.9395 | 1489.0141 | 2.306 | -7.248
86645 | 1789.7472 | 372.126 | 1828.0243 | 2.306 | -11.531
86655 | 2109.709 | 552.5892 | 2180.8775 | 4.613 | -12.519
86665 | 2194.9758 | 788.4396 | 2332.2855 | 6.259 | -10.214
86675 | 1997.2204 | 666.3378 | 2105.4443 | 1.318 | -5.93
86685 | 1687.0759 | 452.9096 | 1746.812 | -0.329 | -2.964
86695 | 1394.3051 | 284.1329 | 1422.9611 | -0.989 | -1.318
86705 | 1266.7772 | 255.6264 | 1292.3117 | 0.329 | -2.306
86715 | 1219.0511 | 346.1513 | 1267.2436 | 1.977 | -2.636
86725 | 1243.9512 | 278.3276 | 1274.7081 | -0.329 | -3.624
86735 | 1437.1894 | 73.9086 | 1439.0885 | -2.636 | -6.589
86745 | 1832.4721 | 3.9533 | 1832.4764 | -1.318 | -10.872
86755 | 2232.9995 | 223.4961 | 2244.1562 | 2.966 | -12.849
86765 | 2350.3648 | 278.4695 | 2366.8038 | 0.988 | -10.212
86775 | 2296.9235 | 282.0826 | 2314.1798 | 0.988 | -8.237
86785 | 2193.2885 | 116.4432 | 2196.3773 | -1.976 | -6.918
86795 | 2348.3181 | 23.638 | 2348.4371 | -1.318 | -10.543
86805 | 2322.7384 | -4.1697 | 2322.7422 | -0.988 | -7.577
86815 | 2204.9262 | 33.6825 | 2205.1834 | 0 | -6.26
86825 | 1943.1326 | 61.4221 | 1944.1031 | 0 | -2.965
86835 | 1622.9145 | 226.8344 | 1638.6901 | 2.635 | -0.658
86845 | 966.3778 | 258.057 | 1000.2397 | 0.988 | 6.918
86855 | 403.4704 | 372.4105 | 549.07 | 2.965 | 8.236
86865 | -97.7615 | 354.2608 | 367.5024 | 0.989 | 10.542
86875 | -151.9552 | 54.6615 | 161.4876 | -3.624 | 5.272
86885 | -30.2272 | 2.7534 | 30.3523 | -0.659 | 2.965
86895 | 24.1246 | 7.3223 | 25.2114 | -0.659 | 2.965
86905 | -203.0855 | -77.7261 | 217.4513 | -1.977 | 6.918
86915 | -307.0163 | -359.9729 | 473.1168 | -5.6 | 5.272
86925 | -289.6398 | -478.2961 | 559.1586 | -3.954 | 3.953
86935 | -288.9734 | -576.1659 | 644.5717 | -4.613 | 3.953
86945 | -193.9623 | -466.8431 | 505.5332 | -1.317 | 1.977
86955 | -379.9752 | -588.645 | 700.6312 | -4.942 | 6.259
86965 | -765.6388 | -582.0051 | 961.7342 | -2.635 | 9.885
86975 | -1219.1227 | -556.4867 | 1340.126 | -2.636 | 12.848
86985 | -1466.3649 | -534.1023 | 1560.6061 | -2.306 | 11.531
86995 | -1436.699 | -542.8989 | 1535.8526 | -2.636 | 8.236
87005 | -1438.4333 | -538.238 | 1535.8355 | -2.306 | 8.566
87015 | -1342.5998 | -343.7352 | 1385.9033 | 0.989 | 6.259
87025 | -1262.9413 | -136.7931 | 1270.3279 | 1.976 | 5.93
87035 | -1194.0163 | 129.5691 | 1201.0259 | 4.283 | 5.272
87045 | -1158.6205 | 263.3792 | 1188.1793 | 3.295 | 5.271
87055 | -1052.0872 | 303.3856 | 1094.9568 | 2.635 | 3.624
87065 | -843.1962 | 297.1565 | 894.0256 | 1.976 | 1.318
87075 | -852.9445 | 318.5551 | 910.4898 | 2.307 | 3.953
87085 | -929.9789 | 326.292 | 985.5594 | 1.977 | 4.612
87095 | -999.2003 | 142.48 | 1009.3076 | -1.318 | 4.942
87105 | -1066.2726 | -36.2967 | 1066.8902 | -1.977 | 5.272
87115 | -1038.8235 | 8.5038 | 1038.8583 | 0.659 | 3.953
87125 | -1072.0364 | 196.2735 | 1089.8556 | 2.965 | 4.941
87135 | -1053.6769 | 309.2688 | 1098.1267 | 2.635 | 3.955
87145 | -959.0918 | 200.6489 | 979.8556 | -0.329 | 2.635
87155 | -797.8264 | 128.5363 | 808.1142 | 0 | 0.988
87165 | -647.9952 | 19.6294 | 648.2924 | -1.318 | 0.33
87175 | -512.0931 | 15.6946 | 512.3335 | 0 | -0.33
87185 | -283.5507 | 161.7542 | 326.4435 | 2.307 | -2.636
87195 | -228.3539 | 328.496 | 400.0689 | 3.294 | -0.658
87205 | -381.4643 | 457.5961 | 595.7425 | 3.624 | 2.306
87215 | -703.5586 | 525.0064 | 877.8533 | 3.295 | 5.93
87225 | -966.8558 | 474.628 | 1077.071 | 1.647 | 6.589
87235 | -1017.0005 | 397.4661 | 1091.9109 | 0.988 | 4.612
87245 | -863.1983 | 314.2961 | 918.6367 | 0.33 | 1.647
87255 | -771.3106 | 203.1819 | 797.6233 | -0.659 | 1.977
87265 | -787.0281 | 87.9096 | 791.9226 | -1.318 | 2.966
87275 | -750.1652 | -9.276 | 750.2226 | -1.647 | 1.976
87285 | -677.8232 | -287.0774 | 736.1099 | -5.271 | 1.317
87295 | -455.8811 | -462.8985 | 649.6942 | -4.613 | -1.646
87305 | -115.5182 | -529.9961 | 542.4392 | -3.954 | -4.613
87315 | 67.3757 | -502.6445 | 507.14 | -2.635 | -3.624
87325 | 138.3048 | -467.8546 | 487.869 | -2.306 | -2.964
87335 | 116.1473 | -283.3394 | 306.2212 | 0.659 | -1.648
87345 | -29.1878 | -147.3908 | 150.2531 | 0.658 | 0.659
87355 | -281.903 | -110.181 | 302.67 | 0 | 3.295
87365 | -550.0236 | -131.0626 | 565.4232 | -0.658 | 4.941
87375 | -631.7835 | -243.2066 | 676.9785 | -2.306 | 3.294
87385 | -400.0115 | -365.401 | 541.7814 | -2.966 | -1.318
87395 | 48.0193 | -407.6841 | 410.5024 | -2.305 | -5.93
87405 | 399.3863 | -334.4956 | 520.9575 | -0.659 | -6.588
87415 | 738.5194 | -183.228 | 760.9096 | 0.988 | -8.566
87425 | 888.3277 | -2.6352 | 888.3316 | 2.306 | -6.919
87435 | 906.2709 | 215.9625 | 931.6473 | 3.953 | -5.601
87445 | 757.4803 | 293.5337 | 812.366 | 2.636 | -2.635
87455 | 485.0756 | 276.3779 | 558.2858 | 1.648 | 0.329
87465 | 382.5407 | 229.7961 | 446.2552 | 0.987 | -0.988
87475 | 382.1192 | 166.0939 | 416.656 | 0.33 | -1.647
87485 | 348.7306 | 107.4705 | 364.915 | 0 | -0.989
87495 | 378.3944 | 110.4152 | 394.1749 | 0.659 | -1.976
87505 | 409.0819 | 178.2421 | 446.2267 | 1.648 | -1.977
87515 | 408.6904 | 306.4476 | 510.8209 | 2.964 | -1.647
87525 | 369.279 | 380.2589 | 530.0602 | 2.636 | -0.988
87535 | 264.7661 | 463.2281 | 533.5554 | 3.294 | 0.329
87545 | 266.5909 | 470.7539 | 540.999 | 2.307 | -0.989
87555 | 167.8743 | 452.2105 | 482.3651 | 1.977 | 0.989
87565 | 102.3844 | 234.5764 | 255.9466 | -1.648 | 0.659
87575 | 201.2624 | 87.9904 | 219.6563 | -1.318 | -1.648
87585 | 320.3699 | 27.0524 | 321.51 | -0.988 | -2.306
87595 | 298.9555 | 7.3629 | 299.0461 | -0.659 | -0.658
87605 | 327.4046 | 107.9718 | 344.7487 | 1.318 | -1.648
87615 | 226.123 | 146.6849 | 269.5331 | 0.658 | 0.659
87625 | 140.2638 | 100.7946 | 172.7238 | -0.329 | 0.659
87635 | 91.6316 | -13.1289 | 92.5674 | -1.647 | 0.659
87645 | 174.7144 | -95.5886 | 199.154 | -1.648 | -1.318
87655 | 108.5103 | -108.3627 | 153.3524 | -0.987 | 0.989
87665 | 96.5121 | -95.1004 | 135.4941 | -0.659 | 0
87675 | 102.0509 | -89.5138 | 135.7465 | -0.659 | 0
87685 | 236.2855 | -167.1735 | 289.444 | -1.977 | -2.306
87695 | 72.3489 | -96.9074 | 120.9355 | 0.329 | 2.306
87705 | -60.1722 | 26.7549 | 65.8523 | 1.318 | 1.976
87715 | -207.9785 | 183.5134 | 277.3665 | 2.635 | 3.295
87725 | -414.0543 | 389.0783 | 568.175 | 4.284 | 4.941
87735 | -659.7838 | 419.7736 | 782.0003 | 2.306 | 6.59
87745 | -990.3686 | 481.5454 | 1101.2339 | 3.295 | 9.225
87755 | -1156.9413 | 542.3795 | 1277.7671 | 3.293 | 7.906
87765 | -1108.1154 | 413.769 | 1182.846 | 0.331 | 5.272
87775 | -1056.1936 | 331.1181 | 1106.8803 | 0.658 | 4.941
87785 | -928.8432 | 159.3152 | 942.4071 | -1.647 | 2.965
87795 | -805.6993 | 11.0458 | 805.775 | -1.977 | 2.306
87805 | -696.7382 | -82.1558 | 701.5652 | -1.976 | 1.647
87815 | -609.1457 | -144.9763 | 626.1602 | -1.977 | 1.319
87825 | -573.3096 | -229.5189 | 617.5458 | -2.635 | 1.647
87835 | -535.274 | -161.643 | 559.1482 | -0.331 | 1.317
87845 | -487.4938 | -160.1747 | 513.1336 | -1.317 | 0.989
87855 | -473.1224 | -102.585 | 484.1162 | 0 | 1.318
87865 | -562.5642 | 1.9558 | 562.5676 | 0.988 | 2.964
87875 | -632.6625 | -100.8425 | 640.6489 | -1.976 | 2.966
87885 | -692.683 | -215.6309 | 725.4698 | -2.306 | 3.295
87895 | -678.201 | -150.9218 | 694.7906 | 0 | 2.306
87905 | -624.1206 | -32.9736 | 624.9911 | 0.987 | 1.647
87915 | -608.6009 | 81.1289 | 613.9845 | 1.648 | 1.977
87925 | -720.7779 | 271.9376 | 770.3706 | 3.624 | 3.953
87935 | -829.9819 | 412.0943 | 926.6562 | 3.624 | 4.283
87945 | -938.5174 | 482.6586 | 1055.355 | 3.295 | 4.942
87955 | -1055.6502 | 628.3707 | 1228.5142 | 4.942 | 5.6
87965 | -1045.1482 | 611.3063 | 1210.7973 | 2.635 | 3.954
87975 | -991.248 | 661.9146 | 1191.9327 | 3.953 | 3.294
87985 | -981.7891 | 624.7256 | 1163.6975 | 2.306 | 3.624
87995 | -1005.6237 | 610.4055 | 1176.3817 | 2.636 | 3.954
88005 | -1008.137 | 653.3147 | 1201.3161 | 3.294 | 3.624
88015 | -990.5698 | 556.9172 | 1136.3913 | 0.989 | 3.294
88025 | -865.6603 | 304.6832 | 917.7144 | -1.977 | 1.318
88035 | -387.6215 | -296.9387 | 488.2858 | -9.224 | -5.272
88045 | 9.8534 | -778.8002 | 778.8625 | -9.884 | -5.93
88055 | 508.9678 | -1084.8527 | 1198.3128 | -9.884 | -10.212
88065 | 801.8604 | -1086.807 | 1350.6034 | -6.259 | -8.896
88075 | 892.2612 | -849.9133 | 1232.2673 | -2.306 | -7.248
88085 | 772.1118 | -560.9863 | 954.391 | 0 | -3.953
88095 | 561.0608 | -343.9374 | 658.0898 | 0.658 | -1.647
88105 | 107.7142 | -193.9568 | 221.8593 | 0.989 | 3.953
88115 | -328.5509 | -2.0206 | 328.5571 | 2.636 | 5.93
88125 | -530.6571 | 98.8756 | 539.7901 | 1.976 | 4.613
88135 | -494.8339 | 43.5267 | 496.7446 | 0 | 1.976
88145 | -481.9058 | -39.5408 | 483.5253 | -0.658 | 2.306
88155 | -378.6462 | -145.503 | 405.6404 | -1.648 | 0.33
88165 | -282.6151 | -255.7507 | 381.1557 | -2.306 | 0
88175 | -304.3383 | -195.1059 | 361.5081 | 0 | 1.318
88185 | -351.6362 | -97.7684 | 364.9749 | 0.659 | 1.647
88195 | -362.6689 | -114.5452 | 380.3279 | -0.659 | 1.318
88205 | -558.9096 | -43.3047 | 560.5848 | 0.988 | 4.612
88215 | -735.7675 | -17.4667 | 735.9748 | 0.329 | 4.942
88225 | -828.3478 | 125.0632 | 837.7355 | 2.637 | 4.612
88235 | -967.5451 | 67.3739 | 969.888 | -0.33 | 5.93
88245 | -963.031 | 1.6604 | 963.0325 | -0.329 | 3.953
88255 | -795.549 | 239.3681 | 830.7799 | 4.283 | 1.318
88265 | -775.2838 | 415.8797 | 879.7845 | 3.953 | 2.966
88275 | -770.8604 | 479.4807 | 907.8147 | 3.295 | 2.635
88285 | -860.6999 | 521.7456 | 1006.4903 | 3.293 | 4.283
88295 | -993.8667 | 424.9496 | 1080.9039 | 0.989 | 5.271
88305 | -1010.5498 | 350.9086 | 1069.7419 | 0.989 | 3.953
88315 | -954.8081 | 315.5774 | 1005.608 | 0.988 | 2.966
88325 | -843.0359 | 354.4516 | 914.5192 | 1.977 | 1.647
88335 | -633.0109 | 466.8932 | 786.5698 | 3.294 | -0.658
88345 | -406.8165 | 646.2188 | 763.6088 | 4.942 | -1.978
88355 | -254.7847 | 641.4263 | 690.176 | 2.636 | -1.977
88365 | -213.0294 | 600.509 | 637.1755 | 2.306 | -0.988
88375 | -109.8867 | 468.9031 | 481.6069 | 0.329 | -2.305
88385 | 75.6673 | 220.0446 | 232.6912 | -2.306 | -3.954
88395 | 330.3657 | 102.4901 | 345.8984 | -1.318 | -5.931
88405 | 536.5183 | 2.743 | 536.5253 | -1.977 | -6.259
88415 | 583.8142 | -247.2903 | 634.028 | -4.941 | -4.612
88425 | 595.4237 | -477.5803 | 763.2905 | -5.601 | -4.283
88435 | 793.3613 | -805.5705 | 1130.6485 | -8.566 | -7.248
88445 | 981.471 | -1072.053 | 1453.4727 | -8.895 | -7.578
88455 | 842.9566 | -985.8305 | 1297.0881 | -4.283 | -2.964
88465 | 632.1668 | -677.6264 | 926.7213 | -0.329 | -1.318
88475 | 508.4526 | -417.2849 | 657.7619 | 0.658 | -1.318
88485 | 269.669 | -51.7556 | 274.5906 | 4.284 | 1.647
88495 | 94.2105 | 131.9685 | 162.1459 | 2.965 | 1.647
88505 | -30.3953 | 59.8821 | 67.1546 | 0 | 1.977
88515 | -136.195 | 190.9953 | 234.5811 | 3.294 | 2.306
88525 | -193.1721 | 243.3535 | 310.703 | 1.977 | 1.977
88535 | -386.7792 | 456.313 | 598.1803 | 5.271 | 4.612
88545 | -561.8093 | 690.1117 | 889.8786 | 6.26 | 4.942
88555 | -851.9254 | 830.4037 | 1189.6836 | 5.93 | 7.907
88565 | -958.8808 | 715.2991 | 1196.288 | 2.306 | 5.93
88575 | -1054.9122 | 662.4918 | 1245.6866 | 2.965 | 6.589
88585 | -1085.2892 | 578.8862 | 1230.0251 | 1.647 | 5.6
88595 | -898.8709 | 482.168 | 1020.0269 | 0.988 | 1.978
88605 | -782.8354 | 499.8336 | 928.7975 | 2.307 | 2.306
88615 | -730.8761 | 508.3158 | 890.2611 | 1.977 | 2.306
88625 | -702.7316 | 432.4543 | 825.1354 | 0.658 | 2.306
88635 | -764.5387 | 355.6546 | 843.2138 | 0.33 | 3.624
88645 | -779.5824 | 385.0169 | 869.475 | 1.647 | 2.965
88655 | -628.8683 | 358.7932 | 724.022 | 0.66 | 0.329
88665 | -417.4712 | 329.2812 | 531.7032 | 0.658 | -1.318
88675 | -179.5523 | 331.698 | 377.1771 | 0.988 | -2.964
88685 | -110.4499 | 278.1744 | 299.2995 | 0 | -1.318
88695 | -97.7018 | 175.981 | 201.2833 | -0.988 | -0.989
88705 | -41.5684 | 141.5483 | 147.5258 | -0.329 | -1.646
88715 | 9.3167 | 67.8909 | 68.5271 | -1.318 | -1.648
88725 | 28.1393 | 45.3405 | 53.3627 | -0.659 | -1.318
88735 | 63.2192 | 73.6287 | 97.0456 | 0 | -1.647
88745 | 76.7536 | 111.0737 | 135.0129 | 0.329 | -1.318
88755 | 68.4881 | 94.4747 | 116.688 | -0.329 | -0.988
88765 | 28.1969 | 94.1257 | 98.2584 | 0 | -0.329
88775 | -151.4508 | 135.3596 | 203.1245 | 0.659 | 2.305
88785 | -208.0359 | 223.0847 | 305.0339 | 1.647 | 0.988
88795 | -359.6976 | 208.7057 | 415.8611 | 0.329 | 3.295
88805 | -539.9359 | 320.3269 | 627.8058 | 2.636 | 4.283
88815 | -700.838 | 493.8187 | 857.3394 | 3.954 | 4.942
88825 | -736.698 | 670.9043 | 996.4118 | 4.941 | 3.624
88835 | -755.0833 | 775.3134 | 1082.2484 | 4.613 | 3.624
88845 | -702.668 | 786.8027 | 1054.8937 | 3.624 | 2.306
88855 | -665.8108 | 814.7787 | 1052.2207 | 3.953 | 2.306
88865 | -613.5162 | 847.3627 | 1046.148 | 3.953 | 1.647
88875 | -578.714 | 817.9797 | 1001.9983 | 2.965 | 1.647
88885 | -503.2951 | 816.8923 | 959.4889 | 3.295 | 0.66
88895 | -543.7915 | 866.302 | 1022.8334 | 3.953 | 2.306
88905 | -587.247 | 869.9068 | 1049.5698 | 3.295 | 2.306
88915 | -572.7916 | 888.8407 | 1057.4158 | 3.624 | 1.647
88925 | -616.242 | 891.2847 | 1083.5786 | 3.295 | 2.635
88935 | -656.2206 | 893.8036 | 1108.8329 | 3.294 | 2.637
88945 | -584.9876 | 842.9255 | 1026.0282 | 2.306 | 0.987
88955 | -565.4336 | 843.8885 | 1015.8065 | 2.965 | 1.648
88965 | -507.0325 | 836.6486 | 978.2959 | 2.636 | 0.659
88975 | -421.4678 | 848.8526 | 947.7266 | 2.964 | 0
88985 | -343.5327 | 785.5387 | 857.3714 | 1.648 | -0.33
88995 | -309.9057 | 715.0869 | 779.3528 | 1.318 | 0
89005 | -250.6934 | 613.7828 | 663.0057 | 0.329 | -0.658
89015 | -144.5814 | 560.0777 | 578.4383 | 0.66 | -1.648
89025 | -46.1257 | 433.0191 | 435.4689 | -0.989 | -1.976
89035 | 22.5259 | 313.8032 | 314.6106 | -1.318 | -1.977
89045 | 148.9395 | 195.6318 | 245.8756 | -1.977 | -3.295
89055 | 210.4551 | 108.7894 | 236.9103 | -1.977 | -2.635
89065 | 268.1892 | 104.8619 | 287.9609 | -0.987 | -2.966
89075 | 299.2277 | 102.6096 | 316.332 | -0.989 | -2.635
89085 | 285.7976 | 13.8027 | 286.1307 | -2.306 | -1.976
89095 | 222.9022 | 34.2838 | 225.5233 | -0.659 | -0.989
89105 | 221.2018 | 58.7856 | 228.8798 | -0.659 | -1.648
89115 | 233.9356 | 160.3096 | 283.5931 | 0.989 | -1.647
89125 | 225.3669 | 215.616 | 311.8982 | 0.658 | -1.317
89135 | 162.9405 | 260.4014 | 307.1783 | 0.989 | -0.329
89145 | 176.0502 | 272.5541 | 324.4679 | 0.659 | -1.318
89155 | 140.5585 | 199.9019 | 244.3716 | -0.659 | -0.33
89165 | 204.3378 | 142.7792 | 249.2786 | -0.66 | -1.976
89175 | 244.537 | 109.1298 | 267.7829 | -0.658 | -1.648
89185 | 265.0709 | 85.6846 | 278.5757 | -0.659 | -1.647
89195 | 320.0565 | 48.6126 | 323.7273 | -0.988 | -2.306
89205 | 364.5113 | -0.48498 | 364.5116 | -1.319 | -2.307
89215 | 414.1729 | 39.5453 | 416.0565 | 0 | -2.635
89225 | 453.13 | 54.9288 | 456.4471 | -0.329 | -2.635
89235 | 482.1487 | 36.104 | 483.4986 | -0.658 | -2.637
89245 | 505.6754 | 19.3784 | 506.0466 | -0.66 | -2.635
89255 | 449.0203 | 46.0152 | 451.372 | 0 | -1.318
89265 | 367.4014 | 9.2439 | 367.5176 | -0.988 | -0.658
89275 | 335.6955 | -26.716 | 336.7569 | -0.989 | -0.989
89285 | 302.8261 | -29.8741 | 304.2961 | -0.658 | -0.659
89295 | 259.3453 | -31.2495 | 261.2212 | -0.659 | -0.329
89305 | 152.4106 | -35.5133 | 156.4934 | -0.659 | 0.988
89315 | 110.7275 | -21.3804 | 112.7728 | -0.33 | 0.329
89325 | 110.426 | 7.8232 | 110.7027 | 0 | 0
89335 | 127.7825 | 46.2312 | 135.8886 | 0.33 | -0.329
89345 | 157.2805 | 33.3984 | 160.7874 | -0.33 | -0.659
89355 | 156.9486 | 37.4199 | 161.3478 | 0 | -0.329
89365 | 171.1317 | 6.1476 | 171.2421 | -0.658 | -0.66
89375 | 144.937 | -20.8669 | 146.4314 | -0.66 | 0
89385 | 82.6928 | -17.9148 | 84.6111 | -0.329 | 0.66
89395 | -57.8986 | 62.6698 | 85.3215 | 0.989 | 2.306
89405 | -162.3174 | 104.6174 | 193.1107 | 0.658 | 2.306
89415 | -170.7701 | 67.3721 | 183.5795 | -0.329 | 1.318
89425 | -191.8013 | 55.5846 | 199.6932 | 0 | 1.647
89435 | -158.8563 | 35.1911 | 162.7075 | -0.329 | 0.659
89445 | -171.7587 | 18.615 | 172.7645 | -0.329 | 1.318
89455 | -153.9217 | -30.0812 | 156.8335 | -0.989 | 0.658
89465 | -138.3413 | -67.8402 | 154.0799 | -0.988 | 0.659
89475 | -151.8634 | -111.0002 | 188.1051 | -1.318 | 0.989
89485 | -146.2649 | -143.6377 | 205.0005 | -1.318 | 0.658
89495 | -159.9719 | -147.1558 | 217.3611 | -0.988 | 0.989
89505 | -154.9424 | -130.3516 | 202.4813 | -0.66 | 0.659
89515 | -149.6189 | -101.1306 | 180.5913 | -0.329 | 0.659
89525 | -167.7438 | -82.6532 | 187.0014 | -0.329 | 0.988
89535 | -164.4614 | -15.5961 | 165.1993 | 0.658 | 0.659
89545 | -159.9162 | 35.515 | 163.8125 | 0.66 | 0.659
89555 | -159.1353 | 27.5493 | 161.5024 | 0 | 0.659
89565 | -179.0692 | -1.4772 | 179.0753 | -0.33 | 0.989
89575 | -176.4648 | 37.8187 | 180.4719 | 0.659 | 0.658
89585 | -191.4185 | -3.3545 | 191.4479 | -0.659 | 0.989
89595 | -128.9938 | -24.1287 | 131.2311 | -0.33 | -0.33
89605 | -58.4039 | -50.0352 | 76.906 | -0.658 | -0.659
89615 | -33.2319 | -89.848 | 95.7968 | -0.989 | -0.329
89625 | -20.084 | -118.316 | 120.0086 | -0.988 | -0.329
89635 | 10.2359 | -156.3533 | 156.688 | -1.318 | -0.66
89645 | 72.8584 | -166.3283 | 181.5859 | -0.988 | -1.317
89655 | 120.0494 | -152.1029 | 193.7709 | -0.659 | -1.318
89665 | 151.2032 | -143.3015 | 208.3212 | -0.659 | -1.318
89675 | 174.3541 | -121.3086 | 212.4032 | -0.329 | -1.317
89685 | 192.9321 | -105.7622 | 220.0192 | -0.329 | -1.319
89695 | 189.1662 | -59.1495 | 198.1982 | 0.329 | -0.988
89705 | 225.7544 | -43.0271 | 229.8181 | 0 | -1.648
89715 | 239.7145 | -56.1946 | 246.2131 | -0.329 | -1.317
89725 | 227.9555 | -46.8196 | 232.7139 | 0 | -0.989
89735 | 202.0242 | 21.2297 | 203.1366 | 0.987 | -0.658
89745 | 205.3215 | 73.4579 | 218.0664 | 0.989 | -0.989
89755 | 213.1418 | 163.2374 | 268.4695 | 1.977 | -0.988
89765 | 199.6287 | 135.6205 | 241.339 | 0.329 | -0.659
89775 | 266.3034 | 161.8327 | 311.6205 | 1.318 | -1.977
89785 | 284.4254 | 175.7151 | 334.3255 | 0.988 | -1.317
89795 | 346.4067 | 182.3556 | 391.4731 | 0.989 | -2.307
89805 | 379.716 | 190.0518 | 424.6221 | 0.988 | -1.977
89815 | 418.0082 | 178.3517 | 454.4669 | 0.658 | -2.306
89825 | 430.6273 | 151.1872 | 456.3962 | 0.331 | -1.976
89835 | 438.9863 | 114.3375 | 453.6321 | 0 | -1.977
89845 | 449.0464 | 109.088 | 462.107 | 0.329 | -1.977
89855 | 382.1721 | 186.8532 | 425.4053 | 1.647 | -0.658
89865 | 330.8901 | 209.2672 | 391.5112 | 0.988 | -0.66
89875 | 322.6625 | 176.8531 | 367.9512 | 0.329 | -0.988
89885 | 321.1661 | 230.5159 | 395.3292 | 1.648 | -0.988
89895 | 319.4213 | 241.5994 | 400.5 | 0.989 | -0.988
89905 | 337.5884 | 260.3971 | 426.348 | 1.318 | -1.318
89915 | 352.3927 | 278.8606 | 449.3816 | 1.317 | -1.318
89925 | 380.8031 | 349.7676 | 517.0574 | 2.306 | -1.648
89935 | 325.8671 | 387.0706 | 505.9773 | 1.977 | -0.329
89945 | 298.5779 | 350.7848 | 460.6504 | 0.988 | -0.659
89955 | 403.4613 | 303.8386 | 505.0732 | 0.659 | -2.636
89965 | 468.3725 | 199.5619 | 509.1147 | -0.659 | -2.306
89975 | 502.8717 | 85.1766 | 510.0344 | -1.318 | -2.306
89985 | 470.5398 | -48.5236 | 473.0351 | -2.306 | -1.318
89995 | 425.1573 | -66.8376 | 430.3789 | -0.988 | -0.988
90005 | 456.0854 | 65.5463 | 460.7713 | 1.317 | -1.976
90015 | 448.8814 | 143.3293 | 471.2088 | 0.989 | -1.318
90025 | 494.766 | 27.4599 | 495.5274 | -1.647 | -2.306
90035 | 478.22 | 26.0201 | 478.9273 | 0 | -1.318
90045 | 458.0578 | 65.148 | 462.6674 | 0.329 | -1.318
90055 | 468.5083 | 87.6646 | 476.6394 | 0.329 | -1.648
90065 | 421.7314 | 138.3785 | 443.8535 | 0.989 | -0.658
90075 | 363.8822 | 118.7376 | 382.7648 | 0 | -0.33
90085 | 345.8835 | 173.0699 | 386.7668 | 1.318 | -0.658
90095 | 337.6804 | 222.7483 | 404.5304 | 1.317 | -0.66
90105 | 291.8558 | 214.0635 | 361.9434 | 0.66 | 0
90115 | 255.2289 | 223.453 | 339.2242 | 0.988 | 0
90125 | 193.3174 | 197.5956 | 276.4338 | 0.329 | 0.66
90135 | 145.7804 | 156.8481 | 214.1337 | 0 | 0.658
90145 | 114.0717 | 149.722 | 188.226 | 0.329 | 0.659
90155 | 109.5343 | 149.3492 | 185.2105 | 0.331 | 0.329
90165 | 67.2891 | 51.8451 | 84.9455 | -1.318 | 0.989
90175 | 10.7487 | -6.5895 | 12.6078 | -0.989 | 1.318
90185 | -68.7458 | -38.2316 | 78.6615 | -0.988 | 1.977
90195 | -147.8872 | -100.2983 | 178.6907 | -1.647 | 2.306
90205 | -166.3377 | -110.9242 | 199.931 | -0.989 | 1.647
90215 | -234.8958 | -113.8701 | 261.041 | -0.988 | 2.635
90225 | -276.1582 | -140.4068 | 309.8022 | -1.318 | 2.306
90235 | -322.6318 | -240.6494 | 402.4965 | -2.635 | 2.636
90245 | -381.6161 | -242.2518 | 452.0142 | -1.319 | 2.965
90255 | -408.8016 | -270.5675 | 490.2301 | -1.976 | 2.636
90265 | -409.8094 | -302.3475 | 509.2718 | -1.977 | 2.306
90275 | -414.9167 | -325.5227 | 527.3717 | -1.977 | 2.306
90285 | -405.8889 | -344.4971 | 532.3758 | -1.976 | 1.977
90295 | -383.2232 | -360.9657 | 526.4563 | -1.977 | 1.647
90305 | -371.1111 | -318.0368 | 488.7441 | -0.989 | 1.647
90315 | -425.6361 | -324.0158 | 534.9321 | -1.647 | 2.637
90325 | -472.2989 | -320.0895 | 570.5467 | -1.317 | 2.635
90335 | -483.6897 | -219.4571 | 531.147 | 0.329 | 2.306
90345 | -530.353 | -200.6539 | 567.0417 | -0.658 | 2.965
90355 | -571.1971 | -125.6051 | 584.8442 | 0.658 | 2.965
90365 | -580.9499 | -43.7451 | 582.5946 | 0.988 | 2.636
90375 | -531.2512 | 9.9041 | 531.3435 | 0.989 | 1.647
90385 | -457.6439 | -11.7407 | 457.7945 | 0 | 0.988
90395 | -429.9946 | 7.4178 | 430.0586 | 0.658 | 1.318
90405 | -418.8766 | 127.4221 | 437.8287 | 2.307 | 1.318
90415 | -430.9037 | 143.1721 | 454.0663 | 0.988 | 1.648
90425 | -384.0972 | 102.3737 | 397.506 | 0.329 | 0.658
90435 | -344.9925 | 77.8752 | 353.6727 | 0.33 | 0.659
90445 | -245.7406 | 67.4358 | 254.8254 | 0.33 | -0.659
90455 | -131.4622 | -33.177 | 135.584 | -1.318 | -1.318
90465 | -149.8073 | -207.1663 | 255.6562 | -2.966 | 0.329
90475 | -232.0462 | -213.9115 | 315.6003 | -0.987 | 1.318
90485 | -151.0788 | -237.7002 | 281.649 | -1.648 | -0.987
90495 | -92.7815 | -287.0696 | 301.6908 | -1.976 | -0.66
90505 | -177.6694 | -381.906 | 421.2109 | -2.966 | 1.318
90515 | -188.7431 | -435.2489 | 474.4107 | -2.635 | 0.329
90525 | -352.9136 | -238.1671 | 425.76 | 1.318 | 3.295
90535 | -351.6056 | -198.1462 | 403.5944 | -0.66 | 0.988
90545 | -401.1827 | -145.4504 | 426.7357 | 0.33 | 2.307
90555 | -376.066 | -175.3098 | 414.9206 | -0.988 | 0.988
90565 | -405.7209 | -130.6332 | 426.2329 | 0.329 | 1.976
90575 | -439.3269 | -105.3476 | 451.7812 | 0 | 1.977
90585 | -422.3163 | -152.1363 | 448.8837 | -0.989 | 1.318
90595 | -484.6927 | -208.2241 | 527.5265 | -1.317 | 2.635
90605 | -444.3876 | -301.5765 | 537.0556 | -2.306 | 0.989
90615 | -153.2056 | -466.054 | 490.5897 | -3.954 | -3.295
90625 | -69.0903 | -605.152 | 609.0833 | -4.283 | -0.987
90635 | 12.6882 | -563.1922 | 563.3351 | -1.976 | -1.977
90645 | -222.8618 | -483.5235 | 532.4118 | -1.318 | 3.294
90655 | -109.3893 | -400.9647 | 415.6185 | -0.659 | -1.977
90665 | -69.2444 | -694.5749 | 698.018 | -6.589 | -0.329
90675 | -165.4295 | -632.124 | 653.4124 | -1.318 | 1.318
90685 | -43.5376 | -419.0158 | 421.2715 | 0.659 | -1.977
90695 | 70.0894 | -340.8005 | 347.9332 | -0.329 | -1.976
90705 | 425.0923 | -422.765 | 599.5279 | -2.306 | -6.919
90715 | 489.1996 | -239.8029 | 544.8134 | 1.976 | -3.295
90725 | 590.308 | 37.1368 | 591.475 | 3.954 | -4.941
90735 | 613.351 | 165.8463 | 635.3774 | 2.964 | -3.624
90745 | 816.7642 | 393.9983 | 906.8288 | 5.601 | -6.919
90755 | 817.867 | 344.9423 | 887.6326 | 1.647 | -3.953
90765 | 815.1651 | 52.8653 | 816.8776 | -2.306 | -4.284
90775 | 489.594 | 178.033 | 520.9587 | 3.295 | 1.648
90785 | 314.7152 | 228.4037 | 388.8623 | 1.647 | 0.33
90795 | 349.8055 | 100.924 | 364.0736 | -0.659 | -1.648
90805 | 232.932 | -205.0634 | 310.3358 | -4.283 | 0.988
90815 | 69.735 | 132.8199 | 150.0137 | 5.272 | 1.977
90825 | 498.6726 | 134.8096 | 516.5733 | 0 | -7.248
90835 | 854.7751 | -339.0981 | 919.5804 | -6.919 | -7.248
90845 | 1059.9093 | -94.1743 | 1064.0849 | 3.295 | -7.247
90855 | 1698.6105 | 150.5572 | 1705.2698 | 2.965 | -15.814
90865 | 2121.6965 | 6.5681 | 2121.7067 | -1.647 | -14.497
90875 | 1919.3517 | 181.611 | 1927.9247 | 3.624 | -6.588
90885 | 2499.5851 | 240.0239 | 2511.0829 | 1.647 | -19.438
90895 | 2917.7846 | -268.7585 | 2930.1362 | -7.248 | -17.461
90905 | 3394.3002 | 141.6195 | 3397.2533 | 6.589 | -21.414
90915 | 3829.1621 | -295.5996 | 3840.5549 | -7.907 | -22.403
90925 | 4414.3163 | -202.5956 | 4418.9629 | 1.318 | -27.015
90935 | 5004.6525 | -162.6818 | 5007.2959 | -0.989 | -29.322
90945 | 5650.5291 | 104.4961 | 5651.4952 | 3.954 | -32.944
90955 | 6182.0715 | -120.2962 | 6183.2418 | -3.624 | -33.604
90965 | 5655.6286 | -785.043 | 5709.8535 | -11.202 | -17.791
90975 | 5198.8709 | 66.8073 | 5199.3001 | 11.531 | -17.132
90985 | 4973.6259 | 443.3005 | 4993.3426 | 4.942 | -16.802
90995 | 4499.7032 | 372.7176 | 4515.1132 | 1.647 | -10.541
91005 | 5086.1852 | -236.7636 | 5091.693 | -7.906 | -26.357
91015 | 5651.754 | -346.6547 | 5662.3752 | -1.977 | -26.686
91025 | 6992.5628 | -510.9933 | 7011.2088 | -4.942 | -43.816
91035 | 7222.4826 | 163.1315 | 7224.3246 | 9.225 | -29.981
91045 | 6826.3646 | 123.9167 | 6827.4892 | -0.989 | -22.733
91055 | 7999.614 | -182.6382 | 8001.6986 | -3.623 | -46.782
91065 | 7842.4007 | -200.3612 | 7844.9598 | -0.66 | -26.356
91075 | 7490.9157 | -713.8991 | 7524.8568 | -9.883 | -25.367
91085 | 6358.0049 | -212.9672 | 6361.5706 | 5.93 | -8.237
91095 | 5274.1647 | -331.8916 | 5284.597 | -4.283 | -3.953
91105 | 5217.5425 | -1255.6576 | 5366.5097 | -16.472 | -14.496
91115 | 5319.8252 | -1493.3234 | 5525.4461 | -8.896 | -15.155
91125 | 4753.3498 | -2365.9079 | 5309.6002 | -22.732 | -4.941
91135 | 4323.4387 | -1648.5407 | 4627.0735 | 1.977 | -5.601
91145 | 3913.7248 | -1446.7392 | 4172.5647 | -6.259 | -2.965
91155 | 3262.4773 | -1594.4003 | 3631.2354 | -8.237 | 2.965
91165 | 2678.4424 | -1164.8242 | 2920.7652 | 0.989 | 4.612
91175 | 2331.4539 | -1407.0958 | 2723.1592 | -9.225 | 3.624
91185 | 2238.246 | -1509.6253 | 2699.7618 | -6.259 | 0.989
91195 | 1985.4773 | -836.8392 | 2154.6276 | 5.6 | 3.953
91205 | 2443.1008 | -217.0723 | 2452.7254 | 7.247 | -7.906
91215 | 3524.8869 | 510.2012 | 3561.6194 | 13.179 | -20.097
91225 | 3694.3232 | 575.5166 | 3738.8826 | 5.271 | -10.214
91235 | 2407.86 | -480.6908 | 2455.3724 | -12.519 | 11.531
91245 | 1150.5952 | -2421.9148 | 2681.3318 | -32.287 | 16.143
91255 | -262.6047 | -3477.6397 | 3487.5405 | -27.014 | 26.686
91265 | -1706.0823 | -4655.5156 | 4958.2802 | -36.899 | 33.934
91275 | -2729.1724 | -5408.6619 | 6058.218 | -34.263 | 33.934
91285 | -3005.1511 | -5701.0505 | 6444.6031 | -30.639 | 26.356
91295 | -2920.1063 | -5400.482 | 6139.3995 | -21.414 | 21.414
91305 | -1972.8969 | -4787.0874 | 5177.6952 | -14.167 | 4.942
91315 | -1561.5382 | -4184.1399 | 4466.0305 | -10.213 | 9.224
91325 | -953.444 | -3516.1858 | 3643.1605 | -4.942 | 0.988
91335 | -1398.7285 | -2882.094 | 3203.5773 | -1.647 | 16.144
91345 | -1223.9912 | -1659.1117 | 2061.7483 | 12.19 | 5.271
91355 | -1109.8112 | 284.4296 | 1145.6793 | 29.98 | 7.248
91365 | -1540.8543 | 1409.7219 | 2088.4319 | 25.367 | 14.826
91375 | -3223.2137 | 117.4537 | 3225.353 | -8.565 | 37.557
91385 | -4370.1608 | -756.2462 | 4435.1115 | -5.601 | 35.251
91395 | -4625.9359 | -1144.4846 | 4765.4096 | -5.6 | 27.674
91405 | -4349.7437 | -1775.3096 | 4698.0841 | -12.52 | 20.096
91415 | -4389.1904 | -1967.7324 | 4810.0897 | -7.906 | 23.392
91425 | -4025.455 | -1001.4778 | 4148.1617 | 9.883 | 14.825
91435 | -3334.8739 | -1226.6937 | 3553.331 | -6.918 | 7.578
91445 | -2560.1447 | -1221.8546 | 2836.771 | -0.989 | 1.976
91455 | -1421.1001 | -1637.0652 | 2167.8349 | -9.883 | -8.895
91465 | -555.7965 | -2547.6711 | 2607.5923 | -19.438 | -9.883
91475 | -716.2422 | -3292.1257 | 3369.1386 | -21.085 | 2.306
91485 | -438.7854 | -3101.572 | 3132.4561 | -9.554 | -5.601
91495 | 640.946 | -2920.7282 | 2990.2283 | -9.883 | -18.779
91505 | 594.1101 | -2694.8042 | 2759.5174 | -6.919 | -3.953
91515 | 701.3146 | -2007.7084 | 2126.6723 | 2.306 | -8.566
91525 | 1289.291 | -1870.1335 | 2271.4909 | -3.953 | -15.484
91535 | 2251.2887 | -2496.4012 | 3361.5949 | -14.826 | -24.05
91545 | 2250.231 | -1531.6066 | 2722.0137 | 9.884 | -11.86
91555 | 2413.7905 | -1220.8557 | 2704.9719 | 0.33 | -16.144
91565 | 1578.1329 | -376.0134 | 1622.3099 | 13.836 | 1.977
91575 | 568.3206 | 1168.662 | 1299.5227 | 28.333 | 7.906
91585 | -1000.9028 | 1571.4874 | 1863.1638 | 16.144 | 24.051
91595 | -2418.5434 | 1903.4848 | 3077.76 | 19.108 | 28.992
91605 | -2855.4173 | 2040.0354 | 3509.2951 | 15.814 | 20.426
91615 | -3634.6516 | 1824.2354 | 4066.7588 | 10.212 | 29.651
91625 | -3569.5489 | 1351.187 | 3816.7245 | 4.283 | 17.131
91635 | -1459.2922 | 322.6632 | 1494.5385 | -8.236 | -17.131
91645 | 187.4831 | 134.2275 | 230.5795 | 0.988 | -18.45
91655 | 893.0719 | 175.2338 | 910.1012 | 1.647 | -14.167
91665 | 1992.3466 | -740.9605 | 2125.6687 | -14.166 | -25.697
91675 | 2334.5681 | -1380.6099 | 2712.2485 | -12.519 | -16.802
91685 | 1885.0235 | -1651.7258 | 2506.2944 | -10.872 | -6.259
91695 | 1005.1098 | -1472.5323 | 1782.862 | -4.612 | 3.624
91705 | 272.4887 | -1547.3333 | 1571.1431 | -8.237 | 6.259
91715 | 231.6559 | -1514.694 | 1532.3062 | -5.601 | -0.659
91725 | 718.0962 | -1519.0387 | 1680.2205 | -6.259 | -8.235
91735 | 343.4872 | -1164.9591 | 1214.5423 | 0.329 | 4.282
91745 | 336.7063 | -179.1742 | 381.4113 | 12.52 | -1.977
91755 | 459.5685 | 807.7518 | 929.3364 | 17.131 | -2.636
91765 | 433.1352 | 1036.6474 | 1123.4963 | 9.884 | -0.988
91775 | -311.4069 | 1115.1047 | 1157.7706 | 9.554 | 11.202
91785 | -987.8161 | 1063.2791 | 1451.3246 | 6.918 | 12.849
91795 | -1834.713 | 907.5142 | 2046.8888 | 4.613 | 20.095
91805 | -2265.52 | 821.1812 | 2409.7551 | 4.612 | 16.802
91815 | -1701.8366 | 907.7372 | 1928.791 | 6.59 | 2.637
91825 | -1551.2782 | 1187.928 | 1953.8774 | 9.883 | 7.577
91835 | -1875.4136 | 1231.918 | 2243.8356 | 6.919 | 12.849
91845 | -2293.126 | 1394.2448 | 2683.7186 | 9.554 | 15.484
91855 | -2607.9557 | 1488.3658 | 3002.7764 | 8.565 | 15.814
91865 | -3578.796 | 1147.5372 | 3758.2739 | 1.647 | 28.662
91875 | -3517.6334 | 1117.774 | 3690.957 | 5.601 | 14.496
91885 | -2897.4908 | 683.7944 | 2977.0837 | -2.635 | 6.588
91895 | -2140.9171 | 22.5777 | 2141.0362 | -7.908 | 0.33
91905 | -1708.3224 | -100.2978 | 1711.2642 | -2.306 | 1.318
91915 | -1408.3501 | -278.4856 | 1435.6198 | -4.941 | 0.329
91925 | -932.1811 | -234.4953 | 961.223 | -1.318 | -4.282
91935 | -1115.5942 | -895.2376 | 1430.3848 | -13.507 | 4.942
91945 | -1080.9426 | -528.2772 | 1203.1266 | 2.305 | 0.987
91955 | -947.8029 | -677.6322 | 1165.1247 | -6.918 | 0.33
91965 | -913.1193 | -757.8081 | 1186.617 | -4.283 | 1.318
91975 | -988.9647 | -392.9337 | 1064.1654 | 2.306 | 2.965
91985 | -772.0533 | -271.8065 | 818.5017 | -0.329 | -1.647
91995 | -715.2754 | 103.7617 | 722.7623 | 5.6 | 0.659
92005 | -569.2238 | 940.1722 | 1099.063 | 14.826 | -1.648
92015 | -56.8236 | 1414.2259 | 1415.3671 | 12.519 | -8.236
92025 | 257.903 | 1171.4054 | 1199.4602 | 3.624 | -6.919
92035 | 311.7557 | 795.5572 | 854.4606 | 0.659 | -4.611
92045 | 80.8734 | -58.2862 | 99.6885 | -10.214 | 0
92055 | -387.5472 | -488.2507 | 623.3631 | -6.917 | 5.27
92065 | -303.1886 | 481.925 | 569.3637 | 13.507 | -1.646
92075 | -474.7585 | 1148.4218 | 1242.6859 | 11.53 | 3.623
92085 | -782.0109 | 1691.9975 | 1863.9733 | 14.826 | 5.931
92095 | -660.346 | 1585.4821 | 1717.5012 | 6.259 | 0.329
92105 | -434.0009 | 1342.4932 | 1410.9021 | 4.284 | -1.318
92115 | 302.8248 | 600.5604 | 672.5887 | -6.261 | -11.531
92125 | 285.1318 | 592.0953 | 657.1735 | 2.966 | -1.647
92135 | -40.5536 | 1275.4735 | 1276.118 | 12.849 | 1.976
92145 | -241.1604 | 1755.8043 | 1772.2887 | 12.519 | 1.977
92155 | -271.7896 | 2057.6118 | 2075.4845 | 12.848 | 0.66
92165 | 12.201 | 1270.8941 | 1270.9527 | -4.283 | -4.284
92175 | -245.4029 | 1212.2977 | 1236.8865 | 5.601 | 3.953
92185 | -186.2945 | 1454.484 | 1466.366 | 7.907 | -1.317
92195 | 56.4336 | 1456.8266 | 1457.9192 | 5.271 | -3.624
92205 | 778.889 | 701.612 | 1048.2974 | -7.248 | -13.178
92215 | 979.3911 | 22.5715 | 979.6512 | -8.894 | -7.248
92225 | 7.4866 | 832.0436 | 832.0773 | 12.189 | 10.542
92235 | 49.0773 | 817.4708 | 818.9427 | 0 | -2.965
92245 | -305.2804 | 788.1505 | 845.2085 | 2.635 | 6.589
92255 | -1093.0056 | 1357.7087 | 1742.9957 | 11.861 | 14.167
92265 | -2033.2154 | 1646.3488 | 2616.186 | 9.225 | 20.755
92275 | -2710.2268 | 1348.1768 | 3027.0299 | 1.647 | 21.085
92285 | -3181.0834 | 1108.6643 | 3368.7428 | 1.647 | 21.415
92295 | -2971.0684 | 1159.0566 | 3189.1472 | 4.612 | 11.86
92305 | -2203.3937 | 1184.2003 | 2501.4544 | 3.953 | 1.647
92315 | -1475.4612 | 1207.1281 | 1906.3431 | 4.283 | -1.977
92325 | -1181.8222 | 1189.3145 | 1676.6552 | 3.624 | 0.659
92335 | -1070.4059 | 1039.1554 | 1491.8488 | 1.318 | 1.318
92345 | -1068.6658 | 1233.7486 | 1632.2323 | 6.59 | 2.635
92355 | -491.8664 | 1354.0925 | 1440.6592 | 5.6 | -7.247
92365 | 207.6951 | 1583.5584 | 1597.1206 | 8.566 | -11.201
92375 | 447.9263 | 1302.2114 | 1377.0957 | 0.659 | -7.248
92385 | 539.8346 | 667.3086 | 858.3252 | -5.931 | -6.59
92395 | 823.2454 | 322.9142 | 884.3114 | -4.282 | -9.883
92405 | 199.1779 | 321.5508 | 378.2416 | -0.988 | 4.942
92415 | -853.3055 | 5.2314 | 853.3216 | -6.59 | 14.166
92425 | -1171.7815 | 400.4953 | 1238.3329 | 4.942 | 7.577
92435 | -1064.8687 | 1003.9888 | 1463.5364 | 9.225 | 3.624
92445 | -1013.1813 | 1504.1559 | 1813.5659 | 11.201 | 3.954
92455 | -991.1009 | 1869.562 | 2116.0206 | 11.86 | 3.624
92465 | -504.3315 | 1194.806 | 1296.8854 | -3.953 | -4.612
92475 | -319.0666 | 1023.3121 | 1071.9007 | 2.635 | -1.318
92485 | -558.1895 | 1466.5729 | 1569.2073 | 10.214 | 3.953
92495 | -1244.1505 | 1651.3585 | 2067.5819 | 7.577 | 12.519
92505 | -1261.327 | 1287.8595 | 1802.6447 | 0 | 4.283
92515 | -990.622 | 1098.6985 | 1479.3479 | 1.648 | 0.989
92525 | -1089.2006 | 710.6422 | 1300.5269 | -3.625 | 5.601
92535 | -1191.953 | 507.4739 | 1295.4851 | -1.976 | 5.27
92545 | -979.6091 | 532.6684 | 1115.0648 | 0.329 | 0.66
92555 | -1288.7516 | 362.0941 | 1338.6533 | -2.965 | 8.895
92565 | -1576.0603 | 455.6876 | 1640.615 | 1.318 | 8.894
92575 | -1379.9861 | 493.433 | 1465.5503 | 0.329 | 2.637
92585 | -554.1878 | 623.5459 | 834.2264 | 2.635 | -8.567
92595 | 357.1751 | 607.8275 | 705.0024 | 0.66 | -13.836
92605 | 347.7322 | 474.763 | 588.4875 | -0.989 | -3.295
92615 | 869.1257 | 339.1276 | 932.9454 | -1.647 | -13.836
92625 | 985.9453 | 362.6259 | 1050.5168 | 0.33 | -7.578
92635 | 643.1353 | 237.3993 | 685.5519 | -2.307 | -1.318
92645 | 353.6828 | 391.3509 | 527.4913 | 2.307 | -0.329
92655 | -205.606 | 588.5555 | 623.4352 | 3.294 | 6.588
92665 | -226.9612 | 515.2516 | 563.0236 | 0 | 0
92675 | -240.8717 | 223.6402 | 328.6854 | -3.624 | 1.318
92685 | -167.2999 | 205.1588 | 264.7251 | -0.33 | -0.658
92695 | 510.695 | 343.9556 | 615.723 | 1.648 | -11.201
92705 | 898.4961 | 551.377 | 1054.1878 | 3.624 | -8.896
92715 | 991.9554 | 461.4521 | 1094.0354 | -0.33 | -6.919
92725 | 1172.0195 | 151.9032 | 1181.8225 | -3.953 | -8.895
92735 | 1062.1867 | 8.6898 | 1062.2222 | -2.636 | -4.283
92745 | 485.7416 | -103.7312 | 496.6942 | -3.294 | 3.954
92755 | 359.6368 | 422.1287 | 554.5551 | 7.247 | -0.988
92765 | 716.6185 | 825.9874 | 1093.5252 | 6.919 | -7.248
92775 | 566.1699 | 552.4676 | 791.0555 | -1.647 | 0
92785 | 1005.5099 | 825.9527 | 1301.2486 | 7.248 | -10.543
92795 | 1057.4009 | 1032.7963 | 1478.095 | 5.93 | -4.612
92805 | 943.3601 | 1003.9882 | 1377.6504 | 3.624 | -3.295
92815 | 1229.9705 | 919.047 | 1535.407 | 2.636 | -9.224
92825 | 1653.8792 | 929.2654 | 1897.0636 | 3.624 | -12.191
92835 | 1505.9048 | 781.407 | 1696.5689 | 0.658 | -4.611
92845 | 1332.684 | 412.8507 | 1395.1675 | -3.624 | -4.283
92855 | 1158.5834 | 205.776 | 1176.7154 | -2.635 | -2.636
92865 | 1007.0288 | 281.6893 | 1045.6844 | 0.659 | -1.977
92875 | 1067.6747 | 156.7891 | 1079.1256 | -2.635 | -4.612
92885 | 1076.0596 | -8.3542 | 1076.092 | -3.295 | -3.624
92895 | 529.0477 | 341.3196 | 629.5955 | 4.612 | 5.601
92905 | 369.2748 | 590.6877 | 696.6174 | 3.953 | 0.988
92915 | 39.4858 | 412.0728 | 413.9603 | -1.317 | 5.93
92925 | -428.7842 | 329.7417 | 540.9117 | 0 | 9.224
92935 | -818.1789 | 342.7471 | 887.0694 | 0.658 | 10.214
92945 | -933.6855 | 603.268 | 1111.6208 | 4.943 | 7.577
92955 | -1352.6869 | 862.3537 | 1604.1869 | 5.93 | 13.508
92965 | -1784.197 | 777.8955 | 1946.4019 | 1.647 | 14.825
92975 | -1624.8625 | 804.4565 | 1813.0991 | 3.624 | 6.919
92985 | -1057.5252 | 1049.3723 | 1489.8127 | 6.918 | -0.33
92995 | -736.3995 | 891.1616 | 1156.0507 | 0.989 | 0.659
93005 | 442.5766 | 735.4688 | 858.3638 | 0.987 | -16.802
93015 | 1620.2064 | 714.8313 | 1770.8904 | 1.978 | -21.415
93025 | 2115.879 | 848.2457 | 2279.5755 | 4.283 | -16.802
93035 | 2125.2056 | 817.5031 | 2277.0178 | 1.976 | -11.86
93045 | 2048.3979 | 849.706 | 2217.6416 | 3.295 | -10.212
93055 | 1791.0451 | 1082.3632 | 2092.6903 | 6.589 | -5.931
93065 | 1761.2821 | 1183.5711 | 2122.0168 | 5.271 | -8.236
93075 | 1701.9287 | 906.6782 | 1928.3741 | -0.329 | -6.589
93085 | 1219.1917 | 785.9716 | 1450.5792 | 1.318 | 0.988
93095 | 725.0311 | 915.1998 | 1167.5876 | 4.282 | 3.295
93105 | -201.7831 | 905.6514 | 927.8582 | 2.306 | 13.836
93115 | -676.8337 | 701.21 | 974.5765 | -0.658 | 10.214
93125 | -1383.1538 | 722.4778 | 1560.477 | 2.306 | 17.79
93135 | -2844.9375 | 385.0715 | 2870.8795 | -4.283 | 33.275
93145 | -3709.115 | 273.1825 | 3719.1616 | -1.318 | 29.321
93155 | -3762.1116 | 238.4009 | 3769.6577 | -1.318 | 21.085
93165 | -3742.9473 | 469.2659 | 3772.2493 | 3.295 | 20.097
93175 | -4118.8901 | 667.9625 | 4172.7006 | 3.624 | 25.367
93185 | -4371.8722 | 666.0099 | 4422.3112 | 1.647 | 23.721
93195 | -4826.9798 | 645.9515 | 4870.009 | 1.647 | 28.332
93205 | -5098.9872 | 755.7439 | 5154.6891 | 3.624 | 26.356
93215 | -4911.8159 | 807.2784 | 4977.7137 | 2.965 | 19.768
93225 | -4386.2058 | 812.3946 | 4460.8056 | 2.636 | 12.849
93235 | -3877.3863 | 951.9211 | 3992.5278 | 4.941 | 9.883
93245 | -3248.4387 | 912.6341 | 3374.2043 | 2.307 | 4.282
93255 | -2570.8592 | 824.0373 | 2699.6953 | 1.647 | 0
93265 | -2000.8941 | 733.8182 | 2131.2124 | 0.988 | -1.976
93275 | -1466.2251 | 674.5833 | 1613.9637 | 0.988 | -4.612
93285 | -913.0596 | 619.2995 | 1103.2722 | 0.66 | -7.577
93295 | -589.1514 | 598.6108 | 839.9014 | 0.988 | -6.261
93305 | -484.2658 | 605.9301 | 775.6704 | 1.318 | -4.282
93315 | -377.5601 | 629.2866 | 733.8619 | 1.647 | -4.612
93325 | -229.8095 | 682.5001 | 720.1519 | 2.306 | -5.271
93335 | 72.181 | 720.1818 | 723.79 | 2.306 | -8.237
93345 | 393.9421 | 800.0245 | 891.7564 | 3.295 | -9.554
93355 | 554.675 | 803.0321 | 975.9738 | 2.306 | -8.236
93365 | 614.2877 | 814.8094 | 1020.4233 | 2.636 | -7.248
93375 | 542.7143 | 714.7301 | 897.4285 | 0.658 | -4.942
93385 | 468.643 | 749.8087 | 884.2167 | 2.637 | -4.283
93395 | 368.1142 | 814.7612 | 894.0603 | 2.964 | -2.965
93405 | 274.2432 | 739.4069 | 788.6265 | 0.989 | -2.306
93415 | 187.674 | 673.3643 | 699.0286 | 0.988 | -1.648
93425 | 138.8076 | 598.3116 | 614.2021 | 0.329 | -1.646
93435 | 194.1271 | 543.8473 | 577.4558 | 0.33 | -2.966
93445 | 343.6011 | 450.6806 | 566.7228 | -0.659 | -4.613
93455 | 572.0528 | 455.8414 | 731.4614 | 0.659 | -6.588
93465 | 874.5198 | 565.2283 | 1041.2818 | 2.306 | -8.895
93475 | 1422.317 | 546.4275 | 1523.6694 | 0.659 | -14.497
93485 | 1987.4328 | 493.7149 | 2047.8387 | 0.329 | -17.131
93495 | 2344.0408 | 479.1923 | 2392.5201 | 0.66 | -16.473
93505 | 2072.7728 | 491.3577 | 2130.2159 | 0.987 | -7.577
93515 | 1146.9491 | 383.9657 | 1209.5131 | -0.987 | 4.613
93525 | 614.4505 | 294.5268 | 681.3923 | -0.989 | 2.635
93535 | 740.0233 | 239.3688 | 777.7736 | -0.988 | -4.283
93545 | 1221.1599 | 488.0053 | 1315.0591 | 3.953 | -10.212
93555 | 1577.6471 | 801.5075 | 1769.5718 | 5.93 | -10.543
93565 | 1411.4562 | 1024.6508 | 1744.1668 | 6.259 | -3.953
93575 | 1122.5623 | 1015.538 | 1513.758 | 3.624 | -1.648
93585 | 1100.3597 | 956.0427 | 1457.6725 | 2.966 | -4.282
93595 | 1296.0991 | 1139.8379 | 1726.008 | 6.588 | -7.248
93605 | 1271.4369 | 1222.6383 | 1763.9151 | 5.272 | -4.284
93615 | 995.0968 | 1089.2679 | 1475.3718 | 2.306 | -0.329
93625 | 757.426 | 1065.8511 | 1307.5675 | 3.624 | 0.329
93635 | 419.7486 | 1000.4067 | 1084.8975 | 2.307 | 3.624
93645 | 115.1071 | 851.8229 | 859.565 | 0.658 | 4.613
93655 | -300.7169 | 689.9614 | 752.6469 | -0.329 | 8.236
93665 | -860.4441 | 485.5599 | 987.9942 | -1.977 | 12.519
93675 | -1478.8816 | 397.0036 | 1531.2422 | -0.988 | 16.144
93685 | -1884.3015 | 366.0715 | 1919.5313 | -0.659 | 15.484
93695 | -2028.6818 | 319.3463 | 2053.663 | -0.989 | 13.178
93705 | -1930.2028 | 162.2404 | 1937.0092 | -2.964 | 9.554
93715 | -1725.8821 | 75.6085 | 1727.5375 | -2.307 | 6.919
93725 | -1498.3057 | 41.9097 | 1498.8918 | -1.977 | 4.941
93735 | -1346.9816 | -6.8688 | 1346.9991 | -2.306 | 4.613
93745 | -1249.0365 | 6.2605 | 1249.0522 | -1.318 | 4.282
93755 | -1175.2314 | 73.1908 | 1177.5082 | -0.329 | 3.954
93765 | -1093.9528 | -19.7958 | 1094.1319 | -2.635 | 3.294
93775 | -1041.5502 | -108.5559 | 1047.192 | -2.637 | 3.295
93785 | -1070.4961 | -107.3983 | 1075.87 | -1.646 | 4.283
93795 | -1234.5859 | -65.8547 | 1236.3411 | -0.989 | 6.589
93805 | -1340.9647 | -100.2519 | 1344.707 | -1.976 | 6.259
93815 | -1366.651 | -119.2874 | 1371.8471 | -1.648 | 5.601
93825 | -1462.1221 | -111.6674 | 1466.3801 | -1.318 | 6.919
93835 | -1544.9523 | -32.4063 | 1545.2921 | 0 | 6.918
93845 | -1641.8379 | 101.8193 | 1644.992 | 1.318 | 7.577
93855 | -1642.2552 | 116.4838 | 1646.3811 | 0 | 6.26
93865 | -1523.9637 | 14.1985 | 1524.0298 | -1.647 | 4.283
93875 | -1385.9214 | -23.4699 | 1386.1202 | -0.988 | 3.295
93885 | -1166.3764 | -57.0124 | 1167.769 | -1.318 | 0.987
93895 | -953.7535 | -65.8062 | 956.021 | -0.989 | 0
93905 | -794.753 | -70.5022 | 797.874 | -0.988 | -0.329
93915 | -630.1834 | 18.8678 | 630.4658 | 0.659 | -1.318
93925 | -528.4298 | 88.1645 | 535.7341 | 0.659 | -0.988
93935 | -459.1664 | 165.4616 | 488.069 | 1.317 | -0.989
93945 | -423.0119 | 163.6252 | 453.5551 | 0.331 | -0.658
93955 | -411.7564 | 76.8684 | 418.87 | -0.989 | -0.329
93965 | -339.4965 | 90.922 | 351.4608 | 0.329 | -1.319
93975 | -198.4453 | 96.6654 | 220.7368 | 0 | -2.635
93985 | -110.0891 | 190.0087 | 219.5972 | 1.647 | -2.306
93995 | -70.0994 | 284.2862 | 292.8012 | 1.977 | -1.977
94005 | -113.5703 | 267.6609 | 290.7586 | 0.659 | -0.659
94015 | -180.8426 | 304.6165 | 354.2531 | 1.647 | 0
94025 | -179.7648 | 324.3684 | 370.8507 | 1.318 | -0.658
94035 | -203.8296 | 276.9235 | 343.8505 | 0.329 | 0
94045 | -106.9665 | 260.5311 | 281.635 | 0.66 | -1.977
94055 | 35.7499 | 199.8137 | 202.9867 | -0.33 | -2.966
94065 | 96.9643 | 152.3676 | 180.6045 | -0.33 | -2.306
94075 | 57.1398 | 143.6346 | 154.5829 | 0 | -0.988
94085 | 48.4237 | 120.8036 | 130.1475 | -0.329 | -1.317
94095 | 56.3176 | 81.712 | 99.2397 | -0.658 | -1.319
94105 | 27.6953 | 52.8357 | 59.6544 | -0.66 | -0.658
94115 | -49.4464 | 14.1449 | 51.4298 | -0.988 | 0.329
94125 | -25.2316 | -15.8992 | 29.8231 | -0.989 | -0.989
94135 | 6.9348 | 1.4944 | 7.094 | -0.329 | -0.987
94145 | 64.6402 | -61.2503 | 89.0503 | -1.647 | -1.648
94155 | 109.6084 | -98.2845 | 147.2204 | -1.317 | -1.647
94165 | 178.4061 | -41.7698 | 183.2306 | 0 | -2.306
94175 | 213.1533 | -93.9247 | 232.9296 | -1.648 | -1.977
94185 | 370.1562 | -109.6773 | 386.0631 | -0.989 | -4.283
94195 | 535.9169 | -92.9043 | 543.9101 | -0.658 | -4.942
94205 | 591.3916 | -121.7923 | 603.8024 | -1.318 | -3.953
94215 | 644.7057 | -187.913 | 671.5331 | -1.977 | -4.283
94225 | 675.3949 | -255.9788 | 722.2765 | -2.306 | -3.954
94235 | 624.5022 | -265.349 | 678.5375 | -1.647 | -2.635
94245 | 532.6122 | -191.736 | 566.0728 | -0.329 | -1.647
94255 | 399.1745 | -158.0076 | 429.3095 | -0.66 | -0.33
94265 | 271.1743 | -203.2919 | 338.9145 | -1.647 | 0.33
94275 | 188.8084 | -280.3386 | 337.9917 | -2.306 | 0.329
94285 | 156.2545 | -276.8238 | 317.8787 | -1.317 | 0
94295 | 39.7548 | -209.1028 | 212.8483 | -0.331 | 1.647
94305 | -53.5833 | -200.7196 | 207.7487 | -0.987 | 1.648
94315 | -36.2487 | -225.1934 | 228.0922 | -1.319 | 0.329
94325 | 39.325 | -262.4159 | 265.3461 | -1.647 | -0.659
94335 | 145.9984 | -250.9085 | 290.294 | -0.988 | -1.647
94345 | 217.6547 | -238.5415 | 322.9173 | -0.989 | -1.647
94355 | 183.8994 | -233.9583 | 297.5827 | -0.987 | -0.33
94365 | 190.5286 | -271.0416 | 331.3076 | -1.648 | -0.988
94375 | 225.155 | -282.5468 | 361.2858 | -1.318 | -1.319
94385 | 249.9568 | -228.9754 | 338.981 | -0.329 | -1.317
94395 | 208.6992 | -130.704 | 246.2497 | 0.658 | -0.329
94405 | 136.8194 | -81.6213 | 159.316 | 0.33 | 0.329
94415 | 31.0611 | -93.5065 | 98.5305 | -0.33 | 1.317
94425 | -120.8776 | -65.7305 | 137.5932 | 0.33 | 2.637
94435 | -248.6202 | -38.2512 | 251.5455 | 0.33 | 2.964
94445 | -372.9807 | -97.3493 | 385.4757 | -0.989 | 3.624
94455 | -502.8463 | -49.0181 | 505.2298 | 0.659 | 4.284
94465 | -540.8746 | -94.83 | 549.1248 | -0.988 | 3.294
94475 | -564.297 | -161.2199 | 586.8756 | -1.318 | 3.294
94485 | -572.3749 | -221.3687 | 613.6914 | -1.648 | 2.966
94495 | -641.1791 | -243.1351 | 685.7297 | -1.317 | 3.953
94505 | -664.3142 | -236.0301 | 704.999 | -0.989 | 3.295
94515 | -658.9725 | -193.3016 | 686.7389 | -0.329 | 2.964
94525 | -584.7283 | -163.0529 | 607.0366 | -0.329 | 1.648
94535 | -475.1783 | -165.8896 | 503.3028 | -0.66 | 0.659
94545 | -346.5763 | -190.1035 | 395.2904 | -0.988 | -0.33
94555 | -183.3422 | -246.0786 | 306.8698 | -1.647 | -1.647
94565 | 46.2631 | -287.2781 | 290.9794 | -1.647 | -3.623
94575 | 191.9579 | -332.4501 | 383.8892 | -1.977 | -3.295
94585 | 188.0981 | -424.033 | 463.8803 | -2.965 | -1.648
94595 | 142.4979 | -397.4588 | 422.2311 | -1.318 | -0.988
94605 | 63.1466 | -347.7655 | 353.452 | -0.988 | 0
94615 | -141.5228 | -340.1007 | 368.371 | -1.318 | 2.636
94625 | -366.3658 | -360.8396 | 514.2267 | -1.647 | 3.953
94635 | -515.2391 | -416.2412 | 662.3655 | -2.307 | 3.953
94645 | -496.1403 | -573.4201 | 758.265 | -4.282 | 1.977
94655 | -339.1465 | -519.4248 | 620.3406 | -1.318 | -0.329
94665 | -95.7945 | -457.5524 | 467.4727 | -1.318 | -2.636
94675 | 147.5926 | -314.4795 | 347.3916 | 0.659 | -3.954
94685 | 271.9567 | -227.5246 | 354.5813 | 0.329 | -3.293
94695 | 214.1584 | -141.2484 | 256.5442 | 0.989 | -0.989
94705 | 90.3466 | -115.5984 | 146.7157 | 0.329 | 0.329
94715 | -82.8657 | -141.2964 | 163.8029 | -0.329 | 1.977
94725 | -181.1521 | -119.5585 | 217.0491 | 0.329 | 1.647
94735 | -159.5756 | -133.0973 | 207.7962 | -0.329 | 0.329
94745 | -41.1071 | -127.4545 | 133.9195 | 0 | -1.317
94755 | 62.6614 | -117.1874 | 132.8884 | 0 | -1.647
94765 | 108.0823 | -109.624 | 153.9455 | 0 | -1.318
94775 | -76.0155 | -84.0078 | 113.2946 | 0.329 | 2.306
94785 | -414.2784 | -101.441 | 426.5171 | -0.329 | 5.6
94795 | -688.6748 | -59.9616 | 691.2802 | 0.659 | 6.261
94805 | -866.3324 | 36.2688 | 867.0912 | 1.647 | 6.259
94815 | -854.2791 | 67.6109 | 856.9504 | 0.988 | 3.953
94825 | -666.7615 | 82.1825 | 671.8072 | 0.989 | 0.989
94835 | -385.1562 | 39.2399 | 387.15 | 0 | -1.647
94845 | -62.7228 | 45.1287 | 77.2706 | 0.658 | -3.954
94855 | 155.7301 | 117.8661 | 195.3056 | 1.648 | -3.953
94865 | 102.6029 | 212.2419 | 235.7414 | 2.306 | -0.66
94875 | -66.722 | 278.6884 | 286.5642 | 2.306 | 1.318
94885 | -271.161 | 266.0149 | 379.8582 | 1.318 | 2.965
94895 | -521.7063 | 273.4922 | 589.0463 | 1.647 | 4.942
94905 | -734.2098 | 250.4332 | 775.7453 | 0.989 | 5.601
94915 | -780.3059 | 117.9671 | 789.1727 | -0.989 | 3.953
94925 | -725.7858 | 39.6386 | 726.8674 | -0.659 | 2.636
94935 | -655.1569 | 37.1034 | 656.2067 | 0 | 1.977
94945 | -577.4881 | 58.9476 | 580.4889 | 0.33 | 1.317
94955 | -490.8467 | 34.0429 | 492.0258 | -0.33 | 0.66
94965 | -376.396 | 48.7784 | 379.5435 | 0.33 | -0.33
94975 | -335.205 | 45.8289 | 338.3233 | 0 | 0.33
94985 | -450.3873 | 58.1 | 454.1193 | 0.329 | 2.635
94995 | -579.26 | 127.0965 | 593.0393 | 1.318 | 3.295
95005 | -680.0476 | 179.3712 | 703.3056 | 1.318 | 3.624
95015 | -786.0413 | 230.5416 | 819.1522 | 1.648 | 4.282
95025 | -805.7956 | 152.8625 | 820.1667 | -0.331 | 3.295
95035 | -640.9547 | 106.7959 | 649.791 | 0 | 0.329
95045 | -421.4398 | 68.0846 | 426.904 | -0.329 | -1.318
95055 | -258.0978 | 97.8924 | 276.0388 | 0.66 | -1.646
95065 | -192.1624 | 222.0092 | 293.623 | 2.305 | -0.989
95075 | -343.9289 | 236.5519 | 417.4253 | 0.988 | 2.306
95085 | -558.6061 | 192.9196 | 590.9812 | 0.331 | 3.953
95095 | -679.2215 | 68.6522 | 682.6822 | -1.319 | 3.624
95105 | -538.4035 | -21.8582 | 538.847 | -1.318 | 0
95115 | -305.4529 | -56.5369 | 310.6412 | -0.987 | -1.977
95125 | -189.4862 | -39.8378 | 193.6287 | -0.331 | -1.317
95135 | -317.2555 | -65.8396 | 324.0153 | -0.988 | 1.977
95145 | -402.8496 | -54.573 | 406.5293 | -0.329 | 1.646
95155 | -404.0447 | -42.3532 | 406.2584 | -0.329 | 0.989
95165 | -379.1617 | 19.3647 | 379.6559 | 0.658 | 0.659
95175 | -381.5496 | 8.5764 | 381.646 | -0.329 | 0.989
95185 | -271.5972 | 66.7229 | 279.673 | 0.988 | -0.989
95195 | -143.8771 | 137.4914 | 199.0088 | 1.318 | -1.648
95205 | -78.7732 | 164.0054 | 181.9423 | 0.988 | -1.317
95215 | -57.1273 | 140.5092 | 151.6785 | 0.33 | -0.989
95225 | -1.6531 | 142.0864 | 142.096 | 0.659 | -1.647
95235 | 7.6786 | 72.9636 | 73.3665 | -0.659 | -0.988
95245 | -84.5442 | 17.5917 | 86.355 | -0.659 | 0.659
95255 | -209.3119 | 24.2104 | 210.7074 | 0 | 1.647
95265 | -309.7511 | 71.9759 | 318.0036 | 0.659 | 1.977
95275 | -296.92 | 124.7083 | 322.0461 | 0.988 | 0.658
95285 | -239.484 | 82.4512 | 253.28 | -0.329 | 0
95295 | -164.0448 | 120.355 | 203.4601 | 0.989 | -0.658
95305 | -112.5822 | 179.6393 | 212.0025 | 1.317 | -0.659
95315 | -157.3846 | 198.9205 | 253.6519 | 0.988 | 0.659
95325 | -176.553 | 170.5319 | 245.463 | 0.33 | 0.329
95335 | -238.3646 | 130.1598 | 271.5865 | 0 | 1.318
95345 | -363.4072 | 85.4966 | 373.3289 | -0.33 | 2.635
95355 | -433.9615 | 36.3057 | 435.4775 | -0.659 | 2.307
95365 | -436.5602 | 2.3158 | 436.5664 | -0.659 | 1.648
95375 | -321.4248 | -39.0579 | 323.7891 | -0.987 | -0.331
95385 | -254.884 | -70.5425 | 264.4657 | -0.989 | 0
95395 | -337.5033 | -92.3254 | 349.9035 | -0.989 | 1.977
95405 | -426.4154 | -147.3099 | 451.1434 | -1.646 | 2.307
95415 | -461.9508 | -210.5856 | 507.6858 | -1.977 | 1.977
95425 | -443.9965 | -236.4831 | 503.0478 | -1.648 | 1.317
95435 | -391.9666 | -272.3353 | 477.2885 | -1.976 | 0.659
95445 | -395.5159 | -245.7803 | 465.6616 | -0.989 | 1.317
95455 | -387.7494 | -223.415 | 447.5085 | -0.988 | 0.989
95465 | -398.1697 | -196.0266 | 443.808 | -0.659 | 1.318
95475 | -428.344 | -197.488 | 471.6779 | -0.988 | 1.648
95485 | -450.3438 | -242.4152 | 511.4437 | -1.648 | 1.646
95495 | -407.0702 | -258.3701 | 482.1424 | -1.318 | 0.66
95505 | -333.4586 | -265.6708 | 426.3515 | -1.318 | 0
95515 | -360.7594 | -311.7083 | 476.7698 | -1.976 | 1.318
95525 | -391.4017 | -407.1004 | 564.7354 | -2.965 | 1.317
95535 | -368.6712 | -420.3989 | 559.1545 | -1.977 | 0.659
95545 | -405.7032 | -459.7627 | 613.1695 | -2.636 | 1.647
95555 | -401.7488 | -439.9912 | 595.8141 | -1.647 | 0.989
95565 | -410.5329 | -536.6762 | 675.6912 | -3.624 | 1.318
95575 | -421.253 | -622.6665 | 751.7763 | -3.624 | 1.317
95585 | -332.0368 | -657.9907 | 737.0211 | -3.294 | -0.329
95595 | -241.6051 | -683.1413 | 724.6068 | -3.295 | -0.659
95605 | -184.5741 | -744.6972 | 767.2297 | -3.953 | -0.659
95615 | -108.4835 | -796.0775 | 803.4352 | -3.953 | -1.318
95625 | 64.8097 | -756.6776 | 759.448 | -2.637 | -3.294
95635 | 138.5703 | -668.2576 | 682.4734 | -1.647 | -2.306
95645 | 274.3755 | -611.6267 | 670.35 | -1.646 | -3.954
95655 | 232.5056 | -620.0337 | 662.1938 | -2.307 | -1.318
95665 | 71.6773 | -652.1268 | 656.0541 | -2.635 | 0.659
95675 | -72.7946 | -655.7659 | 659.7939 | -2.306 | 1.318
95685 | -180.4163 | -694.2826 | 717.3411 | -2.966 | 1.647
95695 | -172.9357 | -727.5489 | 747.8196 | -2.965 | 0.33
95705 | -61.3313 | -730.3952 | 732.9656 | -2.636 | -1.319
95715 | -0.19791 | -693.5883 | 693.5884 | -1.976 | -0.987
95725 | -7.1125 | -687.1303 | 687.1671 | -2.306 | -0.33
95735 | -91.9732 | -613.0558 | 619.9166 | -0.989 | 0.988
95745 | -192.7795 | -554.5184 | 587.0729 | -0.988 | 1.648
95755 | -201.3151 | -501.5444 | 540.4392 | -0.659 | 0.658
95765 | -120.6496 | -425.5105 | 442.2845 | 0 | -0.658
95775 | -61.7287 | -427.517 | 431.9505 | -0.988 | -0.659
95785 | 29.2965 | -398.1214 | 399.1979 | -0.329 | -1.647
95795 | 193.3015 | -329.662 | 382.1551 | 0.329 | -3.295
95805 | 332.3883 | -259.5557 | 421.724 | 0.658 | -3.624
95815 | 444.3447 | -152.4729 | 469.7768 | 1.648 | -3.953
95825 | 525.4959 | -148.6946 | 546.1282 | 0.329 | -3.954
95835 | 527.9261 | -155.2131 | 550.27 | 0.329 | -2.965
95845 | 568.5958 | -188.9469 | 599.1678 | -0.329 | -3.624
95855 | 515.8457 | -307.7238 | 600.6586 | -1.977 | -1.977
95865 | 339.1509 | -393.4704 | 519.4634 | -1.976 | 0.33
95875 | 119.7619 | -481.4532 | 496.1251 | -2.635 | 1.977
95885 | -26.507 | -583.1773 | 583.7794 | -3.295 | 1.977
95895 | -117.3387 | -540.0946 | 552.6939 | -1.318 | 1.976
95905 | -45.9451 | -401.219 | 403.8411 | 0.329 | -0.329
95915 | 129.3149 | -306.2483 | 332.431 | 0.33 | -2.307
95925 | 171.4136 | -212.5599 | 273.0647 | 0.988 | -0.988
95935 | 122.3632 | -125.9141 | 175.5765 | 1.318 | 0
95945 | 67.3119 | -103.9922 | 123.876 | 0.659 | 0.33
95955 | 52.1715 | -53.4789 | 74.7118 | 1.318 | 0
95965 | 84.6091 | 29.9006 | 89.737 | 1.976 | -0.659
95975 | 205.6423 | 131.1855 | 243.9229 | 2.636 | -2.307
95985 | 314.7909 | 244.28 | 398.4545 | 3.294 | -2.635
95995 | 307.9094 | 270.0386 | 409.5474 | 2.306 | -1.318
96005 | 255.8515 | 245.6447 | 354.6848 | 1.648 | -0.659
96015 | 223.9264 | 196.3554 | 297.8229 | 0.989 | -0.658
96025 | 169.6823 | 109.9586 | 202.1954 | 0 | 0
96035 | 72.832 | 90.9554 | 116.522 | 0.658 | 0.988
96045 | 22.9802 | 51.7433 | 56.6168 | 0 | 0.658
96055 | 71.864 | 39.8812 | 82.1884 | 0.329 | -0.658
96065 | 54.0148 | 56.9135 | 78.4649 | 0.66 | 0.329
96075 | 85.8946 | 89.6041 | 124.124 | 0.988 | -0.659
96085 | 154.5565 | 190.147 | 245.038 | 2.306 | -1.318
96095 | 201.2871 | 228.3853 | 304.428 | 1.647 | -1.318
96105 | 153.0073 | 265.656 | 306.5687 | 1.977 | 0
96115 | 130.9912 | 297.8554 | 325.3867 | 1.976 | -0.329
96125 | 124.4925 | 322.0561 | 345.2803 | 1.977 | -0.33
96135 | 216.005 | 322.6633 | 388.2908 | 1.647 | -1.976
96145 | 250.8651 | 324.5061 | 410.1676 | 1.648 | -1.318
96155 | 187.2169 | 388.1577 | 430.9485 | 2.636 | 0
96165 | 157.4512 | 364.3983 | 396.9597 | 1.317 | -0.33
96175 | 146.1623 | 357.9268 | 386.62 | 1.647 | -0.329
96185 | 119.3182 | 363.6824 | 382.7554 | 1.648 | 0
96195 | 98.8511 | 369.6391 | 382.6286 | 1.647 | 0
96205 | 85.9498 | 279.9327 | 292.8304 | 0 | 0
96215 | 153.6528 | 267.8404 | 308.7841 | 0.989 | -1.318
96225 | 265.3718 | 274.2851 | 381.6471 | 0.988 | -2.306
96235 | 323.0328 | 314.7401 | 451.0117 | 1.647 | -1.976
96245 | 240.9434 | 289.0076 | 376.27 | 0.659 | 0
96255 | 59.4641 | 320.5316 | 326.0008 | 1.647 | 1.976
96265 | -201.6099 | 295.4364 | 357.672 | 0.66 | 4.283
96275 | -327.5824 | 249.9565 | 412.054 | 0.329 | 3.294
96285 | -303.1026 | 221.2152 | 375.2431 | 0.329 | 1.648
96295 | -168.4492 | 184.7512 | 250.0163 | 0 | -0.329
96305 | 57.5077 | 196.3419 | 204.5905 | 0.659 | -2.637
96315 | 251.0255 | 190.1239 | 314.8982 | 0.329 | -3.293
96325 | 355.7104 | 180.5475 | 398.9076 | 0.33 | -2.966
96335 | 383.9294 | 193.5775 | 429.9698 | 0.659 | -2.306
96345 | 288.3929 | 223.3811 | 364.787 | 0.988 | -0.329
96355 | 198.9114 | 263.3457 | 330.0253 | 1.318 | 0
96365 | 148.4302 | 291.1316 | 326.786 | 1.318 | 0
96375 | 215.0452 | 366.5767 | 424.9975 | 2.306 | -1.647
96385 | 349.3981 | 386.7893 | 521.2341 | 1.647 | -2.966
96395 | 347.298 | 393.8393 | 525.0955 | 1.648 | -1.318
96405 | 330.1703 | 325.9817 | 463.979 | 0.329 | -1.317
96415 | 365.3121 | 292.8625 | 468.2108 | 0.659 | -1.977
96425 | 339.2936 | 318.0093 | 465.0269 | 1.318 | -0.989
96435 | 429.9933 | 378.091 | 572.5793 | 1.976 | -2.964
96445 | 510.6482 | 421.1047 | 661.8842 | 1.977 | -2.966
96455 | 502.6092 | 390.5683 | 636.5214 | 0.989 | -1.976
96465 | 454.2297 | 345.0373 | 570.4168 | 0.658 | -1.318
96475 | 385.8357 | 279.0831 | 476.1897 | 0 | -0.659
96485 | 244.9891 | 252.085 | 351.5203 | 0.33 | 0.988
96495 | 143.0542 | 238.9537 | 278.502 | 0.329 | 0.989
96505 | 42.4736 | 286.1882 | 289.3228 | 1.318 | 1.647
96515 | -11.8761 | 285.4659 | 285.7128 | 0.66 | 1.318
96525 | -27.7979 | 295.022 | 296.3287 | 0.987 | 0.988
96535 | -22.2117 | 286.4593 | 287.3191 | 0.659 | 0.659
96545 | 16.5892 | 258.2872 | 258.8193 | 0.33 | 0
96555 | 22.8328 | 257.4104 | 258.4211 | 0.659 | 0.33
96565 | 19.124 | 202.7029 | 203.603 | -0.33 | 0.329
96575 | 34.5551 | 138.2874 | 142.5393 | -0.659 | 0
96585 | 45.6322 | 57.0422 | 73.0487 | -1.317 | 0
96595 | 31.251 | 16.9991 | 35.5752 | -0.989 | 0.329
96605 | -39.7444 | 11.8038 | 41.4602 | -0.659 | 1.319
96615 | -55.7336 | 44.9959 | 71.6301 | 0 | 0.658
96625 | -117.1713 | 86.634 | 145.7209 | 0.33 | 1.648
96635 | -150.2824 | 92.4175 | 176.4251 | 0 | 1.318
96645 | -188.4183 | 148.3404 | 239.8048 | 0.989 | 1.646
96655 | -258.7195 | 173.6494 | 311.5926 | 0.658 | 2.307
96665 | -159.0689 | 126.8043 | 203.4263 | -0.329 | -0.329
96675 | -74.2931 | 108.5148 | 131.5102 | 0 | -0.331
96685 | -68.5026 | 63.9846 | 93.7371 | -0.66 | 0.331
96695 | -129.54 | -10.0844 | 129.9319 | -1.317 | 1.317
96705 | -175.7623 | -82.3868 | 194.1133 | -1.647 | 1.318
96715 | -164.9925 | -113.1972 | 200.0903 | -1.318 | 0.658
96725 | -134.8137 | -132.7522 | 189.2033 | -1.318 | 0.33
96735 | -135.4886 | -111.8281 | 175.6778 | -0.659 | 0.659
96745 | -64.2882 | -38.9962 | 75.1909 | 0.329 | -0.659
96755 | -64.6555 | 11.5746 | 65.6834 | 0.33 | 0.33
96765 | -57.7616 | 20.388 | 61.2542 | 0 | 0
96775 | -8.9506 | 80.3605 | 80.8574 | 0.988 | -0.66
96785 | 47.1677 | 167.342 | 173.8624 | 1.648 | -0.987
96795 | 47.0172 | 208.2214 | 213.4638 | 1.317 | -0.33
96805 | 99.6472 | 135.9381 | 168.5489 | -0.329 | -1.318
96815 | 49.8812 | 59.5525 | 77.6829 | -0.659 | 0.329
96825 | 22.3665 | -62.8817 | 66.741 | -1.977 | 0
96835 | -5.7169 | -132.7566 | 132.8796 | -1.647 | 0.33
96845 | -103.3875 | -231.0804 | 253.1543 | -2.635 | 1.647
96855 | -177.113 | -249.9573 | 306.3457 | -1.648 | 1.648
96865 | -203.2196 | -236.6516 | 311.933 | -1.318 | 1.318
96875 | -142.9591 | -156.0766 | 211.6534 | 0 | 0
96885 | -96.9352 | -40.4663 | 105.0427 | 0.989 | 0
96895 | -92.4931 | 94.0493 | 131.91 | 1.977 | 0.329
96905 | -55.2757 | 186.2654 | 194.2941 | 1.976 | -0.329
96915 | 13.6217 | 264.5714 | 264.9219 | 2.306 | -0.989
96925 | 120.0034 | 226.0068 | 255.8903 | 0.659 | -1.977
96935 | 158.1827 | 95.1063 | 184.5724 | -0.988 | -1.318
96945 | 81.0504 | -71.6219 | 108.1613 | -2.307 | 0.33
96955 | 22.3791 | -203.1149 | 204.3441 | -2.635 | 0.33
96965 | -46.5121 | -288.5408 | 292.2656 | -2.635 | 0.987
96975 | -95.6458 | -270.1988 | 286.6279 | -1.318 | 0.989
96985 | -145.5029 | -175.9587 | 228.3256 | 0 | 1.318
96995 | -105.3489 | -74.4354 | 128.9923 | 0.658 | 0
97005 | -11.9693 | 28.1189 | 30.5604 | 1.318 | -0.988
97015 | 108.9943 | 116.5485 | 159.5722 | 1.648 | -1.977
97025 | 250.1587 | 137.643 | 285.5258 | 0.988 | -2.966
97035 | 310.5935 | 109.3614 | 329.2844 | 0.33 | -2.306
97045 | 364.7428 | 33.076 | 366.2394 | -0.66 | -2.635
97055 | 256.3084 | -39.0862 | 259.2716 | -0.988 | 0
97065 | 149.5096 | -84.5024 | 171.7375 | -0.988 | 0.33
97075 | 108.3999 | -113.3478 | 156.8383 | -0.988 | 0
97085 | 49.1789 | -76.027 | 90.5465 | 0 | 0.658
97095 | -72.8444 | -84.0764 | 111.2436 | -0.66 | 1.977
97105 | -201.0858 | -118.4967 | 233.403 | -0.988 | 2.636
97115 | -327.1629 | -123.8888 | 349.8342 | -0.659 | 3.294
97125 | -417.1404 | -163.2309 | 447.9402 | -1.317 | 3.294
97135 | -576.224 | -119.885 | 588.5631 | 0 | 4.943
97145 | -566.3118 | -42.1992 | 567.8819 | 0.658 | 2.635
97155 | -448.5719 | 8.8314 | 448.6589 | 0.659 | 0.989
97165 | -353.9942 | 59.0213 | 358.8808 | 0.989 | 0.658
97175 | -224.4948 | 56.9862 | 231.6146 | 0.329 | -0.658
97185 | -152.9384 | 12.8308 | 153.4757 | -0.329 | -0.33
97195 | -152.0085 | 1.7517 | 152.0186 | 0 | 0.33
97205 | -135.6065 | -37.7728 | 140.769 | -0.659 | 0
97215 | -60.7133 | -50.0952 | 78.7124 | -0.33 | -0.989
97225 | 16.1768 | 23.278 | 28.347 | 0.989 | -1.317
97235 | 48.9022 | 22.9806 | 54.0327 | 0 | -0.989
97245 | 50.0637 | 29.9133 | 58.3196 | 0.329 | -0.659
97255 | 33.2673 | 2.1386 | 33.336 | -0.329 | -0.329
97265 | -14.437 | 36.2208 | 38.992 | 0.658 | 0.329
97275 | -8.9647 | 49.7957 | 50.5963 | 0.329 | -0.329
97285 | -15.5825 | 53.7685 | 55.981 | 0.331 | 0
97295 | -100.3503 | 38.6291 | 107.5285 | 0 | 1.317
97305 | -318.82 | 46.1757 | 322.1465 | 0.329 | 3.953
97315 | -306.607 | 74.7383 | 315.5847 | 0.659 | 0.989
97325 | -230.6673 | 18.8556 | 231.4367 | -0.659 | 0.33
97335 | -322.7951 | 28.8391 | 324.0809 | 0.329 | 2.635
97345 | -350.2205 | 28.5473 | 351.3821 | 0 | 1.647
97355 | -317.7552 | 61.4483 | 323.6422 | 0.659 | 0.989
97365 | -239.1325 | 108.3808 | 262.5466 | 0.989 | 0
97375 | -88.6169 | 178.6157 | 199.3904 | 1.647 | -1.647
97385 | -19.6727 | 172.2468 | 173.3666 | 0.659 | -0.989
97395 | -3.4765 | 121.5666 | 121.6163 | 0 | -0.659
97405 | 28.0427 | 126.62 | 129.6882 | 0.658 | -0.988
97415 | 55.83 | 100.7451 | 115.1805 | 0 | -0.988
97425 | 153.2274 | 77.5395 | 171.7295 | 0 | -2.306
97435 | 230.8443 | 45.4892 | 235.2836 | -0.329 | -2.306
97445 | 243.1345 | 41.1963 | 246.5999 | 0 | -1.648
97455 | 250.315 | 41.5914 | 253.7468 | 0 | -1.647
97465 | 185.2066 | 21.0236 | 186.3961 | -0.329 | -0.329
97475 | 79.042 | 4.0941 | 79.1479 | -0.33 | 0.658
97485 | 8.796 | 12.551 | 15.3264 | 0 | 0.659
97495 | -32.5775 | 0.77866 | 32.5868 | -0.329 | 0.659
97505 | -59.944 | 26.9348 | 65.7173 | 0.329 | 0.659
97515 | -2.5064 | 11.1983 | 11.4754 | -0.329 | -0.659
97525 | 63.2046 | 12.3383 | 64.3976 | 0 | -0.989
97535 | 65.215 | 17.2703 | 67.463 | 0 | -0.329
97545 | 2.3815 | 0.09981 | 2.3836 | -0.329 | 0.659
97555 | -101.5911 | -33.5022 | 106.9727 | -0.66 | 1.647
97565 | -174.1991 | -57.4707 | 183.4345 | -0.658 | 1.647
97575 | -200.6042 | -92.1649 | 220.7633 | -0.989 | 1.319
97585 | -159.9935 | -80.2413 | 178.9876 | -0.329 | 0.329
97595 | -168.206 | -125.4539 | 209.8379 | -1.319 | 0.989
97605 | -184.7571 | -205.0042 | 275.9745 | -1.976 | 0.988
97615 | -157.4315 | -242.1767 | 288.8498 | -1.647 | 0.329
97625 | 56.2737 | -283.4833 | 289.0147 | -1.977 | -2.965
97635 | 238.7576 | -298.1751 | 381.9864 | -1.647 | -3.294
97645 | 467.0995 | -211.8462 | 512.8944 | 0 | -5.272
97655 | 673.738 | -146.5548 | 689.4935 | 0 | -5.93
97665 | 739.336 | -207.5005 | 767.9025 | -1.647 | -4.613
97675 | 741.413 | -242.8775 | 780.1812 | -1.318 | -3.953
97685 | 906.7854 | -201.2995 | 928.8602 | -0.329 | -6.588
97695 | 934.5248 | -225.6786 | 961.3883 | -1.318 | -4.613
97705 | 1131.7249 | -158.0183 | 1142.7034 | 0.329 | -7.907
97715 | 1303.9169 | -98.6748 | 1307.6452 | 0.329 | -7.907
97725 | 1303.5552 | -122.6616 | 1309.3135 | -0.658 | -5.93
97735 | 1376.807 | -127.0554 | 1382.6571 | -0.33 | -7.248
97745 | 1435.71 | -238.6743 | 1455.4135 | -2.306 | -6.918
97755 | 1269.3391 | -135.9637 | 1276.6001 | 0.988 | -3.295
97765 | 970.613 | -75.1956 | 973.5215 | 0.329 | -0.329
97775 | 656.172 | -108.6193 | 665.1014 | -0.658 | 1.647
97785 | 582.7692 | 16.9754 | 583.0164 | 1.977 | -0.659
97795 | 615.8505 | 47.7982 | 617.7026 | 0.658 | -1.647
97805 | 384.0134 | 147.4422 | 411.3459 | 2.307 | 2.635
97815 | 208.1318 | 347.5196 | 405.0787 | 4.283 | 2.306
97825 | 102.7453 | 166.9636 | 196.0445 | -1.318 | 2.307
97835 | 218.1058 | 21.9204 | 219.2045 | -0.988 | -0.989
97845 | 349.4365 | 220.373 | 413.1224 | 3.624 | -1.647
97855 | 384.4884 | 140.127 | 409.2272 | -0.66 | -0.988
97865 | 414.1722 | 117.3701 | 430.4815 | 0.66 | -1.318
97875 | 378.5843 | 165.6472 | 413.2373 | 1.317 | -0.329
97885 | 307.2691 | 105.0906 | 324.7435 | -0.329 | 0.329
97895 | 487.9753 | 166.4565 | 515.5847 | 1.647 | -3.624
97905 | 658.2448 | 401.6673 | 771.1179 | 4.613 | -3.953
97915 | 606.3894 | 383.1571 | 717.2987 | 1.317 | -1.318
97925 | 436.2824 | 280.8073 | 518.8401 | 0.329 | 0.659
97935 | 262.6054 | 258.7325 | 368.6517 | 0.989 | 1.646
97945 | -5.2778 | 180.3339 | 180.4112 | -0.329 | 4.284
97955 | -66.542 | -92.8947 | 114.2684 | -3.954 | 1.977
97965 | -393.5646 | -104.6898 | 407.2506 | -0.659 | 7.248
97975 | -492.6708 | -442.0549 | 661.9192 | -6.918 | 4.282
97985 | -452.5456 | -535.728 | 701.2859 | -3.624 | 2.966
97995 | -340.4806 | -252.2833 | 423.7616 | 1.647 | 1.317
98005 | -405.2338 | -234.5983 | 468.2423 | -1.647 | 3.624
98015 | -596.2252 | -350.7191 | 691.7286 | -2.965 | 5.601
98025 | -776.523 | -393.8533 | 870.6942 | -2.306 | 6.26
98035 | -863.4545 | -472.9331 | 984.4894 | -3.295 | 5.601
98045 | -942.6652 | -461.8332 | 1049.7179 | -1.977 | 5.93
98055 | -876.8307 | -465.3301 | 992.6551 | -2.306 | 3.624
98065 | -768.8509 | -325.4451 | 834.8929 | 0.33 | 2.635
98075 | -669.4883 | -273.8891 | 723.3463 | -0.659 | 1.976
98085 | -533.8286 | -335.581 | 630.5455 | -1.977 | 0.66
98095 | -403.0261 | -384.8824 | 557.2832 | -1.976 | 0
98105 | -164.5934 | -355.8839 | 392.1025 | -0.989 | -2.636
98115 | 30.2275 | -291.5783 | 293.141 | -0.329 | -2.965
98125 | 290.3656 | -287.3588 | 408.5183 | -0.989 | -5.271
98135 | 484.6799 | -273.8307 | 556.6847 | -0.659 | -5.272
98145 | 710.8083 | -279.8569 | 763.9164 | -0.989 | -6.918
98155 | 768.9486 | -210.285 | 797.1836 | 0.331 | -4.941
98165 | 973.5843 | -57.0977 | 975.2572 | 1.976 | -7.908
98175 | 1017.7626 | 72.4552 | 1020.3384 | 2.306 | -5.601
98185 | 861.6923 | 80.1952 | 865.416 | 0.988 | -2.635
98195 | 699.1831 | 20.1542 | 699.4735 | 0 | -1.647
98205 | 568.0167 | -17.9394 | 568.2999 | 0 | -0.989
98215 | 468.7774 | -35.4096 | 470.1129 | 0 | -0.659
98225 | 426.1284 | -120.896 | 442.9461 | -1.317 | -0.988
98235 | 479.8824 | -70.8555 | 485.0852 | 0.659 | -2.306
98245 | 447.7289 | 20.6992 | 448.2072 | 1.318 | -0.988
98255 | 335.1605 | 22.64 | 335.9243 | 0.329 | 0.329
98265 | 312.5957 | 53.0469 | 317.0647 | 0.988 | -0.659
98275 | 328.8996 | 44.8131 | 331.9385 | 0.33 | -0.988
98285 | 338.1458 | 92.1349 | 350.4731 | 1.317 | -0.988
98295 | 360.9256 | 77.5467 | 369.1623 | 0.33 | -1.318
98305 | 358.5364 | 155.4175 | 390.7722 | 1.977 | -0.989
98315 | 257.0431 | 205.4573 | 329.0651 | 1.646 | 0.659
98325 | 178.2785 | 60.5089 | 188.2673 | -1.317 | 0.659
98335 | 111.8284 | -112.266 | 158.459 | -2.306 | 0.989
98345 | 25.5165 | -222.3662 | 223.8254 | -2.307 | 1.646
98355 | 38.1052 | -310.8929 | 313.2194 | -2.635 | 0.33
98365 | -41.2092 | -317.2935 | 319.9584 | -1.647 | 1.977
98375 | -287.5824 | -240.6681 | 374.9997 | -0.329 | 4.941
98385 | -415.168 | -130.2982 | 435.1345 | 0.658 | 3.954
98395 | -545.5779 | -77.1457 | 551.0052 | 0.329 | 4.942
98405 | -515.9237 | -11.1869 | 516.045 | 0.989 | 2.636
98415 | -331.7487 | 134.6579 | 358.0362 | 2.635 | 0
98425 | -14.2388 | 147.3077 | 147.9943 | 0.989 | -3.295
98435 | 320.5635 | 159.5977 | 358.0955 | 1.318 | -5.271
98445 | 486.6258 | 140.7443 | 506.5704 | 0.659 | -4.283
98455 | 624.2891 | 126.378 | 636.9524 | 0.658 | -4.942
98465 | 693.2193 | 83.7656 | 698.2619 | 0 | -4.283
98475 | 626.8851 | -23.7433 | 627.3346 | -1.317 | -2.307
98485 | 522.4689 | -5.3122 | 522.4959 | 0.33 | -1.317
98495 | 461.4834 | 216.355 | 509.6826 | 3.624 | -1.318
98505 | 431.2445 | 286.6614 | 517.8287 | 1.976 | -1.318
98515 | 376.766 | 252.6714 | 453.6469 | 0.988 | -0.658
98525 | 414.7441 | 230.5697 | 474.5261 | 0.989 | -1.977
98535 | 511.0965 | 223.5541 | 557.8495 | 0.988 | -2.966
98545 | 406.3113 | -8.2903 | 406.3958 | -2.965 | 0
98555 | 235.3898 | -93.9792 | 253.457 | -1.318 | 1.319
98565 | 219.5394 | -67.3574 | 229.6401 | -0.329 | -0.33
98575 | 53.6511 | -164.3219 | 172.8587 | -2.306 | 2.636
98585 | -201.3831 | -269.9943 | 336.8265 | -2.636 | 4.612
98595 | -456.6431 | -320.4892 | 557.8855 | -2.306 | 5.93
98605 | -577.2224 | -354.083 | 677.1709 | -2.306 | 4.942
98615 | -673.5977 | -247.9531 | 717.7845 | 0 | 5.271
98625 | -620.3869 | -126.8508 | 633.2227 | 0.659 | 2.965
98635 | -483.0754 | 42.8173 | 484.9693 | 2.305 | 1.318
98645 | -302.1464 | 67.4557 | 309.5848 | 0.66 | -0.329
98655 | 27.5201 | -10.2899 | 29.3809 | -0.66 | -3.954
98665 | 186.6621 | -83.1677 | 204.3517 | -0.987 | -2.635
98675 | 308.7035 | -242.2068 | 392.3798 | -2.966 | -3.295
98685 | 402.8133 | -129.9367 | 423.2518 | 0.989 | -3.295
98695 | 258.9126 | 37.5267 | 261.6181 | 1.977 | 0.33
98705 | 124.1206 | 256.7919 | 285.2157 | 3.953 | 0.659
98715 | -7.1078 | 336.1061 | 336.1813 | 2.635 | 1.647
98725 | -58.0086 | 221.5538 | 229.022 | 0 | 0.988
98735 | -83.4305 | 77.5129 | 113.881 | -0.988 | 0.989
98745 | -142.5347 | -30.3499 | 145.73 | -1.318 | 1.647
98755 | -227.9579 | -20.8966 | 228.9136 | 0 | 2.306
98765 | -213.5322 | 131.1061 | 250.5689 | 2.306 | 0.989
98775 | -195.0176 | 282.3389 | 343.143 | 2.966 | 0.988
98785 | 59.1699 | 494.7473 | 498.273 | 4.942 | -3.295
98795 | 295.412 | 554.2238 | 628.0384 | 3.294 | -3.953
98805 | 307.9042 | 656.7128 | 725.3115 | 4.612 | -1.647
98815 | -85.634 | 747.0874 | 751.9792 | 4.612 | 4.942
98825 | -499.1132 | 638.3654 | 810.3236 | 1.648 | 6.918
98835 | -917.1626 | 551.735 | 1070.3265 | 1.647 | 9.554
98845 | -1498.9815 | 588.4714 | 1610.3553 | 2.965 | 14.497
98855 | -1790.5058 | 628.857 | 1897.7281 | 2.965 | 12.189
98865 | -1833.648 | 712.5492 | 1967.2293 | 3.953 | 9.883
98875 | -1817.6014 | 740.4673 | 1962.6427 | 3.295 | 8.895
98885 | -1736.6099 | 774.2305 | 1901.3802 | 3.624 | 7.249
98895 | -1696.2446 | 806.0163 | 1878.0064 | 3.624 | 7.248
98905 | -1481.8269 | 696.8046 | 1637.4821 | 1.318 | 3.624
98915 | -1345.9319 | 573.3008 | 1462.9445 | 0.659 | 3.953
98925 | -1127.0078 | 421.1203 | 1203.1163 | -0.659 | 1.318
98935 | -948.6358 | 314.7219 | 999.4798 | -0.659 | 0.988
98945 | -800.4973 | 94.1726 | 806.0176 | -3.294 | 0.329
98955 | -602.0925 | -94.1366 | 609.4071 | -3.624 | -1.317
98965 | -379.795 | -141.3131 | 405.2328 | -2.307 | -2.636
98975 | -126.1774 | -130.0742 | 181.2182 | -1.647 | -4.283
98985 | -38.252 | -34.8279 | 51.732 | 0 | -2.635
98995 | 31.6608 | 68.4652 | 75.4314 | 0.659 | -2.965
99005 | 309.2639 | 130.1219 | 335.5233 | 0.659 | -6.59
99015 | 609.424 | 30.2101 | 610.1724 | -1.648 | -7.907
99025 | 857.8502 | -36.0405 | 858.607 | -1.317 | -8.565
99035 | 1134.1059 | -32.6835 | 1134.5768 | -0.659 | -10.213
99045 | 1249.7979 | -66.6578 | 1251.5743 | -1.317 | -8.565
99055 | 1194.7052 | -3.5137 | 1194.7103 | 0.329 | -6.261
99065 | 1167.0462 | 88.2885 | 1170.381 | 0.988 | -6.259
99075 | 1042.0557 | 184.8939 | 1058.3316 | 1.647 | -3.953
99085 | 824.2998 | 269.5749 | 867.2605 | 1.977 | -1.648
99095 | 567.4677 | 249.7423 | 619.9925 | 0.659 | 0.33
99105 | 264.4024 | 112.1589 | 287.2077 | -1.318 | 2.635
99115 | -77.9961 | 70.3775 | 105.0542 | -0.329 | 4.942
99125 | -239.185 | 135.1202 | 274.7125 | 0.988 | 3.624
99135 | -84.5548 | 261.611 | 274.936 | 2.306 | -0.658
99145 | 267.7354 | 388.4773 | 471.8017 | 2.965 | -4.613
99155 | 584.8105 | 473.5946 | 752.5259 | 2.966 | -5.93
99165 | 806.4346 | 510.9824 | 954.6935 | 2.635 | -6.26
99175 | 1011.2333 | 633.5913 | 1193.3276 | 4.282 | -7.248
99185 | 1161.4283 | 637.7767 | 1325.0188 | 2.637 | -7.248
99195 | 1269.0431 | 628.247 | 1416.0384 | 2.635 | -7.248
99205 | 1160.9784 | 613.7346 | 1313.2178 | 2.306 | -3.953
99215 | 1096.9692 | 665.1052 | 1282.8509 | 3.294 | -4.283
99225 | 1003.1475 | 616.2655 | 1177.3224 | 1.648 | -2.965
99235 | 862.9676 | 591.2731 | 1046.0961 | 1.976 | -1.647
99245 | 847.4276 | 566.8172 | 1019.5172 | 1.648 | -2.965
99255 | 932.4663 | 454.0226 | 1037.1258 | 0 | -4.284
99265 | 862.1421 | 331.0358 | 923.5116 | -0.659 | -1.976
99275 | 641.384 | 173.7353 | 664.4978 | -1.976 | 0.659
99285 | 465.0816 | 79.7925 | 471.8768 | -1.648 | 0.988
99295 | 566.5258 | 78.707 | 571.9671 | -0.659 | -2.635
99305 | 814.1401 | 175.7201 | 832.8876 | 0.989 | -5.271
99315 | 867.6858 | 147.5755 | 880.1461 | -0.66 | -3.295
99325 | 896.8792 | 68.1259 | 899.4628 | -1.317 | -3.624
99335 | 811.8475 | -83.5269 | 816.133 | -2.966 | -1.648
99345 | 762.6725 | -177.6221 | 783.083 | -2.635 | -1.976
99355 | 742.0832 | -120.9165 | 751.8699 | -0.659 | -1.977
99365 | 671.7318 | -74.7959 | 675.8831 | -0.659 | -0.988
99375 | 752.4475 | -18.3213 | 752.6705 | 0 | -3.294
99385 | 961.1717 | -96.1706 | 965.971 | -1.977 | -5.601
99395 | 1071.3022 | -110.2535 | 1076.9607 | -0.988 | -4.942
99405 | 979.3172 | -69.7031 | 981.7947 | -0.33 | -2.306
99415 | 769.8674 | -43.2375 | 771.0806 | -0.329 | 0
99425 | 511.8952 | -49.9377 | 514.3253 | -0.659 | 1.976
99435 | 528.363 | -78.0911 | 534.1026 | -0.988 | -1.318
99445 | 646.3499 | -214.8424 | 681.1207 | -2.965 | -2.635
99455 | 623.8603 | -378.5627 | 729.7337 | -3.953 | -0.989
99465 | 510.7418 | -548.4037 | 749.4024 | -4.942 | 0.331
99475 | 505.9734 | -439.0554 | 669.9095 | -0.989 | -0.989
99485 | 534.9695 | -359.1258 | 644.3319 | -1.317 | -1.318
99495 | 492.4081 | -271.1972 | 562.1509 | -0.33 | -0.33
99505 | 471.8694 | -133.6507 | 490.4317 | 0.988 | -0.658
99515 | 423.4409 | -76.6652 | 430.3252 | 0.33 | 0
99525 | 133.5116 | -145.0754 | 197.1603 | -1.318 | 4.282
99535 | -284.2599 | -392.0746 | 484.279 | -4.612 | 7.578
99545 | -576.9879 | -478.1799 | 749.3805 | -2.966 | 7.577
99555 | -576.8205 | -454.9892 | 734.668 | -1.976 | 4.284
99565 | -430.9692 | -383.2903 | 576.7546 | -0.988 | 1.976
99575 | -343.955 | -240.9958 | 419.981 | 0.658 | 1.977
99585 | -308.3949 | -237.4625 | 389.2247 | -0.988 | 1.977
99595 | -218.043 | -178.0832 | 281.5251 | 0.33 | 0.658
99605 | -154.7767 | 10.9428 | 155.163 | 2.635 | 0.659
99615 | -102.6807 | 112.5319 | 152.3376 | 1.977 | 0.33
99625 | -30.4392 | 111.7036 | 115.7767 | 0.988 | -0.33
99635 | 96.5923 | 52.0046 | 109.7021 | 0 | -1.647
99645 | 72.7602 | -5.7673 | 72.9884 | -0.329 | 0.33
99655 | 134.3276 | 76.3205 | 154.4951 | 1.648 | -1.318
99665 | 291.6997 | 168.7522 | 336.9956 | 1.976 | -2.966
99675 | 386.2206 | 247.2501 | 458.5836 | 2.306 | -2.635
99685 | 385.7864 | 245.4155 | 457.2307 | 1.318 | -1.648
99695 | 402.2018 | 143.4086 | 427.0039 | -0.33 | -1.976
99705 | 443.1511 | 51.5748 | 446.1422 | -0.659 | -2.306
99715 | 495.7303 | 16.3526 | 495.9999 | -0.329 | -2.636
99725 | 478.3558 | 94.313 | 487.5645 | 1.318 | -1.647
99735 | 462.2803 | 234.1363 | 518.192 | 2.635 | -1.647
99745 | 478.0507 | 158.3592 | 503.5971 | -0.329 | -1.977
99755 | 667.5606 | 139.8425 | 682.0506 | 0.659 | -4.942
99765 | 971.323 | 339.0589 | 1028.7999 | 3.953 | -7.577
99775 | 1090.8948 | 534.1385 | 1214.642 | 4.613 | -5.93
99785 | 1059.3923 | 371.6948 | 1122.7062 | -0.329 | -4.284
99795 | 1079.3208 | 132.1397 | 1087.3796 | -1.978 | -4.941
99805 | 883.4768 | -36.7306 | 884.24 | -2.306 | -0.989
99815 | 346.362 | -219.1389 | 409.864 | -3.624 | 5.601
99825 | 16.5635 | -216.08 | 216.7139 | -1.317 | 4.613
99835 | -94.9906 | -158.7871 | 185.0312 | -0.66 | 3.295
99845 | -129.4213 | -148.4002 | 196.9073 | -0.988 | 2.635
99855 | -220.9409 | -17.4715 | 221.6306 | 1.318 | 3.624
99865 | -303.2531 | 26.6727 | 304.4239 | 0.33 | 3.624
99875 | -269.2435 | 115.8991 | 293.1291 | 1.646 | 1.976
99885 | -263.2727 | 72.6077 | 273.1015 | -0.329 | 2.306
99895 | -257.3819 | -31.5449 | 259.3078 | -1.317 | 1.977
99905 | -219.6613 | -62.0195 | 228.2488 | -0.66 | 1.318
99915 | -139.37 | -72.8636 | 157.2676 | -0.658 | 0.329
99925 | 10.0067 | -102.2309 | 102.7195 | -0.989 | -1.318
99935 | 229.743 | -29.8437 | 231.6733 | 0.659 | -3.293
99945 | 249.0673 | -8.2691 | 249.2045 | 0 | -0.989
99955 | 104.4357 | -24.7113 | 107.3194 | -0.329 | 1.318
99965 | 174.6571 | 97.8277 | 200.1884 | 1.977 | -1.648
99975 | 273.9687 | 121.1144 | 299.5456 | 0.658 | -1.976
99985 | 46.3355 | 4.505 | 46.554 | -1.318 | 2.964
99995 | -181.0362 | 32.9821 | 184.0161 | 0.66 | 3.624
100005 | -339.0935 | -59.517 | 344.2771 | -1.648 | 3.954
100015 | -464.813 | -201.8996 | 506.7688 | -2.636 | 4.283
100025 | -632.4946 | -258.9347 | 683.4447 | -1.976 | 5.601
100035 | -683.971 | -290.1795 | 742.9808 | -1.977 | 4.283
100045 | -617.1349 | -412.733 | 742.4311 | -3.624 | 2.635
100055 | -478.5078 | -299.7929 | 564.664 | 0 | 0.989
100065 | -465.7112 | -312.0349 | 560.5825 | -1.977 | 2.305
100075 | -498.9058 | -293.6359 | 578.9033 | -0.988 | 2.637
100085 | -484.9801 | -213.9858 | 530.0902 | 0 | 1.976
100095 | -510.9998 | -274.0485 | 579.8477 | -1.976 | 2.636
100105 | -423.2012 | -199.5081 | 467.8705 | 0.329 | 0.658
100115 | -254.9595 | -88.7585 | 269.9674 | 0.988 | -0.988
100125 | -177.9958 | -75.678 | 193.4158 | 0 | -0.329
100135 | -157.4865 | -134.4329 | 207.0609 | -0.988 | 0
100145 | -85.1681 | -157.0505 | 178.6574 | -0.659 | -0.989
100155 | -45.0073 | -106.9963 | 116.077 | 0.33 | -0.658
100165 | -97.869 | -239.6989 | 258.9091 | -2.636 | 0.658
100175 | -139.0095 | -219.0622 | 259.4454 | -0.33 | 0.66
100185 | -216.5925 | -178.6302 | 280.7509 | -0.329 | 1.646
100195 | -388.9967 | -140.7027 | 413.6613 | 0 | 3.624
100205 | -476.653 | -153.1697 | 500.6586 | -0.66 | 2.966
100215 | -486.4027 | -167.6451 | 514.4827 | -0.658 | 2.306
100225 | -455.0251 | -136.5345 | 475.0679 | 0 | 1.647
100235 | -436.2433 | -91.4484 | 445.7252 | 0.329 | 1.647
100245 | -507.1386 | -137.9576 | 525.5681 | -0.988 | 2.966
100255 | -509.6843 | -83.5048 | 516.4796 | 0.659 | 1.976
100265 | -463.8669 | 8.5257 | 463.9452 | 1.318 | 1.318
100275 | -511.2564 | 70.155 | 516.0473 | 1.318 | 2.636
100285 | -634.5928 | 52.233 | 636.7388 | 0.329 | 3.953
100295 | -628.4493 | 35.3309 | 629.4417 | 0.33 | 2.306
100305 | -552.5743 | 11.0857 | 552.6855 | 0 | 1.318
100315 | -426.8257 | 71.9846 | 432.8533 | 1.318 | 0
100325 | -359.4348 | 86.641 | 369.7297 | 0.658 | 0.329
100335 | -265.4832 | 88.6346 | 279.8882 | 0.659 | -0.658
100345 | -213.2702 | 55.2465 | 220.3097 | 0 | -0.33
100355 | -162.9703 | 11.0249 | 163.3428 | -0.329 | -0.659
100365 | -161.6477 | 2.0855 | 161.6612 | 0 | 0
100375 | -182.4722 | 0.66081 | 182.4734 | 0 | 0.329
100385 | -270.1989 | 37.2071 | 272.7486 | 0.658 | 1.648
100395 | -295.8969 | 85.6297 | 308.038 | 0.989 | 0.988
100405 | -186.6873 | 79.8506 | 203.0474 | 0.329 | -0.988
100415 | 14.5894 | 109.1383 | 110.1092 | 0.989 | -2.965
100425 | 214.7256 | 98.5422 | 236.2576 | 0.329 | -3.954
100435 | 312.317 | 28.3616 | 313.6021 | -0.658 | -3.294
100445 | 239.7575 | -41.6297 | 243.3448 | -0.989 | -0.989
100455 | 184.0167 | -47.9579 | 190.1634 | -0.329 | -0.988
100465 | 297.1289 | 126.61 | 322.9794 | 2.635 | -3.294
100475 | 338.574 | 300.1996 | 452.4955 | 3.295 | -2.306
100485 | 202.179 | 352.7195 | 406.5555 | 2.306 | 0.329
100495 | -34.912 | 322.2154 | 324.1012 | 1.318 | 2.635
100505 | -215.724 | 148.6275 | 261.9675 | -1.318 | 2.966
100515 | -290.2651 | 98.6103 | 306.558 | 0 | 2.306
100525 | -258.818 | 202.4373 | 328.5842 | 1.976 | 0.988
100535 | -62.01 | 225.472 | 233.8437 | 0.989 | -1.977
100545 | 62.4898 | 14.9282 | 64.2481 | -2.636 | -1.647
100555 | 168.4586 | -167.8467 | 237.8041 | -2.965 | -2.307
100565 | 187.1849 | -279.3343 | 336.2526 | -2.965 | -1.317
100575 | 135.5624 | -200.4582 | 241.993 | -0.329 | -0.329
100585 | 62.6391 | -37.3576 | 72.9331 | 1.318 | 0.329
100595 | -60.6373 | 11.4779 | 61.7141 | 0.329 | 1.648
100605 | -186.4432 | -11.2374 | 186.7816 | -0.329 | 2.306
100615 | -251.1749 | -9.7506 | 251.3641 | 0 | 1.976
100625 | -464.2175 | -80.2775 | 471.1076 | -1.318 | 4.941
100635 | -613.7205 | -99.3928 | 621.7168 | -0.659 | 4.613
100645 | -725.4181 | -103.2767 | 732.7329 | -0.659 | 4.942
100655 | -790.7911 | -147.3713 | 804.406 | -1.318 | 4.612
100665 | -743.8327 | -144.9081 | 757.8162 | -0.659 | 2.966
100675 | -652.9851 | 15.9917 | 653.1809 | 1.977 | 1.976
100685 | -387.9942 | 196.6923 | 435.0027 | 2.965 | -1.647
100695 | -175.4119 | 180.2224 | 251.4945 | 0.659 | -1.977
100705 | -200.5159 | 53.9008 | 207.6341 | -0.988 | 0.659
100715 | -276.082 | -50.5426 | 280.6703 | -1.318 | 1.318
100725 | -376.5316 | -75.1835 | 383.9644 | -0.659 | 2.306
100735 | -329.7621 | -27.1034 | 330.8741 | 0.329 | 0.329
100745 | -125.9229 | 105.0215 | 163.9698 | 1.977 | -2.306
100755 | 22.6632 | 277.3997 | 278.3239 | 3.295 | -2.306
100765 | 16.9858 | 223.3887 | 224.0335 | 0.329 | -0.659
100775 | -92.3382 | -10.0133 | 92.8795 | -2.636 | 0.989
100785 | -282.1565 | -78.0024 | 292.7399 | -0.988 | 2.965
100795 | -394.1977 | -98.3199 | 406.2741 | -0.989 | 2.635
100805 | -323.7939 | -21.6339 | 324.5158 | 0.66 | 0.33
100815 | -319.8605 | 57.898 | 325.0584 | 0.988 | 1.318
100825 | -354.5716 | 86.5515 | 364.9825 | 0.659 | 1.647
100835 | -379.5483 | 120.3562 | 398.174 | 0.988 | 1.648
100845 | -377.0561 | 108.7582 | 392.4279 | 0.329 | 1.317
100855 | -105.5754 | 135.0383 | 171.4104 | 0.989 | -3.294
100865 | 222.2547 | 122.645 | 253.8482 | 0.329 | -5.272
100875 | 324.5404 | -44.8801 | 327.6289 | -2.306 | -3.294
100885 | 278.5661 | -95.9704 | 294.6344 | -0.988 | -1.648
100895 | 365.4513 | 4.2116 | 365.4755 | 0.988 | -3.624
100905 | 453.0049 | 99.4611 | 463.7951 | 1.319 | -3.624
100915 | 435.9718 | 21.7887 | 436.516 | -0.989 | -2.306
100925 | 383.3959 | -49.1307 | 386.5311 | -0.989 | -1.647
100935 | 336.1352 | -68.8406 | 343.1121 | -0.659 | -1.318
100945 | 368.6031 | -59.9471 | 373.4459 | -0.329 | -2.306
100955 | 288.1066 | -169.3402 | 334.1879 | -2.306 | -0.329
100965 | 123.9254 | -221.3078 | 253.6427 | -1.647 | 1.318
100975 | 30.7112 | -246.4174 | 248.3238 | -1.648 | 0.988
100985 | 16.5782 | -171.6244 | 172.4233 | 0 | 0.329
100995 | -47.597 | -93.8608 | 105.2394 | 0.33 | 1.318
101005 | -140.9363 | -163.3969 | 215.7813 | -1.648 | 1.977
101015 | -149.8829 | -150.4754 | 212.3859 | -0.329 | 0.988
101025 | -110.8389 | -202.9179 | 231.2162 | -1.647 | 0.33
101035 | -163.622 | -329.3924 | 367.7927 | -2.965 | 1.647
101045 | -233.5908 | -363.0873 | 431.7373 | -1.977 | 1.977
101055 | -319.4282 | -356.4949 | 478.668 | -1.647 | 2.635
101065 | -459.9162 | -356.2324 | 581.7426 | -1.647 | 3.953
101075 | -603.4362 | -361.3048 | 703.3323 | -1.648 | 4.613
101085 | -608.4395 | -310.3232 | 683.0074 | -0.658 | 2.965
101095 | -565.3626 | -156.5498 | 586.6368 | 1.317 | 2.307
101105 | -563.9086 | -121.6515 | 576.8813 | 0 | 2.635
101115 | -613.249 | -96.5019 | 620.7954 | 0.329 | 3.294
101125 | -636.2724 | -33.6089 | 637.1594 | 0.989 | 2.965
101135 | -555.5019 | -24.0617 | 556.0228 | 0.329 | 1.318
101145 | -322.0907 | -3.4461 | 322.1092 | 0.659 | -1.647
101155 | -77.2304 | -21.1464 | 80.0731 | 0 | -2.965
101165 | -31.4332 | -17.1051 | 35.7859 | 0.33 | -0.989
101175 | -56.9298 | -26.9413 | 62.9829 | 0 | -0.329
101185 | 28.8487 | 22.4167 | 36.5343 | 0.988 | -1.977
101195 | 164.0199 | 84.2957 | 184.4134 | 1.318 | -2.965
101205 | 49.3048 | 49.2334 | 69.677 | 0 | 0.66
101215 | -206.3184 | -79.4491 | 221.0869 | -1.647 | 3.293
101225 | -436.9666 | -113.2871 | 451.4131 | -0.659 | 4.284
101235 | -585.8869 | -63.9002 | 589.3613 | 0.329 | 4.282
101245 | -721.9455 | -46.339 | 723.4311 | 0 | 4.943
101255 | -784.5916 | -22.414 | 784.9117 | 0.33 | 4.282
101265 | -750.1462 | 15.6803 | 750.3101 | 0.658 | 2.965
101275 | -651.0736 | -33.9522 | 651.9582 | -0.658 | 1.647
101285 | -549.3568 | 18.7825 | 549.6778 | 0.988 | 0.989
101295 | -448.8656 | 33.0236 | 450.0788 | 0.33 | 0.329
101305 | -402.1324 | 33.0402 | 403.4875 | 0.329 | 0.659
101315 | -473.0161 | 16.6255 | 473.3082 | 0 | 2.307
101325 | -684.7574 | 4.5747 | 684.7727 | 0 | 4.941
101335 | -800.9477 | 17.802 | 801.1455 | 0.329 | 4.283
101345 | -807.9722 | -27.8235 | 808.4511 | -0.658 | 3.294
101355 | -772.7829 | 29.7304 | 773.3546 | 0.988 | 2.636
101365 | -811.2313 | 26.1859 | 811.6538 | 0 | 3.624
101375 | -890.2366 | 68.9626 | 892.9038 | 0.988 | 4.283
101385 | -872.0015 | 12.2036 | 872.0869 | -0.659 | 2.965
101395 | -890.3129 | -20.8358 | 890.5567 | -0.329 | 3.624
101405 | -897.0216 | 42.556 | 898.0304 | 0.988 | 3.294
101415 | -939.8158 | 74.9046 | 942.7961 | 0.659 | 3.953
101425 | -901.2723 | 89.4231 | 905.6976 | 0.658 | 2.637
101435 | -809.6463 | 4.5913 | 809.6593 | -0.987 | 1.647
101445 | -729.7421 | -24.5728 | 730.1557 | -0.33 | 1.317
101455 | -660.9711 | -51.9433 | 663.009 | -0.659 | 0.989
101465 | -461.0137 | -55.4096 | 464.3317 | -0.329 | -1.647
101475 | -193.2268 | -16.8632 | 193.9613 | 0.329 | -3.624
101485 | 32.0012 | 11.6533 | 34.0569 | 0.33 | -4.283
101495 | 50.8011 | -49.364 | 70.8347 | -0.989 | -1.977
101505 | -5.1294 | -100.1062 | 100.2375 | -0.988 | -0.989
101515 | -146.8836 | -110.3168 | 183.697 | -0.659 | 0.989
101525 | -281.18 | -38.2485 | 283.7695 | 0.659 | 1.648
101535 | -112.2102 | -40.625 | 119.3378 | -0.33 | -2.637
101545 | 115.0515 | -93.569 | 148.297 | -0.988 | -3.953
101555 | 71.8954 | -150.2856 | 166.5975 | -1.318 | -0.658
101565 | -251.6345 | -130.6744 | 283.5414 | -0.329 | 3.953
101575 | -426.8701 | -71.6678 | 432.8445 | 0.329 | 2.964
101585 | -208.4716 | -89.8252 | 227 | -0.658 | -2.306
101595 | 184.8504 | -112.8936 | 216.5979 | -0.66 | -5.929
101605 | 338.7696 | -29.269 | 340.0316 | 0.989 | -3.954
101615 | 165.4604 | 77.0405 | 182.5168 | 1.647 | 0.329
101625 | -122.5787 | 51.0296 | 132.7763 | 0 | 2.966
101635 | -330.1267 | -76.1592 | 338.7976 | -1.647 | 3.294
101645 | -226.1568 | -127.3713 | 259.558 | -0.989 | -0.659
101655 | 46.3115 | -207.1404 | 212.2543 | -1.977 | -3.624
101665 | 214.482 | -212.4435 | 301.8854 | -0.987 | -3.295
101675 | 216.3784 | -73.0248 | 228.3686 | 1.318 | -1.646
101685 | 151.9197 | 31.3238 | 155.1153 | 1.317 | -0.66
101695 | 266.7828 | 33.5318 | 268.8818 | 0.329 | -3.294
101705 | 371.9664 | 142.9408 | 398.4859 | 2.307 | -3.294
101715 | 226.5616 | 255.0368 | 341.1362 | 2.635 | 0.329
101725 | -8.1588 | 309.2297 | 309.3373 | 2.306 | 2.306
101735 | -258.1543 | 287.4612 | 386.3646 | 1.318 | 3.953
101745 | -446.7009 | 252.3357 | 513.0448 | 0.989 | 4.283
101755 | -455.9138 | 196.279 | 496.3697 | 0.329 | 2.307
101765 | -451.8683 | 159.2832 | 479.1201 | 0.33 | 2.306
101775 | -636.3418 | 197.0941 | 666.1659 | 1.318 | 5.271
101785 | -808.1152 | 288.7853 | 858.165 | 2.306 | 5.601
101795 | -883.2871 | 277.9557 | 925.9889 | 0.988 | 4.941
101805 | -915.734 | 239.7669 | 946.6028 | 0.659 | 4.613
101815 | -696.8691 | 180.0414 | 719.7509 | 0 | 0.329
101825 | -280.2332 | 138.9196 | 312.7768 | 0 | -3.953
101835 | 84.3118 | 153.3758 | 175.0218 | 0.659 | -5.271
101845 | 377.3049 | 206.6061 | 430.1686 | 1.318 | -6.26
101855 | 637.0859 | 282.8024 | 697.0335 | 1.976 | -7.248
101865 | 690.0536 | 317.0832 | 759.418 | 1.648 | -4.942
101875 | 526.5268 | 278.5463 | 595.6664 | 0.658 | -1.647
101885 | 223.65 | 94.9521 | 242.9717 | -1.976 | 1.647
101895 | 98.8665 | 35.4165 | 105.0187 | -0.659 | 0.329
101905 | 160.4283 | 72.9125 | 176.2199 | 0.329 | -1.646
101915 | 272.7339 | 42.2003 | 275.9794 | -0.659 | -2.636
101925 | 482.8077 | 27.5679 | 483.5941 | -0.329 | -4.942
101935 | 599.1677 | 2.1774 | 599.1717 | -0.659 | -4.283
101945 | 494.9058 | 37.8266 | 496.3493 | 0.329 | -1.318
101955 | 353.9577 | 106.6686 | 369.6813 | 0.989 | -0.329
101965 | 212.2147 | 133.3929 | 250.6566 | 0.659 | 0.659
101975 | -92.2925 | 107.137 | 141.408 | 0 | 4.283
101985 | -355.7101 | -10.1219 | 355.8541 | -1.648 | 4.942
101995 | -295.3398 | -20.7207 | 296.0658 | -0.329 | 0.988
102005 | -132.9074 | 25.7835 | 135.3852 | 0.329 | -0.659
102015 | 196.6988 | 36.8599 | 200.1227 | 0 | -4.613
102025 | 509.9057 | 76.0349 | 515.5435 | 0.659 | -5.93
102035 | 636.515 | 68.673 | 640.2088 | 0 | -4.611
102045 | 710.2659 | 56.4901 | 712.5088 | 0 | -4.613
102055 | 849.0135 | 165.9496 | 865.0798 | 1.978 | -5.93
102065 | 961.5333 | 273.0057 | 999.539 | 2.305 | -5.93
102075 | 1042.1829 | 263.8603 | 1075.0662 | 0.988 | -5.93
102085 | 990.899 | 363.7422 | 1055.5516 | 2.966 | -3.953
102095 | 876.1975 | 413.9829 | 969.0737 | 2.306 | -2.637
102105 | 979.6301 | 324.3285 | 1031.9225 | 0.329 | -5.6
102115 | 1275.7615 | 332.4374 | 1318.3634 | 1.647 | -8.896
102125 | 1609.4886 | 396.633 | 1657.6403 | 2.306 | -10.871
102135 | 1746.5761 | 366.0924 | 1784.5313 | 0.989 | -9.225
102145 | 1830.1357 | 354.7942 | 1864.2091 | 1.318 | -9.224
102155 | 1944.8792 | 414.0507 | 1988.465 | 2.306 | -9.885
102165 | 2062.0283 | 404.5598 | 2101.3399 | 1.318 | -10.212
102175 | 1810.2734 | 427.8143 | 1860.1384 | 1.977 | -4.283
102185 | 1535.6767 | 491.8536 | 1612.5206 | 2.635 | -2.965
102195 | 1260.8967 | 347.5902 | 1307.9295 | -0.658 | -0.988
102205 | 1096.4594 | 226.8414 | 1119.6787 | -0.66 | -1.318
102215 | 940.913 | 120.9458 | 948.6544 | -1.317 | -0.329
102225 | 884.8969 | 46.2029 | 886.1022 | -1.318 | -1.318
102235 | 1045.8792 | 53.9651 | 1047.2705 | -0.33 | -4.613
102245 | 1149.9148 | -13.7926 | 1149.9975 | -1.647 | -4.283
102255 | 1297.2752 | -18.3829 | 1297.4054 | -0.658 | -5.93
102265 | 1387.6446 | -13.7989 | 1387.7132 | -0.66 | -5.601
102275 | 1153.3567 | 1.8185 | 1153.3581 | -0.329 | -0.658
102285 | 984.2014 | -8.1815 | 984.2354 | -0.659 | -0.989
102295 | 817.1303 | -155.6678 | 831.826 | -2.965 | 0.329
102305 | 696.0459 | -176.307 | 718.0278 | -1.318 | 0.33
102315 | 443.428 | -192.0092 | 483.2142 | -1.648 | 3.294
102325 | 55.4534 | -79.2667 | 96.7383 | 0.66 | 6.59
102335 | -167.7488 | 124.7223 | 209.0343 | 2.635 | 5.601
102345 | -193.3043 | 456.7519 | 495.9726 | 5.93 | 3.624
102355 | -136.4509 | 464.2948 | 483.9303 | 1.977 | 2.306
102365 | 3.3091 | 259.0138 | 259.035 | -0.988 | 0.329
102375 | 72.7065 | 311.5871 | 319.9574 | 2.306 | 0.658
102385 | -55.098 | 445.5573 | 448.9511 | 3.294 | 3.295
102395 | -358.8521 | 419.6905 | 552.191 | 1.319 | 6.59
102405 | -736.5923 | 194.2003 | 761.7624 | -1.977 | 9.224
102415 | -1042.9199 | 87.1476 | 1046.5546 | -0.989 | 9.884
102425 | -1255.0592 | 17.7972 | 1255.1854 | -1.318 | 9.883
102435 | -1372.7247 | -53.5013 | 1373.7669 | -1.647 | 9.225
102445 | -1331.9929 | -124.8594 | 1337.8322 | -1.977 | 6.918
102455 | -1118.8922 | -158.2103 | 1130.0222 | -1.646 | 3.624
102465 | -826.1061 | -142.849 | 838.3658 | -0.989 | 0.988
102475 | -427.2627 | -56.5765 | 430.9922 | 0.329 | -2.635
102485 | 76.8387 | 42.5727 | 87.8443 | 0.989 | -6.589
102495 | 714.9097 | 144.2218 | 729.3119 | 1.647 | -11.531
102505 | 1398.1513 | 251.5588 | 1420.6016 | 2.306 | -15.484
102515 | 1551.8684 | 288.0208 | 1578.3699 | 1.648 | -9.883
102525 | 1197.4726 | 153.6868 | 1207.2946 | -0.989 | -2.637
102535 | 625.7979 | 242.2606 | 671.0538 | 2.306 | 2.966
102545 | -73.3816 | 395.3635 | 402.1158 | 3.294 | 8.565
102555 | -546.6145 | 419.1851 | 688.8422 | 1.977 | 8.566
102565 | -725.7648 | 385.1756 | 821.6415 | 1.318 | 6.59
102575 | -493.5367 | 404.2895 | 637.9878 | 1.977 | 0.658
102585 | -259.9449 | 428.4961 | 501.1789 | 1.976 | -0.329
102595 | -190.1465 | 445.8983 | 484.7483 | 1.977 | 0.659
102605 | -241.9443 | 498.7316 | 554.3196 | 2.636 | 1.976
102615 | -306.5237 | 599.3889 | 673.219 | 3.623 | 2.306
102625 | -311.1919 | 617.2507 | 691.2589 | 2.637 | 1.648
102635 | -348.9987 | 564.436 | 663.6174 | 1.647 | 2.305
102645 | -384.7276 | 471.8182 | 608.7921 | 0.658 | 2.307
102655 | -371.6076 | 410.5299 | 553.7391 | 0.659 | 1.648
102665 | -284.52 | 433.5179 | 518.5455 | 1.647 | 0.329
102675 | -260.924 | 399.7628 | 477.38 | 0.66 | 0.988
102685 | -353.5479 | 347.36 | 495.636 | 0.329 | 2.636
102695 | -369.4114 | 255.5069 | 449.1643 | -0.658 | 1.647
102705 | -368.2164 | 226.3423 | 432.2201 | 0 | 1.647
102715 | -372.5022 | 233.1118 | 439.4303 | 0.329 | 1.647
102725 | -435.7925 | 216.7109 | 486.7019 | 0 | 2.636
102735 | -545.2793 | 142.025 | 563.4719 | -0.989 | 3.624
102745 | -605.4888 | 64.6939 | 608.9351 | -1.318 | 3.294
102755 | -527.7385 | 11.9885 | 527.8746 | -1.317 | 1.318
102765 | -197.6146 | 71.2221 | 210.0574 | 0.329 | -3.294
102775 | 430.0211 | 273.0475 | 509.385 | 2.966 | -9.884
102785 | 1053.005 | 417.9464 | 1132.916 | 2.964 | -12.848
102795 | 1568.9438 | 523.0164 | 1653.8231 | 3.295 | -14.496
102805 | 1832.8515 | 500.4115 | 1899.9358 | 1.647 | -12.848
102815 | 1706.7309 | 456.7643 | 1766.7948 | 1.317 | -7.578
102825 | 1386.3153 | 416.2224 | 1447.4499 | 0.989 | -3.624
102835 | 746.6012 | 334.3035 | 818.0295 | 0 | 3.954
102845 | 164.4639 | 237.4143 | 288.8146 | -0.658 | 6.259
102855 | -146.4515 | 191.2943 | 240.9181 | -0.331 | 5.271
102865 | -472.8719 | 184.0798 | 507.4378 | 0 | 7.578
102875 | -701.5657 | 178.8285 | 723.9987 | 0 | 7.248
102885 | -935.7656 | 171.7307 | 951.393 | 0 | 8.565
102895 | -1061.8472 | 164.7325 | 1074.5494 | 0 | 7.577
102905 | -999.0663 | 139.0008 | 1008.6896 | -0.329 | 4.942
102915 | -901.9263 | 213.7949 | 926.9192 | 1.318 | 3.954
102925 | -894.7572 | 352.2238 | 961.5883 | 2.635 | 4.612
102935 | -893.6265 | 409.2538 | 982.882 | 1.977 | 4.283
102945 | -802.9589 | 437.9264 | 914.616 | 1.978 | 2.635
102955 | -643.9448 | 461.0005 | 791.951 | 1.976 | 0.989
102965 | -442.4609 | 441.0986 | 624.7716 | 1.317 | -0.658
102975 | -383.3142 | 445.2857 | 587.545 | 1.648 | 0.658
102985 | -361.0967 | 455.4124 | 581.1982 | 1.647 | 0.659
102995 | -475.5359 | 405.7518 | 625.1151 | 0.659 | 2.965
103005 | -701.1957 | 232.546 | 738.751 | -1.647 | 5.272
103015 | -763.872 | 8.5678 | 763.9201 | -3.294 | 3.624
103025 | -767.4602 | -145.2475 | 781.0838 | -3.295 | 3.293
103035 | -815.6018 | -225.6809 | 846.2494 | -2.966 | 3.955
103045 | -821.0509 | -378.6536 | 904.1588 | -4.611 | 3.293
103055 | -842.1352 | -348.2669 | 911.3076 | -1.977 | 3.624
103065 | -923.3703 | -311.6355 | 974.5406 | -1.977 | 4.613
103075 | -969.3648 | -342.901 | 1028.2262 | -2.636 | 4.283
103085 | -979.6712 | -299.8385 | 1024.5286 | -1.317 | 3.953
103095 | -913.4169 | -188.2747 | 932.6187 | 0 | 2.636
103105 | -846.8161 | -113.4441 | 854.3811 | 0 | 2.306
103115 | -847.5512 | -52.6794 | 849.1868 | 0.329 | 2.965
103125 | -876.6973 | -30.7812 | 877.2375 | 0 | 3.294
103135 | -802.3748 | -0.59127 | 802.375 | 0.329 | 1.648
103145 | -644.9473 | 42.9578 | 646.3764 | 0.659 | 0
103155 | -477.0899 | 93.6285 | 486.1903 | 0.989 | -0.989
103165 | -267.8395 | 110.5804 | 289.7689 | 0.658 | -2.635
103175 | -251.8403 | 120.0126 | 278.9741 | 0.66 | -0.329
103185 | -374.1382 | 129.3133 | 395.8552 | 0.659 | 1.647
103195 | -475.3886 | 176.0288 | 506.9324 | 1.318 | 1.977
103205 | -493.8457 | 175.3973 | 524.0685 | 0.658 | 1.318
103215 | -362.0267 | 208.1945 | 417.6221 | 1.318 | -0.989
103225 | -277.3963 | 200.603 | 342.3306 | 0.659 | -0.659
103235 | -288.0216 | 171.3647 | 335.1452 | 0.329 | 0.33
103245 | -356.9449 | 153.4354 | 388.5255 | 0.329 | 1.318
103255 | -441.6952 | 86.7369 | 450.131 | -0.658 | 1.976
103265 | -477.53 | 55.1008 | 480.6985 | -0.329 | 1.647
103275 | -476.1445 | 39.8633 | 477.8103 | -0.33 | 1.318
103285 | -435.5213 | 47.3773 | 438.0906 | 0 | 0.659
103295 | -386.3039 | 34.3968 | 387.8322 | -0.329 | 0.33
103305 | -353.7168 | 20.9762 | 354.3382 | -0.33 | 0.329
103315 | -294.4793 | 31.327 | 296.1409 | 0 | -0.329
103325 | -248.9186 | 39.8207 | 252.0836 | 0 | -0.33
103335 | -180.5186 | 24.2132 | 182.1352 | -0.33 | -0.988
103345 | -69.9973 | 10.6514 | 70.803 | -0.329 | -1.977
103355 | 69.6733 | 40.5697 | 80.6243 | 0.329 | -2.966
103365 | 170.6416 | 84.1434 | 190.2594 | 0.66 | -2.964
103375 | 201.5312 | 74.3478 | 214.8078 | 0 | -2.306
103385 | 147.1521 | 80.7675 | 167.8605 | 0.329 | -0.989
103395 | 110.8497 | 70.8648 | 131.5655 | 0 | -0.989
103405 | 136.296 | 61.2996 | 149.4465 | 0 | -1.646
103415 | 278.9692 | 94.6734 | 294.5961 | 0.659 | -3.624
103425 | 390.6196 | 102.7592 | 403.9098 | 0.329 | -3.624
103435 | 462.7035 | 103.598 | 474.1593 | 0.329 | -3.624
103445 | 477.9414 | 105.6442 | 489.478 | 0.331 | -2.966
103455 | 490.3803 | 107.555 | 502.0368 | 0.329 | -2.964
103465 | 546.8452 | 109.3212 | 557.6655 | 0.329 | -3.624
103475 | 577.2918 | 72.5768 | 581.8361 | -0.329 | -3.295
103485 | 541.6875 | 5.092 | 541.7114 | -0.989 | -2.306
103495 | 517.9697 | -42.3816 | 519.7007 | -0.988 | -2.307
103505 | 549.8071 | -72.28 | 554.5379 | -0.989 | -2.964
103515 | 523.4472 | -55.0918 | 526.3383 | -0.329 | -1.977
103525 | 404.3115 | -60.0448 | 408.7459 | -0.658 | -0.329
103535 | 281.1804 | -51.0173 | 285.7712 | -0.33 | 0.329
103545 | 202.6424 | -43.3527 | 207.2279 | -0.33 | 0.329
103555 | 95.7184 | -40.591 | 103.9694 | -0.329 | 1.319
103565 | -22.4583 | -97.595 | 100.1457 | -1.318 | 1.976
103575 | -124.7499 | -66.92 | 141.5656 | 0 | 2.306
103585 | -196.9218 | -53.5808 | 204.0811 | -0.33 | 2.306
103595 | -191.352 | -52.5334 | 198.4322 | -0.329 | 1.318
103605 | -166.9696 | -71.1955 | 181.5149 | -0.658 | 0.988
103615 | -157.5877 | -105.9023 | 189.8662 | -0.989 | 0.989
103625 | -138.3667 | -111.7339 | 177.8477 | -0.659 | 0.658
103635 | -127.1087 | -132.1322 | 183.3454 | -0.989 | 0.66
103645 | -238.8871 | -111.9733 | 263.8277 | -0.329 | 2.635
103655 | -388.1762 | -170.863 | 424.1166 | -1.647 | 3.624
103665 | -433.2207 | -165.7548 | 463.8479 | -0.659 | 2.635
103675 | -379.2958 | -113.6243 | 395.9492 | 0 | 1.318
103685 | -361.4721 | -97.7642 | 374.4595 | -0.329 | 1.648
103695 | -496.6496 | -74.2074 | 502.1629 | 0 | 3.953
103705 | -415.2101 | -74.817 | 421.8969 | -0.329 | 0.659
103715 | 71.0969 | -1.9319 | 71.1231 | 0.987 | -6.26
103725 | 508.9888 | 38.5714 | 510.4482 | 0.659 | -7.577
103735 | 651.468 | -17.4911 | 651.7027 | -0.659 | -5.271
103745 | 537.7123 | -120.1853 | 550.98 | -1.647 | -1.977
103755 | 437.8269 | -209.311 | 485.287 | -1.977 | -1.647
103765 | 354.3965 | -190.4113 | 402.31 | -0.658 | -0.988
103775 | 151.0525 | -129.8292 | 199.1795 | 0 | 1.647
103785 | -73.2472 | -33.7206 | 80.6364 | 0.988 | 2.965
103795 | -355.7522 | 129.4671 | 378.5781 | 2.636 | 5.271
103805 | -576.8047 | 246.7008 | 627.3476 | 2.635 | 5.601
103815 | -454.9518 | 244.0593 | 516.281 | 1.318 | 0.989
103825 | -365.861 | 216.8808 | 425.3135 | 0.988 | 1.317
103835 | -526.4285 | 167.3914 | 552.401 | 0.33 | 4.613
103845 | -857.367 | 0.81392 | 857.3673 | -1.976 | 7.906
103855 | -1192.9858 | -237.5166 | 1216.4002 | -3.955 | 9.554
103865 | -1444.0228 | -382.8932 | 1493.9241 | -3.624 | 9.883
103875 | -1446.8766 | -491.4996 | 1528.0784 | -3.953 | 6.919
103885 | -1402.9879 | -553.2558 | 1508.1336 | -3.624 | 6.259
103895 | -1319.3439 | -559.8078 | 1433.1968 | -2.964 | 4.943
103905 | -1175.9249 | -529.8344 | 1289.7766 | -2.306 | 3.294
103915 | -911.8613 | -495.6318 | 1037.8545 | -1.977 | 0.33
103925 | -689.8049 | -440.7558 | 818.5942 | -1.318 | -0.33
103935 | -455.7623 | -386.3276 | 597.4682 | -0.989 | -1.976
103945 | -232.6674 | -295.7464 | 376.2978 | 0 | -2.966
103955 | 56.1263 | -192.9447 | 200.9423 | 0.66 | -5.271
103965 | 326.819 | -46.9231 | 330.1703 | 1.976 | -6.259
103975 | 574.437 | 58.6111 | 577.4194 | 1.977 | -7.248
103985 | 717.7341 | 126.9938 | 728.8825 | 1.977 | -6.589
103995 | 705.3296 | 99.6841 | 712.3389 | 0.658 | -4.613
104005 | 720.6455 | 77.1965 | 724.7684 | 0.66 | -4.941
104015 | 910.4554 | 52.6386 | 911.9758 | 0.329 | -7.578
104025 | 1051.083 | 38.3141 | 1051.7811 | 0.329 | -7.247
104035 | 1146.8004 | 13.6888 | 1146.8821 | 0 | -7.248
104045 | 1186.8019 | -41.3383 | 1187.5216 | -0.658 | -6.59
104055 | 1146.5079 | -80.439 | 1149.3263 | -0.66 | -5.271
104065 | 1088.0223 | -199.4934 | 1106.1601 | -2.306 | -4.612
104075 | 907.9975 | -252.6437 | 942.4905 | -1.647 | -1.977
104085 | 743.1716 | -298.15 | 800.7481 | -1.977 | -1.318
104095 | 491.3604 | -316.0586 | 584.2329 | -1.647 | 1.318
104105 | 214.7551 | -270.2394 | 345.1798 | -0.659 | 2.965
104115 | -87.915 | -217.5027 | 234.5986 | -0.329 | 4.942
104125 | -417.3364 | -224.658 | 473.963 | -0.989 | 6.919
104135 | -633.2597 | -295.0556 | 698.6241 | -1.977 | 6.588
104145 | -779.6694 | -367.2316 | 861.8256 | -2.306 | 6.59
104155 | -835.2439 | -376.8972 | 916.3427 | -1.647 | 5.6
104165 | -804.5817 | -321.4392 | 866.415 | -0.658 | 4.283
104175 | -812.9176 | -262.9587 | 854.39 | -0.331 | 4.613
104185 | -762.8263 | -284.981 | 814.3207 | -1.317 | 3.293
104195 | -730.843 | -290.4766 | 786.4529 | -0.989 | 3.295
104205 | -531.531 | -250.4171 | 587.5661 | -0.329 | 0
104215 | -305.4531 | -181.753 | 355.4374 | 0.329 | -1.318
104225 | -122.9022 | -95.299 | 155.5213 | 0.989 | -1.977
104235 | 35.2745 | -54.0555 | 64.5468 | 0.659 | -2.635
104245 | 87.7087 | -68.3441 | 111.1923 | 0 | -1.647
104255 | 98.7038 | -40.9483 | 106.8606 | 0.658 | -1.318
104265 | 170.6165 | -31.8897 | 173.5711 | 0.331 | -2.306
104275 | 233.3194 | -8.9257 | 233.4901 | 0.658 | -2.306
104285 | 315.8898 | 50.4246 | 319.889 | 1.318 | -2.966
104295 | 361.8486 | 76.7855 | 369.906 | 0.988 | -2.635
104305 | 470.6202 | 72.8112 | 476.2193 | 0.659 | -3.953
104315 | 675.4884 | 52.3092 | 677.5107 | 0.33 | -5.93
104325 | 771.4709 | 40.1966 | 772.5174 | 0.329 | -4.942
104335 | 579.2825 | 54.9422 | 581.8822 | 0.659 | -0.659
104345 | 277.993 | -84.6763 | 290.6031 | -1.977 | 1.977
104355 | 100.209 | -197.0788 | 221.0925 | -1.977 | 1.647
104365 | 171.3473 | -204.8966 | 267.1002 | -0.987 | -1.318
104375 | 316.4526 | -241.9555 | 398.3525 | -1.648 | -2.636
104385 | 390.843 | -123.8388 | 409.9931 | 0.988 | -2.306
104395 | 469.988 | -7.0679 | 470.0412 | 1.318 | -2.964
104405 | 395.4617 | 62.5645 | 400.3802 | 1.318 | -0.66
104415 | 233.3843 | 30.388 | 235.3543 | 0 | 0.989
104425 | 181.597 | -56.6394 | 190.2249 | -0.989 | 0
104435 | 142.8474 | -57.3341 | 153.9239 | 0 | 0.329
104445 | 149.202 | -45.2267 | 155.9061 | 0 | -0.329
104455 | 272.6133 | -39.9528 | 275.5254 | 0 | -2.306
104465 | 404.0413 | 20.9725 | 404.5853 | 0.989 | -2.966
104475 | 392.7707 | 88.2671 | 402.5666 | 1.317 | -1.318
104485 | 352.2739 | 94.5641 | 364.7455 | 0.66 | -0.987
104495 | 292.6858 | 74.7507 | 302.0805 | 0.329 | -0.33
104505 | 309.7453 | 82.6728 | 320.5884 | 0.659 | -1.318
104515 | 332.0911 | 36.0698 | 334.0443 | -0.33 | -1.318
104525 | 344.3251 | -1.7338 | 344.3294 | -0.329 | -1.318
104535 | 410.4121 | -3.396 | 410.4261 | 0 | -2.306
104545 | 424.2958 | 36.975 | 425.9038 | 0.659 | -1.647
104555 | 426.7845 | 48.2415 | 429.5023 | 0.329 | -1.648
104565 | 566.865 | 89.4606 | 573.8808 | 0.989 | -3.953
104575 | 929.5537 | 180.8671 | 946.9863 | 1.976 | -8.236
104585 | 1025.2693 | 248.0457 | 1054.8478 | 1.977 | -5.271
104595 | 923.2619 | 156.6303 | 936.4537 | -0.329 | -2.966
104605 | 913.9348 | 42.6725 | 914.9304 | -0.989 | -3.953
104615 | 1163.8359 | 10.9668 | 1163.8876 | -0.329 | -7.907
104625 | 1364.4972 | 152.448 | 1372.9868 | 2.306 | -7.906
104635 | 1453.5202 | 148.4987 | 1461.0862 | 0.33 | -7.248
104645 | 1555.1237 | 102.505 | 1558.4983 | 0 | -7.907
104655 | 1449.6035 | 210.9062 | 1464.8657 | 2.306 | -4.613
104665 | 1345.58 | 283.9786 | 1375.2197 | 1.977 | -4.282
104675 | 1219.0457 | 189.1892 | 1233.6389 | -0.33 | -2.966
104685 | 1096.6846 | 150.1114 | 1106.9104 | 0.33 | -2.306
104695 | 1077.592 | 120.1081 | 1084.265 | 0 | -3.295
104705 | 942.6202 | 174.1901 | 958.5797 | 1.318 | -0.987
104715 | 698.5814 | 105.837 | 706.5532 | -0.66 | 1.318
104725 | 564.3905 | 2.9067 | 564.398 | -1.318 | 0.658
104735 | 427.8317 | -140.9177 | 450.4417 | -2.635 | 1.648
104745 | 514.5979 | -206.3083 | 554.4133 | -1.977 | -1.648
104755 | 535.2031 | -243.0698 | 587.814 | -1.977 | -0.658
104765 | 639.1016 | -235.3316 | 681.052 | -1.318 | -2.637
104775 | 547.3015 | -230.2807 | 593.7745 | -1.317 | 0.33
104785 | 435.2536 | -195.3308 | 477.0743 | -0.659 | 0.659
104795 | 403.9648 | -171.1382 | 438.7207 | -0.659 | 0
104805 | 425.416 | -121.7428 | 442.493 | 0 | -0.659
104815 | 515.2707 | 10.0093 | 515.3679 | 1.648 | -1.977
104825 | 713.0365 | 29.8021 | 713.6591 | 0.329 | -4.283
104835 | 758.5026 | 104.5548 | 765.6748 | 1.647 | -2.635
104845 | 806.5917 | 54.5932 | 808.4371 | -0.329 | -3.295
104855 | 677.6366 | -14.5008 | 677.7918 | -0.66 | -0.329
104865 | 474.8445 | 22.6229 | 475.3831 | 0.66 | 1.317
104875 | 262.528 | 21.6058 | 263.4156 | 0 | 2.637
104885 | 136.429 | -26.471 | 138.9733 | -0.66 | 2.305
104895 | 113.2174 | -41.8585 | 120.7076 | -0.329 | 1.319
104905 | 78.353 | -85.4875 | 115.9625 | -0.988 | 1.647
104915 | -54.5653 | -178.4746 | 186.6294 | -1.977 | 3.294
104925 | -258.0296 | -208.1315 | 331.5087 | -1.318 | 4.942
104935 | -388.3998 | -278.7782 | 478.0918 | -2.305 | 4.613
104945 | -475.5375 | -261.0671 | 542.4868 | -0.989 | 4.612
104955 | -468.0192 | -277.9605 | 544.3381 | -1.648 | 3.294
104965 | -330.2595 | -205.5437 | 388.9981 | 0 | 0.988
104975 | -179.0658 | -146.1032 | 231.1076 | 0 | 0
104985 | -87.8674 | -17.9391 | 89.68 | 1.648 | 0
104995 | -94.1213 | 39.991 | 102.2648 | 0.989 | 0.989
105005 | -165.9392 | -8.1354 | 166.1385 | -0.331 | 1.977
105015 | -161.0935 | 11.8134 | 161.5261 | 0.66 | 0.987
105025 | -52.3158 | 20.3439 | 56.1322 | 0.329 | -0.658
105035 | -49.5709 | -15.9303 | 52.0677 | -0.329 | 0.658
105045 | -103.626 | -61.9147 | 120.7136 | -0.66 | 1.319
105055 | -121.8717 | -110.6513 | 164.6099 | -0.988 | 0.988
105065 | -148.772 | -124.6647 | 194.099 | -0.659 | 1.317
105075 | -37.0086 | -130.8324 | 135.966 | -0.659 | -0.987
105085 | 130.831 | -40.9142 | 137.0792 | 0.989 | -2.306
105095 | 243.6158 | 10.7747 | 243.8539 | 0.659 | -2.307
105105 | 256.7385 | 55.9118 | 262.7562 | 0.989 | -1.317
105115 | -84.9452 | -44.7958 | 96.0331 | -1.319 | 4.612
105125 | -656.8127 | -224.5246 | 694.1284 | -2.965 | 9.883
105135 | -1055.2358 | -366.7841 | 1117.163 | -3.295 | 9.884
105145 | -1018.2618 | -458.5949 | 1116.766 | -3.294 | 4.941
105155 | -815.0231 | -444.8966 | 928.5449 | -1.976 | 2.307
105165 | -558.7061 | -316.0661 | 641.9114 | 0 | 0
105175 | -375.3139 | -225.7166 | 437.9594 | 0 | -0.33
105185 | -343.8571 | -157.5672 | 378.2395 | 0.329 | 0.989
105195 | -356.0736 | -150.3473 | 386.5135 | -0.329 | 1.318
105205 | -515.5385 | -285.9363 | 589.5249 | -2.636 | 3.953
105215 | -716.0554 | -121.3327 | 726.2623 | 1.976 | 5.271
105225 | -735.8991 | -122.6753 | 746.0541 | -0.658 | 3.294
105235 | -732.9021 | -177.6938 | 754.1356 | -0.989 | 3.295
105245 | -646.9314 | -208.3464 | 679.6532 | -0.988 | 1.647
105255 | -468.5187 | -206.8602 | 512.1532 | -0.658 | -0.329
105265 | -325.7625 | -164.9721 | 365.1534 | 0 | -0.659
105275 | -333.4161 | -172.3309 | 375.3188 | -0.66 | 0.988
105285 | -332.3673 | -184.7593 | 380.2684 | -0.659 | 0.659
105295 | -244.4139 | -171.6789 | 298.6834 | -0.329 | -0.659
105305 | -39.8664 | -83.461 | 92.4936 | 0.988 | -2.965
105315 | 149.7396 | 22.4416 | 151.4119 | 1.647 | -3.624
105325 | 218.8978 | 74.76 | 231.3122 | 1.318 | -2.635
105335 | 145.8618 | 68.1039 | 160.9777 | 0.659 | -0.659
105345 | 93.7524 | 5.2836 | 93.9012 | -0.329 | -0.659
105355 | 73.5853 | -76.6415 | 106.2484 | -0.989 | -0.659
105365 | 66.2468 | -53.0748 | 84.8856 | 0.33 | -0.659
105375 | -69.357 | -100.8717 | 122.4152 | -0.989 | 1.647
105385 | -385.4919 | -281.2042 | 477.1581 | -3.294 | 5.271
105395 | -556.3124 | -395.5282 | 682.5877 | -2.965 | 4.284
105405 | -420.9675 | -366.6146 | 558.2292 | -1.318 | 0.329
105415 | -194.0871 | -281.6192 | 342.0222 | -0.329 | -1.647
105425 | 47.8326 | -131.8018 | 140.2129 | 1.318 | -3.295
105435 | 171.8485 | -84.5719 | 191.5314 | 0.329 | -2.635
105445 | 91.2295 | -105.7123 | 139.635 | -0.329 | 0
105455 | 82.3513 | -159.2008 | 179.239 | -0.989 | -0.989
105465 | 79.2921 | -253.22 | 265.3443 | -1.977 | -0.659
105475 | 210.9094 | -89.2436 | 229.0135 | 1.977 | -2.965
105485 | 473.5295 | 91.0269 | 482.1992 | 2.635 | -5.601
105495 | 529.35 | 279.5275 | 598.6209 | 3.955 | -3.295
105505 | 430.1113 | 317.37 | 534.5273 | 2.305 | -1.317
105515 | 114.5882 | 157.7382 | 194.9662 | -0.659 | 2.965
105525 | -151.1183 | -16.341 | 151.9992 | -1.646 | 3.624
105535 | -275.8448 | -181.4079 | 330.1503 | -2.637 | 2.965
105545 | -390.721 | -157.7592 | 421.3678 | -0.329 | 3.624
105555 | -499.021 | -180.0946 | 530.5243 | -1.318 | 3.954
105565 | -540.2977 | -155.1511 | 562.133 | -0.329 | 3.294
105575 | -607.9974 | -131.2834 | 622.0098 | -0.33 | 3.954
105585 | -764.296 | -120.5554 | 773.7454 | -0.329 | 5.6
105595 | -963.5212 | -230.4402 | 990.6946 | -2.307 | 6.919
105605 | -1089.4824 | -338.3505 | 1140.8125 | -2.635 | 6.589
105615 | -1003.0531 | -330.3444 | 1056.0506 | -1.318 | 3.624
105625 | -858.8023 | -258.452 | 896.8494 | -0.329 | 2.306
105635 | -716.5094 | -230.3123 | 752.6151 | -0.659 | 1.318
105645 | -685.4985 | -239.8251 | 726.2399 | -0.989 | 2.306
105655 | -699.8067 | -268.4391 | 749.5258 | -1.317 | 2.636
105665 | -614.7693 | -270.4667 | 671.635 | -0.989 | 0.988
105675 | -488.2486 | -269.0577 | 557.4753 | -0.988 | 0
105685 | -345.5041 | -212.6936 | 405.7236 | 0 | -0.988
105695 | -131.1481 | -188.2823 | 229.456 | -0.33 | -2.966
105705 | 5.8568 | -140.0219 | 140.1443 | 0.33 | -2.635
105715 | 111.7657 | -102.0503 | 151.3467 | 0.33 | -2.965
105725 | 230.9442 | -116.6944 | 258.7524 | -0.33 | -3.624
105735 | 322.7036 | -53.399 | 327.0918 | 0.988 | -3.624
105745 | 371.4615 | -74.5281 | 378.8642 | -0.329 | -3.295
105755 | 372.3909 | -120.4267 | 391.379 | -0.659 | -2.635
105765 | 359.5678 | -70.8533 | 366.4822 | 0.659 | -2.306
105775 | 359.7868 | -83.0222 | 369.2414 | -0.329 | -2.307
105785 | 311.0999 | -82.9454 | 321.9676 | 0 | -1.317
105795 | 297.0843 | -38.2351 | 299.5347 | 0.658 | -1.648
105805 | 298.7614 | -41.9549 | 301.6929 | 0 | -1.647
105815 | 341.584 | 26.1528 | 342.5837 | 1.318 | -2.306
105825 | 320.753 | 84.5593 | 331.7118 | 1.317 | -1.318
105835 | 281.3779 | 63.2533 | 288.3999 | 0.331 | -0.988
105845 | 182.3589 | 62.7231 | 192.8443 | 0.658 | 0.329
105855 | 72.2318 | 70.8061 | 101.1481 | 0.659 | 0.988
105865 | -76.9495 | 96.831 | 123.6829 | 0.989 | 2.306
105875 | -164.7988 | 137.5908 | 214.6855 | 1.318 | 1.978
105885 | -141.603 | 129.4249 | 191.839 | 0.658 | 0.658
105895 | -44.3414 | 120.0308 | 127.9592 | 0.659 | -0.658
105905 | 79.0924 | 156.6224 | 175.4599 | 1.318 | -1.648
105915 | 180.0425 | 168.8906 | 246.859 | 0.989 | -1.976
105925 | 207.005 | 135.7156 | 247.5273 | 0.329 | -1.318
105935 | 47.3145 | 92.4029 | 103.8121 | 0 | 1.647
105945 | -95.5273 | 65.183 | 115.6473 | 0 | 1.977
105955 | -277.1167 | 30.1891 | 278.7563 | -0.329 | 3.624
105965 | -351.5079 | -52.923 | 355.4696 | -1.318 | 2.635
105975 | -314.8095 | -76.5172 | 323.9752 | -0.66 | 1.318
105985 | -212.1375 | -65.6886 | 222.075 | -0.329 | 0
105995 | -67.4153 | -21.4425 | 70.7432 | 0.329 | -1.318
106005 | 10.8125 | 67.4157 | 68.2773 | 1.318 | -0.988
106015 | 35.1278 | 53.5563 | 64.0487 | 0 | -0.659
106025 | -45.4366 | 11.7453 | 46.9301 | -0.329 | 0.988
106035 | -204.2443 | -52.0028 | 210.7606 | -0.989 | 2.636
106045 | -430.418 | -97.23 | 441.2633 | -0.988 | 4.613
106055 | -590.1766 | -163.7877 | 612.4825 | -1.647 | 4.611
106065 | -693.1739 | -194.9935 | 720.0781 | -1.318 | 4.613
106075 | -690.9998 | -193.9835 | 717.7119 | -0.988 | 3.294
106085 | -611.3214 | -194.5622 | 641.5359 | -0.989 | 1.977
106095 | -484.5068 | -179.6288 | 516.7334 | -0.658 | 0.659
106105 | -421.149 | -169.7734 | 454.081 | -0.659 | 0.988
106115 | -390.6515 | -147.0888 | 417.4251 | -0.33 | 0.989
106125 | -333.0589 | -188.6457 | 382.7733 | -1.317 | 0.329
106135 | -347.9847 | -245.1393 | 425.6602 | -1.648 | 1.318
106145 | -271.3906 | -244.4395 | 365.2445 | -0.988 | -0.329
106155 | -146.8101 | -200.7724 | 248.7222 | -0.33 | -1.318
106165 | 15.8498 | -151.6322 | 152.4584 | 0 | -2.636
106175 | 170.5127 | -101.2198 | 198.2928 | 0.33 | -3.294
106185 | 220.0244 | -67.2264 | 230.0655 | 0.329 | -2.307
106195 | 287.4483 | -64.7041 | 294.6407 | 0 | -2.965
106205 | 270.8046 | -6.869 | 270.8917 | 0.989 | -1.647
106215 | 216.927 | 79.8287 | 231.1492 | 1.647 | -0.989
106225 | 148.7239 | 121.574 | 192.0912 | 1.318 | -0.329
106235 | 144.8546 | 127.4707 | 192.955 | 0.988 | -0.988
106245 | 114.8728 | 133.0591 | 175.7854 | 0.989 | -0.329
106255 | 167.189 | 102.8315 | 196.2816 | 0.329 | -1.647
106265 | 196.5225 | 138.5492 | 240.4516 | 1.318 | -1.319
106275 | 210.9411 | 97.5018 | 232.3849 | 0 | -1.318
106285 | 242.6084 | 97.5974 | 261.5035 | 0.659 | -1.647
106295 | 172.6651 | 89.239 | 194.3626 | 0.329 | 0
106305 | 76.8414 | 3.7742 | 76.934 | -0.988 | 0.659
106315 | -22.674 | -41.947 | 47.683 | -0.659 | 1.318
106325 | -205.6535 | -45.9708 | 210.7289 | -0.33 | 3.294
106335 | -360.12 | -105.3787 | 375.2214 | -1.318 | 3.624
106345 | -442.5232 | -58.8224 | 446.4155 | 0.329 | 3.295
106355 | -479.5478 | -52.2467 | 482.3855 | -0.329 | 2.966
106365 | -432.773 | -59.6327 | 436.8622 | -0.329 | 1.646
106375 | -361.9 | -44.5845 | 364.636 | 0 | 0.989
106385 | -224.5443 | -13.364 | 224.9416 | 0.329 | -0.659
106395 | -166.2935 | -49.2568 | 173.4352 | -0.658 | 0
106405 | -44.2954 | -62.7283 | 76.7914 | -0.33 | -1.647
106415 | 51.045 | -104.3827 | 116.1953 | -0.988 | -1.648
106425 | 72.2332 | -119.0183 | 139.2228 | -0.659 | -0.988
106435 | 7.1769 | -86.5283 | 86.8254 | 0 | 0.329
106445 | -136.1701 | -81.2772 | 158.5821 | -0.329 | 1.978
106455 | -312.9041 | -102.9441 | 329.4032 | -0.66 | 3.293
106465 | -414.3444 | -119.4409 | 431.2162 | -0.658 | 2.966
106475 | -341.7063 | -129.7786 | 365.5211 | -0.659 | 0.658
106485 | -165.7962 | -98.8816 | 193.0439 | 0 | -1.317
106495 | 49.8635 | -112.7437 | 123.2782 | -0.659 | -2.965
106505 | 234.6817 | -91.4639 | 251.8753 | 0 | -3.624
106515 | 415.5858 | -109.2584 | 429.708 | -0.659 | -4.612
106525 | 468.8386 | -51.5402 | 471.663 | 0.659 | -3.295
106535 | 383.169 | -59.1431 | 387.7066 | -0.33 | -1.318
106545 | 247.4334 | -37.3683 | 250.2392 | 0.33 | 0
106555 | 142.8673 | -53.0417 | 152.3959 | -0.33 | 0.329
106565 | -15.2853 | -88.9388 | 90.2427 | -0.658 | 1.977
106575 | -90.9486 | -55.1524 | 106.3646 | 0.329 | 1.318
106585 | -16.031 | -100.7306 | 101.9983 | -0.989 | -0.658
106595 | 82.9193 | -105.7783 | 134.4048 | -0.329 | -1.319
106605 | 201.7762 | -81.0098 | 217.431 | 0 | -2.305
106615 | 380.7455 | -25.9507 | 381.6288 | 0.659 | -3.954
106625 | 529.2213 | -5.2603 | 529.2474 | 0.33 | -4.283
106635 | 609.2436 | 42.3102 | 610.711 | 0.988 | -3.954
106645 | 645.3635 | 23.1034 | 645.7769 | 0 | -3.624
106655 | 617.8675 | 21.3835 | 618.2374 | 0.329 | -2.635
106665 | 601.2417 | 8.2136 | 601.2978 | 0 | -2.636
106675 | 523.6803 | 93.4675 | 531.9561 | 1.647 | -1.317
106685 | 448.9974 | 68.4235 | 454.181 | 0 | -0.989
106695 | 347.7484 | 92.7945 | 359.9163 | 0.989 | 0
106705 | 296.0183 | 46.2374 | 299.6077 | -0.329 | -0.329
106715 | 268.1997 | 23.2329 | 269.2041 | 0 | -0.33
106725 | 190.4414 | 15.7396 | 191.0908 | 0 | 0.659
106735 | 129.7887 | 10.5243 | 130.2147 | 0 | 0.659
106745 | 110.0601 | 7.0301 | 110.2844 | 0 | 0.33
106755 | 97.15 | 23.8123 | 100.0258 | 0.329 | 0.329
106765 | 122.8742 | 18.1584 | 124.2086 | 0 | -0.329
106775 | 161.3033 | -8.3575 | 161.5197 | -0.329 | -0.66
106785 | 127.0844 | 11.0721 | 127.5658 | 0.329 | 0.33
106795 | 74.9208 | -65.9368 | 99.8037 | -1.318 | 0.659
106805 | 78.4023 | -112.5689 | 137.1812 | -0.988 | 0
106815 | 66.4863 | -117.084 | 134.6443 | -0.659 | 0.329
106825 | 90.5906 | -138.8085 | 165.7542 | -0.988 | -0.329
106835 | 168.474 | -120.373 | 207.0583 | -0.33 | -1.318
106845 | 204.9776 | -103.9965 | 229.8502 | -0.33 | -0.988
106855 | 242.0364 | -39.0938 | 245.1733 | 0.66 | -1.318
106865 | 328.2231 | 10.0944 | 328.3783 | 0.658 | -2.306
106875 | 374.0825 | 0.75498 | 374.0832 | 0 | -1.977
106885 | 323.885 | 28.4101 | 325.1286 | 0.659 | -0.659
106895 | 284.2665 | 35.8909 | 286.5233 | 0.33 | -0.659
106905 | 322.799 | 75.8832 | 331.5983 | 0.988 | -1.647
106915 | 300.3357 | 71.1082 | 308.6388 | 0.329 | -0.659
106925 | 294.9992 | 62.2883 | 301.5035 | 0.33 | -0.988
106935 | 317.36 | 79.1573 | 327.083 | 0.659 | -1.319
106945 | 315.3946 | 36.6973 | 317.5223 | -0.329 | -0.987
106955 | 349.7593 | 39.3945 | 351.9709 | 0.329 | -1.648
106965 | 321.7817 | 50.1559 | 325.6671 | 0.329 | -0.658
106975 | 333.1856 | 75.009 | 341.5245 | 0.659 | -1.318
106985 | 273.101 | 55.7201 | 278.7273 | 0 | 0
106995 | 183.7719 | 75.8194 | 198.7981 | 0.659 | 0.658
107005 | 123.9219 | 96.9283 | 157.3268 | 0.659 | 0.66
107015 | 66.8149 | 51.9287 | 84.6216 | -0.329 | 0.988
107025 | 5.3477 | 15.1086 | 16.0271 | -0.33 | 1.318
107035 | -1.2294 | 52.26 | 52.2744 | 0.659 | 0.658
107045 | -22.1497 | 84.6434 | 87.4935 | 0.658 | 0.989
107055 | -121.1006 | 102.7688 | 158.8295 | 0.66 | 2.306
107065 | -237.7595 | 95.5449 | 256.239 | 0.329 | 2.965
107075 | -319.5455 | 31.4747 | 321.0919 | -0.658 | 2.965
107085 | -395.5155 | 21.8379 | 396.1179 | 0 | 3.295
107095 | -396.7499 | -33.5428 | 398.1653 | -0.989 | 2.306
107105 | -299.7331 | -60.8801 | 305.8534 | -0.659 | 0.659
107115 | -232.7298 | -74.39 | 244.3297 | -0.659 | 0.659
107125 | -141.5977 | -47.2519 | 149.2738 | 0 | -0.33
107135 | -38.8641 | -64.4812 | 75.2877 | -0.659 | -0.988
107145 | 10.5667 | -103.7654 | 104.3021 | -0.988 | -0.659
107155 | 77.3269 | -73.8331 | 106.9148 | 0 | -1.318
107165 | 148.4882 | -104.0844 | 181.3348 | -0.988 | -1.647
107175 | 83.355 | -97.7842 | 128.4905 | -0.33 | 0.329
107185 | -11.5571 | -67.5159 | 68.4979 | 0 | 0.989
107195 | -12.5734 | -28.72 | 31.3517 | 0.33 | 0
107205 | -40.0969 | -98.6635 | 106.5 | -1.318 | 0.658
107215 | -28.155 | -120.5552 | 123.7993 | -0.659 | 0
107225 | -13.8864 | -86.4767 | 87.5846 | 0 | 0
107235 | 12.1416 | -42.2655 | 43.9749 | 0.329 | -0.329
107245 | 50.6237 | -13.6737 | 52.4379 | 0.33 | -0.659
107255 | 116.0752 | 3.6891 | 116.1338 | 0.329 | -1.318
107265 | 183.1429 | -3.6322 | 183.179 | 0 | -1.647
107275 | 229.2687 | 9.116 | 229.4499 | 0.33 | -1.647
107285 | 203.3012 | 2.8094 | 203.3207 | 0 | -0.659
107295 | 200.7459 | -61.8133 | 210.0472 | -0.989 | -0.989
107305 | 150.1279 | -72.0799 | 166.535 | -0.329 | 0
107315 | 110.5461 | -12.7992 | 111.2846 | 0.659 | 0
107325 | -45.5731 | -83.768 | 95.3624 | -1.318 | 2.307
107335 | -127.4442 | -53.6492 | 138.276 | 0.33 | 1.647
107345 | -131.7505 | -111.2631 | 172.4461 | -1.318 | 0.988
107355 | -134.139 | -129.0309 | 186.1243 | -0.659 | 0.989
107365 | -84.0341 | -131.6111 | 156.1513 | -0.66 | 0
107375 | 68.62 | -116.9665 | 135.6093 | -0.329 | -1.977
107385 | 198.5752 | -87.0619 | 216.8222 | 0 | -2.306
107395 | 318.5417 | -66.9286 | 325.497 | 0 | -2.965
107405 | 345.9994 | -36.1621 | 347.884 | 0.329 | -1.977
107415 | 339.3402 | -51.7764 | 343.2675 | -0.329 | -1.647
107425 | 283.02 | -67.8446 | 291.0381 | -0.329 | -0.66
107435 | 205.7301 | -75.8942 | 219.2824 | -0.329 | 0
107445 | 137.0073 | -80.8733 | 159.0958 | -0.33 | 0.331
107455 | 16.4573 | -122.6436 | 123.7429 | -0.988 | 1.647
107465 | -91.2779 | -97.998 | 133.9226 | 0 | 1.977
107475 | -142.9344 | -72.5072 | 160.2733 | 0 | 1.646
107485 | -41.9608 | -59.3821 | 72.7114 | 0 | -0.658
107495 | 75.9237 | -51.2592 | 91.6074 | 0 | -1.318
107505 | 205.6146 | -45.747 | 210.6422 | 0 | -2.306
107515 | 199.0737 | -60.9843 | 208.2052 | -0.33 | -0.659
107525 | 122.3507 | -73.1303 | 142.5403 | -0.329 | 0.329
107535 | 33.0986 | -137.4823 | 141.4104 | -1.318 | 0.989
107545 | -83.2527 | -168.3729 | 187.8309 | -0.988 | 1.977
107555 | -88.4987 | -183.7452 | 203.9468 | -0.989 | 0.658
107565 | -22.717 | -196.1217 | 197.433 | -0.989 | -0.329
107575 | -16.8796 | -148.4389 | 149.3955 | 0 | 0.329
107585 | 72.1171 | -130.1891 | 148.829 | -0.329 | -1.318
107595 | 144.3163 | -67.4446 | 159.2984 | 0.66 | -1.317
107605 | 225.3557 | -56.4961 | 232.3295 | 0 | -1.978
107615 | 188.7246 | -57.1844 | 197.198 | 0 | -0.329
107625 | 75.1895 | -35.6529 | 83.2142 | 0.329 | 0.989
107635 | -59.8989 | -36.8927 | 70.3487 | 0 | 1.977
107645 | -131.7418 | -21.1669 | 133.4314 | 0.329 | 1.647
107655 | -193.5709 | -25.4729 | 195.2397 | 0 | 1.977
107665 | -240.8488 | -69.2853 | 250.6165 | -0.658 | 1.976
107675 | -275.2217 | -63.1153 | 282.366 | 0 | 1.977
107685 | -263.8792 | -70.6045 | 273.1616 | -0.331 | 1.318
107695 | -236.5406 | -22.2758 | 237.5872 | 0.66 | 0.988
107705 | -106.9109 | -39.5226 | 113.9824 | -0.329 | -0.988
107715 | -29.5519 | -80.7872 | 86.0226 | -0.66 | -0.659
107725 | 11.0417 | -49.5047 | 50.7211 | 0.329 | -0.659
107735 | 19.645 | -38.8946 | 43.5743 | 0 | -0.329
107745 | 43.8033 | -18.3134 | 47.4775 | 0.331 | -0.66
107755 | 84.4462 | 17.9268 | 86.328 | 0.658 | -0.988
107765 | 76.2741 | 24.8236 | 80.2119 | 0.33 | -0.329
107775 | -10.2336 | 7.3835 | 12.6191 | 0 | 0.988
107785 | -92.9103 | -4.5175 | 93.0201 | 0 | 1.318
107795 | -183.1715 | 9.0114 | 183.393 | 0.329 | 1.977
107805 | -247.1365 | 2.0692 | 247.1451 | 0 | 1.976
107815 | -308.6688 | -5.6315 | 308.7201 | 0 | 2.306
107825 | -374.3657 | -28.4554 | 375.4456 | -0.329 | 2.636
107835 | -384.9416 | -64.9171 | 390.3771 | -0.659 | 1.977
107845 | -390.284 | -32.8385 | 391.6631 | 0.329 | 1.977
107855 | -400.5049 | -3.1742 | 400.5175 | 0.33 | 1.976
107865 | -411.7701 | -25.6347 | 412.5672 | -0.33 | 1.977
107875 | -403.7787 | -7.3392 | 403.8454 | 0.33 | 1.647
107885 | -360.9387 | -6.9919 | 361.0064 | 0 | 0.988
107895 | -350.8767 | 27.3982 | 351.9447 | 0.659 | 1.318
107905 | -332.1398 | 18.02 | 332.6283 | 0 | 0.989
107915 | -260.2089 | -14.0193 | 260.5863 | -0.33 | 0
107925 | -187.8064 | -15.8323 | 188.4726 | 0 | -0.33
107935 | -141.0294 | -12.8498 | 141.6136 | 0 | -0.329
107945 | 23.9846 | 7.393 | 25.0981 | 0.33 | -2.636
107955 | 95.0514 | 61.5622 | 113.2461 | 0.988 | -1.647
107965 | 34.1238 | 101.6218 | 107.198 | 0.989 | 0
107975 | -88.4499 | 164.9788 | 187.1935 | 1.646 | 1.318
107985 | -54.2885 | 117.2835 | 129.2388 | 0 | -0.659
107995 | 202.2106 | 188.4719 | 276.425 | 1.978 | -4.283
108005 | 279.6318 | 219.7153 | 355.6244 | 1.317 | -2.306
108015 | 286.861 | 193.0492 | 345.7704 | 0.659 | -1.977
108025 | 299.8861 | 116.7986 | 321.8285 | -0.33 | -1.976
108035 | 239.4008 | 82.6827 | 253.2769 | 0 | -0.66
108045 | 98.6119 | 48.2317 | 109.7752 | -0.329 | 0.989
108055 | -75.5691 | -16.19 | 77.284 | -0.988 | 2.306
108065 | -250.9186 | -101.959 | 270.8428 | -1.647 | 3.295
108075 | -274.6517 | -66.8195 | 282.663 | 0 | 1.647
108085 | -220.299 | -69.325 | 230.9493 | -0.66 | 0.659
108095 | -110.228 | -64.5206 | 127.7228 | -0.329 | -0.659
108105 | -16.1704 | -20.7288 | 26.29 | 0.329 | -0.989
108115 | 60.8339 | 49.3874 | 78.3574 | 0.989 | -1.318
108125 | 74.3235 | 78.4577 | 108.0722 | 0.658 | -0.658
108135 | 59.5131 | 73.8946 | 94.88 | 0.331 | -0.33
108145 | 32.3767 | 108.6415 | 113.3632 | 0.988 | 0
108155 | -100.0624 | 81.5267 | 129.0701 | 0 | 1.977
108165 | -181.1604 | 35.9793 | 184.6986 | -0.33 | 1.647
108175 | -206.755 | 7.5494 | 206.8928 | -0.329 | 1.319
108185 | -281.195 | -9.4503 | 281.3537 | -0.329 | 2.305
108195 | -246.1503 | -40.2224 | 249.415 | -0.66 | 0.659
108205 | -210.5969 | -25.4079 | 212.124 | 0 | 0.66
108215 | -156.9556 | -10.4937 | 157.306 | 0 | 0
108225 | -42.2016 | -42.1401 | 59.6386 | -0.658 | -1.319
108235 | 2.139 | -11.4999 | 11.6971 | 0.329 | -0.659
108245 | 79.9397 | -1.2994 | 79.9503 | 0 | -1.646
108255 | 200.4904 | 18.5051 | 201.3426 | 0.329 | -2.637
108265 | 345.2463 | 54.0526 | 349.452 | 0.66 | -3.624
108275 | 449.1866 | 40.7832 | 451.0342 | 0 | -3.624
108285 | 539.362 | 64.6869 | 543.2272 | 0.658 | -3.953
108295 | 627.7206 | 88.4416 | 633.9204 | 0.659 | -4.283
108305 | 695.6264 | 45.3322 | 697.1019 | -0.329 | -4.282
108315 | 882.5215 | 29.1456 | 883.0026 | 0 | -6.59
108325 | 1301.6799 | -32.6871 | 1302.0903 | -0.988 | -11.201
108335 | 1463.2015 | -254.9353 | 1485.2443 | -3.955 | -8.565
108345 | 2412.3247 | -383.8167 | 2442.6678 | -3.293 | -23.392
108355 | 4159.4651 | -1552.3865 | 4439.7132 | -22.074 | -40.193
108365 | 4500.1422 | -1843.6797 | 4863.1712 | -11.201 | -24.38
108375 | 3607.4153 | -657.6602 | 3666.8736 | 10.212 | -7.577
108385 | 2798.3821 | 6.3543 | 2798.3893 | 6.261 | -4.283
108395 | 2230.2647 | 208.9197 | 2240.0286 | 4.282 | -2.306
108405 | 2997.2686 | 276.6252 | 3010.0067 | 3.295 | -21.415
108415 | 1075.7125 | 1061.8901 | 1511.5449 | 15.813 | 23.063
108425 | 1097.4284 | -303.6933 | 1138.6741 | -18.449 | -5.93
108435 | 1378.435 | -1207.7497 | 1832.6872 | -13.508 | -4.284
108445 | 1301.0484 | -73.3641 | 1303.1152 | 13.508 | -1.647
108455 | 1501.5559 | 390.7015 | 1551.5533 | 5.271 | -6.589
108465 | 3133.1407 | -233.9134 | 3141.8603 | -7.906 | -31.627
108475 | 3618.2292 | -535.1757 | 3657.5942 | -4.613 | -18.45
108485 | 4149.7009 | 340.356 | 4163.6354 | 12.519 | -25.038
108495 | 3444.5567 | 1350.6849 | 3699.9082 | 17.791 | -4.942
108505 | 3264.0877 | 1946.1266 | 3800.2207 | 16.802 | -12.19
108515 | 2873.2343 | 2133.4132 | 3578.6768 | 13.507 | -4.941
108525 | 1561.2981 | 2396.8266 | 2860.4947 | 15.814 | 12.189
108535 | 804.2297 | 2441.4259 | 2570.4758 | 12.519 | 8.566
108545 | 1191.5023 | 1953.324 | 2288.0455 | 3.624 | -5.271
108555 | 2371.939 | 1525.7372 | 2820.2781 | 2.306 | -19.767
108565 | 3041.2832 | 1497.365 | 3389.9123 | 5.93 | -17.132
108575 | 2250.7441 | 1141.7456 | 2523.7733 | -0.659 | 2.636
108585 | 1800.6832 | 1349.6283 | 2250.3236 | 7.907 | -0.989
108595 | 1742.3977 | 2075.281 | 2709.7492 | 16.473 | -3.294
108605 | 1197.8742 | 2173.6493 | 2481.865 | 9.225 | 5.6
108615 | 370.0927 | 2621.6318 | 2647.6257 | 17.131 | 12.191
108625 | 153.9895 | 2496.9229 | 2501.6668 | 8.237 | 5.93
108635 | 409.1532 | 2091.6117 | 2131.2546 | 3.953 | 0
108645 | 482.2711 | 1875.758 | 1936.7637 | 4.612 | 1.647
108655 | 241.578 | 1845.4994 | 1861.2437 | 5.93 | 5.601
108665 | 613.6575 | 1649.4264 | 1759.8815 | 2.636 | -4.283
108675 | 1068.4338 | 1377.3474 | 1743.1685 | 0.659 | -6.589
108685 | 1132.2386 | 251.4808 | 1159.8305 | -15.484 | -2.965
108695 | 1169.8557 | -421.6151 | 1243.5118 | -12.19 | -3.624
108705 | 616.2658 | 5.5122 | 616.2904 | 1.647 | 6.589
108715 | 460.4836 | 131.907 | 479.0037 | -2.306 | 1.647
108725 | 234.267 | -138.2878 | 272.0378 | -6.59 | 4.942
108735 | 306.3896 | -53.286 | 310.9887 | -1.317 | 0.329
108745 | 194.9603 | -187.7471 | 270.6631 | -5.271 | 3.624
108755 | -545.6148 | -261.0176 | 604.8353 | -3.953 | 14.166
108765 | -926.8944 | -1320.0439 | 1612.9628 | -21.415 | 10.872
108775 | -980.9589 | -1884.2701 | 2124.3244 | -16.472 | 8.237
108785 | -893.2214 | -1799.3506 | 2008.8572 | -9.884 | 5.93
108795 | -775.8539 | -1889.0086 | 2042.132 | -12.519 | 4.612
108805 | -661.5753 | -1737.5816 | 1859.2664 | -7.578 | 3.624
108815 | -389.8217 | -1795.9658 | 1837.7851 | -10.542 | 0
108825 | -6.669 | -1629.3226 | 1629.3363 | -5.93 | -3.295
108835 | -113.275 | -1957.4671 | 1960.7419 | -13.837 | 2.966
108845 | -111.4471 | -1940.7795 | 1943.9767 | -8.236 | 0.658
108855 | -533.3591 | -1705.7368 | 1787.1794 | -5.272 | 8.566
108865 | -668.1822 | -1541.4453 | 1680.0361 | -4.942 | 4.943
108875 | -958.1214 | -1436.4612 | 1726.6782 | -4.612 | 9.224
108885 | -1182.5151 | -1126.1045 | 1632.9278 | -0.329 | 8.895
108895 | -1289.6075 | -837.0274 | 1537.4337 | 0.659 | 8.237
108905 | -967.181 | -673.3837 | 1178.5096 | 0.329 | 1.317
108915 | -911.596 | -684.6268 | 1140.0531 | -1.648 | 4.613
108925 | -725.0694 | -854.0459 | 1120.3214 | -4.282 | 0.987
108935 | -592.7832 | -973.4413 | 1139.728 | -4.283 | 1.319
108945 | -715.7102 | -270.6289 | 765.1673 | 8.896 | 4.612
108955 | -881.901 | -355.9233 | 951.0156 | -2.307 | 5.601
108965 | -855.5464 | -711.0908 | 1112.4791 | -5.272 | 3.294
108975 | -800.6486 | -1043.1744 | 1315.0099 | -7.247 | 2.965
108985 | -428.3329 | -1395.0197 | 1459.2975 | -9.555 | -2.965
108995 | -276.874 | -1102.0347 | 1136.2832 | -0.329 | -0.659
109005 | -214.7048 | -837.0713 | 864.1681 | -0.329 | -0.658
109015 | 47.543 | -526.9991 | 529.1393 | 2.636 | -4.284
109025 | 428.2455 | -343.4352 | 548.9462 | 1.977 | -7.247
109035 | 737.2948 | -407.1989 | 842.2675 | -0.989 | -7.908
109045 | 1312.5922 | -387.1149 | 1368.4869 | 0.329 | -14.165
109055 | 1524.0566 | -250.038 | 1544.4312 | 1.977 | -10.214
109065 | 1268.9612 | -66.9756 | 1270.7275 | 3.294 | -3.953
109075 | 896.0456 | -300.3497 | 945.0437 | -2.965 | -0.659
109085 | 610.2448 | -211.9488 | 646.0039 | 1.978 | 0.329
109095 | 363.4733 | 84.3331 | 373.1285 | 4.941 | 1.648
109105 | 123.4025 | 120.7543 | 172.6551 | 1.976 | 2.964
109115 | -2.7733 | -17.0382 | 17.2624 | -0.329 | 2.307
109125 | -272.9666 | -512.1794 | 580.3779 | -7.248 | 5.601
109135 | -485.8186 | -858.4002 | 986.3421 | -6.919 | 5.601
109145 | -855.7434 | -1137.179 | 1423.1911 | -8.236 | 9.554
109155 | -1045.6752 | -895.1532 | 1376.494 | -0.658 | 7.906
109165 | -1103.0393 | -549.2156 | 1232.2067 | 1.647 | 6.919
109175 | -1078.4161 | -664.4672 | 1266.6878 | -3.954 | 5.601
109185 | -1073.3454 | -779.21 | 1326.3629 | -3.623 | 5.6
109195 | -1109.6012 | -720.8048 | 1323.1683 | -1.647 | 5.93
109205 | -957.5972 | -649.0969 | 1156.8574 | -1.319 | 2.636
109215 | -822.6742 | -281.402 | 869.471 | 4.283 | 2.306
109225 | -789.0111 | 40.5224 | 790.051 | 4.942 | 2.965
109235 | -990.964 | 50.4092 | 992.2453 | 1.648 | 6.589
109245 | -808.118 | -60.6055 | 810.3874 | 0 | 0.659
109255 | -671.8691 | 8.4687 | 671.9225 | 2.305 | 1.318
109265 | -590.1384 | 163.8732 | 612.4686 | 3.624 | 0.988
109275 | -611.723 | 45.9799 | 613.4486 | -0.329 | 2.306
109285 | -675.1706 | -252.7088 | 720.914 | -3.624 | 2.965
109295 | -601.8092 | -245.3374 | 649.8959 | 0 | 0.989
109305 | -554.5787 | -351.5681 | 656.6259 | -2.636 | 1.317
109315 | -532.5101 | -338.2585 | 630.8612 | -0.659 | 1.318
109325 | -382.5573 | -423.5894 | 570.7697 | -2.635 | -0.988
109335 | -379.7726 | -311.0313 | 490.8846 | 0.659 | 0.988
109345 | -398.7051 | -130.6541 | 419.5667 | 1.976 | 0.989
109355 | -556.0789 | -224.2834 | 599.6055 | -1.647 | 3.623
109365 | -715.9614 | -299.3851 | 776.0362 | -1.318 | 4.284
109375 | -875.1191 | -198.5577 | 897.3621 | 0.989 | 5.271
109385 | -718.355 | -36.439 | 719.2786 | 2.306 | 0.659
109395 | -484.3196 | 112.4148 | 497.1947 | 2.965 | -0.989
109405 | -451.5992 | 59.7057 | 455.5289 | 0.329 | 0.989
109415 | -260.8991 | -242.9631 | 356.5101 | -3.953 | -2.306
109425 | -5.4134 | -443.2989 | 443.332 | -3.624 | -3.953
109435 | 439.1893 | -364.2402 | 570.577 | -0.329 | -8.567
109445 | 731.1598 | 37.8436 | 732.1385 | 5.271 | -7.906
109455 | 665.8243 | 5.7159 | 665.8489 | -0.33 | -3.624
109465 | 530.1915 | -289.3695 | 604.018 | -3.953 | -2.306
109475 | 423.2179 | -319.3361 | 530.1782 | -0.988 | -1.648
109485 | 212.6431 | -493.4247 | 537.2942 | -4.284 | 0.988
109495 | 6.9182 | -586.4544 | 586.4952 | -3.293 | 1.977
109505 | -27.0707 | -672.7131 | 673.2575 | -3.954 | 0.329
109515 | -51.4834 | -646.6184 | 648.6647 | -2.307 | 0.66
109525 | -134.5576 | -563.3717 | 579.2179 | -1.317 | 1.647
109535 | -256.2683 | -608.0907 | 659.8847 | -2.965 | 2.635
109545 | -305.1193 | -524.0826 | 606.4324 | -0.659 | 1.977
109555 | -216.943 | -333.6088 | 397.9436 | 1.317 | 0
109565 | 42.718 | -163.195 | 168.6933 | 1.977 | -3.295
109575 | 441.2241 | -13.9378 | 441.4442 | 2.636 | -6.918
109585 | 471.7459 | -24.998 | 472.4078 | 0.659 | -2.636
109595 | 317.0835 | 32.5247 | 318.7472 | 1.976 | -0.329
109605 | 334.3054 | -21.9197 | 335.0233 | 0 | -2.306
109615 | 319.8574 | -32.6 | 321.5145 | 0.66 | -1.318
109625 | 206.1146 | -100.5705 | 229.3418 | -0.66 | 0.329
109635 | 240.0732 | -76.7186 | 252.0335 | 0.66 | -1.647
109645 | 247.5452 | -44.3515 | 251.4869 | 0.658 | -0.988
109655 | 262.1778 | -121.3004 | 288.8788 | -0.988 | -1.318
109665 | 162.1958 | -241.265 | 290.7169 | -1.977 | 0.659
109675 | 119.9609 | -244.7485 | 272.5664 | -0.659 | 0
109685 | 104.441 | -195.0306 | 221.2349 | 0 | 0
109695 | 73.0923 | -124.0535 | 143.9852 | 0.659 | 0.33
109705 | 241.052 | -114.0288 | 266.662 | 0 | -2.966
109715 | 243.0837 | -114.6671 | 268.7717 | 0 | -0.658
109725 | 312.2648 | -246.5673 | 397.8753 | -2.306 | -2.306
109735 | 321.4846 | -311.8684 | 447.8998 | -1.647 | -1.318
109745 | 202.4358 | -457.7602 | 500.5244 | -3.624 | 0.658
109755 | 37.0422 | -303.7486 | 305.9989 | 0.988 | 1.977
109765 | 98.7672 | -220.9204 | 241.9934 | 0 | -0.988
109775 | 128.1591 | -114.4096 | 171.7973 | 1.319 | -0.329
109785 | 150.5906 | 44.0766 | 156.9085 | 2.635 | -0.66
109795 | 129.6138 | -35.8175 | 134.4717 | -0.659 | 0
109805 | 90.2074 | -96.1912 | 131.8716 | -0.33 | 0.329
109815 | -109.4166 | -61.6578 | 125.5933 | 0.659 | 3.295
109825 | -398.1986 | -86.4956 | 407.4845 | -0.329 | 5.601
109835 | -503.6062 | -112.4046 | 515.998 | -0.33 | 3.953
109845 | -577.662 | -163.7877 | 600.433 | -0.988 | 4.284
109855 | -604.4565 | -105.7962 | 613.6452 | 0.659 | 3.624
109865 | -453.2598 | 43.6071 | 455.3526 | 2.307 | 0.658
109875 | -437.7945 | 226.7923 | 493.0505 | 3.623 | 2.306
109885 | -534.1333 | 200.2669 | 570.443 | 0.988 | 3.624
109895 | -608.1953 | 161.9192 | 629.3802 | 0.989 | 3.624
109905 | -406.9607 | 342.3841 | 531.8307 | 4.283 | -0.658
109915 | -418.3376 | 550.2363 | 691.2065 | 5.271 | 2.306
109925 | -389.8215 | 708.8125 | 808.9351 | 5.601 | 0.988
109935 | -315.9326 | 569.4984 | 651.2618 | 1.317 | 0.33
109945 | -285.8081 | 452.558 | 535.2523 | 1.318 | 0.658
109955 | -348.2771 | 436.642 | 558.5277 | 1.977 | 1.977
109965 | -475.4781 | 284.689 | 554.1906 | -0.659 | 3.295
109975 | -353.9906 | 357.4142 | 503.045 | 2.635 | -0.329
109985 | -492.2164 | 287.3572 | 569.9572 | 0 | 3.953
109995 | -457.1313 | 134.5243 | 476.5143 | -1.318 | 0.988
110005 | -54.1392 | 223.7811 | 230.2369 | 1.978 | -4.941
110015 | 190.0742 | 235.5985 | 302.7125 | 0.659 | -3.955
110025 | 305.6198 | -28.3477 | 306.9317 | -3.625 | -3.623
110035 | 656.5475 | -137.0666 | 670.7025 | -1.976 | -8.237
110045 | 1069.6843 | -280.0165 | 1105.7277 | -3.624 | -10.542
110055 | 1300.5744 | -261.6764 | 1326.638 | -1.318 | -9.554
110065 | 1261.5232 | -290.9934 | 1294.6498 | -2.306 | -6.26
110075 | 1271.5546 | -197.4851 | 1286.799 | 0 | -6.919
110085 | 872.173 | -274.988 | 914.4967 | -2.635 | 0.66
110095 | 930.367 | -204.8053 | 952.6426 | 0 | -5.601
110105 | 726.588 | -306.7297 | 788.6781 | -2.966 | 0
110115 | 383.1432 | -235.0858 | 449.5154 | 0 | 2.636
110125 | 98.4208 | -370.2412 | 383.0995 | -3.624 | 3.624
110135 | -184.0648 | -230.3992 | 294.896 | 0.989 | 5.271
110145 | -270.123 | -209.7512 | 341.9971 | -0.989 | 3.295
110155 | -354.4296 | -381.908 | 521.0318 | -3.624 | 3.953
110165 | -509.9954 | -320.2247 | 602.1953 | -0.329 | 5.271
110175 | -652.4954 | -54.7266 | 654.7864 | 2.965 | 5.601
110185 | -468.3418 | 114.403 | 482.1121 | 2.635 | 0.659
110195 | -357.6066 | 38.8846 | 359.7144 | -0.329 | 1.318
110205 | -315.9965 | 27.1638 | 317.1619 | 0.659 | 1.317
110215 | -640.5101 | 156.536 | 659.3608 | 2.636 | 7.248
110225 | -924.3102 | 46.8924 | 925.4989 | -0.989 | 7.577
110235 | -1158.5298 | 77.4523 | 1161.1159 | 1.318 | 8.566
110245 | -1443.6377 | 129.6809 | 1449.4506 | 1.317 | 10.542
110255 | -1446.7454 | 217.5606 | 1463.0123 | 2.307 | 6.919
110265 | -1623.1555 | 438.5827 | 1681.3651 | 4.941 | 10.214
110275 | -1601.8686 | 412.986 | 1654.2492 | 1.648 | 6.917
110285 | -1377.5116 | 482.2679 | 1459.4932 | 3.624 | 3.624
110295 | -1479.2984 | 502.2766 | 1562.2438 | 2.636 | 7.908
110305 | -1469.1767 | 604.8187 | 1588.8001 | 4.283 | 5.601
110315 | -1614.0282 | 444.4247 | 1674.0969 | 0 | 8.565
110325 | -1536.5516 | 421.6549 | 1593.3561 | 1.976 | 4.942
110335 | -1611.0774 | 421.4495 | 1665.2898 | 1.648 | 7.577
110345 | -1643.1159 | 397.3858 | 1690.4867 | 1.317 | 6.589
110355 | -1522.8629 | 439.4033 | 1584.9879 | 2.307 | 4.283
110365 | -1243.9113 | 439.312 | 1319.2083 | 1.647 | 0.988
110375 | -1048.4841 | 548.1804 | 1183.1402 | 3.624 | 0.989
110385 | -1029.6363 | 601.0237 | 1192.2166 | 2.965 | 2.635
110395 | -1087.2198 | 723.5649 | 1305.9836 | 4.612 | 3.624
110405 | -1066.7323 | 746.0762 | 1301.7478 | 3.294 | 2.636
110415 | -943.1862 | 769.9905 | 1217.5736 | 3.624 | 0.988
110425 | -927.1124 | 778.8975 | 1210.8752 | 3.295 | 2.306
110435 | -892.1469 | 710.4036 | 1140.4383 | 1.977 | 1.648
110445 | -876.6834 | 584.2307 | 1053.5176 | 0.658 | 1.976
110455 | -868.1364 | 326.208 | 927.4009 | -2.306 | 1.977
110465 | -839.7625 | 273.8186 | 883.2767 | 0 | 1.647
110475 | -758.3947 | 323.382 | 824.4625 | 0.989 | 0.659
110485 | -868.7418 | 314.7032 | 923.9861 | 0.329 | 3.624
110495 | -869.2891 | 276.9534 | 912.3414 | 0 | 1.977
110505 | -826.141 | 210.116 | 852.4422 | -0.658 | 1.647
110515 | -721.7114 | 255.6809 | 765.6632 | 0.988 | 0.329
110525 | -489.3653 | 355.6797 | 604.9681 | 1.976 | -2.306
110535 | -375.4023 | 287.2492 | 472.6933 | -0.329 | -1.317
110545 | -81.4712 | 276.8517 | 288.5904 | 0.658 | -5.271
110555 | -0.56892 | 265.2691 | 265.2697 | 0.331 | -2.636
110565 | -104.7665 | 136.2194 | 171.848 | -1.648 | -0.33
110575 | -191.5762 | 188.9641 | 269.089 | 0.988 | 0
110585 | -290.5135 | 229.5647 | 370.2676 | 0.66 | 0.989
110595 | -239.0287 | 185.5111 | 302.5708 | -0.331 | -0.989
110605 | -277.9038 | 51.3727 | 282.6123 | -1.976 | 0.659
110615 | -300.0759 | 28.7052 | 301.4458 | -0.659 | 0.33
110625 | -304.4029 | -49.7026 | 308.4339 | -1.976 | 0.329
110635 | -209.4735 | -157.7397 | 262.2231 | -2.637 | -1.318
110645 | -324.3023 | -119.2007 | 345.5152 | -0.658 | 1.977
110655 | -563.2526 | -100.2929 | 572.112 | -0.988 | 4.283
110665 | -131.0414 | 90.3187 | 159.1519 | 2.306 | -5.93
110675 | 107.3216 | 295.927 | 314.7867 | 3.295 | -3.624
110685 | 3.7834 | 311.741 | 311.764 | 1.317 | 0
110695 | -216.9966 | 439.0202 | 489.7206 | 3.624 | 2.307
110705 | -572.4686 | 243.4717 | 622.0923 | -1.648 | 5.929
110715 | -649.975 | 340.0959 | 733.5754 | 2.966 | 2.965
110725 | -667.2388 | 248.2475 | 711.923 | -0.659 | 2.965
110735 | -577.4225 | 320.8455 | 660.5745 | 2.306 | 0.988
110745 | -586.5812 | 211.5675 | 623.569 | -0.988 | 2.307
110755 | -690.7431 | 279.0503 | 744.9799 | 1.976 | 3.624
110765 | -845.9245 | 261.1012 | 885.3034 | 0.33 | 4.941
110775 | -861.2356 | 420.0235 | 958.1996 | 3.623 | 3.295
110785 | -916.3394 | 421.2616 | 1008.5332 | 1.319 | 4.283
110795 | -798.3078 | 472.4126 | 927.6146 | 2.636 | 1.318
110805 | -777.2109 | 410.486 | 878.9514 | 0.658 | 2.635
110815 | -729.8176 | 392.2259 | 828.5378 | 1.318 | 1.647
110825 | -555.7299 | 490.1112 | 740.9756 | 2.965 | -0.658
110835 | -427.1223 | 490.855 | 650.6705 | 1.647 | -0.659
110845 | -387.8791 | 381.4558 | 544.0208 | 0 | 0
110855 | -403.3114 | 264.2542 | 482.1726 | -0.658 | 0.659
110865 | -373.9472 | 246.4946 | 447.8796 | 0.329 | 0
110875 | -247.0789 | 71.6334 | 257.2534 | -2.635 | -1.648
110885 | -225.9571 | 120.2297 | 255.9527 | 0.658 | -0.329
110895 | -108.5226 | 260.9423 | 282.6094 | 1.977 | -2.306
110905 | -83.88 | 254.3791 | 267.8518 | 0.329 | -0.989
110915 | 75.183 | 326.1401 | 334.6937 | 1.977 | -3.624
110925 | 56.5683 | 294.8733 | 300.2503 | 0.329 | -0.987
110935 | -54.4934 | 257.2393 | 262.9479 | 0.331 | 0.329
110945 | -65.679 | 238.013 | 246.9087 | 0.329 | -0.659
110955 | 21.7957 | 187.6084 | 188.8703 | -0.329 | -1.977
110965 | 148.1652 | 436.9686 | 461.4049 | 4.611 | -2.965
110975 | 238.214 | 103.4377 | 259.7023 | -4.611 | -2.965
110985 | 337.3754 | 180.2585 | 382.5118 | 1.976 | -3.624
110995 | 183.4085 | 483.7183 | 517.322 | 4.941 | 0.33
111005 | 75.3322 | 417.9061 | 424.6415 | 0.33 | 0
111015 | -70.7323 | 174.2097 | 188.0215 | -2.306 | 1.646
111025 | -80.6861 | 9.6489 | 81.261 | -2.306 | 0
111035 | -260.9127 | 103.6195 | 280.7355 | 0.988 | 3.295
111045 | -373.1827 | 169.9526 | 410.06 | 0.659 | 2.636
111055 | -146.2411 | 23.7343 | 148.1545 | -2.306 | -2.307
111065 | 132.6338 | 74.8065 | 152.2752 | 0.659 | -3.953
111075 | 329.7762 | 254.3834 | 416.4892 | 2.635 | -4.283
111085 | 419.0273 | -45.5501 | 421.4958 | -4.612 | -3.624
111095 | 669.5232 | -39.0455 | 670.6608 | 0 | -6.918
111105 | 621.3234 | -54.1256 | 623.6765 | -1.318 | -2.636
111115 | 613.5327 | 101.6657 | 621.899 | 1.977 | -3.624
111125 | 601.2134 | 191.2651 | 630.904 | 1.318 | -2.965
111135 | 537.3726 | 98.4598 | 546.3183 | -0.989 | -1.977
111145 | 419.8825 | -36.8539 | 421.4968 | -1.977 | -0.658
111155 | 437.2041 | -183.231 | 474.0475 | -2.964 | -2.306
111165 | 565.7012 | -16.0344 | 565.9284 | 1.647 | -3.954
111175 | 603.0017 | -4.3618 | 603.0175 | -0.659 | -2.965
111185 | 425.0413 | 5.6983 | 425.0795 | 0 | 0.329
111195 | 327.1776 | 156.4801 | 362.6723 | 2.307 | -0.329
111205 | 166.3894 | 194.7054 | 256.1164 | 0.987 | 1.647
111215 | 120.9072 | 202.7366 | 236.0522 | 0.989 | 0.33
111225 | 86.249 | 175.2045 | 195.2831 | 0.329 | 0.658
111235 | 72.729 | 96.9691 | 121.2127 | -0.659 | 0.33
111245 | 82.5456 | 80.0181 | 114.9637 | 0 | 0
111255 | 144.7709 | 250.9028 | 289.6737 | 2.965 | -0.988
111265 | 74.2937 | 134.8395 | 153.952 | -1.318 | 0.988
111275 | -108.0569 | -157.2268 | 190.7788 | -4.282 | 2.965
111285 | -143.2138 | -51.7535 | 152.2781 | 0.989 | 1.318
111295 | -284.3106 | 48.47 | 288.4127 | 0.658 | 3.624
111305 | -328.1106 | -61.4637 | 333.8179 | -1.977 | 2.306
111315 | -595.5494 | -61.0207 | 598.6674 | -0.329 | 6.59
111325 | -796.6337 | 36.0291 | 797.448 | 0.988 | 6.259
111335 | -729.7628 | 7.8627 | 729.8052 | -0.659 | 2.965
111345 | -671.0405 | -10.176 | 671.1177 | -0.329 | 2.965
111355 | -577.473 | 119.541 | 589.7162 | 1.977 | 1.647
111365 | -419.3334 | 164.4229 | 450.417 | 0.988 | 0
111375 | -235.6994 | 159.9878 | 284.8689 | 0.659 | -1.318
111385 | -170.6579 | 62.5899 | 181.7735 | -0.989 | -0.329
111395 | -24.6354 | 200.2024 | 201.7124 | 2.636 | -2.306
111405 | 303.8682 | 114.3961 | 324.6881 | -0.988 | -5.93
111415 | 623.8838 | 57.5563 | 626.5331 | -0.33 | -7.248
111425 | 686.8009 | 190.6856 | 712.7808 | 2.306 | -4.613
111435 | 752.5412 | 182.841 | 774.4347 | 0.33 | -5.271
111445 | 669.2762 | 192.3835 | 696.3778 | 0.988 | -2.636
111455 | 394.1539 | 114.7088 | 410.5062 | -0.659 | 0.989
111465 | 126.7418 | -84.0891 | 152.1002 | -2.965 | 2.306
111475 | 93.2489 | -112.2606 | 145.9376 | -0.988 | 0
111485 | 133.6351 | 25.2527 | 136.0002 | 1.318 | -0.659
111495 | 175.174 | 201.6033 | 267.0764 | 2.635 | -0.988
111505 | 257.7495 | 394.6907 | 471.3974 | 3.953 | -1.977
111515 | 144.774 | 297.5001 | 330.8562 | 0 | 0.988
111525 | 159.5292 | 105.6885 | 191.3625 | -1.646 | -0.988
111535 | 194.6074 | -132.2695 | 235.3025 | -3.624 | -0.989
111545 | 173.6286 | -104.5218 | 202.6615 | -0.33 | -0.329
111555 | 327.2227 | -171.2673 | 369.3334 | -2.306 | -3.295
111565 | 396.6122 | -206.8756 | 447.324 | -1.648 | -2.306
111575 | 350.0009 | -320.3214 | 474.4538 | -3.294 | -0.988
111585 | 314.5077 | -433.4772 | 535.5535 | -3.624 | -0.988
111595 | 202.8514 | -337.8275 | 394.0508 | -0.659 | 0.659
111605 | 118.9408 | -333.1822 | 353.7757 | -1.977 | 0.659
111615 | 50.2779 | -413.2863 | 416.3333 | -2.964 | 0.988
111625 | 40.0186 | -494.1635 | 495.7813 | -3.295 | 0.33
111635 | 210.0009 | -512.3347 | 553.7032 | -2.636 | -2.636
111645 | 71.5341 | -522.7126 | 527.5846 | -2.635 | 1.976
111655 | 86.7807 | -325.6248 | 336.9903 | 0.988 | -0.658
111665 | 15.6531 | -210.8159 | 211.3962 | 0.33 | 1.318
111675 | 21.7839 | -116.3804 | 118.4015 | 0.988 | 0
111685 | 251.4951 | -143.7944 | 289.7009 | -0.659 | -3.624
111695 | 425.8158 | -20.857 | 426.3263 | 1.977 | -3.624
111705 | 548.2845 | 88.4967 | 555.3805 | 1.976 | -3.954
111715 | 538.224 | 155.5898 | 560.2618 | 1.977 | -2.307
111725 | 523.5967 | 222.5258 | 568.9211 | 2.306 | -2.305
111735 | 506.5164 | 178.376 | 537.0073 | 0.659 | -1.977
111745 | 248.7828 | -89.6243 | 264.4341 | -3.294 | 2.306
111755 | -160.9704 | -364.1662 | 398.1564 | -4.613 | 5.93
111765 | -444.7886 | -483.0537 | 656.6413 | -3.623 | 5.931
111775 | -585.3137 | -378.8362 | 697.2152 | -0.66 | 5.27
111785 | -643.815 | -238.6315 | 686.6169 | 0.329 | 4.613
111795 | -788.5345 | -288.9367 | 839.8042 | -1.976 | 6.259
111805 | -1027.8946 | -386.0537 | 1098.0004 | -2.635 | 8.237
111815 | -1036.3724 | -353.8855 | 1095.1268 | -0.989 | 5.272
111825 | -968.4739 | -203.9379 | 989.7132 | 0.989 | 4.282
111835 | -805.0136 | -154.9728 | 819.7947 | 0 | 1.977
111845 | -618.6251 | -330.5311 | 701.3899 | -3.295 | 0.658
111855 | -328.8611 | -334.2698 | 468.92 | -0.988 | -2.306
111865 | 87.6591 | -327.1388 | 338.6797 | -1.318 | -5.93
111875 | 227.6547 | -121.734 | 258.1586 | 2.306 | -3.294
111885 | 235.6174 | 21.6429 | 236.6094 | 1.977 | -2.306
111895 | 154.9496 | -109.1893 | 189.5565 | -1.648 | -0.66
111905 | 64.7948 | -201.4977 | 211.6593 | -1.317 | 0
111915 | -62.9063 | -264.1665 | 271.5532 | -1.647 | 1.318
111925 | -188.1689 | -249.5511 | 312.5432 | -0.66 | 1.977
111935 | -192.5517 | -135.8508 | 235.6514 | 0.989 | 0.66
111945 | -298.3497 | -14.0054 | 298.6782 | 1.647 | 2.635
111955 | -427.9259 | 65.8313 | 432.9599 | 1.648 | 3.294
111965 | -592.1225 | -93.6081 | 599.476 | -1.977 | 4.612
111975 | -597.0675 | -223.8608 | 637.6545 | -1.977 | 2.637
111985 | -413.3933 | -314.7808 | 519.5969 | -2.307 | -0.331
111995 | -435.6196 | -395.6119 | 588.4498 | -2.635 | 2.307