## READ ME
BAL-002-2 Compliance Calculations for Reportable Balancing Contingency Events
The rules to determine if a Balancing Contingency Event whose size exceeds the applicable lower reporting threshold size
is exempt from compliance evaluation are provided in the "EXEMPTION" tab. It is assumed in the remaining tabs provided in CRFORM1 that the
Reportable Balancing Contingency Event is NOT EXEMPT. See the recommendations for documenting exempt events in the "EXEMPTION" tab.
A verbal description of the compliance calculation process is provided in the "Description" tab
The mathematical expression of the compliance calculation process is provided in the "Formulas" tab.
The step by step instructions for entering data on the "Calculator" tab are contained in the "Entry instructions" tab.
The "Calculator" tab is used for entering the required data and computing the compliance score for the Reportable Balancing Contingency Event.
To facilitate compliance checks, It is recommended that each compliance evaluation performed within a year be stored in a folder for that year.
It is recommended that the Calculator tab's results for each Reportable Balancing Contingency Event be stored in a file with the following naming
convention: BAL-002-2 MM-DD-YYYY HHMMSS where the month day, year, hour, minute, and second are included in the file name.
Once the user has sufficent familiarity with this compliance calculation process, the user should simply go directly to the Calculator tab to
enter the needed data for the compliance calculation and save the result in that year's folder.

## EXEMPTION
Rules For Determining if a Balancing Contingency Event is Exemp From Compliance Evaluation
Under unusual circumstances, the Responsible Entity may experience a Balancing Contingency Event that would otherwise qualify as a Reportable
Balancing Contingency Event based on its size exceeding the reportable event minimum size threshold(s), but it is determined from the rules in BAL-002-2
that it should be exempt from compliance evaluation. This tab is intended to assist in determining if the event warrants exemption.
For ease of maintenance of CRFORM1 over time, the subsequent tabs within CRFORM1 assume that the Reportable Balancing Contingency Event
is not exempt. Changes to exemption rules will require changes only to this tab.
If a Responsible Entity determines that exemption is warranted by the rules described below, then reporting of the event is not required within CRFORM1.
It is recommended that CRFORM1 be completed with an explanation being included in the comment field in the "calculator" tab.
It is also recommended that the CRFORM1 for such an event be archived with the usual naming convention described in the "READ ME" tab, but with the
characters "EXEMPT" being added at the end of the file name (BAL-002-2 MM-DD-YYYY HHMMSS EXEMPT). Some form of documentation is recommended.
If the Balancing Contingency Event meets any of the following criteria, it is exempt from compliance evaluation.
(1) If the Responsible Entity is experiencing a Reliability Coordinator approved Energy Emergency Alert Level under which Contingency Reserves
have been activated.
(2) If the magnitude of the Balancing Contingency Event exceeds the Most Severe Single Contingency (MSSC)
(3) If the sum of the megawatt losses of multiple Balancing Contingency Events occurring within 105 minutes of each other exceeds MSSC.

## Description
Description Of Compliance Calculations For Reportable Balancing Contingency Events
To determine compliance with R1, the measured contingency reserve response is computed and compared with the megawatts lost
as follows (assuming all resource loss values, i.e. Balancing Contingency Events, are positive):
(1) If the Pre-Reportable Contingency Event ACE Value is greater than or equal to zero, then the measured contingency reserve response equals
(a) the megawatt value of the Reportable Balancing Contingency Event plus (b) the most positive ACE value within its Contingency Event
Recovery Period (and following the occurrence of the last subsequent event, if any) plus
© the sum of the megawatt losses of subsequent Balancing Contingency Events occurring within the Contingency Event
Recovery Period of the Reportable Balancing Contingency Event.
(2) If the Pre-Reportable Contingency Event ACE Value is less than zero, then the measured contingency reserve response equals
(a) the megawatt value of the Reportable Balancing Contingency Event plus (b) the most positive ACE value within its Contingency Event
Recovery Period (and following the occurrence of the last subsequent event, if any) plus
© the sum of the megawatt losses of subsequent Balancing Contingency Events occurring within the Contingency Event
Recovery Period of the Reportable Balancing Contingency Event, minus (d) the Pre-Reportable Contingency Event ACE value.
(3) If the measured contingency reserve response is greater than or equal to the megawatts lost,
then the Reportable Balancing Contingency Event Compliance equals 100 percent.
(4) If the measured contingency reserve response is less than or equal to zero,
then the Reportable Balancing Contingency Event Compliance equals 0 percent.
(5) If the measured contingency reserve response is less than the megawatts lost but greater than zero,
then the Reportable Balancing Contingency Event Compliance equals
100% * (1 – ((megawatts lost – measured contingency reserve response) / megawatts lost)).

## Formulas
Formulas Used In The Compliance Calculations For Reportable Balancing Contingency Events
Variable definitions:
ACE_BEST – most positive ACE during the Contingency Event Recovery Period occurring after the last subsequent event, if any (MW)
ACE_PRE - Pre-Reportable Contingency Event ACE Value (MW)
COMPLIANCE - Reportable Balancing Contingency Event Compliance percentage (0 - 100%)
MEAS_CR_RESP - measured contingency reserve response for the Reportable Balancing Contingency Event (MW)
MW_LOST - megawatt loss of the Reportable Balancing Contingency Event (MW)
SUM_SUBSQ - sum of the megawatt losses of subsequent Balancing Contingency Events occurring within the
Contingency Event Recovery Period of the Reportable Balancing Contingency Event (MW)
The formulas used:
If ACE_PRE is greater than or equal to 0, then
MEAS_CR_RESP = MW_LOST +ACE_BEST + SUM_SUBSQ [1]
If ACE_PRE is less than 0, then
MEAS_CR_RESP = MW_LOST +ACE_BEST + SUM_SUBSQ – ACE_PRE [2]
If MEAS_CR_RESP is greater than or equal to MW_LOST, then
COMPLIANCE = 100 [3]
If MEAS_CR_RESP is less than or equal to 0, then
COMPLIANCE = 0 [4]
If MEAS_CR_RESP is greater than 0, and,
MEAS_CR_RESP is less than MW_LOST, then
COMPLIANCE = 100 * (1 – ((MW_LOST – MEAS_CR_RESP)/ MW_LOST)) [5]

## Entry Instructions
Entry Instructions For The Compliance Calculations For Reportable Balancing Contingency Events
All enterable fields are shown in green. Most entries are self-explanatory.
Enter the Balancing Authority name in cell B4.
If actively participating in a Reserve Sharing Group for this Reportable Balancing Contingency Event, enter its name in cell B5.
Enter the net MW loss, date, time, and resource name of the Reportable Balancing Contingency Event in row 8. (enter loss as a positive value)
Losses associated subsequent Balancing Contingency Events are also entered as positive values.
Entry of subsequent Balancing Contingency Events
For most Reportable Balancing Contingency Events, there are no subsequent Balancing Contingency Events, so entries are not needed in rows 13-16.
Enter the MW loss, date, time, and resource name of the subsequent Balancing Contingency Events in rows 13-16 for up to 4 events in
chronological order, if the Reportable Balancing Contingency Event is followed by subsequent Balancing Contingency Events within 15 minutes of its start.
If there are more than 4 subsequent Balancing Contingency Events, sum the 4th through "nth" largest and put the sum in as the fourth event.
The summation of subsequent Balancing Contingency Events is computed for you in cell B17.
Enter the Most Severe Single Contingency (MSSC) in MW in cell B19.
Enter the Pre-Reportable Contingency ACE Value in MW in cell B20.
Enter the most positive ACE value in the Contingency Event Recovery Period in cell B21.
Note that if a subsequent Balancing Contingency Event is included, then the most positive ACE value cannot precede its occurrence.
Note that if multiple subsequent Balancing Contingency Events are included, then the most positive ACE value cannot precede
the occurrence of the subsequent Balancing Contingency Event that is the last to occur.
Optionally enter comments in cells A28 through B39 to clarify what occurred that affected the recovery.
The Reportable Balancing Contingency Event Compliance is calculated for you in cell B25.

## Calculator
CR Form 1 - Compliance Calculations For Reportable Balancing Contingency Events
Enterable fields are in green
Enter name of the Balancing Authority in which the Reportable Balancing Contingency Event occurred
If a Reserve Sharing Group deployed contingency reserve for this event, enter its name here
|  | date | time
| MW | mm/dd/yy | hh:mm:ss | resource name
Enter the MW loss, date, time, and resource name of the Reportable Balancing Contingency Event | 0
(resource MW loss is entered as a positive value)
Enter the MW loss, date, time, and resource name of subsequent Balancing Contingency Events
for up to 4 events in chronological order, and sum any additional events with the 4th event
Subsequent Balancing Contingency Event #1 | 0
Subsequent Balancing Contingency Event #2 | 0
Subsequent Balancing Contingency Event #3 | 0
Subsequent Balancing Contingency Event #4 | 0
summation of subsequent Balancing Contingency Events | 0
Enter the Most Severe Single Contingency (MSSC) in MW | 0
Enter the Pre-Reportable Contingency ACE Value in MW | 0
Enter the most positive ACE value in the Contingency Event Recovery Period | 0
Measured Contingency Reserve Response = | 0
Reportable Balancing Contingency Event Compliance (%) = | 0
Optionally enter comments in the fields below to clarify what occurred that affected the recovery